46340 | 0 | ASCO VALVE |  |  |  |  | 2010-09-18 | 2010-10-18 13:09 | 2010-11-11 | POTENTIAL EXTERNAL LEAKAGE IN SOLENOID VALVE The following notification was received via fax: "On 9/18/10 a single solenoid valve was returned to ASCO with a reported problem of external leakage at the bonnet area below the coil housing. The valve was returned from Cooper Nuclear Station through AREVA, who was the distributor. "The returned valve was retested at ASCO. No external leakage was observed when the valve was tested in the de-energized state. However, when the valve was tested in the energized state, the reported leakage was confirmed. The root cause of the leakage was determined to be a misaligned O-ring between the solenoid base sub-assembly and the valve body. "The customers that were shipped affected valves are being notified of the potential non-conformance. ASCO will recommend the affected valves be returned to be retested in accordance with updated test procedures." * * * UPDATE FROM ROBERT ARNONE TO JOE O'HARA VIA FAX AT 1308 ON 11/11/10 * * * "In our continuing investigation of the external leakage in NP8320 solenoid valves (Ref A), ASCO has identified an additional group of valves which could be potentially susceptible to such leakage. The initial review focused on our standard NP8320 products and did not include our special construction valves. However, we expanded our review to include all special as well as standard NP8320 valves. As a result, the quantity of potentially affected valves has increased from 174 to 438. In response to this new information, revised notices were sent to the original customers and the newly identified customers: ASCO Canada, SPX Industries, and Flowserve. "As of this date, 115 valves have been returned. None of these returned valves has exhibited external leakage when retested per the updated procedure." Through their expanded review process, ASCO did not identify any additional commercial nuclear power plant customers which had purchased valves susceptible to the leakage issue. Notified R4DO (Gaddy) and Part 21 Group via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-10-18
46339 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-10-18 10:00 | 2010-10-18 09:34 | 2010-10-18 | UNAVAILABILITY OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) FOR SCHEDULED MAINTENANCE "At approximately 10:00 a.m. on Monday, October 18, 2010, the Cook Nuclear Plant (CNP) Unit 2 Plant Process Computer (PPC) will be removed from service for scheduled power supply distribution panel preventive maintenance. This will remove Unit 2 PPC data input to ERDS rendering the system non functional for providing data to the NRC Operations Center. The scheduled maintenance will also affect the Safety Parameter Display System (SPDS), the Real Time Data Repository (RDR), and PPC data to Emergency Response Facilities at CNP. "The scheduled maintenance is expected to take up to 6 hours to complete. "Compensatory measures exist within the CNP Emergency Response procedure to provide plant data via the Emergency Notification System to the NRC Operations Center until the ERDS can be returned to service. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)." CNP Unit 2 is currently defueled. * * * UPDATE FROM DEAN BRUCK TO JOE O'HARA AT 1518 EDT ON 10/18/10 * * * "Functionality has been restored to ERDS following restoration of the Unit 2 PPC at 1422. SPDS, RDR, and PPC data to Emergency Response Facilities at CNP have also been restored to service at 1422." The NRC Resident Inspector has been notified. Notified R3DO(Orth). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-18
46338 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-10-17 09:53 | 2010-10-17 14:35 | 2010-10-17 | REACTOR TRIP ON LOW STEAM GENERATOR LEVEL DURING PLANT STARTUP "At 0953 CDT, Wolf Creek experienced a reactor trip due to low steam generator level. At the time of the trip the plant was in Mode 1 approximately 16% power following a forced outage. A feedwater isolation signal [FWIS] was generated due to high S/G level (P-14) in 'B' S/G [steam generator]. The FWIS resulted in a low S/G level. Although a manual reactor trip was ordered by the duty Shift Manager, the manual trip signal was not inserted before the reactor automatically tripped on low steam generator level. "Auxiliary Feed Water systems actuated as expected due to low steam generator levels. "The plant is presently in Mode 3 at normal operating temperature and pressure. "The Senior Resident Inspector has been notified." All control rods fully inserted during the trip. All three Auxiliary Feedwater Pumps started to maintain S/G levels. The plant was stabilized with the motor driven startup feedwater pump maintaining S/G level. Decay heat is being removed using the atmospheric steam dumps. There is no primary to secondary leakage. The plant is in its normal shutdown electrical lineup. A press release will be issued. | 0 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-10-17
46337 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-10-17 05:12 | 2010-10-17 06:38 | 2010-10-18 | AUTOMATIC REACTOR TRIP DUE TO 4 KV GROUP BUS UNDERVOLTAGE CONDITION "On 10/17/10 at 0512 [EDT], Unit 2 experienced an [automatic] reactor trip due to 4 kV group bus under voltage. While restoring the voltage regulator to automatic, following a swap to manual at 0123 [EDT] on 10/17/10 while 500 kV line 5014 was being restored to service, the reactor tripped after placing the voltage regulator in automatic. "The crew entered EOP [Emergency Operating Procedure] Trip 1, and then EOP Trip 2 as required. The plant was stabilized at no load conditions. All rods fully inserted on the trip, and all systems responded as designed with RCS [Reactor Coolant System] temperature being controlled via 21 RCP [Reactor Coolant Pump] and the steam dump system. 22, 23, and 24 RCP's tripped on group bus under voltage. The AFW [Auxiliary Feed Water] Pumps started in response to low steam generator levels. 23 AFW was subsequently tripped per procedure since 21 and 22 AFW pumps were in service feeding 21-24 steam generators. "Salem Unit 2 is currently in Mode 3. RCS temperature is 547 degrees. RCS pressure is 2235 pounds. All Emergency Core Cooling Systems and Engineered Safety Function Systems are available. No personnel injuries occurred as a result of the trip. No radiological release is in progress due to this event." At 0123 EDT, following the restoration of a 500 kV line, perturbation in the line caused an over current condition which shifted the voltage regulator to manual. After engineering's recommendation, the voltage regulator was placed in automatic shortly prior to the reactor trip. The plant is in a normal shutdown electrical lineup. There was no impact on Salem Unit 1 as a result of this event. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BILL MUFFLEY TO JOHN SHOEMAKER 1138 EDT ON 10/18/10 * * * Notified by the licensee that the AFW Pumps started on loss of Steam Generator Feed Pumps which had tripped on low suction pressure. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-10-17
46336 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-10-15 23:21 | 2010-10-16 01:52 | 2010-10-16 | AUTOMATIC REACTOR TRIP DUE TO A TURBINE TRIP "An automatic reactor trip of Salem Unit 1 [occurred] due to a turbine trip above P-9. The crew entered EOP [Emergency Operating Procedure] Trip 1, appropriately transitioned to EOP Trip 2, and stabilized the plant at no load conditions. All rods fully inserted on the trip, and all systems responded as designed with decay heat removal being removed via the steam dump system with condenser vacuum being maintained. The Auxiliary Feed Water Pumps automatically started due to low steam generator levels. Salem Unit 1 is currently in Mode 3. Reactor Coolant System temperature is 547 degrees, and pressure is 2235 pounds. All Emergency Core Cooling Systems and Engineered Safety Function Systems are available. No personnel injuries occurred as a result of the trip. No radiological release [occurred] due to this event." Approximately 5 minutes prior to the turbine trip, Salem Unit 1 lowered reactive loading on the voltage regulator as requested by the load dispatcher while Hope Creek Unit 1 was coming off line due to their outage. The cause of the trip is still under investigation. There was no impact on Salem Unit 2 as a direct result of this event. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-10-16
46335 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2010-10-14 07:54 | 2010-10-14 16:55 | 2010-10-14 | CONTRACT NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2010-10-14
46334 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2010-10-14 04:22 | 2010-10-14 15:15 | 2010-10-14 | BOTH TRAINS OF CONTROL ROOM AIR CONDITIONING INOPERABLE "While Control Room Air Conditioning System 'A' was tagged out for planned maintenance, the 'B' Control Room Air Conditioning System tripped and could not be restarted. TS 3.7.4 Condition B was entered at 0422 [CDT] 10/14/10, for both Control Room Air Conditioning systems inoperable. Temporary cooling was used to assist in maintaining control room temperature below TS limit of 90 degrees F. Corrective maintenance was performed on Control Room Air Conditioning System 'B' and it was restored to functional status at 1017 [CDT] 10/14/10. No TS limits were exceeded and no plant shutdown actions were required." The licensee noted that their report was late and did not meet the 8-hour reporting criteria. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-10-14
46333 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-04-06 | 2010-10-14 13:43 | 2010-10-14 | OHIO AGREEMENT STATE REPORT - D90 DOSE LESS THAN PRESCRIBED DOSE The following information was obtained from the State of Ohio via email: "Note: This information is reported as a result of a special inspection performed [by the State of Ohio] on July 28 and 29, 2010, limited to the licensee's prostate implant program. "The licensee performed a prostate seed implant on April 6, 2010. The patient was prescribed a dose of 100 Gy using Iodine-125 seeds. The D90 post implant dosimetry performed on May 12, 2010, indicated a D90 of 62.5 Gy was given. This is a difference of 37.5% from the prescribed dose. The post plan dosimetry was performed by a radiation therapist on May 12, 2010, and the results were reviewed by a medical physicist on May 18, 2010. This qualifies as a Medical Event per rule 3701:1-58-101(A)(1)(a) of the Ohio Administrative Code (OAC). "The licensee failed to notify by telephone the Ohio Department of Health no later than the next calendar day after the discovery of the medical event, and submit a written report within fifteen days after discovery of the medical [event]. This is a violation of ODH requirements as referenced in rule 3701:1-58-101 (c) and (D)." Ohio Report Number: OH100025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-10-19
46332 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-08-30 | 2010-10-14 13:43 | 2010-11-09 | OHIO AGREEMENT STATE REPORT - ABANDONED MOISTURE DENSITY GAUGES The following information was obtained from the State of Ohio via email: "On August 11, 2010, the licensee submitted a request to [the State of Ohio to] terminate their portable gauge license. On September 9, 2010, the Ohio Department of Health (ODH) was notified by a third party that Lee Testing had vacated the premises at 3530 Parkway Lane and had left behind a total of seven (7) devices containing radioactive materials. Upon contacting the building owner, it was determined that the licensee had moved out of the building sometime during the prior week, and that the keys to the building and its contents were relinquished to the building owner. "On September 13, 2010, representatives from ODH and a licensed service provider visited the 3530 Parkway Lane location and removed the seven devices present at that location. This removal was determined to be necessary as authorized under rule 3701:1-38-06(E) of the Ohio Administrative Code (OAC). The seven devices are currently in a safe and secure storage location pending a decision on final disposition. "ODH is conducting an ongoing investigation. "The NRC Registry of Radioactive Sealed Sources and Devices indicates that [three Troxler Model] 3411-B gauges contain a Cs-137 source with a maximum activity of 0.33 GBq (9 mCi) and an Am-Be source with a maximum activity of 1.63 GBq (44 mCi). The Registry indicates that [Troxler Model] 3241-C gauge contains an Am-Be source with a maximum activity of 11.1 GBq (300 mCi). The Registry also indicates that the [three Humboldt Scientific Model] 5001 gauges contain a Cs-137 source with a maximum activity of 0.41 GBq (11 mCi) and an Am-Be source with a maximum activity of 1.63 GBq (44 mCi)." Ohio Report Number: OH100494 * * * UPDATE FROM STEPHEN JAMES TO JOHN KNOKE AT 1212 EST ON 11/09/10 * * * The state of Ohio provided serial numbers for the following sources: Source Number: 1 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 47-2403 Radionuclide or Voltage (kVp/MeV): AM-241 Source Number: 10 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 508801 Radionuclide or Voltage (kVp/MeV): CS-137 Source Number: 11 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: NJ00192 Radionuclide or Voltage (kVp/MeV): AM-241 Source Number: 12 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 5843GF Radionuclide or Voltage (kVp/MeV): CS-137 Source Number: 13 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: NJ00663 Radionuclide or Voltage (kVp/MeV): AM-241 Source Number: 14 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 1195GH Radionuclide or Voltage (kVp/MeV): CS-137 Source Number: 2 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 00009159 Radionuclide or Voltage (kVp/MeV): CS-137 Source Number: 3 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 475790 Radionuclide or Voltage (kVp/MeV): AM-241 Source Number: 4 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 406594 Radionuclide or Voltage (kVp/MeV): CS-137 Source Number: 5 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 477088 Radionuclide or Voltage (kVp/MeV): AM-241 Source Number: 6 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: 409291 Radionuclide or Voltage (kVp/MeV): CS-137 Source Number: 7 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: Unknown Radionuclide or Voltage (kVp/MeV): AM-241 Source Number: 8 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: Unknown Radionuclide or Voltage (kVp/MeV): CS-137 Activity: Ci GBq Source Number: 9 Source/Radioactive Material: SEALED SOURCE GAUGE Serial Number: XX00166 Radionuclide or Voltage (kVp/MeV): AM-241 Ohio Item Number: OH100020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-10-19
46331 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-10-14 09:15 | 2010-10-14 13:18 | 2010-10-28 | EMERGENCY SIRENS WILL BE TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "From October 14, 2010 to October 22, 2010, Palo Verde personnel will be performing maintenance on public prompt notification system sirens. Sirens will be removed from service one at a time, and then each will be restored prior to continuing to the next siren. "Siren #36 provides notification to approximately 470 members of the public within five miles of Palo Verde. "Siren #23 provides notification to approximately 614 members of the public within five miles of Palo Verde. "Siren #25 provides notification to approximately 335 members of the public within five miles of Palo Verde. "Siren #18 provides notification to approximately 586 members of the public within five miles of Palo Verde. "Siren #15 provides notification to approximately 1133 members of the public within five to ten miles of Palo Verde. "Siren #22 provides notification to approximately 1015 members of the public within five miles of Palo Verde. "Siren #17 provides notification to approximately 1196 members of the public within five miles of Palo Verde. "Each of these are considered by Palo Verde to be a 'large segment of the population.' "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). The Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area. The MCSO is prepared to implement this contingency should it become necessary. "There are no events in progress that require siren operation. A follow-up call will be placed when the affected sirens are returned to service. "The NRC Resident Inspector has been notified of the siren maintenance and this ENS call." * * * UPDATE FROM JORGE RODRIGUEZ TO JOE O'HARA AT 1149 EDT ON 10/28/10 * * * "Maintenance on the Palo Verde public prompt notification sirens listed on ENS #46331 has been completed. The sirens are operable and are back in service. "The NRC Resident Inspector has been notified of the siren maintenance and this ENS call." Notified R4DO (Proulx). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-14
46330 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-10-14 01:00 | 2010-10-13 09:50 | 2010-10-14 | TECHNICAL SUPPORT CENTER EMERGENCY VENTILATION SYSTEM SCHEDULED MAINTENANCE "This ENS is being issued in advance of a planned activity. "On 10/14/10 at 0100 hours Limerick Generating Station will apply a clearance to inspect and repair fire suppression equipment associated with the onsite Technical Support Center (TSC) Emergency Ventilation System and perform corrective maintenance associated with the MD-1 (outside air) damper. While the clearance is applied, the TSC Emergency Ventilation system will not be available to be restored within the time period required to staff and activate the TSC Emergency Response Organization (ERO). This work is expected to be completed 10/14/10. If an emergency is declared requiring TSC ERO activation, the TSC will be staffed and activated using emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable procedures. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility because of the planned unavailability of the TSC Emergency Ventilation system. The NRC Resident Inspector has been informed." * * * UPDATE FROM JOHN WEISSINGER TO HOWIE CROUCH AT 1833 EDT ON 10/14/10 * * * The Technical Support Center Emergency Ventilation System maintenance is complete and the system has been returned to service. The licensee has notified the NRC Resident Inspector. Notified R1DO (Jackson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-13
46328 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2010-10-12 | 2010-10-12 13:26 | 2010-10-14 | AGREEMENT STATE - TROXLER MOISTURE DENSITY GAUGE MISSING IN TRANSIT One Troxler moisture/density gauge and three thin layer density gauges were transported to InstroTek, Inc. on September 23, 2010. The licensee was later notified that only three Troxler thin layer density gauges had arrived. The licensee searched their loading docks and did not find the missing gauge. InstroTek and R and L Trucking have also performed searches, but did not locate the gauge. The information about the gauge is below: Troxler Model 3440 Nuclear Moisture/Density gauge Serial Number 22504 CS-137, 8 mCi, Serial Number 47-4236 Am-241 Be, 40 mCi, Serial Number 47-18335 KS NMED KS100012 * * * UPDATE ON 10/14/2010 AT 1052 FROM DAVID WHITFILL TO MARK ABRAMOVITZ * * * The Troxler Moisture Density Gauge was found at the R and L Trucking Terminal in Wilson, NC (about 40 miles from the intended destination of Raleigh, NC). The gauge is being delivered to InstroTek today (10/14/2010). Notified the R4DO (Haire) and FSME (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-10-15
46327 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-10-11 13:05 | 2010-10-11 22:05 | 2010-10-29 | TECHNICAL SPECIFICATION DOES NOT ACCOUNT FOR POWER UPRATE "On October 11, 2010 at 1305 CDT it was identified that the analysis of record for the Technical Specification 3.3.5.1, Table 3.3.5.1-1 function 1e and 2e, Reactor Steam Dome Pressure Permissive-Bypass timer (Pump Permissive) did not reflect current plant conditions. Specifically, the analysis was not updated to account for any increase in plant licensed power and a change to the RWCU (Reactor Water Cleanup System) isolation for enhanced ability to isolate RWCU on a line break on critical crack. The allowable value for these function is greater than or equal to 18 minutes and less than or equal to 22 minutes. "All equipment associated with emergency core cooling function are unaffected. Discussion with General Electric indicates that a margin exists to accommodate the higher power level. Additionally, the changes to the RWCU isolation logic added leak detection instruments that will isolate RWCU earlier for the majority of pipe leaks. This discovery is being reported as an unanalyzed condition solely due to the lack of a formal analysis of current plant conditions." The NRC Resident Inspector has been notified. * * * RETRACTION FROM MARTIN RAJKOWSKI TO JOHN KNOKE AT 1451 ON 10/29/10 * * * "Under NUREG-0737, Item II.K.3.18 is a regulatory requirement to implement a modification to extend the ADS [Automatic Depressurization System] to a unique event sequence that involves multiple failures including HPCI [High Pressure Coolant Injection] plus no operator action after 10 minutes. According to Item II.K.3.18, the bypass timer logic complements, but does not replace, the existing ADS actuation logic. This requirement is not associated with any design basis accident mitigation sequence at MNGP [Monticello Nuclear Generating Plant]. "The plant has performed an evaluation that addresses the changes in plant thermal power and RWCU (Reactor Water Cleanup System) enhanced isolation capabilities to the analysis of record. This evaluation concluded that Peak Clad Temperature (PCT) will remain under the 2200 ?F acceptance limit with the current Technical Specification allowable value, current plant configuration and current licensed thermal power. GEH [General Electric] did an independent evaluation that concluded that based on use of limiting scenarios analyzed for MNGP, this condition is only a lack of formal analysis of current plant conditions and that no Substantial Safety Hazard exists. It is judged that the maximum Reactor Steam Dome Pressure Permissive-Bypass timer (Pump Permissive) setting of 22 minutes will not result in a predicted PCT higher than 2200?F with consideration of the RWCU pipe break isolation instrumentation modification. "Since the timers with their current setpoint will protect the fuel cladding, this event does not significantly degrade safety. Therefore, the event notification made on October 11, 2010 is being retracted." The licensee has notified the NRC Resident Inspector. Notified R3DO (Skokowski) | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-10-11
46326 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-10-10 11:45 | 2010-10-11 21:15 | 2010-10-11 | CALIFORNIA AGREEMENT STATE REPORT - DAMAGE TO RADIOGRAPHY CAMERA GUIDE TUBE The following information was received from the state via email. "On October 10, 2010, at approximately 11:45 P.M., an IESCO radiography team was performing radiography operations at the Conoco Phillips Refinery in Wilmington, CA. The team was exposing a small pipe when a 6 inch pipe spool fell approximately 2 feet from a work bench to the ground where the source guide tube was lying while the source was extended during an exposure. The flange end struck the guide tube and it crimped the tube, preventing the source from being retracted after the exposure time had elapsed. The RSO was contacted at approximately 1150 and he responded to the scene. While waiting for the RSO to arrive, the radiographer sent the assistant away from the area and proceeded to adjust the boundary around the scene to where the dose rate at the boundary was 2 mr/hour (actual dose rate) or less and to maintain constant surveillance of the boundaries so that no one could enter the area where the incident had occurred. "When the RSO arrived, he had both the radiographer and assistant stay out of the area of the incident and he proceeded to retrieve the source. He proceeded to straighten the guide tube and then placed 20 lb. lead shot bags on the source (the collimator had fallen off when the pipe spool struck the guide tube) to shield the source. The RSO then proceeded to cut open the source guide tube with tin snips. He then flattened the guide tube with lead sheets to expose the drive cable at the area where the guide tube was crimped to allow the source to be retracted back to the exposure device. While he was cutting the guide tube, the RSO placed his survey meter between himself and the source to monitor his exposure, along with two direct reading pocket dosimeters (DRPD) place at his chest (on had a 0-200 Mr range and the other had a 0-500 Mr range). He stated that his hands and chest were both approximately the same distance from the source during this phase of the recovery. While cutting the guide tube, the RSO periodically went to the crank to attempt to retrieve the source and then returned to cut more of the guide tube until the source was able to cranked without any resistance. After enough of the guide tube was removed to allow source to bypass the crimp, the RSO then went to retract the source. After the source had been retrieved, the exposure device was surveyed to ensure that the source was in the shielded position and then the exposure device was locked. The whole retrieval operation took approximately 30-45 minutes. "The estimated dose to the RSO during this incident was 110 millirem on both DRPD's, which is equivalent to being exposed by a radiation field of 200 mR/hr for 33 minutes. The radiographer was discovered to have a DRPD that was off scale and thus was told to stay out of the area of the incident and his dosimeter was sent to Mirion Technology (formerly Global Dosimetry) for emergency processing. The radiographers assistant's dose was estimated at 10 millirem as read by his DRPD. An estimate of the radiographer's dose will need to be reported to determine if an over exposure has occurred. Since all reporting of the incident was timely and the procedures were followed for this incident and for the off-scale DRPD, there is no evidence that a violation has occurred and the licensee will not be cited at this time. Any future actions will be determined after a review of the 30 day report which will be provided by the licensee as required under 10 CFR 34.101(a)." The radiography camera is a QSA Global A424-9 with Ir-192 35.6 Ci source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR | 30.50(b)(2) |  |  |  | 0 | 2010-10-14
46325 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-10-11 10:04 | 2010-10-11 13:38 | 2010-10-20 | AUTOMATIC REACTOR SCRAM DURING TRANSFER OF REACTOR PROTECTION SYSTEM BUS "On October 11, 2010 in preparation for maintenance, the 'A' Reactor Protection System Bus was being transferred from the normal to the reserve power supply. As a part of the transfer, a half scram is expected. During the transfer a [full] reactor scram occurred. All rods inserted to their full-in positions. "Following the reactor scram, all systems operated as expected. Reactor vessel inventory is being maintained by the Condensate / Feedwater system. "Following the scram, the Unit 2/3 Emergency Diesel Generator auto started due to the transfer of the Auxiliary Power system. "Currently the cause of the full Reactor Protection System [scram] is unknown. Troubleshooting is in progress to determine the malfunction. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." The auto-start of the EDG was expected as a result of the 'A' RPS bus transfer and has been secured and placed back in standby. Decay heat is being discharged to the condenser. The Unit is in a normal shutdown electrical line-up. The scram had no impact on Unit 2. The licensee characterized the scram as uncomplicated. The NRC Resident Inspector has been notified. * * * UPDATE FROM RILEY RUFFIN TO ERIC SIMPSON 1415 EDT ON 10/20/10 * * * The second to last paragraph of the original report has been updated to read as follows: "The auto-start of the EDG was anticipated as a result of the Auxiliary Power System transfer and has been secured and placed back in standby." The R3DO (Orth) has been notified. | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-10-11
46324 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-10-11 11:10 | 2010-10-11 12:10 | 2010-10-14 | TECHNICAL SUPPORT CENTER OOS FOR MAINTENANCE "This is an eight-hour report as required per 10 CFR 50.72(b)(3)(xiii) due to maintenance which will result in the Fort Calhoun Station Technical Support Center (TSC) being degraded. On Monday, October 11th scheduled maintenance will commence on the TSC Air Handling unit that will render the unit non-functional. This maintenance is scheduled to be completed on Thursday, October 14th. Station procedures contain compensatory measures to ensure appropriate habitability monitoring and, if necessary, relocation of TSC personnel should the need exist to activate the emergency response organization." The NRC Resident Inspector has been notified. * * * UPDATE FROM BARTON SCHAWE TO HOWIE CROUCH AT 1643 EDT ON 10/14/10 * * * At 1519 CDT, the TSC Air Handling Unit was returned to service and is functional. The licensee will notify the NRC Resident Inspector. Notified R4DO (Haire). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-11
46323 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-10-09 16:00 | 2010-10-09 21:03 | 2010-10-09 | LOCKING MECHANISM MALFUNCTION ON RADIOGRAPHY CAMERA On October 9, the radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunction of the locking system on an INC IR-100 exposure device. After completing radiography activities, the source was cranked in and the camera was surveyed per the proper procedure. There were no abnormal readings observed during the survey and the key was turned to the lock position. When the crank assembly was removed it was noted that the pigtail was not fully seated. The 2 mR/Hr boundary was reconfirmed and the Radiation Safety Supervisor was notified. A trained radiographer came to the site and removed the locking system and cleaned it. The locking system was successfully reinstalled. The camera has been returned to service. Exposure Device: Industrial Nuclear IR-100 Device S/N: 6631 Source S/N: P661 Source Activity: 61 curies Source Type: Ir192 Source Model # INC Model 32 There was no exposure to the crew or the general public during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-10-09
46322 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2010-10-08 15:00 | 2010-10-08 19:45 | 2010-10-08 | AGREEMENT STATE REPORT - DAMAGE TO TROXLER PORTABLE DENSITY GAUGE A Troxler portable density gauge was run over by a front end loader, at a construction site, causing damage and bending the source rod. The source rod is retracted but the shutter door is open. The density gage was returned to its storage container. Survey of the device and area indicates that no leakage occurred. The unit will be returned the licensee location for storage in a locked area for the weekend. The density gauge will be sent out for repair next week. The density gauge is a Model 3430 Troxler with a nominal 8 mCi Cs-137 gamma source and a 40 mCi Am-241:Be neutron source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2010-10-13
46321 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-10-08 11:00 | 2010-10-08 13:54 | 2010-11-09 | INTEGRATED PLANT COMPUTER REMOVED FROM SERVICE FOR UPGRADE WORK "At 1100, October 8, 2010, Unit 1 Integrated Plant Computer (IPC) was shutdown for upgrade work. This includes the SPDS [Safety Parameter Display System] system which is a function of the IPC. The IPC will be returned to service in approximately two weeks and SPDS function will be restored at that time. In addition, the ERDS [Emergency Response Data System] is out of service and will be restored in the same time frame. Per the 50.54.Q that was prepared by our Emergency Preparedness group, notification has been made to the NRC ERDS group of the unavailability of the ERDS system. While the IPC is out of service, control board indications are being utilized by the control room crew. In addition, the safety-related Plant Safety Monitoring System (PSMS) is OPERABLE. Restoration of SPDS and ERDS functions have been given the highest priority during restoration of the system. Both the NRC Ops Center and the NRC ERDS group will be notified when SPDS and ERDS capability have been restored." The NRC Resident Inspector has been notified. * * * UPDATE ON 11/9/2010 AT 1555 EST FROM CECIL WILLIAMS TO MARK ABRAMOVITZ * * * "On Oct 8, 2010, EN# 46321 was made for notification that the Unit 1 Integrated Plant Computer (IPC) was shutdown for upgrade and that the SPDS function was out of service until the upgrade was completed. The IPC has been returned to service sufficiently to support SPDS Functionality. All data points have been verified and associated Control Room annunciator tested. Therefore, at this time SPDS is considered returned to service. The ERDS function has previously been tested with the NRC ERDS Group and returned to service." The licensee notified the NRC Resident Inspector. Notified the R2DO (Blamey). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-08
46320 | 0 | LIBERTY HOSPITAL |  |  |  |  | 2010-10-06 09:00 | 2010-10-07 11:32 | 2010-10-08 | DELIVERED DOSE POTENTIALLY DIFFERENT THAN THE PRESCRIBED DOSE During a brachytherapy, a patient was prescribed a dose of 125 Gray to the prostrate. The delivered dose resulted in about 11 percent of the prescribed dose. The physician notified the patient and his guardian and also determined there was no radiation impact on the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-10-14
46319 | 0 | COMMUNITY HOSPITAL |  |  |  |  | 2010-10-06 | 2010-10-08 09:57 | 2010-10-26 | DELIVERED DOSE POTENTIALLY DIFFERENT THAN THE PRESCRIBED DOSE During a brachytherapy treatment, the patient breast received an incorrect entry of the catheter position from a treatment planning system. Because of this, the prescribed dose was 340 centi-Gray at 1 centimeter from the tumor cavity while the actual dose received was 680 centi-Gray at 1 centimeter from the tumor cavity. The physician notified the patient of the potential dose difference. Based on physician review, it was determined that there was no affect on the patient. The reason for the potential dose difference was due to a missed change of a program default in the software program of the radiation treatment planning system. A new check step has been added to the Community Hospital procedure in order to correct the issue. * * * UPDATE AT 1550 EDT ON 10/26/10 FROM ANDREA BROWNE TO S. SANDIN * * * The licensee is updating this report to confirm that upon further evaluation this is a medical event. Notified R3DO (Skokowski) and FSME (Burgess). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-10-14
46318 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-10-07 13:52 | 2010-10-07 21:06 | 2010-11-15 | DEGRADED FIRE BARRIER "During a walkdown for the Fire Penetration Seal Project a degraded fire barrier was identified in the wall between the Unit 1 and Unit 2 Normal 480V Switchgear Rooms. The wall is listed as an Appendix R wall between Fire Area (FA) 37 and FA 38. The wall separates redundant safe shutdown cables. "There is a 2 inch gap where the top of the wall meets the ceiling. The gap is filled with combustible foam - some loose and some stationary. This has been identified as a missing fire barrier such that the required degree of separation for redundant safe shutdown trains is lacking. "A fire watch has been established as a compensatory measure and will remain in place until the fire barrier is repaired. "The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10CFR50.72(b)(3)(ii)(B). "The licensee has notified the NRC Resident Inspector of this event." * * * RETRACTION ON 11/15/2010 AT 1328 EST FROM STEPHEN SEILHYMER TO MARK ABRAMOVITZ * * * "An eight hour report per 10 CFR 50.72(b)(3)(ii)(B) was conservatively reported on October 7, 2010 for a degraded fire barrier between Fire Area (FA) 37 and FA 38. Subsequent engineering analysis determined that the degraded fire barrier maintained the required degree of separation for redundant safe shutdown trains and plant safety was not significantly degraded. The 10 CFR 50.72(b)(3)(ii)(B) report is retracted. "The NRC Resident [Inspector] has been informed." Notified the R3DO (Cameron). | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-10-07
46317 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-10-07 13:15 | 2010-10-07 18:08 | 2010-10-07 | FEEDWATER ISOLATION INADVERTENTLY DISABLED "At about 1315 hours EDT on October 7, 2010, with the unit in Mode 3 and operators performing recovery actions following a reactor trip that had occurred at 0013 hours (see EN#46313), it was discovered that actions that had been performed to restore the main feedwater system had inadvertently resulted in disabling the feedwater isolation function. The feedwater isolation function, as described in Technical Specifications Section 3.3.2, Table 3.3.2 1, Function 5, requires that the feedwater isolation function be operable in Modes 1, 2, and 3, when the feedwater system is not isolated by the main feedwater isolation valves, main feedwater regulating valves, and bypass valves or by a closed manual valve. At approximately 1018 hours, during actions being taken to restore operation of the main feedwater system, the feedwater isolation key switches for the three steam generators, A, B, and C, were placed in the override/reset position. Although it was not realized at that time, this action was contrary to the Technical Specifications Section 3.3.2 operability requirements for the feedwater isolation function. This inoperability of the feedwater isolation function would have prevented the automatic feedwater isolation function described in the basis of Technical Specifications Section 3.3.2, which states that the primary function of the feedwater isolation signal is to stop excessive flow of feedwater into the steam generators. It also states that this function is necessary to mitigate the effects of overfeeding the steam generators, which could result in overcooling of the primary system. This function is actuated by a safety injection signal. There is no Technical Specifications allowed condition for both trains of the feedwater isolation function to be inoperable. Therefore, Technical Specifications Limiting Condition for Operation (LCO) 3.0.3 was applicable from the time the feedwater isolation switches were placed in the override/reset position, until the feedwater isolation function operability was restored at approximately 1329 hours. The LCO 3.0.3 completion time to be in Mode 4 within 13 hours was not exceeded. This condition is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of a safety function." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-10-07
46316 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-10-03 | 2010-10-07 15:45 | 2010-10-22 | AGREEMENT STATE - RADIOGRAPHY SOURCE FAILED TO RETRACT "On October 4, 2010, the Arkansas Radiation Control Program was notified by Team Industrial Services, Arkansas license number ARK-0344-03320, involving the failure of a radiography source to retract into the camera. The radiography crew involved in this incident was based in Sulphur, Louisiana. "On October 3, 2010, radiography work was being conducted in Fulton, Arkansas using a rented SPEC-300 Camera, serial number 017, containing a 27 Curie SPEC G-70 source, serial number GE2503, both manufactured by Source Production and Equipment Company. The source was last leak tested on 10/1/2010. A J-Tube manufactured by QSA, owned by the licensee, was also employed in the radiography work. "The source was cranked out of the SPEC-300 and the radiographer was unable to retract the source back into the camera. The radiography crew contacted the RSO and the crew attempted to safely straighten out the guide tube. After realigning the guide tube, the source was retracted into the camera. "After the source was determined to be safely stored in the camera, the crew returned to the office to determine the cause of the inability to retract the source. SPEC was also notified. "At this time, no overexposures have been reported by the licensee. "The Radiation Control Program is awaiting a written report on the incident from the licensee." Report #: ARK-0344-03320 * * * UPDATE FROM STEVE MACK TO ERIC SIMPSON AT 1500 EDT ON 10/22/10 * * * The following report was received from the State of Arkansas via e-mail: "The [Arkansas Department of Health (ADH)] received a written report in accordance with RH-1801.k of the Arkansas Regulations describing the event, root cause and exposure information. "The SPEC G-70 source is a Cobalt-60 source. "During the initial exposure, it is believed that the source did not reach the end of the J-Tube and was temporarily 'hung up' at the connection between the guide tube and J-Tube. The radiography crew re-verified the controlled area boundaries and made notifications. After consulting with the local RSO for the radiography crew and the Corporate RSO an attempt was made to 'straighten' the guide tube to decrease the likelihood of any binding of the crank-out/source and the guide tube. After the utilization of a 'long pole' the source was able to be retracted and locked into the exposure device. Surveys were made and the exposure device was transported to the office of the radiography crew. The total time the source was exposed was 60 minutes. "Inspections of the exposure device, guide tubes, crank out, and source revealed all were in proper working condition. SPEC has stated that the J-Tube utilized is not approve for use with the device and that no J-Tubes are approved for use with the SPEC-300 and G-70 Co-60 source configuration. "Total exposure from the direct reading pocket dosimeters: lead radiographer 90 mRem; radiographer A, 12 mRem; and radiographer B, 8 mRem. There were no exposures above the annual limit to any members of the public due to this event. "It appears that the root cause of the event was incompatibility of the J-Tube and source. The State of Louisiana has been notified of this event and the written report will also be forwarded. "The [ADH] considers this event closed." Notified R4DO (Campbell) and FSME EO (Einberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2010-10-12
46315 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-10-07 10:41 | 2010-10-07 12:39 | 2010-10-07 | LOSS OF 4160 VOLT SAFETY BUS "Oyster Creek experienced a loss of 4160 volt 'D' safety bus. Emergency diesel generator number 2 fast started and re-powered the 'D' bus, as expected. All other safety systems responded as expected. Investigation into the loss of 'D' 4160 volt safety bus is in progress." The licensee was performing grid undervoltage testing on the 'D' 4160 at the time of the event. The licensee has staffed the Outage Control Center. There is no affect on the other 4160 volt bus. Offsite power is normal. Plant risk was 'yellow' prior to and following the event as a result of Reactor Building Closed Cooling Water Pump 1-2 out of service for planned maintenance. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-10-07
46314 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2009-12-03 | 2010-10-07 09:25 | 2010-10-07 | AGREEMENT STATE REPORT - UNPLANNED EXPLOSION DAMAGING MIXTURE OF 400 MILLICURIES OF CARBON 14 This information was emailed from the state as follows: During a routine health and safety inspection, the [state] inspector learned that an explosion had occurred at the facility on December 3, 2009. An Authorized User was quenching a mixture containing 400 milliCuries of Carbon-14 at the time of the explosion. The individual showered and was taken to the emergency room. The individual had several bioassays done prior to returning to work. The licensee decontaminated the area of concern within the lab. Iowa Item Number: IA100005 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-10-12
46313 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-10-07 00:13 | 2010-10-07 04:06 | 2010-10-07 | AUTOMATIC REACTOR TRIP DUE TO A ONE LOOP REACTOR COOLANT LOW FLOW "At 0013 hours EDT on October 7, 2010, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the One Loop Low Flow reactor protection function. Reactor Coolant Pump (RCP) 'C' tripped during the event. "The Auxiliary Feedwater System automatically actuated, as expected due to low steam generator water level, and provided feedwater to the steam generators. Steam generator and pressurizer Power Operated Relief Valves (PORVs) and Main Steam Safety Valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently stable in Mode 3. "The Main Turbine Lube Oil Deluge System actuated without a fire during the event. A fire hose station pipe ruptured after the deluge system actuation. The fire hose station was isolated. "In addition, the 'B' Main Feedwater (MFW) Pump tripped during the event and the 'A' Main Feedwater pump subsequently tripped due to high steam generator level in the 'C' Steam Generator at about 0023 hours. "There is currently indication of RCP 'C' Number 2 seal leakage of approximately 2.5 gpm. "At approximately 0405 EDT the Auxiliary Feedwater (AFW) system actuated due to a trip of MFW Pump 'A' while attempting to start the pump in accordance with procedure GP-004, Post Trip Stabilization. The AFW system actuation signal caused motor-driven AFW Pump 'B' to start. The motor-driven AFW Pump 'A' was already in operation due to the post-trip condition. "The cause of the MFW Pump 'A' trip is under investigation. This AFW system actuation is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "The cause of the reactor trip is under investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-10-07
46312 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-10-06 11:06 | 2010-10-06 21:40 | 2010-10-06 | 24 HOUR NOTIFICATION UNDER BULLETIN 91-01 CONCERNING COOLDOWN VERIFICATION OF UF6 CYLINDERS "At 1106 CDT, on 10/06/2010 the Plant Shift Superintendent was notified that the independent verification of cylinder cool down time had not been completed on the following Uranium Hexafluoride (UF6) Cylinders: PP5436, PP5453, PP5389, PP5435, PP5388, PP5424, PP5459, and PP5443 in accordance with NCSA GEN-003. "NCSA GEN-003 requires that prior to movement of a cylinder from a liquid UF6 cylinder handling area it shall be determined, independently verified, and documented that the required cooling time has passed. The purpose of this requirement is to ensure the cylinder does not contain liquid UF6 before it is moved from a liquid handling area. Upon discovery of the violation, it was determined that the cylinders had, in fact, met the required cool down period prior to movement; however, the independent verification had not been completed. "Since this independent verification was not completed, double contingency was not maintained. Therefore, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01 Supplement 1. SAFETY SIGNIFICANCE OF EVENTS "Although an NCSA control was violated, cylinder integrity was maintained. POTENTIAL CRITICALITY PATHWAYS (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) "A solid UF6 cylinder would have to have been breached and sufficient moderator entered the cylinder in order to support a criticality. ESTIMATED AMOUNT, ENRICHMENT, FORM OF MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS) "The assay of any material involved is less than or equal to 5.5 wt. % U235. The cylinders involved were 10 ton cylinders. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Double contingency is maintained by implementing two independent controls on one parameter (moderation). "The first leg of double contingency relies on it being unlikely that industrial grade cranes, forklifts, and cylinder haulers would drop an ANSI N14.1 designed cylinder in such a way that it would be breached. This moderation control was maintained. "The second leg of double contingency relies on independent verification that the required cool down time has passed, prior to moving a cylinder from a liquid cylinder handling area. This control helps ensure that the cylinder does not contain liquid UF6 prior to movement. The independent verification was not performed or documented. Therefore, this moderation control was violated. Upon discovery of the violation, it was determined that the cylinders had, in fact, met the required cool down period prior to movement. "Double contingency relies on two independent controls on the same parameter. Since one of the two independent controls on moderation was violated, double contingency was not maintained; however, the moderation parameter was maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED "The cool down times for the identified cylinders have been independently verified thus bringing them back into compliance with double contingency." The NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2010-10-06
46311 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-10-06 00:08 | 2010-10-06 07:13 | 2010-10-06 | VALID ACTUATION OF AUXILIARY FEEDWATER SYSTEM IN RESPONSE TO VALID STEAM GENERATOR LOW-LOW LEVEL SIGNALS "At 0008 on Wednesday, October 6, 2010, Cook Nuclear Plant (CNP) Unit 2 had a Valid Automatic Actuation of the Unit 2 Turbine Driven Auxiliary Feedwater Pump. Cook Nuclear Plant Unit 2 Reactor had been manually tripped at 0001 from 14% power per normal operating procedures in preparation for the Unit 2 refueling outage. "Following the reactor trip, water level in steam generators 23 and 24 lowered to 21% causing an automatic start of the Unit 2 Turbine Driven Auxiliary Feedwater Pump. Manual operator actions were in progress to restore steam generator water levels at the time of the actuation. The Turbine Driven Auxiliary Feedwater Pump operated normally to provide auxiliary feedwater flow to all four Unit 2 steam generators, and steam generator levels were restored to normal post trip values. Prior to the trip of Unit 2 reactor, the Unit 2 East and West Motor Driven Auxiliary Feedwater Pumps were manually started per procedure, as part of the pre-planned reactor trip, to control steam generator water levels. The cause of the low steam generator levels is still under investigation." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-10-06
46310 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-10-06 07:00 | 2010-10-06 06:45 | 2010-10-06 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0700 on Wednesday, October 6, 2010, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems have been removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 1600 on Wednesday, October 6, 2010. "The licensee has notified the NRC Resident Inspector." "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE AT 1738 ON 10/6/2010 FROM BRADDOCK LEWIS TO BILL HUFFMAN * * * TSC ventilation was returned to service at 1645 EDT. The licensee notified the NRC Resident Inspector. Notified the R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-06
46309 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-10-04 22:00 | 2010-10-04 23:06 | 2010-10-04 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On 10/4/2010, at 2200 CDT, Wolf Creek Generating Station (WCGS) commenced a plant shutdown due to inoperability of the 'A' Train of Essential Service Water (ESW). On 10/2/2010, at 0642 CDT, 'A' Train ESW was declared inoperable due to indications of a leak on the buried ESW supply line. Technical Specification 3.7.8, Essential Service Water (ESW) System, Condition A, allows 72 hours to restore an inoperable ESW train. Location of the leak was identified using Ground Penetrating Radar and confirmed by excavation. Work is underway to evaluate and repair the leak. Since this work is expected to take longer than the allowed completion time (72 hours), it was decided to commence plant shutdown prior to expiration of the allowed 72 hours (10/5/2010 at 0642 CDT). Plant shutdown is required by Technical Specification 3.7.8, Condition B. Current plan is for the plant to be in Mode 3 (Hot Standby) by 0700 CDT on 10/5/2010. Plant cool down to Mode 5 will commence following shutdown and continue until such time as the leak has been repaired and the train restored to operable or until Mode 5 is reached." The leak has been quantified as approximately 11.5 gpm. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-10-04
46308 | 0 | WATERFORD | 3 |  |  | [3] CE | 2010-10-04 15:00 | 2010-10-04 19:40 | 2010-10-04 | OIL SHEEN ENTERS INTAKE STRUCTURE FROM UPSTREAM "This is a Non-Emergency 4 hour notification being made in accordance with 10CFR 50.72(b)(2)(xi), an Offsite Notification. On October 4, 2010, at 1500 CDT, the Waterford 3 Operations supervision was notified by the Outside Operations watchstander that there appeared to be a diesel oil film from upstream of the Mississippi River collecting on the upstream side of the Waterford 3 non-safety related Circulating Water intake weir. The Chemistry Department environmental expert went to investigate with the Outside watch and verified that a diesel film was washed upon the north wall of the weir at the shore line forming about a 50 square foot sheen of diesel. Safety systems are not impacted by this condition. "At 1609, the National Response Center was notified of the discovery of the sheen at our intake from an unknown source upstream. The incident report number was 956006. The Coast Guard was notified and the Waterford 3 environmental chemist received a call from the Coast Guard requesting information. The information was confirmed that a diesel film was washed upon the north wall of the intake structure weir at the shore line forming about a 50 square foot sheen of what appears to be red colored diesel. At 1734, Louisiana Hazardous Materials Hotline was notified (IR# 10-05779)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-10-04
46307 | 0 | 3M |  |  |  |  | 2010-10-04 09:30 | 2010-10-04 16:23 | 2010-10-04 | NUCLEAR PROCESS GAUGE MISALIGNED "This is a report of failure of equipment to function as designed resulting in increased radiation levels. "The equipment is an NDC [model 302] beta gauge, serial number 8996, containing a 200 mCi Kr-85 radioactive source. The gauge is installed on the 33 Coater at the Frame 4 position at the 3M Co. manufacturing plant, 3211 East Chestnut Expressway, Springfield, MO 65802. "The gauge had been shut down last week when operators noted incorrect thickness readings. The gauge shutter was closed at that time. This morning, Oct. 4, 2010, at about 9:30 AM [CDT] maintenance personnel inspected the gauge. At that time they determined that the gauge heads were misaligned. The facility Radiation Safety Officer was contacted. It was further determined that the gauge shutter could be opened with the gauge heads in misaligned position. As the detector head serves as the beam stop with the shutter open this could result in personnel exposure. "The RSO determined that no personnel were in the immediate vicinity of the gauge at the time when the incorrect readings were obtained and the shutter closed. Therefore there were no personnel exposures that resulted." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-10-04
46306 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-02-06 | 2010-10-04 14:59 | 2010-10-04 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE DURING PROSTATE BRACHYTHERAPY The following report was received via e-mail: The following report details "three Ohio Event Reports for two unreported medical events in 2008 (OH100022 and OH100023) and one unreported medical event in 2009 (OH100024). These events were discovered as a result of a special inspection conducted by ODH on 9/10/2010." Ohio Report Number OH100022: "An unreported medical event occurred at Clinton Memorial Hospital in Wilmington, Ohio on 2/6/08. On that date the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 144 Gray to the prostate. Post implant dosimetry showed that the received dose was >20 % below the prescribed dose." [The actual dose delivered was 97.5 Gray] Ohio Report Number OH100023: "An unreported medical event occurred at Clinton Memorial Hospital in Wilmington, Ohio on 3/21/08. On that date the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 145 Gray to the prostate. Post implant dosimetry showed that the received dose was >20 % below the prescribed dose." [The actual dose delivered was 102.5 Gray] Ohio Report Number OH100024: "An unreported medical event occurred at Clinton Memorial Hospital in Wilmington, Ohio on 5/20/09. On that date the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 144 Gray to the prostate. Post implant dosimetry showed that the received dose was >20 % below the prescribed dose." [The actual dose delivered was 107.5 Gray] A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-10-10
46305 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-10-02 13:30 | 2010-10-03 12:58 | 2010-10-03 | UNANALYZED CONDITION WHEN FUEL PELLET BOATS BECAME STACKED "At approximately 1330 hours on October 2, 2010 it was discovered that boats of fuel pellets had become stacked in a UO2 sintering furnace located in the GNF-A Fuel Manufacturing Operation. The furnace had been shutdown due to an apparent boat jam, which was detected by an overload sensor on the equipment that pushes boats into the furnace. This sensor is designated as an IROFS [Item Relied On For Safety] in the ISA [Integrated Safety Analysis] Summary. The stacked boat condition was discovered after process engineering removed two boats of fuel from the entrance of the furnace as part of the boat jam investigation. With these boats removed the stacked boats could be clearly seen and proper notifications were made to management. "The sintering furnace process has independent controls on geometry, which limit the process to a single layer of boats, and moderation, which prevent water and other forms of moderator from entering the process. In this event, the geometry control was compromised however the moderation control remained intact. The stacked boat condition has been analyzed as a process upset condition and is demonstrated safe in a documented safety analysis. "The IROFS that were intended to detect a misalignment of boats functioned properly during the event as the misalignment was detected. The IROFS mitigated the severity of the boat jam and the furnace operation was shutdown due to the misalignment. This event did not result in an unsafe condition, however the declared IROFS did not prevent the loss of geometry and resulted in a failure to meet performance requirements. "As a result, this event is being reported pursuant to 10CFR70 Appendix A (b)(1). "SAFETY SIGNIFICANCE OF THE EVENT - Low Safety Significance - No unsafe conditions existed due to this event. "SAFETY EQUIPMENT STATUS - Safety equipment associated with the sintering furnace operation is functional. "STATUS OF CORRECTIVE ACTIONS - The sintering furnace operation remains shutdown pending investigation and implementation of corrective actions." System design is such that boats cannot overturn and no spillage of fuel pellets has occurred. The furnace will have to cooldown before repairs can be completed. Applicable State and Local agencies will be notified by the facility. Marvin Sykes of NRC Region 2 has been notified by the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-10-03
46304 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-10-02 10:11 | 2010-10-02 15:38 | 2010-10-02 | RESIDUAL HEAT REMOVAL SYSTEM PIPING LEAK "Approximately five hours after Beaver Valley Power Station Unit No. 1 was shutdown at 0011 hours [EDT] to enter a scheduled refueling outage, an approximate 5 drops per minute leak was identified from a drain valve on the Residual Heat Removal (RHR) System inside containment. This leak is downstream of the two series RHR isolation valves on a pipe which connects to both trains of RHR. The actual location of the leak on the valve was not immediately evident. An evaluation was requested. At 1011 hours, the evaluation reported a 270 degree circumferential crack in the socket weld on the RHR side of the valve. Without reasonable assurance of RHR System operability, both trains of RHR were declared inoperable. Both trains of the RHR System are currently in service, along with three steam generators/condenser remaining available for decay heat removal. Actions to address this condition are being pursued. "This is being reported as a condition that at the time of discovery could have prevented the fulfillment of the safety function of systems needed to remove decay heat pursuant to 10 CFR 50.72(b)(3)(v)(B) since both trains of RHR were declared inoperable. "Beaver Valley Power Station Unit No. 2 is unaffected by this event and remains at 100 percent power. "The NRC Resident Inspector has been notified." T.S. Action 3.4.7 requires that efforts be immediately initiated to restore RHR as soon as possible. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-10-02
46303 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-10-01 09:51 | 2010-10-01 17:56 | 2010-10-01 | HIGH HEAD SAFETY INJECTION REDUCED CAPABILITY "This is an eight-hour non-emergency notification to the NRCOC for a condition that could have prevented the fulfillment of safety function of a system required to mitigate the consequences of an accident in accordance with 10 CFR 50.72(b)(3)(v)(D). "Unit 4 High Head Safety Injection (SI) system was at reduced capability from approximately 0951[hrs. EDT] to 1027 [hrs.]. This was due to an open flowpath from the High Head Safely Injection Pump discharge to the Unit 3 Reactor Coolant System (RCS) and refueling cavity. This flow path was established during the execution of an Equipment Clearance Order for Unit 3 SI system when SI valves MOV-3-843A and MOV-3-843B were opened prior to closing SI lsolation Valve 3-867. This condition could have impacted the ability of the SI pumps to provide required flow to the RCS cold legs should the SI system have been required based on Engineering judgment. This condition was discovered at approximately 1005 [hrs.]. "Unit 3 is in Mode 6 for a planned refueling outage. Unit 4 is in Mode 1 at 100%" Unit 3 and Unit 4 share a common High Head SI System discharge header. Unit 4 entered T.S. 3.0.3 from 0951[hrs.] to 1027 [hrs.] when SI Isolation Valve 3-867 was closed. The licensee has notified NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-10-01
46302 | 0 | PALISADES | 1 |  |  | [1] CE | 2010-10-01 13:25 | 2010-10-01 15:31 | 2010-10-01 | UNANALYZED CONDITION - APPENDIX R NON-COMPLIANCE ISSUE IDENTIFIED "At 1325 EDT on October 1, 2010, an Appendix R non-compliance issue was identified associated with a potential loss of safety related 2400 VAC Bus 1C and 1D due to specifically sequenced fires affecting control cables and power cables routed in common fire areas but different raceways. An extent of condition corrective action identified that three 2400 VAC breakers 152-103 (Bus 1 C Service Water Pump P-7B), 152-205 (Bus 1D Service Water Pump P-7C), and 152-208 (Bus 1D Component Cooling Water Pump P-52B) all have control cables routed in the same fire areas as the associated power cables. "There are three fire areas, the 1C switchgear room 116A (Fire Area 4), screen house room 136 (Fire Area 9), and component cooling water room 123 (Fire Area16) that contain both control cables and power cables for the associated breakers. The concern is that a fire could first damage the control cable(s), resulting in the opening of the control power fuses which would disable the control power and render the breaker protection circuitry nonfunctional. The 2400 VAC breakers fail-as-is on loss of control power. As such if the breakers were closed they would remain closed until manually opened. If the same fire then damaged the power cable(s) on the same breaker, the loss of the breaker protection circuitry would prevent the individual breaker from automatically opening and the clearing of the cable fault would propagate upstream to the next coordinated breaker which would result in the associated 2400 VAC bus feeder breaker opening and a loss of the entire bus. "Breaker 152-103 has the issue of both control and power cables present in the screen house room 136 (Fire Area 9) which has potential to result in the loss of the 1C bus for a fire in the screen house. The Appendix R safe shutdown analysis credits both 1C and 1D busses remaining available for a fire in Fire Area 9 and credits 1D bus remaining available for a fire in Fire Area 4. "Breaker 152-205 has the issue of both control and power cables present in the screen house room 136 (Fire Area 9) and in the 1C Switchgear room 116A (Fire Area 4) which has potential to result in the loss of 1C and 1D busses for a fire in the screen house or the 1C switchgear room. The Appendix R safe shutdown analysis credits both 1C and 1D busses remaining available for a fire in Fire Area 9 and credits 1D bus remaining available for a fire in Fire Area 4. "Breaker 152-208 has the issue of both control and power cables present in the component cooling water room 123 (Fire Area 16) which has the potential to result in the loss of 1D bus for a fire in the component cooling water room. The Appendix R safe shutdown analysis credits both 1C and 1D busses remaining available for a fire in Fire Area 16. "The 1C and 1D busses are relied on to provide power to safety related equipment. The busses are normally supplied by offsite power. In the event that offsite power is lost, power is supplied to the busses by the emergency diesel generators. Existing hourly fire tours of the 1C switchgear room, the screen house room, and the component cooling water room are credited as initial compensatory measures. "As a compensatory measure, existing hourly fire tours of the 1C switchgear room, the screen house room, and the component cooling water room are credited. "This is considered to be an unanalyzed condition that significantly degrades plant safety." The NRC Resident Inspector has been notified. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-10-01
46301 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2010-10-01 08:11 | 2010-10-01 13:05 | 2010-10-01 | NON-FIXED RAD SURFACE CONTAMINATION GREATER THAN LIMITS "[This report is being made] to report receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than reporting limits. "The package was received today, October 1, 2010, at around 0811 CDT by the Amarillo Veterans Administration (VA) Health Care System, Amarillo, Texas. "A wipe test performed on the external surface of the package indicated a removable contamination level of 1300 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2. "The package was immediately bagged and secured within the VA nuclear medicine department where it will be stored for decay. Wipes were taken throughout the department with all readings being at background levels. "The package contained 80 milliCuries of Tc-99m-labeled radiopharmaceuticals and was shipped from Panhandle Pharmacy, Amarillo, Texas. The vendor/shipper also serves as the delivery carrier. The VA nuclear medicine staff immediately notified the carrier before he left the nuclear medicine department and also contacted staff at Panhandle Pharmacy about the contaminated package at around 0825 CDT. "We will notify our NRC Project Manager at NRC Region III of this event." The VA facility RSO indicated that the VA staff offered to survey the carrier, but he declined. The external exposure rate readings on the package were within limits: 0.4 mR/hr on contact. The receiving facility was scanned for contamination. The results came back as reading background. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | TX | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2010-10-01
46300 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-09-30 | 2010-10-01 11:50 | 2010-10-01 | TEXAS AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING GAMMA KNIFE THERAPY The following was received from the State of Texas via e-mail: "On October 1, 2010, the Agency [Texas Department of Health] received a phone call from the licensee's Radiation Safety Officer (RSO). The RSO stated that a medical event occurred on September 30, 2010, when, while conducting a single fraction exposure to a patient, the computer screen froze. The patient was immediately removed from the gamma knife device. Approximately five percent of the prescribed dose was delivered. The intended dose was 20 gray to one location, and 15 gray to a second location, both to be delivered simultaneously. The referring physician and patient have been notified of the event. "The gamma knife is a Leksell Gamma Knife System, model number 24001 containing GE model 43047 sealed cobalt (Co) - 60 sources. "Additional information will be provided as it is received in accordance with SA-300." This is Texas Incident #: I-8790. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-10-07
46299 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-10-01 03:40 | 2010-10-01 07:23 | 2010-10-01 | OFFSITE NOTIFICATION DUE TO A TURBINE BUILDING EVACUATION "At 0340 EDT on Friday, October 1, 2010, the turbine building was evacuated as a precaution while station employees investigated the presence of a chemical odor. The source of the odor was identified as paint fumes from planned outage activities and air samples confirmed that no safety hazard existed. Workers were returned to the building approximately 45 minutes later. An Event of Potential Public Interest was issued to outside agencies." State and local agencies were notified. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-10-01
46298 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-09-30 19:04 | 2010-10-01 01:35 | 2010-10-01 | STANDBY DIESEL GENERATOR AUTOSTART DUE TO LOSS OF A SWITCHYARD BUS DURING MAINTENANCE "At 1904 [CDT] on 9/30/2010, the South Texas Project (STP) North switchyard bus was lost due to a Transmission & Distribution Service Provider (TDSP) human performance error that occurred while performing maintenance on breaker Y-0530. This resulted in a loss of power to Standby transformer 1 which was supplying power to the Unit 1 B Train Engineered Safety Features (ESF) 4160v bus. The B Train Standby Diesel Generator automatically started due to the Loss of Offsite Power (LOOP) on its associated bus. The Mode II (LOOP) ESF loads sequenced onto the bus. All safety related equipment responded as expected. Action (e) of Technical Specification (TS) 3.8.1.1, 'AC Electrical Power Sources', was momentarily entered due to the loss of two independent offsite circuits while the North bus was de-energized. The North bus was de-energized for approximately 5 minutes. Action (a) of Technical specification (TS) 3.8.1.1, 'AC Electrical Power Sources', was entered due to the loss of one independent offsite circuit. All Technical Specification Limiting Condition of operation have been exited at this time. "An 8-hour notification is required for this event due to the valid actuation of safety related equipment as described in 10CFR50.72 (b) (3) (iv) (A). [A notification is required for] any event or condition that results in valid actuation of any of the systems listed in paragraph (b) (3) (iv) (B) of this section, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "The NRC Resident Inspector has been notified." Unit 2 briefly entered a Technical Specification Limiting Condition of Operation, while all electrical buses remained energized. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-10-01
46297 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2010-09-30 16:16 | 2010-09-30 21:39 | 2010-11-30 | UNANALYZED CONDITION DUE TO POTENTIAL FLOODING VIA CONDENSATE DRAIN LINES "USAR Section 2.7.1.2, River Stage and Flow, states flooding protection against the 1,014 foot flood in the auxiliary building is provided by removable flood barriers and sandbagging. When required, these flood barriers are installed in openings leading to safety related equipment on the 1,007 foot and 1,011 foot floor elevations. "It has been identified that the condensation drains from the switchgear room's air handling units VA-87 and VA-88 (located in the auxiliary building), and the upper electrical penetration room's air handling units VA-85 and VA-86 (located in the auxiliary building), have no isolation valves or check valves to prevent backflow from the drain line's discharge in the turbine building basement. This means that flooding of the turbine building above approximately the 1011 foot elevation (floor level of the switchgear rooms) would result in water back-flowing via the drain lines into the switchgear rooms. "River level is currently at the 999' 6" elevation and stable. Procedure changes are currently being developed to block the affected drain lines." River level has never reached the 1011 foot elevation at the facility. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO ERIC SIMPSON AT 1307 EST ON 11/30/10 * * * "A further evaluation of the reported flooding issue determined that the flow into the switchgear rooms would be insufficient to affect the operability of safety related equipment in the auxiliary building; therefore, the incident could not have prevented fulfillment of a safety function nor could it have caused the inoperability of independent trains of safety related equipment. The situation does not constitute an unanalyzed condition. Therefore, this event is being retracted." The NRC Resident Inspector has been notified. Notified R4DO (Powers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-09-30
46296 | 0 | ABB, INC. |  |  |  |  | 2010-09-09 | 2010-09-30 17:35 | 2010-09-30 | PART 21 REPORT ON SOLID STATE RELAYS ABB, Inc. notified the NRC of solid state relays that failed to comply with ABB manufacturing specifications. Subject relays are 27H catalog numbers 411R0175-DP-1E and 411R0175-1E. The failure to comply is in regard to improper installation of a jumper on the main printed circuit board (PCB) of the relay. Manufacturing specifications require the jumper leads to extend far enough beyond the surface plane of the PCB to ensure proper connection. The jumper enables the relay to provide high-speed, instantaneous trip capability. If the jumper were not installed properly, the trip function may be erratic. The subject relays were manufactured between October 1, 2009 and September 9, 2010. Two safety-related versions of this relay have been purchased by South Texas Project. ABB, Inc. is investigating whether any nuclear plants have purchased the affected relays for use in non safety-related applications. ABB will be notifying South Texas Project of this defect. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21 |  |  |  | 0 | 2010-09-30
46295 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-07-12 15:49 | 2010-09-30 17:35 | 2010-09-30 | SAFEGUARDS REPORT - UNAUTHORIZED ACCESS INTO PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-09-30
46294 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-09-29 14:15 | 2010-09-30 15:36 | 2010-09-30 | DISCOVERY OF MICROTHERM INSULATION IN CONTAINMENT WHICH COULD IMPACT SUMP STRAINER PERFORMANCE "On September 12, North Anna Power Station Unit 1 entered a scheduled refueling outage. During the outage while performing reviews for a design change, it was determined that some uncontrolled plant drawings indicated that Microtherm insulation may have been installed on some piping locations inside the containment. The Microtherm insulation impacts the new containment sump strainers installed to address NRC GSI-191 requirements. It was subsequently confirmed via walk downs that the Unit 1 containment contained some Microtherm insulation. "Based on conflicting information on the possible installation of Microtherm inside Unit 2 containment and the identification of Microtherm insulation on Unit 1, a conservative decision was made to shutdown Unit 2 on September 29, and the Unit was cooled down to Mode 5 to allow a detailed inspection to be performed. The areas where the Microtherm insulation was potentially installed could not be inspected with the Unit at power. "Subsequent inspections have confirmed that the Microtherm insulation was installed in some areas of the Unit 2 containment. These locations include the reactor vessel nozzles and reactor coolant pump casings. Plans are being developed to remove this insulation on both units. "The overall impact of the Microtherm insulation on the containment sump operation is being evaluated by engineering." The licensee has notified the NRC Resident Inspector and the Louisa County Administrator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Refueling | Cold Shutdown |  | Refueling | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2010-09-30
46293 | 0 | DEL VALLE GROUP |  |  |  |  | 2010-09-29 09:00 | 2010-09-30 14:15 | 2010-09-30 | LOST/STOLEN MOISTURE DENSITY GUAGE An employee returning from a job site in Bayamon, Puerto Rico, stopped overnight at his home in San Lorenzo with a licensed moisture density gauge in the back of his truck. On the next day, while traveling to the next job site in Miramar, San Juan, the employee noticed that the moisture density gauge was missing from the truck bed. The driver retraced his steps, but was unable to locate the gauge and was not able to determine whether it had fallen off of the back of the truck or was stolen overnight. The San Lorenzo Police Department has been notified. The police report number is 2010606705020. The Puerto Rico Department of Health has been notified. A press release is planned to assist in recovering the moisture density gauge. The gauge is a Seaman Model C200, S/N L508, which contains a 8 mCi Cs-137 source and a 40 mCi Am/Be source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-09-30
46292 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-09-30 06:50 | 2010-09-30 09:39 | 2010-09-30 | OFFSITE NOTIFICATION - INADVERTENT ALARM ACTUATION "At 0650 [EDT] on September 30, 2010, site personnel were notified by multiple Calvert County residents of a single siren activation (Siren C21) at 0645 [EDT] for approximately 2-3 minutes. "Following a detailed review of the site's Alert and Notification System, the site identified multiple activations of the siren in addition to the first inadvertent activation of the siren that occurred at 0645 [EDT]. The multiple siren activations were not related to any condition or event at Calvert Cliffs. The siren has experienced multiple losses of power as a result of the effects from heavy rain and wind associated with the passing of Tropical Storm Nicole. Each time the power had restored to the siren, it performed a full cycle test as opposed to the standard silent test. "County Officials were notified and are taking actions to communicate to Calvert County residents concerning the inadvertent siren actuation. "Site maintenance locally deactivated the siren at 0827 [EDT] and will further investigate the extent of issue with the siren once the Tropical Storm Nicole has passed. In response to deactivating the siren, Calvert County has implemented the back-up method of route alerting in the event that actual siren activation is required. "The NRC Resident Inspector has been informed of the activations." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-30
46291 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-09-29 07:50 | 2010-09-29 21:15 | 2010-09-29 | AGREEMENT STATE REPORT - SOURCE HOUSING ON DENSITOMETER DETACHED FROM EQUIPMENT The following information was sent from the commonwealth via fax: "Excessive equipment vibration while the licensee was working at a job site caused the source housing of the Berthold LB8010 densitometer (Ser. No. 10049) to dislodge itself from the base plate, and detach from the equipment it was mounted to. The source housing was not damaged, the shutter is fully functional, and current survey readings similarly match past surveys; approximately 200 microroentgen per hour (uR/h) being the highest reading at 1 meter, with the shutter was closed and beam pointed toward the ground. The SS&D sheet on this densitometer notes a [maximum] 50 milliCuries (mCi) of Cs-137 source. Exact current activity on this unit to be determined. "CAUSE OF THE EVENT: Excessive vibration during use, and [perhaps] a design problem with how the source housing is bolted to a mounting plate. "ACTIONS: To prevent this from happening in the future, the clamps will be switched out on all the licensee's inline densitometers. In the meantime, the device is being sent back to Berthold to be remounted using a new version clamp. They will try to send whatever they can of the old clamp that failed to Berthold so it can be inspected. "PaDEP/BRP [state] will be performing an inspection of the device and equipment, as well as interviewing those involved with the source housing recovery for additional details. "The licensee will also be providing a full report with their findings and corrective actions." PA Event Report No: PA100023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-10-04
46290 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-09-29 15:25 | 2010-09-29 20:04 | 2010-09-29 | TECHNICAL SUPPORT CENTER HVAC EMERGENCY DAMPER FAILED QUARTERLY TEST "During quarterly testing of the Technical Support Center (TSC) HVAC System, Emergency Damper MD-1 failed to fully close when the system was placed into the Emergency mode of operation. This damper being not fully closed allows outside air to bypass the filter train and renders the Emergency mode of operation unavailable. "At 1725 the Emergency Damper MD-1 was failed to the closed position which makes the Emergency mode of the TSC HVAC system available. "Troubleshooting and restoration of Emergency Damper MD-1 will continue on dayshift 9/30/2010." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-29
46289 | 0 | DRESSER MASONEILAN |  |  |  |  | 2010-09-29 | 2010-09-29 15:00 | 2010-09-29 | POTENTIAL ISSUES WITH CERTAIN REGULATOR MODEL 77N-40 AIR REGULATORS Dresser Masoneilan initiated a 10 CFR Part 21 investigation because of the failure of three (3) Air Regulators (model number 77N-40) at the PSE&G Salem Station within three months of being installed. Upon testing and evaluation, Dresser Masoneilan concluded that the internal O-ring used for pressure isolation in the Air Regulators were damaged during factory assembly contributing to the failure of the units to regulate pressure. Dresser Masoneilan has developed a corrective action plan and an in-service test method and acceptance criteria to determine if a unit is experiencing pressure loss due to the issue. Due to the volume, age and distribution of these models, Dresser Masoneilan is issuing a general notice to all utilities. Contact Bill Comeau of Dresser Masoneilan at (508) 941-5477 with any questions concerning this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-09-29
46288 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-09-29 13:50 | 2010-09-29 14:47 | 2010-09-29 | ACTUAL INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Actual introduction of contraband into a protected area. Compensatory measures were taken upon discovery. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-09-29
46287 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2010-09-29 10:24 | 2010-09-29 10:43 | 2010-09-29 | LOSS OF COMM/ASMT/RESPONSE CAPABILITY "On September 29, 2010, at 1024 EDT, the Control Room Emergency Ventilation system on St. Lucie Unit 1 was declared out of service due to pre-planned maintenance on the Unit 1 Control Room ventilation system. This maintenance renders the control room envelope out of service for a portion of the maintenance. The Technical Support Center (TSC) ventilation system is part of the Unit 1 Control Room Emergency Ventilation system, therefore, the TSC ventilation system has been rendered non-functional during the course of the work activities. The TSC ventilation is expected to be returned to service later today. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Should the TSC become uninhabitable, the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE AT 1547 ON 9/29/2010 FROM DAVID LANYI TO ERIC SIMPSON * * * "The maintenance has been completed and the Control Room Ventilation System has been declared operable. The TSC has been deemed to be fully functional." The NRC Resident Inspector has been notified. The R2DO (Lesser) has been notified. | 100 | 84 | 0 | 100 | 84 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-29
46286 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-09-27 | 2010-09-28 15:01 | 2010-11-09 | OHIO AGREEMENT STATE REPORT - 95% MEDICAL UNDERDOSAGE DUE TO EQUIPMENT FAILURE The following report was received from the State of Ohio via email: "On September 27, 2010, the Gamma Knife gave a Fatal Error and terminated treatment to a patient. The error appears to be a failed computer disc drive. The safety system of the Gamma Knife functioned as designed, moving the patient out of the treatment machine and closing the Gamma Knife doors. The patient was safely removed from the treatment room. A service representative was immediately contacted and repair of the Gamma Knife is in progress. "It is intended to give the remaining dose from the plan to the patient once the Gamma Knife is repaired." The device in question is a Leksell, Model Perfexion Gamma Knife unit [S/N MV010], which contains a 13,824 Ci Co-60 source. The intended dose was 1400 rad. The delivered dose was 71.5 rad. The target organ was the brain. There is no effect on the patient. Ohio report #: OH100021. * * * UPDATE FROM STEPHEN JAMES TO JOHN KNOKE AT 1212 EST ON 11/09/10 * * * "On 11/9/10 the problem was diagnosed as faulty computer on unit. Computer was replaced and fully tested on 9/28/10. Patient remained in hospital overnight on 9/27/10 and received remainder of treatment on 9/28/10. No adverse effects anticipated due to delay in completing treatment. Licensee has contacted the manufacturer to review this incident for applicability to other units." Ohio Item Number 100021 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-10-01
46285 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2010-09-28 11:30 | 2010-09-28 15:04 | 2010-09-28 | OFFSITE NOTIFICATION - FAULTY ALARM ACTUATION "At 1130 hrs. on September 28, 2010, the site was notified by Wayne County, New York of a single siren activation at 0620 hrs. for approximately 2 minutes. The single siren activation was not related to any condition or event at Ginna Station. "The NRC Resident Inspector has been informed of the activation." A maintenance crew is currently investigating the cause of the spurious activation. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-28
46284 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-09-27 13:41 | 2010-09-28 12:50 | 2010-09-28 | UNUSUAL BUILDUP OF MATERIAL IN ALUMINUM CENTRIFUGE AREA "During the unloading of centrifuges in the Building 333 U-Aluminum centrifuge area, a crusty buildup of material (~1/8" thick) was observed on the inside of the centrifuge 'jacket' that contains the centrifuge bowl. The buildup was also observed on the underside of the centrifuge lid ('cake pan'). This level of material buildup was unusual and had not been previously observed. It should be noted that some dusting or spattering had been previously observed. The system is designed with drains on the bottom that are designed to prevent the accumulation of liquid within the centrifuge 'jacket'. There is also a requirement to inspect the 'jacket' when solution is observed draining from the overflows. This was considered an unanalyzed or improperly analyzed condition because the mechanism for buildup of this extent was not considered in the safety analysis (i.e. there was no indication of buildup provided by the overflows). "The following corrective actions were taken: 1) operations in the affected area were suspended; 2) the area was posted to maintain the integrity of the as-found conditions; 3) the area was inspected by safety personnel; 4) the issue was entered into the internal Problem Identification, Resolution, and Correction System (PIRCS); 5) an Unusual Incident Evaluation was performed; 6) calculations were performed with bounding conditions; 7) photographs were taken of the equipment; 8) the system was scanned to determine U-235 mass (~46 grams U-235); 9) material samples were taken and delivered to the laboratory for analysis; and 10) an investigation has been initiated." There were no control or control system failures. There were no actual or potential safety consequences to workers, the public, or the environment. No degradations or failures have been identified. The system is currently in a safe and stable condition. An investigation has been initiated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-10-06
46283 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2010-09-22 07:40 | 2010-09-27 13:47 | 2010-09-27 | UNEXPECTED CHANGES IN RESTRICTED AREA DOSE RATES On Wednesday morning, September 22, 2010, the Senior Reactor Operator (SRO) pulled some oil samples, housed in aluminum racks, out of the well groove around the reflector near the top of the reactor where the samples had been exposed to radiation for 8 hours and then allowed to decay for 12 hours. When the samples and sample holder were removed from the pool, three detectors alarmed: two were expected to alarm, and a third, the Control Room Evacuation Alarm, was not expected to alarm. The Control Room Evacuation Alarm has a conservative, audible, alarm set point of 2.5 mR/h which is well below the actual evacuation threshold of 100 mR/h. The Control Room Evacuation Alarm alerted the SRO that conditions were not normal. Within 30 seconds, the SRO placed the aluminum sample holder behind a lead shield and the oil samples behind a beta shield. According to facility procedures, the facility did not need to be evacuated because the easily visible Control Room Evacuation Alarm meter had not exceeded the evacuation threshold of 100 mR/h. The SRO estimated his dose as being approximately 1 Rem Total Effective Dose Equivalent (TEDE) which is less than the 5 Rem/yr, Part 20 limit; and approximately 15 Rem extremity dose which is less than 50 Rem/yr Part 20 limit. Follow-up dosimetry reports indicated that the SRO only received 147 mRem deep dose and 148 mRem shallow dose. No members of the public were in the vicinity at the time of the event. The facility believes that the cause of the high radiation field was possibly due to a high level of impurities in the aluminum sample holder and not from the oil samples. However, the oil samples received greater than normal neutron exposure and shorter than normal decay before removal from the reactor pool. This particular experiment required that these samples decay for only 12 hours, whereas normally, a decay time of 2 to 5 days is required before the samples are removed from the pool. The Reactor Safeguards Committee has recommended that the facility perform irradiation tests on each of its sample holders to prevent unexpectedly high radioactivity from unknown impurities. Kansas State University is making this report per their license requirements and Technical Specification 6.9.a.6, an observed inadequacy in the implementation of either administrative or procedural controls, such that the inadequacy has caused the existence or development of an unsafe condition in connection with the operations of the reactor. The State of Kansas has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | KS | NPR | [5 empty] | 0 | 2010-09-27
46282 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2010-09-27 08:48 | 2010-09-27 12:24 | 2010-09-27 | OFFSITE NOTIFICATION - LOSS OF ONE EMERGENCY RESPONSE SIREN "One of the 37 Prompt Notification System sirens surrounding the James A. FitzPatrick (JAF) /Nine Mile Point (NMP) sites spuriously activated at 0848 for a period of 3-5 minutes. This has been confirmed by siren report back system software and siren repair personnel. A member of the public called to report the activation to the Oswego County 911 Dispatch Center. The Dispatch Center notified Oswego County Emergency Management Office. County personnel took action to cancel the activation using the remote activation control system, notified the Licensee Emergency Preparedness personnel, and dispatched a siren repair crew. Siren repair personnel have isolated the siren and are performing troubleshooting to determine the cause. No press releases are currently planned by either Oswego County or the licensees." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-27
46281 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-09-27 | 2010-09-27 12:23 | 2010-09-27 | OFFSITE NOTIFICATION - LOSS OF ONE EMERGENCY RESPONSE SIREN "One of the 37 Prompt Notification System sirens surrounding the James A. FitzPatrick (JAF) /Nine Mile Point (NMP) sites spuriously activated at 0848 for a period of 3-5 minutes. This has been confirmed by siren report back system software and siren repair personnel. A member of the public called to report the activation to the Oswego County 911 Dispatch Center. The Dispatch Center notified Oswego County Emergency Management Office. County personnel took action to cancel the activation using the remote activation control system, notified the licensee emergency preparedness personnel, and dispatched a siren repair crew. Siren repair personnel have isolated the siren and are troubleshooting to determine the cause. No press releases are currently planned by either Oswego County or the licensees." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-27
46280 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-09-25 02:57 | 2010-09-25 11:30 | 2010-09-25 | LOSS OF ERDS, SPDS AND TSC PHONE LINES DUE TO UNINTERUPTABLE POWER SUPPLY FAILURE "On 9/25/10 at approximately 0237 CDT, the site experienced a loss of the Uninterruptable Power Supply UPS Y91. This resulted in a loss of power to the Safety Parameter Display System (SPDS) and site computer servers which disabled the Emergency Response Data System (ERDS). In addition, in-house Technical Support Center (TSC) telephones were lost [the NRC phone lines in the TSC are still available] rendering the TSC non-functional. The alternate TSC is functional and will be used, if needed, to implement the Emergency Plan (EOF Phones were unaffected). Alternate assessment capability is fully functional and will meet necessary requirements to implement the Emergency Plan. Troubleshooting efforts are underway. This event is reportable under 10 CFR 50.72(b)(3)(xiii)." The licensee stated that the Y91 UPS supplies a non-vital 125 volt dc bus and has no safety impact on plant operation and is not subject to any technical specification LCO. The NRC Resident Inspector has been notified. * * * UPDATE FROM MARTIN RAJKOWSKI TO PETE SNYDER AT 1656 ON 9/25/10 * * * All equipment noted as out of service above has been returned to service as of 1541 CDT on 9/25/10. Notified R3DO (Skokowski). | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-25
46279 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2010-09-25 02:10 | 2010-09-25 10:24 | 2010-09-25 | HIGH PRESSURE CORE SPRAY SYSTEM ROOM COOLING FANS FOUND NOT OPERATING "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D), event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. During steady state operations 2VD05C, Division 3 Switchgear Room / Core Standby Cooling System (CSCS) Pump Room Supply Fan and 2VD07C, Division 3 Switchgear Room / Core Standby Cooling System (CSCS) Pump Room Return Fan were found not operating. Division 3 ventilation supplies cooling to the High Pressure Core Spray System (HPCS), which is a single-train system. At the time of this discovery, there was not assurance that the HPCS would fulfill its safety function without mitigating manual actions due to the fan failure, and thus this condition is reportable. Operators are now briefed to manually operate the fan if needed to maintain proper temperature conditions until maintenance begins, thus restoring system function." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-09-25
46278 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-09-22 | 2010-09-24 17:24 | 2010-09-24 | AGREEMENT STATE REPORT - RADIOGRAPHER OVEREXPOSURE The following report was received via e-mail: "During the last radiographic exposure on 9/22/10 the source did not fully retract. The workers did not do a survey and did not have their rate alarms turned on. They noticed that their dosimeters were off scale and discovered the problem. The film badges were processed on 9/24/10 by Landauer and found the assistant radiographer received 0.742 Rem and the lead [radiographer] received 114.4 Rem. Since they were both together this is questionable. Landauer reports the lead's badge shows an uneven surface reading which is an indication it has been damaged by dropping. Licensee calculations show 0.750 REM for both. The lead has been sent for a blood test. Licensee will send a written report. Florida is investigating." The camera contained a 71 Ci Ir-192 source. Florida report number: FL10-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-09-29
46277 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2008-01-10 | 2010-09-24 12:25 | 2010-09-24 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following report was submitted via e-mail: "On January 16, 2008, Saint John Medical Center (SJMC) Lic. # OK-00376-02, of Tulsa, OK notified the Oklahoma Department of Environmental Quality (ODEQ) that on January 10, 2008 a patient had been administered a dose of I-131 that differed from the intended dose by greater than 20%. The intended dose was 100 mCi. The administered dose was 25 mCi. The misadministration occurred because the 100 mCi dose provided by Nuclear RX, PC (NRX) Lic. # OK-31035-01MD of Tulsa, OK was divided among three capsules. Two capsules contained 25 mCi, while the third contained 50 mCi I-131. The bottle received by SJMC was opaque and stated that it contained one capsule of 309 mCi because of a software error at NRX. When the dose was administered to the patient, one capsule was dispensed from the bottle, while the other two stuck in the bottom of the bottle. The presumed empty bottle was then repackaged and shipped back to NRX where it was discovered that two capsules remained in the bottle. It was determined that the capsules contained a total of 75 mCi I-131. The capsules were not discovered before shipping because the tech at SJMC errantly surveyed the package before placing the bottle inside. Corrective actions by SJMC involve surveying the bottle prior to returning it to the transport shielding, refresher training on transport requirements in 49 CFR, and determining the transport index (TI) by survey outside of the hot lab. Corrective actions by NRX included contacting the software developer for an update that would ensure that all shipments are accurately labeled. NRX also agreed to write the number of capsules contained in each bottle on the lid of the bottle. "Due to an oversight, this event was not reported at the time it was received by ODEQ." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2010-09-30
46276 | -1 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-09-24 10:58 | 2010-09-24 11:18 | 2010-09-29 | UNUSUAL EVENT DECLARED BASED ON SHORT DURATION LOSS OF SECURITY EQUIPMENT The licensee declared an Unusual Event at 1053 EDT based on a short duration loss of a security system. The basis for the Unusual Event is Emergency Action Level (EAL AU6.1.1.) for a security process issue. Compensatory issues were implemented. The equipment has been restored and proper function is being verified. The licensee has notified the NRC Resident Inspector, State and local authorities. Contact the HOO for additional details. * * * UPDATE AT 1323 ON 9/24/2010 FROM JAMES HUBER TO MARK ABRAMOVITZ * * * The licensee exited the Unusual Event at 1315 EDT on 9/23/2010. Notified the R1DO (Dentel), NRREO (Lee), IRD (Marshall), ILTAB (Pearson), DHS (Hill), FEMA (Biscoe), and 73.71 group (e-mail). * * * UPDATE AT 1403 ON 9/29/2010 FROM JOE GIOFFRE TO ERIC SIMPSON * * * "While performing planned maintenance on the security computer, the computer unexpectedly froze. As a result, compensatory actions were implemented and a site unusual event was declared. Further review has determined that the security event was misclassified. The security computer froze due to equipment malfunction caused by a hardware issue, not a security threat. Unusual event criteria was not met. Therefore, this notification is being retracted. This event has been entered in our corrective action program. The NRC Resident Inspector has been notified." Notified the R1DO (Gray). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | MD | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-09-24
46275 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2010-09-19 11:30 | 2010-09-23 20:31 | 2010-09-23 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE NOT FULLY RETRACTED The following report was received via fax: "Event Location: QEP Ironhorse Gas facility plant near Bonanza Utah on Uintah-Ouray reservation land. "Event Description: While conducting Industrial Radiography operations with a SPEC-150 camera, Serial # 816, the guide tube detached from the fitting used to attach the guide tube to the camera. The Ir-192 pigtail source was being retracted at the time. The source was not fully retracted when the guide tube fell away. The radiographers were unable to fully retract the source since the pigtail was at a ninety degree angle to the cable. The camera was approximately 25' in the air located on pipe rigging. The radiographers appropriately determined a 2mR/hr boundary and secured the area. Upon examination through binoculars, the RSO determined that the source was still secured to the cable. He reset his pocket dosimeter and, using a man lift, was lifted up to near the back of the camera. He used a 4' long grabber tool to gently lift the pigtail, allowing it to be retracted into the camera. He measured 190 mRem on the pocket dosimeter and sent in his film badge for immediate processing. The film badge showed a reading of 260 mRem for the period of time from September 1, 2010 to September 19, 2010. The RSO examined the camera and tube and determined that the tube pulled out of the crimping on the fitting. At the time of the incident the licensee had a total of five employees present at the location. Three currently qualified radiographers (including the RSO) and two currently qualified radiography assistants." Utah report UT-10-0004. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2010-09-28
46274 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2010-09-23 17:14 | 2010-09-23 17:52 | 2010-09-24 | REACTOR TRIP DUE TO INADVERTENT ENERGIZATION GENERATOR TRIP "Unit 3 reactor and turbine tripped due to Inadvertent Energization Generator Trip. All systems functioned as normal with the exception of Control Rod G5 in Control Bank A which remains at 18 steps. Entered and exited E-0 Reactor Trip and entered ES-0.1 Reactor Trip Response. All 4kV buses have power from the Unit 3 Start Up Transformer." Heavy weather conditions existed at the time of the reactor trip and is suspected as the cause for the Inadvertent Energization Generator Trip. Aux feed initiated during the trip recovery due to low steam generator level. Decay heat is being removed using condenser steam dumps and atmospheric steam dumps. There is no primary to secondary leakage. The plant is in its normal shutdown electrical lineup. There was no affect on unit-4 which is shutdown. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 2106 ON 9/24/2010 FROM TIM SEILKOP TO MARK ABRAMOVITZ * * * "Control Rod G5 in Control Bank A has been verified to be fully inserted. The Rod Position Indicator for Rod G5 currently indicates zero steps after being adjusted." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Hopper). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-23
46273 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-12-10 | 2010-09-23 15:56 | 2010-09-23 | AGREEMENT STATE REPORT - UNREPORTED MEDICAL PROSTATE THERAPY UNDERDOSE DISCOVERED DURING AUDIT The following information received via e-mail is historical and was discovered/reported to the State of Ohio on 05/04/2010: "NOTE: The information entered in this event notice was received from the licensee as a result of an audit ordered by the Ohio Department of Health for all brachytherapy procedures performed by the licensee since November 2004. This incident was referenced in Ohio NMED Item # OH100003. [See EN # 46272] "On 12/10/08 the licensee performed a prostate seed implant with fifty-four (54) I-125 seeds prescribed to deliver a dose of 145 Gray [104.76 Gray actually delivered] to the prostate. During the procedure, six (6) seeds were 'stuck' in one needle, and inadvertently placed inferior to the prostate. The post implant dosimetry calculation performed on 2/12/09 showed a D90 of 72.25%, resulting in an underdose to the prostate greater than 20% of the prescribed dose." Ohio NMED Item # OH100019. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-09-29
46272 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-12-02 | 2010-09-23 15:56 | 2010-09-23 | AGREEMENT STATE REPORT - UNREPORTED MEDICAL PROSTATE THERAPY UNDERDOSES DISCOVERED DURING AUDIT The following information received via email is historical and was discovered/reported to the State of Ohio on 04/27/2010: "NOTE: The information entered in this event notice was received from the licensee as a result of an audit ordered by the Ohio Department of Health for all brachytherapy procedures performed by the licensee since November 2004. This incident was referenced in Ohio NMED Item # OH100003. [NMED Item Number: 100113 - Ohio Agreement State Report EN #45750] "On 12/2/04 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 160 Gray [107.4 Gray actually delivered] to the prostate. A post implant dose calculation showed a underdose to the prostate greater than 20% of the prescribed dose; however, the licensee determined the dose to be clinically adequate. No further therapy was planned at that time. [Ohio NMED Item # OH100012] "On 12/14/04 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 108 Gray [66.27 Gray actually delivered] to the prostate. Post implant dosimetry showed a low dose distribution to the base of the prostate, which was not felt to be clinically significant. No further therapy was recommended at that time, since the patient also received external beam radiotherapy. [Ohio NMED Item # OH100013] "On 7/3/07 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 160 Gray [101.82 Gray actually delivered] to the prostate. A post implant dose calculation showed a underdose to the prostate greater than 20% of the prescribed dose; however, the licensee determined the dose to be clinically adequate. There was limited dose distribution at the gland base. No further therapy was planned at that time. [Ohio NMED Item # OH100014] "On 1/11/05 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 160 Gray [101.7 Gray actually delivered] to the prostate. A post implant dose calculation revealed a suboptimal dose distribution to the base of the prostate gland. No further therapy was planned at that time. [Ohio NMED Item # OH100015] "On 7/14/05 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 160 Gray [57.4 Gray actually delivered] to the prostate. Following the final dosimetry testing in 2005, the patient and the referring urologist were notified of a clinically suboptimal dose to the base of the prostate. Post implant prostate volume on which the dosimetry was calculated was 40% greater than the intraoperative prostate volume. Thus, dosimetry was inaccurate due to gland edema. The patient and the referring urologist opted for close monitoring of the prostate and PSA levels without additional therapy. No further therapy was planned at that time. [Ohio NMED Item # OH100016] "On 4/17/07 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 108 Gray [58.6 Gray actually delivered] to the prostate. Seed implant was utilized as a boost to the prostate gland following IMRT. Post implant dosimetry showed a suboptimal dose distribution at the base; however, satisfactory dose was observed about the mid gland where biopsy proven adenocarcinoma was present. No further therapy was planned at that time. [Ohio NMED Item # OH100017] "On 9/23/05 the licensee performed a prostate seed implant with I-125 seeds prescribed to deliver a dose of 108 Gray [79.4 Gray actually delivered] to the prostate. The patient received external beam radiation therapy (4500cGy) and seed implant was utilized as a boost to the prostate gland following IMRT. Post implant dosimetry indicated a clinically satisfactory dose distribution. No further therapy was planned at that time. [Ohio NMED Item # OH100018]" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-09-29
46271 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-09-23 06:00 | 2010-09-23 06:03 | 2010-09-23 | LOSS OF EMERGENCY RESPONSE CAPABILITY - TSC/OSC IS UNAVAILABLE "Unavailability of TSC/OSC Ventilation System Due to Scheduled Maintenance. "At 0600 [EDT] on Thursday, September 23, 2010, the Pilgrim Nuclear Power Station (PNPS) Technical Support Center (TSC) / Operations Support Center (OSC) emergency ventilation system was removed from service for planned maintenance. The balance of the TSC/OSC ventilation is not affected by the maintenance and remains available. "Under certain accident conditions the TSC/OSC may become unavailable due to inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC/OSC personnel to the Emergency Offsite Facility (EOF) and to the Control Room. In the event of a declared emergency, all OSC personnel will report to the Control Room Annex. TSC minimum staffing will report to the Control Room and all other TSC staff will report to the EOF. "The maintenance is scheduled to be completed by 1900 hours on Thursday September 23, 2010. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b) (3) (xiii) due to the loss of an emergency response facility." The licensee also informed the Commonwealth of Massachusetts. * * * UPDATE ON 9/23/2010 AT 1625 FROM MERT TROBASCO TO MARK ABRAMOVITZ * * * TSC/OSC ventilation was restored to operable status at 1600 EDT. The licensee notified the NRC Resident Inspector. Notified the R1DO (Dentel). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-23
46270 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-09-22 21:54 | 2010-09-22 22:24 | 2010-09-22 | NOTIFICATION OF UNUSUAL EVENT DUE TO A TRANSFORMER FIRE "At 2132 [EDT] on 9/22/2010, [the licensee] received a breaker tripout associated with the intertie transformer. Switching was ongoing in the switchyard at the time. At 2135 [EDT], the MCR [Main Control Room] was notified that flames were present on the A intertie transformer. NOUE was declared at 2154 [EDT]. The state of Tennessee was notified at 2200 [EDT]. There have been no observable effects on other plant equipment or structures at this time. This occurrence does not affect safety related equipment. "Flames were extinguished at 2154" [EDT]. The intertie transformer converts power between the 500 kV and 161 kV power lines. The transformer spilled an unknown quantity of oil into the gravel sump surrounding the transformer. The fire was extinguished by the onsite fire brigade and no offsite assistance was required. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TRAVIS TO KLCO ON 9/22/10 AT 2327 * * * The licensee terminated the Unusual Event based on the fire being extinguished and no further action is needed. The licensee is in the process of tagging out the failed transformer. Notified the R2DO (Hopper), NRR EO (Lee), IRD (Marshall), DHS (Kettleson) and FEMA (O'Connell). * * * UPDATE FROM TRAVIS TO HUFFMAN ON 9/23/10 AT 0035 EDT * * * The licensee plans to issue a media / press release concerning this event. Notified the R2DO (Hopper). | 85 | 100 | 0 | 85 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-09-22
46269 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-09-22 17:53 | 2010-09-22 20:23 | 2010-09-22 | SIRENS UNAVAILABLE DUE TO INCLEMENT WEATHER "During a thunder storm that extended across southern Pennsylvania and northern Maryland, 21 emergency sirens lost power in York County Pennsylvania and 8 emergency sirens lost power in Harford County Maryland. Exelon is communicating to the appropriate utilities to make emergent repairs to restore these sirens." In accordance with Peach Bottom plant specific procedures because greater than 25% of sirens were unavailable, the licensee contacted the following: Pennsylvania and Maryland Emergency Management; Harford and Cecil counties in Maryland and Lancaster, Chester and York counties in Pennsylvania. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE | OFFSITE NOTIFICATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) | 50.72(b)(2)(xi) |  |  | 0 | 2010-09-22
46268 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2010-09-22 08:30 | 2010-09-22 15:09 | 2010-11-18 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE DUE TO A MINOR LUBE OIL LEAK "At 0830 [EDT] on 09/22/2010, the Unit 2 High Pressure Coolant Injection (HPCI) system was determined to be inoperable due to a minor lube oil leak on the 'A' supply filter. LCO 3.5.1 for the HPCI system was entered at 0830 [EDT] on 09/22/2010. "The leak on the 'A' filter could not be immediately corrected. The 'B' filter was placed in service and leak checked satisfactorily. The LCO 3.5.1 action statements were closed at 1454 [EDT] on 09/22/2010. "This incident is being reported as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident in accordance with 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM RONALD FRY TO DONG PARK AT 1609 EST ON 11/18/10 * * * "At 1501 on September 22, 2010, PPL Susquehanna, LLC reported that the Unit 2 High Pressure Coolant Injection (HPCI) system was inoperable due to a minor lube oil leak on the 'A' supply filter. Subsequent investigation and evaluation determined that HPCI was capable of performing all of its safety functions with the identified oil leak. The operability determination was based on the following: "Investigation of the leak identified that the installed filter housing cover o-ring was undersized and had to be inappropriately stretched to fit in the o-ring groove in the housing cover. The cover is torqued to 75 ft-lbs by four bolts on the outer diameter of the cover, enclosing the o-ring in a metal to metal connection. There is no concern for the o-ring to extrude from the cover under this configuration. The worst case that can be postulated as a result of the undersized o-ring is a leak in which the drops break into a small stream. This type of leak is expected to result in less than 10 gallons of oil loss during the system's 6 hour mission time. The vendor recommended oil reserve level is approximately 124 gallons. The lube oil sump has a 155 gallon capacity and the remaining oil (approximately 145 gallons) is sufficient to support operability. As a result, the worst case leakage is not expected to affect operability of HPCI or result in system failure during the HPCI mission time. Operations verifies oil level weekly and prior to any planned run." The licensee has notified the NRC Resident Inspector. Notified R1DO (Gray). | 0 | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-09-22
46267 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-09-21 17:30 | 2010-09-22 13:26 | 2010-09-22 | AGREEMENT STATE REPORT - DAMAGED FIXED GAUGE The State of Iowa was notified by Louisa Generating Station, a coal-fired electrical generating plant, that a fixed gauge source had been damaged. "The facility has two 50 mCi Cs-137 sources attached to coal crushers. The gauges are used as low level alarm detection devices and detect whether or not coal is in the hopper at any given time. At approximately 5:30 p.m. on 9.21.10 there was a machine failure. [The licensee] suspects that as a result of the failure there was vibrational damage to one of the gauges (manufactured by Texas Nuclear, housing model 5192, serial number B2724). The gauge was visibly damaged but has not resulted in elevated rad levels. No employees were exposed as a result of this event. The gauges are mounted 15 ft from the floor in a building that is not occupied by staff. The machine (coal crusher) remains out of service since the time of failure on 9.21.10. "Again, [the licensee] reports no source damage. Their calibrated instrument reads 0.5-1.0 mrem 1 ft from the source, 0.2-0.3 mrem at 2 ft and 0.1 mrem at 3 ft from the source. "A technician out of Illinois is scheduled to arrive at the facility on Tuesday, September 28th for further testing and possible repair." The gauge is located in a contained building. The shutter is normally open and the suspected vibration damage resulted in being unable to close the shutter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-09-27
46266 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-09-22 08:26 | 2010-09-22 10:36 | 2010-09-22 | TECHNICAL SUPPORT CENTER HVAC UNIT OUT OF SERVICE FOR MAINTENANCE "Technical Support Center (TSC) HVAC unit [was] taken out of service for maintenance on [the] unit. The maintenance to be performed includes replacing the evaporator coil, the fan and the expansion valve. This work will be performed with high priority around the clock until the work is completed. Equipment unavailability hours will be reported to and tracked by the TSC HVAC System Engineer. Compensatory measures for performing essential TSC functions during this maintenance period have been established. These measures include the relocation of the TSC staff in the event of a declared emergency if the Emergency Director deems the TSC uninhabitable. The maintenance period is scheduled to last 13 to 16 hours, at which point the TSC HVAC [unit] will be restored to operable status." The licensee has notified the NRC Resident Inspector. | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-22
46265 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-09-21 20:17 | 2010-09-21 22:28 | 2010-09-21 | AUTOMATIC REACTOR TRIP "At 2017 [EDT] on 9/21/10, Turkey Point Unit 4 spuriously tripped. The cause of the reactor trip is currently under investigation. "At the time of the trip, reactor power was 100%. Auxiliary feedwater [AFW] was automatically initiated when steam generator levels lowered below the actuation setpoint. Steam generator levels are now stable at their normal Mode 3 band and auxiliary feedwater is secured. "Unit 4 has been stabilized in Mode 3 on normal off-site power. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) - actuation of the reactor protection system with the reactor critical and 10 CFR 50.72(b)(3)(iv)(A) - valid actuation of an ESF system (AFW)." All control rods inserted into the core. Decay heat is being removed through the steam dumps to atmosphere. There was no activation of PORVs or SRVs. The reactor is at shutdown NOP and NOT. The reactor trip response was uncomplicated and there was no impact on Unit 3. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-21
46264 | 0 | SOUTHEAST MISSOURI HOSPITAL |  |  |  |  | 2010-09-20 21:00 | 2010-09-21 18:22 | 2010-09-21 | HIGH DOSE RATE AFTERLOADER STUCK / EXPOSED SOURCE On 9/20/10, the licensee was having scheduled maintenance work performed on a Varian High Dose Rate (HDR) afterloader. A source exchange was also scheduled to be performed. During the source exchange, the source became "stuck, partially exposed, not fully shielded in the shield" of the HDR machine and became inoperable. The licensee believes this to be due to personnel error on the part of the service technician. The service technician then vacated the room. Varian was called and said they would dispatch personnel to the hospital on 9/21/10. Security was notified of the radiation safety problem. The door to the room was secured. The door to the room was posted with hazard warning tape, with a do not enter sign, and with a high radiation area sign. The department was also locked down. Varian personnel arrived on-site on 9/21/10. Varian service personnel secured the source back in the machine. Radiation levels in the room then returned to normal background readings. The source wire was found kinked and shipped out today. The hospital is scheduled to receive a new source and have it installed tomorrow. Service personnel were wearing "active monitors" and received only a few milli-rem during the repair operation. It is not known at this time how much dose the first service technician received. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 30.50(b)(2) |  |  |  | 0 | 2010-09-21
46263 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2010-09-21 11:54 | 2010-09-21 13:37 | 2010-11-09 | ACTUAL ENTRY OF AN UNAUTHORIZED PERSON An actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM CURT STEFFES TO MARK ABRAMOVITZ AT 1655 EST ON 11/09/10 * * * "Based on subsequent reviews, ENS Report # 46263 is being retracted." Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. Notified R3DO (Stone) and 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-09-21
46262 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-09-20 17:04 | 2010-09-20 19:37 | 2010-09-20 | AUTOMATIC REACTOR TRIP "At 1704 CDT, Braidwood Unit 1 experienced an automatic reactor trip. The reactor trip red first out was Over Temperature Delta Temperature (OTDT). At the time of the reactor trip, the Instrument Maintenance Department was performing a calibration of Power Range Channel N-43 and a calibration of the 1C S/G Narrow Range Level Channel 1L-0538. The cause of the trip is unknown at this time. "After the reactor trip occurred, all four Steam Generators reached their Low-2 reactor trip setpoint and Pressurizer pressure reached its low pressure reactor trip setpoint which is an expected response on a trip from full power. Steam Generator levels and Pressurizer pressure have been restored. Both the 1A and 1B Auxiliary Feedwater pumps auto started on the Low-2 Steam Generator levels as expected. All control rods fully inserted into the core. "Train B Main Control Room Filtration system shifted to makeup mode and the Train B Fuel Handling Building ventilation shifted to Emergency Mode due to a spurious actuation signal. "No secondary relief valves lifted and no secondary steam [was] released as a result of the reactor trip. The Main Steam Dumps are in service to the Main Condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. This report is being made per 10CFR50.72(b)(2)(iv)(B) for RPS actuation, 4-hr. notification, and per 10CFR50.72(b)(3)(iv)(A) for automatic actuation of the Auxiliary Feedwater system, 8-hr. notification. "AC power is being provided by offsite power with the Diesel Generators in standby and all safety systems available. There is no Unit 2 impact." The licensee notified the NRC Resident Inspector. The licensee also anticipates that there will be a press release issued regarding this event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-20
46261 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-09-16 13:43 | 2010-09-20 17:26 | 2010-11-15 | UNANALYZED CONDITION - DEGRADED FIRE BARRIER IDENTIFIED "This is a late eight hour report submitted under 10CFR50.72(b)(3)(ii), 'Degraded or Unanalyzed Condition.' "During walk downs for the Fire Penetration Seal Project on September 16, 2010 at 1343 [hrs. CDT], a degraded fire barrier was identified in the wall between the Unit 1 and Unit 2 sides of the Electrical Piping Area. The wall is listed as an Appendix R wall between Fire Area (FA) 29 and FA 30. The wall separates safety related redundant cables. "There is an approximately one inch gap filled with loose fitting foam from the top of the wall to the concrete ceiling above it. In one place the foam has a gap approximately one inch wide. This has been identified as a missing fire barrier such that the required degree of separation for redundant safe shutdown trains is lacking. "A fire watch was established as a compensatory measure on 9/16/10. The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B). "The licensee has notified the NRC Resident Inspector of this event." The fire watch remains in place. * * * RETRACTION ON 11/15/2010 AT 1328 EST FROM STEPHEN SEILHYMER TO MARK ABRAMOVITZ * * * "An eight hour report per 10 CFR 50.72(b)(3)(ii)(B) was conservatively reported on September 20, 2010 for a degraded fire barrier between Fire Area (FA) 29 and FA 30. Subsequent engineering analysis determined that the degraded fire barrier maintained the required degree of separation for redundant safe shutdown trains and plant safety was not significantly degraded. The 10 CFR 50.72(b)(3)(ii)(B) report is retracted. "The NRC Resident [Inspector] has been informed." Notified the R3DO (Cameron). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-09-20
46260 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-09-18 18:25 | 2010-09-20 12:18 | 2010-09-20 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO WEAPONS CONTROL Safeguards system degradation related to weapons control. Compensatory actions taken. Call the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-09-20
46259 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2010-09-20 07:00 | 2010-09-20 00:10 | 2010-10-06 | ERDS AND SPDS OUT OF SERVICE FOR COMPUTER UPGRADE "On 9/20/2010 at approximately 0700 EDT, the Hope Creek Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) will be taken out of service for approximately nine days to support a planned modification which will install a new (upgraded) computer system. During this timeframe, ERDS and SPDS will be unavailable. Should the need arise, plant status information will be communicated to the NRC, State and local responders using other available communication systems. SPDS and ERDS are expected to be restored on 9/29/2010. This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a 'Major Loss of Assessment Capability'." The licensee has notified Lower Alloways Creek Township and the NRC Resident Inspector of the planned outage. * * * UPDATE AT 1540 ON 9/29/2010 FROM DAVID HALL TO ERIC SIMPSON * * * "SPDS and ERDS systems were removed from service to support planned computer upgrade. Planned work which resulted in the removal from service of the SPDS and ERDS has been completed. The SPDS system has been returned to service. During the ERDS testing, a problem was discovered with the NRC's communication link supplied by Verizon. An update will be provided when ERDS testing is completed." Notified R1DO (Gray). * * * UPDATE AT 1306 ON 10/6/2010 FROM DAVID HALL TO MARK ABRAMOVITZ * * * "The ERDS communication problem was repaired and successfully tested. SPDS and ERDS are now fully functional and all work is complete." The licensee notified the NRC Resident Inspector. Notified the R1DO (Joustra) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-20
46258 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-09-18 16:27 | 2010-09-18 17:20 | 2010-10-07 | UNUSUAL EVENT DECLARED DUE TO HIGH-HIGH REACTOR BUILDING SUMP LEVEL ALARM "This is a one-hour report for the discovery of a condition that met an Emergency Activation Level (EAL) for a Notification of an Unusual Event [NOUE]. "EAL HU-1 - Natural and Destructive Phenomena Affecting the Protected Area Threshold Value 6 states, 'Exceed Max Normal Operating Values specified in EOP 31 EO-EOP-014-1 SC - Secondary Containment Control Table 5 Secondary Containment Operating Water Levels.' "Plant Hatch Unit 1 declared a NOUE on 9/18/10 at 1627 based on HU-1 Natural and Destructive Phenomena Affecting the Protected Area due to exceeding the Max Normal Operating Value for the Reactor Building NE Diagonal Floor Drain Sump. At 1615, both the Level High and Level High-High annunciators alarmed. Water has not overflowed the sump. However, due to its design, it is not possible to immediately visually confirm the sump level. The sump pumps were not running and would not run with their switches in START indicating either: (1) there is no water in the sump, (2) both pumps are OOC [Out of Commission], or (3) there is a problem in the sump level control system. Maintenance is assessing the situation." The licensee has notified the state and local agencies and will notify the NRC Resident Inspector. * * * UPDATE FROM STEVE BURTON TO HOWIE CROUCH @ 0427 EDT ON 9/19/10 * * * At 0400 EDT, the NOUE was terminated. The termination criteria was that the NE Diagonal Floor Drain Sump level was in its normal operating range with no abnormal sump in-leakage detected. Compensatory measures are in place to measure level in the sump. An investigation into the abnormal level indication is still in progress. The licensee will be notifying state and local authorities as well as the NRC Resident Inspector. Notified R2DO (Henson), IRD (Gott), NRR EO (Howe), DHS (Inser) and FEMA (Via). * * * RETRACTION FROM STEVE BURTON TO JOE O'HARA AT 1533 EDT ON 10/7/10 * * * "On September 18, 2010, a notification, Event Number 46258, was submitted to the NRC to report a circumstance at Plant Hatch Unit 1 which appeared to be a 'High-High' reactor building sump level alarm. Such an alarm would meet the designated Emergency Activation Level (EAL) for a Notification of an Unusual Event (NOUE). On the day of the event, it was thought that receipt of both the 'High' and 'High-High' level annunciators for the reactor building northeast diagonal floor drain sump was indicative of the sump level having reached its maximum normal operating level, and a NOUE was made. "During a subsequent Investigation, engineering personnel determined that the 'High' and 'High-High' level switches for this sump are wired such that both alarms are actuated concurrently when the 'High' level in the sump is reached at approximately 52 Inches. The 'High-High' sump level annunciation (the level at which the NOUE must be made) Is supposed to alarm at approximately 60 inches. Engineering personnel also determined that the level logic is currently improperly configured to clear both the 'High' and 'High-High' level alarms when the sump level rises to 60 inches. "The initial 'High' and 'High-High' level alarms in the main control room were received at approximately 1615 EDT on September 18, 2010. At that time the sump level would have reached an actual level of approximately 51 inches (albeit with a false indication of approximately 60 inches due to the configuration error noted above) based on the setpoint at which this alarm occurs. The normal leakage into this sump at the time of this event was at a rate of approximately 1 inch per hour. The sump pumps were started at approximately 1800 EDT to pump down the sump. This action resulted in a maximum actual sump level of approximately 53.5 inches, assuming the normal leakage into the sump was occurring during this period. At no time did the sump level actually reach the 'High-High' sump level criteria of 60 inches, nor did the annunciated level clear prior to pumping down the sump which also demonstrated that the 60 inch criteria was not met. "It is now apparent that the initial NOUE was a conservative report that was properly made based on the information available to the operators at the time. The subsequent investigation provided additional information regarding actual sump level conditions including information that both 'High' and 'High-High' alarms annunciate at the 'High' sump level and would have cleared had the 'High-High' level been reached. Since the 'High-High' sump maximum normal operating level of 60 inches was never reached during this event, the determination has been made that the EAL was not appropriate given the actual sump conditions, thereby making the event non-reportable and an NOUE unnecessary. "Based on the preceding Information, Southern Nuclear Company (SNC) hereby provides notification that Event Number 46256 is retracted." The licensee will notify the NRC Resident Inspector. Notified R2DO(McCoy). | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-09-18
46257 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-09-16 | 2010-09-17 18:23 | 2010-09-17 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE DAMAGED WHEN STRUCK BY VEHICLE The following information was received via facsimile: "A nuclear gauge, Troxler Laboratories 4640 Thin Lift density gauge, Serial No. 1997, Nuclide CS-137, GBq 0.296, mCi 8, was damaged in a construction zone hit-and-run accident. The RSO for a construction company was carrying the thin lift gauge to his truck when he was struck by a female driver in a grey sedan. The RSO, who was approximately 10 feet inside the coned area of the construction control zone, was able to move his body at the last minute and did not sustain major injuries. The gauge was destroyed but the source remained intact in the damaged housing. The RSO and the Nevada Highway Patrol [NHP] conducted radiation surveys. "NHP contacted Radiation Control Program 30 minutes after notified. The licensee reported to RCP within 3 hours. "The damaged gauge has been leak tested and is stored at the licensee's facility pending instruction from Troxler on shipping for disposal." The State of Nevada has not yet assigned a state event number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-09-22
46256 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-09-02 15:59 | 2010-09-17 10:08 | 2010-09-17 | AGREEMENT STATE REPORT - SOURCE RECEIVED WITH EXTERNAL CONTAMINATION The State reported that QSA Global received a radioactive source shipment that had external contamination on the source (but internal to the shipping container) and evidence of leakage. The source originated from Westex Company of Oxnard, California. The source was an old Amersham source Model T-2-T, S/N C778 containing an estimated 7.1 curies of Cobalt-60. The source was sent to QSA for disposal. It had been in long-term storage at the Westex facility. When the shipment arrived at QSA, it was receipt inspected and found to be clean on the outside of the Type B shipping package. When the package was opened and interior swipes taken, surface contamination was discovered on the source exterior. The highest swiped reading obtained was about 1.17 microCuries of Co-60. QSA does not believe that any contamination ever existed exterior to the package during transport or preparation of shipment at the originator's site. The source has been stored in the container at Westex without use or removal from the container for decades. QSA Global has been in contact with Westex about the contamination and Westex confirmed no contamination at their facility. QSA plans on disposing of the source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-09-22
46255 | 0 | VOGTLE 3&4 |  |  |  |  | 2010-09-16 10:28 | 2010-09-17 09:52 | 2010-09-17 | FAILURE TO PERFORM FFD KNOWLEDGE EXAMINATIONS FOR CONTRACTOR PERSONNEL "SNC [Southern Nuclear Company] was informed on September 16, 2010 that the training records for a limited number of contractor employees, who are subject to the 10 CFR 26 subparts A through H, N and O requirements, did not include evidence of completion of the examination required by 10 CFR 26.29(b). The individuals had received training on the knowledge and abilities described in 10 CFR 26.29(a) but, due to personnel error, had not completed the testing required by 10 CFR 26.29(b) prior to being authorized to perform duties for which such examination is a prerequisite under 10 CFR 26. Authorization of the affected individuals to perform duties subject to 10 CFR 26 subparts A through H, N and O has been withdrawn until the required testing is completed in accordance with 10 CFR 26.29(b). Prior to discovery of this deficiency, enhancements to procedural guidance had been made to provide additional programmatic controls on subparts A through H, N and O required records. Since the procedural enhancements were implemented, required comprehensive examinations have been performed. SNC is providing this notification under the provisions of 10 CFR 26.719(b)(4) as a discovered vulnerability of the FFD program." The licensee has started testing the above mentioned personnel and expect full compliance by the beginning of next week. They will be notifying the Public Service Commission of Georgia and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 1 | GA | OTH | GEN | 26.719 |  |  |  | 0 | 2010-09-17
46254 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2010-09-15 17:40 | 2010-09-15 21:00 | 2010-09-29 | BOTH CONTAINMENT HYDROGEN ANALYZERS OUT OF SERVICE DUE TO FAILED SURVEILLANCES "At 1740 CDT, VA-81A, Hydrogen Analyzer Panel, was declared not functional due to failing surveillance test OP-ST-VA-0006, Containment Hydrogen Monitor Monthly Check. VA-81B, Hydrogen Analyzer Panel, was previously not functional due to performance of surveillance test IC-ST-VA-0033, 18 Month Channel Calibration of Containment Hydrogen Analyzer, VA-81B. "This results in no Hydrogen Analyzers being available to monitor containment, which prevents being able to assess for potential loss of containment barrier for Emergency Action Level purposes via the containment hydrogen greater than 3% method. "USAR [Updated Safety Analysis Report] section 9.10.2.5 allows for both Hydrogen Analyzers to be out of service for up to 72 hours. " The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO JOHN KNOKE AT 1152 EDT ON 9/29/10 * * * "Fort Calhoun Station had previously reported that the loss of both hydrogen monitors on September 15, 2010, constituted a major loss of emergency response assessment capability. Additional investigation has determined that other methods of assessment were available that would have provided sufficient indication to make the proper emergency classification. Therefore, this event is being retracted." The licensee has notified the NRC Resident Inspector. Notification was sent to R4DO (Thomas Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-15
46253 | -1 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-09-15 03:13 | 2010-09-15 12:03 | 2010-10-08 | HPCI DECLARED INOPERABLE DURING SURVEILLANCE TESTING "In preparation for quarterly valve testing, the High Pressure Coolant Injection system was declared inoperable and the technical specification required actions were implemented. The system was available for on-line risk. During the testing, the inboard steam isolation valve was stroked closed and reopened and operated properly. The valve was reclosed to continue with valve testing. When an attempt was made to reopen the inboard isolation valve, the valve failed to indicate full open. "The system remained inoperable due to the valve malfunction. Therefore, the condition is being reported in accordance with 10 CFR 50.72 (b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "Maintenance activities are currently in progress to restore the system to the operable status." The licensee entered a 14-day Limiting Condition of Operation per Technical Specification 3.5.1. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM SCOTT BRILEY TO BILL HUFFMAN 1302 EDT ON 10/8/10 * * * "On September 15, 2010, the NRC Operation Center was notified of Event Number 46253 that described a failure of the High Pressure Coolant Injection (HPCI) system inboard steam isolation valve to fully reopen using the Main Control Room (MCR) control switch. "At the time, it was not readily apparent that the system was capable of performing its intended safety function. Therefore, the condition was reported in accordance with 10 CFR 50.72 (b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "Troubleshooting identified that a contact in the control switch circuit had malfunctioned. This contact is bypassed during an initiation signal. Therefore the valve would have opened fully in the event the HPCI system received an initiation signal. "In light of these findings, the HPCI function was not impaired as a result of the contact malfunction and would have been capable of performing its safety function. Therefore, the notification associated with Event Number 46253 is being retracted." The NRC Resident Inspector has been notified. R3DO (Dave Passehl) has been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-09-15
46252 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2010-09-14 14:45 | 2010-09-15 10:21 | 2010-09-15 | AGREEMENT STATE REPORT - MISSING GERMANIUM-68 CHECK SOURCE The following report was obtained from the State of Maryland via e-mail: "As follow-up to a telephone discussion [on the] afternoon of Sept. 14, 2010 at 1445, [the RSO sent the State of Maryland] this email as a written notification of a presumed lost sealed source containing radioactive material. The telephone notification and this email serve [as] compliance with Section D.1201a, which requires an immediate report of a theft or loss of a source of radiation. "The sealed source in question contains Germanium-68, a nuclide of half-life 271 days. This nuclide decays to Gallium-68, which itself then decays (with positron emission) with a half-life of 68 minutes to stable Zinc-68. The annihilation radiation from the positron emission is used for PET scanner quality assurance, as in the case of this source. "This sealed source originally contained 500 microCi of Ge-68 on March 1, 2000. The contained activity of the lost source has been computed to be 0.03 microCi (59000 dpm) as of the date of this notice. The exposure rate of a 1 microCi point (unsealed) source is 5.4 mR/hr at 1 cm; therefore, the exposure rate estimated for this sealed line source at 0.03 microCi is about 0.1 to 0.2 mR/hr at 1 cm. A description of the physical source is [as follows]. The source was manufactured by IPL (product code HEGL-0109) and is 6 inches in length and 1/8 inches in diameter with steel encapsulation. "The source had been stored and not used (due to low activity), and was last inventoried (and leak-tested) on July 22, 2010. An investigation is currently underway to determine the disposition of this source, and will be submitted to the MDE RHP [Maryland Department of the Environment, Radiological Health Program] per D.1201b within thirty days of this notice." The State of Maryland will be conducting a follow-up investigation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2010-09-20
46251 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-09-14 08:15 | 2010-09-14 15:04 | 2010-09-14 | MINOR DIESEL FUEL SPILL INTO THE OCEAN "On September 14, 2010, at approximately 0815 PDT, a minor diesel fuel spill was discovered at the boat dock in the intake cove at the Diablo Canyon Power Plant. A rainbow sheen was observed on the water around the kelp harvester. Harvester operators immediately began deploying absorbent booms and absorbent pads to contain the sheen. It is estimated that less than 2 ounces of diesel fuel reached the water. Mechanics on scene discovered that a small hose clamp had failed on the diesel fuel return line. Repairs were made and the spill was contained. Absorbent pads were used to clean up the residual diesel fuel on the pontoons of the harvester. Repairs were complete and most of the diesel fuel has been absorbed by pads and booms." "The licensee notified the NRC Resident Inspector." The licensee also notified the California State Office of Emergency Services, National Response Center, San Luis Obispo County Environmental Health and the Regional Water Quality Control Board. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-14
46250 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2010-09-14 09:17 | 2010-09-14 14:49 | 2010-09-14 | LOSS OF COMPUTER TRAINS ASSOCIATED WITH ERDADS "At approximately 0917 [EDT], St. Lucie Units 1 and 2 lost both of the computer trains associated with the Emergency Response Data Acquisition and Display System [ERDADS]. After some troubleshooting, the system was restored to service at 1155 [EDT]. This is reportable in accordance with 10 CFR 50.72(b)(3)(xiii), as a major loss of emergency assessment capability." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-14
46249 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-09-09 | 2010-09-14 12:57 | 2010-09-14 | AGREEMENT STATE REPORT - DELIVERED DOSE IS DIFFERENT FROM THE PRESCRIBED DOSE The following information was received by facsimile: "On September 14, 2010, the Department [Wisconsin Department of Health Services] received a facsimile from the licensee's Radiation Safety Officer (RSO) that a medical event occurred on September 9, 2010, involving a permanent implant of I-125 seeds for a prostate manual brachytherapy procedure where the total dose delivered differs from the prescribed dose by 20% or more. This is a medical event as described in DHS 157.72(1)(a)1. The prescribed dose was 145 Gy; the dose delivered was 80 Gy. The licensee uses D80 < 80% as their dose based criteria for determining medical events. Using the licensee's dose based criteria of D80 < 80% the dose received by the prostate was 55% of the intended dose. The underdose was identified during the post-implant planning for the procedure. The RSO indicated that the possible cause was the maximum insertion depth was 0.6 cm below the base of the prostate gland and all needles were implanted distal to the base resulting in the area being 'cold'. Possible corrective actions are under review by the licensee's staff and a one month post-implant CT is planned to determine the impact to the patient. "[Department] inspectors will investigate this medical event on September 16, 2010." Wisconsin Event Report: WI100015 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-09-20
46248 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2010-09-13 10:31 | 2010-09-13 12:35 | 2010-09-13 | SCHEDULED TELEPHONE CABLE REROUTING IMPACTS TO THE CONTROL ROOM AND TECHNICAL SUPPORT CENTER "This is an eight hour report per 10 CFR 50.72 (b)(3)(xiii). Nine Mile Point is implementing a scheduled modification to reroute telephone cables as part of a planned Interim Spent Fuel Storage (ISFSI) modification. This rerouting will enable construction of the roadway to the ISFSI storage location and ensure no damage to telephone cables which currently pass through the roadway. The re-routing will ensure that no cabling important to control room and or TSC will pass under the roadway "This work required that all Federal Telephone System (FTS) 2001 lines including Emergency Notification System (ENS), Health Physics Network (HPN) and Emergency Response Data System (ERDS) be removed for a period of approximately 1 hour. "During the upgrade starts only 5 circuits were removed at a time and tested upon completion of re-routing. There was at least 2 alternate means of communication (via commercial telephone lines) continuously available. "If an emergency had been declared during this period, the Control Room had the capability to make the notification to the offsite agencies using commercial telephone lines. The emergency preparedness communications procedure provides adequate instructions for use of these backup means. The Nine Mile Point procedures provide for alternate means of emergency assessment capability. "All work associated with this modification was performed in an expeditious manner consistent with the goal of minimizing unavailability of the systems listed above. A test of all systems will be performed at the completion of the upgrade. "All Control Room personnel have been briefed on this work and expected contingent actions. "This job began on Monday, September 13, 2010 at approximately 1031 [EDT] and was completed at 1153 [EDT]. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-13
46247 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2010-09-13 09:00 | 2010-09-13 12:17 | 2010-09-13 | OFFSITE NOTIFICATION FOR DISCHARGE OF 200 GAL UNTREATED SANITARY WATER "At 0900 [EDT] this morning, Seabrook Station experienced leakage of approximately 200 gallons of untreated sanitary water to the storm drain system, which discharges to the circulating water system. Since Seabrook is not authorized to discharge untreated sanitary water, this event has been reported to the town of Seabrook and will be reported to the New Hampshire Department of Environmental Services and the Environmental Protection Agency. The preliminary apparent cause of the leak was a failure of the sanitary lift station discharge pumps to start automatically, which resulted in untreated sanitary water overflowing into the storm drain system. The leak was stopped by restarting the sanitary lift station discharge pumps. This event is being reported under 10CFR50.72(b)(2)(xi) for an event related to the protection of the environment for which notification to other government agencies has been or will be made." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-13
46246 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-09-09 15:34 | 2010-09-10 19:46 | 2010-09-10 | MANUAL REACTOR TRIP DURING STARTUP DUE TO A CONTROL BANK STEP COUNTER FAILURE "During a Unit 4 reactor startup on 9/9/2010 while the reactor was subcritical in Mode 3, the Control Bank C Group 1 Step Counter failed [due to a battery failure]. The reactor trip breakers were opened in accordance with procedures as required by the Action of Technical Specification 3.1.3.3. All rods fully inserted. The unit remained in Mode 3. This was a manual actuation of the reactor protection system. "This report is made in accordance with 10 CFR 50.72(b)(3)(iv)(A) - Valid actuation of the Reactor Protection System. This is a late report. Reportability was not recognized at the time of the event as a result of misleading guidance in 0-ADM-115 'Notification of Plant Events' [site specific] procedure. A condition report is being initiated [by the licensee] to evaluate procedure changes to avoid further occurrences." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-09-10
46245 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2010-02-22 | 2010-09-10 17:29 | 2010-11-19 | AGREEMENT STATE REPORT - BROKEN FIXED GAUGE SHUTTER The following information was received via facsimile: "Jeld-Wen Wood Fiber of Oregon located in Klamath Falls possesses 5 fixed gauges at their wood door manufacturing facility. "In late December 2009, the Radiation Protection Services [RPS] office [State of Oregon] received a phone call from [the Jeld-Wen] Maintenance Manager, who talked to [the] RPS Licensing Manager and stated that he wished to report that there were two gauges at their facility that were having shutter mechanism problems. [The Maintenance Manager] stated he would elaborate on the issue in an email. "On February 22, 2010, [the Maintenance Manager] emailed [the RPS Licensing Manager] and stated that the gauge with the broken shutter mechanism (Ronan, model SA-8, serial M2119, 20 mCi Cs-137, high level indicator gauge, installed 12-15-88) was operating in the open shutter position and unable to close. [The Maintenance Manager] stated that the licensee had manufactured a 1.5" thick shutter (by approximately 8 inches wide by approximately 1 meter long) that fits between the gauge and the vessel it is attached to. He also stated that this gauge is in a restricted access area that is roped off and the closest area of worker frequency is 20 feet away. [The Maintenance Manager] stated that the other gauge with the 'sticking' shutter (Ronan, model GS-200, serial 3401, 50 mCi Cs-137, digester level indicator, installed 12-15-88) is closable and is also operating. He stated that he would be scheduling a repair for the 50 mCi gauge and would be evaluating whether a replacement will be needed for the 20 mCi gauge. "On March 15, 2010, [the Maintenance Manager's] email to [the RPS Licensing Manager] was given to [an RPS employee] in radioactive materials licensing. From [the RPS Licensing Manager's] email, another staff member may be working on this incident. [The RPS employee] phoned [the Maintenance Manager] and found that this was an event possibly not entered into the system but he would check with materials inspectors to see if that was the case. [The Maintenance Manager] stated that he was scheduling for repair of the 50 mCi gauge and possibly the 20 mCi gauge but not sure of the latter. [The Maintenance Manager] also stated that he would be submitting an amendment request naming him as Radiation Safety Officer. "On May 21, 2010, [the RPS employee] requested an update on the repairs/actions by the licensee for the two gauges. No response was received. "On June 9, 2010, [the Maintenance Manager] phoned [the RPS employee]. He stated that the company did not have the fiscal ability to replace the 20 mCi gauge and asked if the company could continue operating the gauge for approximately 2 more years. [The RPS employee] stated that the SS&D sheet would have to be reviewed as well as an onsite inspection of the gauge. "On June 23, 2010, [the RPS employee] reviewed the SS&D for the 20 mCi device. For a 500 mCi Cs-137 source, exposure rates with the shutter open were listed as 43 mR per hr at 2 inches, 4.3 mR per hr at 1 foot, and 0.6 mR per hr at 1 meter. At 4 percent of maximum activity allowed, the 20 mCi source located in a restricted access area using 1 meter distance should give an exposure rate of approximately 300 microR per hr maximum. It was also determined that an inspection would be made of the facility in Klamath Falls in late July [in order] to verify exposure rates around the gauge with the shutter open. "On July 27, 2010, an inspection of the facility was performed by [another employee of RPS]. [This other RPS employee] determined exposure rates around the 20 mCi gauge to be approximately 100 microR per hr at 1 meter. [This other RPS employee] also noted that the gauge is located at or below the catwalk that accesses that area. The licensee was allowed to continue operation with the shutter. [The other RPS employee] also discovered that the 50 mCi gauge with the sticking shutter was not actually sticking but merely hard to open and close due to residue/resin buildup. The licensee cleaned the residue off and covered the shutter mechanism and gauge with a metal canopy to prevent future buildup. Vendor work on this gauge was not performed as the licensee corrected the issue internally. Management approval for the modified shutter of the 20 mCi gauge will be sought at this time. [The Maintenance Manager] noted also during the inspection that the issues with the two gauges had been known by the licensee for approximately 2 years and was only then being reported because he was to become the new RSO and thought it should be. "On September 10, 2010, a review of this incident was performed and it was found that the NRC HOO had not been notified. A copy of open NMED events for Oregon was also reviewed and no mention of this incident was found. NRC was notified of the incident at this time. Oregon RPS management has not made a final decision on the 20 mCi gauge with the broken shutter mechanism." * * * UPDATE FROM DARYL LEON TO HOWIE CROUCH VIA FAX ON 11/19/10 @ 1450 EST * * * "On October 1,2010, [the owner of] an Oregon-licensed fixed gauge service vendor company (RS&S Calibration LLC), Oregon license ORE-91083) contacted the Oregon Radiation Protection Services (RPS) office by email stating that he had cleaned and oiled the shutter mechanism on the gauge with the shutter stuck open (Ronan model SA-8, s/n M2119) and the unit is working properly. The handle is broken yet and [the vendor owner] stated that the customer is going to order a new handle. "On October 25, 2010, Daryl Leon of RPS emailed the site RSO, Rob Reifel to determine status of handle repair. Mr. Reifel emailed that he was still trying to get a quote on the part and asked if his site maintenance personnel can manufacture a new handle. He also added that [the repair vendor] indicated he (Reifel) should use one provided by the manufacturer. Mr. Leon responded by email stating that the part should be obtained from the manufacturer since safety evaluation of the device was performed with parts originally from the manufacturer and a locally-manufactured part would not suffice. Mr. Reifel indicated that he would 'push harder' to get this done. "On November 8, 2010, Mr. Reifel emailed Mr. Leon stating that the handle was fixed and that the fix was performed November 4,2010. "This event is ready for closure for the HOO and NMED (incident 100458)" Notified R4DO (Pick) and FSME EO (Villamar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2010-09-15
46244 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-09-10 10:00 | 2010-09-10 17:00 | 2010-09-10 | DEGRADATION OF SAFETY EQUIPMENT "At approximately 1000 [EDT] on September 10, 2010 during normal operation of a Gad slugger feed hood in the Fuel Manufacturing Building, a connection between the powder hopper and the vibrating feeder was observed as being not properly secured. After starting the vibrating feeder a small amount of powder leaked from the vibrating feeder into the hood. The base of the hood is equipped with a photo-sensor that detected the powder accumulation and automatically shut down the vibrating feeder to stop the leak. A total of 2.2 kg of powder was removed from the hood. An investigation determined that a clamp on the feed tube had not been properly reinstalled following an equipment cleanout. "The two controlled parameters for criticality safety of this equipment are moderation and geometry and Items Relied on for Safety (IROFS) are established for both. With the clamp improperly installed, the geometry-related IROFS was in a degraded state. Additional IROFS on moderation remained available to perform their intended safety functions and were not challenged. Geometry control was maintained by the photo-sensor interlock; however this IROFS is not credited for this accident sequence in the ISA. "Although, this event did not result in an unsafe condition and double contingency was maintained, the performance requirements could not be met when taking no credit for the degraded IROFS. As a result, this report is conservatively being made per 10CFR70 Appendix A (b)(2). "The Gad slugger and similar equipment have been shutdown pending implementation of additional corrective actions." The licensee will notify the NRC Region 2 Office, the North Carolina Radiation Protection Section and the New Hanover County Emergency Preparedness Organization. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-09-10
46243 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-09-09 14:30 | 2010-09-10 14:00 | 2010-09-10 | ACCIDENT EVALUATION IMPROPERLY ANALYZED IN THE INTEGRATED SAFETY ANALYSIS "During a GNF-A [Global Nuclear Fuel-Americas] review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was determined at [1430 EDT] on September 9, 2010 that the accident evaluation associated with hydrogen containment in the Dry Conversion Process was improperly analyzed in the ISA. A loss of hydrogen containment was analyzed in the ISA, however appropriate Items Relied on for Safety (IROFS) to prevent or mitigate a hydrogen explosion, resulting in a loss of UF6 or HF containment, were not identified in the ISA. "The affected equipment was promptly shut down on September 9, 2010. Existing hydrogen detection systems were augmented to assure controls are available and reliable to perform their intended safety functions as interim compensatory measures. These controls were functionally verified prior to restart of the affected operations at 2230 [EDT] on September 9, 2010. The interim controls will be designated as IROFS upon completion of the ISA documentation update currently underway. "This event is being reported pursuant to the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours of discovery." The licensee considers this discovery to be of low safety significance because the discovery did not result in an unsafe condition. The required IROFS have been identified and are in place. The licensee notified the NRC Region 2 Office, the North Carolina Radiation Protection Section and the New Hanover County Emergency Preparedness Organization. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-09-10
46242 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2010-09-09 15:20 | 2010-09-10 13:47 | 2010-09-10 | EMERGENCY SIRENS INADVERTENTLY ACTUATE "Spurious siren activation at Point Beach affects associated sirens (P001 - P010) at Kewaunee Power station. A separate 50.72 notification is to be made for Kewaunee per procedure GWP-11.08.04. "At 1216 CDT, 09/10/10 station EP personnel notified the control room staff that an inadvertent activation of EP sirens occurred for the Point Beach Station at 1520, 09/09/10. This information was relayed to the EP personnel via Manitowoc County EP personnel, who had received the information from Point Beach personnel previously. Below is the information from the Point Beach notification: "At 1520 CDT, Point Beach was notified by Manitowoc County Sherriff's Department (MCSD) and citizens of audible EP siren actuation in the city of Two Rivers and the town of Two Creeks, WI. System troubleshooting was in progress at the time of actuation. "Alert and Notification System siren configuration was restored to normal at approximately 1630 CST, 09/09/10. All required ANS sirens were 'poll tested' and are fully functional. "Further reviews indicated that sirens P-001 through P-013 (13 sirens) had each simultaneously received a 180 second activation. At this time the cause of the activation signal is unknown. All troubleshooting and testing are currently suspended; event investigation has commenced." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-10
46241 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2010-09-09 21:29 | 2010-09-10 00:29 | 2010-09-10 | MANUAL REACTOR TRIP DUE TO SERVICE WATER LEAK IN THE MAIN GENERATOR EXCITER HOUSING "On September 9, 2010, at approximately 2129 hours [EDT], Indian Point 3 manually tripped the reactor from the control room following indications of a service water leak in the Main Generator Exciter housing. Unit 3 is currently stable in mode 3. All automatic actions occurred as required. All control rods fully inserted. No primary or steam generator safety relief valves lifted. The motor driven auxiliary feedwater pumps automatically started on low steam generator level as designed. Decay heat removal is via the steam generators to the main condenser. Offsite power is available and supplying all safeguards busses. "Unit 2 is unaffected and remains in Mode 5 in a forced outage for 21 RCP [Reactor Coolant Pump] repair. "During the Fast Bus Transfer [the] 34 Reactor Coolant Pump tripped. The cause is being investigated. "There was an inadvertent release of CO2 to 31 Main Boiler Feed Pump. The cause was due to the suction relief valve lifting which has subsequently reseated. "The NRC Sr. Resident Inspector and New York State Public Service Commission have been notified." The reactor is currently being maintained at normal operating temperature and pressure. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-10
46240 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-09-09 15:20 | 2010-09-09 20:25 | 2010-09-12 | EMERGENCY SIRENS INADVERTENTLY ACTUATE "At 1520 [CDT], Point Beach was notified by Manitowoc County Sheriff's Department (MCSD) and citizens of audible EP Siren actuation in the City of Two Rivers and the Town of Two Creeks, WI. System troubleshooting was in progress at the time of actuation. "Alert and Notification System Siren configuration was restored to normal at approximately 1630 [CDT]. All required ANS sirens were 'Poll tested' and are fully functional. "Further reviews indicated that Sirens P-001 through P-013 (13 sirens) had each simultaneously received a 180 second activation. At this time the cause of the activation signal is unknown. All troubleshooting and testing are currently suspended; event investigation has commenced." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RIVAS TO KLCO ON 9/12/10 AT 1156 * * * "This notification is an update to ENS notification #46240 made by Point Beach. "Notification #46240 was submitted September 9 at 2025 EDT regarding Point Beach notification by Manitowoc County Sheriff's Department (MCSD) and citizens of audible EP Siren actuation in the City of Two Rivers and the town of Two Creeks, WI. System troubleshooting was in progress at the time of actuation. "This notification is to inform [the NRC] of the planned press release to inform the citizens of the affected communities of the event. "At 0834 CDT 9/12/2010 Point Beach issued a letter to the Editor of Manitowoc Times Herald Times Reporter Newspaper regarding inadvertent Siren Activation. "Corrective actions have been taken in the [Point Beach] EP siren maintenance program to avoid a recurrence and the Site Resident NRC Inspector has been notified." Notified the R3DO (Lipa). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-09
46239 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-09-09 14:50 | 2010-09-09 18:45 | 2010-09-09 | MISSING TRITIUM EXIT SIGN The following information was received by e-mail: "[The licensee] reported that during demolition work by their Maintenance Staff a wall with a tritium exit sign was demolished and the debris was removed from the facility. The manufacturer of the sign is Safety Light. [The licensee] will investigate the model of the sign that was installed. [The licensee] confirmed that the debris has left their facility as waste. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-09-14
46238 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-09-09 14:37 | 2010-09-09 18:04 | 2010-09-09 | REACTOR TRIP DUE TO OVERTEMPERATURE DELTA-T SIGNAL "At 1437 hours EDT on September 9, 2010, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the Overtemperature Delta-T reactor protection function. "During the event, the steam generator power operated relief valves (PORVs) and one pressurizer PORV briefly opened and re-closed, in response to pressure changes in the steam generators and pressurizer due to the plant transient condition. The Auxiliary Feedwater System automatically actuated, as expected, and provided feedwater to the steam generators. The main steam safety valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently stable in Mode 3. "There was an indication of an approximate 0.65 gpm leak to the pressurizer relief tank following the reactor trip. The isolation valve to the pressurizer PORV that opened during the reactor trip was closed and the leak indication stopped. The indicated leakage was within Technical Specification leakage rate limits. "The cause of the reactor trip and indication of pressurizer PORV leakage is under investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-09
46237 | 0 | ROTORK CONTROLS |  |  |  |  | 2010-07-16 | 2010-09-09 14:36 | 2010-09-09 | PART 21 REPORT FOR AN OPTIONAL SUBASSEMBLY USED ON VALVE ACTUATORS The following information was received by facsimile: "Rotork designs and manufactures valve actuators; a product that attaches to a valve to permit the remote operation of the valve. "[Rotork Controls] is writing to notify the NRC that Duke Energy has received from Rotork a basic assembly containing a defective sintered gear Pt. No. 22641. No other [NRC] licensee has received this part. The defective component is part of an optional subassembly called an 'Add On Pack' (AOP). Duke Energy purchased AOPs with all Rotork NA1E type actuators. "The defective gear could cause the AOP to seize and fail to operate. The actuator will continue to perform its safety related function with a seized AOP. The AOP provides position information, through auxiliary switches, during the actuator's operation. "Duke Energy was first notified of the condition on July 16, 2010 and on August 6, 2010 received a formal letter in which the extent of condition was communicated. Rotork proceeded to investigate the problem, run life tests and understand the failure mode. On September 3, 2010 Duke Energy informed Rotork in writing that the AOP must support the design-basis function of the associated valve/actuator assembly. On the same date Rotork shared with Duke energy [information] which confirmed that the gear design was sound and that the gear failure was attributable to the supplier's manufacturing process. "The gear supplier's production process has been corrected and Rotork quality assurance is verifying that subsequent batches are conformant to specification. Duke Energy is being provided with replacement AOPs and conformant gears on an as requested basis." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2010-09-09
46236 | 0 | VA MEDICAL CENTER JACKSON |  |  |  |  | 2010-09-08 | 2010-09-09 14:00 | 2010-09-09 | MEDICAL DOSE DIFFERENT THAN PRESCRIBED DOSE The following information was received by e-mail from a program manager with the U.S. Department of Veterans Affairs, Veterans Health Administration (VHA), National Health Physics Program (NHPP): " [The VHA is] notifying the NRC of 11 medical events at G.V. (Sonny) Montgomery VA Medical Center, Jackson, Mississippi. These medical events occurred for Iodine-125 permanent prostate seed implant brachytherapy. "As historical information, 10 medical events were reported to NRC on earlier dates for prostate seed implants at this medical center under NRC Event Report No. 44522. "Following up on those medical event reports, VHA initiated a comprehensive external review and reanalysis of post-treatment dose parameters for all prostate seed implants performed at the medical center. "Upon evaluation of updated dose information generated by the external review, medical center staff, working with NHPP, discovered on September 8, 2010, that 11 additional medical events need to be reported. "10 of the 11 events were based on updated D90 values (considered to be final values) for the planned treatment site being 80% or less than the prescribed dose. This circumstance is interpreted as meeting the definition of a medical event per 10 CFR 35.3045(a)(1)(i). "1 of the 11 events was based on absorbed dose to a tissue other than the treatment site exceeding the expected dose by 50% or more. This circumstance is interpreted as meeting the definition of a medical event per 10 CFR 35.3045(a)(3). "As additional information, medical center staff, working with NHPP, has determined that 4 of the 10 previously reported medical events under NRC Event Number 44522 could be retracted because updated D90 values (considered to be final values) from the external review are above 80% of the prescribed dose. If retraction of these 4 events is pursued, NHPP will discuss the dose information with NRC Region III prior to notifying the NRC Operations Center of the retractions. "NHPP will ensure that the medical center follows NRC requirements for notification of the referring physician and patient for these medical events. The patients involved in the medical events have been tracked by the medical center and the clinical outcomes for the patients have been verified to be consistent with expected clinical outcomes for successful prostate seed implants. "A 15-day written report of these medical events will be submitted to NRC Region III. "[The VHA] will notify the NRC Project Manager, Cassandra Frazier (NRC Region III), of these medical events. "In summary, [VHA is] confirming a total of 17 medical events for the medical center. 11 medical events are reported today (10 based on a low dose to treatment site; 1 based on elevated dose to other organs and tissues). 6 medical events were reported previously under NRC Event No. 44522. 4 of the 10 medical events previously reported under NRC Event No. 44522 no longer meet criteria as medical events and might later be retracted. "Additional Information: "Department of Veterans Affairs has a Master Materials License (MML) from the NRC: License No. 03-23853-01VA. Permits are issued under the MML to VA facilities. The VA submits reports to the NRC through the VHA's National Health Physics Program office located in North Little Rock, AR. "Address of permittee involved in this event: G.V. (Sonny) Montgomery VA Medical Center, 1500 East Woodrow Wilson Drive, Jackson, Mississippi 39216. "VHA permit number of permittee involved in event: Permit No. 23-08786-01." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | MS | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-09-15
46235 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-09-08 13:45 | 2010-09-08 15:52 | 2010-09-08 | AUTOMATIC REACTOR TRIP DURING MAINTENANCE ON A REACTOR PROTECTION SYSTEM RELAY "At 1345 [EDT] on 9/8/10, Turkey Point Unit 4 automatically tripped during the repair of a failed Turbine Stop Valve Relay which inputs into the Reactor Protection System. During the replacement of this relay, the logic condition was met causing a Reactor Trip and Turbine Trip. "At the time of the trip, reactor power was 100%. Auxiliary Feedwater was automatically initiated when Steam Generator levels lowered below the actuation setpoint. Steam Generator levels are now stable at their normal band and Auxiliary Feedwater is now secured. "Additionally, the Source Range Detectors did not automatically energize and were manually energized and are operating correctly. "Unit 4 has been stabilized in Mode 3 on normal off-site power. This event is reportable per 10CFR50.72(b)(2)(iv)(B) - actuation of the Reactor Protection System with the reactor critical and 10CFR50.72(b)(3)(iv)(A) - valid actuation of an ESF system (AFW)." The trip was characterized as uncomplicated. All rods fully inserted. No relief valves lifted during the transient. Normal feedwater has been re-established to the steam generators and decay heat is being removed via the turbine bypass valves to the condenser. The unit is in a normal shutdown electrical lineup. There was no impact on Unit 3. The license has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-08
46234 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-09-08 07:47 | 2010-09-08 11:00 | 2010-09-08 | OFFSITE NOTIFICATION DUE TO BODY DISCOVERED IN THE OWNER CONTROLLED AREA "At 0747 hours on September 8, 2010, a body was discovered on the beach along the Owner Controlled Area at the Cook Nuclear Plant. "Local law enforcement agencies have been notified. It is expected that a press release will be issued from local law enforcement. "The NRC Senior Resident Inspector was notified. Plant operation was not impacted by the event. The fatality did not occur on site. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of offsite agencies and expected media involvement related to the discovery." Although unconfirmed, the licensee believes that the body belongs to a person that went missing on the lake last week. The licensee notified Lake Township, Berrien County Sheriffs Office, Federal Bureau of Investigation and the U.S. Coast Guard. Either Berrien County or Lake Township will be issuing a press release. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-09-08
46233 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-09-04 | 2010-09-07 11:54 | 2010-09-07 | LOCKING MECHANISM MALFUNCTION ON RADIOGRAPHY CAMERA "On September 4th the radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an INC IR-100 exposure device (serial number 6631). "At the end of the shift the source was cranked in and the camera was surveyed per the proper procedure. There were no abnormal readings observed during the survey and the key was turned to the lock position. When the crank assembly was removed it was noted that the pigtail was not fully seated. "The 2 mR/Hr boundary was reconfirmed and the Radiation Safety Supervisor was notified. A trained radiographer came to the site and removed the locking system and cleaned it. The locking system was successfully reinstalled. The camera has been returned to service. "Exposure Device: Industrial Nuclear IR-100 Device S/N: 6631 Source S/N: P661 Source Activity: 84 curies Source Type: Ir192 Source Model # INC Model 32 "There was no exposure to the crew or the general public during this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-09-07
46232 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-09-07 10:43 | 2010-09-07 10:43 | 2010-09-30 | PLANT IN-PROCESS COMPUTER OOS FOR MAINTENANCE "The Beaver Valley Power Station (BVPS) Unit 1 In-Plant Computer (IPC) will be taken out of service for approximately 4 weeks (9/7/10 - 9/30/10) to implement a planned modification. The current IPC is being replaced and a computer outage is required to allow for installation of a new IPC. During this time period the Emergency Response Data System (ERDS) data link to the NRC will not be available at BVPS Unit 1. Other computer based systems not directly associated with the IPC (e.g. Safety Parameter Display System (SPDS), meteorological data) will remain in operation. ERDS parameters will be available to be monitored by control board indications and temporary computer system set up prior to the IPC outage. Compensatory actions have been developed to direct one of the Technical Support Center (TSC) Operations communicators to respond to the control room during a BVPS Unit 1 emergency, should it occur, to facilitate data transfer to the NRC while the ERDS is out of service. Work on replacing the IPC and returning ERDS to service will be ongoing continuously until complete. "This is an 8-hour reportable event per 10 CFR 50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of BVPS Unit 1 and Unit 2 plant systems will not be adversely affected due to this planned action. BVPS Unit 2 ERDS will not be affected by these modifications. "The NRC Resident Inspector has been notified." * * * UPDATE FROM THOMAS MIGDAL TO HOWIE CROUCH @ 2215 EDT ON 9/30/10 * * * "The Beaver Valley Power Station Unit 1 In-Plant computer has been returned to service. The Emergency Response Data System data link to the NRC is now available. "The NRC Resident Inspector has been notified." Notified R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-09-07
46231 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-09-02 | 2010-09-03 15:30 | 2010-09-03 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILURE The State of Texas submitted the following information via e-mail: "On September 3, 2010, the [State of Texas] received a phone call from the licensee informing them that on September 2, 2010, while conducting routine gauge inspections, the shutter on an Ohmart Vega model SH-F1-A nuclear gauge failed to close. The gauge contains two milliCuries of Cesium (Cs) 137. Open is the normal operating position for the gauge. Radiation surveys in the area of the gauge were measured and were normal. The licensee tried to free the shutter operating mechanism using light oil, but it did not respond. The licensee stated that the gauge is 11 feet off of the ground and there is no access to it without the use of scaffolding and it does not pose a risk of exposure to anyone. The licensee will contact the manufacturer to request repairs on the gauge." Texas Incident No. I-8779. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-09-08
46230 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2010-09-03 | 2010-09-03 15:23 | 2013-12-16 | PART 21 - FAILURE TO INCLUDE SEISMIC INPUT IN REACTOR CONTROL BLADE CUSTOMER GUIDANCE The following is text of a facsimile submitted by the vendor: "GE Hitachi Nuclear Energy (GEH) has identified that engineering evaluations that support the guidance provided in SC 08-05, Revision 1, do not address the potential impact of a seismic event on the ability to scram as it relates to the channel-control blade interference issue. Note that the seismic loads are not a consideration in the scram timing, but rather the ability to insert the control blades. In other words, the control blades must be capable of inserting during the seismic event, but not to the timing requirements of the Technical Specifications. GEH is evaluating the impact of the seismic loads between the fuel channel and the control blade associated with an Operating Basis Earthquake (OBE), and a Safe Shutdown Earthquake (SSE) on BWR/2-5 plants. The scram capability is expected to be affected due to the added seismic loads at low reactor pressures in the BWR/2-5 plants. The ability to scram for the BWR/6 plants is not adversely affected by the seismic events. Additional evaluation is required to determine to what extent the maximum allowable friction limits specified for the BWR/2-5 plants in SC 08-05 Revision 1 is affected by the addition of seismic loads. "GEH issues this 60-Day Interim Report in accordance with the requirements set forth in 10 CFR 21.21 (a)(2) to allow additional time to for this evaluation to be completed." Affected US plants previously notified by vendor and recommended for surveillance program include: Nine Mile Point, Units 1 and 2; Fermi 2; Columbia; FitzPatrick; Pilgrim; Vermont Yankee; Grand Gulf; River Bend; Clinton; Oyster Creek; Dresden, Units 2 and 3; LaSalle, Units 1 and 2; Limerick, Units 1 and 2; Peach Bottom, Units 2 and 3; Quad Cities, Units 1 and 2; Perry, Unit 1; Duane Arnold; Cooper; Monticello; Brunswick, Units 1 and 2; Hope Creek; Hatch, Units 1 and 2; and Browns Ferry, Units 1and 2. Affected US plants previously notified by vendor and provided information include: Susquehanna, Units 1 and 2 and Browns Ferry, Unit 3. * * * UPDATE FROM DALE PORTER TO ERIC SIMPSON AT 1556 ON 09/27/2010 * * * The following update was received via fax: "This letter provides a revision to the information transmitted on September 2, 2010 in MFN 10-245 concerning an evaluation being performed by GE Hitachi Nuclear Energy (GEH) regarding the failure to include seismic input in channel-control blade interference customer guidance. Two changes have been made in Revision 1: "1) A statement was added regarding the applicability of this issue to the ABWR and ESBWR design certification documentation. "2) The original MFN 10-245 referenced the Safety Communication SC 08-05 R1 that was transmitted to the US NRC via MFN 08-420. The references to SC 08-05 were changed to MFN 08-420 to prevent possible confusion. "As stated herein, GEH has not concluded that this is a reportable condition in accordance with the requirements of 10CFR 21.21(d) and continued evaluation is required to determine the impact of a seismic event on the guidance contained in MFN 08-420." Notified the R1DO (Gray), R2DO (Hopper), R3DO (Orth), R4DO (Farnholtz), NRR EO (Lee) and Part 21 Group (via email). * * * UPDATE FROM DALE PORTER TO MARK ABRAMOVITZ AT 1723 ON 12/15/2010 * * * The following update was received via fax: "This letter provides information concerning an on-going evaluation being performed by GE Hitachi Nuclear Energy (GEH) regarding the failure to include seismic loads in the guidance provided in MFN 08-420. As stated herein, GEH has not concluded that this is a reportable condition in accordance with the requirements of 10CFR21.21(d) and continued evaluation is required to determine the impact of a seismic event on the guidance contained in MFN 08-420. "GEH has not completed the evaluation of the impact of the seismic loads between the fuel channel and the control blade associated with an Operating Basis Earthquake (OBE), and a Safe Shutdown Earthquake (SSE) on BWR/2-5 plants." GEH expects the task to be completed by August 15, 2011. Notified the R1DO (Holody), R2DO (Henson), R3DO (Kozak), R4DO (Werner), NRR EO (Evans) and Part 21 Group (via email). * * * UPDATE AT 1808 EDT ON 08/11/11 FROM DALE PORTER TO JOE O'HARA * * * The following was received via fax: "GE Hitachi Nuclear Energy (GEH) identified, in July 2010, that engineering evaluations did not address the potential impact of a seismic event on the ability to scram as it relates to the channel-control blade interference issue. GEH provided status of the on-going evaluation in [December 2010]. GEH has not completed the evaluation of the impact of the seismic loads between the fuel channel and the control blade associated with a bounding Safe Shutdown Earthquake (SSE) on BWR/2-5 plants. The scram capability is expected to be affected due to the added seismic loads at low reactor pressures [less than 1000 psig] in the BWR/2-5 plants. Additional evaluations are required to determine to what extent the maximum allowable friction limits specified for the BWR/2-5 plants are affected by the addition of SSE seismic loads at low reactor pressures. "GEH issues this 60-Day Interim Report in accordance with the requirements set forth in 10CFR 21.21 (a)(2) to allow additional time for this evaluation to be completed." The following sites are noted as having channel-control blade concerns: Region 1: Nine Mile Point, Fitzpatrick, Pilgrim, Vermont Yankee, Oyster Creek, Limerick, Peach Bottom, Susquehanna, and Hope Creek Region 2: Browns Ferry, Brunswick, Hatch, Region 3: Fermi, Clinton, Dresden, LaSalle, Quad Cities, Perry, Duane Arnold, Monticello Region 4: Columbia, Grand Gulf, River Bend, Cooper. Notified R1DO (Powell), R2DO (Hopper), R3DO (Dickson), R4DO (Farnholtz) and NRR Part 21 Grp via email. * * * UPDATE AT 0037 EDT ON 9/27/11 FROM PORTER TO HUFFMAN VIA E-MAIL * * * The following is a summary of information received from GE Hitachi Nuclear Energy via e-mail of a letter, Reference MFN 10-245 R4, addressed to the NRC and dated September 26, 2011: "GE Hitachi (GEH) has determined that the scram capability of the control rod drive mechanism in BWR/2-5 plants may not be sufficient to ensure the control rod will fully insert in a cell with channel-control rod friction at or below the friction limits specified in MFN 08-420 with a concurrent Safe Shutdown Earthquake (SSE). The plant condition for which incomplete control rod insertion might occur is when the reactor is below normal operating pressure (<900 psig) and a scram occurs concurrent with the SSE, for Mark I containment plants, and for the SSE with concurrent Loss-of-Coolant Accident (LOCA) and Safety Relief Valve (SRV) events for Mark II containment plants. In this scenario a Substantial Safety Hazard results because the affected control rods might not fully insert to perform the required safety function. "GEH has determined that when channel-control blade interference is present at reduced reactor pressure and at friction levels considered acceptable in MFN 08-420, a simultaneously occurring Safe Shutdown Earthquake (SSE) may result in control rod friction that inhibits the full insertion of the affected control rods during a reactor scram from these conditions. This scenario was not explicitly considered in MFN 08-420. "GEH has also quantified maximum allowable control rod friction for channel-control blade interference during the SSE with reactor system pressure greater than or equal to 900 psig. The previous conclusion regarding the scram capability for the BWR/2-5 plants, last communicated in MFN 10-245 R2, was based upon a reactor system pressure of 1000 psig. The updated evaluation at 900 psig has resulted in modifications to the guidance specified in MFN 08-420. "The GE Hitachi Letter recommends testing with new allowable friction limits that will ensure control rods fully insert at low reactor pressure concurrent with an SSE (for Mark I containment plants) and SSE with concurrent LOCA (for Mark II containment plants). The enclosure in the GEH letter provides a description of the evaluation, with surveillance recommendations for BWR/2-5 plants. The recommended surveillance is intended to augment the surveillance requirements in the plant Technical Specifications and define populations of control rods to be tested, and the method for testing, until other actions that mitigate or limit the potential for channel control blade interference can be identified and implemented. "Based upon the evaluation, GEH has concluded that a Reportable Condition under 10CFR Part 21 exists for BWR/2-5 plants. This determination does not apply to BWR/6 or ABWR plants or the ABWR/ESBWR Design Control Document's (DCD). The information contained in this document informs the NRC of the conclusions and recommendations derived from GEH's evaluation of this issue." The list of potentially affected plants has previously been noted in this Part 21 notification and have been previously notified by GE Hitachi of the concern. Notified R1DO (Doerflein), R2DO (Lesser), R3DO (Passehl), R4DO (Werner) and NRR Part 21 Grp via email. * * * UPDATE AT 1205 EDT ON 2/7/12 FROM LISA SCHICHLEIN TO CHARLES TEAL VIA E-MAIL * * * GE Hitachi Nuclear Energy (GEH) provided an update to its guidance and supporting evaluations that were reported in MFN 10-245 R4 on September 26, 2011. Notified R1DO (Burritt), R2DO (Calle), R3DO (Giessner), R4DO (Camplbell) and Part 21 Group via email. * * * UPDATE AT 1427 EST ON 12/16/13 FROM LISA SCHICHLEIN TO JOHN SHOEMAKER VIA EMAIL * * * GE Hitachi Nuclear Energy (GEH) provided an update to its guidance and supporting evaluations that were reported in MFN 08-420 R0 on December 19, 2008 and MFN 10-245 R5 on February 7, 2011. Notified R1DO (Dimitriadis), R2DO (Rose), R3DO (Riemer), R4DO (Lantz) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-09-03
46229 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2010-09-03 10:58 | 2010-09-03 13:11 | 2010-09-03 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO HIGH STEAM GENERATOR LEVEL "On September 3, 2010, at approximately 1058 hrs., Indian Point Unit 2 automatically tripped from 41% power due to High Steam Generator Level. At the time of the trip, Unit 2 was performing a power reduction to take the unit offline for a planned maintenance outage. Unit 2 is currently stable in Mode 3. All automatic actions occurred as required. All control rods fully inserted with the exception of rod H-8 - which indicates 26 inches withdrawn. No primary or steam generator safety or relief valves lifted. The motor driven auxiliary feedwater pumps automatically started on low steam generator level as designed. Decay heat removal is via the steam generators to the main condenser. Offsite power is available and supplying all safeguards busses. "The cause of the trip and rod H-8 position indication are under investigation. "Unit 3 is unaffected and remains in Mode 1 at 100% power." The NRC Resident Inspector has been notified. Offsite notification was made to the State of New York. No press releases are planned. | 0 | 0 | 0 | 41 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-09-03
46228 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-09-02 10:00 | 2010-09-03 11:26 | 2010-09-03 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILURE The following was received from the State of Texas via e-mail: "On September 3, 2010, the [State of Texas] was notified by the licensee that on September 2, 2010 the shutter on a NDC Model 103 nuclear gauge failed to fully open during a routine maintenance check. The gauge contains a 150 milliCurie Americium - 241 source. The gauge shutter has been locked closed. The gauge has been removed from the vessel and placed into storage. The dose rate measured at 3 feet from the gauge was 0.4 milliRem per hour. No significant radiation exposure was received by an individual during this event. The manufacturer was contacted and intends to be on site on September 3, 2010 to repair the gauge." Texas Incident No. I - 8778. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-09-08
46227 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2010-09-02 22:50 | 2010-09-02 23:45 | 2010-09-03 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO HIGH WATER LEVEL IN THE RCIC INSTRUMENT SUMP "This is a one-hour report for the discovery of a condition that met an emergency action level (EAL) for a Notification of Unusual Event (NOUE). EAL HU1 - Natural and Destructive Phenomena Affecting the Protected Area Threshold Value 6 states: 'Exceeding Max Normal Operating Values specified in EOP 31EO-EOP-014-1(2) SC - Secondary Containment Control Table 5 Secondary Containment Operation Water Levels.' "On September 2, 2010 Plant Hatch Unit 2, as part of an on-going RCIC [Reactor Core Isolation Cooling] system outage, was restoring a tagout which un-isolated the CST [Condensate Storage Tank] from the RCIC system. The shift crew received several alarms in a short period of time for RCIC Northwest Diagonal Instrument Sump levels culminating with receiving the RCIC N-W DIAG INSTRSUMP LVL HIGH HIGH HIGH alarm at 2240. There was a report of water on the floor of the diagonal and 2E51-FV005 (a vent valve on the discharge of the barometric condensate pump) was identified as the source. The shift crew closed 2E51-F010 [suction isolation valve to the CST] to isolate the CST from the RCIC system. The Shift Manager declared an NOUE at 2250 for HU-1 Natural and Destructive Phenomena Affecting the Protected Area. At 2255 the Triple High alarm cleared." Plant personnel have visually confirmed that the sump level has been pumped down to normal level. The water level in the RCIC room did not rise to a level such that any equipment was adversely affected. Plant Hatch notified the following agencies: Georgia EMA, Appling County EMA, Jeff Davis County EMA, Tattnall County EMA, and Toombs County EMA. At the time of this notification, exit criteria for exiting the NOUE had been met and Hatch personnel were in the process of officially terminating the NOUE. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM BILL DUVALL TO DONALD NORWOOD AT 0022 EDT ON 9/3/2010 * * * The licensee officially terminated the NOUE at 0013 EDT on 9/3/2010. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-09-03
46226 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2010-09-02 18:00 | 2010-09-02 18:01 | 2010-09-02 | HURRICANE WITHIN 500 NAUTICAL MILES OF THE FACILITY "A hurricane is within 500 nautical miles from Indian Point Energy Center with wind speed in excess of 87 knots. The National Weather Service has issued a hurricane warning for a hurricane with wind in excess of 87 knots (approximately 100 mph) within 500 nautical miles of the facility. Per the Technical Requirement Manual a prompt report shall be made to the NRC Incident Response Center within 1 hour of receipt of that hurricane warning." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2010-09-02
46225 | 0 | IDAHO STATE UNIVERSITY |  |  |  |  | 2010-09-02 | 2010-09-02 15:45 | 2011-04-06 | MISPLACED BUTTON SOURCES On 9/2/2010, the licensee concluded that they were unable to account for two (2) Pu-239 solid sources that are about the size of a quarter each. Each source is estimated to weight about 1 gm with a source strength of 60 milliCuries and is in a non-dispersible form. The licensee noted that these sources were missing as a result of a normal inventory and leak test procedure on 8/19/10. Since that time the licensee has conducted an intensive search for the material both visually and using detection instrumentation but was unable to locate the material. The licensee discovered that the lost sources were last checked out of their storage location as part of a group of 10 such sources in April 2010. In July 2010 records indicate that only 8 of 10 sources were checked out since only 8 were available at the time. The licensee has restricted access to the sources and implemented additional controls for being able to check out the sources that include using a two man rule. * * * UPDATE AT 1727 EST ON 2/11/11 FROM BREY TO HUFFMAN * * * As of 2/11/11 at approximately 1710 EST, the licensee has formally declared the two plutonium button sources lost. The licensee stated that following extensive searching the sources are considered lost. The licensee notes that it has been in contact with responsible staff at NRC Region 4 and that the NRC had sent inspectors to the facility on October 4 and October 18, 2010. The licensee will continue to stress an awareness of the missing sources to personnel and emphasize continued vigilance for finding the sources. The licensee has not reached any conclusion as to what happened to the lost sources. R4DO (Clark), FSME (McConnell), and ILTAB (Hahn) notified. * * * UPDATE FROM RICHARD BREY TO JOE O'HARA AT 1705 EDT ON 4/6/11 * * * The two missing plutonium sources have been found inside a source vault mixed in with other radioactive materials in storage for decay purposes. Notified R4DO(O'Keefe), FSME(Michalak), and ILTAB(Johnson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-09-02
46224 | 0 | PROVIDENCE HOSPITAL |  |  |  |  | 2010-08-30 14:00 | 2010-09-02 13:30 | 2010-09-14 | MISPLACED PALLIATIVE SOURCE IMPLANTS On August 30, 2010, a patient was implanted with I-125 seeds in the anus for a palliative procedure. Two days later, September 1, 2010, a follow-up CT scan on the patient showed that the implants had been inserted 4 cm superior to the intended location which would lead to less dose at the target location. The intended dose was 90 Gy to the anus. More imaging studies are planned to estimate the actual dose to the intended target area. The patient will be implanted again after the imaging study is complete. A decision will be made at that time whether to correct the original implants. The reason for the error is believed to be twofold: The tumor had progressed markedly since the original planning and the decision was made to correct the plan for the additional growth based on palpation indications. Also, the 10 cm mark on the needle may have been mistaken for the 5 cm mark. No long term complications are anticipated. Both patient and physician have been informed. * * * UPDATE AT 1330 EDT ON 09/14/10 FROM VRINDA NARAYANA TO S. SANDIN * * * The licensee is updating this report to provide the results of the normal tissue doses from the permanent implants at the end of the treatment plan to the following organs: Bladder: Prescribed .07 Gy - Delivered 3.75 Gy Seminal Vesicles: Prescribed 5.38 Gy - Delivered 25.17 Gy Prostate: Prescribed 6.24 Gy - Delivered 4.2 Gy Rectum: Prescribed 45.18 Gy - Delivered 3.16 Gy The above information will be provided in the 15-day written report. Notified R3DO (Hills) and FSME (Burgess). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-09-08
46223 | -1 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-09-02 05:05 | 2010-09-02 11:10 | 2010-09-11 | SAFEGUARDS REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the Protected Area. Compensatory measures were taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM DALE WAY TO DONALD NORWOOD AT 1420 EDT ON 9/11/10 * * * After further review, the licensee has determined that this event should not have been reported as a 10CFR73.71 report. The licensee is retracting this event. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R3DO (Lipa), ILTAB (Johnson), and via E-mail the 73.71 Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-09-02
46222 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2010-09-01 16:00 | 2010-09-01 16:53 | 2010-09-01 | LOSS OF TEMPERATURE INSTRUMENTATION "On September 1, 2010 at 1600 hrs. [it was] identified that the 21 and 22 Hot Leg Remote Shutdown Temperature Instruments are inoperable. This constitutes a safety system functional failure which is reportable. The cause of the inoperability is under investigation. Per Technical Specification 3.3.4, these instruments must be restored to operable status within 30 days." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-09-01
46221 | 0 | PALISADES | 1 |  |  | [1] CE | 2010-08-23 22:10 | 2010-09-01 15:34 | 2010-09-01 | LOSS OF LOAD TRIP SIGNAL ON ALL FOUR CHANNELS OF REACTOR PROTECTION SYSTEM "On August 23, 2010, at approximately 2210 hours, with the Palisades unit at 100% power, the turbine protection relays, 305L and 305R, were identified as being inoperable due to a loss of electrical power from their 125 VDC power supply. On an actual turbine low auto stop oil pressure condition, 305L and 305R energize to generate a loss of load trip signal to all four channels of the Reactor Protection System (RPS). 305L provides input to RPS channels A and C. 305R provides input to RPS channels B and D. The RPS generates a reactor trip upon receipt of two (2) of four (4) loss of load trip signals. The loss of load trip is required by Technical Specification (TS) Limited Condition of Operation (LCO) 3.3.1 and was inoperable until 305L and 305R were reenergized on August 24, 2010, at approximately 0939 hours. "The on-shift operations crew entered a TS 3.3.1 LCO, however, TS 3.0.3 LCO should have also been entered. TS 3.0.3 LCO was applicable due to all four (4) loss of load input signals to the RPS being inoperable. The eight (8) hour notification was not reported within the required time frame due to a misinterpretation of the event that has since been re-evaluated and determined to meet the eight hour immediate notification requirement. "The safety significance of this event was minimal. Although required by TS, the loss of load trip function is not credited in the plant safety analysis. "The licensee has informed the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-09-01
46220 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2010-07-26 18:19 | 2010-09-01 13:42 | 2010-09-01 | 60-DAY TELEPHONIC NOTIFICATION IN LIEU OF A WRITTEN LICENSEE EVENT REPORT OF INVALID ACTUATION "On July 26, 2010, at 1819 hours [CDT], with Unit 1 in Mode 1 (Run), the Division 1 Diesel Generator Cooling Water Pump (DGCWP) restarted after being secured. The DGCWP provides the Emergency Service Water to the 1A Residual Heat Removal (RHR) pump room area cooler and the Reactor Core Isolation Cooling (RCIC) water pump/Low Pressure Core Spray [LPCS] pump room area cooler. "The apparent cause of the restart was the momentary interruption of the DGCWP run logic. The Division 1 DGCWP was in operation to support cooling of the Unit 1 RCIC/LPCS pump room area (run logic satisfied). When the Operator placed the Division 1 DGCWP control switch to the normal-after-stop position, the DGCWP feed breaker opened. The Operator reset the DGCWP feed breaker trip by returning the control switch to the normal-after-stop position and, because the run logic for the DGCWP was still satisfied [due to elevated room temperatures], the DGCWP restarted. "This invalid start signal from the Division 1 DGCWP breaker being reset resulted in the automatic actuation of the Division 1 DGCWP. The Division 1 DGCWP responded satisfactorily. "This report is being made in accordance with 10CFR50.73(a)(1), which states that in the case of an invalid actuation reported under 10CFR73(a)(2)(iv)(A), other than an actuation of the Reactor Protection System (RPS) when the reactor is critical, the licensee may provide a telephone notification to the NRC Operations Center with 60 days after discovery of the event instead of submitting a written LER." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-09-01
46219 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2010-09-01 11:00 | 2010-09-01 11:24 | 2010-09-30 | SAFEGUARDS REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the Protected Area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1259 ON 9/30/2010 FROM LLOYD ZERR TO ERIC SIMPSON * * * The licensee is retracting the Part 73.71(b)(1) portion of this notification. The NRC Resident Inspector has been notified. Contact the Headquarters Operation Officer for additional details. Notified R3DO (Orth), ILTAB (Allston) and 73.71 Group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2010-09-01
46218 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2010-08-31 11:12 | 2010-08-31 17:45 | 2010-08-31 | FITNESS FOR DUTY REPORT - DISCOVERY OF A POTENTIAL PROHIBITED SUBSTANCE IN THE PROTECTED AREA The licensee discovered a potential prohibited substance in the protected area. The substance has been removed from the facility. The licensee has notified the NRC Resident Inspector, the Illinois Emergency Management Agency and the DeWitt County Sheriff Office. Contact the Headquarters Operations Officer for additional details. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2010-08-31
46217 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-08-27 14:30 | 2010-08-31 16:48 | 2010-09-16 | AGREEMENT STATE REPORT - UNAUTHORIZED ACCESS TO RADIOACTIVE MATERIALS SUBJECT TO INCREASED CONTROLS At 1430 hrs. on 8/27/10 the Massachusetts Radiation Control Program (MRCP) was notified by Brigham and Women's Hospital of the discovery that a number of individuals not approved for unescorted access had in fact been given unescorted access to radioactive materials at the facility that are subject to NRC Security Orders for Increased Controls (i.e., Cat 1 and Cat 2 quantities of concern). 7 individuals (including 2 foreign nationals) were identified as having access to radioactive materials a total of 27 times over a 90-day period. The unescorted access was granted by individuals who had approved access by loaning access cards and PIN numbers to the individuals in question. The unauthorized access was to a self shielded irradiator device used for medical and research purposes. The foreign nationals involved in the access were a Japanese student and a Lebanese student, both having since returned to their countries. Upon discovery, local site security staff took immediate action to investigate the incidents using surveillance videos and other records. It does not appear at this time that any device tampering was involved. A material inventory has confirmed all material is accounted for. MRCP has formed an inspection team and has initiated an investigation that is expected to continue over the next week. In addition, MRCP will be meeting with individuals from the Boston Police Department, Boston-area FBI and MA State Police on Thursday, 9/2/10, at 0800 hrs. to discuss the event. * * * UPDATE AT 0839 EDT ON 9/1/10 FROM ROBERT GALLAGHAR TO ERIC SIMPSON * * * The self shielded irradiator is an AECL Model Gamma Cell 1000 with a 2,880 Ci Cs-137 source. Notified the R1DO (Conte), FSME (McIntosh), IRD (Grant) and ILTAB (Whitney). * * * UPDATE AT 1608 EDT ON 9/16/10 FROM ROBERT GALLAGHAR TO DONG PARK * * * At 1630 EDT on 9/15/10, the Massachusetts Radiation Control Program was informed by the Radiation Safety Officer at the Brigham and Women's Hospital that three additional unauthorized access events has occurred. Contact the Headquarters Operations Officer for additional details. Notified the R1DO (Dentel), FSME (Suber), IRD (Gott), R1IAT (Dimitriadis), and ILTAB (Hahn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 1 | 2010-09-03
46216 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-08-19 10:30 | 2010-08-31 12:59 | 2010-08-31 | CALIFORNIA AGREEMENT STATE REPORT - SOURCES DAMAGED BY FIRE The following information was obtained from the State of California via e-mail: "Six sources of Am-241 were involved in a fire. Three of the sources were not damaged. The other three are believed to be encased in melted/solidified masses of metal that had encased the sources. Each source was approximately 24 nanocuries. Initial surveys did not identify radiological contamination. Further analysis of the solidified metal believed to contain the three sources is planned. " The fire was initiated by the spontaneous combustion of charcoal fines used at the facility. There were no personnel injuries related to the fire event. Local media carried a story on the fire, but not the radiological component. The Am-241 sources are used as stabilizing sources in the air monitors. The sealed sources are not believed to have been breeched. The State and licensee will be performing follow-up investigations into the final disposition of the three sources encased in the solidified metal. California Report Number: 5010-081910. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-09-03
46215 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-08-26 15:30 | 2010-08-30 15:57 | 2010-08-30 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of California via email: "[On August 26, 2010] at 3:30 p.m., [the licensee Radiation Safety Officer (RSO)] received a call from a technician at the Caltrans Paso Robles Construction office, stating that a compaction gauge had been removed from his truck while parked at the construction laboratory. The gauge had been placed in the aluminum metal transportation box adhered to his truck, but unlocked and last seen at 12:30 p.m. [PDT]. He had gone back into the lab to continue work and went to the jobsite at 3:15 p.m. where he discovered the gauge missing. He called [the RSO] immediately and [the RSO] called the local police and filed a report. "The moisture/density gauge missing is a Troxler 3440, Serial No. 30701, containing 10 mCi of cesium 137 and 40 mCi of americium 241. The Paso Robles Police Report is case No. 1Q-2886. "[The RSO will be] placing an advertisement in Craigslist and in the local newspaper for the return of the gauge with a cash reward, no questions asked. [The RSO] will also speak personally to authorized gauge users about the importance of keeping the gauges locked up at all times, when not in use. A letter addressing the same will be sent to all." California Report Number: 5010-082710 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-09-02
46214 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-08-26 | 2010-08-30 13:24 | 2010-11-09 | OHIO AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the State of Ohio via e-mail: "Ohio Department of Health (ODH) was informed on 8/27/10 of an incident involving a portable moisture density gauge. The incident occurred on 8/26/10 at a work site in Lima, Ohio. The incident occurred due to operator error on behalf of a BBC&M Engineering, Inc. (BBCM) employee - the employee backed over the gauge with a BBCM truck. BBCM staff followed established company emergency procedures - the area was cordoned off, all other site personnel were kept more than 20 feet away from area, and a BBCM employee stayed in the area until further notice. "BBCM obtained a Radiation Alert Monitor and a lead 'pig' from CTS, Inc. and used the monitor at the project site in the area of the damaged gauge, truck, and original testing location of the gauge. The reading near the gauge (at 1 meter) was 2.0 mrem/hr. All other readings taken at the sire measured only background level readings. The gauge was damaged but the radiation sources were not comprised and/or leaking. As the source rod would not retract into the gauge, BBC&M installed a lead cap ('pig') over the rod tip/source end. The gauge was then transported to BBCM's Dublin, Ohio office to be stored until it can be transported to CTS, Inc. for further inspection." The gauge contains 0.010 Ci Cs-137 and 0.050 Ci Am/Be sources. Ohio incident #2010-051. * * * UPDATE FROM STEPHEN JAMES TO JOHN KNOKE AT 1212 EST ON 11/09/10 * * * "On 11/9/10 ODH inspected licensee and issued Notice of Violation for incident. Licensee has provided additional training for employees. Device was returned to manufacturer for repair." Source Number: 1 Source/Radioactive Material: SEALED SOURCE GAUGE Radionuclide or Voltage (kVp/MeV): CS-137 Activity: 0.010 Ci 0.37 GBq Source Number: 2 Source/Radioactive Material: SEALED SOURCE GAUGE Radionuclide or Voltage (kVp/MeV): AM-BE Activity: 0.050 Ci 18.5 GBq Device Number: 1 Device Name: PORTABLE GAUGE Manufacturer: TROXLER Model Number: 3430 Serial Number: 25983 Ohio Item Number: OH100011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-09-02
46213 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-08-03 | 2010-08-30 13:03 | 2010-08-30 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL FOUND IN SCRAP SHIPMENT "On August 3, 2010, the Department [Colorado Department of Public Health and Environment] received a phone call from the Utah Division of Radiation Control. A steel mill in Utah was returning a shipment of scrap metal to Colorado due to the portal monitor indicating radioactive material present in the shipment The shipment origin was Van Gundy Ampco at 1018 S. 5th Street, Grand Junction, Colorado (a scrap metal company, not a radioactive materials licensee). "On August 12, 2010, the DOT paperwork was faxed from Utah to the Department. The DOT special permit indicated the material was a railcar with a side which scanned at 22 [micro]R/hr (background = 0.005 mrem/hr). "On August 19, 2010, the railcar was returned to Van Gundy Ampco in Grand Junction. The Department made the determination using an IdentiFinder that the material was an oilfield pump contaminated with Ir-192 with a dose rate of 0.34 mrem/hr. The pump was isolated from public and workers with barrier tape. "On August 25, 2010, Protechnics (license CO-545-01) agreed to take possession of the pump to decay in storage. Protechnics is licensed for Ir-192, so no provisional license will need to be issued to Van Gundy Ampco or Protechnics. On August 27, 2010, Protechnics took possession of the oilfield pump. Personnel from Protechnics cleaned an oily residue out from the oilfield pump. The pump at this point scanned as indistinguishable from background and was released for unrestricted disposal. The oily rags and materials used to decontaminate the pump were taken to the Protechnics site in Fruita, Colorado for decay in storage. "The source of the Ir-192 is unknown as the oilfield pump was in a railcar full of scrap metal and the pump bore no identifying marks. Therefore, no Notice of Violation has been issued in regards to this incident. Additionally, the public dose in regards to this incident is also unknown as it is not known how long the pump was in public and the route the pump took from the oilfield to the scrap yard. "This incident is considered closed." Colorado Incident I10-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-09-02
46212 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-08-29 19:05 | 2010-08-29 19:58 | 2010-08-29 | UNUSUAL EVENT DECLARED DUE TO LOSS OF ANNUCIATORS IN THE CONTROL ROOM At 1905 EST, Vermont Yankee declared a Notice of an Unusual Event (NOUE) based on EAL SU 4.1, loss of 75% of the control room annunciators associated with safety related systems for greater than 15 minutes. Around 1845 EST, several annunciators were received and based on the failure mode, the licensee conservatively estimated that greater than 75% of the annunciators in the control room were inoperable. The licensee will notify the NRC Resident Inspector. * * * NOTIFIED BY BOB VITA TO BILL HUFFMAN AT 2037 EST ON 8/29/10 * * * The licensee determined that the cause of the annunciator loss was a blown fuse. The fuse was replaced and the annunciators were restored without further issues. Vermont Yankee exited the NOUE at 2028 EST. The licensee has notified State authorities and will notify NRC Resident Inspector. Notified R1DO (Henderson), NRR EO (Evans), IRD (Gott), DHS (Vestal), and FEMA (Visce). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | VT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-08-29
46211 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-08-28 17:00 | 2010-08-28 21:09 | 2010-08-28 | LOSS OF THE OPERATIONS SUPPORT CENTER DUE TO INOPERABLE EMERGENCY HVAC "During the performance of procedure 34S0-Z41-006-0 section 7.3.1.8, which tests the operability of the HP/CHEM area emergency HVAC, the system failed to indicate proper flow of the system. On panel 1Z41-N030, the system flow gauge failed upscale high and could not be lowered. The decision was made to halt the procedure at 1700 [EDT] on step 7.3.1.8 and restore the normal HP/CHEM HVAC lineup. "The HP/CHEM area emergency HVAC is required for functionality of the Operations Support Center (OSC), as this area may be used during declared emergencies. Alternate OSC facilities have been verified to be available. All efforts and resources have been made available to restore the HP/CHEM emergency HVAC to functional status. "This event is reportable per 10CFR50.72(b)(3)(xiii) and TRM 3.10.1.B.2" The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-28
46210 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-08-27 | 2010-08-27 17:33 | 2010-09-11 | AGREEMENT STATE REPORT INVOLVING ORPHANED / MISSING GENERAL LICENSE SOURCES The following information was received from the State of Pennsylvania via fax: "Event Report ID No: PA100020 "License No: PA-G0241, PA-G0029, PA-G0141 "Licensee(s): New Castle Rolling Mills, Sharon Strip Steel and/or Cedar Mills "Event date and time: Unknown "Event location: 902 North Cedar Street, New Castle, PA 16102 "Event type: Five (5) missing [licensed material] GL sources and shutter function failure "Notifications: July 2010 PA DEP Southwest Regional Office Inspection "Event Description: Since becoming an Agreement State in March 2008, DEP has transitioned hundreds of NRC specific and general licenses (GL) to PA state control. Recently, working from an NRC spreadsheet, DEP has been issuing GL certificates of registration for certain category GLs, and tracking unresponsive GL owners. The original information we had from the NRC indicated 11 sources had been distributed to the above location over time. The current facility owner is not a steel manufacturer, and was unaware these GL sources were on their property. "An inspection in July 2010 noted 6 of potentially 11 'C-frame' thickness gauge GL sources could be accounted for, with 4 onsite and 2 recently transferred back to a gauge manufacturer. Each of the 11 GL gauges contained a one (1) curie americium-241 sealed source. Since there is no NRC data on possible return or transfer of GL sources, and two manufacturers are no longer in business, the tracking of 5 GL sources appears to be impossible. The event location noted above has had three different owners / GL licensees over the years, two of which are known out of business. A third firm may still be in business, and will be pursued regarding the 5 unaccounted for sources. Lastly, 1 of the 4 GL sources was found to have an open shutter. All 4 'orphan' sources have been registered with the DOE/LANL OSRP [Off-Site Source Recovery Project] program for transfer. "Due to the unaccountability of the five 1 Ci Am-241 GL sources, DEP believes this to be reportable under 20.2201 (a)(1)(i). And, since one of the six sources that were accounted for had an open shutter, DEP finds this to be reportable under 30.50(b)(2)(i). "CAUSE OF THE EVENT: Improper transfer of GL sources and ineffective regulatory control. "ACTIONS: Two of the devices have been returned to a manufacturer. Four of the sources remain at the facility in New Castle, PA in a secured location. More investigation is being done to track the five unaccountable GL devices. "Media attention: None at this time" * * * UPDATE FROM DAVID ALLARD TO VINCE KLCO ON 9/11/2010 AT 2131* * * The following information was received by facsimile: "After a PaDEP [Pennsylvania Department] teleconference with the NRC on August 31,2010, it was determined that all gauges associated with this event are accounted for, and this update is needed to retract the notification of five (5) missing one (1) curie Am-241 GL sources. Apparently a duplication of data error occurred on the NRC's GL spreadsheet, resulting in the miscalculation of eleven (11) total gauges, when in fact only six (6) gauges were transferred to this site over the years. "Two (2) gauges have been returned to a manufacturer while four (4) gauges remain at the location, securely stored, awaiting disposal or transfer. These sources are registered with the DOE/LANL OSRP program, and will soon be registered on the CRCPD's 'source exchange' program for possible reuse or recycle. "However, due to the fact that one of the four GL sources was found to have an open shutter and this remains reportable under 10 CFR 30.50(b)(2)(i). The current property owner was instructed to contact a gauge service vendor to correct the open shutter, and inform the [Pennsylvania] Department when complete. "CAUSE OF THE EVENT: Improper tracking of GL sources, and failure to control the GL sources on the part of the licensees. "ACTIONS: Two of the devices have been returned to a manufacturer. Four of the sources remain at the facility in New Castle, PA in a secured location. "Media attention: None at this time" Notified R1DO(Cook) and FSME EO(Foster) Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-09-01
46209 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-08-27 07:40 | 2010-08-27 16:13 | 2010-08-27 | 24 HOUR FITNESS-FOR-DUTY REPORT "A supervisor had a positive for alcohol during a follow-up fitness-for duty test. The employee's access to the facility has been suspended. Contact the Headquarters Operation Officer for further details." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2010-08-27
46208 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-08-26 16:49 | 2010-08-26 22:22 | 2010-08-26 | BOTH TRAINS OF HIGH HEAD SAFETY INJECTION PUMPS DECLARED INOPERABLE "Beaver Valley Power Station Unit No.1, while operating at 100% full power, performed Ultrasonic Testing on the High-Head Emergency Core Cooling System Pump suction headers (6" and 8") following a fill and vent of the 'A' High Head Emergency Core Cooling System Pump. This is required because the fill point for the out of service Emergency Core Cooling System Pump 1CH-P-1A, is it's suction valve from the 8" Charging header, 1CH-19, which was opened. Preliminary indications were such that the 6" suction header was full of water and an air void did exist in the 8" suction header, but the size was indeterminate and had to be calculated by System Engineering. Operations commenced additional monitoring for cavitation of the running charging pump with none identified. Operations then vented the 8" suction header multiple times. At 1649 hours today, the results of the Ultrasonic Test (UT) was provided by System Engineering indicating that an air void existed in the Emergency Core Cooling System Pump 8" Suction header that was in excess of the Acceptance Criteria. At 1649 hours, both trains of High Head Safety Injection pumps were declared Inoperable but remain Available. Technical Specification (TS) 3.5.2 - ECCS operating is not met. Required Action C.1 requires entry of TS LCO 3.0.3 immediately. "Per 10CFR50.72(b)(3)(v)(A)&(D) - Event or Condition That Could Have Prevented Fulfillment of a Safety Function, and 10CFR50.72(b)(3)(ii)(B) Unanalyzed Condition, this event is reportable to the NRC within 8 hours. "At 1715 additional venting of the 6" Charging Pump suction header revealed no air present. Additional venting of the 8" Charging Pump suction header revealed additional air pockets. The 8" header was then vented multiple times, with a short delay in between each venting, until no air was identified. "At 1718, follow up UT on both Charging Pump Suction headers revealed it remained full of water with no voids present. Both trains of High Head Safety Injection are declared OPERABLE restoring compliance to TS LCO 3.0.3 and 3.5.2. Reactor power remained at 100% during these evolutions. "The NRC Resident Inspector was informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2010-08-26
46207 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-08-23 15:30 | 2010-08-25 12:56 | 2010-08-25 | AGREEMENT STATE REPORT- BASIS WEIGHT GAUGE ABB MODEL TG-1(U-7) SHUTTER FAILED TO CLOSE The following report was received via e-mail: "The Minnesota Department of Health was notified on 8/24/2010 by a representative from Boise Cascade that a Basis Weight Gauge located at the Off Machine Coater Reel had a shutter failure. The shutter is designed to close after going off sheet; however it remained in the open position. When power was cut to the device the device failed closed (shutter did close). "The gauge was taken out of service and repaired by ABB. The problem was determined to be shorted out wires in the device. The device has been repaired and placed back in service. The source is 250 mCuries Kr-85, serial number K-1988E. Event Report Number: MN100003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2010-08-30
46206 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-08-25 08:30 | 2010-08-25 10:38 | 2010-08-25 | OFFSITE NOTIFICATION - RELEASE OF HYDROGEN GAS IN EXCESS OF THE REPORTABLE QUANTITY OF TEN POUNDS "On August 25, 2010 [the licensee] made a notification to] the Massachusetts Department of Environmental Protection and the Plymouth Massachusetts Fire Department in accordance with 310CMR40.300, Massachusetts Contingency Plan Notification of Oil and Hazardous Material; Identification and Listing of Oil and Hazardous Material. [The licensee made the notification] due to a release of hydrogen gas to the environment exceeding the reportable quantity of ten pounds via the designed system release path. The release occurred when restoration of a system vacuum pump following planned maintenance resulted in higher than normal system makeup rates. Combustible gas sampling of equipment areas confirmed that the excess hydrogen gas had been released to the environment via a remote roof vent designed to continuously exhaust [hydrogen] removed from the seal oil system by the vacuum pump. The release of hydrogen gas was secured when the vacuum pump was removed from service. The estimated quantity of hydrogen gas released was approximately twenty pounds. This event posed no danger to the health and safety of plant personnel or members of the general public. "The NRC Senior Resident Inspector is on-site and has been notified." The licensee is investigating the cause of the excessive makeup rate. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-25
46205 | -1 | ARCELORMITTAL BURNS HARBOR |  |  |  |  | 2010-08-24 10:15 | 2010-08-25 09:50 | 2010-08-26 | LEVEL DETECTION GAUGE SHUTTER CONTROL ROD DISENGAGED "After completion of casting operations at our #1 Slab Caster, a trained worker proceeded to the mould strand area to remove the Berthold Co-60 rod source from the mould and place it in proper storage. The source is 3.97 mCi and is used to measure mould level of liquid steel. After properly securing the source into its shielded source holder, the trained worker began transporting the holder to the storage cabinet. During transport, the holder fell over and hit the ground. When it hit the ground, the steel 'D' arm (for lifting the holder) structure on the outside of the holder was bent. "Also, the device is designed such that the source insertion/removal rod is stored on the outside of the holder. It actually slides through openings on the 'D' arm and screws into the shutter door when in the closed position. After the fall, the threaded portion of the shutter door which receives the insertion rod broke. I immediately removed the rod and replaced it with a positive lock. "During this event, the source rod and its shielding were not compromised and there was no exposure to employees. Also, we are making immediate modifications to the transporting device to prevent this from recurring." The shutter was closed throughout this event. * * * UPDATE AT 1339 EDT ON 8/26/10 FROM CHRIS SARVANIDIS TO S. SANDIN * * * The licensee is retracting this report based on the following text provided by the ArcelorMittal Burns Harbor Radiation Safety Officer (RSO): "Further investigation has revealed new information which we feel warrants a retraction of the reported event as a non-reportable event. "Originally, we stated that the Co-60 source rod was removed from the mould and safely inside the holder (post-casting) when the holder fell over, however, it was actually not in the holder. The source rod had actually been properly installed in the mould (pre-casting), and the employee was actually returning the empty holder to the storage cabinet when the holder fell over. "I also have three very important attachments. One is our Steel Producing department's preliminary investigation report which reveals more accurate facts of the event. The second is a quote from Berthold's Source and Device Registry document which can be interpreted as indicating that the insertion rod screwing into the shutter 'door' is not part of a safety design function of the device (see attached photo). The photo shows a positive lock installed on a separate portion of the shutter 'door' which serves as the actual safety locking function. The insertion rod screwed into the shutter 'door' serves merely as a storage location for the insertion rod when the device is not in use. Therefore, the damaged (de-threaded) opening on the shutter 'door' which receives the insertion rod is strictly for insertion rod storage only. Also, the insertion rod and its threading were not damaged in this event. The insertion rod itself is still able to be installed into its stored position (without being screwed-in) and can be used in operations if necessary. Lastly, we would have redundancy of insertion rods if necessary. "Further, there was no loss of functionality to the source holder, Co-60 source rod, or shutter mechanism as a result of this event, and the shutter is still lockable. The device is fully functional and no safety features have been breached. Nonetheless, I have taken the device out of service and secured it in a location controlled by me as RSO. I've begun the process of having the manufacturer repair the device." The above information was discussed with the NRC Region III staff prior to submittal as a retraction. Notified R3DO (Lara) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-08-25
46204 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-08-25 08:45 | 2010-08-25 08:47 | 2010-08-25 | LOSS OF SEVERAL DISPLAY SYSTEMS DUE TO PLANNED COMPUTER MODIFICATIONS "At 0845 hours EDT, on August 25, 2010, the Emergency Response Facility Information System (ERFIS) computer system was removed from service to perform a planned modification of the ERFIS. This modification will remove obsolete software and hardware related to the Emergency Response Data System, which has been replaced by an upgraded system. The expected duration of ERFIS inoperability is approximately 3 hours. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above-described functions. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS Computer system is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remained available to assess plant conditions, make notifications, and accomplish required communications, as necessary. An additional message will be provided when the ERFIS is restored. It should also be noted that during the period of ERFIS inoperability, it is likely that the system could be restored within one hour to support Emergency Response Facility activation. This report is provided to conservatively cover the possibility that restoration within one hour may not be able to be accomplished if facility activation were to occur. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DON GRANT TO JOE O'HARA AT 1454 ON 8/25/10 * * * "At 1430, the ERFIS system was returned to service." The NRC Resident Inspector has been notified. Notified the R2DO(Franke) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-25
46203 | -1 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-24 11:40 | 2010-08-24 20:02 | 2011-10-19 | ESSENTIAL SERVICE WATER PLACED IN A LINE-UP THAT MAY HAVE PREVENTED ITS SAFETY FUNCTION "At 1140 [CDT] on August 24th, Unit 2 received Essential Service Water (SX) discharge header pressure low and SX strainer delta pressure high alarms indicative of high flow. At the time, a 2B SX ASME surveillance was in progress which involved field operations by Equipment Operators (EO's). At the time of the event, SX discharge header pressure dropped to 65 psig, less than the 89 psig necessary for operability. The Control Room responded by directing the EO's to restore SX discharge header pressure, which was promptly restored. "The 2B SX ASME surveillance sets initial conditions prior to data collection. The surveillance has the total SX flow be adjusted to 24000 gpm via the U2 Component Cooling Water (CC) heat exchanger outlet throttle valve, 2SX007. The subject flow was intended to be measured via an installed ultrasonic flow gauge 2FE-SX147. The EO's, instead used the U2 CC heat exchanger flow gauge 2FE-SX031. As a result, in an attempt to achieve 24000 gpm through the U2 CC heat exchanger, total SX flow exceeded the 24000 gpm since the U2 CC heat exchanger is but one of many loads the 2B SX pump is serving. "For the 5 minutes described above, the SX system was in a lineup that may have prevented it to fulfill its safety function and placed Unit 2 in a potentially unanalyzed condition. This condition is still being evaluated." Site Engineering has determined no runout conditions existed. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM JOE KLEVORN TO VINCE KLCO ON 10/19/2011 AT 1626 EDT* * * "The evaluation of the condition has been completed. Based on Essential Service Water (SX) system flow model runs performed, the conditions that existed at the time of the low SX header pressure would have resulted in low flow supplied to multiple safety related components. However, the safety function to provide necessary cooling to required safety-related safe shutdown equipment would have been met under design basis conditions with the auto-start of the 2A SX pump. Therefore, this did not result in a condition that could have prevented fulfillment of a safety function or in an unanalyzed condition that significantly degraded plant safety. Therefore, ENS notification 46203 is being retracted." The licensee notified the NRC Resident Inspector. Notified the R3DO (Daley). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-08-24
46202 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2010-08-24 09:22 | 2010-08-24 17:09 | 2010-08-24 | LOSS OF OFFSITE COMMUNICATIONS "At 0922 hours [CDT] on August 24, 2010, it was identified that offsite telecommunications capability was lost (including ENS, HPN, and ERDS) for Quad Cities Station when a fiber optic phone cable was cut during offsite work activities. "A commercial communication link with the NRC Operations Center was re-established at 1105 hours when site offsite telecommunications were re-routed through the Exelon network to an available commercial system. "A follow-up notification will be provided when normal offsite telecommunications have been reestablished. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a major loss of communications capability. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DAVE GEEVER TO JOE O'HARA AT 1925 EDT ON 8/24/10 * * * "ERDS has been restored as of 1815 CDT." Notified R3DO(Riemer) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-24
46201 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-08-24 08:14 | 2010-08-24 16:57 | 2010-08-24 | LOSS OF OFFSITE POWER TO EMERGENCY STATION SERVICE TRANSFORMER "During planned maintenance on the Startup Station Service Transformer (SSST), an undervoltage condition occurred on the 69 kV offsite power supply to the Emergency Station Service Transformer (ESST). At the time of this event, utility personnel were isolating 161 kV offsite power to the SSST from the grid. As a result, the offsite power voltage to the ESST lowered below the level where the essential 4160 VAC buses are automatically prevented from loading on the ESST. "From 0814 to 0816, BKR IFS and 1GS Auto Closure Not Permitted alarms were received when the system control operator was switching out the 161 kV line which supplies the SSST. ESST Secondary Winding voltage lowered to 4309 V and the 69 kV line voltage lowered to 69.4 kV. The nominal setpoint for the Closure not Permitted action is 4330 V. Actions were taken per the alarm response procedures. "The ESST was declared inoperable as the automatic closure of the supply breakers to the 4160 V essential buses was precluded. With the SSST already inoperable, LCO 3.8.1 Condition C (two offsite circuits inoperable) was entered for the ESST inoperability. Required action C.1 directs declaring required features inoperable when the redundant required features are inoperable within 12 hours of discovery; and required action C.2 directs restoring one offsite circuit to operable status within 24 hours. "At 0816, the system control operator placed the 69 kV capacitor bank in service, restoring the 69 kV line voltage to 71.5 kV and ESST Secondary Winding voltage to 4461 V. "At 0846, the ESST was declared Operable following restoration of supply voltage, and meeting acceptance criteria of SR 3.8.1.1, and exited the above LCO required actions for the ESST. The plant remains in LCO 3.8.1, Condition A for the SSST inoperability for planned maintenance. "This condition is being reported in accordance with 10CFR50.72(b)(3)(v) as a condition that could have prevented fulfillment of a safety function. Per the discussion in NUREG 1022, both offsite electrical power and onsite power are considered to be separate functions by GDC 17. Per the GDC, the offsite sources must be capable of automatically connecting to the essential buses within a few seconds. Due to the automatic transfer to the ESST being prevented, the auto transfer function described in the GDC was prevented. The lowest voltage recorded by the system control operator was 69.4 kV, corresponding to 4309 V on the essential 4160 V buses. The 69 kV line voltage was promptly restored, and the Closure not Permitted alarms cleared. The ESST could have been manually aligned to the essential buses during this event. " The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-08-24
46200 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-08-20 | 2010-08-23 16:21 | 2010-08-23 | AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE MODEL 3411B DAMAGED AT CONSTRUCTION SITE The following was received from the State of Iowa via e-mail: "The licensee reported [to the IDPH (Iowa Department of Public Health)] on Saturday, August 21, 2010 of an event that occurred the previous day. A Troxler, model 3411B moisture/density gauge was run over at a temporary job site in Camanche, Iowa by a large dump truck. The construction vehicle was backing up and the driver did not see the gauge or the gauge user. The licensee's RSO reported the following to IDPH on August 23, 2010. The source rod was severed from the handle at the upper weld. The index rod was bent, and two of the faceplate screws were bent. The source rod was lifted up by hand and brought back into the gauge (safe position, with the exception that the source rod could pull completely out the top of the gauge). The bottom shutter closed as usual. No physical damage to the source rod was evident on the bottom half of the source rod. A leak test was completed on the gauge and the swabs were overnighted to Qal-Tek Associates (3998 Commerce Cr. Idaho Falls, Idaho 83401) on Friday night. Once the results are known, delivery of the gauge will be made to Qal-Tek to repair the gauge or dispose of as required. Direction will be given to us [IDPH] from Qal-Tek based on the leak test results. They are a certified disposal site. A survey was conducted on the soil surrounding the site of the accident. Based on a background radiation check 200' away from the site, no change in reading was observed at the actual accident site. The survey meter was also used to check the gauge itself compared to another gauge with a current leak test that had passed, and no change in reading was observed. The gauge is stored in a metal storage container on the jobsite in Camanche, Iowa. The windows are barred shut. The gauge is locked in its case to the inside of the storage container, and the container is locked shut at all times. Only the authorized user has access to this container. The gauge's source rod is duct taped to the index rod, and will have a ubolt binding the source rod to the index rod to prevent movement of the source rod from the gauge." The Troxler gauge contained .009 Curies Cs-137 and .044 Curies Am-241/Be. Item Number: IA100003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-08-26
46199 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-08-23 09:00 | 2010-08-23 14:06 | 2010-08-23 | LOSS OF ERDS CAPABILITY "This report is being made per 10 CFR 50.72(b)(3)(xiii) regarding a loss of offsite communication capability in that Oyster Creek Nuclear Generating Station would not have been able to establish a connection with the NRC Emergency Response Data System (ERDS) within one hour if the need had arisen. This condition was discovered at 0900 hours on August 23, 2010, and existed from approximately 1900 hours on August 20 until 1123 hours on August 23, 2010. "Oyster Creek Nuclear Generating Station switched the plant telephone system from a digital system to a Voice Over IP system at approximately 1900 hours on August 20, 2010. This change resulted in eliminating the requirement to dial the number '9' prior to dialing an outside line. The plant process computer (PPC) modem function program contained the NRC modem number preceded by the number '9' and when the changeover occurred the '9' was not deleted in the PPC program. This would have resulted in an error message if an attempt to connect with the NRC had been made. Information Technology (IT) estimates that it would have taken two hours to reprogram and establish the ERDS connection to the NRC. The ERDS data on the PPC was available but would have to have been transmitted to the NRC by an alternate method. 10 CFR 50.72(a)(4) requires one hour to activate the ERDS after declaring an emergency class of alert, site area, or general emergency. "This situation was recognized at 0900 hours on August 23, 2010 by IT personnel. The ERDS connection capability was restored to fully functional status at 1123 hours on August 23, 2010." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-23
46198 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-08-23 08:14 | 2010-08-23 12:33 | 2010-08-23 | TECH SPEC REQUIRED SHUTDOWN DUE TO BOTH EDGS AND AN RHR LOOP INOPERABLE "On 8/23/2010 at 0814 [hrs. CDT] with the unit in Mode 1, 100%, Control Room personnel were informed by a Maintenance Planner that each (A and B) Emergency Diesel Generator [EDG] was missing a u-bolt on the relief valve tail pipes on Auxiliary Lube Oil Keep Warm system. The System Engineer concluded that this could affect the seismic qualification of the EDGs. Both EDGs were declared inoperable as a result. In addition, 'A' Residual Heat Removal (RHR) was out of service for emergent work. This resulted in less than 100% of the ECCS flow equivalent to a single ECCS train and entry into LCO 3.0.3 as required by TS 3.5.2, Condition C. A plant shutdown was commenced at 0907. "At 0935, the Control Room was informed by Engineering that a calculation existed for continued operation of the EDGs with the u-bolt missing from the tailpipe of the relief valves on the Auxiliary Lube Oil Keep Warm system. Both EDGs were declared operable and LCO 3.0.3 was exited. The power reduction was stopped at 0940 with reactor power at 96%. "The NRC Senior Resident Inspector was informed." | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-08-23
46197 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2010-08-23 03:30 | 2010-08-23 04:42 | 2010-08-23 | SHUTDOWN DUE TO PLANNED EMERGENCY DIESEL GENERATOR OUTAGE EXCEEDING ALLOWED TIME "This is a 4 hour non-emergency 10 CFR 50.72(b)(2)(i) notification due to a Technical Specification required shutdown. 2EDG-2 (Unit 2 Emergency Diesel Generator #2) is currently inoperable due to a planned outage which has exceeded the allowed 14 day time clock IAW [in accordance with] TS 3.8.1.1. This requires that Unit 2 be in at least Hot Standby within the next 6 hours and in Cold Shutdown within the following 30 hours. Unit 2 is currently at 68% power and shutting down to comply with Technical Specifications." The licensee notified the Arkansas Department of Health and the NRC Resident Inspector. | 0 | 68 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-08-23
46196 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-08-21 17:00 | 2010-08-22 00:15 | 2010-11-24 | ONE TRAIN ECCS DECLARED INOPERABLE DUE TO VOID IN "A" RHR HEAT EXCHANGER "On 8/21/10 at 1700 [CDT] with the Unit in Mode 1, 100% power, Engineering personnel provided information to the Control Room that a known void in the 'A' Residual Heat Removal (RHR) heat exchanger could move from the heat exchanger to other locations in the Emergency Core Cooling System (ECCS). The analysis provided by a vendor indicates that during a specific RCS leak scenario with a failure of the A' RHR Pump, our [Unit 1] piping configuration could potentially allow the void to be swept from the 'A' RHR heat exchanger and be transported to the 'A' Centrifugal Charging Pump (CCP) and 'A' Safety Injection Pump (SIP) while in the cold leg recirculation mode of operation. This condition results in one train of ECCS being inoperable. The ECCS safety function is maintained due to redundant and interconnecting piping, in both injection and recirculation phases of operation. "The NRC Resident has been informed." The licensee declared one train of ECCS inoperable placing Unit 1 in the 72-hour Technical Specification [TS] 3.5.2, Condition A, Action A.1. Corrective actions are on going to remove the void and exit the TS Action Statement. * * * RETRACTION FROM RICK HUBBARD TO JOHN SHOEMAKER ON 11/24/10 AT 12:24 EST * * * "Additional information has been obtained by Engineering. The largest void identified in the 'A' RHR heat exchanger would not prevent the RHR system from performing its safety function. Hydraulic analysis models of this void moving through the system have shown that no pressure pulses will occur that could challenge the structural integrity of the system. The model results also show that ingestion of the void by the higher head ECCS pumps during the ECCS recirculation mode has no adverse affect on the ECCS high head pumps and they would remain capable of performing their safety function. "As a result, this event is not reportable per 50.72(b)(3)(ii)(B). This event is being retracted." The licensee notified the NRC Resident Inspector. R4DO (Lantz) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-08-22
46195 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-21 15:09 | 2010-08-21 15:47 | 2010-08-21 | NOTIFICATION OF STATE AGENCIES DUE LEAK OF A WATER TREATMENT CHEMICAL "At 1509 on 08/21/2010, a notification to outside state agencies, Tennessee Department of Environment and Conservation (TDEC) and Tennessee Emergency Management Agency (TEMA), was made due to a Towerbrom 960 [a microbiocide] chemical leak that developed at the Essential Raw Cooling Water (ERCW) intake station. The leak occurred during scheduled chemical treatment of the ERCW system. The leak was identified at 1850 EDT on 08/20/2010 and terminated at 1955 EDT on 08/20/2010. Chemically treated ERCW containing 55 ppm total residual chlorine reached the waters of the US which is above the 0.1 ppm allowed by the plant's National Pollutant Discharge Elimination System (NPDES) permit. There have been no observable adverse effects to the environment at this time. This occurrence does not affect safety related or other plant equipment." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-21
46194 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2010-08-21 11:00 | 2010-08-21 11:41 | 2011-10-14 | FLOOD BARRIERS NEEDED TO PROTECT SAFETY RELATED EQUIPMENT MISSING "On August 21, 2010 an inspection of the Air Intake Tunnel (AIT) sump identified missing flood barriers needed to protect safety related equipment in the plant. If enough flood water had entered into the AIT, water could have entered into the Auxiliary Building (AB) through the ventilation ductwork that connects the AIT and the AB. If flood water continued to enter the AB, then safety related equipment in the AB could have been affected. "This condition could have resulted in the unavailability of equipment in the Auxiliary Building including the 1A and 1B Decay Heat pumps, the 1A and 1B Building Spray pumps and 1A, 1B and 1C Make-up Pumps. This is reportable as an 8 hour ENS notification under 10CFR50.72(b)(3)(v)(B) and 10CFR50.72(a)(1)(ii) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. "Flood protection barriers have been established for the affected penetrations. Inspections of the flood protection barriers are ongoing. Further engineering review is being performed to determine the impact of the potential water intrusion into the AIT and AB." The licensee notified the NRC Resident Inspector. The licensee will notify the Pennsylvania Bureau of Radiation Protection. * * * RETRACTION FROM MICHAEL FITZWATER TO JOHN SHOEMAKER AT 1437 EDT ON 10/19/10 * * * "EN# 46194 made on August 21, 2010 at 1100 EDT is being retracted. Upon further Engineering review it was determined that the external flood barrier design deficiency in the Air Intake Tunnel (AIT) did not result in a condition that could have prevented the fulfillment of the safety function needed to remove residual heat. The AIT sump pump is in the cavity that had the degraded barrier where the in leakage of concern enters through conduits from yard electrical vaults. This pump starts automatically and has capacity in excess of the in leakage during the Probable Maximum Flood (PMF). The AIT sump pump's functional capability was confirmed to be available over the past three years. Therefore the ability to prevent flood water from the AIT reaching and impacting safety related equipment needed to remove residual heat was maintained. The event is therefore NOT reportable." The Licensee has notified the Resident Inspector. Notified R1DO. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-08-21
46193 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-08-16 | 2010-08-20 21:00 | 2010-08-20 | CALIFORNIA AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the State of California via email: "On 08/20/10, the ARSO at Stanford University called and informed RHB [California Department of Public Health - Radiologic Health Branch] of the following: "On 8/16/10, it was discovered that one of our Contractors, Vance Brown, lost control of 28 signs they removed from two buildings (Building 05-600 Moore South (row 475) and Building 05-610 Moore North (row 493). The signs were placed into a plastic bin and Vance Brown cannot determine what happened to them. "Representatives from Vance Brown and Redwood City Electric, the electrical subcontractor who removed the signs, conducted an investigation to determine the fate of the signs. They determined that while the signs had been removed and stored properly awaiting disposal by EH&S [Stanford University Environmental Health and Safety], they vanished from the secured construction site at an undetermined time between 6/28/2010 and 8/16/10. "EH&S met with representatives from Vance Brown and Redwood City Electric on 8/19/10. Several avenues were explored during the meeting. Vance Brown explained that the site was broken into on 7/29/2010 and several tools and other valuables were stolen. Vance Brown filed a police report, but did not notice the signs missing at that time. Vance Brown and Redwood City Electric also questioned their employees, reviewed truck logs, and looked through both construction site storage containers and their off-site warehouses. "Stanford EH&S has also conducted an internal investigation to determine if any Stanford employees had picked up the signs. None had. Stanford EH&S also queried the waste hauler used by Redwood City Electric (Quick Light Recycle) who stated they had not picked up the signs. "At this time Vance Brown and Stanford EH&S has exhausted potential locations for the plastic bin of 28 tritium exit signs and considers them to be lost and/or missing. " California Report No.: 5010-082010 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-08-25
46192 | 0 | JANX INTEGRITY GROUP |  |  |  |  | 2010-08-20 13:00 | 2010-08-20 18:24 | 2010-08-20 | DAMAGED RADIOGRAPHY CAMERA GUIDE TUBE PREVENTING SOURCE RETRACTION JANX crew was working on a piping fabrication. A piece of 2 inch pipe fell while making an exposure. It is believed that the falling pipe struck the guide tube. The radiographer then attempted to retrieve the source. The source partially retracted and then became stuck. The area was then cordoned off. The area is being well controlled. JANX's customer is Dominion Gas Transmission. There are no residential units close to this area. Source Production & Equipment Co. Inc. (SPEC) has been contacted. SPEC is dispatching personnel to effect source retrieval. No overexposures resulted from this event. The radiography camera is a SPEC model 150 containing 90 curies IR-192. GPS coordinates of event location: 39.10699 N 80.49879 W Notified R1DO (White) and FSME EO (Delligatti). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-08-20
46191 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-08-20 15:25 | 2010-08-20 17:47 | 2010-08-20 | AUTOMATIC REACTOR TRIP DUE TO AN INADVERTENT TURBINE TRIP SIGNAL DURING TESTING " At 1525 [hrs. CDT] on 08/20/10, Unit 1 experienced an automatic reactor trip while the plant was stable at 100% power in Mode 1. All systems actuated as designed. The reactor trip was caused by an inadvertent turbine trip signal initiated during testing. "All ESF [Engineered Safety Features] systems actuated as designed. The following systems actuated: Auxiliary Feed Water and Feed Water Isolation." All control and shutdown rods fully inserted. The plant is currently stable at normal operating pressure and temperature with decay heat being removed via steam dumps to the condenser. No primary or secondary relief valves lifted during the transient. The plant is in its normal shutdown electrical lineup with no problems noted. The trip was uncomplicated. The turbine trip signal was generated by a human performance error during reactor trip breaker testing. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-08-20
46190 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-19 17:45 | 2010-08-19 21:45 | 2010-08-20 | SAFEGUARDS REPORT - SAFEGUARDS INFORMATION IMPROPERLY CONTROLLED The licensee discovered improperly controlled safeguards information. Compensatory measures have been taken. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM ROBERT ZIMKOWSKI TO DONALD NORWOOD AT 1508 EDT ON 8/20/2010 * * * The licensee has determined that there was no compromise of safeguards information. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R4DO (Miller) and via E-mail the 73.71 Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-08-19
46189 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2010-08-18 | 2010-08-19 16:56 | 2010-08-19 | ILLINOIS AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING YTTRIUM-90 UNDER DOSE The following information was obtained from the State of Illinois via email: "On the afternoon of August 18, [REDACTED], the licensee's Radiation Safety Officer [RSO] called the Agency [Illinois Emergency Management Agency] to report a medical event in accordance with 32 Ill. Adm. Code 336.1080. The licensee was conducting a treatment involving the use of colloidal Y-90 'SIR-Spheres' under consultation with the manufacturer's representative. A dose of 15.4 milliCi was prescribed by the authorized user and the entire volume of material appeared to be delivered without any unexpected complications, including a complete repeated flushing of the delivery line. However, measurements of the associated tubing, vial and other contaminated items in accordance with accepted procedures showed a notable quantity of Y-90 remained. It was subsequently determined that the dose received was less than 80% of the intended dose. [The RSO] contacted the Agency within the prescribed notification period after verifying the measurements and calculations. The Medical Center also notified the attending physician and the patient the same day. Estimates are that 72% [11.1 milliCi] of the intended dose was delivered. "[The RSO] was advised of the regulatory reporting requirements and was beginning preparations for providing that information. Initially, it is believed that the underdose will not have any adverse effect on the patient. The prescribed treatment was intended as a palliative measure for liver tumors secondary to colon cancer. [The RSO] was asked to obtain the opinion of the manufacturer's rep as to the cause of the underdose and any recommended corrective actions the manufacturer suggests in these treatments. [The RSO] was also requested to provide the initial corrective action the hospital intends to take for this and subsequent treatments. "A separate conversation was held with the authorized physician user [REDACTED] who attended and oversaw the patient treatment. [The physician] advised that there were no spills, leaks, adverse patient reactions or shunting of the dose outside of the hepatic artery that led to the underdose. Comments from all involved at the time of the treatment, including the manufacturer's representative, was that the administration of the palliative treatment was as good as could be expected and there were no visual indications that any anomalies were present in delivery of the dose. Patient will undergo PET and CT scans in 6 weeks and 12 weeks respectively to determine if any additional actions are warranted such as making up the difference in dose, conducting a repeat of the treatment or if taking no action at all is appropriate. The overriding issue will be the patient's general quality of life. At this point, preliminary indications are that no changes in procedures or processes are necessary and that general delivery system design, coupled with characteristics of material to be administered, resulted in the unintended coagulation and accumulation of microspheres either within the Sir-Sphere three way stopcock or the microcatheter despite routine agitation of the suspension delivery vial." Illinois Case Number: IL10055 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2010-08-25
46188 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-08-18 07:42 | 2010-08-18 16:30 | 2010-08-19 | LOSS OF SEVERAL PUBLIC WARNING SYSTEM SIRENS "On August 18, 2010, at approximately 0742 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department discovered that public warning system sirens Nos. 17, 23, and 34 were not responding, and therefore, were out of service. The loss of these sirens could potentially impact a population of approximately 1800 people in the 5-mile emergency planning zone (EPZ). Since the loss of these sirens could impair Arizona Public Service Company's ability to inform greater than 5% of the population within the EPZ, this notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). If an event occurs while the sirens are out of service, the Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area. The MCSO is prepared to implement this contingency should it become necessary. Troubleshooting to determine the cause of the failure has commenced. "The NRC Resident Inspector has been notified of the out of service sirens and this ENS call. "[At the time of the notification to the NRC], siren #23 was restored at 1316 MST. The out of service sirens are now Nos. 17 and 34 with an affected population of 1196 within the 5 mile EPZ." * * * UPDATE FROM ELKINTON TO HUFFMAN AT 1104 EDT ON 8/19/10 * * * The licensee restored siren #17 at 1647 MST on 8/18/10. The restoration of this siren provided coverage to all the population within the 5-mile EPZ. The licensee has notified the NRC Resident Inspector and will also notify State and local authorities. R4DO (Miller) notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-18
46187 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-08-16 20:00 | 2010-08-18 15:08 | 2010-08-18 | AGREEMENT STATE REPORT - DAMAGED CO-60 CASTER GAUGE Received the following report from the State of Ohio via email: "At approximately 2000 [CDT] on 8/16/2010 a molten metal overflow event occurred at Charter Steel. Molten metal flowed down a tube outside the crucible where the caster gauge is located. The caster gauge, a Berthold LB300MLT containing 5 mCi of Co-60, was covered in molten metal as a result. On the morning of 8/17/2010 the licensee's environmental contractor was called to help assess the situation. Radiological surveys were conducted and no contamination was found. The gauge manufacturer recommended that the licensee contact Radiametrics (Ohio license # 03225480000) to recover the gauge. Radiametrics responded on the afternoon of 8/17/2010. Ohio Department of Health dispatched an inspector to investigate the incident and observed as Radiametrics removed the gauge from the now solidified block of steel. The gauge was found intact and the shutter was found in the closed position. Radiation surveys indicated that the source was intact and was not leaking. At approximately 1400 on 8/17/2010 the gauge was placed in secure storage at Charter Steel. The licensee has contracted with Radiametrics to transfer the source to a new Berthold gauge when it arrives in the next few days." Ohio Incident # OH100010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-08-23
46186 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-08-18 13:00 | 2010-08-18 14:27 | 2010-08-25 | NON-BADGED CONSTRUCTION CONTRACTOR TAMPERED WITH THE VEHICLE BARRIER SYSTEM "Non-badged construction contractor tampered with the vehicle barrier system (VBS) without authorization. The VBS is located outside the protected area. He tried to lift the VBS arm with a skid loader. Contractor was escorted from the work site. Event reported per 73.71(b)(1), Appendix G(I)(a)(3). "NRC Resident has been informed." Individual was an equipment operator. When questioned, the individual said his actions were not intentional. However, site security had observed the action as it occurred and felt that the action was intentional. No permanent damage was done to the VBS. * * * RETRACTION FROM DARREN KARNES TO HOWIE CROUCH @ 1557 EDT ON 8/25/10 * * * Based on subsequent investigation, the licensee has retracted this event. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-08-18
46185 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2010-07-09 | 2010-08-18 13:01 | 2010-08-18 | AGREEMENT STATE REPORT - TRITIUM EXIT SIGN WITH BROKEN TUBES DISCOVERED Received the following report from the State of Utah via facsimile: "On July 9, 2010, while working under reciprocity to package and ship 70 H-3 [Tritium] exit signs for Canyons School District, Philotechnics, Ltd. discovered a Tritium exit sign with broken tubes. The broken sign was manufactured in November, 1992 by Safety Sign Technologies and contained 20 Ci of H-3 ( Model #13200, S/N 550047). It is unknown when or how the sign was broken. At the time of discovery, Philotechnics, Ltd. was not equipped to conduct surveys or decontamination procedures, so the sign was placed in a secure area. The school district has appropriate control over the broken sign and is seeking contract for decontamination." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2010-08-23
46184 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2010-08-17 14:14 | 2010-08-17 16:54 | 2010-08-17 | MANUAL REACTOR SCRAM INITIATED DUE TO RECIRCULATION PUMP TRIP "On August 17, 2010, at 1414 hours, a manual scram was inserted on Unit 2 due to rising reactor water level. The water level increase was caused by a trip of the 2B Recirculation Pump. Restoration of the 2B Recirculation Pump Programmable Logic Controller (PLC) on the 2B Adjustable Speed Drive (ASD) was in progress at the time of the event. Following the reactor scram, reactor water level decreased to approximately minus 15 inches, which resulted in automatic Group II and III isolations as expected. All systems responded properly to the event. The cause of the event is still under investigation. "Unit I was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." All control rods inserted on the scram. No ECCS initiations occurred. No safety or relief valves lifted. The unit is stable in Mode 3 at 926 psig and 530 degrees Fahrenheit. Pressure is being controlled on the turbine bypass system. The licensee notified the NRC Resident Inspector and the Illinois Department of Nuclear Safety. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2010-08-17
46183 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-17 07:35 | 2010-08-17 16:32 | 2010-08-17 | EMPTY BEER CAN FOUND INSIDE THE PROTECTED AREA "On August 17, 2010, an empty beer can was discovered in a recycle container inside the Protected Area (PA). The can has been removed from the PA. Further investigation as to how the can was introduced into the PA is in progress. No personnel fitness-for-duty issues related to the consumption of alcohol have been identified. The presence of alcohol with the PA is being reported in accordance with 10CFR26.719(b)(1)." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2010-08-17
46182 | -1 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2010-08-17 03:00 | 2010-08-17 13:56 | 2010-09-14 | UNANALYZED CONDITION DUE TO POTENTIAL WIRING DISCREPANCY "On August 16, 2010, at about 0100 PDT, SONGS Unit 2 Train 'A' Emergency Diesel Generator (EDG) 2G002 was removed from service for planned maintenance. Train 'A' EDG is the Appendix R protected Train. "At about 1545 the same day, Southern California Edison (SCE) discovered a potential wiring discrepancy in the electronic governor. At 0300 on August 17, 2010, SCE determined two wires on a fire isolation fuse were confirmed to be terminated differently than specified in plant drawings and that the discrepancy would prevent the fuse and associated fire isolation switch from performing its Appendix R fire isolation function for the Train 'A' EDG. In accordance with NUREG-1022, Rev. 2, SCE is reporting this occurrence in accordance 10CFR50.72(b)(3)(ii)(B). "While the incorrect wiring impacted the Appendix R qualifications of the Train 'A' EDG, it did not impact its other design functions and the EDG was capable to fulfill its safety function for all other Design Basis Events. Therefore, SCE considers the safety significance of the condition to be minimal. "In accordance with LCS specification 3.7.113.1 Condition A, SCE will implement hourly Fire Watches for the impacted plant areas until such time that the wiring on the Unit 3 Train 'A' Emergency Diesel Generator 3G002 is conformed to be correct or has taken actions to correct any wiring discrepancy. An evaluation will be conducted to determine the cause of this condition. "At the time of this occurrence, Unit 2 and Unit 3 were both at 100% power." "The NRC Resident Inspector will be notified of this occurrence and will be provided with a copy of this report." * * * RETRACTION FROM KELMENSON TO KLCO ON 9/14/10 @ 1528 [EDT]* * * The licensee is retracting the event based on the following: "Upon further investigation, SCE determined the suspected wiring discrepancy was only an issue with an elementary diagram that was used for circuit verification. SCE had already flagged this elementary diagram as requiring revision and a change to the diagram was pending and had not been released to the field. The fire isolation fuse was wired correctly." "Consequently, SCE is retracting the 8-Hour Telephone Notification made to the NRC on August 17, 2010 (Event Log No. 46182)." "The NRC Resident Inspector will be notified of and will be provided with a copy of this retraction." Notified the R4DO (Clark) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-08-17
46181 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-07-30 | 2010-08-17 13:53 | 2010-09-03 | AGREEMENT STATE REPORT - RADIOGRAPHER'S BADGE HAD READING OF 37 REM On August 17, 2010, at 1115 hours, the Agency (State of Texas) was notified by the licensee that their dosimetry processor had notified them that a radiographer's badge was reading 37.060 rem for the month of July, 2010. The Radiation Safety Officer (RSO) stated that he had reviewed the daily dose records for the radiographer and the radiographer's recorded total exposure was less than 50 millirem for the exposure period. Also, the radiographer's coworker's badge reading was normal for the same period. The RSO stated that he believed that it was a badge only exposure. He stated that the radiographer works the afternoon shift, so he has not had a chance to interview him. The RSO stated that the radiographer has been removed from all activities which would expose him to any additional radiation exposure. The RSO stated that he was not aware of any single event which would have caused this type of exposure. The RSO stated that he interacts with the radiographer on a daily basis and has not noted any indications of an exposure of this magnitude. The RSO stated that medical exams would be considered if they could not prove that the exposure was to the badge only. Additional information will be provided as it is received in accordance with SA-300. Texas Incident # I-8773 * * * UPDATE FROM ART TUCKER TO JOHN KNOKE AT 1655 EDT ON 8/18/10 * * * Received the following report from the State of Texas via email: "On August 18, 2010 at 1045 hours, the Agency [State of Texas] was contacted by the licensee's Radiation Safety Officer (RSO) and informed that they had conducted an interview with the radiographer receiving the over exposure. The radiographer stated that he did not remember ever dropping his TLD. He could not think of any reason why he would have received so much exposure. The RSO stated that the radiographer had performed all of his work within the shooting bays at their facilities. The licensee sent the radiographer to a medical facility for blood work. The RSO stated that the results of the blood work were normal. The RSO stated that the radiographers badge may have been intentionally exposed by another individual. He stated that they have security cameras and would review the tapes for any activities that could explain the exposure. The RSO stated that they had implemented new controls on their workers TLD's. Shift managers will control access to the badges when the workers are not wearing them. The RSO stated that the dosimetry processor could not determine if the dose recorded by the badge was while the badge was moving or stationary." Notified R4DO (Geoffrey Miller), FSME (Mark Delligatti) * * * UPDATE FROM ART TUCKER TO ERIC SIMPSON AT 1030 EDT ON 9/3/2010 * * * The following report was received from the State of Texas via e-mail: "The [State of Texas] was contacted by the licensee and informed the Radiation Emergency Assistance Center/Training Site has sent the licensee notification that based on their evaluation of the samples submitted to them by the licensee, no overexposure had occurred." Notified R4DO (Deese) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-08-20
46180 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-08-07 | 2010-08-17 09:45 | 2010-08-17 | AGREEMENT STATE - POSSIBLE EXPOSURES OF MEMBERS OF GENERAL PUBLIC FROM A THYROID ABLATION PATIENT A representative of the Iowa Bureau of Radiological Health reported a possible exposure event involving members of a medical center staff and perhaps others who were exposed to a patient that had recently been given a thyroid ablation treatment. The patient had been administered a dose of 150 millicuries of I-131 to ablate the thyroid on 8/6/10. The patient was then released and cautioned on avoiding contact with other people. On 8/7/10, the patient experienced an medical condition that resulted in an incoherent condition and was rushed to a medical center for treatment of that condition. The medical center was unaware of the patient's recent I-131 thyroid ablation treatment. The Radiology Group that administered the thyroid ablation subsequently became aware of the patient's admittance to the medical center. The Radiology Group is working with the medical center and also contacted the State of Iowa with the concerns about exposure that general members of the public may have received from the thyroid patient. The State does not know details on the radiation levels that were present near the thyroid patient at the time of this event. The State is investigating the details of the event and possible exposures. The State is uncertain if the event is reportable under the State equivalent of 10 CFR 35.75 assuming that the patient met the release criteria after the thyroid treatment at the Radiology Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-08-23
46179 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-08-16 13:40 | 2010-08-16 18:02 | 2010-08-16 | NPDES LIMIT WAS EXCEEDED FOR RIVER TEMPERATURE DISCHARGE REQUIREMENTS "Browns Ferry Nuclear Plant inadvertently exceeded a limitation of its National Pollutant Discharge Elimination System (NPDES) Permit for Tennessee River temperature conditions which was reported to the Alabama Department of Environmental Management (ADEM) at 1340 Central Daylight Time, on August 16, 2010. As such, this is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' "The NPDES Permit requires that when the 24 hour ambient average river temperature exceeded 90 degrees Fahrenheit, the 24 hour average downstream river temperature may equal but not exceed the upstream value. The 24 hour average upstream temperature was found to be 90.4 (rounded to 90) degrees Fahrenheit and the downstream temperature was found to be 90.6 (rounded to 91) degrees Fahrenheit. "Browns Ferry had been maintaining compliance with the NPDES permit. The departure is thought to be due to a summer storm cooling off the upstream temperature. With the time delay between upstream temperature changes and the ensuing rate at which the downstream temperature changes are observed, the resultant 24 hour average downstream river temperature exceeded the upstream value. Duration of this condition was found to be only several hours. "The three Browns Ferry units, which had already been derated to approximately 50 percent rated thermal power in order to maintain compliance with the NPDES Permit river temperature limits, were further derated to achieve compliance with the NPDES Permit. "There is no corresponding requirement for written follow-up in accordance with 10 CFR 50.73." The licensee has notified the NRC Resident Inspector. | 45 | 45 | 45 | 50 | 50 | 50 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-16
46178 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-16 02:06 | 2010-08-16 06:23 | 2010-08-16 | AUTOMATIC REACTOR TRIPS AT BOTH UNITS "Braidwood Unit 2 automatically tripped at 0206 [CST] due to a turbine generator trip due to generator lockout relay actuation. All systems responded as expected, with the auxiliary feed water pumps starting on Low-2 Steam Generator level. The Unit is stable in Mode 3, all primary systems are stable with the secondary heat sink being maintained via aux feed water and the steam dumps. Offsite power is supplying Unit 2, and both emergency diesel generators are available. Cause of generator lockout is under investigation. "Braidwood Unit 1 automatically tripped at 0219 [CST] on a turbine trip caused by a loss of condenser vacuum. All systems responded as expected, with the auxiliary feed water pumps supplying steam generator levels. Secondary heat sink is steam generator PORVs. One steam generator safety valve is not fully seated. No steam generator tube leakage. Cause of the loss of vacuum is under investigation. "For both Units all control rods fully inserted. There were no complications during the trip and all systems functioned as required. Offsite power remained available throughout the transient. "The licensee notified the NRC resident inspector." Braidwood Unit 1's loss of condenser vacuum was caused by the loss of an electrical bus supplying the circ water pumps. At the time of this report, both plants were in a normal shutdown electrical lineup with the exception of the deenergized bus supplying power to the circ water pumps on Unit 1. The steam generator safety valve that has not fully seated was characterized as weeping a small amount of steam. The licensee is uncertain if the Unit 1 trip is related to the Unit 2 trip. | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-08-16
46177 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-08-15 15:24 | 2010-08-15 22:25 | 2010-08-15 | VALID AUX FEEDWATER SYSTEM ACTUATION DURING POWER REDUCTION FOR TURBINE MAINTENANCE "At 1524 EDT, on 8/15/2010, Watts Bar Nuclear Plant Unit 1 had a valid actuation of the Auxiliary Feedwater System in response to a trip of all Main Feedwater Pumps. The Auxiliary Feedwater Pumps were started manually in anticipation of the trip of all Main Feedwater Pumps. Main Feedwater Pump B had been tripped manually as part of the power reduction in preparation for taking the Main Turbine offline to perform repairs on the Electrohydraulic Control System. Main Feedwater Pump A was tripped manually before it experienced a loss of suction in response to an unplanned isolation of the Intermediate Pressure Heater string. "Following manual actuation of the Auxiliary Feedwater Pumps, reactor power was further reduced, and at 1526 [EDT], Watts Bar Unit 1entered MODE 2. "No plant safety systems beyond Auxiliary Feedwater were required or actuated in response to this event. The plant was stabilized using Auxiliary Feedwater and the Main Steam dump valves. Operators followed their Abnormal Operating Instruction, and reactor trip was not required. This event is being reported as a valid actuation of the auxiliary feedwater system in accordance with 10 CFR 50.72(b)(3)(iv)." Offsite power is normal and EDG's are operable. The licensee notified the NRC Resident Inspector. | 2 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Startup | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-08-15
46176 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-08-15 10:45 | 2010-08-15 12:54 | 2010-08-15 | OFFSITE NOTIFICATION DUE TO DISCHARGE OF AMERTAP NEOPRENE BALLS INTO WATERWAY "During the performance of TP-1539, Unit 1 Amertap ball check on 8/15/10 at 0933, it was discovered that approximately 1300 balls could have been lost to the environment via the external circulating water system from the #12 Amertap Ball System. "The Xcel Energy environmental service informed the plant that reports were made to the Minnesota Pollution Control Agency at 1050 CDT on 8/15/10 and the Minnesota State Duty Officer at 1045 CDT on 8/15/10. "The Prairie Island Indian Community Tribal Council will be notified. "The #12 Amertap Ball System is shutdown and will remain out of service until repairs are completed." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-15
46175 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-08-15 00:45 | 2010-08-15 04:15 | 2010-08-15 | TS REQUIRED SHUTDOWN ENTERED DUE TO HIGH CONTAINMENT TEMPERATURE "Due to failure of Service Water from RCP Motor Air Cooler valve MOV3134 to stroke satisfactorily during scheduled surveillance testing, [the licensee] entered TS 3.6.3 Condition A for Containment Isolation Valves. MOV3134 did not indicate full closed by remote indication in the Control Room when time-stroked at 0119, 8/14/10. Consequently, the isolation valve inside containment, MOV3131, was closed and deenergized to provide containment isolation. This isolated a source of Service Water cooling for containment, and the average temperature of containment started trending up from 117.5F at 0000, 8/14/10. At 1400, 8/14/10, containment average temperature exceeded 120F and entry into TS 3.6.5 Condition A was required. At 2200, 8/14/10, containment average temperature had not been restored to [less than or equal to] 120F, and TS 3.6.5 Condition B was entered. To ensure compliance with TS 3.6.5 Condition B, a ramp down to MODE 3 was initiated at 0045, 8/15/10. "At 0057, 8/15/10, the NRC authorized enforcement discretion for Farley Nuclear Plant Unit 1 with regard to LCO 3.6.5 and containment temperature in excess of 120F. The ramp down was halted and power stabilized at 96% Rx power. The enforcement discretion duration is 18 hours starting from 2200, 8/14/10. There were two stipulations on the discretion: "1. If the LLRT [Local Leak Rate Test] on MOV3134 fails, a controlled shutdown will be initiated. Time from the enforcement discretion will be used as necessary to achieve a controlled shutdown. "2. If containment average temperature exceeds 122F, a controlled shutdown will be initiated. Time from the enforcement discretion will be used as necessary to achieve a controlled shutdown. "An update will be sent if a ramp down is recommenced. There is no radiological release in progress." The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 8/15/10 AT 0903 EDT FROM BILL ARENS TO HUFFMAN * * * The LLRT of valve MOV3134 was completed satisfactorily at 0500 CDT on 8/15/10. The valve was declared OPERABLE (but degraded due to the need for additional limit switch and/or torque switch adjustments that do not affect its isolation capability). At 0800 CDT, service water cooling flow was re-established to the RCP Motor Air Coolers. The current containment temperature is 120.4 degrees Fahrenheit. The licensee plans to remain at 96% power until containment temperature drops below 120 degrees. The licensee has notified the NRC Resident Inspector. R2DO (Rudisail) notified. | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-08-15
46174 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2010-08-13 20:10 | 2010-08-13 20:47 | 2010-08-13 | VOLUNTARY NOTIFICATION FOR AN ITEM OF REGULATORY INTEREST "NUREG 1022 provides event reporting guidelines. The NRC encourages voluntary reporting of items of potential regulatory interest that do not meet any reporting criteria. Dominion Nuclear Connecticut (DNC) has elected to shut down Millstone Power Station Unit 3 to repair a small leak in the residual heat removal system connected to the reactor coolant system. The leak is in the vicinity of a component that was recently identified as not being in full compliance with its design requirements. Although the leak does not appear to be associated with the non-conforming component, it is inaccessible while the unit is operating. Therefore, DNC has elected to shut down the unit, repair the leak, and address the non-conformance. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW | [5 empty] | 0 | 2010-08-13
46173 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2010-08-13 10:56 | 2010-08-13 14:27 | 2010-08-13 | OFFSITE NOTIFICATION FOR FISH KILL DUE TO HIGH LAKE TEMPERATURE "At 1056 CDST on 08/13/10, it was discovered that a fish kill took place in LaSalle County Nuclear Station's cooling lake, due to increased temperatures. Approximately 2,000 fish, primarily gizzard shad, but also included bass and walleye were found by plant workers. As summer air temperatures increased, the cooling lake temperatures increased above 93 degrees F, the threshold at which species susceptible to increased temperature begin to perish. Illinois Department of Natural Resources (IDNR) has been notified that a fish kill has occurred. Efforts are under way to contact the IDNR district fish biologist to quantify the mortality. "This notification is made in accordance with the LaSalle County Station Facility Operating License, Appendix B, Section 4.1 'Unusual or Important Environmental Events', and 10CFR50.72(b)(2)(xi). "The licensee notified the NRC Resident Inspector. "A news release is planned for this event." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-13
46172 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-07-16 | 2010-08-13 10:40 | 2010-08-13 | AGREEMENT STATE REPORT- TEXAS - STUCK OPEN SHUTTER ON A PROCESS GAUGE The following report was received via e-mail from the State of Texas Department of State Health Services Radiation Branch: "On August 13, 2010, the Agency [Texas Department of Health] was notified by the licensee that on July 16, 2010 they discovered that the shutter on a TN Technologies Model 5205 nuclear gauge containing 100 millicuries (original activity) of Cesium (Cs) - 137 was inoperable. The gauge shutter was stuck in the open position, which is the normal operating position. There was no additional exposure risk to any individual due to the failure. The licensee discontinued the use of the gauge and contacted the manufacturer to schedule the repair of the gauge shutter. On July 29, 2010, the manufacturer's technician arrived at the plant to repair the gauge. The technician found a build up of corrosion had occurred preventing the gauge shutter from operating properly. The technician advised the licensee that the gauge and source should be replaced due to the corrosion. "The gauge was removed from the vessel on July 29, 2010. The technician secured shielding over the source. No significant exposures were received during the source/gauge removal. A leak test of the source was conducted and the results were below the limit. The licensee is making arrangements to dispose of the source and gauge. Additional information will be provided as it is received in accordance with SA 300." Texas Incident #: I - 8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-08-18
46171 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2010-08-12 19:52 | 2010-08-12 23:50 | 2010-08-12 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO ENVIRONMENTAL CONDITIONS RESULTING IN ELEVATED ULTIMATE HEAT SINK TEMPERATURE "At 2050 [CDT] on 8/12/10, LaSalle Unit 1 and Unit 2 commenced a Plant Shutdown. At 1952 [CDT] on 8/12/10, LaSalle Ultimate Heat Sink exceeded the 101.25?F limit per Technical Specification LCO 3.7.3, Condition B. Per Technical Specification LCO 3.7.3, Required Action B.1, both Unit 1 and Unit 2 are to be in Mode 3 (Hot Shutdown) in 12 hours. Per Technical Specification LCO 3.7.3 Required Action B.2, both Unit 1 and Unit 2 are to be in Mode 4 (Cold Shutdown) in 36 hours. Technical Specification LCO 3.7.3, Ultimate Heat Sink requires that both Unit 1 and Unit 2 to be in MODE 3 by 8/13/10 at 0752 [CDT] and MODE 4 by 8/14/10 at 0752 [CDT]. "Unit 1 was initially at 76% Power due to a response to elevated Main Condenser In-Leakage, not related to the Ultimate Heat Sink High Temperature. Unit 2 was initially at 82% Power due to elevated Condensate Temperature and in response to worsening Main Condenser Backpressure. For Unit 2, both of these parameters were related to the elevated Ultimate Heat Sink Temperature. "The Ultimate Heat Sink Temperature is currently 101.33?F. All Systems are responding as expected." This condition is a result of the hot environmental conditions and is not due to any equipment problems or other operating issues at the site. The licensee has notified the NRC Resident Inspector. | 76 | 82 | 0 | 76 | 82 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-08-12
46170 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2010-02-13 | 2010-08-12 12:22 | 2010-08-16 | AGREEMENT STATE REPORT - BREAK-IN AT RADIOGRAPHY SOURCE STORAGE LOCATION On 2/13/2010, Coder X-Ray Services experienced a break-in at their of McPherson, KS business location. Local police responded within minutes. A laptop computer was stolen but there was no indication of attempted theft involving radioactive sources. The licensee added additional security measures as part of their increased controls for radioactive materials. The State of Kansas discovered this event on a recent inspection. * * * UPDATE FROM AARON SHORT TO JOHN KNOKE AT 1603 EDT ON 8/16/10 * * * The State of Kansas received a police report identifying the burglary at Coder X-ray and Welding in McPherson Kansas. The State also received a letter from the licensee outlining additional security measures they are taking at their facility. Contact the Headquarters Operations Officer for further details. Notified R4DO (Geoffrey Miller), FSME (Richard Turtil) and emailed ILTAB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-08-17
46169 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2010-08-12 03:58 | 2010-08-12 08:04 | 2010-08-12 | UNIT 1 REACTOR AUTOMATIC SCRAM DUE TO TURBINE TRIP "While performing a main condenser flow reversal at 0358 [CDT] on August 12, 2010 the Unit 1 reactor received an automatic scram on turbine stop valve closure. Turbine stop valve closure was initiated from a turbine trip on low vacuum. Reactor water level decreased to approximately -3 [inches], which resulted in automatic Group II and III isolations as expected. All systems responded properly to the event. Unit One remains in Mode 3, maintaining reactor pressure with reactor water level in the normal level band. The cause of the event is still under investigation. "Unit 2 was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." All rods fully inserted. Normal feedwater is supplying the reactor with decay heat removal via the turbine bypass valves. No safety relief valves lifted during the transient. The transient was initiated during the condenser flow reversal when one of the flow reversal valves failed to fully reverse the flow. This resulted in inadequate heat transfer to circ water at full power operation causing the condenser vacuum to increase. In addition, the condenser vacuum trip of the turbine appears to have initiated before it was actually required. Overall, the scram was characterized as uncomplicated and all systems functioned as required. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-08-12
46168 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-01-25 09:50 | 2010-08-11 14:45 | 2010-08-11 | DEGRADATION OF AN ITEM RELIED ON FOR SAFETY "On January 25, 2010 during normal operation of a slugger press in the Fuel Manufacturing Building, a tube connecting the feed hood to the press became disconnected. After starting the vibrating feeder, an operator discovered the feed tube was slightly misaligned and some [uranium] powder had spilled into the hood. The operator immediately used the emergency stop button and the equipment was shutdown. A total of 6.9 kg was removed from the hood. An investigation determined that a clamp on the feed tube came loose, allowing the tube to separate from the fit up device. "The two controlled parameters for criticality safety for this equipment are moderation and geometry and Items Relied on for Safety (IROFS) are established for both. When the tube became misaligned, one geometry related IROFS became unavailable to perform its intended safety function. Additional lROFS on geometry and moderation remained available to perform their intended safety functions and were not challenged. Therefore, this did not result in an unsafe condition. "GNF-A's [Global Nuclear Fuel-Americas] initial review determined this event was not reportable. However, during an inspection February 22 to 26, 2010, NRC evaluated the event and determined that during the period when the tube was misaligned, one IROFS was not available to perform its intended safety function. Therefore, facility performance requirements were not met and a report to the NRC was required. "The NRC issued a notice of violation to GNF-A on March 26, 2010 (70-1113/2010-002-01) for failure to report the event pursuant to 10CFR70 Appendix A(b)(2). The event is now being reported retroactively to satisfy this reporting requirement." The licensee notified the NRC Region 2 Office, the North Carolina Radiation Protection Section and the New Hanover County Emergency Response Organization. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-08-11
46167 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2010-08-11 12:07 | 2010-08-11 13:04 | 2010-08-11 | UNIT 3 DECLARED AN UNUSUAL EVENT DUE TO LOSS OF ANNUNCIATORS "While repairing a control room alarm panel, a screw was dropped. This appears to have caused a breaker (3D1B-27) to trip, which caused a loss of greater than 50% of the control room alarm panels. "A team is being assembled to develop trouble shooting plan to restore alarm panels. Enhanced plant monitoring is being put in place until alarm panels are restored." Approximately half of the control room annunciators are locked in and/or non-functional. The licensee notified the NRC Resident Inspector. Notified DHS (Hill), FEMA (Heyman), DOE (Yates), HHS (Baker) and USDA (Shaffer). * * * UPDATE FROM JOHN SAWYER TO VINCE KLCO ON 8/11/10 AT 2151 EDT* * * At 2130 EDT, Unit 3 exited from the UNUSUAL EVENT based on returning to service greater than 50% of alarm panels. Compensatory measures are in place for the alarm panels which have no audible signal. The licensee notified appropriate state and local agencies. The licensee also notified the NRC Resident Inspector. Agencies that the licensee notified included South Carolina and North Carolina warning points, the South Carolina Emergency Management Agency and the Oconee and Pickens County Emergency Management Agencies. Notified R2DO (Desai), NRR EO (Nelson), IRD Manager (Gott), DHS ( Gates), FEMA (Blankenship), DOE (Bailey), HHS(Grimes) and USDA (Timmons). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-08-11
46166 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-11-23 | 2010-08-10 14:14 | 2010-08-10 | AGREEMENT STATE REPORT INVOLVING UNACCOUNTED FOR IONIZERS The following information was received by fax: "[The North Carolina Radiation Protection Section] received a telephone call and an e-mail from the [Radiation Safety Officer] RSO with RF Micro Devices [RFMD] in Greensboro that they had just resolved on issue with NRD,LLC that there were 24 Ionizers that were unaccounted for in RFMD inventory as of November 4, 2009 when they shipped by [common carrier]. [There were] 34 model P2021 ionizers (1.3 ounces each) in one box weighing 5 pounds to NRD,LLC for disposal. NRD,LLC is located at 2937 Alt. Blvd., Grand Island, NY 14072. The package was shipped by [common carrier] with a package reference # 677000/99562. NRD,LLC signed for 1 box, but only reported 10 ionizers were received on Nov. 23. 2009. At this point RFMD and NRD began discussions as to what happened to the other 24 ionizers(serial numbers A2GL910 thru A2GL933). Both sites have investigated, but cannot account for these ionizers. "Please note-These ionizers are listed by NRD,LLC as Nuclecel Static Eliminators-Model P-2021 containing 10 mCi each of polonium 210 with a 1 year shelf life." North Carolina Incident Number: 10-38 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2010-08-13
46165 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-08-09 12:30 | 2010-08-10 13:43 | 2010-08-10 | 4160 VAC CONTROL AND TRANSFER BREAKER SWITCH DEFECT "On August 9, 2010 at 12:30 CDT, Nebraska Public Power District (NPPD) completed a reportability determination which concluded that certain General Electric - Hitachi (GEH) Type SB-1 Control and Transfer Switches, contained a defect that would have prevented the remote and/or automatic opening and closing of safety related 4160 VAC breakers at Cooper Nuclear Station (CNS), had the switches been installed as received. NPPD has concluded this condition is reportable per 10 CFR Part 21. "Specifically, GEH supplied 23 Type SB-1 Control and Transfer Switches under GEH part number Q16SB1EB4G75SSS1C142 to CNS. 14 of the 23 switches exhibited a failure to maintain the established contact logic when implementing the logic feature of these switches. This condition was discovered during pre-installation testing in support of a station modification of 4160 VAC breaker control. The defect would have prevented the remote and/or automatic opening and closing of the essential affected 4160 VAC breakers. This would have prevented the transfer of the essential 4160 VAC switchgear from the normal station service transformer to either source of offsite power or the emergency diesel generators and the sequential loading of emergency core cooling system pumps in response to a design basis accident LOCA. "All of the switches have been returned to GEH, and none were installed in the station. Therefore, the condition is not reportable under 10 CFR 50.72 or 50.73. These switches were designed and supplied by GEH as a safety related part, specifically for CNS. NPPD is unaware as to if this specific switch design has been supplied to any other licensee. The condition is being reported under 10 CFR 21.21(d)(3)(i). The Responsible [NPPD] Corporate Officer has been notified of this condition per 10 CFR 21.21(d)(3)(i) on August 9, 2010 at 15:45 CDT- Pursuant to 10 CFR 21.21(d)(3)(ii) written notification is due to the NRC within 30 days of this notification." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 21.21 |  |  |  | 0 | 2010-08-10
46164 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-08-10 09:11 | 2010-08-10 10:02 | 2010-08-11 | ALERT DECLARED DUE TO FREON-12 LEAK IN REACTOR BUILDING CHILLER "At 0911 EDT, the Susquehanna LLC Shift Manager was notified that a member of the SSES [Susquehanna Steam Electric Station] work force was feeling ill effects from a Freon-12 leak located in a plant vital area. This met the declaration criteria for an Alert under [EAL] OA-7 of the emergency plan which was declared at 0922 EDT. "The affected area has been evacuated and recovery actions are in progress to isolate the leak. No personnel were injured or medical attention was required." The leak is in the 1A Reactor Building chiller unit. At the time of notification, the leak was still active. The licensee is preparing a team to enter the area to investigate. No outside assistance is required. Notified DHS (Hill), FEMA (Heyman), DOE (Smith), USDA (Mitchell) and HHS (Rolle). * * * UPDATE FROM DARVIN DUTTRY TO DONALD NORWOOD AT 0044 EDT ON 8/11/2010 * * * "At 2335 EDT on 8/10/10, the Alert was terminated. The Chiller has been evacuated of Freon-12. Freon detectors show no presence of Freon-12 on U1 Reactor Building Elevation 749 [feet], except in the immediate vicinity from the leak site with temporary ventilation in service. "All state and local agencies have been advised, the NRC Resident Inspector has been notified and a press release will be made." Agencies that the licensee notified included the Columbia County Emergency Management Agency, the Luzerne County Emergency Management Agency, the Pennsylvania Emergency Management Agency and the Pennsylvania Department of Environmental Protection. Notified R1DO (Ferdas), NRR EO (Nelson), IRD Manager (Gott), DHS (Doyle), FEMA (O'Connell), DOE (Morrone), HHS (White), and USDA (Timmons). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-08-10
46163 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-08-09 08:35 | 2010-08-09 17:16 | 2010-08-09 | APPENDIX R SAFE SHUTDOWN INSTRUCTIONS DO NOT CONTAIN TWO REQUIRED OPERATOR MANUAL ACTIONS "The Browns Ferry Nuclear Plant (BFN) 10 CFR 50 Appendix R Safe Shutdown Instructions provide manual actions to limit diesel loading. From the Tennessee Valley Authority's review of the design input calculation, 'Appendix R - Auxiliary Power System Alignments and Diesel Generator Loading,' it was determined that two 4 kV breakers (one in each of two fire scenarios) that should be tripped and/or tripped and isolated during a postulated Appendix R event were not part of the BFN Safe Shutdown Instructions. Without additional operator manual actions to trip and/or trip and isolate the affected breakers, spurious closure of the breakers could overload the credited emergency generator. "Interim actions to trip and/or trip and isolate these breakers for Appendix R Safe Shutdown Instructions are being put in place. "This event is reportable within 8 hours under 10CFR50.72 (b)(3)(v)(A) - any event or condition that results in the condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: Shut down the reactor and maintain it in a safe shutdown condition. This event is also reportable within 60 days under 10CFR50.73(a)(2)(v)(A) - as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: Shut down the reactor and maintain it in a safe shutdown condition. "This condition was self-identified. The condition has been documented in the BFN Corrective Action program as Service Request 228891. Unit 1, 2, and 3 remain at power and are not affected by this event. The NRC Resident Inspector has been notified." | 50 | 50 | 50 | 50 | 50 | 50 | -1 | -1 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-08-09
46162 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-08-09 08:12 | 2010-08-09 13:04 | 2010-08-09 | OFFSITE NOTIFICATION DUE TO LOSS OF CONDENSER TUBE CLEANING (AMERTAP) BALLS "During the performance of TP-1539, Amertap Ball Check on 8/08/2010 at 1326 [CDT], it was discovered that [about] 1400 balls could have been lost to the environment [Mississippi River] via the External Circulating Water System from the 11 Amertap Ball System. "The Xcel Energy Environmental Service informed the plant that reports were made to the Minnesota Pollution Control Agency on 8/09/2010 at 0817 and the State of Minnesota Duty Officer on 8/09/2010 at 0812. "The Prairie Island Indian Community Tribal Council was notified. "The 11 Amertap Ball System is shutdown and will remain out of service until repairs are completed." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-09
46161 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-08-09 07:42 | 2010-08-09 12:32 | 2010-08-09 | DISCOVERY OF FIREARM DURING X-RAY SCREENING "At 0742 CDT on 08/09/2010, Prairie Island Nuclear Generating Plant (PINGP) personnel discovered a hand gun in a personal bag being processed through an x-ray search machine in the Security Access Facility. Security personnel immediately established control of the weapon and the owner. The owner of the weapon is a permanent employee of PINGP. The owner has been determined to hold proper permits for the weapon. "The Local Law Enforcement Agency and the Prairie Island Community Tribal Council was notified. "The NRC Resident Inspector has been notified. "This notification is being conducted in accordance with 10CFR50.72(b)(2)(xi) for notification to an outside government agency." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-09
46160 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-09 05:00 | 2010-08-09 04:23 | 2010-08-09 | TECHNICAL SUPPORT CENTER DECLARED OUT OF SERVICE FOR PLANNED MAINTENANCE "A condition is being reported per Technical Requirements Manual 13.13.1, 'Emergency Response Facilities', Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance being performed on the TSC HVAC. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with high priority. A 10CFR50.54(q) evaluation has been performed for this planned maintenance activity. The NRC Resident Inspector has been notified." * * * UPDATE FROM PAUL BURWINKEL TO VINCE KLCO ON 8/9/10 AT 1438 EDT * * * "The planned maintenance of the TSC HVAC was completed and the Technical Support Center was returned to functional status as of 8/9/10 at 1153 EDT. The NRC Resident Inspector has been notified." Notified the R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-09
46159 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2010-08-07 14:51 | 2010-08-07 18:47 | 2010-08-07 | MANUAL REACTOR TRIP AFTER REACTOR COOLANT PUMPS HIGH VIBRATION "At 1451 on 8/7/2010, Oconee Unit 1 initiated a manual reactor trip from approximately 17% power due to indicated vibrations on 1A1 and 1A2 reactor coolant pumps [RCP] reaching the high vibration trip criteria. All systems responded normally following the reactor trip. Unit 1 is currently stable in MODE 3. An investigation is in progress to determine the cause of the elevated reactor coolant pump vibrations." All control rods fully inserted on the trip. Decay heat is being removed via the turbine bypass valves to the main condenser. Steam generator water level is being maintained with main feedwater. There is no evidence that the PORVs or safety valves lifted. The plant is in its normal shutdown electrical lineup. There were no indications on the loose parts monitor except for the RCP high vibration. There was no affect on units 2 or 3. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-08-07
46158 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2010-08-07 00:15 | 2010-08-07 03:53 | 2010-08-07 | OFFSITE NOTIFICATION DUE TO INADVERTENT SOUNDING OF ONE OFFSITE EMERGENCY SIREN "River Bend Station is making a 4 hour report in accordance with 10CFR50.72(b)(2)(xi) of an event that occurred at approximately 0015 hours on August 7, 2010 when one offsite emergency siren for River Bend located in West Feliciana Parish inadvertently sounded. The siren activation was not related to any condition or event at River Bend. River Bend has notified West Feliciana Parish authorities and the Governor's Office of Homeland Security and Emergency Preparedness of the inadvertent siren activation. "At 0230 hours on August 7, 2010 the malfunctioning siren was disabled to prevent any further inadvertent sounding. "The site NRC Resident Inspector's office has been informed of the inadvertent siren activation and that a 4 hour notification is being made. "The River Bend alert and notification system remained operable for the duration of the event. "The Governor's Office of Homeland Security and Emergency Preparedness does not intend to air the inadvertent siren sounding message over the emergency alert system. A press release from Entergy is not planned at this time." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-08-07
46157 | 0 | TRIPLER ARMY MEDICAL CENTER |  |  |  |  | 2010-06-07 | 2010-08-06 16:14 | 2010-08-06 | UNPLANNED IODINE-131 DOSE TO AN EMBRYO A patient was receiving a thyroid ablation for cancer on 6/7/2010. Prior to the administration of the I-131 capsules, the patient received a blood serum test to check for potential pregnancy. The results were negative. On 7/8/2010, the patient returned for a follow-up visit and informed the doctor that she was pregnant. An ultrasound estimated that the date of conception was 6/1/2010. The RSO was notified of this event on 8/4/2010. The patient will be notified on 8/11/2010. Source: I-131 capsules 154.9 mCi. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 35.3047(a) |  |  |  | 0 | 2010-08-06
46156 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2010-08-05 15:00 | 2010-08-05 15:39 | 2010-08-06 | LOSS OF ALL POWER AND EMERGENCY RESPONSE FUNCTION AT THE TECHNICAL SUPPORT CENTER DUE TO SCHEDULED MAINTENANCE "The Technical Support Center (TSC) will be without power during performance of planned maintenance activities starting at approximately 1500 CDT on August 5, 2010. The maintenance activities, including electrical isolation and restoration, are expected to last approximately 12 hours. Contingency plans for emergency [response] situations have been established and the Emergency Response Organization members have been notified of their contingency actions. "This event is reportable per 10CFR50.72(b)(3)(xiii) since this constitutes a loss of an emergency response facility for the duration of the maintenance activities. "Region IV was notified of this planned outage. "The licensee notified [State and local agencies and] the NRC Resident Inspector." * * * UPDATE ON 8/6/10 AT 0407 FROM BONVILLIAN TO HUFFMAN * * * The Technical Support Center was restored to functional status at 0407 EDT. All systems verified operational. The licensee will notify State and local agencies and the NRC Resident Inspector. R4DO (Hagar) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-05
46155 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-08-05 11:45 | 2010-08-05 15:30 | 2010-08-05 | MOMENTARY LOSS OF SECONDARY CONTAINMENT DUE TO PERSONNEL PASSING THROUGH OPEN AIRLOCKS "On August 5, 2010 at 1145 CDT, both doors in Airlock 413 from Secondary Containment (SCT) to the 985 ft Radwaste Pump Room were simultaneously open for a period of approximately five (5) seconds and subsequently reclosed. This condition caused an unplanned entry into Technical Specification 3.6.4.1.A for SCT. The condition could have prevented the Standby Gas Treatment system from developing a negative pressure with SCT following a design basis accident. This negative pressure is required to prevent ground level release of radioactivity and to minimize onsite and offsite dose consequences following an accident. The Standby Gas Treatment system remained operable throughout the event." The licensee will inform the State and has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-08-05
46154 | 0 | ARCELORMITTAL BURNS HARBOR |  |  |  |  | 2010-07-22 02:30 | 2010-08-05 15:13 | 2010-08-05 | NUCLEAR GAUGE DISLODGED FROM STEEL CASTER AND LATER RETRIEVED "After completion of casting operations at the #1 Slab Caster, a trained worker proceeded to the mold strand area to remove the Berthold Co-60 rod source from the mold and place it in proper storage. The source is 3.97 mCi [Co-60] and is used to measure mold level of liquid steel. After all machinery and equipment was moved away from the mold so it could be accessed, the trained worker removed the plug to access the source for proper removal. Upon removing the plug, the trained worker noticed dirt and debris in the opening so he used compressed air to clean the area. The force of the compressed air into the source opening caused the source rod to lift out of the seated position and drop approximately 10 feet into the mold. The trained worker and a co-worker were able to retrieve the rod and place it back into its appropriate source holder. Investigation and exposure calculations indicated that neither employee was exposed above regulatory limits." The licensee performed exposure calculations and estimated the trained radiation worker received a dose to the hands of 10.2 mRem. The assistant (not a trained radiation worker and not carrying dosimetry) received a calculated dose to the hands of 0.12 mRem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-08-05
46153 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-08-05 13:55 | 2010-08-05 14:53 | 2010-08-05 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION MEETING UNUSUAL EVENT CRITERIA "At 1345 EDT, following maintenance on 1-CHÀLCV-1115A, VCT divert valve, testing was commenced. At 1355 EDT, the valve failed to the full divert position and could not be repositioned from the normal control system, resulting in 75 gpm letdown flow being diverted to the gas stripper. "At 1401 EDT, the normal letdown flowpath was isolated in accordance with plant procedures and the leakage isolated. "The identified flow rate exceeded the threshold for entry into a Notice of Unusual Event under EAL tab SU6.1 due to identified leakage greater than 25 gpm." The licensee will inform State and local agencies and has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | VA | POW | [5 empty] | 0 | 2010-08-05
46152 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-08-06 07:00 | 2010-08-05 13:43 | 2010-08-06 | TECHNICAL SUPPORT CENTER (TSC) PLANNED MAINTENANCE ACTIVITY "On 8/6/10 at 0700 CDT the Monticello Nuclear Generating Plant's [MNGP] Technical Support Center uninterruptible power supply will be isolated to perform a planned maintenance activity. The maintenance activity requires implementation of compensatory measures to maintain TSC functions during the activity. The compensatory measures include having the Emergency Director report to the Control Room and co-locating the remaining TSC staff at the EOF should an event be declared requiring ERO activation. The ERO has previously successfully demonstrated the ability to implement these compensatory measures. The maintenance activity is scheduled to be completed with the TSC returned to full functionality by the end of the dayshift on 8/6/10. The Site Emergency Response Organization has been notified of the maintenance activity and instructed on the planned compensatory measures to be implemented during the activity. MNGP will notify the NRC upon completion of the activity restoring full TSC operability. This event is considered reportable per 10CFR50.72(b)(3)(xiii). The licensee has notified the NRC Resident Inspector." The licensee will inform both State and local agencies. * * * UPDATE AT 2015 EDT ON 8/6/10 FROM MARTIN RAJKOWSKI TO S. SANDIN * * * "On 8/6/10 at 1705 CDT the Monticello Nuclear Generating Plant's Technical Support Center was returned to full operability. The Monticello Emergency Response Organization has been notified and the compensatory measures that were in effect have been terminated. The licensee has notified the NRC Resident Inspector." The licensee will inform both State and local agencies. Notified R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-08-05
46151 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-08-05 07:30 | 2010-08-05 11:36 | 2010-08-05 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of Florida via fax: "A soil moisture density gauge (Troxler) was discovered stolen at approximately 0730 [EDT] on 5 Aug 2010, this office notified at 1015 [EDT]. Gauge stored in a locked conex box, case chained to the conex box, case was locked and gauge itself was locked; owner still has control of gauge's key. Conex box lock found broken and chain lock broken also. Licensee will offer a reward. Orlando Inspection Office will investigate. This office will take no further action on this incident. "The incident location was a jobsite on Dunn Avenue 3/4 mile west of Williamson Blvd. in Daytona Beach. Daytona Beach PD case number 2010016305." The stolen gauge is a Troxler Model 3430, S/N 60176, containing two (2) sources; 40 mCi Am-241/Be and 8 mCi Cs-137. Florida Incident Number - FL10-089 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-08-10
46150 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-08-05 07:30 | 2010-08-05 11:35 | 2010-08-05 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of Florida via fax: "A soil moisture density gauge (Troxler) was discovered stolen at approximately 0730 [EDT] on 5 Aug 2010, this office notified at 1015 [EDT]. Gauge stored in a locked conex box, case chained to the conex box, case was locked and gauge itself was locked; owner still has control of gauge's key. Conex box lock found broken and chain lock broken also. Licensee will offer a reward. Orlando Inspection Office will investigate. This office will take no further action on this incident. "The incident location was a jobsite on Dunn Avenue 3/4 mile west of Williamson Blvd. in Daytona Beach. Daytona Beach PD case number 2010016305." The stolen gauge is a Troxler Model 3430, S/N 26007, containing two (2) sources; 40 mCi Am-241/Be and 8 mCi Cs-137. Florida Incident Number: FL10-088 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-08-10
46149 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2010-08-03 | 2010-08-05 08:53 | 2010-08-05 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE A representative from the State of Maryland Radiological Health Program reported the theft of a Troxler moisture density gauge. The Troxler gauge (Model 3440, Serial Number 21688, with 40 mCi of Am-241/Be and 8 mCi Cs-137) was stolen on 8/3/10 from a truck parked overnight at the home of a Penniman and Browne employee. Both company and State representatives have searched for the gauge in areas nearby the location of the theft without success. The theft has been reported to the Howard County Sheriff and the State plans to issue a press release on the incident. The State noted that the storage of the Troxler in a truck at the employee's home was not authorized. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2010-08-10
46148 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-12-31 | 2010-08-04 16:04 | 2010-08-04 | AGREEMENT STATE REPORT- EXTREMITY OVEREXPOSURE DISCOVERED DURING AN AUDIT The following information was received from the State of Florida via fax: "During a scheduled state audit, it was discovered [that] an employee received an overexposure greater than 50 rem (51881 mr) to an extremity in December of 2008. Licensee is implementing corrective action, as in leaded gloves, increased shielding, review of radiation protection manual and procedures. Further action is referred to Licensing and Materials Office. This office will take no further action on this incident." The State of Florida incident date is 04-Aug-10 with the investigation conducted on 27 July 2010. Florida Incident No.: FL10-087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-08-09
46147 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2010-08-02 | 2010-08-04 15:10 | 2010-08-04 | AGREEMENT STATE REPORT INVOLVING A SOURCE FOUND IN A LOAD OF SCRAP The following report was received from the State of Alabama via fax: "The Agency [Alabama Office of Radiation Control] received a call from representatives at Huron Valley Steel Corporation in Anniston, AL on August 2, 2010 regarding elevated readings from a load of scrap. Huron Valley personnel indicated that the facility received the load from American Cast Iron Pipe Company (ACIPCO) in Birmingham, Alabama. An Agency representative asked Huron Valley personnel [to] isolate and secure the scrap. Agency representatives visited Huron Valley Steel on August 3, 2010 to assist with measurement, identification, and securing the possible source of radiation. Agency representatives noted that the source of radiation was approximately 6 inches wide x 2 inches deep x 1-2 inches [in] height. Agency representatives noted that the source of radiation no longer bore any identifying marks and appeared to be compacted. Agency representatives noted that exposure readings were approximately 330 mR/hr at approximately 4 inches from the source. Agency representatives measured for removable contamination in the field (none noted); representatives noted that areas around the source's location in the scrap did not appear to be contaminated. Agency representatives ensured that the source of radiation was isolated, shielded, and secured as of the date and time of submission of this report. "The Alabama Office of Radiation Control (Agency) is investigating the origination point of this source of radiation. Agency personnel are gathering data for personnel exposure estimations. Agency personnel are in the process of identifying the nuclide in the source of radiation. The aforementioned information is the most current information available to the Agency as of the date of report submission, August 4, 2010 at 2:00 p.m. central time. "Alabama Incident 10-35 - Report regarding Source of Radiation Found in Scrap" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2010-08-09
46146 | -1 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-08-03 15:06 | 2010-08-03 20:34 | 2010-08-26 | POTENTIAL SAFETY SYSTEM FUNCTIONAL FAILURE OF THE ACCIDENT MITIGATING FUNCTION "On 8/3/10 South Texas Project Unit 2 was in a scheduled A Train work week with the following equipment inoperable for planned maintenance; Essential Cooling Water Pump, Essential Chiller, Component Cooling Water Pump, Engineered Safety Function (ESF) Diesel Generator (DG), High Head Safety Injection (HHSI) pump, Low Head Safety Injection (LHSI) pump, and Containment Spray (CS) pump. "At 0754 [CDT] on 8/3/10 the B train sequencer trouble alarm was received. The immediate operability determination was the sequencer remained operable. It was later identified during testing that the sequencer was inoperable. The B train sequencer was declared inoperable at 1506 [CDT] on 8/3/10. Due to loss of the automatic load sequencing support function, all associated train B safety equipment that is sequenced on the B train 14.16 kv bus during a Mode 1 Safety Injection (SI) was also declared inoperable. "This condition resulted in an inoperable condition on two out of three safety trains for the accident mitigating function including the A and B train HHSI, LHSI, and CS pumps. All C train safety injection pumps remained operable. Pending a formal operability determination, this is conservatively considered to be a safety system functional failure of the accident mitigating function. "This was determined to be reportable within 8 hours as required by 10 CFR 50.72(b)(3)(v)(D)." The B train trouble alarm, an auto test feature, was discovered by operators during their rounds. The licensee entered their configuration risk management plan within the 1 hour as required. Currently, the licensee is working on completing the scheduled A train maintenance and restoring operability sometime in the morning. Also, a work package is under development to repair the faulty B train sequencer. The risk based time limit for restoring operability requires completion by 0449 [CDT] on 8/8/10. Unit 1 is unaffected and continues to operate at 100% power. The licensee informed the NRC Resident Inspector. * * * RETRACTION AT 1638 EDT ON 08/26/2010 FROM JIM MORRIS TO S. SANDIN * * * "The purpose of this update is to retract the notification made in ENS Report #46146 (August 3, 2010). "Following the ENS notification, troubleshooting determined the cause of the Train B sequencer alarm to be the failure of an Output Mode I Actuation Timing Switch Module. An engineering evaluation of the event has been completed and determined that a failure of this module did not affect the ability of the ESF load sequencer to perform its design function. Therefore, the Train B sequencer and associated Train B ESF equipment remained technically operable during the time that Train A equipment was inoperable due to scheduled maintenance, and a condition reportable per 10 CFR 50.72(b)(3)(v) did not exist. "The licensee will notify the NRC Resident Inspector." Notified R4DO (Walker). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-08-03
46145 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2010-08-03 06:50 | 2010-08-03 17:32 | 2010-08-03 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION UNUSUAL EVENT DUE TO A HIGH LEVEL WATER ALARM "This is a one-hour report for the discovery of a condition that met an emergency action level (EAL) for a Notification of Unusual Event (NOUE) but was not determined classifiable until after conditions meeting the EAL level for the NOUE no longer existed. A detailed review of the conditions that existed at 0650 [EDT], on August 3, 2010 during a planned system drain down of the 2A loop of RHR to the northeast diagonal sump met the criteria for an NOUE: EAL HU1 - Natural and Destructive Phenomena Affecting the Protected Area. "Threshold Value 6 states: 'Exceeding Max Normal Operating Values specified in EOP 31EO-EOP-014-1(2) SC - Secondary Containment Control Table 5 Secondary Containment Operation Water Levels.' "At 0650 [EDT] on August 3. 2010 the Hatch Unit 2 crew received a HIGH-HIGH-HIGH alarm which is the Max Normal Level described in 31EO-EOP-014-1(2). This occurred during a planned draindown evolution when a valve (2T45-F004) which is required to transfer water from the sump to radwaste failed to open. At 0656 [EDT] on August 3, 2010 the RHR drain valve (2E11- F069A) was closed discontinuing draining into the northeast diagonal sump. It is estimated that no more than 800 gallons of water was in the system and internal flooding was not a significant concern. However, despite the low safety significance, the EAL threshold criteria was technically met and therefore this report is being made. "This event is a one hour report based on the guidance in NUREG-1022 Section 3.1.1 for a condition that met an EAL and the condition for the classification no longer existed at the time of discovery. A courtesy notification will be made to state and local agencies." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | GA | POW | [5 empty] | 0 | 2010-08-03
46144 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2010-08-03 14:52 | 2010-08-03 17:25 | 2010-08-03 | UNIT 1 ENTERED A TECH SPEC REQUIRED SHUTDOWN AFTER DECLARING EDG 102 INOPERABLE "Nine Mile Point Unit 1 entered a Technical Specification (TS) Required Shutdown due to unplanned inoperability of Emergency Diesel Generator [EDG] 102 during planned maintenance on opposite division Liquid Poison pump 12. In accordance with TS 3.0.1, Limiting Condition for Operation [LCO] Applicability and TS 3.1.2, Liquid Poison System, normal orderly shutdown commenced at 1551 [EDT] which was within one hour of declaring Emergency Diesel Generator 102 inoperable." The unplanned inoperability of EDG 102 was caused by the failure of its lube oil circulating pump due to thermal overload. The licensee is pursuing restoration of EDG 102 and the Liquid Poison pump 12 in order to exit the LCO Action Statement. The licensee informed the NRC Resident Inspector. * * * UPDATE FROM ROY GREEN TO VINCE KLCO ON 8/3/10 @ 2118 EDT * * * "The Nine Mile Point Unit 1 TS required shutdown was suspended at 1929 [EDT] upon restoration of Emergency Diesel Generator (EDG) 102 to operable. With operability of EDG 102 restored, Liquid Poison Pump 11 was also made operable. Accordingly, the TS shutdown action for an inoperable liquid poison system was exited. The lowest power level reached was 92.5% of the licensed thermal power limit. Power ascension is in progress, and [the licensee expects] to be at rated power by 2200 [EDT]." The licensee notified the NRC Resident Inspector. Notified the R1DO (DeFrancisco) | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-08-03
46143 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2010-07-09 | 2010-08-03 10:22 | 2010-08-03 | AGREEMENT STATE REPORT - PATIENT EXPOSURE TO AN UNINTENDED AREA On July 9, 2010, a cervical cancer brachytherapy study was being performed using a Cs-137 source (44.2 mCi). The physician failed to place the source in the afterloader and the source fell on the patient's buttocks. The source was later recovered from the trash before it left the facility. The licensee estimates the maximum dose received was 1050 centiGray. The patient's physician and the patient were notified of this event. No reddening of the skin has been noticed. The state was notified on 7/12/2010 and a written report was received from the licensee on 7/26/2010. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2010-08-09
46142 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-07-28 15:27 | 2010-07-30 20:44 | 2010-08-03 | AGREEMENT STATE REPORT - POTENTIAL MISSING SOURCES The following information was received by e-mail: "Chevron left a voicemail message on 7/28/10, reporting two devices missing [to the Los Angeles County - Region 7- State of California-Health and Human Services Agency otherwise known as the 'Agency']. [The Agency and the licensee] exchanged voicemail messages until [the Agency] was able to talk with the [licensee Radiation Safety Officer] RSO on 7/30/10. [The devices] are Nitons, serial numbers U2779 & U 2778. Each contains 20 mCi Fe-55 and 10 mCi Cd-109. The reporting quantities (1,000X) are 100 mCi Fe-55, and 1 mCi for Cd-109; the Cd-109 is the source that makes this immediately reportable. The sources were last leak tested on November 5, 2007. The RSO looked for them again in May 2008 at the Chevron's 'storehouse,' where these devices were kept. [The storehouse] was moving and [personnel] said they didn't know where [the sources] were [located]. Subsequently, the storehouse said they had been sent back to Niton, as a trade-in for devices using X-ray instead of a radioactive source. Chevron asked Niton to send them a letter saying they had received the devices, but Niton said they had never received the devices. Chevron does have devices using X-ray. They continue to look for the devices, and will check their invoice to see if they had received any trade-in credit when they purchased the X-ray devices." * * * UPDATE AT 1937 EDT ON 8/3/10 FROM CASS KAUFMAN TO S. SANDIN VIA EMAIL * * * The following information was provided as an update: "This is an update for the missing gauges previously reported on 7/30/10. The licensee found records of source exchange, which makes this a 30 day reporting event, and not an immediate reporting event as previously stated. The two gauges remain missing." "This is a follow-up to our conversation a few minutes ago, & to clarify the reporting requirement. These missing gauges are still required to be reported, but within 30 days, rather than immediately. The sources that require reporting are cadmium 109. Now that we have information that the sources were exchanged in February 2006, the activity of Cd-109 is below 1 mCi (the current activity is about 0.85 mCi). So this is required to be reported within 30 days." Notified R4DO (Hagar) and FSME (Lewis). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-08-04
46141 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-07-16 | 2010-07-30 17:45 | 2010-07-30 | AGREEMENT STATE REPORT - NUCLEAR GAUGES LEFT IN WAREHOUSE BY BANKRUPT BUSINESS The following information was received via facsimile: "On 7-16-2010, MSDH DRH [Mississippi State Department of Health Division of Radiological Health] received a call from a gentleman who owns a warehouse in Columbus, MS. He stated that as he was going through the contents of his warehouse to determine what could be sold as used equipment or as scrap metal, he discovered a nailed-shut wooden crate with the word 'Radioactive' written in marker on the side. On 7/19/10, DRH inspectors went to the warehouse and discovered that 2 fixed nuclear gauges were in the wooden box. Both gauges were the same model, FM1R-1, manufactured by Mahlo. Labels indicated that each had been loaded with one 100 mCi Pm-147 (Promethium) source. According to the assay dates found on the labels on the gauges, both sources were decayed to less than 0.1 mCi. One other gauge was found in the warehouse. This one was still bolted to a piece of manufacturing equipment. It was an Ohmart fixed gauge loaded with a 60 mCi Kr-85 source in 1994, therefore it is decayed to approximately 10 mCi. DRH inspectors brought the three gauges to DRH office for safe storage until proper disposal can be arranged. Note: The man who reported the box with 'Radioactive' marked on it, had been leasing to a company involved in textile manufacture. The leasee went bankrupt and owed the warehouse owner substantial payments. The owner is legally selling the contents of the warehouse to recoup some of his losses. The owner has no knowledge or background with nuclear gauges. Gauge info follows: Manufacturer Model Gauge Ser # Isotope Mahlo FMIR-1 610/61/U1 Pm-147 Mahlo FMIR-1 610/61/IU2VG89 PM-147 Ohmart BAL 2860BX Kr-85 "Further investigation revealed that the Ohmart gauge was identified on a General License in Alabama, licensed to Crown Textile Co.(now out of business). Also a former employee of a company named American Nonwovens (now out of business) said that all three gauges were brought from Alabama to the warehouse in Columbus, MS where they were found. "MSDH Div of Radiological Health continues to keep the abandoned gauges for safe-keeping and has contacted a disposal company to dispose of the gauges." MSDH DRH Report: MS-10005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2010-08-04
46140 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-07-30 07:20 | 2010-07-30 15:50 | 2010-07-30 | LOSS OF EMERGENCY SIREN "On July 30, 2010, at approximately 0720 Mountain Standard Time (MST), the Palo Verde Emergency Planning Department discovered that public warning system siren No. 17 was not responding, and therefore, is out of service. The loss of siren No. 17 could potentially impact a population of approximately 1196 people in the 5-mile emergency planning zone (EPZ). "Since the loss of siren No. 17 could impair Arizona Public Service Company's ability to inform greater than 5% of the population within the EPZ, this notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). If an event occurs while siren No. 17 is out of service, the Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area. The MCSO is prepared to implement this contingency should it become necessary. "Troubleshooting to determine the cause of the failure has commenced." The NRC Resident Inspector has been notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-30
46139 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-07-29 07:40 | 2010-07-29 18:02 | 2010-07-29 | 24 HOUR FITNESS-FOR-DUTY REPORT A non-licensed contract foreman had a confirmed positive during a follow-up fitness-for duty test. The contract employee's unescorted access has been terminated. Contact the Headquarters Operation Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2010-07-29
46138 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2010-07-28 14:00 | 2010-07-29 13:40 | 2010-07-29 | INCORPORATION OF 'INCREDIBLE' CRITICALITY SEQUENCES INTO INTEGRATED SAFETY ANALYSIS "This notification is being made based on 10 CFR 70 Appendix A (b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10 CFR 70.61.' "Westinghouse Environmental Health and Safety (EH&S) staff evaluated the compliance posture concerning the extent of condition for an open Notice of Violation (NOV) 70-1151/2009-201-01, and evaluation of the information provided in the 'Summary of the June 28, 2010, Public meeting to discuss the use of Design Features to meet the performance requirements of Title 10 of the Code of Federal Regulations part 70, Subpart H,' (ML101950377). This evaluation identified a contradiction between the guidance and [the] approved SNM-1107 License and procedures. Therefore, criticality events evaluated as incredible in accordance with procedure NCS-010 'Categorizing Potential Criticality Scenarios and Criticality Safety Significant Controls' are no longer deemed in compliance with 10 CFR Part 70. Following the NCS-010 methodology allowed for an incredibility conclusion 'based on crediting passive engineered controls or passive design features.' When the logic demonstrated that the passive control or design feature absolutely prevented the scenario from leading to a criticality, the scenario was categorized as incredible; the control was designated as a Safety Significant Control (SSC) in the Integrated Safety Analysis (ISA). SSCs are subject to Management Measures required by the SNM-1107 License to ensure they are available and reliable to perform their intended function. However, failure to identify these accident sequences as credible led to these sequences not being included in the ISA Summary, and therefore Items Relied on For Safety (IROFS) were not designated for these sequences. "Immediate Corrective Actions: A governing policy was issued as an interim compensatory measure to identify all current Nuclear Criticality Safety (NCS) engineered SSCs as IROFS. A currently in place NCS Facility Walk-through Assessment process, procedure RA-316, is also designated as an Administrative IROFS as a verification activity of the engineered controls. "Interim controls are being established on modifications pertaining to Criticality Safety Related SSCs to ensure no situation occurs where a modification may require NRC pre-approval. "This event has been entered into the Facility Corrective Action Process CAPS #10-210-C002." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-07-29
46137 | -1 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2010-07-28 23:58 | 2010-07-29 01:55 | 2010-07-29 | SAFEGUARDS REPORT - DEGRADATION OF SECURITY ALARM MONITORING CAPABILITY Safeguards system degradation related to monitoring and assessment capability. Compensatory actions taken. Partial system restoration completed. Full restoration in progress. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM GREG HUDNALL TO DONALD NORWOOD AT 1832 EDT ON 7/29/2010 * * * Further investigation by the licensee concluded that security plan requirements were met for the event and the event is not reportable. Contact the Headquarters Operations Officer for additional details. Notified R4DO (Proulx) and via E-mail the 73.71 Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-07-29
46136 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-07-28 14:22 | 2010-07-28 19:04 | 2010-09-27 | THREE AUXILIARY FEEDWATER (AFW) TRAINS DECLARED INOPERABLE "At 1422 CDT, while operating in MODE 1 at approximately 100% rated thermal power (RTP), Wolf Creek Generating Station (WCGS) entered Technical Specification 3.7.5, 'Auxiliary Feedwater (AFW) System,' Condition D for three AFW trains inoperable. The AFW pumps are equipped with recirculation lines to prevent pump operation against a closed system. The recirculation line for each pump combines into a common header that flows to the condensate storage tank (CST). The common recirculation line transitions from safety-related to non-safety related at the AFW to CST pipe tunnel. During a review of the system design information, it was identified that a seismic event or tornado could result in damage to this portion of the recirculation line and thereby restrict or block the recirculation flow causing pump damage. "TS 3.7.5, Required Action D.1, requires the immediate initiation of action to restore one AFW train to OPERABLE status. The Note to Required Action D.1 specifies that LCO 3.0.3 and all other LCO Required Actions requiring MODE changes are suspended until one AFW train is restored to OPERABLE status. The plant remains in MODE 1 at approximately 100% RTP with activities that could lead to the need to maneuver the plant being suspended. "WCGS personnel are developing an evaluation to support the OPERABILITY of the AFW trains with the reliance on compensatory measures as an interim action until final corrective action to resolve the condition are completed. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 1719 ON 9/27/2010 FROM MARCY BLOW TO MARK ABRAMOVITZ * * * "Further evaluation by the Engineering Department determined that the capability of the AFW system was not reduced. The postulated condition is considered a design deficiency (nonconforming condition) to be corrected before considering the equipment fully qualified. The safety functions and the capability of the AFW system to mitigate a design basis event are not impaired. As a result, the condition has been determined to not be reportable per 10 CFR 50.72(b)(3)(ii)(B), 10 CFR 50.72(b)(3)(v)(A) or 10 CFR 50.72(b)(3)(v)(B)." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) |  | 0 | 2010-07-28
46135 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-07-28 17:00 | 2010-07-28 17:45 | 2010-07-28 | FITNESS FOR DUTY REPORT A licensed operator was determined to have violated the licensee's Fitness for Duty Policy related to self-reporting a legal action. The employee's access to the Protected Area has been revoked. Contact the Headquarters Operations Officer for additional details. | 0 | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2010-07-28
46134 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2010-07-27 | 2010-07-28 17:25 | 2010-07-28 | OKLAHOMA AGREEMENT STATE REPORT - IRRETRIEVABLE WELL LOGGING SOURCE The following information was obtained from the State of Oklahoma via email: "A well logging source has been lost down hole in Woods County, OK. The source information is Cesium 137, 1.78 Curie, S/N A3128, QSA Global model Y3. The licensee is Thrubit, Oklahoma license OK-32115-01. "The source is at a depth of 4452 [ft.] according to the gamma ray log. Surface location is Section 13-28N 13W, Lat 36.899418, Long -98.555695. "The well operator is Chesapeake." "The licensee has monitored to verify that there is no leakage of radioactivity from a source rupture. Four unsuccessful fishing attempts have been made and the licensee believes that the source is lodged in rubble where it can't be retrieved. The licensee informs DEQ [Oklahoma Dept. of Environmental Quality] they expect to submit a request to abandon the source. The Cesium source is lost as mentioned, but no AmBe or Californium source is lost. "The above is based on telephonic information received from the licensee and is a preliminary report. This information may be modified or updated based on written reports from the licensee or a DEQ investigation." It is unclear at this time when the source was lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2010-08-02
46133 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-07-28 09:45 | 2010-07-28 16:32 | 2010-07-28 | OFFSITE NOTIFICATION OF A SULFURIC ACID SPILL "On Wednesday, July 28, 2010, at about 0945 PDT, Southern California Edison (SCE) determined that a spill of a total of about 110 gallons of sulfuric acid had occurred from two different locations earlier in the same day. All the acid was contained within the chemical berms around the acid transfer pumps in the Unit 3 intake area at the 9 foot level and the 30 foot level caustic berm. No acid was released to the environment. "At 1050 PDT, SCE initiated notification to the San Diego County Department of Environmental Health (Report # 10-063463), the California Emergency Management Agency (CalEMA) (Report # 10-4518) and the National Response Center (Report # 949176). Notifications were completed by 1100 PDT. "SCE is making this notification in accordance with 10CFR50.72(b)(2)(xi). " The NRC Senior Resident Inspector has been notified. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-28
46132 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-07-23 11:20 | 2010-07-28 14:14 | 2010-07-28 | AGREEMENT STATE REPORT - POTENTIAL WHOLE BODY DOSE ABOVE REGULATORY LIMITS The following report was received via fax from the State of Massachusetts: "Licensee RSO, called to report that he received notification from the Corporate Office that a Landaur exposure report indicates one of his radiographer's whole body badge read in excess of 17,000 mrem for June of 2010. This person performs radiography operations using the x-ray vault. [The RSO] does not feel that the exposure is real, however, he is initiating an investigation. He stated it's more likely that the WB badge was left in the radiography vault inadvertently." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-08-02
46131 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-07-28 01:15 | 2010-07-28 07:40 | 2010-07-28 | SAFEGUARDS REPORT - DEGRADATION OF SECURITY ALARM MONITORING CAPABILITY Safeguards system degradation related to alarm monitoring capability for which compensatory measures were not immediately employed. Compensatory measures were employed upon identification. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-07-28
46130 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-07-26 15:10 | 2010-07-27 12:04 | 2010-09-03 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following was received via email from the State of Arkansas: "The following are the findings of the Arkansas Department of Health, Radioactive Materials Program, concerning Event Number [AR] 07-10-01 involving a stuck radiography source in Wilburn, Arkansas at a pipeline location. The Department was contacted on July 26, 2010 and informed by the licensee that the incident occurred around 9:30 a.m. on the first shot. The camera involved was an Industrial Nuclear IR-100 (Serial Number 6961) that contained a 34 Curie Iridium-192 source (Model G-40T, Serial Number RC3103). [Source Production and Equipment Company] (SPEC) [- the vendor -] had been contacted and was expected to arrive at the location around 5:00 a.m. on July 27, 2010. In the meantime, the crew and both of the Assistant Radiation Safety Officers maintained constant surveillance. "Health Physicists from the Arkansas Department of Health also went to the incident location. On arrival, it was discovered that the source was in an approximately 10 foot hole and it was indicated that the radiography crew had performed three cranks and then the source would not retract back into the shielded position. SPEC successfully retrieved the source. The source, camera and associated equipment are being transported to the SPEC facility in Louisiana for evaluation. "It appears that this incident may have been caused by the failure of the locking mechanism of the camera. The licensee and SPEC [are] to supply the Department with a written report. "The Department will provide updates as information is received." This is Arkansas Department of Health, Radioactive Materials Program event number 07-10-01. * * * UPDATE FROM KAYLA AVERY TO ERIC SIMPSON AT 0925 EDT ON 9/3/2010 * * * The following report was received via e-mail from the State of Arkansas: "A report received from SPEC states that the cause of the incident was a source misconnect and the source locking mechanism failing to function properly. The report also states that if the camera had been operating properly, the radiographer should not have been able to push the flag down and release the source. There was no evidence of damage to the drive cable connector or to the source assembly. The source was reloaded into the camera and returned to the licensee. "The Arkansas Department of Health considers this incident to be closed." Notified R4DO (Deese) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2010-07-30
46129 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-07-26 20:01 | 2010-07-26 22:45 | 2010-07-26 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM "On 7/26/2010 at 2001 [hrs. CDT], Control Room personnel initiated a manual reactor trip from approximately 19% reactor power. Unit 1 was in the process of coming off-line to support Main Generator repair. The generator breaker had just been opened and load transferred to condenser steam dumps when a loss of condenser vacuum occurred. The reactor was manually tripped due to a loss of main condenser vacuum with reactor power above P-10 permissive. All systems functioned as expected. All control rods fully inserted. Main Steam Isolation valves were manually shut. All reactor coolant system parameters are as expected, with reactor coolant temperature being maintained by atmospheric steam dumps." Currently, the plant is at normal operating temperature and pressure with the steam generators being fed by the main feed pumps. Feedwater is being supplied via the condenser and condensate storage tank. There were no lifts of safeties or reliefs during the transient. The plant is in its normal shutdown electrical line-up with no effect on Unit 2. There is no known primary-to-secondary leakage. The cause of the loss of vacuum is under investigation. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-07-26
46128 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-07-26 11:27 | 2010-07-26 20:46 | 2010-07-26 | 24-HOUR FITNESS-FOR-DUTY REPORT A licensed (not active) employee supervisor had a confirmed positive during a random fitness-for-duty test. The employee's unescorted access has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2010-07-26
46127 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-05-25 13:14 | 2010-07-26 14:18 | 2010-07-26 | 60-DAY OPTIONAL REPORT FOR INADVERTENT SAFETY INJECTION SYSTEM ACTUATION "At 1314 hours [EDT] on May 25, 2010, with the unit defueled during Refueling Outage 26, an inadvertent Safety Injection (SI) Signal occurred. The signal was received when Safeguards Train 'A' breaker DP-A-20 was closed during the performance of procedure PIC-020, 'Time Delay Relay Calibration Safeguards Train 'A'.' The SI Signal resulted in a containment phase 'A' isolation, containment ventilation isolation, control room ventilation transfer to emergency pressurization mode, and Radiation Monitors R-11 and R-12 (Containment Vessel Airborne Particulate and Gas Monitors) isolation. Emergency Bus 1 and Emergency Diesel Generator 'A' were under clearance, including the Train 'A' sequencer. Therefore, automatic loading of the 'A' Train Sequencer did not occur and no actual injection into the reactor vessel occurred. The affected systems actuated as expected. "The cause of the inadvertent SI Signal resulted from SI Initiation Latching Relay SIA1 when power was restored to Safeguards Rack 51. Subsequent investigation determined the SIA1 relay was in an unexpected position (i.e., latched). The SIA1 relay likely became inadvertently latched while performing cable pulls in Safeguards Rack 51 for work associated with Water Cooled Condensing Unit 1A. "Corrective actions include a revision to a procedure to address additional steps to require reset of SI Initiation Latching Relays SIA1 and SIA2 after cleaning and lubrication and development of a planning tool to better assess the risk associated with work being performed [on] plant equipment. In addition, a procedure will be developed for Operations to manually reset safeguards SI Initiation Latching Relays SIA1 and SIA2 prior to restoring system power. These actions are expected to be completed before or on December 16, 2010." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-07-26
46126 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2010-07-24 11:00 | 2010-07-24 16:22 | 2010-07-24 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE On 7/24/10, after doing work in Oklahoma City, an employee of the licensee put a Troxler Model 3440 moisture density gauge in the back of a pick-up truck. The gauge was in its locked case and was locked with a single chain to the truck. When the employee arrived at his destination he found that the gauge was missing. The employee did not notice anything unusual while driving. The licensee searched the route traveled with no results. During the search the licensee informed the police of the missing gauge. The licensee will offer a reward for the proper return of the gauge. The State of Oklahoma is investigating and is formulating a notice to the media on the incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2010-07-28
46125 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-07-23 10:00 | 2010-07-23 17:43 | 2010-07-23 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a presumptive positive based on a failure to report for a random fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2010-07-23
46124 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-06-09 | 2010-07-23 16:59 | 2010-07-23 | AGREEMENT STATE REPORT - HIGHER THAN EXPTECTED DOSE RATE The following information was received from the State via e-mail: "On July 16, 2010, the Agency [Texas Department of State Health Services] was notified by the licensee that they had received notification from their dosimetry processor that an employee's badge had exceeded an annual exposure limit. The event was sent to the Nuclear Material Events Database on July 21, 2010. On July 23, 2010, the licensee reported that while conducting their investigation into the overexposure event, they found that an arrival survey conducted on June 9, 2010, exceeded the allowable limit for a type Yellow II package. "The survey was on receipt of a package containing 494 milliCuries of Fluorine (F) - 18 and indicated that the package was reading 47 milliRem per hour at 1 meter. The dose rate on contact exceeded the measuring capabilities of their instrument. The Service Manager opened the package and found that a vial of F-18 had separated from its shielding. The vial was removed from the package by the Service Manager and taken to an appropriate storage location. A removable radioactive contamination survey was conducted on the package and found to be within the acceptable limits. "The shipper has been notified of the event. This Agency will provide additional information as it is received." Texas Incident #: I-8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-07-28
46123 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-07-23 08:52 | 2010-07-23 16:31 | 2010-07-23 | TEMPORARY OUTAGE OF PUBLIC PROMPT NOTIFICATION SYSTEM DUE TO A BOMB THREAT OFFSITE "The Siren Control Panel at the Houston County Courthouse was unavailable due to a bomb threat [FNP-0-EIP-8.0, step 13.6.3] which caused a loss to the Public Prompt Notification System (i.e. Tone Alert Radio system and the Sirens) for greater than one hour. The bomb threat occurred at 0852 [07/23/10] and Houston County Courthouse evacuation was commenced. Farley Nuclear Plant was notified of the bomb threat and subsequent evacuation at approximately 0945 [07/23/10]. The bomb threat resulted in the Houston County Emergency Management Agency (HCEMA) and the Houston County Sheriff's dispatcher to be evacuated, which resulted in the Alert Notification System (ANS) activation consoles being inaccessible. "The HCEMA office was evacuated at 0915 [07/23/10] and the Houston County Sheriff Dispatcher evacuated at 0925. When Farley Nuclear Plant was notified of the bomb threat, Farley Nuclear Plant Emergency Preparedness personnel were dispatched to the local MET Tower console for ANS actuation (TAR's and Sirens) per approved plant procedures, if required. Farley Nuclear Plant Emergency Preparedness personnel were on station at the MET Tower ANS console at 0959 [07/23/10] with capability to activate the ANS console if required. Farley Nuclear Plant Emergency Preparedness personnel were in contact with HCEMA at 1000 [07/23/10]. "All clear from bomb threat given by Houston County Sheriff's Department and normal access was restored to the HCEMA office at 1100 [07/23/10]. At 1109 [07/23/10] HCEMA notified Farley Nuclear Plant Emergency Preparedness personnel that the HCEMA office was manned and the MET Tower ANS console manning was secured. "During the time that the HCEMA office was unmanned, Alabama Emergency Management Agency (AEMA) was the notification point for HCEMA and that any decision to activate the ANS console could be made by HCEMA by direction of AEMA and then performed by Farley Nuclear Plant Emergency Preparedness personnel. "The total length of time that the Alert Notification System was unavailable was 68 minutes. This was based on the bomb threat and evacuation time at 0852 [07/23/10] until Farley Nuclear Plant Emergency Preparedness personnel were in contact with HCEMA at 1000 [07/23/10]." The licensee notified Alabama and Georgia Emergency Management Agencies as well as Houston County and Early County Management Agencies. The licensee also notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-23
46122 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2010-07-23 13:27 | 2010-07-23 16:32 | 2010-07-23 | 24 HOUR REPORT - DISCOVERY THAT WASTE WATER FILTER PRESS NOT CONFIGURED FOR PASSIVE DESIGN FEATURE "Facility: "Westinghouse Electric Company LLC, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt.% U-235) fuel fabricator for commercial light water reactors. License: SNM-1107. "Time and Date of Event: "July 23, 2010, 1:27 p.m. EST "It was reported to EH&S Management that on July 23, 2010, two filter plates (P1 and P2) in the Integral Fuel Burnable Absorber (IFBA) waste water system filter press were found to be missing pegs utilized in the 'peg-and-hole' passive design of feature SSC-IFBA-MISC-101. The press did not contain more than the allowed four filter press plates. Operations involving the filter press were immediately stopped and EH&S notified of the event by phone and the 'Redbook' reporting system. (Redbook Issue #16126.) The actual configuration remained bounded by the analysis evaluated in the criticality safety calculations and sub-critical margins were not compromised. There was no actual safety consequence to the workers, the public or the environment. "Notification is made based on 10CFR70 Appendix A (b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10CFR70.61.' The potential for an inadvertent criticality event was evaluated in Criticality Safety Evaluation (CSE) CSE-14-C for Miscellaneous Operations in the Integrated Fuel Burnable Absorber Area and the applicable Integrated Safety Analysis for this system. "The CSE evaluated scenario's addressing the installation of the incorrect number or type of filter plates which had the potential to lead to an inadvertent criticality event. These scenarios were determined to be not-credible. Certain safeguards were identified, including SSC-IFBA-MISC-101, to maintain the basic process design of the system. Failure to identify this sequence event was credible led to that event not being included in the ISA Summary and therefore no Items Relied on For Safety (IROFS) were designated for this accident sequence. "Immediate Corrective Actions: "As stated previously, the IFBA area Filter Press operation was shutdown and will remain so until appropriate analysis is completed and IROFS are properly selected and identified. "Similar Filter Press operations in the Uranium Recovery and Recycle System were shutdown and will remain so until appropriate analysis is completed and IROFS are properly selected and identified. "This event has been entered into the Facility Corrective Action Process CAPS#10-204-C012." The licensee will inform the NRC Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.74 APP. A |  |  |  | 0 | 2010-07-23
46121 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-07-22 | 2010-07-23 14:54 | 2010-07-23 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE The following information was received from the State of Pennsylvania via fax: "Event location: Sharon Coatings "Event Type: Shutter Failure "Notifications: A call from the licensee was received July 23, 2010 @ 1410 by the Department of Environmental Protection explaining the event. This falls under 24 hour reporting under 10CFR31.2 and 30.50(b)(2). "Event Description: It was discovered on July 22, 2010 at 15:30 that during a calibration of an ESC Resources (Model #NDS-200, Serial #20938), by the vendor the shutter was stuck open. Vendor was able to make repairs and restore shutter. The device is currently in use. Vendor checked all other gauges and found one other (Model #SH-5000, Serial #80209B), to be stuck as well. Vendor restored both to operational use. "CAUSE OF THE EVENT: Equipment failure "ACTIONS: Both devices have been repaired and restored back to operation" PA Event Report ID No.: PA100017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-07-28
46120 | 0 | HUMBOLDT BAY | 3 |  |  | [3] GE-1 | 2010-06-24 12:00 | 2010-07-23 14:08 | 2010-07-23 | CALIBRATION SOURCE DISCOVERED MISSING DURING INVENTORY "This is a 30-day notification to inform the NRC of missing licensed material in accordance with 10 CFR 20.2201 (a)(1)(ii). "On June 24, 2010, while conducting the quarterly inventory of radioactive sources in accordance with Humboldt Bay Power Plant (HBPP) Unit 3 Radiation Control Procedure RCP-6D, 'INVENTORY AND CONTROLS FOR RADIOACTIVE SOURCES,' it was discovered that source number 498 was missing from the count room. This source is for the calibration of gamma detectors, but had not been used for that purpose this year. The source is a filter, mixed gamma source with an activity of 1.025 microCi as of July 1, 2008. The radionuclide mix of the source is as follows: Gammas/second Activity (Ci) 10 CPR 20 Appendix C (Ci) Am-241 7.02e+02 5.20e-08 1.00e-09 Cd-109 9.80e+02 7.12e-07 1.00e-06 Co-57 5.10e+02 1.61e-08 1.00e-04 Ce-139 7.10e+02 2.39e-08 1.00e-04 Hg-203 1.61e+03 5.63e-08 1.00e-04 Sn-113 1.01e+03 4.19e-08 1.00e-04 Cs-137 6.29e+02 2.00e-08 1.00e-05 Y-88 2.42e+03 6.99e-08 1.00e-05 Co-60 1.18e+03 3.18e-08 1.00e-06 "The above radionuclide composition yields an aggregate quantity of missing licensed material of 53 times the quantity specified in 10 CFR 20 Appendix C, which exceeds which exceeds the 30-day reporting criterion of 10 times the quantity specified in Appendix C. An extensive search has not been successful in locating the source to date, and thus PG&E is making this 30-day notification in accordance with the requirements of 10 CFR 20.2201(a)(1)(ii). "PG&E is continuing to investigate the cause of this event using the Technical Review Group (TRG) process and will provide a written report within 30-days in accordance with the requirements of 10 CFR 20.2201(b)(1)(a)." This material was last accounted for on 4/8/10. The licensee informed NRC Region IV staff. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-07-23
46119 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2010-07-21 15:00 | 2010-07-23 13:13 | 2010-07-23 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT INVOLVING LESS THAN PRESCRIBED DOSE The following information was received from the State of New Mexico via email: "Medical Event was reported 7/23/2010 at 8:39 am by the Radiation Safety Specialist, UNM Radiation Safety Office. "Location: UNM Nuclear Medicine Department 1801 Tucker Avenue Albuquerque, NM 87131 "Medical Event: 7/21/2010 at 3:00 pm, patient written directive order to receive Iodine-131 Therapy treatment 200 mCi (NaI), patient received 80 mCi. "A detailed report will be supplied to State of New Mexico Radiation Control Bureau by UNM RSO within 15 days." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2010-07-29
46118 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2010-07-22 15:30 | 2010-07-22 19:38 | 2010-07-22 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State of Oklahoma reported that on 7/22/10, at about 1530 CDT, a moisture density gauge at a construction site in Orienta, OK south of the intersection of Highway 60 and Highway 412, was run over by a tractor-trailer rig followed by 3 other vehicles. None of the drivers stopped. The road was closed so that the area could be searched to locate the gauge. Initially the source rod (typically containing a Cesium-137 source) was not found after searching the scene. The Oklahoma Department of Transportation (ODOT) was the licensee and owner of the gauge. The ODOT Radiation Safety Officer was contacted. At the time of this report the source rod was located and the RSO determined the source to be intact. A major newspaper in the area posted information on the issue on their website. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2010-07-27
46117 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-07-21 12:00 | 2010-07-22 13:30 | 2010-07-22 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT "Narrative: On 7/21/2010 at 12:00 p.m at the Hot Lab: 17 yr old patient came in for MIRALUMA study. STD dose is 25 mCi of Tc-99m MIRALUMA. Based on patient weight, (105 lbs), pediatric dose is calculated at 17.5 mCi. IV was started by mammography technician. Nuclear medicine technician went to physician to notify about pediatric dose. At this time, mammography technician assayed dose at 24.0 mCi and injected patient. "Reported to the Nevada Radiation Control Program at around 3:00 p.m. "The event is NRC reportable under 10CFR35.3045, since it is a dose different from the prescribed dose. Since 10 CFR 35 has been adopted by the state, it is reportable under state requirements too. "Persons involved: Pediatric patient, mammography technician and nuclear medicine technician. "Corrective Actions: Communication and cross-checking correct dosing especially during pediatric procedures. "Root causes and contributing factors: Haste and the mammography technician not recognizing the fact that the patient was a pediatric patient. "Isotope Details: Tc-99m: 24.0 mCi. "Procedure administered: MIRALUMA study. "Dose intended: 17.5 mCi of Tc-99m "Dose Administered: 24.0 mCi of Tc-99m "Target organ: Breast "Patient Informed: N "% Dose Exceeds Prescribed: 37 "Diagnostic Study: Breast (MIRALUMA study) "Radiopharmaceutical: Tc-99m MIRALUMA "Effect on Patient: UNKNOWN "Source/Radioactive Material: UNSEALED SOURCE RADIOPHARM "Manufacturer: Cardinal Health PSC "Model Number: 190" Nevada Report No.: NV100011 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-07-28
46116 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-06-03 | 2010-07-22 09:24 | 2010-07-22 | AGREEMENT STATE REPORT - POTENTIALLY LOST RADIOACTIVE MATERIAL The following was received via fax from the State of Massachusetts: "On June 3, 2010, two packages containing I-125 seeds were received by the Medical Physicist [MP], who brought them to the radiation oncology hot lab. The MP removed the paperwork and left the packages in the lab while he went back to his office to update the inventory system. He returned to the hot lab to place the cartridges containing the seeds in the vault. He put one cartridge in the vault next to a cartridge that was left over from a canceled treatment. The MP thought that the other cartridge already in the vault was from one of the packages just received, and proceeded to remove the labels from the packages and survey the packages before discarding them. Since the seeds are shielded by a stainless steel cartridge, the survey measurement was indistinguishable from background. The event was discovered by him on Tuesday, June 8, when he was preparing for a treatment and noticed the serial numbers on the cartridges did not match the ones in the inventory system. He reported his findings to the Radiation Safety Officer. The event was reported to Massachusetts Radiation Control Program on Thursday, June 10. "Approximately 43 milliCuries of I-125 seeds were disposed in the clean trash system. Attempts to locate the material in the trash were unsuccessful and they concluded on Tuesday, June 8, that the package had left the premises via the trash." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-07-27
46115 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2010-05-29 08:49 | 2010-07-22 08:32 | 2010-07-22 | INVALID ACTUATION OF PRIMARY CONTAINMENT ISOLATION VALVES DUE TO A FAULTY TRANSISTOR "This report is being made under 10CFR50.73(a)(2)(iv)(A). On May 29,2010, at 0849 EDST Unit 2 received a trip of the 'B' RPS alternate supply. This trip was due to a faulty transistor on the internal circuit board for the voltage regulator. The transistor was replaced, the voltage regulator tested and replaced in the system. The trip of the 'B' RPS alternate supply resulted in isolation of Primary Containment Isolation Valves in more than one system. The systems that were isolated due to this event were Reactor Water Clean-up and Fission Products Monitoring. Except for critical scrams, invalid actuations are not reportable by telephone under º 50.72. NUREG 1022 defines by examples given that actuation of the reactor protection system constitutes actuation of RPS full scram signal when the reactor is critical. In the condition that occurred during day shift on Saturday, May 29, 2010 only one channel of RPS actuated on failure of the Unit 2 'B' RPS alternate supply. That being the case there was not sufficient logic made up to result in a reactor scram or RPS actuation. An RPS actuation would be considered a reportable event; however, the trip of only the 'B' alternate RPS supply would not be considered an RPS actuation. This condition did involve the initiation of some containment isolation signals resulting in containment isolation valves in more than one system since RWCU and fission product monitor isolation valves closing as a result of the loss of the 'B' RPS system. Valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. In this case the isolation signal was caused by the loss of power to the affected instrumentation rather than response to required conditions or parameters which makes this an 'invalid' isolation signal. For this event, Plant Hatch has chosen to make this telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. "All actuations above were complete. "No system actuations resulted from the trip of the 'B' RPS alternate supply." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-07-22
46114 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-07-21 17:30 | 2010-07-21 19:48 | 2010-07-21 | NOTIFICATION OF NORTH CAROLINA WILDLIFE RESOURCES DUE TO STRIPED BASS MORTALITY "Duke Energy Scientific Services group notified the NC [North Carolina] Wildlife Resources Commission that we (McGuire Nuclear Station) were experiencing some Striper mortalities in and around the Cowan's Ford Dam. "Since Monday (7/19/2010) of this week we have collected approximately 100 dead stripers. Some appear to have died from fishing related activities (catch and release) but some were also noted to be stressed from oxygen deprivation. "[The Duke Energy Scientific Services group representative] also notified the NC Wildlife Resources Commission the McGuire Nuclear Station was operating their Low Level Intake [LLI] Pumps to support maintenance of their NPDES Permit 99 degree Fahrenheit average monthly temperature limit. "July has been unusually hot and plant management has felt the need to run the LLI approximately 6 days to achieve compliance with our temperature limit. During the operation of the LLI pumps, Duke Energy's Scientific Services group is monitoring water quality and fish in the lake via the following activities: "1) Daily hydroacoustic surveys of the Cowans Ford Dam forebay both immediate to the dam and also an approximately 2 mile run up the Catawba River channel. "2) Around-the-clock monitoring of fish behavior in the immediate vicinity of the LLI. A DIDSON camera sits atop the LLI (25 meter deep) and is automated to record hourly video of areas both above the LLI and in front of the LLI using motorized rotators. These videos are monitored by [personnel] throughout the day and night. "3) Every other day water quality monitoring including dissolved oxygen and temperature profiles at every meter to the bottom of the lake. These profiles occur in the forebay and at multiple locations up the channel. "4) Daily surveys for dead striped bass by boat up the major tributaries of the lake. We will record lengths and condition of both dead and dying stripers before disposing of them. "5) Hourly MNS discharge temperature monitoring. "These activates will continue to be exercised until the pumps are turned off." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-21
46113 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-07-21 08:16 | 2010-07-21 11:39 | 2010-07-21 | INADVERTENT MANUAL INITIATION OF EMERGENCY ALERT SIRENS "At 0816 [CDT] on 7/21/2010, the Monticello Nuclear Power Generating Plant (MNGP) received a report from the Sherburne County Sheriff Dispatcher that there had been an inadvertent manual initiation of Emergency Preparedness sirens in the county while performing siren testing. All plant conditions/parameters are normal. A total of 48 emergency sirens were on for approximately 1 minute before being secured. The inadvertent initiation of the sirens was determined to be reportable under 10 CFR 50.72(b)(2)(xi), 'News Release or Notification of Other Government Agency.' "Sherburne County, the State of Minnesota, and the site NRC Resident Inspector have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-21
46112 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-07-19 | 2010-07-21 08:30 | 2010-07-21 | AGREEMENT STATE REPORT - PROCESS GAUGE STUCK SHUTTER The following was received via fax from the State of Texas: "On July 20, 2010, the Agency [Texas Department of Health] was notified by the licensee's Radiation Safety Officer (RSO) that while performing a routine test of the shutter on a Ronan Engineering nuclear gauge, the shutter failed to close. The gauge is a model SA-1 serial number 9724 GG containing 10 milliCuries (original activity) of Cesium (Cs) 137 and is used for level detection. The RSO stated that while they were trying to close the shutter, they applied too much pressure to the operating arm, and the operating pin which attaches the arm to the shutter sheared off. The shutter is stuck in the open position, which is the normal operating position for this gauge. The RSO stated that the current radiation level at one foot from the gauge is 0.015 millirem per hour, and presents no additional risk of radiation exposure to any individual. The gauge is located approximately 10 to12 feet off of the ground in an area that is not routinely occupied by individuals. This gauge, along with three additional gauges, are currently only used as a back up system. The RSO believes the gauge was installed in the late 1990s. The RSO stated that they will contact a service provider and either repair the gauge, or dispose of it." Texas Incident # I-8763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-07-26
46111 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-07-20 20:20 | 2010-07-20 23:37 | 2010-07-20 | LOCAL 911 ACTIVATION OF EMERGENCY SIRENS DUE TO POTENTIAL TORNADO IN THE AREA "Exelon Nuclear Peach Bottom Atomic Power Station received notification from the Harford and Cecil County 911 centers that Harford County emergency sirens were intentionally activated due to a potential tornado in the area. The siren activation was due to the tornado and is in no way related to the operation of Exelon Nuclear Peach Bottom Atomic Power Station." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-20
46110 | 0 | GLOBAL X-RAY AND TESTING |  |  |  |  | 2010-06-24 23:59 | 2010-07-20 15:09 | 2010-07-20 | FAILURE TO RETRACT RADIOGRAPHY SOURCE TO SHIELDED POSITION The licensee was performing radiography at the South Timbalier 55 site in the Gulf of Mexico, under an NRC license, when the source failed to retract to the shielded position. They were using a SPEC-150 camera (serial #860) with a 58 Ci Ir-192 source (serial #RC1106). The RSO went to the site and retrieved the source. During the retrieval, there were no overexposures to personnel. The camera was returned to the manufacturer who determined that the pig tail connector failed. The device was repaired by the manufacturer and returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-07-20
46109 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-07-20 08:35 | 2010-07-20 09:26 | 2010-07-21 | FAILURE TO IMPLEMENT REQUIRED SECURITY COMPENSATORY MEASURES "Babcock & Wilcox Nuclear Operations Group (B&W NOG-L) security management was notified and determined on July 20, 2010 at 0835 hrs. that a system degradation had occurred on June 27, 2010 which required compensatory measures that were not initiated per security safeguards procedures. The incident is being reviewed by B&W NOG-L security management. Details of the B&W NOG-L Security Safeguards Procedure are classified as Confidential National Security Information (CNSI). B&W NOG-L security management has placed the event on the internal corrective action system. "A written follow-up report shall be submitted to the NRC within sixty (60) days of the one-hour reportable." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2010-07-21
46108 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2010-07-19 10:30 | 2010-07-19 15:42 | 2010-07-19 | EMERGENCY RESPONSE DATA SYSTEM DISCOVERED TO BE OUT OF SERVICE "At approximately 1230 [EDT] on 07/19/2010, Emergency Preparedness notified OPS that the Emergency Response Data System (ERDS) was found out of service to the NRC. The issue was first discovered at 1030 on 07/19/2010." The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-19
46107 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-07-19 12:00 | 2010-07-19 15:16 | 2010-07-19 | OFFSITE NOTIFICATION TO THE COMMONWEALTH OF PENNSYLVANIA DUE TO TRITIUM DISCOVERED IN PROCESSED WATER "PPL Susquehanna LLC personnel notified the PA DEP Bureau of Water Quality Management that Susquehanna Unit 1 experienced a large leak of river water in the turbine building on 7/16/2010 (reported under EN#46103). Efforts are currently underway to process that water prior to its return to the river. The NRC Resident Inspectors have also been notified. "This notification is in accordance with 10CFR50.72(b)(2)(xi), in that an offsite notification has been completed regarding an event related to the protection of the environment." The licensee reported to the PA DEP since the water that is being processed for return to the river contains less than EPA reportable quantities of tritium. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-19
46106 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-07-18 23:30 | 2010-07-18 23:30 | 2010-07-19 | LOSS OF COMMUNICATIONS CAPABILITY DUE TO PLANNED AT&T FIBER OPTIC CABLE OUTAGE "The notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii) as a Major Loss of Communication. "A planned outage of commercial phone lines is scheduled to occur between 0000 and 0800 on Monday, July 19, [2010]. This outage is allowing AT&T to replace phone lines along one of the local roadways. Even though actual work is estimated to take less than four hours, the outage is scheduled for an eight-hour window. "The impact to the site has been evaluated and the following losses will be experienced. "Outside Commercial Phone Lines ENS Line HPN Line RSCL PMCL ERDS "This condition is reportable as an event that resulted in a loss of offsite communication capability due to the loss of ENS and HPN. The notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii). "Satellite and Mobile phones are available to allow contact with offsite agencies and personnel. Communications between Emergency Response Facilities (Main Control Room, Technical Support Center, and Emergency Operation Facility) are available and will not be affected by the outage. "Information Technology personnel will be at job site and at the plant site during this evolution. "A follow-up notification will be made following restoration of the communications lines. "State and affected Local agencies have been made aware of the pending communication outage. The NRC Resident Inspector has been made aware of the ENS notification." * * * UPDATE FROM PHILLIP PRATER TO VINCE KLCO ON 7/19/10 AT 0407 EDT * * * Notified that planned cable outage is complete. Notified the R3DO (Dickson). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-18
46105 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-07-17 14:07 | 2010-07-18 14:06 | 2010-07-18 | 24 HOUR 91-01 BULLETIN REPORT ON LOSS OF ONE OF TWO CRITICALITY CONTROL CONTINGENCIES "At 1407 CDT, on 07/17/2010 the Plant Shift Superintendent was notified that cracks had been discovered in the C-400 Spray Booth containment pan by Quality Control Inspectors. The floor pan for the spray booth storage tanks, near the hand tables, was found to be inadequate and would allow solution to leak directly onto the concrete floor, in violation of NCSE (Nuclear Criticality Safety Evaluation) 015. The floor pan is a Safety Related Item that is intended to prevent solution from leaking to the concrete floor beneath the floor pan and accumulating in or creating an unsafe geometry/volume. "Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC Bulletin 91-01 Supplement 1. "The process conditions relied upon for double contingency for this scenario are mass and geometry. The first leg of double contingency is based on the mass of uranium in solution form that leaks out of the system. The analysis credits both the integrity of the Spray Booth system and the fact that the tanks and piping are inspected for leakage. Small leaks will be identified and fixed before they have leaked enough uranium mass, in solution form, to be a concern. This control was not violated. "The second leg of double contingency relies on the integrity of the floor pan to prevent accumulated liquids from leaking to the underlying concrete floor and accumulating in unfavorable geometries that may be present or created under the containment pan. Because a portion of the floor pan was discovered to have a hole, the Safety Related Item was violated; therefore, this control was violated. Pressure was placed on the Spray Booth floor pan in the area around the crack. Based on this inspection, there are no indication of unsafe geometry voids being present or having been created under the floor pan. Because the integrity of the floor pan was not maintained, this leg of double contingency is conservatively being considered as having been lost. Double contingency is conservatively considered to have been lost since the integrity of the spray booth storage tank floor pan was lost. "In order for a criticality to be possible, greater than a safe mass of fissile material, in solution form, would have to leak out of the system undetected, leak under the floor pan, dissolve the concrete floor, and accumulate in an unsafe geometry. "While the intended safety function of the Safety Related Item was violated, there was no significant uranium solution leak from the Spray Booth system. Additionally, there are no indications of unsafe geometry voids under the floor pan. "The NRC Senior Resident Inspector has been notified of this event." The crack was characterized as through-wall and approximately 9 inches long. Since the pan is flush to the concrete floor it is mounted on, the licensee does not believe that any material has accumulated under the pan. A preliminary inspection of the pan did not reveal any indication of voiding under the pan. The licensee still has not determined if the pan will be lifted to inspect underneath. The crack was found during an annual inspection of the pan. The cause of the cracking is still under investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2010-07-18
46104 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2010-07-16 21:34 | 2010-07-17 00:51 | 2010-07-17 | OFFSITE NOTIFICATION DUE TO EMERGENCY SIREN INADVERTENTLY ALARMING "At 2134 [CDT] on 7/16/2010 the NextEra Energy Duane Arnold control room was informed that an emergency siren in the Cedar Rapids area was alarming with an emergency message. This information came via a local news station stating that they had been receiving several phone calls regarding the siren message. "No emergency condition existed at NextEra Energy Duane Arnold and the siren appears to have malfunctioned and incidentally relayed the emergency message. NextEra Energy Duane Arnold has informed local media and the Linn County Emergency Director of the malfunctioning siren, and that no emergency condition exists at NextEra Energy Duane Arnold. The single siren (of the 144 total in the local siren system) was deactivated." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-17
46103 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-07-16 16:41 | 2010-07-16 20:03 | 2010-07-16 | MANUAL SCRAM DUE TO UNISOLABLE CIRCULATING WATER SYSTEM LEAK "At approximately 1641 EDT on July 16, 2010, Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to a large unisolable circulating water system leak in the main condenser area. Attempts to isolate the source of the leakage were unsuccessful. During these attempts, reactor operators lowered reactor power from approximately 90% to about 39%. Based on rising water level in the condenser area and unsuccessful isolation of the source of the leakage, Operations decided to shut down the plant. The reactor operator placed the mode switch in shutdown. All control rods [fully] inserted. Reactor water level lowered to -28 inches causing Level 3 (+13 inches) isolations. The Operations crew subsequently maintained reactor water level at the normal operating band using RCIC. No steam relief valves opened. The main steam isolation valves were manually closed and the circulating water system was shut down. Pressure control was initiated using HPCI in the pressure control mode. All safety systems operated as expected. The reactor is currently stable in Mode 3. Actions to isolate and investigate the cause of the circulating water system leakage are underway. Unit 2 continued power operation." The licensee has notified the NRC Resident Inspector, and will be issuing a press release. | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-07-16
46102 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2010-07-02 | 2010-07-16 15:53 | 2010-07-16 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN "On July 2, 2010 it was discovered during the morning walk-through that one exit sign containing 7.5 curies of H-3 [tritium] was stolen. The licensee searched the trash cans and talked with janitorial staff. The sign was not found. A police report was filed with the Alexandria Police Department." Virginia Event Number: VA-10-06 The sign was manufactured by Isolite, model 2040-50B. The sign contained 7.5 Ci at the time of manufacture however, the date of manufacture and thus the current sign activity is not known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2010-07-21
46101 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-07-07 | 2010-07-16 15:44 | 2010-07-23 | AGREEMENT STATE REPORT - DELIVERED DOSE DIFFERED FROM THE PRESCRIBED DOSE BY GREATER THAN 50% The following was received via fax from the Pennsylvania Department of Environmental Protection: "On July 7, 2010 a patient was beginning the first of three vaginal treatment fractions with an Ir-192 HDR. It was discovered on July 14, 2010 that the end of the treatment tube was placed 3.5 cm short of its intended location. When the patient returned for the second treatment, she was imaged again, and staff noticed the treatment tube was in a different location from the previous treatment. Licensee estimates that, for the first fraction, the intended treatment volume received only about 10% of the intended dose for that fraction. Per 10CFR35.3045(a)(1)(iii), it is required for the licensee to report any event in which the fractionated dose delivered differs from the prescribed dose, for a single fraction, by 50% or more. "It is believed the medical staff mis-identified the treatment location and the end of the treatment tube was placed 3.5cm short of its intended location. The licensee is considering making up this dose by adding a fourth treatment fraction. There is no anticipated adverse effect to the patient. "There is a PaDEP/BRP reactive inspection scheduled to investigate this ME at U Penn. The patient and the referring physician were notified. A follow-up written report from the licensee is expected." PA Report # PA100015 * * * UPDATE FROM DAVID ALLARD TO DONG PARK AT 0936 EDT ON 7/23/10 * * * The following was received via fax from the Pennsylvania Department of Environmental Protection: "Due to further information received from the licensee, an amendment is being made to the original sent July 16, 2010, the CAUSE OF THE EVENT has been modified to reflect updated information. "Event Description: On July 7, 2010 a patient was beginning the first of three vaginal treatment fractions with an Ir-192 HDR. It was discovered on July 14, 2010 that the end of the treatment tube was placed 3.5 cm short of its intended location. When the patient returned for the second treatment, she was imaged again, and staff noticed the treatment tube was in a different location from the previous treatment. Licensee estimates that, for the first fraction, the intended treatment volume received only about 10% of the intended dose for that fraction. Per 10CFR35.3045(a)(1)(iii), it is required for the licensee to report any event in which the fractionated dose delivered differs from the prescribed dose, for a single fraction, by 50% or more. "CAUSE OF THE EVENT: The applicator was placed correctly by the medical staff as confirmed by MRI but moved 3.5 cm short of its intended location prior to treatment. The licensee is considering making up this dose by adding a fourth treatment fraction. There is no anticipated adverse effect to the patient. "ACTION: There is a PaDEP/BRP reactive inspection scheduled to investigate this ME at U Penn. The patient and the referring physician were notified. A follow-up written report from the licensee is expected." Notified R1DO (Doerflein) and FSME EO (Villamar). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-07-22
46100 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-07-16 | 2010-07-16 14:16 | 2010-07-16 | AGREEMENT STATE REORT - THIRTEEN TRITIUM EXIT SIGNS LOST The following was received via fax from the NE Division of Radioactive Materials: "Six Isolite model 2040-01-12 Tritium exit signs were shipped to Campbell Soup Company at 333 South 3rd Street in Tecumseh, NE in 1993 with 10 Curies of tritium per sign. Six Evenlite model 201 Tritium exit signs were shipped in 1995 with 12.5 Curies of Tritium per sign. One additional sign from Brandhurst, Inc was shipped in 1986. Isolite, Evenlite and Brandhurst did not provide Nebraska with the serial numbers. MBA Poultry bought the facility from Campbell Soup Company in 1998. MBA Poultry sold it to Tecumseh Poultry in 2000. Tecumseh Poultry does not know where the 13 tritium exit signs went." Manufacturer Activity Model Manufacturer Activity Model 1) Isolite 10.0 Ci 2040 7) Evenlite 12.5 Ci 201 2) Isolite 10.0 Ci 2040 8) Evenlite 13.5 Ci 201 3) Isolite 10.0 Ci 2040 9) Evenlite 12.5 Ci 201 4) Isolite 10.0 Ci 2040 10) Evenlite 12.5 Ci 201 5) Isolite 10.0 Ci 2040 11) Evenlite 12.5 Ci 201 6) Isolite 10.0 Ci 2040 12) Evenlite 12.5 Ci 201 13) Brandhurst unknown 201 Nebraska Report No: NE100001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-07-21
46099 | 0 | MID-PACIFIC TESTING |  |  |  |  | 2010-07-15 15:30 | 2010-07-15 22:07 | 2010-07-15 | DAMAGED MOISTURE DENSITY GAUGE The licensee was using a MC3 moisture density gauge (s/n M38098467) at a construction site in Kauai, HI. During the construction of the Kamualaii road a water truck drove over the gauge and damaged the casing. The source was able to be returned to the shielded position. Licensee is contacting the manufacturer for transporting the MC3 gauge back to them for repair. The radionuclides used with the gauge are 50 mCi of Am-241/Be and 10 mCi of Cs-137. Licensee said they would perform a test for any source leakage. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-07-15
46098 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2010-07-13 | 2010-07-15 18:29 | 2010-07-15 | AGREEMENT STATE REPORT - MISSING BRACHYTHERAPY SOURCES "On July 15, 2010 the Director of Radiological Services at Riverside Medical Center (IL-01242-01), Kankakee, IL called the Agency [Illinois Emergency Management Agency] to advise that they were missing several sealed sources associated with their inactive brachytherapy program. She had been contacted by her radiation safety officer, who made the initial discovery on Tuesday, July 13, 2010. The staff began a visual search the same day. "The Riverside Medical Center Administration was notified the following day and directed that additional searches be conducted of more potential locations as the old storage area had since been demolished as part of a facility remodeling project and the safe could have been relocated to another area of the Medical Center. Housekeeping, Maintenance, Facility Management, Radiology and Security Departments at the Medical Center were directed to take part in the search as well. "Prior to the remodeling, 14 sources of Cs-137 were stored in a lead lined 'safe' which had been locked and secured in a basement storage room of the facility. The new RSO had been in the process of conducting a routine inventory/leak test of the sources when the discovery was made. The key to the safe was still in the possession of the RSO. The 'safe' is approximately 1.5'x1.5'x2.0'. Its weight precludes one or two individuals from removing the safe without additional mechanical assistance. It was marked and labeled with appropriate warning signs. "The specific inventory of sources is as follows with activities corrected as of today's date; 2 sources of 46 milliCi, 4 sources of 31 milliCi, 4 sources of 23 milliCi and 4 sources of 16 milliCi. The manufacturer's safety sheets infers that these sources have a dose rate of 3.6 milliR/h at a distance of 1 foot for each milliCi of activity (46 milliCi; 167 milliR/h). The sources are nickel plated and appear metallic. The radioactivity is doubly encapsulated within stainless steel. Individually the sources are less than a tenth of an inch (3 millimeters) in diameter and less than an inch (20 millimeters) in length. The sources were last used for a medical treatment in October of 2003 but were included in routine inventories and leak tests. The licensee has no information to suggest any nefarious activity associated with the missing storage safe/sources and currently suspects it may have been removed from the site as part of the construction debris associated with last year's remodeling. A consultant has been contracted to perform additional monitoring at their facility with more sensitive radiation instruments in hopes of locating the storage safe. "The Agency [Illinois Emergency Management Agency] is monitoring the licensee's search efforts. Sources of this nature are likely to set off radiation monitor alarms which are established at scrap metal facilities and some landfills however, an intact storage safe with the sources still inside is less likely to set off such alarms, due to its inherent shielding to protect medical staff. Maximum surface readings from the safe as measured previously by Agency personnel during site inspections are approximately 35 milliR/h with readings falling to 0.5 to 2 milliR/h at one foot. All sources were physically confirmed as being present by the Agency during a 2005 inspection." Illinois Report Number: IL10049 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2010-07-20
46096 | 0 | VOGTLE |  |  |  | [1] W-4-LP,[2] W-4-LP | 2010-07-14 13:47 | 2010-07-15 12:59 | 2010-10-12 | FITNESS FOR DUTY PROGRAMMATIC ISSUE APPLICABLE TO CONSTRUCTION UNITS 3 AND 4 "On July 2, 2010, Southern Nuclear Operating Company (SNC) provided a non-emergency event notification (EN# 46067) for an apparent non-compliance with 10 CFR 26.61 relating to self-disclosure requirements. During implementation of corrective actions for that event, Shaw Nuclear Services Inc. (Primary Construction Contractor for Vogtle 3&4) personnel identified that several of the self-disclosure forms received from a sub-contractor had very similar handwriting. An incident investigation was initiated to ascertain the relevant facts. During that investigation, Shaw identified two supervisory personnel from the sub-contractor organization who apparently provided the suspect self-disclosure documents for other employees from their company. Unescorted access for the two supervisory personnel was suspended and they were removed from the site pending completion of the investigation. All suspect self-disclosure forms were removed from the files, and the affected individuals have completed and submitted new self-disclosure forms. No other evidence of policy violations has been identified during this process. The investigation into the FFD event continues. On July 14, 2010, Shaw notified SNC that sufficient indication exists that the actions of the sub-contractor supervisory personnel may have violated the Shaw FFD policy. As such, this issue is reportable in accordance with 10 CFR 26.719(b)(2)(ii), which requires a non-emergency event notification." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1446 ON 10/12/2010 FROM JIM DAVIS TO CHARLES TEAL * * * "On July 15, 2010, Southern Nuclear Operating Company (SNC) provided a non-emergency event notification (EN# 46096) for an apparent violation of the Shaw Fitness for Duty (FFD) policy by two subcontractor supervisory personnel who provided suspect self-disclosure documents for other employees from their company. On October 11, 2010, SNC was notified by Shaw that a third sub-contractor supervisory individual was identified as being involved in the original event reported on July 15, 2010. This supervisory individual has been relieved of duty and removed from Vogtle 3&4 site. The documents affected by this individual were part of the documents identified in the original notification (EN# 46096) made on July 15, 2010. As part of the corrective actions from the root cause investigation into the previously reported events, Shaw has verified that a self-disclosure form has been completed by each individual as required by 10 CFR 26. This notification is being made as an update to EN# 46096 to identify that a third individual was involved in violating the Shaw FFD policy." The licensee notified the NRC Resident Inspector. Notified R4DO (McCoy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2010-07-15
46095 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2010-07-14 | 2010-07-15 10:28 | 2012-10-04 | POTENTIALLY MISSING GENERAL LICENSED GAUGES The following information was received by facsimile: On July 14, 2010, Saint-Gobain Performance Plastics contacted the New Hampshire Department of Health and Human Services and provided notification that an inventory had been completed and three thickness gauges were discovered missing. Saint-Gobain is still trying to locate the gauges. Saint-Gobain is located at 701 Daniel Webster Highway, Merrimack, New Hampshire and possesses the radioactive gauges under a general license. The company is not a specific licensee. The following missing Beta gauges were supplied by NDC: Sensor serial number 3195, equipment number 103 (7441 LX), source assembly date of 11/27/1992, 150 mCi of AM-241; sensor serial number 3108, equipment number 103 (4414 LX), source assembly date of 11/6/1991, 150 mCi of Am-241; sensor serial number 2271, equipment number 102 (1473 LX), source assembly date of 2/26/1990, 150 mCi of Am-241. * * * UPDATE AT 1145 EDT ON 10/04/12 FROM KENNA TO HUFFMAN * * * The State of New Hampshire called to report that two additional Generally Licensed sources were determined to be missing from Saint-Gobain Performance Plastics. On 8/18/10, the licensee could not account for two Polonium-210 static eliminator sources (Serial #'s A2GG-266 & 267). The sources were rated at 5 mCi each. R1DO (Conte) notified. ILTAB (Hahn) and FSME Event Resources informed via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2010-07-20
46094 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-07-14 19:34 | 2010-07-14 19:53 | 2010-07-15 | TECH SPEC SHUTDOWN DUE TO THROUGH WALL FLAWS IN S/G SAMPLE LINE, SECONDARY SIDE "At 1834 hours on 7/14/10, the Unit 1 'C' Reactor Coolant Loop was declared inoperable due to small unisolable leaks on the 'C' Steam Generator secondary side surface sample line. Two small through-wall flaws were identified in the piping upstream of 1 -SS-217, 'C' Steam Generator surface sample line manual isolation valve. The piping is Class 2 and the non-conforming condition could not be evaluated with the steam generator pressurized. Based on the condition of the piping and the inability to evaluate the flaw, the 'C' Steam Generator was declared inoperable per Technical Requirements Manual 3.4.6, ASME Code Class 1, 2 and 3 Components. Subsequently, Technical Specification 3.4.4 was entered to place Unit 1 in Mode 3 within 6 hours. "At 1934 hours on 7/14/10, North Anna Unit 1 initiated a shutdown in accordance with Technical Specification 3.4.4. The unit will be shutdown and the line will be evaluated and repaired." The licensee is presently at 82% power and coasting down in power. All safety systems are fully operable. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM PAUL TRENT TO DONALD NORWOOD AT 0015 HRS ON 7/15/2010 * * * North Anna Unit 1 entered mode 3 at 2353 hrs. There were no complications during shutdown. One source range monitor failed downscale low. The other source range monitor is operating correctly. The failure of this source range monitor did not affect shutdown capabilities. Notified R2DO (Seymour). | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-07-14
46093 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-07-14 13:55 | 2010-07-14 16:37 | 2010-07-14 | TSC OUT OF SERVICE FOR PLANNED MAINTENANCE "Planned preventive maintenance activities are being performed on the Hatch Nuclear Plant's Technical Support Center (TSC) Emergency Ventilation System on July 14, 2010. These maintenance activities include the performance of preventive maintenance on the TSC air handling unit and the TSC condensing unit. These work activities are planned to be completed within the (12) hour day shift on 7/14/2010. "During the time these activities are being performed, the TSC air handling unit, TSC condensing unit, TSC filter train and the fan unit for the TSC filter train will not be available for operation. As such, the TSC HVAC will be rendered non-functional during the performance of this work activity. If an emergency is declared requiring activation of the TSC during the time these work activities are being performed, then the contingency plans call for utilization of the TSC, as long as habitability and radiological conditions allow. Procedure 73EP-EIPÀ063-0, Technical Support Center activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-14
46092 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2010-07-14 07:20 | 2010-07-14 10:06 | 2010-07-14 | POWER LOST TO THE EMERGENCY OPERATIONS FACILITY "At approximately 0720 hours, an offsite 4 kv feeder to the Indian Point Energy Center Emergency Operations Facility (EOF) faulted and power was lost to the EOF. [Power was] restored at approximately 0915 hours. The Alternate Emergency Operations Facility (AEOF) was available during the time the EOF was without power, as were all sirens of the Alert Notification System (ANS). Investigation of the event is in progress." The licensee notified the NRC Resident Inspector and the New York Public Service Commission (PSC). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-14
46091 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-07-13 17:07 | 2010-07-13 22:21 | 2010-07-13 | CONTAINMENT OVERPRESSURE NOT ENSURED IN THE APPENDIX R ANALYSIS "A review of the Appendix R analyses conducted as part of the transition to National Fire Protection Association (NFPA) 805 indicates a potential for the loss of Containment Overpressure (COP) if drywell cooling is not secured or due to fire induced spurious operation of certain primary containment isolation valves. During all Appendix R scenarios, the plant is analyzed to conduct post fire plant cool down with the MSIVs closed, and with Torus cooling provided by the Residual Heat Removal (RHR) system. Based on current design basis calculations, should the containment be depressurized due to a 'smart fire' adequate Net Positive Suction Head (NPSH) may not be available to support Residual Heat Removal (RHR) pump operation during an Appendix R fire event. The design calculations credit COP during Appendix R fire events to provide adequate NPSH to the RHR pumps, as Torus temperature may reach approximately 217 degrees, with a corresponding containment pressure of approximately 10 psig. "There are five scenarios identified where a potential exists for COP loss. One or more of these scenarios could affect several Appendix R analysis areas. The loss of COP could affect safe shutdown capability during an Appendix R fire event. This condition is being reported under 10 CFR 50.72 (b)(3)(ii) as a condition that results in the plant being in an unanalyzed condition which significantly degrades plant safety. "Hourly fire patrols have been established for the susceptible fire areas that do not contain both fire detection and suppression equipment. This includes several areas of the reactor and control buildings. "This issue is a noncompliance with the current design basis, and does not result in the inoperability of any Technical Specification nor Technical Requirements Manual systems." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-07-13
46090 | 0 | U.S. ARMY |  |  |  |  | 2010-07-02 08:00 | 2010-07-13 18:00 | 2010-07-13 | FIRE INVOLVING TWO CHEMICAL DETECTION DEVICES CONTAINING NICKEL-63 An electrical fire consumed a wooden building at Ft. Bragg, NC which housed two chemical detection devices. The first device was an Advanced Chemical Detection Alarm (M22) which contained 20 milliCuries of Ni-63 and the second device was an Improved Chemical Agent Monitor (ICAM) which contained 10 milliCuries of Ni-63. The SSDR numbers for these devices are NR0155-D-125-S and NR0155-D-103-S, respectively. The building was destroyed and the area is covered with a foot of ash. The fire department has not been able to find the devices, and they do not know the configuration of the material. The area is secured and the base RSO is sampling the area for loose surface contamination material. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2010-07-13
46089 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-07-13 08:10 | 2010-07-13 08:15 | 2010-07-13 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0810 EDT on Tuesday, July 13, 2010, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems have been removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 1800 EDT on Tuesday, July 13, 2010. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM DEAN BRUCK TO CHARLES TEAL ON 7/13/10 AT 1730 EDT * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1730 EDT." Notified R3DO (Dickson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-13
46088 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-07-12 19:25 | 2010-07-12 21:38 | 2010-07-12 | SAFEGUARDS REPORT - DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM "Discovered vulnerability in a safeguards system that could allow access to a controlled area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional information." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-07-12
46087 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-07-12 13:10 | 2010-07-12 18:31 | 2010-07-12 | HPCI INADVERTENTLY ISOLATED DURING TESTING "On 07/12/10 at 1310 CDT, while performing 2-SR-3.3.6.1.2(3B), High Pressure Coolant Injection (HPCI) System Steam Supply Low Pressure Functional Test, HPCI inadvertently isolated. The cause of isolation is unknown with an]investigation in progress. HPCI has been returned to standby readiness. "This incident is reportable as an 8-hour ENS notification under 10CFR 50.72 (b)(3)(v) as any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. It also requires a 60 day written report. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-07-12
46086 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-07-12 12:00 | 2010-07-12 17:58 | 2010-07-15 | ELECTRICAL FAULT DISABLED PUBLIC ADDRESS SYSTEM WHICH SUPPORTS VARIOUS ALARM ANNUNCIATORS "At approximately 1200 hours (EST) on 7/12/2010, an electrical fault was identified in the fire alarm system. This fault disabled the public address portion of the system which supports annunciation of plant alarms including the following: fire alarm, criticality alarm, take-cover alarm, [carbon dioxide] discharge alarms. Trouble shooting of the problem is continuing. There is no impact to actual detection, suppression, etc. systems. Compensatory measures include the following: stop SNM handling and movement, fire patrols, restriction of hot work, notification to facility personnel, evacuation of nonessential personnel from production areas, fire brigade on standby and radios provided to fire brigade officers and some fire brigade members. "It is believed that the condition was associated with heavy rainfall and possible water intrusion. "There were no actual safety consequences to workers, the public, or the environment associated with the event. Potential consequences to workers, the public, or the environment are mitigated by compensatory measures." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RANDY SHACKELFORD TO JOHN KNOKE AT 1628 ON 7/15/10 * * * "The public address portion of the plant alarm system was restored on 7/13/2010. It appears that recent rain storms caused some wiring to develop short circuits. These short circuits were corrected. The system is continuing to be monitored and wiring may be identified that requires replacement. It was confirmed that the criticality alarm portion of the plant alarm system was not impacted during the recent outage." The licensee notified the NRC Resident Inspector. Notified R2 DO (Seymour), NMSS EO (Hiltz) , Fuels Grp (Email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2010-07-14
46085 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC. |  |  |  |  | 2010-07-12 | 2010-07-12 10:57 | 2010-07-12 | PART 21 REPORT FOR CERTAIN MODEL 3051N PRESSURE TRANSMITTERS Pursuant to 10 CFR Part 21, section 21.21 (b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that a limited number of Model 3051N pressure transmitters listed in the attachment may exhibit non-linear and non-repeatable performance. The affected transmitters were shipped from RNII between August 12, 2002 and September 27,2006. 1.0 Name and address of the individual providing the information; Mr. Marc D. Bumgarner Vice President & General Manager Rosemount Nuclear Instruments, Inc. 8200 Market Boulevard Chanhassen, MN 55317 2.0 Identification of items supplied: Certain Model 3051N pressure transmitters identified in the attachment. 3.0 Identification of firm supplying the item: Rosemount Nuclear Instruments. Inc. 8200 Market Boulevard Chanhassen, MN 55317 4.0 Nature of the failure and potential safety hazard; The Model 3051N Smart Pressure Transmitter is dedicated for nuclear use consistent with the requirements of 10 CFR Part 21. It is qualified for use in safety related applications per IEEE 323-1983 (mild environment) and IEEE 344À1987 for seismic applications as documented in its associated qualification reports. Procurement and production records indicate that 53 Model 3051N pressure transmitters (Ranges 1, 2 and 3) manufactured between August 2002 and September 2006 have sensor module castings that were not solution annealed, and therefore may contain elevated levels of hydrogen in the sensor module fill fluid. Solution annealing is a heat treatment process for castings. It is used to homogenize the casting by reducing any segregated elements that include carbon, which can greatly reduce corrosion resistance. This process also reduces the level of mobile hydrogen in the casting to a point where out gassing is no longer a reliability concern. Elevated levels of hydrogen in the sensor module casting can create a reliability concern because mobile hydrogen can diffuse through the metal into the sensor module fill fluid and may eventually reach gas solubility limits of the fill fluid. When this occurs, gas vapor bubbles may form, primarily under vacuum process conditions, resulting in a sensor output shift. A transmitter with hydrogen bubbles in the sensor module fill fluid will annunciate itself by exhibiting non-linear and non-repeatable performance. To date, RNII has not received any 3051N field returns for this issue. However, there have been two confirmed failures related to this issue on a commercially available Rosemount product using the identical sensor module casting. Additionally, there have been other confirmed failures related to this issue on a commercially available Rosemount product using a similar, but not identical casting. These commercial grade product returns prompted additional internal testing and analysis that indicated a potential reliability concern on 3051N transmitters that were manufactured with non-solution annealed module castings. As a result, a thorough evaluation was completed and a notification about the potential substantial safety hazard identified on 7/1/10 is being made in accordance with 10 CFR Part 21 to customers that purchased a 3051N pressure transmitter from the potentially affected population. 5.0 The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action: - The last shipment of a 3051N transmitter With a non-solution annealed sensor module casting was September 2006. - Following September 2006, all sensor module castings utilized on the 3051N have been solution annealed. - Procurement drawings for the module castings have been reviewed and the requirement to solution anneal all module castings for a model 3051N transmitter has been verified. - Model 3051N pressure transmitters affected by this notification may be returned to RNII for replacement at no charge. 6.0 Any advice related to the potential failure of the item: The end user is advised to determine the impact of this potential reliability issue upon its plant's operation and safety, and take action as deemed necessary. Affected transmitters may be returned to RNII for replacement at no charge. Rosemount Nuclear Instruments, Inc. is committed to the nuclear industry and remains dedicated to the supply of high quality products to our customers. If you have any questions, or require additional information related to this issue, please contact: Mike Dougherty (208) 865-1112, Gerard Hanson (952) 949-5233, Bob Cleveland (952) 949-5206, or Matt Doyle (952) 949-5204. The attachment provided with this notification identified pressure transmitters delivered to the following power plants: Vermont Yankee (U.S.), Krsko (Slovenia), Santa Marie de Garona (Spain), Kuosheng Nuclear Power Station (Taiwan), and Ulchin 5 and 6 facilities (Korea). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2010-07-12
46084 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-07-12 03:40 | 2010-07-12 03:37 | 2010-07-14 | PLANNED TECHNICAL SUPPORT CENTER OUTAGE "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance being performed on the TSC HVAC. "Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. A 10CFR50.54 (q) evaluation has been performed for this planned maintenance activity." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RICHARD COTTY TO JOHN KNOKE AT 2100 EDT ON 07/14/10 * * * The licensee has completed the required maintenance on the TSC HVAC. The Technical Support Center is now fully functional. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-12
46083 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-07-09 | 2010-07-09 15:55 | 2010-07-20 | OFFSITE NOTIFICATION DUE TO ELEVATED LEVELS OF TRITIUM FOUND IN A WELL SAMPLE "Entergy Pilgrim Station has twelve groundwater monitoring wells used to sample for tritium and other radioactive nuclides in accordance with the Nuclear Energy Institute's (NEI) voluntary Groundwater Protection Initiative (GPI). One of the wells, MW-205, located in the vicinity of the Condensate Storage Tanks (CST) indicated an elevated level of tritium, however well below the limits established by the NEI Groundwater Protection Initiative, the Nuclear Regulatory Commission's (NRC) limits for liquid effluent release and the Environmental Protection Agency's (EPA) limits for tritium in drinking or non-drinking water wells. The latest sample taken on June 21, 2010, returned a test result of 11,072 picocuries per liter of tritium. To date, tritium is the only isotope detected in the samples collected at the site. This information has been communicated to federal, state and local stakeholders and a press advisory is expected to be issued by the Massachusetts Department of Public Health (MDPH). On that basis and the anticipated interest to the general public this notification is being made. "This event has no impact on the health and/or safety of the public. "The NRC Resident Inspector is on-site and has been notified." * * * UPDATE FROM MERT PROBASCO TO HOWIE CROUCH @ 1808 EDT ON 7/20/10 * * * "Entergy Pilgrim Station has received the results of its most recent weekly tritium sample taken on July 7, 2010 for groundwater monitoring well, MW-205. The sample results have shown an increase in the tritium concentration to 25,552 picocuries per liter (pCi/L) from the previous sample taken on June 30, 2010 which had a test result of 8,477 pCi/L. The latest results remain below any regulatory reporting requirements and the Environmental Protection Agency's (EPA) limits for tritium in non-drinking water wells. This information has been communicated to federal, state and local stakeholders. There remains no threat to drinking water sources and no impact on the health and/or safety of the public. "The NRC Resident Inspector is on-site and has been notified of this update. "This is an update to the 4-hour non-emergency notification made in accordance with 50.72(b)(2)(xi) on July 9, 2010 at 1555 hours." Notified R1DO (Doerflein). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-09
46082 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-07-09 | 2010-07-09 12:50 | 2010-07-20 | AGREEMENT STATE - BRACHYTHERAPY TREATMENT DOSE DELIVERED DIFFERS FROM PRESCRIBED The following was received via fax from the State of Wisconsin: "On July 8, 2010, the licensee's Radiation Safety Officer (RSO) reported the preliminary identification of six medical events involving permanent implants of I-125 for prostate brachytherapy where the total dose delivered differs from the prescribed dose by 20% or more. During recent routine inspection, DHS [Department of Health Services] inspectors determined that the licensee was not reviewing prostate brachytherapy cases against the medical event criteria. The licensee is currently evaluating all 269 prostate implants performed since August 2003. This review is ongoing and will include an assessment of whether any implants involved doses to an organ or tissue above 0.50 Sv and 50% more than the expected dose. The licensee is in the process of notifying the affected patients and referring physicians. "The reported medical events involve two locations of use. One facility identified three under doses (74.8%, 75.2%, and 76.5%) and one overdose (121.4%). The second facility identified one under dose (78.2%) and one overdose (121.0%). DHS inspectors are investigating these medical events and will send a special inspection team following completion of the licensee's review" Event Report No.: WI100012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM MEGAN SHOBER TO HOWIE CROUCH VIA FACSIMILE ON 7/20/10 @ 1709 EDT * * * "This is an update to Event Notification 46082. On July 20, 2010, the licensee's Radiation Safety Officer reported the identification of three additional medical events involving permanent implants of I-125 for prostate brachytherapy where the doses to all organ or tissue is above 0.50 Sv and 50% more than the expected dose. The licensee increased the cases reviewed to 275 prostate brachytherapy cases against the medical event criteria. The licensee is in the process of notifying the affected patients and referring physicians. "The three additional medical events were overdoses to the urethra (159.7%, 161.3% and 151.6%). DHS inspectors are investigating these medical events and will send a special inspection team." Notified R3DO (Stone) and FSME (Ries). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-07-15
46081 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-07-09 | 2010-07-09 12:07 | 2010-07-09 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The following was received via email from the state of Texas: "On July 9, 2010, the Agency [Texas Department of Health] was notified by the licensee that one of their technicians had reported that a moisture/density gauge had been stolen from his truck that morning. The gauge is a Humboldt model 5001 EZ (serial # 4438) containing a 40 millicurie Americium (Am) 241 source, and a 10 millicurie Cesium (Cs) 137 source. The technician had completed testing on concrete rebar and returned to his truck. He found the tailgate down and the two locked chains used to secure the gauge in the truck bed had been cut. The gauge and additional equipment were missing. The technician searched the area for the gauge and when he could not find it, contacted the company Radiation Safety Officer (RSO). The RSO stated that the truck was parked in a position where the technician could not see it while he was performing his testing. The RSO contacted Local Law Enforcement and informed them of the event. A reward will be offered for the gauges return. The RSO stated that he will have the technician provide a written report, which he will forward to this Agency [Texas Department of Health]. Additional information will be provided as it is received in accordance with Reporting Material Events - SA-300." Texas Incident #: I-8761 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-07-14
46080 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-07-09 06:47 | 2010-07-09 10:44 | 2010-07-09 | MANUAL REACTOR TRIP DUE TO A FEEDWATER REGULATING VALVE FAILURE "On 07/09/10 at 0647 [CDT] hours, control room personnel initiated a manual reactor trip of Unit 2 from approximately 64% power as a result of a failure of the "A" feedwater regulating valve (FRV). All [other] systems functioned as expected. All rods fully inserted into the core. The unit is stable in MODE 3 at normal RCS [Reactor Coolant System] pressure and temperature. The cause of the FRV failure is being investigated. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The unit electrical power is lined up to offsite power in a normal configuration. Decay heat is being removed from the steam generator through the steam dumps to the main condenser. The FRV failed open and the valve controller was unable to place the FRV into the correct position. The steam generator HI-Hi level provided a feedwater isolation signal and a high level lockout of the FRV. Currently, the feedwater bypass valve is controlling steam generator level. There was no impact on Unit 1. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 64 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-07-09
46079 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-07-08 14:33 | 2010-07-08 16:35 | 2010-07-08 | MATERIAL CONTROL AND ACCOUNTABILITY (MC&A) ALARM ACTUATION "10 CFR 74.57 (f) (2) requires notification within 24 hours that an MC&A alarm resolution procedure has been initiated. The input minus output value exceeded the limit in the Solvent Extraction Area of Building 333. The input minus output value has been resolved. There is no indication that a material loss has occurred. "There were no actual or potential safety consequences to workers, the public, or the environment. "An input minus output process monitoring material balance was calculated for the Building 333 Solvent Extraction Area as specified by applicable procedures and requirements. The input minus output value exceeded the limit. An investigation was initiated." The licensee has notified the NRC Resident Inspector. Similar EN #46064. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2010-07-10
46078 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2010-07-08 | 2010-07-08 15:25 | 2010-07-09 | AGREEMENT STATE REPORT - MISSING THICKNESS GAUGE The following information was received from the Commonwealth of Virginia via email: "On July 8, 2010 the licensee reported a missing thickness gauge, NDC Model 103, serial number 3794. The gauge contains a 150 milliCurie Americium-241 sealed source. The gauge had been in storage for several years and was last visually verified in March 2010. It was discovered to be missing on the morning of July 8th. The licensee stated that the original labels were on the gauge and that the gauge housing was intact. The licensee has initiated a site search and has conducted interviews with personnel." Event Report No.: VA-10-05 * * * UPDATE FROM MICHAEL WELLING TO CHARLES TEAL ON 7/9/10 AT 1559 * * * "On July 9, 2010 a Radiation Safety Specialist from the Virginia Radioactive Materials Program performed an investigation at Polymer Group, Inc.'s site. During the investigation, a radiation survey of the storage location was performed which indicated 20 mrem/hr. Further investigation revealed that the spring on two NDC 103 gamma gauges shutters were not properly working, thus leaving the shutter open. The shutters were placed in their closed position and tape secured over them to ensure their position. A lock was placed on the storage cabinet to ensure further security of the remaining gauges. Polymer Group, Inc. is working with a licensed broker for proper disposal of the remaining 5 gauges. A visual inspection of the facility was performed and all employees were questioned. The gauge remains lost at this time." Notified R1DO (Dimitriadis) and FSME EO (Hsueh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2010-07-13
46077 | 0 | WATERFORD | 3 |  |  | [3] CE | 2010-07-07 14:00 | 2010-07-08 12:23 | 2010-07-08 | ADMINISTRATIVE REVIEW REVEALED FITNESS FOR DUTY PROGRAM ISSUES "Pursuant to Fitness For Duty and Fatigue Rule reporting requirements of 10CFR26.719(b)(2)(ii), Entergy is making this notification associated with violation of Waterford 3 working hour policy. This is a conservative report to proactively document the identified working hour issues. "The site assembled a team for the purpose of reviewing working hours within the Waterford 3 Security Department to determine if the department is in compliance with procedure EN-OM-123 (Fatigue Management Program) and 10 CFR 26 Subpart I (Managing Fatigue). While this comprehensive review is still in progress, two examples have been identified associated with supervisory violations of the Fatigue Rule 'Working Hours.' This report is intended to capture these examples and to encompass any other examples that may be identified during this review process. "The two examples of procedural violations are: "Security supervisor had exceeded the 26 hours maximum in any 48 hour period by working 16 hours on 6/1/2010 and 11.5 hours on 6/2/2010 with no waiver in effect [10CFR26(d)(1)(ii)]. "Security supervisor had exceeded a 9 day period without a 34 hour break during the period of 5/16/2010 to 5/24/2010 with no waiver in effect [10CFR26(d)(2)(ii)]. "Security has verified the current watch bill meets the procedural and regulatory requirements. Security has implemented interim measures for the supervisors to perform a documented validation of work hour management system (PQ&S) data. Condition Report CR-WF3-2010-4156 has been initiated and entered into the Waterford 3 corrective action program. The ongoing comprehensive review will be completed. "Waterford 3 has communicated this issue with the Waterford 3 NRC Senior Resident [Inspector], the NRC Region IV Security Branch Chief, and the NRC NRR Project Manager. "[During] the week of July 26, a follow up call is planned with NRC Region IV associated with the working hour issues." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2010-07-08
46076 | 0 | WAL-MART |  |  |  |  | 2010-06-17 | 2010-07-08 08:26 | 2010-07-08 | GENERAL LICENSE TRITIUM EXIT SIGN MISSING During a remodel of Wal-Mart Store #566 in Boonville, Indiana, the remodeling contractor found one tritium sign. According to the Wal-Mart Radiation Safety Officer (RSO), the sign was an Isolite model with an estimated 11 Curie source strength. The contractor was instructed to properly isolate and store the tritium sign. When a Wal-Mart consultant arrived at the Wal-Mart store to inspect the tritium sign, the sign could not be found in the storage location. Wal-Mart considers the tritium sign to be lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AR | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-07-08
46075 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-07-07 11:17 | 2010-07-07 13:22 | 2010-07-08 | AUTOMATIC REACTOR TRIP CAUSED BY MAIN GENERATOR AND TURBINE TRIP "Salem Unit 1 experienced an automatic reactor trip at 1117 hours due to a trip of the main generator and turbine. The main generator tripped as a result of a fault on the B Main Power Transformer (MPT). The B MPT fire protection deluge system automatically actuated and extinguished a small fire that occurred on the B MPT. The fire existed for approximately 5 minutes prior to being extinguished. "All control rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the Steam Dump system with condenser vacuum maintained. All three AFW [Auxiliary Feed Water] Pumps auto started as expected due to low Steam Generator level. Following the trip, the Reactor Coolant Pump (RCP) thermal barrier supply valve 1CC131 automatically closed and was subsequently reopened with no issue. "Salem Unit 1 is currently in mode 3. The Reactor Coolant System temperature is 547 degrees F with pressure at 2235 psig (NOT and NOP). All ECCS and ESF Systems are available and no ECCS [Emergency Core Cooling System] systems actuated during the event. The 13 AFW pump has not yet been reset following the trip, per the Emergency Operating Procedures and is unavailable. "No personnel injuries occurred as a result of the trip. There is no primary to secondary leakage. There was no impact on Unit 2." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ERIC POWELL TO CHARLES TEAL ON 7/8/10 AT 1535 * * * "Based on additional reviews, the reactor trip occurred at 1118 hours following actuation of the B Main Power Transformer (MPT) fire protection deluge system at 1116 hours. Personnel in the area stated that an arc flash occurred on the high voltage bushing of the B MPT following the deluge system actuation and there was no fire present when the deluge system actuated." Notified the R1DO (Dimitriadis). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-07-07
46074 | 0 | WEST VIRGINIA UNIVERSITY HOSPITAL |  |  |  |  | 2010-01-20 | 2010-07-07 11:37 | 2010-07-07 | MEDICAL TREATMENT TERMINATED PRIOR TO ADMINISTERING FULL DOSE A patient's liver was being treated using SIR-Spheres through a catheter. During the administration of the Y-90 SIR-Spheres, the physician believed that there was leakage around the stopper and halted the medical procedure with only 21.9 mCi administered instead of the complete dose of 30.7 mCi i.e. 71% of the prescribed dose. The manufacturer was notified of the potential manufacturing defect and the hospital was directed to ship the delivery apparatus (as is) back to the manufacturer after the Y-90 had decayed. The equipment was returned to the manufacturer on April 5, 2010 and a report was received from the manufacturer on June 21, 2010. "The manufacturer noted that there was leaking but could not conclude that it was a manufacturer defect or if the physician applied too much pressure to the V-vial during the procedure." The patient was notified of the dose received. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | WV | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-07-13
46073 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2010-07-06 13:05 | 2010-07-06 18:02 | 2010-08-20 | POST CONTINGENCY LOW VOLTAGE ALARM RECEIVED FOR OFFSITE POWER "The Rochester Gas and Electric (RG&E) Energy Control Center (ECC) notified Ginna Operations that the Post Contingency Low Voltage Alarm was received for the offsite power system. Ginna Operations entered procedure O-6.9, Operating Limits for Ginna Station Transmission, and declared the offsite power inoperable per ITS 3.8.1 [72 hour LCO]. Per NUREG-1022, section 3.2.7, if either offsite power or onsite emergency power is unavailable to the plant, it is reportable per 50.72(b)(3)(v)(A) regardless of whether the other system is available. "The RG&E ECC monitors 115 kV voltage using their State Estimation and Contingency Analysis System. The State Estimation portion of the system evaluates real time system power flow and voltages on the 115 and 34.5 kV transmission systems. The Contingency Analysis portion analyzes the voltage effect of a Ginna main generator trip concurrent with worst case accident loading. If the Station 13A voltage would drop below the minimum required voltage for offsite power alignment a Ginna Post Contingency Low Voltage Alarm occurs. "If the main generator should trip, then the absence of a Post Contingency Low Voltage Alarm on the RG&E State Estimation and Contingency Analysis System will ensure that the subsequent offsite 115kV system voltage transient will not result in Ginna Station experiencing an under voltage condition on the 480V Safeguard Busses. "The RG&E ECC notified Ginna operations that the Post Contingency Low Voltage Alarm cleared at 1311 EDST on 07/06/2010. The plant was maintained at 100% steady state conditions throughout the event. Both circuits remain inoperable but available for use. And will be restored to operable status when the system reliability is assured. "The licensee notified the NRC Resident Inspector." * * * RETRACTION AT 0852 ON 8/20/10 FROM DETTMAN TO HUFFMAN * * * "The purpose of this report is to retract the event discussed in ENS report #46071 (July 6, 2010). The ENS report covered an offsite power related event which occurred on July 6, 2010. In this event, both sources of offsite power were declared inoperable following notification to the R.E. Ginna Nuclear Power Plant that the calculated post contingency off-site system voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. "Since the ENS report, an engineering analysis of the event has been completed. The analysis determined that the offsite power system was actually operable at all times on July 6, 2010. The 'Post Contingency Low Voltage Alarm (PCLVA)' computer model that is being utilized by the transmission system provider, Rochester Gas & Electric, to calculate the post contingency offsite system voltage, is inherently conservative in that it assumes the site is relying on a worst case single source of offsite power. However on July 6, 2010, both offsite power sources were available and the site was aligned in the 50/50 Normal offsite power configuration. The engineering analysis calculated the acceptable voltage in this configuration and identified that at no point did the calculated post contingency voltage decrease below the 50/50 Normal offsite power configuration's acceptable value. As such, the July 6, 2010 event is being retracted. "The licensee notified the NRC Resident Inspector." R1DO (Burritt) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-07-06
46072 | 0 | TRENTEC |  |  |  |  | 2010-05-25 | 2010-07-06 12:41 | 2010-07-06 | PART 21 REPORT CONCERNING FAILURE OF OIL-FILLED CAPACITOR The information below is a summary of a report received via facsimile from Trentec dated July 6, 2010. "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: "The basic component containing the defect is a Ronken oil filled capacitor with a rating of 70 micro Farad-660 VAC @ 60 Hz. The part number is P91D23706H05 with a 06-06 date code (manufactured in 2006). The capacitor is commercially dedicated by Trentec for use in safety related applications. The associated Trentec part number is 7T20701 with a 06-06 date code. "Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: "Trentec, Business Unit of Curtiss Wright Flow Control Corporation, 4600 East Tech Drive, Cincinnati, OH 45245 "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: "The defect pertains to 70 micro Farad capacitors that failed in the inverter circuitry for the uninterruptible power supply (UPS) for the turbine driven auxiliary feedwater pump (TDAFWP). The failure of the capacitors was determined by an independent testing lab to be a manufacturing defect in which the internal spot-welded (no solder used) connection points on the capacitors were inadequate and resulted in poor/high resistance connection points which culminated in internal arcing at several of the connection points. "The Auxiliary Feedwater (AFW) system for each unit consists of two motor driven pumps and one turbine driven pump. The TDAFWP UPS for each unit has an A and B section for system redundancy, with two 70 micro Farad capacitors used in each section. The capacitors currently installed in the Farley 1 TDAFWP UPS B section and Farley 2 TDAFWP UPS B section have the suspect date code (total of four). "Given a loss of a TDAFWP UPS due to the capacitor failures, together with a single failure of one of the motor driven AFW pumps leaves the one remaining motor driven AFW pump to ensure the reactor coolant system is properly cooled via the steam generators during emergency conditions. However, two of the three AFW pumps are required to satisfy the flow demand for the most limiting associated design basis accidents and transients, i.e., feedwater line break, main steam line break, and loss of main feedwater. Accordingly, the flow demand is needed to mitigate the consequences of these events which can result in over pressurization of the reactor coolant pressure boundary, and to prevent uncovering the reactor core and potential radiological releases. Additionally, credit for operation of the TDAFWP is needed for coping with a station blackout event during which the TDAFWP is the only source of AFW. "The date on which the information of such defect or failure to comply was obtained: "Farley Condition Report 2010107145 was written on May 25, 2010 to determine 10 CFR 21 reportability of the capacitor failures. Trentec Failure Evaluation Plan was written on 6/7/10. Trentec's capacitor evaluation and report was completed 6/30/10. "In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part: "The Ronken 70 micro Farad capacitors with 06-06 date code have only been supplied to the Farley Plant on PO number QP070496 for a quantity of 8 each, shipped 5/11/2007 with Trentec tag number 7T20701. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: "Corrective actions have been scheduled for Farley Maintenance to replace the suspect 06-06 date code capacitors by July 30, 2010. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: "Perform a failure analysis of any recently failed Trentec qualified Ronken 70 micro Farad capacitor to determine proper corrective action. Replace any Trentec qualified Ronken 70 micro Farad capacitor with a date code of 06-06. They should also be removed from stock to prevent their future use. "In the case of an early site permit, the entities to whom an early site permit was transferred" "Not applicable." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2010-07-06
46071 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2010-05-05 | 2010-07-06 11:17 | 2010-07-06 | AGREEMENT STATE REPORT - PATIENT RECEIVED DOSE LESS THAN PRESCRIBED The following information was received from the State of North Carolina via email: "On 05/05/10, a physician at Iredell Memorial Hospital (NC License 049-0412-2) performed a prostate seed implant procedure. The prescribed dose was 1440 cGray (~1440 REM). After the seeds were implanted, they did a scan and discovered a seed in the urethra. They removed the seed and it was part of a strand of four seeds. "On 05/19/10, the patient returned for a follow-up and had an additional strand of three seeds. The patient said the seeds had come out during urination about a week before. "The patient went through the post-implant CT scan. On 07/02/10, the post-dose calculations were performed. The D-90 actual dose (dose to 90% of the mass) was calculated as 77% of the prescribed dose. "The hospital has made the notification [to the North Carolina Division on Radiation Protection] and is attempting to make the physician and patient notification. A report will be prepared and delivered within 15 days." State Event No.: NC 10-32 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2010-07-12
46070 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-05-17 | 2010-07-06 11:38 | 2010-07-06 | 60 DAY REPORT - INVALID ACTUATION OF HPCI AND RCIC SYSTEMS "Invalid Primary Containment And Vessel Isolation Control System (PCIS) signal results in partial actuation of Emergency Core Cooling System (ECCS) components: "The following information is provided as a sixty (60) day telephone notification to the NRC in accordance with 50.73(a)(1) in lieu of the submittal of a written LER to report a condition that resulted in an invalid actuation of the high pressure coolant injection (HPCI) and reactor core isolation coolant (RCIC) systems. NUREG-1022, Revision 2, identifies the information that needs to be reported as discussed below. "On May 17, 2010, during the Refueling Outage 28 ECCS test control room personnel identified the reactor vessel level was lowering. Valves HPCI-15 and 16 automatically isolated due to an invalid high steam flow isolation signal. The control room personnel immediately started both control rod drive (CRD) pumps as required by procedure. It was determined that the lowering of reactor vessel level was due to water flowing down the HPCI system and RCIC system turbine steam supply lines. The RCIC-15 valve was manually isolated terminating the event. At this time one CRD pump was secured. Acceptable water level in the reactor vessel was maintained throughout the event. The condition has been entered into the Vermont Yankee Nuclear Power Station Corrective Action Program for evaluation and implementation of corrective actions to preclude recurrence. "The high steam flow isolation signal is considered invalid because: 1) At the time of the event, the unit mode switch was in a mode where PCIS was not required; 2) No steam was being generated; and 3) The water flow past differential pressure instrument generated a false high steam flow signal. "The event is being reported in accordance with 50.73(a)(1) and 50.73(a)(2)(iv)(A) as an event or condition that as a result of an invalid initiation signal resulted in the actuation of one or more of the systems listed in paragraph 50.73 (a)(2)(iv)(B)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-07-06
46069 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-07-04 19:30 | 2010-07-04 21:30 | 2010-07-04 | PROBLEM WITH TONE ALERT SYSTEM "At about 1930 on 7/4/10 the control room was notified by the E-plan Duty Officer that the Ames Hill NOAA transmitter (Tone Alert Radio) was inoperable as of 1752 on 7/4/10. "The E-plan Duty Officer has affected repairs and the transmitter is operable as of 2030." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-07-04
46068 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-07-04 11:30 | 2010-07-04 15:16 | 2010-07-04 | TELEPHONE COMMUNICATIONS OUTAGE "At 1130 on 7/4/2010, Station Security contacted Calvert Control Center to notify them of a loss of offsite communication phone lines. Calvert Control Center recognized the loss of phone lines and reported that their phone lines were also out of service. This notification to an offsite government agency is reportable under 50.72(b)(2)(xi) and is a 4 hour ENS report. Security noted the lack of offsite communications at 1122 on 7/4/2010 and communicated this loss of communications to the control room. "The control room verified that the microwave phone system, 800 MHz radio system, plant page, internal phone lines, satellite phone system, Emergency Response Organization Notification System (ERONS) and commercial line to NRC headquarters were still available, this met all of the requirements for contacting offsite agencies in the event of an emergency condition. It was noted that the ENS (dedicated) line to the NRC was not in operation. "Contingency measures were put into place for communications with the NRC (CCNPP can still contact the NRC via commercial lines and the NRC can contact CCNPP via dedicated email and cell phone). The initiating event (loss of offsite communications - specifically the dedicated ENS phone line) which occurred at 1122 is reportable under 50.72(b)(3)(xiii) and is an 8 hour ENS report." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOE KLECHA TO PETE SNYDER ON 7/4/10 AT 1741 * * * DISCOVERY OF AN AFTER-THE-FACT EMERGENCY CONDITION "At 1645, Calvert Cliffs recognized that they were unable to contact St. Mary's County emergency response organization due to a loss of phone communications and radio deficiencies on the counties part. This met the requirement of an Unusual Event in accordance with [EAL] AU 5.1.1 (Unplanned loss of all onsite or offsite communication capabilities). Prior to making the EAL notification, phone communications were restored at 1650 and the conditions of the EAL were no longer met. This report is a one hour ENS notification per 50.72(a)(1)(i) - Declaration of an emergency class, footnote for events which conditions are no longer met." Event classification "Other Unspecified Requirement" was added to the original header for this event concerning the after-the-fact emergency condition discovered by the licensee. Notified R1DO (Powell), NRR EO (Lubinski), and IRD (Grant). | 100 | 85 | 0 | 100 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE | OTHER UNSPEC REQMNT |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2010-07-04
46067 | 0 | VOGTLE |  |  |  | [1] W-4-LP,[2] W-4-LP | 2010-07-01 14:15 | 2010-07-02 14:40 | 2010-07-02 | FITNESS FOR DUTY PROGRAMMATIC ISSUE APPLICABLE TO CONSTRUCTION UNITS 3 AND 4 "An internal audit of a contractors Fitness for Duty program revealed potential non-compliances with elements of 10 CFR 26.61 related to self disclosure requirements. The investigation into the extent of the potential noncompliance continues including whether associated elements of 10 CFR 26.63 are in compliance. Safety related construction activities will be suspended pending resolution and completion of corrective actions. Southern Nuclear Operating Company (SNC) is providing this notification under the provisions of 10 CFR26.719(b)(4)." The licensee will notify the Public Service Commission of Georgia and the NRC Construction Inspection Staff. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2010-07-02
46066 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-07-02 12:32 | 2010-07-02 14:23 | 2010-07-02 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION FROM A LOSS OF POWER TO THE REACTOR PROTECTION SYSTEM (RPS) 3A "This 60 day telephone notification is being made in-lieu of a written report under the requirements specified by 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(1) to describe an invalid actuation of general containment isolation signals affecting more than one system. "On May 12, 2010, at 1232 hours Central Daylight Time (CDT), with Unit 3 operating at 100 percent thermal power the electrical power to the 3A RPS was interrupted during the transfer of the 3A 480V shutdown board from its alternate supply to its normal power supply. During the transfer, the normal breaker did not close for several seconds. This resulted in the interruption of power to the 3A shutdown board which caused the 3A RPS to de-energize, resulting in a half scram and the actuation of PCIS logic Groups 2, 3, 6, and 8, and the initiation of Trains B and C of Standby Gas Treatment, and the initiation of Train A Control Room Emergency Ventilation. "Plant conditions which require PCIS actuations and the associated system initiations (e.g., low reactor water level, high drywell pressure, abnormal area radiation level, or high area temperature) did not exist; therefore, the actuation was invalid. "The affected equipment responded as designed. On May 12, 2010, by approximately 1342 hours CDT, Unit 3 operations personnel restored the 3A RPS power and realigned affected equipment as appropriate. "There were no safety consequences or impact on the health and safety of the public as a result of this event. The event was entered into the corrective actions program as PER 229613. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-07-02
46065 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-07-01 10:30 | 2010-07-02 13:07 | 2010-07-02 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE "[The State of Florida] received [a] report from company's RSO at 1030 hrs today that a soil moisture density gauge and case were stolen yesterday July 1st at 1830 hrs from a truck parked in a lot near the MIC Earlington Heights jobsite in Miami. FL. Thief or thieves apparently used bolt cutters or other device to cut chain used to secure transportation locked box which contained said gauge, then took both transportation box and gauge. Miami-Dade police were contacted (case# PD 100701276792). The licensee will offer a reward for information helping in the recovery. The incident was assigned to the Miami Inspection office for investigation. This office will take no further action on this incident." The Troxler gauge (Model 3440; S/N 23094) contained 40 mCi AmBe and 8 mCi Cs-137. Florida Incident Number: FL10-079 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-07-07
46064 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-07-01 19:18 | 2010-07-01 20:02 | 2010-07-06 | MATERIAL CONTROL AND ACCOUNTABILITY (MC&A) ALARM ACTUATION "10 CFR 74.57(f)(2) requires notification within 24 hours that an MC&A alarm resolution procedure has been initiated. Because the alarm investigation has been initiated, this notification is being made. There is no indication that a material loss has occurred. " Material processing operations related to this alarm have been suspended. The NRC Resident Inspector has been notified. * * * UPDATE FROM RANDY SHACKELFORD TO DONG PARK AT 1509 EDT ON 7/6/10 * * * The investigation from the MC&A alarm resolution procedure has been successfully completed. No material loss occurred, and the alarm was caused by the material being held up in the process. Notified R2DO (Widmann), NMSS EO (Pstrak), and Fuels OUO Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2010-07-08
46063 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2009-10-13 12:07 | 2010-07-01 13:58 | 2010-07-01 | HISTORIC CONDITION WITH CONTAINMENT COOLER FAN RELAYS "[This is a] historical condition previously reported in LER 2009-001 [that] should also have been reported in accordance with 10 CFR 50.72(b)(3)(v)(D). "Due to misapplication of Potter and Brumfield Rotary Relays, both operating Containment Air Cooler Fans were declared inoperable on October 13, 2009, and the fans switched from their normal fast speed alignment to the slow speed alignment used for accidents, which eliminated the relay issue and allowed them to be declared operable. This issue was reported in LER 2009-001 as an operation prohibited by the Technical Specifications on December 14, 2009. The fan control circuitry was modified to correct the condition. "Upon further review, this condition should have been reported per the requirements of 10 CFR 50.72(b)(3)(v)(D) due to both required Containment Air Cooler Fan trains being declared inoperable for the condition. A revision to LER 2009-001 will be submitted per 10 CFR 50.73(a)(2)(v)(D). "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-07-01
46062 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2010-07-01 09:03 | 2010-07-01 11:23 | 2010-07-01 | ONSITE LEAK FROM CONDENSATE STORE TANK RESULTING IN LOCALIZED TRITIUM CONTAMINATION "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of the Illinois Emergency Management Agency (IEMA) and the Illinois Environmental Protection Agency (IEPA) of an unpermitted release of radionuclides at LaSalle County Station. This notification was made at 0903 on July 1, 2010. A news release is planned, which is also reportable under 10 CFR 50.72(b)(2)(xi), this notification satisfies the additional reporting requirement. "On June 30, 2010, a small leak of radioactive water from the Unit 1 Cycled Condensate Storage (CY) Tank to the ground was confirmed by analysis of water from an adjacent groundwater test well. The IEMA / IEPA require notification when a release to soil, groundwater or surface water results in tritium concentrations of 200 pCi/I or more outside the licensee controlled area, or contains tritium at quantities of 0.002 Curies or more on-site. Positive groundwater test well sample result was obtained at 1800 on June 30, 2010 from the well adjacent to the Cycled Condensate Storage Tank. Samples found a tritium concentration of 715,000 pCi/I, with a confirmatory sample result of 696,000 pCi/I. The concentration of tritium in the sampled well makes it likely that the release is in excess of 0.002 Curies. "Based on sampling data obtained to date, the tritium in the groundwater is confined to Exelon property and poses no threat to public safety. The Station continues to track this issue by monitoring groundwater test wells. Plans to repair the leak in the Unit 1 CY tank are in progress." The licensee has notified the NRC Resident Inspector and State authorities. The licensee also plans to notify authorities and will be issuing a press release. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-07-01
46061 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-06-24 12:00 | 2010-07-01 10:23 | 2010-07-01 | AGREEMENT STATE REPORT INVOLVING A FOUND RA-226 SOURCE "[A] transfer station for waste disposal detected radioactive material contained in a roll-off container with other debris. [The] debris came from a house clean-out job in Newton Corners, MA. [The] transfer station called Holliston Fire Department who responded with survey instruments capable of identifying radioactive material (RAM). [The]RAM was identified as Ra-226 contained in a device that appeared to be from a WWII vintage aircraft. "[The] Agency sent an inspector to verify description of RAM trash. [The] inspector confirmed the RAM is Ra-226 contained in an aircraft leveling device. [The] inspector placed the device in a plastic container and sealed [it] with radioactive warning tape. The external dose rate measured 0.1 mR/ hr. The plastic container was placed in secure storage awaiting disposition of RAM. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-07-06
46060 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2009-07-01 | 2010-07-01 09:27 | 2010-07-01 | PART 21 REPORT CONCERNING FAILURE OF TURBINE OVERSPEED RESET CONTROL VALVE DIAPHRAGM The information below is a summary of a report received via facsimile from GE Hitachi; Report MFN 10-192 dated July 1, 2010. Background: "A diaphragm used in a 1" HPCI turbine stop valve / mechanical trip hold valve operator failed at a domestic BWR 4 in July 2009. The failure resulted in a HPCI turbine lube oil leak, which was the indication that the diaphragm had failed. The BWR 4 plant completed an Apparent Cause Evaluation and concluded that a material defect in the diaphragm allowed the diaphragm to tear after being installed for 2 years 8 months." "The diaphragm that failed was a Robertshaw (RS) part number 25471-A2, and was installed in a Robertshaw model VC-210 diaphragm control valve operator. The diaphragm was made from Buna-n rubber and was designed to have two layers of Dacron reinforcement fabric over all pressure bearing surface areas of the diaphragm. The diaphragms are manufactured by Chicago-Allis using a 2-plate compression mold process." "The diaphragms are purchased as commercial grade and are dedicated by GEH and supplied as safety related under GE part number Q25471-A2. The failed diaphragm was manufactured in 2006." Discussion: "Reinforcement fabric is considered a critical design requirement that is essential to ensure durability, reliability, and prevents tearing of the diaphragm material when these diaphragms are used in the HPCI turbine lube oil system as turbine trip and reset valves." "An inspection was performed on six diaphragms, three manufactured in 2006 and three manufactured in 2008. All six of these diaphragms were found to have areas without fabric reinforcement. Inspection of the three samples from 2006 found non-uniform reinforcement. Inspection of the three samples from 2008 found all diaphragms were void of reinforcement in the sidewalls and inspection indicates that the reinforcement fabric was torn away from the inner sidewall during the manufacturing process. The inspections identified no diaphragms that were in full compliance with the design requirements for two layers of reinforcing fabric over all pressure bearing surfaces of the diaphragm." Safety Analysis: "The failure of the HPCI turbine over-speed reset control valve's diaphragm would result in a loss of HPCI turbine lube and control oil through the failed diaphragm. Depending on the amount of oil lost and the system demands, this loss could ultimately result in a failure of the HPCI System. Failure is not imminent, but cannot be precluded. Other safety related equipment is sufficient to mitigate design basis events in the event of a loss of HPCI." Conclusion: "Because of the similarity of the defects in all diaphragms inspected, it is credible to believe that this type of deviation from technical requirement also exists in other diaphragms manufactured by Chicago Allis and sold by GE as part number Q25471-A2 and 25471-A2Q, and as part of Control Valve Assembly DD233A3600P001. The identified defective diaphragms were present in two lots; one manufactured in 2006 and one in 2008. Based on the observations it is reasonable to believe that other diaphragms manufactured in 2006 and 2008 have similar deviations. GEH has been unable to determine if the identified manufacturing deviation exists in diaphragms manufactured prior to 2006. Since GEH is not able to rule out defects in diaphragms manufactured prior to 2006, it is credible to believe that similar deviations existed in diaphragms manufactured prior to 2006. In order to determine the possible extent of condition, all diaphragms in service or in stock at plants as spare parts inventory are suspect. Since the diaphragms have a designated service life of 5 years, and a shelf life of 10 years, the extent of condition is bounded by replacement of all diaphragms purchased by plants since 1995." "GEH has evaluated the consequences of the failure of this diaphragm and concluded that this type of failure could result in the HPCI system not performing its safety function. The HPCI system is considered an essential safety related system. Failure of the HPCI system is considered a major degradation of essential safety related equipment. Therefore this condition is determined to be a Substantial Safety Hazard and is a Reportable condition per 10CFR Part 21." Recommended Action: "GEH has evaluated the consequences of the failure of this diaphragm and concluded that this type of failure could result in the HPCI system not performing its safety function. The HPCI system is considered an essential safety related system. Failure of the HPCI system is considered a major degradation of essential safety related equipment. Therefore this condition is determined to be a Substantial Safety Hazard and is a Reportable condition per 10CFR Part 21." US Plants With Affected Diaphragms: Fermi 2 Limerick Peach Bottom Duane Arnold Cooper Susquehanna Brunswick Hatch Browns Ferry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-07-01
46059 | 0 | 3M COMPANY - ST. PAUL, MN |  |  |  |  | 2010-06-30 10:00 | 2010-07-01 09:07 | 2010-07-01 | SAFETY EQUIPMENT MALFUNCTION - SHUTTER STUCK ON NUCLEAR GAUGE "At approximately 10 AM on June 30 an operator at the 3M Springfield plant determined that the shutter of an LFE beta gauge was not closing. This was reported to supervision and subsequently to the Radiation Safety Officer. The gauge is otherwise functioning normally and has been posted as having an open shutter. A licensed service provider has been contacted to make repairs, scheduled for end of the day, July 1. "The gauge is an LFE model SULP-77A, serial number OS-713. The source is a 1 Curie Kr-85 sealed source dated 1/8/2007. "The 3M facility is located at 3211 E. Chestnut Expressway, Springfield MO 65802. "There has been no personnel exposure as a result of the stuck shutter." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-07-01
46058 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-06-30 11:00 | 2010-06-30 16:04 | 2010-06-30 | AGREEMENT STATE REPORT - SHUTTER ON FIXED INDUSTRIAL GAUGE FAILED TO CLOSE The following report was received via fax from the State of Nebraska: "The licensee uses fixed industrial gauges for measuring densities in flyash hoppers at the Stations precipitator building. The Industrial gauges contain a Cesium 137 sealed source. The Cesium 137 sources were originally installed in 1984 and at the time contained 50 millicuries per source. The sources were manufactured and installed by Kay Ray Inc. The gauge housing Model No. is 7080. "The licensee was performing the semi-annual 'Shutter Function Test' on Unit #4's precipitator sources. The 'external' source closure mechanism for the 4FA-1B & 2B hoppers did not operate as designed and the shutter did not close when the handle on the floor was operated. The external closure cable had detached from the cable clamp on the side of the hopper. In this condition, when the shutter closure mechanism was moved, the cable that operates the source shutter mechanism 20 feet above the floor, bent instead of sliding the cable to the closed position. No personnel were exposed to radiation during this event. "This was the fourth similar event at the licensee's plant (March 25, 27, May 6, & June 30, 2010). On June 17, a NE DHHS (Nebraska Department of Health and Human Services), Radioactive Material inspector performed a follow-up investigation on-site. At this plant, OPPD (Omaha Public Power District) has 58 installed operating nuclear fixed gauges. At the time of the investigation, OPPD had replaced 20 of the old shutter cables with a new redesigned direct replacement cable. OPPD plans to replace all of the 58 shutter cables when they fail to operate or as time permits." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-07-05
46057 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-06-30 09:55 | 2010-06-30 16:03 | 2010-06-30 | OFFSITE NOTIFICATION DUE TO SULFURIC ACID SPILL ONSITE "At 0955 on June 30, 2010, the Control Room was notified that sulfuric acid was leaking from a temporary acid containment berm onto a gravel surface area adjacent to the containment berm. The quantity of this leak was <5 gallons of approximately 93% concentrated sulfuric acid. The leak was in the non-radiologically controlled area of the plant, associated with a temporary acid injection system for cooling tower water treatment. "Spill response personnel responded to contain and neutralize the leakage. No material was directly released to any waterway or offsite area. The quantity of material released is below any environmental regulatory limits. Actions are ongoing in removal of the acid from the leaking tank inside the containment berm area. An offsite company with expertise in the handling of this material has been contacted and will be providing assistance with the response efforts. "A courtesy call was made to the Pennsylvania Emergency Management Agency for an event of potential public interest at 1530 on June 30, 2010." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-30
46056 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2010-06-30 09:10 | 2010-06-30 15:37 | 2010-06-30 | FITNESS FOR DUTY REPORT - CONFIRMED POSITIVE TEST FOR ALCOHOL A licensed senior operator had a confirmed positive test for alcohol during a random test. The employees access has been suspended. Contact the headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2010-06-30
46055 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-06-28 20:35 | 2010-06-29 17:20 | 2010-06-29 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DESTROYED IN FIRE The following report was received via fax from the State of Wisconsin: "On June 28, 2010 at 20:35 the Department of Health Services (DHS) on-call State Radiological Coordinator (SRC) was informed that there had been a fire involving two trailers at the Dodge Concrete Ready Mix plant, W6298 US Hwy 18, Jefferson, WI. One of the trailers contained a Troxler 3440 portable moisture density gauge owned by Tetra Tech, a Wisconsin Radioactive Materials Licensee who was performing licensed activities at the concrete plant. The gauge contains a maximum of 9 milliCuries of Cesium-137 and 44 milliCuries of Americium-241:Beryllium as radioactive sealed sources. The original call to the DHS 24 hour emergency hotline was made by the Tetra Tech Radiation Safety Officer (RSO). "The SRC subsequently received a page from the Wisconsin Emergency Management (WEM) Duty Officer at 20:45. The Duty Officer explained to the SRC that he had been informed of a fire in Jefferson, (WI) involving two burning trailers involving radioactive material. The SRC informed the duty officer that DHS intended on following up on the incident and would provide additional information. "The SRC then contacted the licensee RSO. The RSO was at the scene of the fire interacting with the fire department. He (RSO) indicated that a fire had consumed two of their job trailers at Dodge Ready Mix and that one trailer contained a portable gauge which housed both a Cs-137 and an Am-241/Be radioactive source. The RSO indicated that radiation surveys around the trailer indicated radiation levels of less than 1 mR/hr around the burned trailer containing the gauge. After the RSO proposed his course of action to the SRC, they agreed that it was unsafe to attempt to extract the gauge from the trailer in the dark. The RSO cordoned off the trailer with yellow "Caution-Do Not Enter" tape pending an attempt to extract the gauge the following morning. All of the licensee's proper radiation postings and equipment were also destroyed in the fire. All postings and labels on the gauge transport container and the gauge itself were destroyed. DHS informed the RSO that they would arrive at the scene of the fire the next morning to supervise the extraction and provide technical radiation safety support. "DHS investigators arrived at Dodge Ready Mix in Jefferson, Wl at 09:30. The Tetra Tech RSO and Authorized Users (AU) were present. Both trailers were completely destroyed by the fire and the gauge housing, transport case and associated equipment were melted together and fused to the trailer floor. The melted plastic, gauge and trailer housing had to be removed as a block. The maximum radiation level was ~8 mR/hr near contact with the Cs-137 shielding, which appeared to be intact. The radiation levels indicated that the shielding for both sources had retained its integrity. Contamination wipes were taken on the source rod, source shielding and the source exit point. No evidence of contamination was found. The DHS investigators were informed that the fire department had moved the trailers away from the site garage to reduce the risk of the fire spreading. All debris, trailers and trailer sites were surveyed. No elevated radiation levels were found. These surveys gave the DHS investigators and RSO confidence that the source remained in the fully shielded position. "After consulting with Troxler, the gauge manufacturer, the RSO decided to remove the melted plastic and debris from the gauge remnants so it could be transported and shipped back to Troxler in a standard transport case. The licensee succeeded in removing the debris and melted plastic and at 12:45 was able to package the gauge in the Type-A transport container for return to their office in Wausau. The gauge was to be leak tested prior to shipment to Troxler for disposal. All debris removed from the gauge and the gauge itself was surveyed for contamination and radiation levels. The maximum radiation level remained at ~8 mR/hr and no evidence of contamination was found. The transport index was consistent with what the RSO typically finds with an intact gauge." Event Report ID: WI100011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-07-02
46054 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-04-30 16:48 | 2010-06-29 15:25 | 2010-06-29 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION FROM A LOSS-OF-POWER TO REACTOR PROTECTION SYSTEM (RPS) 1A "This 60-day telephone notification is being made in lieu of a written report, under reporting requirements specified by 10 CFR 50.73(a)(1), 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of general containment isolation signals affecting more than one system. "On April 30, 2010, at 1648 hours Central Daylight Time (CDT) with Unit 1 at 100 percent thermal power, while attempting to change a light bulb, the light socket shorted causing a loss of 1A RPS. The loss resulted in Groups 2, 3, 6, and 8 primary containment isolations, and initiation of Standby Gas Treatment and Control Room Emergency Ventilation. BFN's review of the event found that the bulb caused a direct short and caused the loss of RPS 1A. Plant conditions which require PCIS actuations and system initiations (e.g., low reactor water level, high drywall pressure, abnormal area radiation level, high area temperature) did not exist, therefore the actuation was invalid. "The affected equipment responded as designed. On April 30, 2010, at approximately 1702 hours CDT Unit 1 operations personnel restored 1A RPS and by 1728 hours CDT, the recovery of the loss of 1A RPS was complete. This event had no safety consequences or impact on the health and safety of the public. The event is documented in the Corrective Action Program (PER 227662). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-06-29
46053 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-06-29 09:55 | 2010-06-29 13:55 | 2010-06-29 | FITNESS FOR DUTY - LICENSED EMPLOYEE CONFIRMED POSITIVE FOR ALCOHOL "A non-supervisory licensed employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been denied. The individual had not entered the protected area and had not performed any licensed duties prior to the event. "The licensee notified the NRC Resident Inspector at 1053 hours." | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2010-06-29
46052 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-06-29 01:00 | 2010-06-29 13:04 | 2010-06-29 | LOCK MALFUNCTION ON A RADIOGRAPHY CAMERA "On June 29th [at approximately 0100], the radiography crew working the Alpine Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an Industrial Nuclear Corporation (INC) IR-100 exposure device (serial number 4814). "During the night shift the locking mechanism on the exposure device would not operate properly. When the locking latch was depressed the source could not be moved to the exposed position. When retract pressure was applied, the locking device would not 'pop up', it had to be moved manually. The source never left the safe and secure position. The trained radiographer who can work on the locking mechanism decided that the camera would be tagged out and returned to the manufacturer for repair. The camera will be shipped [on today]. "There was no exposure to the crew or the General Public during this incident." The IR-100 unit uses a 52 Curie Ir-192 source. Source S/N: P311. The licensee has informed Region 4. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-06-29
46051 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-06-29 | 2010-06-29 12:50 | 2010-06-29 | SOURCE LOCKING MALFUNCTION OF RADIOGRAPHY CAMERA "On June 29th [at approximately midnight], the radiography crew working the Alpine Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an Industrial Nuclear Corporation (INC) IR-100 exposure device (serial number 6757). "During the night shift the locking mechanism tripped prematurely. A survey of the exposure device did not reveal any abnormal readings. When the crank assembly was disconnected it was noted that the pigtail was not in the proper position. A trained technician removed the locking assembly and cleaned dirt from the locking assembly. The exposure device was reassembled with the source in the safe and secure position. "There was no exposure to the crew or the General Public during this incident." The IR-100 device uses a 60 Curie Ir-192 source. Source S/N: P344. The licensee has informed Region 4. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-06-29
46050 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2010-06-28 08:00 | 2010-06-28 17:23 | 2010-07-01 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following report was received via email from the State of Oklahoma: "On June 28, 2010, the Oklahoma Department of Environmental Quality (ODEQ) received notification from Standard Testing and Engineering Company (Standard) of Oklahoma City operating under license number OK-17054-03 that one of Standard's nuclear gauges was stolen from the home of an employee living in Tulsa, OK. The gauge is a Troxler Model 3411B moisture/density gauge, serial number 16968. The gauge contained a 0.30 GBq 137-Cs source serial number 506707 and a 1.48 GBq 241-Am source serial number 4712391. Standard stated that it is against company policy to store gauges at employee residences and that the employee has been terminated. It is unclear at this time if the gauge was properly stored within the gauge restraints that are installed in all Standard company vehicles. "There is no reason to believe that this is anything other than a common theft. The licensee has notified local law enforcement. The ODEQ is notifying the FBI. The company has not issued a press release. ODEQ will seek to either issue a press release, or have the company issue a press release to help raise public awareness of the appearance of the gauge and the level of risk it poses, in case it is abandoned in a public place." * * * UPDATE FROM MIKE BRODERICK TO JOE O'HARA VIA EMAIL AT 1724 ON 7/1/10 * * * "The portable gauge reported stolen on June 28th at approximately 4:15 PM has been recovered. A citizen contacted a company that provides services to portable gauge users, and the company contacted Oklahoma DEQ and provided us with information to contact the citizen. We [OK DEQ] placed the licensee in contact with the person who had found the gauge, and the gauge was recovered at about 11 AM on June 30. The gauge appears to be undamaged. Notified R4DO(Lantz), FSME EO(Luehman), and ILTAB via email THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2010-07-01
46049 | 0 | SOUTH CAROLINA DEPARTMENT OF HEALTH |  |  |  |  | 2010-06-28 08:00 | 2010-06-28 10:58 | 2010-06-28 | AGREEMENT STATE - MOISTURE DENSITY GAUGE STOLEN FROM JOB SITE The following information was received from the State of South Carolina via fax: "The South Carolina Department of Health and Environmental Control (SC DHEC) was notified on Monday, June 28, 2010 at 8:00 a.m. that a Humboldt Model 5001 B, SN 2508, portable moisture density gauge had been stolen from a job site storage unit in North Charleston, SC. The gauge contained 11 milliCuries maximum of Cesium 137 and 44 milliCuries maximum of Americium 241:Be. [An] F&ME employee, notified the SC DHEC that a gauge technician arrived for work Monday morning and discovered that the job site storage trailer had been broken into. [The site RSO] was notified immediately and he in turn called local police and fire department personnel. He also notified SC DHEC of the occurrence. The RSO indicated that the trailer had been secured on Friday evening (June 25) with the gauge locked in its storage container in the locked storage cabinet within the trailer. No work was performed over the weekend. The theft was discovered, as outlined above, early Monday morning. There were a few other items stolen as well - a GPS unit and a computer. An inventory was still underway at the time of this notification. The local police responders were made well aware of what type of gauge this was and were in the process of filling out the police report. The RSO was advised to fax the police report to SC DHEC once he obtained it." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2010-07-01
46048 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2010-06-25 20:24 | 2010-06-26 06:07 | 2010-06-26 | HPCS INOPERABLE "At 2024 CDT on 6/25/2010, HVR-UC5, HPCS [High Pressure Core Spray] Pump Room Cooler was secured due to high vibration reported [by the] field operator [which was caused by] rubbing on the fan motor shroud. The HPCS system remains available for auto initiation but inoperable due to securing the support equipment." The licensee will notify the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-06-26
46047 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-06-25 14:27 | 2010-06-25 18:37 | 2010-06-25 | HAZMAT SPILL REQUIRING OFFSITE NOTIFICATIONS "On Friday, June 25, 2010, at about 1235 PDT, Southern California Edison (SCE) spilled about 25 gallons of Ethanolamine (ETA) while filling the ETA bins from the ETA bulk container. The spill occurred at the SONGS MESA Hazmat pad. Approximately 23 gallons remained inside the hazmat berm; approximately 2 gallons were spilled and contained outside the berm. The SONGS Hazardous Materials personnel are in the process of removing the ETA for disposal. "ETA is used to control secondary side chemistry. "SCE completed notification of the San Diego County Department of Environmental Health, the California Emergency Management Agency (CalEMA) and the National Response Center (Incident # 945486) by 1427 PDT. "SCE is making this notification in accordance with 10CFR50.72(b)(2)(xi). "At the time of this report, SONGS Units 2 and 3 are at 100% power. The NRC Senior Resident Inspector has been notified of this occurrence and will be provided with a copy of this report." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-25
46046 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-04-27 17:37 | 2010-06-25 16:32 | 2010-06-25 | INVALID GROUP 6 CONTAINMENT ISOLATION "This notification is being made in lieu of a written report under the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a Group 6 containment isolation signal affecting more than one system. "On April 27, 2010, at 1737 hours Central Daylight Time, with Unit 3 operating at 100 percent thermal power, Unit 3 received a Group 6 ventilation system isolation signal during the performance of a maintenance activity on a Unit 3 Reactor/Refuel Zone Radiation Monitor, 3 RM-90-141/143. This resulted in isolation of the reactor and refuel zone ventilation systems, initiation of Standby Gas Treatment system (Trains A, B, and C) and the Control Room Emergency Ventilation system (Train A). "All equipment responded to the Group 6 ventilation system isolation signal in accordance with the plant design. However, during the recovery effort, one of the Unit 3 Reactor Building Ventilation dampers failed to indicate fully closed. Operations personnel verified by inspection that the damper was fully closed. "There were no safety consequences or impact on the health and safety of the public as a result of this event. The event was entered into the Corrective Action Program (CAP) as PER 227125. "From PER 227125, trouble shooting determined a relay coil had been installed upside down when the coils were recently replaced. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-06-25
46045 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-06-24 14:34 | 2010-06-24 21:34 | 2010-06-27 | INSTRUMENT BUSES 3 AND 8 FAILED CAUSING CLOSURE OF RHR VALVES "At 14:34 hours on June 24, 2010, with the unit in MODE 5, Cold Shutdown, with approximately 50% pressurizer level, during Refueling Outage 26, Instrument Buses 3 and 8 unexpectedly de-energized during performance of testing in accordance with procedure OST-163, 'Safety Injection Test and Emergency Diesel Generator Auto Start on Loss of Power and Safety Injection.' The loss of Instrument Buses 3 and 8 occurred during the loss of power and Safety Injection testing of the 'A' Train. "Instrument Buses 3 and 8 are normally powered from Inverter 'B' which is normally supplied by the Train 'B' DC Bus. During the test, it was noted that the power supply to Instrument Buses 3 and 8 had tripped. The cause of the failure of Inverter 'B' is not currently known. The failure of inverter 'B' caused the closure of the Residual Heat Removal (RHR) Heat Exchanger discharge valve (HCV-758) and the RHR Heat Exchanger bypass valve (FCV-605). "Both trains of RHR continued to operate and reactor coolant system temperature remained in the range of approximately 93 to 96 degrees Fahrenheit. Abnormal Operating Procedure AOP-020, 'Loss of Residual Heat Removal (Shutdown Cooling)' was entered. Power was restored to Instrument Buses 3 and 8 by use of the alternate power supply at 14:49 hours. Normal configuration of the RHR system was restored and AOP-020 was exited at 14:51 hours. "Currently Instrument Buses 3 and 8 are being powered from the alternate power supply which causes the associated 'B' EDG to be inoperable due to the inoperability of the automatic load sequencer that starts the associated Service Water and Component Cooling Water pumps. The 'A' EDG is inoperable due to the need to complete required post-maintenance testing. Therefore, both EDGs are currently inoperable. "Both EDGs are currently considered available and are aligned for automatic starting. Both EDGs would be expected to automatically supply their respective buses if a loss of offsite power were to occur. Manual action would be required to start the required loads on the 'B' Train due to the current alignment of the Instrument Buses 3 and 8 on the alternate power supply. "It is expected that the 'B' EDG will be restored to operable status when Inverter 'B' is restored to operable status and realigned to supply Instrument Buses 3 and 8. "The Technical Specifications (TS) Action Statement currently in effect for loss of Inverter 'B' (TS 3.8.8 Condition A) requires initiation of action to restore AC instrument bus sources to OPERABLE status immediately. The actions to restore Inverter 'B' were initiated immediately and are continuing. "This report is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), for any event or condition that at the time of discovery could have prevented the fulfillment of structures or systems that are needed to mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1408 ON 6/27/2010 FROM ASHLEY VALONE TO MARK ABRAMOVITZ * * * "This is a follow-up notification to Event Notification EN #46045 regarding Instrument Buses 3 and 8 that unexpectedly de-energized during performance of testing in accordance with procedure OST-163, 'Safety Injection Test and Emergency Diesel Generator Auto Start on Loss of Power and Safety Injection.' "Power was restored to Instrument Buses 3 and 8 by use of the normal power supply at 08:03 hours on June 27, 2010. Inverter 'B' has been realigned to supply Instrument Buses 3 and 8. The restoration of inverter 'B' has returned the associated 'B' EDG to operable status at 11:09 hours with the return of the automatic load sequencer that starts the associated Service Water and Component Cooling Water pumps. The 'A' EDG continues to be inoperable due to the need to complete required post-maintenance testing. Currently 'A' EDG is considered available and aligned for automatic starting. "The Technical Specifications (TS) Action Statement for loss of Inverter 'B' (TS 3.8.8 Condition A) that requires initiation of action to restore AC instrument bus sources to OPERABLE status immediately was exited at 11:09 hours on June 27, 2010. TS Action Statement for loss of 'B' EDG (TS 3.8.2 Condition B) that requires initiation of action to restore required DG to OPERABLE status immediately was also exited at 11:09 hours on June 27, 2010." The licensee is still investigating the cause of the failure. The licensee notified the NRC Resident Inspector. Notified the R2DO (Shaeffer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-06-24
46044 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-06-24 09:36 | 2010-06-24 12:35 | 2010-06-24 | FITNESS FOR DUTY - SUPERVISOR TESTED POSITIVE DURING RANDOM DRUG/ALCOHOL TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random drug/alcohol test. Unescorted access has been suspended. Contact the HOO for further details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2010-06-24
46043 | 0 | EXELON NUCLEAR CORPORATE |  |  |  |  | 2010-06-24 09:55 | 2010-06-24 11:32 | 2010-06-24 | EXELON DRUG TESTING CONTRACTOR TESTED POSITIVE DURING RANDOM FITNESS-FOR-DUTY TEST A contractor used by Exelon Corporate for drug testing at six Exelon nuclear sites tested positive for an illegal substance during a random fitness-for-duty test. The individual has been denied unescorted access to Exelon facilities. Contact HOO for details. The licensee will notify the NRC Resident Inspectors at each site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 26.719 |  |  |  | 0 | 2010-06-24
46042 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-06-23 20:51 | 2010-06-23 23:57 | 2010-06-24 | MANUAL REACTOR SCRAM FOLLOWING LOSS OF BOTH RECIRCULATION PUMPS "Limerick Unit 1 was manually scrammed from 100% power on 6/23/10 at 2051 hours in accordance with plant procedure OT-112 'Recirculation Pump Trip' when both 1A and 1B recirc pump MG set drive motor breakers were observed to have tripped, resulting in a loss of both reactor recirculation pumps. Preliminary indication is a loss of power to 114A Load Center, caused by 'A' phase overcurrent trip of 13.2 KV feeder breaker (11-BUS-07) to the 114A Transformer and Load Center. The cause of the MG set drive motor breaker trips is under investigation at this time. "All Control Rods inserted as required. "No ECCS or RCIC initiations occurred. "No Primary or Secondary Containment Isolations were received. "The plant is currently in Hot Shutdown maintaining normal reactor level with feedwater in service." All systems functioned as required during the transient. The manual scram was characterized as uncomplicated. No PORVs or Safety Relief valves lifted during the transient. Decay heat is being discharged to the condenser via turbine bypass valves. The unit is in a normal shutdown electrical lineup and there was no impact on Unit 2. The electrical supplies for the recirc pump MG sets has been walked down by the licensee and no indication of any damage or electrical faults has been found at this time. The NRC Resident Inspector has been notified and the licensee indicated a media or press release will be made. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-06-24
46041 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2010-06-23 12:51 | 2010-06-23 19:23 | 2010-06-23 | UNIT 3 EMERGENCY RESPONSE DATA SYSTEM DECLARED INOPERABLE "The Unit 3 Emergency Response Data System (ERDS) communications link availability is questionable. Some of the data has failed to zero. The system engineer has reported that the historian is not collecting data. Declared U3 ERDS inoperable." The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-23
46040 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-06-11 13:20 | 2010-06-23 17:48 | 2010-06-23 | AGREEMENT STATE REPORT INVOLVING A RADIOGRAPHY SOURCE RECOVERY INCIDENT The following information was received from the State of Colorado via fax: "[A Midwest Inspection Services representative] contacted [the State of Colorado] by phone today (6/15/10) and notified [the State of Colorado] that they had an incident at a temp site Friday the 11th of June. "The radiography crew was doing an elevated (18 ft. aprox.) shot and the rope holding up the camera broke and the camera fell (18 ft. aprox.) leaving the source in an exposed position. The radiographer was unable to retract the source back into the camera. The crew roped off the area, and contacted the (RSO) who responded and covered the source with lead shot bags, using a remote device he was able to straighten the guide tube and retract the source. He [RSO] was wearing dual dosimeters, (chest and on shirt sleeve of the hand that he used to straighten the guide tube). The exposure dosimeter on the chest read 20mr/hr and the shirt sleeve dosimeter read 487mr/hr. [The Midwest Inspection Services representative] is gathering final information from interviews with everybody involved and will submit a written report detailing the incident. Guide tube was kinked with the source in an exposed position. Cause was the camera fell aprox. 18 feet when rope broke or came untied. Camera: INC model IR-I00 Source: INC model 32 s/n P264 (Ir-192, 56.74 Ci) Location: DCP Lucerne gas plant, Greeley, Co. Time: 6/11/10 at aprox. 1:20pm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-06-28
46039 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-06-23 09:10 | 2010-06-23 15:19 | 2010-06-23 | EARLY WARNING SIREN TEST FAILURE "North Anna experienced a severe storm the night of June 22, 2010. At 0910 hours on June 23, 2010, the telecommunications group polled the Early Warning System (EWS) sirens to check operability. The first siren did not respond. It was determined the back-up base radio was not transmitting the audio signal to the sirens. Therefore, activation of the EWS by the state or local agencies would not have been possible. It was possible to activate the EWS sirens locally from North Anna off a separate radio system. At 1040 hours the back-up radio was replaced and tested satisfactory for proper radio function. The primary base radio was also replaced and tested satisfactorily. The polling function test was performed with all 68 sirens responding as designed. The EWS sirens are currently operating off of the primary base radio with the back-up radio available for operation." The EWS was initially on the backup radio. This radio has been replaced. The licensee notified the NRC Resident Inspector, state government and will notify local government. The licensee will contact local media concerning this event. | 98 | 99 | 0 | 98 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-23
46038 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-06-23 14:25 | 2010-06-23 15:16 | 2010-06-23 | UNUSUAL EVENT DECLARED DUE TO AN EARTHQUAKE FELT ONSITE "Event Description: An Unusual Event was declared at 1425 EDT due to reports from site personnel of an earthquake felt onsite. This was verified through the National Earthquake Information Center. Plant seismic monitors did not actuate. "Actions Taken: Implemented OP 3127, Natural Phenomenon, for an earthquake. Plant personnel are walking down systems for any damage indications. [There is no indication of damage] at this time." The licensee informed state/local agencies and the NRC Resident Inspector. The licensee plans to issue a press release. * * * UPDATE AT 1742 ON 6/23/2010 FROM BOB VITA TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 1725 EDT. Plant walkdowns were completed with no damage noted. The licensee notified the NRC Resident Inspector. Notified the R1DO (Dwyer), NRR EO (Cunningham), DHS (Inzer), and FEMA (Hollis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | VT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-06-23
46037 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-06-23 14:28 | 2010-06-23 14:34 | 2010-06-23 | DECLARATION OF UNUSUAL EVENT DUE TO SEISMIC EVENT "At 1428 [EDT] on Wednesday, June 23, 2010, an Unusual Event was declared for Unit 1 and Unit 2 based on Emergency Plan criterion N-1 'Natural or Destructive Phenomena Inside the Protected Area'. "The Unusual Event was declared following detection of ground motion by persons on site, with confirmation based on United States Geological Survey information. Plant operation was not impacted by the event. Site structure and system inspections are in progress in accordance with the Abnormal Operating Procedure for Earthquake. No damage has been identified. "In accordance with Emergency Plan procedures, notifications of Berrien County and State of Michigan were completed. The licensee has notified the NRC Senior Resident Inspector. A follow-up notification will be made after the Unusual Event is terminated. "This notification is being made in accordance with 10 CPR 50.72 (a)(1)(i) due to declaration of an emergency class." * * * UPDATE AT 1645 EDT ON 06/23/10 FROM JAMES SHAW TO S. SANDIN * * * The licensee provided the following information as an update: "A press release has been issued regarding the seismic event. This notification update is being made in accordance with 10 CFR 50.72 (b)(2)(xi) for news release or notification of other government agency." The licensee informed state/local agencies and the NRC Resident Inspector. Notified R3DO (Lara). * * * UPDATE AT 2017 EDT ON 6/23/2010 FROM TIMOTHY WICE TO MARK ABRAMOVITZ * * * "The Unusual Event due to Seismic Event was terminated at 1955 EDT following an examination of plant systems which revealed no damage due to the seismic event. A press release has been issued regarding the termination of the Unusual Event. This notification update is being made to notify of the Unusual Event termination and also notify of the press release describing the Unusual Event termination in accordance with 10 CFR 50.72 (b)(2)(xi) for news release or notification of other government agency." The licensee notified state/local agencies and the NRC Resident Inspector. Notified the R3DO (Lara), NRR EO (Cunningham), DHS (Inzer), and FEMA (Hollis). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2010-06-23
46036 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-06-23 10:48 | 2010-06-23 14:11 | 2010-06-23 | ALERT DECLARED FOR A CARDOX DISCHARGE IN THE TURBINE BUILDING A CARDOX release occurred in the Unit-1 main turbine lube oil room and an Unusual Event was declared. The release resulted in an atmosphere immediately dangerous to life and health resulting in an Alert notification. No injuries resulted, however, the crane bay in the center of the turbine building was evacuated. Approximately 30% of the CARDOX storage tank was discharged due to a malfunctioning solenoid valve. This valve had recently been replaced. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1525 EDT ON 6/23/10 FROM TONY CHITWOOD TO S. SANDIN * * * The licensee provided the following information as an update: "On June 23, 2010, at 1035 PDT, an accidental discharge of CARDOX into Unit 1 Main Lube Oil Reservoir Room occurred during testing. On June 23, at 1048 PDT, an Unusual Event was declared for DCPP Unit 1. On June 23, at 1056 PDT, an Alert was declared for DCPP Unit 1. The DCPP Unit 1 reactor remains at full power. No safety related equipment has been impacted. There were no injuries to personnel and no equipment damage. Offsite assistance was requested to assist in event response. "Pacific Gas and Electric Company issued the first press release at 1225 PDT on June 23, 2010. Further press releases will be issued as necessary until the event is terminated. "The licensee notified the NRC Resident Inspector." The licensee also informed state and local agencies. Notified R4DO (Pick). * * * UPDATE AT 2028 EDT ON 6/23/10 FROM DAVID EFRON TO S. SANDIN * * * The licensee has terminated the Alert at 1715 PDT based on restoring accessibility to all plant area. The licensee will inform state/local agencies, the NRC Resident Inspector and issue a follow-up press release. Notified R4DO (Pick), NRR EO (Cunningham), IRD (Morris), DHS (Inzer), FEMA (Hollis), DOE (Yates), USDA (Petrick), and HHS (Lee). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2010-06-23
46035 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2008-11-01 04:30 | 2010-06-22 15:52 | 2010-06-22 | HISTORICAL CONDITION PREVIOUSLY REPORTED IN LER 2008-005 SHOULD ALSO HAVE BEEN REPORTED IN ACCORDANCE WITH 10 CFR 50.72 (b)(3)(v)(C) "A required containment penetration was not fully closed during fuel movement from November 1, 2008 until November 3, 2008. This was reported in LER 2008-005 as a condition prohibited by plant technical specifications. "Upon further review, the condition that existed at Millstone Power Station Unit 3 and reported to the NRC in LER 2008-005, should also have been reported per the requirements of 10 CFR 50.72(b)(3)(v)(C). A supplement to LER 2008-005 will be submitted. The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2010-06-22
46034 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2009-10-07 10:30 | 2010-06-22 11:32 | 2010-06-22 | HISTORICAL CONDITION PREVIOUSLY REPORTED IN LER 2009-003 SHOULD ALSO HAVE BEEN REPORTED IN ACCORDANCE WITH 10 CFR 50.72 (b)(3)(v)(D) "On October 7, 2009, two independent diesel generators were rendered inoperable. This was reported in LER 2009-003 as a condition prohibited by plant technical specifications and a common cause that resulted in two independent trains becoming inoperable. "Upon further review, the condition which existed at Millstone Power Station Unit 2 and reported to the NRC in LER 2009-003, should also have been reported per the requirements of 10CFR50.72(b)(3)(v)(D). A supplement to LER 2009-003 will be submitted. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-06-22
46033 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-06-22 02:06 | 2010-06-22 03:26 | 2010-06-25 | RIVER WATER LEVEL ABOVE 899 FEET River water level exceeded 899 feet above sea level resulting in the licensee declaring a Notice of Unusual Event at 0206 CDT. The plant continues to operate at 100 percent power. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BARTON CROW TO JOE O'HARA AT 1042 ON 6/22/10 * * * "On 6/22/10 at 0557 Cooper Nuclear Station made a news release concerning the 'Notification of Unusual Event' declared today at 0206 for Missouri River level at 899 feet above sea level. "This is a 4 hour report per 10CFR50.72(b)(2)(xi) for any event or situation for which a news release has been made that causes heightened public or government concern. State and local agencies were notified by the 'Notification of Unusual Event' declaration. "At 0900 CDT Missouri River level was at 899.35 feet above sea level. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM CURTIS MARTIN TO DONG PARK AT 1647 EDT ON 6/25/2010 * * * The Unusual Event was terminated at 1513 CDT. The Missouri River level was at 897.3 feet above sea level and receding. The licensee notified the NRC Resident Inspector, the State, local, and other government agencies. Notified the R1DO (Pick), NRR EO (Cunningham), IRD (Morris), DHS (An), and FEMA (Barden). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2010-06-22
46032 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-06-19 06:36 | 2010-06-19 11:25 | 2010-06-19 | MANUAL REACTOR TRIP DUE TO GENERATOR LOCKOUT "At 0636 hours, control room personnel initiated a manual reactor trip of Unit 2 from MODE 2 at 0% power. Just prior to the initiation of the manual reactor trip, an automatic turbine trip had occurred as a result of the receipt of a generator lockout signal. Prior to the automatic turbine trip, an orderly power reduction to 44% power had been completed and the unit was being maintained in a stable condition in MODE 1. At the time of the turbine trip, two sets of condenser steam dump valves were isolated, in preparation for scheduled condenser waterbox tube cleaning. Following the manual reactor trip, all safety systems and equipment operated as expected. The cause of the turbine trip, including receipt of the generator lockout signal, is under investigation. The unit is stable in MODE 3 at normal RCS temperature and pressure. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) t and 10 CFR 50.72(b)(3)(iv)(A). The NRC Senior Resident Inspector has been notified." Just prior to the trip, the unit was critical in Mode 2. All rods are fully inserted into the core. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-06-19
46031 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-06-17 | 2010-06-18 19:38 | 2010-06-18 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED DOSE FROM GAMMA KNIFE TREATMENT "A patient undergoing Gamma Knife treatment received less than the prescribed dose in the eighth of eight planned treatments. The undertreatment exceeded 50% of the planned treatment dose for the final fractional treatment (only approximately 12 rads of the prescribed approximately 162 rads for the final fractional dose was administered). "The final treatment was terminated approximately 15 seconds into the planned 3.5 minute treatment due to apparent pain on the part of the patient. Upon investigation, it was determined that the head immobilizing bracket was not fully secured. Only approximately 12 rads dose had been administered in the approximately 15 seconds before the treatment was terminated. The planned total treatment dose was 1300 rads. Approximately 1150 rads were administered in the eight treatments. "The licensee reported they likely will not give the patient the remaining 150 rads of the planned treatment." CA Event No.: 061810 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-06-24
46030 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2006-07-27 | 2010-06-18 17:13 | 2010-06-18 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATOR The following information was received from the Kansas Department of Health and Environment via facsimile: "On July 27, 2006, Honeywell reported by phone that an internal review showed that a static eliminator device shipped 12/18/03, activity 10 mCi, was missing. As of the report date, the activity of this device would have been 84 microCi (138 day half-life). This would give a gamma exposure of 172 microR/h at 30 cm (11 microR/h at 1 m). "A search for the device was done, but the device was not found. The root cause was a loss of accountability in that the device was issued to an entire production team or line versus an individual bench within the production line. "Corrective action included issuing of the devices through the Health, Safety, and Environment (HSE) department rather than a tool crib. Also the devices will only be issued to an individual to improve personal accountability. "The manufacturer was notified. This event is considered closed. "Note: This item was determined during the State of Kansas IMPEP [Integrated Material Performance Evaluation] inspection conducted the week of June 14, 2010, that this event was reportable under 10CFR20.2201(a)(1)(ii) - Reporting within 30 days after the occurrence of any lost, stolen or missing material in excess of 10 times the appendix C quantities." Kansas Item Number: KS060014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-06-23
46029 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2007-08-14 | 2010-06-18 17:13 | 2010-06-18 | AGREEMENT STATE REPORT - POTENTIALLY DAMAGED TROXLER The State of Kansas provided the following information via facsimile: "During the course of an inspection performed on 10/31/2007, it was discovered that Tetra-Tech had a gauge damaged in an accident at a temporary jobsite on 8/1/2007. The gauge was leak tested and shipped back to the manufacturer (Troxler) and refurbished and then returned to Tetra-Tech. Tetra-Tech did not notify the State of the damaged gauge and was issued a citation via the Inspection letter dated 11/15/2007. Terra-Tech responded in a letter dated 12/26/2007 and that was accompanied by several pictures of the damaged gauge. Based on the licensee's description and the photos the gauge was only superficially damaged with only a slight dent being visible on one end of the gauge. Had KDHE [Kansas Department of Health and Environment] been notified at the time of the accident on 8/14/2007 and been sent pictures, no response would have been required. The licensee understands, based on their letter, the need to communicate with KOHE regarding future incidents. No further action is required. "This item was determined during the State of Kansas IMPEP [Integrated Materials Performance Evaluation Program] inspection conducted the week of June 14, 2010, that this event was reportable under 10CFR30.50(b)(2). An electronic update to the NMED database will follow." KS Event No.: KS070010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-06-23
46028 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2006-03-28 | 2010-06-18 17:13 | 2010-06-18 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was received from the Kansas Department of Health and Environment via facsimile: "On 3/29/06, Kansas Department of Transportation (KDOT) reported by phone that a portable gauge got hit by a vehicle near SW US 77/50 last night [3/28/06]. The gauge was packed in its shipping container and was ready to load on a truck when the accident happened. The shipping container sustained minor damage. An assessment is being made with details to follow. Follow-up actions will be reviewed in inspection space. "On 4/7/06, an inspection was conducted of licensee's facility. No items of non-compliance were found. Licensee continues to calibrate and clean their own devices as per their license conditions. If necessary, gauges are sent to the manufacturer for repair. "On 5/5/06, reports and narratives were received from KDOT personnel involved with the gauge incident. Gauge failed Validator assessment and is being recalibrated. No other damage to the gauge itself was reported. "Note: This item was determined during the State of Kansas IMPEP [Integrated Material Performance Evaluation] inspection conducted the week of June 14, 2010, that this event was reportable under 10CFR30.50(b)(2)(iii) - The 24 hour report of an event where required equipment is disabled or fails to function as designed when no redundant equipment is available and operable to perform the required safety function." Kansas Item Number: KS060007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-06-23
46027 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2006-10-01 | 2010-06-18 17:13 | 2010-06-18 | AGREEMENT STATE REPORT - FOUND BRACHYTHERAPHY SOURCE PREVIOUSLY LOST The State of Kansas provided the following information via facsimile: "This event that occurred during the 4th quarter of 2006 at Wesley Medical Center, LLC, was determined during the State of Kansas IMPEP [Integrated Materials Performance Evaluation Program] inspection conducted the week of June 14, 2010, to be reportable under 10CFR2201. An electronic update to the NMED database will follow. Below are details of the event. "During an inspection by KDHE [Kansas Department of Health and Environment] of Wesley Medical Center 2/14/2007, a review of the 4th quarter Radiation Safety Committee notes revealed that a brachytherapy source was lost for approximately 45 hours. From the inspector's notes: 'Incident where a Cs-137 brachytherapy source was lost for approximately 45 hours before being found in the sheets in the laundry room by the RSO [Radiation Safety Officer]. RSO did not make a determination of exposure to the patient based on conservative and worst case scenarios. Incident was not reported to the State.' "The RSO notes read: 'We had one recordable event that has been noted in the HNS system. We had one misplaced cesium 137 brachytherapy source. A patient presented for treatment of cervix cancer and we used low-dose Fletcher Suit system where the cesium sources dwell within the patient for 45 hours. The plan was reviewed and the patient was loaded. On the day of removal, one source was missing when the RSO emptied the tandems. Both physicists searched extensively for the source using a Geiger counter. The source was located on the floor in the laundry capture room for women's health. It was determined that the source never reached its destination in the patient, and that it most likely fell into the bed linens during insertion. One environmental service worker spends approximately five minutes per day having an approximate exposure of 1 mRem from that activity. A member of the public would be limited to 100 mRem of exposure per year and the exposure rate would be approximately 1.2 mRem per hour at 3 meters; some of the walls in the room are cinder blocks which provide some shielding. It was suggested that linen be left in the patient's room during their stay to guard against having an incident such as this in the future.' "The licensee was issued a citation for failure to report this as a lost source. "Update information provided during the week of June 14, 2010 indicated that the source activity was 37 mCi (15 mg Ra equivalent)." KS Event No.: KS100006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-06-23
46026 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2010-05-01 | 2010-06-18 14:23 | 2010-06-18 | AGREEMENT STATE REPORT - POTENTIAL DOSE TO EMBRYO OR FETUS The State of Illinois provided the following information via email: "On June 17, 2009, the [Illinois Emergency Management] Agency was contacted with a request to make a dose estimate to a fetus as a result of administration of radioiodine to a patient who was later found to be pregnant. Subsequently when additional information was requested to determine the appropriate parameters, the [Illinois Emergency Management] Agency was advised that the administration had occurred 3 years earlier and that the child had been delivered after a full term pregnancy and was receiving thyroid hormone therapy. The physician indicated that on May 1, 2007 a patient was given 102.9 milliCi of I-131 as a treatment for recurrence of cancer associated with a previous thyroidectomy conducted in 2006. The physician had previously treated the patient with I-131 in 2006 following surgery and had conducted patient interviews/training regarding administration of I-131 at that time, so that when she represented herself for an additional treatment dose, he had been lead to believe she understood the contraindications. The doctor stated that he was told no when he asked if she was pregnant. No independent test was conducted. On June 11, 2007, he was contacted by the physician's obstetrician who advised that she was at 32 weeks gestation as of June 11, 2007. This would infer she was 25-27 weeks (6 month) pregnant at the time of the second administration a month earlier. "Calculations were performed by the [Illinois Emergency Management] Agency for a thyroid patient following ANSI Std. N13.54-2008 which lead to an estimated dose to the fetus of 86 Rad. This event remains open pending submission of the required report from the physician and follow up by the [Illinois Emergency Management] Agency." IL Event No.: IL 10044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2010-06-24
46025 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2010-06-18 08:08 | 2010-06-18 12:04 | 2010-06-18 | UNUSUAL EVENT DECLARED DUE TO DAMAGED ENERGIZED EQUIPMENT "On June 18, 2010, at approximately 0807 MST, a manual turbine trip was initiated due to loss of cooling for Main Transformer X01C. The power supplies for the transformer cooling system was lost due to an inadvertent actuation of the transformer fire protection deluge system. The damage to the energized equipment met the definition for an Emergency Action Level HU 2.2. Based on HU 2.2 the Unit 1 Shift Manager declared a Notification of an Unusual Event (NOUE) at 0808 MST applicable to Palo Verde Unit 1 only. "The manual trip of the turbine initiated a Reactor Power Cutback Large Load Rejection actuation which was successful. The reactor is stable at 25% with Heat Removal via main feedwater and steam bypass to main condenser. A down power to approximately 12% power is being planned. "No anomalies were noted during the manual turbine trip. [There is] no release in progress and no safety systems actuations were required." Palo Verde Unit 1 is in a normal post-trip electrical lineup. State and local authorities have been notified as well as the NRC Resident Inspector. * * * UPDATE FROM BRIAN FERGUSON TO DONG PARK @ 1333 EDT ON 6/18/10 * * * The licensee terminated the Unusual Event at 1030 MST. The reactor remains stable at approximately 12% power, and heat removal is via main feedwater and steam bypass to the main condenser. Notified IRD (Gott), NRR EO (Cheok), R4DO (Jones), DHS (Inzer) and FEMA (Hollis). | 25 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-06-18
46024 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-06-17 14:00 | 2010-06-17 16:02 | 2010-06-17 | OFFSITE NOTIFICATION DUE TO GRASS FIRE OUTSIDE PROTECTED AREA "At 1400 EDT on 6/17/2010, a grass fire was reported by security officers at the main entrance facility. The fire was located outside of the protected area and outside the main entrance to the plant. The cause of the fire appears to be sparks from an 18 wheel truck's wheel contacting a curb. These sparks apparently ignited dry grass in the surrounding area. The site fire response team responded to the incident and discovered approximately a 20' x 20' area of grass burning. Extinguishing agent was applied by on site personnel and the fire was extinguished. Off site assistance (Saint Leonard Volunteer Fire Department) reported to the scene and provided makeup water to the site fire engine. There was no damage to any equipment or structures. A courtesy notification was made to Calvert Control Center at 1445 to ensure local agencies were informed of the call for assistance to the local fire department." The licensee notified the NRC Resident Inspector. | 100 | 85 | 0 | 100 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-17
46023 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-06-17 10:45 | 2010-06-17 14:56 | 2010-06-17 | OFFSITE NOTIFICATION DUE TO INADVERTENT INITIATION OF EMERGENCY PREPAREDNESS SIRENS "At 1045 [CDT] on 6/17/2010, the Monticello Nuclear Power Generating Plant (MNGP) received a report from the Sherburne County Sheriff Dispatcher that there had been an inadvertent manual initiation of Emergency Preparedness sirens in the county while performing siren testing in preparation for inclement weather anticipated later this evening. All plant conditions/parameters are normal. A total of 48 emergency sirens were on for approximately 1 minute before being secured. The inadvertent initiation of the sirens was determined to be reportable under 10 CFR 50.72(b)(2)(xi), 'News Release or Notification of Other Government Agency.' "Sherburne County, the State of Minnesota, and the site NRC Resident Inspector have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-17
46022 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-06-03 | 2010-06-17 13:51 | 2010-06-17 | AGREEMENT STATE REPORT - HIGH DOSE RATE TREATMENT ADMINISTERED TO AN UNINTENDED AREA The following report was received via facsimile from the Commonwealth of Pennsylvania: "The licensee called the PaDEP [Pennsylvania Department of Environmental Protection] Southcentral Regional Office on the morning of June 16, 2010, to provide a 24-hour verbal notice of a medical event. The licensee also notified the patient and attending physician on June 16, 2010. The event involves a dosage that differs from the intended dose by greater than 20%, consequently requiring a 24-hour report per 10 CFR 35.3045. "On June 3, 2010, a patient was undergoing HDR [High Dose Rate] treatment for ovarian cancer. The area to be treated was incorrectly entered into the HDR computer and resulted in the patient receiving a dose to an unintended area. This event was discovered during the second fraction of treatment on June 15, 2010. Cause of the event was human error. "The Department is awaiting more event details at this time and plans to send regional staff to conduct an inspection on June 21, 2010. Final event details will be communicated in a NMED report." PA Event No.: PA100012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-06-23
46021 | -1 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-06-17 05:19 | 2010-06-17 14:15 | 2011-02-01 | UNANALYZED CONDITION DUE TO CONTAINMENT SPRAY RECIRC SUMP ISOLATION VALVE FAILURE TO STROKE CLOSED "At 0519 CDT on June 17th, Unit 2 was closing the 2CS009B, Containment Spray Recirc Sump Isolation Valve, as part of post maintenance testing when the valve stopped stroking (i.e. mid position). The 2CS009B valve was being stroked closed for restoration from a successful timed stroke in the open direction. The 2CS009B valve was manually closed and verified closed via limit switch indication. "With the 2CS009B valve unable to be closed from the Main Control Room, an unanalyzed condition may have existed where, during a large break LOCA requiring cold leg recirc, the Refueling Water Storage Tank (RWST) had an additional flow path to the containment recirc sump. This potentially challenges the operators to complete the switchover prior to the RWST reaching 9%, the point at which pumps taking a suction from the RWST only are shutdown. This condition is still being evaluated." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM P. MOODY TO P. SNYDER AT 0404 ON 2/1/11 * * * "At 0509 on June 17, 2010, Unit 2 was closing the 2CS009B, Containment Spray (CS) Recirculation Sump Isolation Valve, as part of post maintenance testing when the valve stopped stroking (i.e., mid-position). The 2CS009B was being stroked closed for restoration from a successful timed stroke in the open direction. The 2CS009B was manually closed and verified closed via limit switch indication. "With the 2CS009B unable to close from the Main Control Room, an unanalyzed condition may have existed where, during a large break LOCA requiring cold leg recirculation, the Refueling Water Storage Tank (RWST) had an additional flow path to the recirculation sump. This potentially challenged the operators to complete the switchover prior to the RWST reaching 9%, the point at which pumps taking a suction from the RWST only are shutdown. While this condition was being evaluated, an ENS notification was made per ENS 46021 under 10CFR50.72(b)(3)(ii)(B). "As the evaluation approached the 60-day reporting period, LER 2010-002 was issued in accordance with 10 CFR 50.73(a)(2)(ii)(B), assuming the results would yield an unanalyzed condition. "Since then, an evaluation was completed. The results concluded the operators would have performed the switchover steps within the allowed time, before reaching the RWST empty alarm set point. Therefore, the Emergency Core Cooling System (ECCS) and CS system would have performed their design functions. The evaluation also determined the RWST outflows with 2CS009B in the open position during the ECCS switchover sequence did not affect the RWST vortex analysis. Based on no loss of design function, the plant was not in an unanalyzed condition and this event is not reportable per 10CFR 50.72(b)(3)(ii)(B) or 10CFR 50.73(a)(2)(ii)(B). This event was screened for additional reportability criteria contained in the Exelon Reportability Manual. Again, since there was no loss of design function there is no reportability requirement. "Therefore ENS notification 46021 is being retracted." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-06-17
46020 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-06-16 19:20 | 2010-06-16 21:08 | 2010-06-16 | AUTOMATIC REACTOR TRIP DUE TO A LIGHTNING STORM "On 6-16-2010 at 1920 hours, Unit 2 experienced an automatic reactor trip/turbine trip from 98% power. A severe lightning storm was in progress at the time of the trip and a lightning strike appears to be the cause of the event. The reactor trip was actuated from Channel 1 and Channel 2 Over Temperature Delta T. All control rods fully inserted into the core during the trip. The control room staff responded to the trip in accordance with plant procedures and the unit is stable in Mode 3. This event is reportable per 10CFR50.72(b)(2)(iv)(B). "The Auxiliary Feedwater pumps started as designed following the reactor trip and steam generator inventory was restored to normal operating level. The Auxiliary Feedwater pumps have been secured and returned to automatic. This event is reportable per 10CFR50.72(b)(3)(iv)(A) due to the ESF actuation. "Decay heat is being removed by the condenser steam dump system. The 'A' loop wide range hot and cold leg thermocouples remain failed high and the 'B' loop wide range cold leg thermocouple also failed high during the event. The plant is in a normal shutdown electrical lineup." The licensee has notified the NRC Resident Inspector and will notify the local authorities. See EN #41898 for similar occurrence. | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-06-16
46019 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-06-16 12:58 | 2010-06-16 21:01 | 2010-06-16 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "On 06/16/10 at 1320 CDT, while performing 2-SR-3.3.6.1.6(3), HPCI Time Delay Relay Calibration, HPCI was discovered to be isolated. After review of the Integrated Computer System (ICS), HPCI [steam supply valve] had isolated at 1258 CDT. Cause of isolation is unknown with investigation in progress. "This incident is reportable as an 8-hour ENS notification under 10CFR 50.72 (b)(3)(v) as 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "It also requires a 60 day written report. The NRC Resident Inspector has been notified." | 0 | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-06-16
46018 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2010-06-16 17:10 | 2010-06-16 19:20 | 2010-06-16 | MANUAL REACTOR TRIP AFTER TWO CONTROL RODS DROPPED "At 1710 EDT, Unit 1 was manually tripped due to two dropped control rods. All CEAs [Control Element Assemblies] fully inserted on the trip. Steam generator level control responded as expected and no pressurizer or power operated relief valves opened. RCS heat removal is being maintained by main feedwater and steam bypass control systems. All other systems functioned normally and the plant has stabilized at normal operating temperature and pressure in Mode 3. This non-emergency notification is being made pursuant 10 CFR 50.72(b)(2)(iv)(B) due to manual actuation of RPS." The licensee characterized the manual trip as uncomplicated. The second rod dropped within a very short time of the first rod. The cause of the rod drops is still under investigation. The licensee noted that no activities involving the rod control system were in progress when the event occurred. The licensee was at 45% as part of its post outage power ascension unrelated to the rod drop. The manual reactor trip action was taken per procedure when the second rod dropped. The reactor trip had no impact on Unit 2 operation. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-06-16
46017 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-06-16 12:33 | 2010-06-16 17:22 | 2010-06-16 | OFFSITE NOTIFICATION TO THE NEBRASKA DEPARTMENT OF ENVIRONMENTAL QUALITY "Notification was made to the Nebraska Department of Environmental Quality regarding the inability to conform to the NPDES permit, since the discharges from the sludge pond to the Missouri River are uncontrolled at this time. As a result of high Missouri River levels, the sludge pond was overtopped. The discharges into this pond are subject to NPDES Requirements. The inputs into the sludge pond are described in the NPDES permit as low volume wastewater. There are three outfalls which discharge into the pond. Outfall 002B is described as Clearwell Discharge plus Outfall 004 Emergency Overflow. Outfall 002C is described as Floor Drains. Outfall 004 is described as Reverse Osmosis Reject and Boiler Blowdown Waste streams. "Additionally, the high river levels have resulted in media inquiries regarding potential changes in plant operation. Public information personnel and management have responded to these inquiries with information on the impact of river level and preparations for additional actions should conditions warrant additional protective actions. The responses to these inquiries have been referenced in some publications. At the present time, the river appears to be at its crest, with no additional rise forecast. The current level is approximately 3.8 feet below the crest of the 1993 flood, which was the highest flood recorded at the site, and 5 feet below grade elevation. A press release is not planned at this time." The sludge pond does not contain any contaminated material. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-16
46016 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-06-16 10:15 | 2010-06-16 17:16 | 2010-06-16 | LOSS OF EMERGENCY SIRENS "On June 16, 2010, at approximately 1015 hours (CDT), the Monticello Nuclear Generating plant determined that there was a loss of 48 out of 106 Emergency Preparedness sirens. No counties other than Sherburne County were affected. Availability of less than 70% of the total number of sirens is considered to be a loss of emergency off-site response capability and is reportable under 10 CFR 50.72(b)(3)(xiii), 'Loss of Emergency Preparedness Capabilities.' Notification to the public in the event of an emergency has not been compromised since a back-up notification method is provided in the station's Emergency Plan. At this time there is no estimated return to service time for the sirens. "The station is working on restoration of the sirens. A follow-up notification of the return to service of the sirens will be provided once the issue is corrected. "Sherburne County, the State of Minnesota, and the NRC Resident [Inspectors] have been informed of this event. "Updated Information: "At 1320 hours on June 16, 2010, sirens have been returned to service. Siren activation capability has been restored via the secondary method of activation. Investigation and repair of the primary method of siren activation continues." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-16
46015 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-06-15 12:15 | 2010-06-16 15:45 | 2010-06-16 | AGREEMENT STATE REPORT - GAMMA KNIFE TREATMENT ADMINISTERED TO WRONG LOCATION The following report was received via e-mail from the State of Minnesota: "Event description: The Minnesota Department of Health was notified on June 15, 2010 at 3:40 p.m. [CDT] of a medical event involving a gamma knife treatment at the University of Minnesota Medical Center - Fairview, University Hospital, Minneapolis. The total treatment consisted of 10 exposures, and was scheduled between 11:30 a.m. and 1:30 p.m. on Tuesday, June 15th. "Five automatic positioning system (APS) shots were completed successfully, and then the treatment called for 5 additional trunnion exposures. The first trunnion exposure called for a setting of 76.3, 86.5, 148.1 in the X, Y, and Z directions, respectively. Instead, the settings of 76.3, 86.5, 76.3 were used. In effect, the X setting was inadvertently used for the Z setting. The error was noticed when the coordinates for the second trunnion exposure were being set up. The Z coordinate value used for the first shot was very different from the Z coordinate for next exposure. "A new treatment plan was run to determine the dose and the location of the unintended exposure delivery. This plan showed a dose of 3.2 Gy (320 rad) to be delivered to a volume of 0.62 cubic cm at the unintended location. The original plan was re-exported to the GK treatment unit, so the exposure at X, Y, Z setting 76.3, 86.5, 148.1 could be given. Thus, the originally prescribed dose for the treatment region was given. The neurosurgeon and radiation oncologist explained the situation to the patient." Device Manufacturer: Leksell Gamma System Model: 24001 Type C "Source Manufacturer: General Electric Company Model: 43047 Event Report ID: MN100002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2010-06-22
46014 | 0 | TYCO ELECTRONICS |  |  |  |  | 2010-05-21 | 2010-06-16 15:30 | 2010-06-16 | TYCO ELECTRONIC RELAY RECALL The information below is a summary of a report received via facsimile from Tyco electronics: "During normal assembly processing of nuclear E7000 relays, Tyco Electronics experienced an issue with a component. A retainer ring on the spindle assembly was found to have a hydrogen embrittlement issue that may fracture at some point in this products' life cycle. Further investigation revealed this condition is limited to one specific lot of retainer rings. "Tyco purged this lot of retainer rings from their inventory and all 'work in process'. Tyco is able to account for all the retainer rings in this lot. Tyco's records indicate that some relays shipped to the [facilities listed below] were made using this specific retainer ring lot. "Because the retainer ring did not meet stated requirements, Tyco is recalling the specific relays for replacement. Note that only the specific lot numbers listed [below] are affected by this recall. All other lots should function as intended. "Item supplied are E7000 relays with serial numbers beginning with 1019. Certificates of Conformance stating exact relay description and serial numbers were sent to affected customers with Tyco's June 16, 2010 notification. Tyco sold this safety-related item for specified and unspecified applications to the customers listed below: South Carolina Electric & Gas Jenkinsville, SC 3 Relays Entergy Nuclear Operations, Indian Point Energy Center Buchanan, NY 2 Relays Exelon Generation Company/Braidwood Braidwood, IL 2 Relays Trentec Curtis-Wright Flow Control Cincinnati, OH 1 Relay Ergytech Houston, TX 1 Relay Entergy Operations Inc. (Arkansas) Russellville, AR 1 Relay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-06-16
46013 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-06-16 08:59 | 2010-06-16 13:38 | 2010-06-16 | EARLY WARNING SYSTEM FOUND NON-RESPONSIVE DURING TESTING "During performance of the Early Warning System (EWS) Polling Function Test the sirens did not respond. At 0859 hours [EDT] on June 16, 2010, the polling function test of the sirens was started. After four (4) sirens did not respond to the polling, the test was suspended and the Telecommunications group was notified. With Telecommunications monitoring the EWS primary base radio, the polling function test was run again. It was determined the audio signals from the status logger were being transmitted to the EWS primary base radio, however, the radio was not keying or transmitting the audio signal to the sirens. A check of the keying signal from the processor to the primary base radio was noted to be operating properly, however, the primary base radio was still not transmitting the audio signal to the sirens. Therefore, activation of the EWS by the state or local agencies would not have been possible. At 0925 hours, the EWS was switched to the back-up radio base station and tested satisfactory for proper radio function. The polling function test was performed with all 68 sirens responding as designed. All 68 sirens polled satisfactory during the last performance of the EWS Polling Function Test on June 2, 2010." The licensee has notified the State and the NRC Resident Inspector. Local agencies will also be informed. | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-16
46012 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-06-16 10:50 | 2010-06-16 12:04 | 2010-08-05 | DISCOVERED VULNERABILITY IN SAFEGUARDS SYSTEM The licensee discovered a vulnerability in a safeguards system that could have allowed access to a controlled access area for which compensatory measures had not been employed. Compensatory measures were immediately implemented upon discovery. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 8/5/10 AT 1032 EDT FROM SAVAGE TO CROUCH * * * Upon further review, the licensee determined that the subject vulnerability involved an area that should not have been considered a vital area at the time of the event. There was no potential for undetected access to a vital area, therefore this event is not considered reportable. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector and has discussed this with the Region 4 Security Inspector (Larsen). R4DO (Hagar) notified. A copy of this retraction was also sent to the 73.71 e-mail group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-06-16
46011 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-06-14 | 2010-06-15 13:52 | 2010-06-15 | PENNSYLVANIA AGREEMENT STATE REPORT - STUCK SOURCE The following information was received from the Pennsylvania Bureau of Radiation Protection via facsimile: "The licensee called the PaDEP Southwest Regional Office (SWRO) on the morning of June 14, 2010 to provide a 24-hour verbal notice of a stuck source. The licensee secured the location, and contacted the manufacturer and their consultant for instruction on how to proceed. Equipment appears to have failed to function as designed, thus, the licensee and DEP are doing a 24 hour report per 10CFR30.50(b)(2). "On June 14, 2010, the SWRO of the Department received verbal notification of a stuck radioactive source. DEP was informed the threaded cap on the end of their cobalt-60 source became stuck within the mold they were checking. The licensee moved the unit to a secure location, roped-off this area, and began to conduct surveys. The manufacturer (Berthold Technologies), along with an outside consultant were contacted for support on recovering the source. We were told the activity of the source is 5.3 millicurie (mCi), but it is not clear if that is a decayed or initial activity. The source information from their license is as follows: Berthold Technologies, source model P2608-100, Co-60 sealed source capsule. "DEP Central Office is awaiting further details from its Western Regional Office and the licensee's facility staff and consultant to confirm radiation survey measurements and source recovery. It is anticipated that Regional staff will conduct a follow-up inspection. Final even details will be communicated in a NMED report." PA Report ID: PA-100011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-06-18
46010 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-05-20 | 2010-06-15 12:30 | 2010-06-15 | TEXAS AGREEMENT STATE REPORT - TWO TRITIUM EXIT SIGNS MISSING The following information was received via e-mail from the State of Texas Radiation Branch: "On June 15, 2010, the Agency received a letter from a company operating under a General License in the State of Texas. [While] conducting an inventory of tritium (H-3) exit signs used at their facilities, they found that two signs containing 10 curies each of H-3 were missing from a facility in Hewitt, Texas. The signs were manufactured by SRB Technologies, Inc., Model BetaLux-E. A search of the facility was conducted and interview with the individuals working at the facility were held. The interviews did not provide any information on the location or disposition of the signs. The company is removing all exit signs containing tritium and returning them to the manufacturer to prevent a reoccurrence of the event. Additional information has been requested by this Agency and will be provided when received." TX Incident # I-8754 * * * UPDATE FROM TEXAS (TUCKER) TO HUFFMAN (VIA E-MAIL) AT 1515 EDT ON 6/15/10 * * * "The company provided the following information [to the Texas Radiation Branch] during a phone conversation. "The signs were found to be missing on May 20, 2010. The loss was reported to the Health and Safety Group (HSG) on May 25,2010. The HSG Group incorrectly interpreted the reporting criteria for this event and believed that it only required a 30 day written report. The HSG manager stated that they would change their procedure to insure any future required reports would be done on time." R4DO (Powers) and FSME (McIntosh) notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-06-18
46009 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2010-05-26 | 2010-06-15 10:44 | 2010-06-15 | AGREEMENT STATE REPORT - POTENTIAL IMPROPER RADIATION DOSE The following information was received by facsimile: "A misadministration involving the implantation of radioactive seeds into the prostate (permanent brachytherapy) was reported to [the New York State Department of Health] office on May 28, 2010. The patient, a 58 year old male diagnosed with prostate cancer, Gleason score of 6, PSA of 3.8, was implanted on May 26, 2010. The prescribed dose was 145 Gy, to be delivered using Iodine-125 seeds, with an activity of approximately 0.36 mCi/seed. The patient was implanted with 112 seeds. A significant number of seeds (22) were placed outside the prostate gland, inferior to the gland (5.4 cm) and in the perineum. According to the medical physicist's calculations, the implanted area of the prostate received a D90 of 140 Gy. "The initial indication is that the misplacement is a result of misidentification of the prostate by the radiation oncologist who performed the procedure. Ultrasound and C-arm fluoroscopy systems were used to aid with positioning the seeds. It appears that the patient's colon was not properly prepared, which caused poor ultrasound imaging. In addition, a Foley catheter was not inserted into the bladder, which made bladder localization difficult. A post implant confirmatory fluoroscopic image was obtained and the radiation oncologist observed that the sources were outside of the prostate area. On May 28, 2010, a post implant CT scan was performed which confirmed the seed locations and allowed for a calculation of the DVH [Dose-Volume Histogram] to the perineum of 10.0 Gy. The medical record has been requested and will be sent out for an expert review." New York Event Report ID No: NYDOH-10-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2010-06-21
46008 | 0 | TENNESSEE VALLEY AUTHORITY |  |  |  |  | 2010-06-14 11:18 | 2010-06-15 09:44 | 2010-06-15 | NON-LICENSED SUPERVISOR FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The employee's access to TVA nuclear plants has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 1 | TN | OTH | GEN | 26.719 |  |  |  | 0 | 2010-06-15
46007 | 0 | CARRO & CARRO ENTERPRISES INC. |  |  |  |  | 2010-06-10 12:00 | 2010-06-14 19:30 | 2010-06-28 | MISSING SEAMAN MOISTURE DENSITY GAUGE Carro & Carro Enterprises Inc. reported that a Seaman Model C-300 Moisture Density Gauge containing a 4.5 mCi Radium-226 source was discovered missing from a temporary job location in San Juan, Puerto Rico on Thursday, June 10th. A search was conducted on Friday with negative results. A police report was filed on Monday, June 14th, and a reward offered in two local newspapers. * * * UPDATE FROM DANIEL IRIZARRY TO DONALD NORWOOD AT 1135 EDT ON 06/28/2010 * * * Missing gauge was returned to Carro & Carro Enterprises, Inc. this morning at about 0730 local time. The individuals returning the gauge were not identifiable because they were wearing masks at the time. Carro and Carro had a radiation safety consultant check the gauge. No damage to the gauge was noted, however it had been returned without its storage case. A new case will be ordered. Notified R1DO (Dwyer) and FSME DEO (McIntosh). Notified ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-06-14
46006 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-06-14 13:05 | 2010-06-14 16:07 | 2010-06-14 | FITNESS FOR DUTY - NON-LICENSED CONTRACT SUPERVISOR A non-licensed contract security supervisor tested positive for an illegal substance on a random fitness-for-duty test. The supervisor's access to the plant has been denied. A review of the individual's work history is being performed. The NRC Senior Resident Inspector has been informed. Contact the HOO for additional details | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2010-06-14
46005 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-06-14 03:00 | 2010-06-13 15:00 | 2010-06-14 | PLANNED MAINTENANCE ON TSC EMERGENCY VENTILATION SYSTEM "On June 14, 2010 at 0300 hours, Limerick Generating Station will apply a clearance to inspect and repair Fire Suppression Equipment associated with the Onsite Technical Support Center (TSC) Emergency Ventilation System and perform corrective maintenance associated with MD-1 (Outside Air Damper). During the time that the clearance is applied, the TSC Ventilation System will not be available to be restored in a time period required to staff and activate the TSC Emergency Response Organization. This work is expected to be completed on June 16, 2010. "If an emergency is declared requiring TSC activation, the TSC will be staffed and activated using emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature. Radiological or other conditions. If relocation becomes necessary, the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable Site procedures. "This notification is being made in accordance with 10CFR50.72(b}(3)(xiii) due to the Loss of an Emergency Response Facility (ERF) because of the Unavailability of the Emergency Ventilation System. The NRC Resident Inspector has been informed." * * * UPDATE FROM BROILLET TO HUFFMAN AT 2206 EDT ON 6/14/10 * * * The TSC Emergency Ventilation System was returned to service at 2150 EDT on 6/14/10. The licensee has informed the NRC Resident Inspector. R1DO (Holody) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-13
46004 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-06-13 00:35 | 2010-06-13 03:01 | 2010-06-13 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTIVATION "Notification of an inadvertent siren activation by Goodhue County (MN) authorities. "At 0035 (CDT) on June 13, 2010, the Prairie Island Shift Manager was notified by plant security that the Goodhue County Dispatcher had inadvertently pressed a touch screen and activated all sirens in the county. The sirens were deactivated within 10 to 15 seconds. "The [NRC] Resident Inspector has been informed [by the licensee]." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-13
46003 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-06-12 06:44 | 2010-06-12 09:14 | 2010-06-12 | MANUAL REACTOR TRIP DUE TO A CONTROL ROD DROP INDICATION "McGuire Unit 1 was operating at 44% power due to a previously dropped control rod. Indication was received of a second control rod drop and the reactor was manually tripped in accordance with abnormal operating procedure guidance. All control rods fully inserted. The auxiliary feedwater system was manually started due to an approaching autostart setpoint. The unit is stable in Mode 3 at normal operating temperature and pressure. "Normal containment air release remains in progress." The steam generators are being fed through the auxiliary feedwater system and will transition to the normal feedwater system. Decay heat removal is to the condenser through the steam dumps. There was no impact on Unit 2. The licensee is investigating the cause of the control rod drop indication. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 44 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-06-12
46002 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2010-06-11 16:00 | 2010-06-11 17:21 | 2010-06-14 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE At approximately 1600 CDT local time, a Kansas Licensee, Team Industrial Services Inc., reported that they had a radiography camera source become stuck during source retraction. While they were retracting the source, the stand tipped and resulted in the guide tube being bent such that the source could not be fully retracted. The licensee was able to secure the area easily since the shot was being conducted in a vault. Personnel exited the area and the licensee contacted their corporate RSO in Hammond, Indiana. There is no concern by the licensee of any over-exposure. The State, after talking with the licensee's corporate RSO, authorized recovery by a person on-site who is listed under the NRC license in Indiana. The State is expediting reciprocity paperwork to recognize the source recovery. Kansas # KS-100005. * * * UPDATE FROM DAVE WHITFILL TO STEVE SANDIN AT 1848 EDT ON 6/11/10 * * * At 1725 CDT the source was successfully retracted. Notified R4DO (Powers) and FSME (Mauer). * * * UPDATE FROM DAVE WHITFILL TO BILL HUFFMAN AT 1716 EDT ON 6/14/10 * * * The State of Kansas provided the following additional details on this event via facsimile: "Equipment involved: QSA Global model 880D exposure device s/n D3027, Iridium 192 s/n 59219B, 26.6 curies, with associated equipment including drive mechanism, guide tube. And a tungsten collimator. "Description of incident: At approximately 3:15 pm, the magnetic stand used during the exposure set up fell at the conclusion of a radiographic exposure and impacted the source guide tube causing it to crimp and preventing the source assembly from returning to the fully shielded position within the exposure device. "Actions taken to resolve: The exposures were conducted within a shielded room thereby providing radiation attenuation and enhancing control of the area during incident remediation activities. There were no exposures to unmonitored persons or members of the general public. The Radiographer immediately contacted emergency response personnel within Team Industrial Services, Inc. including the Corporate Radiation Safety Officer. The CRSO performed a preliminary assessment of the event and contacted Kansas Department of Health and Environment. A retrieval plan was developed and discussed with on site personnel. The plan used involved the placement of additional shielding (including available steel and bags of welding flux) at the source location using an overhead crane. This reduced the radiation levels to the point that the radiographer could approach the location of the crimp and remove the crimp by applying pressure using large adjustable pliers (i.e. channel-lock type). He then retracted the source into the fully shielded position within the exposure device, surveyed, and locked the device. The exposure for the complete activity including the radiographic operations was 120 mrem for the radiographer and 75 mrem for the assistant radiographer as registered on their assigned direct reading dosimeters. "Corrective Actions taken: The damaged guide tube was immediately removed from service. An inspection of the device and drive assembly, including the drive cable and source assembly, will be conducted to determine if any damage occurred before releasing for continued use. An investigation into the use of the magnetic stand will be conducted to try to determine the problems associated with the use of this type of source positioning device." Notified R4DO (Powers), R3DO (Kunowski), and FSME (Mauer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2010-06-16
46001 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-06-11 09:45 | 2010-06-11 14:56 | 2010-06-11 | UNANALYZED ACCUMULATION OF MATERIAL IN THE URANIUM RECOVERY AREA "Maintenance was being performed on a dissolver enclosure in the Uranium Recovery Facility. Part of the maintenance activities included the spraying of water on the interior surfaces of the enclosure to reduce contamination. A small quantity of this water leaked into an adjoining pass-through glove box, which also had loose contamination on its interior surfaces. As a result, approximately 1 liter of solution with a concentration of approximately 26 grams 235U per liter accumulated on the floor of the pass-through glove box. The amount of uranium mass within the accumulated solution was much less than the minimum amount required for criticality. There was no immediate risk or threat to the safety of workers or the public as a result of this event. "An evaluation is currently being performed on this event. "BWXT is making this 24 hour report in accordance with 10 CFR 70.61, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of [10 CFR] 70.61. "The dissolver system is shutdown pending further investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-06-15
46000 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-06-10 | 2010-06-11 12:15 | 2010-06-11 | AGREEMENT STATE REPORT - PROCESS GAUGE MALFUNCTIONS "On June 11, 2010 at 1100 Central Daylight Time, the Agency, [Texas Department of Health,] was notified by the licensee that the shutters on six gauges failed in the open position. Three of the gauges were manufactured by Berthold [Model 7400D] and each contained 30 millicuries of Cesium (Cs) - 137 (S/N's: 2423, 2425, 2426). The other three gauges were manufactured by Ohmart/VEGA [Model SHD] and each contained 150 millicuries of Cs-137 (S/N's: 74452, 74453, 73491). The licensee stated that dose rates taken in the area were normal, since the shutters failed in their normal operating positions. The licensee has contacted the manufacturer to schedule a repair of the gauges. The Agency reminded the licensee to request an exemption to continue to use the gauges while their shutters are awaiting repair so that that the licensee would not violate a condition of their license." A contractor is making arrangements for the gauges to be repaired by their manufacturers. Texas Incident No: I-8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-06-16
45999 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-06-10 | 2010-06-10 11:18 | 2010-06-10 | AGREEMENT STATE REPORT - BRACHYTHERAPY DOSE RECEIVED WAS GREATER THAN 20% OF PRESCRIBED DOSE The following was received from the State via fax: "On June 9, 2010, the Radiation Safety Officer (RSO) reported that earlier that day a patient undergoing an intravascular brachytherapy procedure was administered a dose to the coronary artery exceeding the prescribed dose by more than 20%. This is a medical event as described in DHS 157.72(1)(a)1. The prescribed dose was 18.4 Gy; the dose delivered was 23 Gy. The treatment device is a Novoste Beta-Cath intravascular brachytherapy device containing Sr-90. The overdose was identified during the post-planning for the procedure. The treatment time for this procedure is based on the measured diameter of the coronary artery. Depending on the diameter, one or three treatment times is selected; in this case the wrong treatment time was selected. The RSO stated that this treatment time is supposed to be independently reviewed and approved on the written directive, which is to be signed by the authorized user. The written directive was not signed by the authorized user prior to administration. [Wisconsin] DHS inspectors will investigate this medical event on June 11, 2010." Event Report No.: WI100008 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-06-16
45998 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-06-10 08:30 | 2010-06-10 10:37 | 2010-06-10 | TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "On June 10, 2010, at 0830 hours CDT, Byron Station removed part of the Technical Support Center (TSC) ventilation (I.e., OVV25C) filtration system from service to facilitate necessary maintenance on the makeup fan. This work is expected to last approximately 10 hours. This maintenance affects the ability of the TSC ventilation to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. If the TSC becomes uninhabitable, then the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility because of the unavailability of the emergency filtration mode of the ventilation system. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM MIKE LINDEMANN TO PETE SNYDER AT 1542 EDT ON 6/10/10 * * * Maintenance has been completed and the TSC ventilation system was returned to service as of 1430 CDT. The licensee notified the NRC Resident Inspector. Notified R3DO (Phillips). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-10
45997 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-06-09 11:35 | 2010-06-09 20:02 | 2010-06-09 | BATTERY ROOMS DECLARED INOPERABLE DUE TO POTENTIAL FLOODING "At 1135 CDT, during a plant walkdown, it was observed that the battery room doors to the Unit 1 and Unit 2 turbine building bottom gap seals were not in contact with their respective door thresholds. The gap was approximately 0.25 inches. It is necessary for each of the door seals to be in contact with the thresholds for the plant to be in the configuration assumed by the turbine building High Energy Line Break (HELB) flooding evaluation. "An analysis was performed of the flood height that would be attained in the battery rooms during a postulated HELB induced flooding event. The result of this analysis was estimated to be a water depth above the limit to maintain operability of safety related components in the battery rooms. This critical flood height would be attained in approximately 30 minutes following a HELB which causes damage to cooling water piping. "These postulated water levels could have potentially resulted in a loss of safety function for Unit 1 and Unit 2 components between 1135 and 1250 CDT. "The condition was repaired and the battery rooms were declared operable at 1250 CDT." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-06-09
45996 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2010-06-08 | 2010-06-09 18:36 | 2010-06-09 | AGREEMENT STATE REPORT - WRONG DOSE The following information was received via e-mail: "On June 8, 2010 at approximately 9:45 am, a patient scheduled for a 30 mCi TC-99m Myoview cardiac scan was mistakenly administered a 27.1 mCi Tc-99m Medronate bone dose. The mistake was discovered shortly after the administration of the dose when the technician noticed the name on the dose did not match that of the patient. The bone scan patient and cardiac patient had very similar sounding last names, which contributed to the error. The patient was notified of the error when he returned for his cardiac scan 45 minutes after injection. The actual bone scan patient was sent home without any scan and was not injected with any dose because they caught the error before he arrived for scanning." Event No.: WA 100041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2010-06-15
45995 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2010-05-20 | 2010-06-09 17:38 | 2010-06-09 | UTAH AGREEMENT STATE REPORT - TWO MISSING TRITIUM EXIT SIGNS The following information was obtained from the State of Utah via email: "Two tritium exit signs were purchased and installed between March 2004 and October of 2005 by Shaw Environmental, Inc., as part of a contract with the United States Army Corp of Engineers [performing] renovation of military recruiting centers. Shaw is conducting an inventory of all tritium exit signs purchased and installed under this contract and identified that the listed signs are not located where installation records indicated that they were installed." "Manufacturer: SRB Technologies, Inc.; Model: BetaLux-E, each contains 10 Ci of H-3, Serial Numbers 000102 ([previously located at] 175 S. Main St., Salt Lake City, UT) and C000108 ([previously located at] 545 E. 4500 St., Ste. E-125, Salt Lake City, UT)" This is the third report of missing tritium exit signs discovered during Shaw Environmental, Inc.'s inventory effort. See EN #45972 and EN #45885. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2010-06-14
45994 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-06-09 11:12 | 2010-06-09 16:56 | 2010-06-09 | PRESS RELEASE CONCERNING A CAUSTIC SPILL "On June 9, 2010, at 10:32 PDT, a caustic spill occurred in the DCPP Unit 1 Turbine Building buttress area. On June 9, 2010, at 10:59 PDT the area was restricted for normal access with SCBAs required for entry into the area. On June 9, 2010, at 11:12 PDT an Unusual Event was declared for DCPP Unit 1. The DCPP Unit 1 reactor remains at full power. No safety related equipment has been impacted. "The Unusual Event was declared based on EP G-1 Attachment 2 - 'HU3.1 Report or detection of toxic, corrosive asphyxiant or flammable gases that have entered or could enter the Owner Controlled Area in amounts that can adversely affect normal plant operations.' "The spill amount was reported as 5 gallons. "The spill was due to a ruptured delivery hose. The hose was isolated initially at the delivery truck and the tank being filled. Hose continued to drain due to residual caustic in the hose. It was reported as 'confined' on June 9, 2010 at 11:02 PDT. "The spill was reported as 'contained' on June 9, 2010 at 11:44 PDT. Access to the immediate area of the spill is still restricted." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-09
45993 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-06-09 | 2010-06-09 16:07 | 2010-06-09 | CALIFORNIA AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE MISSING The following information was obtained from the State of California via email: "On June 8, 2010, [the licensee] contacted RHB-Brea [Radiation Health Branch] about a moisture density gauge (CPN MC-3 M39099120, 10 mCi Cs-137, 50 mCi Am:Be-241) that was missing from their facility since approximately June 3, 2010. The facility was searched with no sign of the missing gauge and all operators were questioned and were instructed to search their residences for the gauge. None of the individuals could find the gauge, none of them could recall using the gauge recently and could not recall if they may have used or misplaced the gauge. A review of the gauge log indicated that gauge had been logged incorrectly and that two individuals were logging in the same gauge at the same day and times, preventing a proper accounting of the whereabouts of their gauge. [The licensee] was notified that a police report must be filed, a reward offered, and a written report must be provided to RHB within 30 days. "At this time, the incorrect use of the gauge in/out log is the only root cause identified though it appears that other factors are likely to also be a potential root cause of this incident. While the investigation is ongoing, the licensee will be cited for failing to maintain control of the gauge and failing to properly log the use of their gauges. Further citations will be deferred until the 30-day report has been received or further infractions have been identified by RHB during our investigation. Also, corrective actions will be verified from the 30-day report or from our investigation. " California Report: 5010-060810 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-06-14
45992 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-06-09 11:12 | 2010-06-09 14:30 | 2010-06-09 | UNUSUAL EVENT DECLARED DUE TO TOXIC GAS/CHEMICAL SPILL IN THE PROTECTED AREA "Toxic gas in the Owner Controlled Area that adversely affects normal operations." The licensee declared an Unusual Event under EAL HU3.1 at 1112 PDT. During sodium hydroxide (NaOH) transfer operations on site, a drain valve leak occurred in the condensate polisher buttress area. Onsite personnel responded and stopped the leak. There were no injuries to personnel, no equipment damage and no offsite assistance required. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SIZEMORE TO CROUCH @ 1517 EDT ON 6/9/10 * * * Responder access to area has been restored. Approximately 5 gallons of NaOH have been contained. NOUE exit criteria will be that normal access to the polisher buttress is restored. The licensee has notified the NRC Resident Inspector. Notified IRD (Gott), NRR EO (Thorp) and R4DO (Powers). * * * UPDATE FROM SIZEMORE TO CROUCH @ 1557 EDT ON 6/9/10 * * * The licensee has terminated from the Unusual Event at 1241 PDT. Normal access to all plant areas has been restored. Notified IRD (Gott), NRR EO (Thorp), R4DO (Powers), DHS (Kettles) and FEMA (O'Connel). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-06-09
45991 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-11 | 2010-06-09 12:26 | 2010-06-09 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT "On June 9, 2010 the Incident Investigation Program was notified via email by the Nuclear Regulatory Commission that the licensee had experienced a failure to retract a radiography source that had occurred on March 11, 2010 somewhere in Texas. A radiography crew out of Sulphur, Louisiana was working in Beaumont, Texas, when the 96 Curie, Iridium 192 radiography source became stuck during the crew's 6th exposure (approximately 1250 Central Daylight Time). The two person radiography team then extended their barricade to about 350 feet from the source. The crew notified their sight representative, as well as the Site Radiation Safety Officer of the Sulphur, Louisiana office. While one of the radiographers verified the 2mR/hr boundary with a survey meter, the other stood behind a large pump at the plant and repeatedly tried to crank the source back into the camera. After approximately 7 minutes, the radiographer was able to return the source to the camera. The radiography crew verified the source local in the shielded position with their survey meter. According to the report submitted by the Louisiana Site RSO (LARSO), no members of the public or workers were overexposed. Later that same day, the LARSO met with the radiographers. The LARSO subsequently sent the radiographers' TLD badges to be read on Friday March 12, 2010. The results were returned on Monday, March 15, 2010. According to the report by the LARSO, it was determined that one of the radiographers received 55mR and the other 210 mR as a result of this event. "On March 15, 2010 the crank out assembly was sent to the manufacturer (QSA Global) for inspection and repair. QSA determined that the bearing assembly in the pistol control crank had come apart. Part of the bearing assembly had worked its way into and lodged into the drive gear assembly. The piece of the bearing assembly then caused a tooth of the drive gear assembly to break off. The tooth was large enough to become jammed between the drive gear and the drive cable in the pistol control. This caused the pistol to malfunction. QSA repaired the assembly and all defective parts were replaced, and the assembly passed all tests. "On June 9, 2010 the Texas Department of State Health Services contacted the Radiation Safety Officer (RSO) for the Texas licensee. The RSO stated that she would submit a report to the State of Texas as soon as possible." Texas Incident Number I-8752. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2010-06-14
45990 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-06-09 03:31 | 2010-06-09 07:58 | 2010-06-10 | REACTOR SCRAM DUE TO CLOSURE OF MAIN STEAM ISOLATION VALVES "At 0331 CDT on 6/9/10, the Unit 2 reactor automatically scrammed due to closure of the Main Steam Isolation Valves (MSIVs). Operating Instruction 2-OI-99 section 8.1, Reactor Protection System (RPS) Bus B Transfer from Motor Generator to Alternate, was in progress for planned maintenance. The MSIVs closed during the RPS power transfer. The cause of the closure of the MSIVs is under investigation. "All systems responded as expected to the reactor scram. Safety Relief Valves (SRVs) opened automatically as designed to limit the pressure transient. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling system (RCIC) reactor water level initiation set points were reached and all expected containment isolation and initiation signals were received. Reactor pressure control was established by manually operating one SRV then maintained using the Main Steam Line Drain Valves. RCIC and the High Pressure Coolant Injection system (HPCI) were manually initiated to control reactor water level. The scram was reset, MSIVs were opened, and the Main Condenser was established as a heat sink. Reactor water level control was established with the Reactor Feedwater System and RCIC and HPCI were returned to standby readiness. "At 0408 CDT on 6/9/10, a full scram signal was received when 2F Intermediate Range Monitor (IRM) spiked momentarily followed by a spike on 2C IRM. The reactor was stable and operating in Mode 3, Hot Shutdown. No ECCS or RCIC initiation set points were reached. No additional containment isolation signals or initiation set points were received. The cause of the 2C and 2F IRM spikes is under investigation. "The scram event from critical is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B), 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). The scram received at 0408 CST is reportable within 8 hours 10CFR 50.72(b)(3)(iv)(A), 'any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation,' and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector was notified." All rods fully inserted as a result of the first reactor scram. The plant is currently in a normal, post-trip electrical line-up. All SRVs did reseat. There was no impact to the other two units. * * * UPDATE FROM BILL BAKER TO PETE SNYDER ON 6/10/10 AT 1749 EDT * * * "Additional review of available data and inspection results revealed that Safety Relief Valves (SRVs) did not lift automatically during the scram. The only operations of SRVs were performed manually to control reactor pressure until the Main Steam Isolation Valves (MSIVs) were reopened. All other details described in the original event notification remain as stated." The licensee notified the NRC Resident Inspector. Notified R2DO (Nease). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-06-09
45989 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2010-06-08 04:30 | 2010-06-08 19:57 | 2010-06-08 | OFFSITE NOTIFICATION OF MINOR HYDAZINE SPILL "At approximately 0430 CDT on June 8, 2010, during restoration following an addition of 10 gallons of hydrazine and a flush of 2 gallons of demineralized water to the Condensate Storage Tank (CST), a water-hydrazine mixture began to leak from check valve KHV0179. KHV0179 is a nitrogen supply check valve that can also be used for hydrazine addition. "Chemistry technicians estimated that a water-hydrazine mixture on the order of 2 gallons leaked through KHV0179 before the line could be isolated. Samples taken from the atmosphere above the spill contained 0.25 ppm hydrazine. The fluid on the ground was measured to contain 15% hydrazine. "The Department of Natural Resources (DNR) was notified of this event at approximately 1000 CDT on June 8, 2010. "The Nuclear Regulatory Commission (NRC) Resident Inspectors will be notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-08
45988 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-06-08 | 2010-06-08 17:15 | 2010-06-08 | TEXAS AGREEMENT STATE REPORT - MEDICAL EVENT On June 8, 2010, the State of Texas was notified by the licensee that during routine chart review, they determined that over a six month period, five patients received 30% to 50% less than prescribed dose. All the patients underwent High Dose Rate Brachytherapy using a Ir-192 Gammamed device. The licensee is still investigating an evaluating patient outcomes due to the under dosages. It is unknown whether the patients and their prescribing physicians were notified. Texas Incident No.: I-8751 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-06-14
45987 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-06-08 11:26 | 2010-06-08 15:10 | 2010-06-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO PRIMARY CONTAINMENT LEAK GREATER THAN LIMITS "On 6/8/10 at 10:15, primary containment was declared inoperable and a 24 [hour] Limiting Condition for Operation (LCO) was entered due to Engineered Safety Features leakage in excess of the 1.0 gpm value assumed in the Alternative Source Term (AST) analysis as described in the UFSAR. "The leakage was from the 'B' RHR heat exchanger relief valve (SR-10-86B) and was estimated at 1.25 gpm. "On 6/8/10 at 11:26, commenced a power reduction for a Technical Specification required shutdown per TS 3.7.A.8. "Actions Taken: "Isolating the 'B' RHR system per Technical Specifications that will allow us to exit the 24 hour LCO. "Planning to replace the relief valve. "Verified relief valve on 'A' RHR system is not leaking." The licensee has notified State and local authorities and the NRC Resident Inspector. The licensee also anticipates a press release. * * * NOTIFICATION FROM KRITZER TO CROUCH AT 1553 EDT ON 6/8/10 * * * The licensee exited the 24 hour LCO TS required shutdown condition at 1548 EDT based on isolation of the 'B' RHR system. R1DO (Henderson) notified. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-06-08
45986 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-06-08 09:48 | 2010-06-08 12:00 | 2010-06-08 | AUTOMATIC REACTOR TRIP WITH SAFETY INJECTION DUE TO LOSS OF VITAL AC BUS "At 0948 hours [EDT] on 6/8/10, a Unit 1 vital AC bus was lost when the uninterruptible power supply inverter failed while the alternate AC source was out of service for scheduled maintenance. The loss of the vital bus inverter caused a loss of 120 VAC vital bus 1-III. The loss of this vital bus caused the 'A' main feed pump recirculation valve to fail open and also caused 2 of the 3 main feedwater regulating valves to fail to automatic-hold mode of operation. This combination of as designed failures resulted in a reduction in main feedwater flow and resulted in an automatic reactor trip due to a feed flow steam flow mismatch in conjunction with low steam generator level. "The loss of vital bus 1-III also resulted in initiation of safety injection due to loss of vital bus 1-III instrumentation in conjunction with the expected momentary RCS cooldown below 543 DEG-F. The safety injection resulted from the high steam flow in conjunction with low RCS T-ave actuation signal. The safety injection actuation also resulted in automatic start of the #1 Emergency Diesel and the #3 Emergency Diesel Generators. Neither EDG was required to load since off-site power remained operable. "The loss of vital bus 1-III also resulted in loss of numerous field inputs to the Plant Computer System [PCS] and resulted in non-functionality of the SPDS [Safety Parameter Display System]. The PCS itself remains functional along with MCR [Main Control Room] annunciators and sufficient MCR instrumentation to monitor critical safety functions. All three auxiliary feedwater pumps automatically initiated as designed on low-low steam generator level following the trip. Currently, RCS temperature is being maintained stable at 547 degrees. All systems functioned as required following the reactor trip. During the post-trip transient, pressurizer PORV [Power Operated Relief Valve], PCV-1455C, cycled as required to maintain RCS pressure due to the safety injection and the loss of normal letdown. "There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(B), 10CFR50.72(b)(2)(iv)(A), 10CFR50.72(b)(3)(iv)(A), and 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector was notified of this event." During the trip, all rods inserted into the core. In addition to the pressurizer PORV lifting, a secondary main steam relief valve lifted. All relief valves properly reseated and there is no known primary to secondary leakage. The plant is in its normal shutdown electrical lineup. Main steam trip valves were isolated during the transient. Decay heat is being removed via main steam bypasses to the condenser and steam generator power operated relief valves. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) | 0 | 2010-06-08
45985 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-06-07 18:44 | 2010-06-07 22:13 | 2010-06-07 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO VOIDING IN THE COMPONENT COOLING WATER SYSTEM "[The licensee] commenced Tech Spec required shutdown at 1844 [CDT] on 6/7/10. Shutdown was commenced due to entry into [Technical Specification] 3.0.3 at 1828 hrs. on 6/7/10 due to voids in Component Cooling Water (CCW) Train causing both trains to be inoperable. "While operating in Mode 1 at 100% rated thermal power, voids were found in the 'B' CCW train that was above the acceptable volume. 'B' CCW train was declared inoperable at 1828 hrs.. 'A' CCW train was already inoperable due to voids. Both trains inoperable required entry into Tech Spec 3.0.3. Shutdown was commenced at 1844 hrs. All system functioned normally. [The NRC] Senior Resident Inspector has been contacted." During the shutdown, the licensee determined that voiding in the "B" train didn't reach the level required to render the "B" train inoperable and stopped the shutdown at 80% power. The licensee intends to begin a power ascension after re-verifying the voiding in the "B" train. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-06-07
45984 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-06-07 | 2010-06-07 15:07 | 2010-06-07 | WISCONSIN AGREEMENT STATE REPORT - STUCK OPEN PROCESS GAUGE SHUTTER The following information was received from the State via facsimile: "On June 7, 2010 a representative of West Short Pipe Line Company notified Wisconsin Radiation Protection Section of a stuck shutter. This was discovered during a routine six-month shutter check. The device is a Ronan SA1 containing 500 mCi of Cs-137. The general licensee performed a radiation survey and radiation levels were normal. Licensee also performed routine leak test, results are pending. Normal operation for the device is with the shutter open. The device is located in a restricted area that is fenced off. The nearest personnel access point is 600 ft away from the device. The licensee will contact the manufacturer for service. "The Radiation Protection Section will continue to monitor the situation and will request information concerning the cause of the stuck shutter." Wisconsin Report No: WI100007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-06-10
45983 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-06-07 | 2010-06-07 14:26 | 2010-06-07 | FLORIDA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of Florida via facsimile: "[The State of Florida] received a report from the company's RSO [Radiation Safety Officer] that a soil moisture density gauge and case was stolen. The licensee parked their truck and left the gauge unattended. Owner still has keys to case and gauge. Unknown as of yet if gauge was chained and locked to vehicle. Licensee will offer a reward. Local police have been notified and licensee is currently awaiting their arrival. Incident assigned to Miami Inspection Office for investigation." The gauge was a Troxler Moisture Density gauge, model 3440, serial number 37225. The gauge has a 40 mCi AmBe-141 source and a 8 mCi Cs-137 source. Florida incident number: FL10-070 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-06-10
45982 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2010-06-07 10:20 | 2010-06-07 13:47 | 2010-06-07 | NOTIFICATION OF FATALITY "At approximately 0918 EDT a contract diver entered the Indian Point discharge canal for scheduled work on the outfall structure. At approximately 0928 hours the diver was unresponsive to communications and was pulled from the water. An Emergency Medical Technician (EMT) stationed at the job site performed emergency medical assistance and an ambulance was requested. The diver was transported to a local hospital where the diver was pronounced dead at 1020 EDT. An investigation of the event is in progress." The licensee has notified State and local authorities. The licensee will also be notifying OSHA and plans to issue a press release. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-07
45981 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-04-16 19:15 | 2010-06-07 11:03 | 2010-06-07 | INVALID SPECIFIED SYSTEM ACTUATION "Invalid actuation of ECCS for boiling water reactors (BWRs) including: high-pressure and low-pressure core spray systems; high pressure coolant injection system; low pressure injection function of the residual heat removal system. "The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of the 10CFR50.73(a)(2)(iv)(B) system checked above. NUREG1022 Revision 2 identifies the information that needs to be reported as discussed below. "This report is being made under 10CFR50.73(a)(2)(iv)(A). On April 16, 2010, at 1717 EDT, Unit 1 received a false ECCS (Emergency Core Cooling System) Loss Of Cooling Accident (LOCA) signal on high drywell pressure. Based on plant data, all plant conditions were normal prior to event. Investigation identified an ATTS Slave Card failed in one of the Card File Racks. The Card File Rack contains ten (10) cards with two (2) being Master Trip Units (MTUs) that actuate on high drywell pressure. For initiation of an ECCS LOCA signal, both of the MTUs in the card file rack would have had to actuate. Cause of the event appears to be a momentary drop in supply voltage on the card file rack due to the failed slave card that lowered the set point of the MTUs to a point where they tripped. The set point is an internal voltage setting within the MTU. The failed ATTS cards have been replaced. "Actuations: Core Spray A and B pumps started; Residual Heat Removal A, B, C, D pumps started; Diesel Generator 1A, 1B, and 1C started; Standby Plant Service Water Pump started; Plant Service Water 1A pump started (it had been in standby); Plant Service Water Valves 1P41-F310A, B, C, D closed (These are the Turbine Building isolation valves); Turbine Building Chiller B tripped; Main Control Room Environmental Control trains A and B started; HPCI Started but was secured prior to injection; Cooling Tower fans on towers A, B, C tripped. "Reactor Water Level was normal at +37 inches and the highest Drywell Pressure indicated was 1.25 psig." The licensee has notified the NRC Resident Inspector. | 86 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-06-07
45980 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-06-06 11:37 | 2010-06-06 12:37 | 2010-06-06 | BRUNSWICK DECLARED ALERT DUE TO HALON DISCHARGE IN EMERGENCY DIESEL GENERATOR BUILDING At 1137 EDT, Brunswick Units 1 & 2 declared an Alert condition due to a discharge of Halon gas into the basement of the emergency diesel generator building (EAL H.A.3.1 for toxic gas discharge into a vital area). Initial inspection indicates that there is no fire. No offsite assistance was required and no personnel injuries as a result of the discharge. Both reactors continue to operate at 100% power. The licensee is investigating the cause of the discharge and will terminate the Alert when the area is ventilated and can be reoccupied. The licensee has notified State and local authorities and the NRC Resident Inspector. * * * UPDATE TO ABRAMOVITZ FROM CINDRIC AT 1616 EDT ON 6/6/10 * * * The licensee terminated the Alert at 1614 EDT based on restoring normal atmosphere conditions in the emergency diesel generator building. The initiating cause of this event is still being investigated. State and local authorities have been notified and the Resident Inspector will be notified. The NRC Operations Center has notified the Federal Agencies initially notified of this event. R2DO (Vias), NRR EO (Galloway) and IRD (Grant) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-06-06
45979 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-06-06 02:38 | 2010-06-06 03:10 | 2010-06-07 | AUTOMATIC REACTOR SCRAM DUE TO PARTIAL LOSS OF OFFSITE POWER "Reactor shutdown. All control rods inserted. Maintaining reactor vessel level with reactor core isolation cooling. Maintaining reactor vessel pressure with reactor core isolation cooling. [Automatic] Reactor scram due to loss of division 2 offsite power. Classification code: Unusual Event (HU1) Natural Destruction Phenomena Affecting the Protected Area." The licensee declared a Notification of Unusual Event at 0253 EDT. All rods fully inserted and decay heat is being removed by the main condensers. Division 1 buses are being powered by 1 of 3 offsite feeds and division 2 buses are being powered by the Emergency Diesel Generators. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JEFF GROFF TO DONG PARK AT 0425 EDT ON 6/6/2010 * * * "Division 2 power provided by Emergency Diesel Generators number 13 and 14. Classification Alert Code: (HA1) Natural Destruction Phenomena Affecting the Plant Vital Area. Main condenser is the heat sink." The licensee declared an Alert at 0417 EDT. The reactor remains stable in Mode 3. Physical damage to the auxiliary and the turbine buildings were noticed after an initial inspection. The licensee has notified the NRC Resident Inspector. Notified R3RA (Satorius), NRR (Grobe), IRD (Morris), R3DO (Pelke), NRR EO (Galloway), DHS (Doyle), FEMA (Guy), DOE(Morrone), USDA (Ussery), HHS (Standifer), and CNSC (Gdesnryxrs). * * * UPDATE FROM JEFF GROFF TO DONG PARK AT 0603 EDT ON 6/6/2010 * * * "At 0238 [EDT], severe weather caused a loss of 345KV [switchyard power]. Reactor scrammed from a turbine trip. Plant is stabilized with RPV [Reactor Pressure Vessel] water level in normal band and RPV pressure at 820 psig. RPV Pressure is being controlled on turbine BPV [By Pass Valve]. Division 2 EDG's [Emergency Diesel Generator] are supplying power to division 2 buses. Plant is currently in Alert due to physical damage to plant due to severe weather." The NRC Senior Resident Inspector is on-site. Notified IRD (Morris), R3DO (Pelke), NRR EO (Galloway). * * * UPDATE FROM ED KOKOSKY TO DONG PARK AT 0247 EDT ON 6/7/2010 * * * "There is no release of radiological materials. No further potential exists for uncontrolled release of radioactive materials to the environment. The Reactor is shut down. Reactor pressure and temperature are within normal bands. Offsite electrical feeds to the site have been restored. An overall damage assessment has been prepared and reviewed to ensure no conditions exist that would create an entry condition to the Emergency Plan. Plant repairs will be accomplished through site processes." At 0220 EDT on 6/7/10, the licensee has terminated from the Alert classification. The licensee has notified the NRC Resident Inspector. Notified R3RA (Satorius), NRR (Grobe), IRD (Grant), R3DO (Pelke), NRR EO (Galloway), DHS (Doyle), FEMA (Blankenship), DOE(Bailey), USDA (Ussery), HHS (Peagler), and CNSC (Gdesnryxrs). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2010-06-06
45978 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2010-05-04 | 2010-06-04 15:20 | 2010-06-10 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION A patient was treated in early May with a vaginal applicator using three doses of High Dose Rate (HDR) brachytherapy. On May 11, 2010, the patient contacted the doctor's office and complained of skin irritation to her leg. On May 18, 2010, the patient again called to report continued skin irritation. On both of these dates, the patient could not come in to see the doctor. On May 26, 2010, the patient was seen by the doctor and radiation irritation was evident on her leg. Initial estimates of the leg dose are greater than 50 REM. Both the patient and doctor have been notified of this event. The source was Yttrium (unknown strength). [See correction below] The State is investigating this event. * * * UPDATE FROM CARL SULLIVAN TO PETE SNYDER ON 6/10/10 AT 1156 EDT * * * The event date in the header was corrected to 5/4/10. The source was Ir-192 with an activity of 3506.34 mCi on 5/4/10. The State continues to investigate this event. Notified R4DO (Shannon) and FSME (Villamar). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2010-06-10
45977 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2010-06-04 10:20 | 2010-06-04 13:40 | 2010-06-04 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2010-06-04
45976 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-06-04 09:30 | 2010-06-04 13:30 | 2010-06-04 | ACTIVE CRITICALITY CONTROLS NOT IN IROFS "During a GNF-A [Global Nuclear Fuels - America] review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was determined at 9:30 AM today (6/4/10) that the list of Items Relied On For Safety (IROFS) associated with the Dry Scrap Recycle Furnace operation was incomplete in the ISA Summary. Although criticality controls exist and these controls associated with moderation intrusion and geometry remained in place, functional, and maintained with appropriate management measures, they were not declared or documented in the ISA as IROFS. "The existing criticality safety analyses of the operation bound the situation, were effective, and were not challenged. At no time was an unsafe condition present. "The affected equipment has been shut down pending revision of the ISA to document IROFS for this process. While this did not result in an unsafe condition, this event is being reported for administrative reporting pursuant with the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours of discovery." The licensee will be changing the list of IROFS to include these criticality controls. The licensee will notify Region II (Gibson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2010-06-04
45975 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-06-03 10:50 | 2010-06-03 17:14 | 2010-06-03 | SECONDARY CONTAINMENT BRIEFLY DEGRADED "On June 3rd, 2010, at 1050 CST, both doors in Airlock 413 from Secondary Containment (SCT) to the Rad Waste 985' Pump Room were opened simultaneously for approximately five seconds and subsequently re-closed. This condition caused an unplanned entry into Technical Specification 3.6.4.1.A for SCT. The condition could have prevented the Standby Gas Treatment system from developing a negative pressure within SCT following a design basis accident. "This negative pressure is required to prevent ground level releases of radioactivity and minimize onsite and offsite dose consequences following an accident, The Standby Gas Treatment system remained operable throughout the event. The site continues to assess the situation." The licensee has notified the NRC Resident Inspector and will also notify State authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-06-03
45974 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2010-05-25 11:35 | 2010-06-02 16:16 | 2010-06-02 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE "Kentucky Department for Public Health Protection and Safety was notified on May 25, 2010, by the RSO for Hinkle Contracting Corporation that a radiological incident involving an accidental crushing of a density gauge occurred at Georgetown Municipal Airport 6206 Paris Pike, Georgetown, KY. Gauge was identified by [the RSO] as a Troxler 4640B Thin Layer Density Gauge. Troxler Gauge containing 9 milliCuries of Cs-137 had been crushed when an asphalt roller struck it. Based upon exposure rate measurements, visual verification, and review of Troxler 4640B specification data, it was determined by the [State of Kentucky] Radiation Health Branch that the radiation source had not been compromised." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2010-06-07
45973 | 0 | BRISTOL HOSPITAL |  |  |  |  | 2010-01-12 | 2010-06-02 15:46 | 2010-06-02 | DOSE LESS THAN PRESCRIBED DOSE IN TWO SEPARATE BRACHYTHERAPY TREATEMENTS "[Patient #1], with localized prostate cancer, had an ultrasound directed transperineal implant with 60 I-125 seeds on 1/12/2010. The total activity implanted was 20.4 mCi. Final dosimetry was based on a CT scan performed on 2/16/2010. This revealed a D90 of 8400 cGy which was lower than the prescribed dose of 14500 cGy. The patient and referring physician were notified and the patient then received supplemental external beam irradiation of the prostate with 3000 cGy delivered between 3/11/2010 and 4/08/2010. The patient is currently doing well with minimal treatment related symptoms. "[Patient #2], with localized prostate cancer, had an ultrasound directed transperineal implant with 66 Cs-131 seeds on 1/12/2010. The total activity implanted was 186 mCi. Final dosimetry was based on a CT scan performed on 2/16/2010. This revealed a D90 of 6500 cGy which was lower than the prescribed dose of 11000 cGy. All seeds were accounted for in the final review. However, careful review of the isodose lines revealed adequate coverage of the involved areas of the prostate. The patient and referring physician were notified and the prescribing physician indicated that additional treatment was not necessary. "[Both] events occurred due to unexpected displacement of the seeds in an inferior (caudal) direction. "[The licensee] continues to use preplanning for all prostate brachytherapy patients with careful direct supervision of needle and seed placement. Six (6) patients have been treated with brachytherapy at Bristol Hospital since January 2010 and the final dosimetry has been acceptable for all." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-06-08
45972 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-05-27 | 2010-06-02 15:00 | 2010-06-02 | OHIO AGREEMENT STATE REPORT - THREE TRITIUM EXIT SIGNS MISSING The following information was obtained from the State of Ohio via email: "A contractor installed tritium self-illuminating exit signs between March 2004 and October 2005 at various locations as part of a US Army Corps of Engineers contract to renovate military recruiting centers. The contractor recently conducted an inventory of the signs it had installed and discovered that some signs were not located where the installation records indicated that they had been installed. "The signs in question are SRB Technologies, Model BetaLux-E, containing 10 Ci of H-3. Three (3) signs identified as missing in Ohio are: S/N 004222, installation address 1300 State Street, Alliance, Ohio, 44601 and S/Ns 009242 and 009243, installation address 2531 Franks Way, Columbus, Ohio, 43232. "The signs were not located during a physical inspection of the properties. Interviews with personnel currently occupying the sites provided no information as to the disposition of the signs. The contractor is currently replacing the H-3 signs with electric signs and is returning the H-3 signs to the manufacturer for proper disposal. "Contractor: Shaw Environmental, Inc. of Stoughton, MA." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-06-07
45971 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-06-01 12:39 | 2010-06-01 18:03 | 2010-06-01 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM DISCOVERED TO BE NON-FUNCTIONAL "At 1239 CDT on June 1, 2010, Byron Station Technical Support Center (TSC) ventilation (OW25C), filtration system was identified as nonfunctional. This failure affects the ability of the TSC ventilation to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities of the TSC are unaffected by this emergent condition. Currently, troubleshooting/investigation is being performed. This condition is considered a major loss of emergency assessment capability and is reportable under 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-01
45970 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-05-24 02:00 | 2010-06-01 17:22 | 2010-06-01 | MISSISSIPPI AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE SOURCE UNABLE TO BE RETRACTED TO SHIELDED POSITION The following information was obtained from the State of Mississippi via email: "On May 24, 2010 around 2:00 a.m. [CDT], a Portable Moisture Density gauge was run over by an asphalt roller. The casing of the gauge was damaged. DRH [Mississippi Division of Radiation Health] was notified and supplied with the following measures of radiation, 22 mR/hr at the surface of the damaged gauge and 0.75 mR/hr at approx. 3 feet from the gauge. DRH [was] informed that the gauge could be safely placed in a sealable carrying case. It was determined that the Cs-137 source was not returning to its fully shielded position. A DRH official went to the site the next morning with a small lead pig. The source holder was extended a few inches in order to tape the pig on the rod's end. The damaged gauge was then taken to MDOT [Mississippi Dept. of Transportation] storage site and a leak test was performed. The wipes were analyzed by the MSDH [Mississippi State Department of Health] Radiological Health Lab. The measured activity was well below the regulatory upper limit of .005 microCuries. Wipe analysis was received 5/26/2010." Isotope(s): Cs-137, 8 mCi and Am-241:Be, 44 mCi. Report No: MS-10004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2010-06-04
45969 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2010-06-01 15:50 | 2010-06-01 16:57 | 2010-06-02 | POTENTIAL LOSS OF RADIATION RELEASE CONTROLS "On May 27, 2010, during a control board walkdown, it was discovered that two sets of auxiliary building tunnel exhaust dampers were open at the same time. This configuration created a pathway from the secondary containment to the outside. The condition was immediately corrected. Additional investigation determined that this condition existed since May 11, 2010, when Millstone 3 was in Mode 5. "Technical Specification 3.6.6.2 'Secondary Containment' is applicable in Modes 1, 2, 3, and 4. The condition discovered on May 27, 2010, rendered Secondary Containment inoperable. Further evaluation since the discovery date concludes that the secondary containment structure was in a condition which could prevent the fulfillment of the safety function for controlling the release of radioactive material. [On June 1, at 1550 EDT the licensee determined that the event was potentially reportable]. "An investigation is on-going. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(c). "The NRC Senior Resident Inspector has been notified [by the licensee]." The State of Connecticut and the Town of Waterford were notified. A press release will be issued. * * * UPDATE FROM FRED PERKINS TO HOWIE CROUCH @ 1304 EDT ON 6/2/10 * * * The licensee reported that no press release will be issued for this event. They will be notifying the NRC Resident Inspector. Notified R1DO (Dentel) | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2010-06-01
45968 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-06-01 07:15 | 2010-06-01 15:36 | 2010-06-01 | PUBLIC WARNING SYSTEM SIREN OUT OF SERVICE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On June 01, 2010, at approximately 0715 Mountain Standard Time (MST), the Palo Verde Emergency Planning Department discovered that public warning system siren No. 17 was not responding, and therefore, is out of service. The loss of siren No. 17 could potentially impact a population of approximately 1196 people in the 5-mile Emergency Planning Zone (EPZ). "Since the loss of siren No. 17 could impair Arizona Public Service Company's ability to inform greater than 5% of the population within the EPZ, this notification is being made in accordance with 10 CFR 10.72(b)(3)(xiii). If an event occurs while siren No. 17 is out of service, the Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area. The MCSO is prepared to implement this contingency should it become necessary. "The NRC Resident Inspector has been notified of siren No. 17 being out of service and this ENS call." * * * UPDATE FROM DAVE OAKES TO HOWIE CROUCH @ 1818 EDT ON 6/01/10 * * * "Siren number 17 was returned to service at 1435 MST. The NRC Senior Resident Inspector has been notified." The remote radio was replaced and all post-maintenance testing was completed. Notified R4DO (Werner). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-01
45967 | 0 | NUCLETRON CORPORATION |  |  |  |  | 2010-05-28 15:30 | 2010-06-01 14:30 | 2010-06-01 | POTENTIALLY LOST SOURCE On the afternoon of May 28, 2010, Nucletron Corporation (Columbia, Maryland) received a call from 21st Oncology Katin Radiation (Martinsburg, West Virginia) who received a phone call from QSA Global (Burlington, Massachusetts) saying they received a call from a GM plant located in the Martinsburg, West Virginia general area. The GM plant had mistakenly received a properly shielded radiation source from a common carrier. Because of an exception in the shipping paperwork, the shielded source was supposed to be shipped back to Katin Radiation. The device is a Microselectron HDR Brachytherapy Afterloader: serial number #31836. The source is IR-192, 4.69 Ci, serial number D36C-1703. The common carrier is investigating the driver's routing and logistics during the day of the event in order to track the source. * * * UPDATE FROM DEBRA BENSEN TO VINCE KLCO ON 6/1/10 AT 1759 EDT * * * Notified by the licensee that the source was located at a GM plant in the Martinsburg, West Virginia area. The common carrier picked up the source and delivered it to Katin Radiation at 1632 EDT. The source packaging was inspected and showed no evidence of damage or tampering. Notified the R1DO (Dentel), FSME (Camper), and ILTAB (English). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-06-01
45966 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-05-30 21:15 | 2010-06-01 12:10 | 2010-06-01 | LATE NOTIFICATION OF A SINGLE INADVERTENT SIREN ACTIVATION DURING THUNDERSTORM ACTIVITY "At approximately 2115 CDT on May 30, 2010, a Pierce County dispatcher was notified of inadvertent siren activations, momentarily activating for approximately 30 minutes. The dispatcher also indicated there were lightning strikes in the area about the same time. The siren vendor was dispatched and the issue was tracked down to a single siren; no physical damage was observed, however, the siren was declared out of service by the siren vendor." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-06-01
45965 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2010-06-01 09:00 | 2010-06-01 11:45 | 2010-06-01 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PREVENTIVE MAINTENANCE "On June 1, 2010, at 0900 hours CDT, Clinton Power Station removed the Technical Support Center (TSC) ventilation system from operation to facilitate preventive maintenance to replace charcoal media in the ventilation system filter assembly. "This work is expected to last approximately 3 days, during which the TSC ventilation system will be unavailable. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification is being made in accordance with 10CFR50.72 (b) (3) (xiii) due to the potential loss of an emergency response facility (ERF) because of the unavailability of the emergency filtration mode of the ventilation system. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM ED TIEDEMANN TO HOWIE CROUCH @ 1716 EDT ON 6/1/10 * * * "At 1300 hours CDT, the charcoal media in the ventilation system filter assembly has been replaced and post maintenance testing completed satisfactorily. The TSC ventilation system is now available." The licensee has notified the NRC Resident Inspector. Notified R1DO (Pelke). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-06-01
45964 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-05-29 17:30 | 2010-05-29 21:16 | 2010-06-21 | CONTAINMENT PURGE ISOLATION SIGNAL CAUSED CONTROL ROOM ISOLATION SYSTEM ACTUATION "While operating in Mode 1, 100% rated thermal power (RTP), Wolf Creek received a Containment Purge Isolation Signal (CPIS) caused by Containment Purge Exhaust Radiation Monitor GT RE-33 exceeding the high radiation trip setpoint. There was no containment purge in progress at the time of the CPIS so no containment dampers actuated or were required to actuate. Control Room Ventilation Isolation Signal (CRVIS) was also received, as expected, from the actuation of the CPIS. All CRVIS components actuated as required. Review of GT RE-33 identified that the radiation monitor spiked high causing the CPIS then returned to normal values. All other containment radiation monitors are indicating normal values. "The NRC Resident has been notified of this event by the Licensee." GT RE-33 is currently removed from service. * * * UPDATE AT 1630 EDT ON 06/21/10 FROM RICK HUBBARD TO S. SANDIN * * * "The licensee is retracting this event based on the following: "The Containment Purge Exhaust Radiation Monitor GT RE-33 failed due to a corrupted database initiated by a Radiation Monitor System (RMS) communication loop problem. The signal was not initiated by actual plant conditions or parameters, so this was an invalid actuation. This actuation did not involve a critical scram. So it is not reportable per 10 CFR 50.72." The licensee will inform the NRC Resident Inspector. Notified R4DO (Pick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-05-29
45963 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2010-05-28 09:15 | 2010-05-28 16:11 | 2010-05-28 | NON-LICENSED CONTRACTOR SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed contract supervisor tested positive for alcohol on a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2010-05-28
45962 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-04-02 21:56 | 2010-05-28 14:53 | 2010-05-28 | OVERVOLTAGE CONDITION CAUSES REACTOR PROTECTIVE SYSTEM ACTUATION "On Friday April 2, 2010, Unit 1 refueling outage activities were in progress and the 1A RPS/UPS Static Inverter was being removed from service. At 2156 hours, the inverter static transfer switch was placed in 'Bypass' which transferred the load from the inverter to the secondary alternate source. The manual bypass switch was then placed in 'Bypass' which was followed by the RPS/UPS series breakers tripping on an overvoltage condition. The actuation caused a loss of power to the IA RPS/UPS power distribution panel loads which provides power to the Division 1A and IIA RPS relays and Division IA and IIA NS4 relays. This caused primary containment isolation valves (PCIVs) to automatically close on more than one system. The IB and IIB channels were unaffected. "Troubleshooting determined that the secondary, alternate source voltage was 132 VAC which exceeded the overvoltage setpoint of 126 VAC. During outages, the 13kV bus voltages are higher than on-line voltages due to low operating equipment loading on the buses. The secondary alternate source to the inverter is not regulated which can result in greater than normal voltage to the RPS/UPS loads. "The portion of the primary containment isolation system that received an actuation signal functioned successfully. All of the affected open isolation valves automatically closed. The isolation was a partial actuation. "This 60-day ENS report is being made per 10CFR 50.73(a)(2)(iv)(A) and 10CFR 50.73(a)(1) to report invalid automatic actuation of systems listed in paragraph (a)(2)(iv)(B). The listed system that actuated was general containment isolation signals affecting containment isolation valves in more than one system. Primary containment isolation valves (PCIVs) closed on drywell chilled water (DWCW), reactor enclosure cooling water (RECW), primary containment instrument gas (PCIG), and suppression pool cleanup." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-05-28
45961 | 0 | C&D TECHNOLOGIES INC |  |  |  |  | 2010-05-28 | 2010-05-28 11:23 | 2010-05-28 | POST CORROSION ON DCU BATTERIES The following was received via fax: C&D Technologies, Inc. (C&D) received a report from a non-domestic customer who is not a U.S. licensee concerning cracks in positive post seals in C&D 3DCU-9 batteries. As a precautionary measure, C&D has chosen to treat this customer's report in the same manner as if the report involved a defect claim by parties regarding matters subject to 10 CFR Part 21. This defect is believed to affect DCU product line batteries 3DCU-7, 2DCU-9, and 3DCU-9, manufactured in the period January 1993 through May 2008. These batteries are used in class 1E applications. The facilities affected by this are DC Cook, Nine Mile Point, Grand Gulf, Susquehanna, Columbia, and Sequoyah. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-05-28
45960 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-05-28 00:03 | 2010-05-28 03:43 | 2010-05-28 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF REACTOR COOLANT PUMP "A Unit-2 reactor trip was initiated by a loss of the Unit-2 'B' station service bus. The loss of the 'B' station service bus caused a reactor trip due to the loss of flow on one-of-three loops due to the loss of the 'B' Reactor Coolant Pump. The Auxiliary Feed Water system actuated as expected due to the reactor trip. The plant was stabilized in Mode 3 using the appropriate emergency procedure. "During the transient, the 'B' Reserve Station Service Transformer de-energized and the Unit-2 'H' Emergency Diesel Generator was previously tagged out for planned maintenance. This resulted in the Unit-2 'H' emergency bus being de-energized. The alternate AC diesel generator has been placed in service and is providing power to the Unit-2 'H' emergency bus. The automatic tap changer for the 'C' reserve station service transformer did not work in automatic and had to be manually adjusted to control voltage. Unit-2 'C' Reactor Coolant Pump remains in service. "All control rods fully inserted on the trip and no relief valves lifted or safety valves lifted in either the primary or secondary systems. The turbine drive and 'B' motor driven Auxiliary Feed Water pumps automatically started and injected into the 'A' and 'B' steam generators on a low level signal. The 'A' motor driven Auxiliary Feed Water pump failed to start due to the loss of the 'H' emergency bus. The 'C' steam generator is being controlled with main feed water though the 'C' main feed regulating valve bypass valve. Decay heat removal is via the condenser steam dumps. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM MICHAEL WHALEN TO HOWIE CROUCH @ 1707 EDT ON 5/28/10 * * * "EN#45960 reported the RPS Actuation (50.72(b)(2)(iv)(B)) and AFW System Actuation (50.72(b)(3)(iv)(A). The event occurred at 0003 EDT on May 28, 2010. Technical Specification (TS) 3.0.3 was entered at 0004 hours on May 28, 2010, for inoperable offsite power sources with the 2H emergency diesel generator (EDG) being inoperable per TS 3.8.1. M. "Update: At the time of the event, the station was experiencing a severe lightning storm. The Auxiliary Feedwater System was returned to auto standby at 0558 hours. At approximately 0942 hours, RCS cooldown to Mode 4 was started on Unit 2. Mode 4 was entered at 1245 hours. The 'A' and 'B' RCPs remain secured in Mode 4. Following repairs and post maintenance testing the 'C' reserve station service transformer (RSST) was declared operable at 1324 hours. This restored two (2) qualified offsite circuits for Unit 1 and one (1) qualified offsite circuit for Unit 2. TS 3.0.3 was cleared at this time on Unit 2. The 'B' RSST remains out of service (OOS) pending repairs and testing. The Unit 2 'B' station service bus remains OOS. "The 2H EDG previously reported OOS for scheduled maintenance is expected to be returned to service on Monday, May 31, 2010. The alternate AC diesel generator continues to supply power to the 2H emergency bus. "Limiting action remains for one (1) offsite circuit for Unit 2 being inoperable along with the 2H EDG OOS." The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Haag). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-28
45959 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-05-06 | 2010-05-27 14:55 | 2010-05-27 | OHIO AGREEMENT STATE REPORT - FAILED SHUTTER LOCKING MECHANISM The following information was obtained from the State of Ohio via email: "The shutter locking mechanism for the licensee's Rock Belt fixed gauge has failed. The shutter is still functional, but is not capable of being locked. This failure was identified by the manufacturer's service technician during a site visit on 5/6/2010 while they were troubleshooting the electronics unit for this particular fixed gauge. "The gauge was manufactured by Ohmart/VEGA, Model SH-100, Serial # M-5800, containing a 50 mCi Cs-137 source installed in June 1991. This style of source holder is currently no longer being manufactured and the licensee is working with Ohmart/VEGA to determine possible repair or replacement options." Ohio Report Number: OH100007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-06-01
45958 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-05-27 02:00 | 2010-05-27 08:31 | 2010-05-27 | LOSS OF COMMUNICATIONS At 0200 EDT on 5/27/10, operators identified that the FTS 2000, NAS [Nuclear Alert System] and commercial phones systems were not functional. ERDS is not functional. The loss of communications appears to be weather related. [The licensee] validated microwave communication with ISO New England and NRC is available. Cell phone communication is functional. The NRC and state were contacted using alternate means. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ANDREW WISNIEWSKI TO VINCE KLCO ON 5/27/2010 AT 1459 * * * Notified by the licensee that FTS 2000, NAS, commercial phone systems and ERDS are functional. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Dwyer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-27
45957 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-05-26 15:26 | 2010-05-26 17:25 | 2010-05-26 | AUTOMATIC REACTOR SCRAM WHILE INCREASING POWER "At 1526 on 5/26/2010, while operators were increasing power with reactor recirculation flow, an RPS (Reactor Protection System) actuation occurred in both channels and all control rods inserted. RPV (Reactor Pressure Vessel) level decreased to 114.5 inches (Low level setpoint is less than 127 inches). Following the scram, the PCIS (Primary Containment Isolation System) groups 2, 3, 4 and 5 received actuation signals and all open valves isolated. Both trains of standby gas treatment system actuated. "Plant actions taken included entering procedures OT-3100, Reactor Scram on RPS Actuation and EOP-1, RPV Control on Low Level Signal. The EOP-1 was exited per shift manager direction because of no emergency. The operators stabilized the plant and reset both RPS and PCIS. An investigation into the cause of the scram is continuing." Electrical power is being supplied from offsite sources through the startup transformers. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 72 | 0 | 0 | -1 | 0 | 0 | A | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-26
45956 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-05-25 | 2010-05-26 17:10 | 2010-05-26 | AGREEMENT STATE REPORT - FAILED LEAK TEST ON CS-137 SOURCE The licensee gave verbal notification on 25 May 2010 of a leak tested Cs-137 (249.2 microcuries) source that failed. The vial source contained a removable amount of 0.287691 uCi. The Florida Bureau of Radiation Control received a written report on 26 May 2010 from the licensee that the source has been taken out of service and identified. Previous leak test was fine, daily surveys have not shown any contamination to other hot lab surfaces or staff. The licensee will return damaged source to manufacturer. No further action will be taken on this incident. The location of the incident is 1110 Lee Blvd Lehigh Acres, FL 33972. The sealed source is a NASI, model # MED3550, serial # 12574. Incident Report # FL10-069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-05-31
45955 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-05-14 | 2010-05-25 18:37 | 2010-05-25 | AGREEMENT STATE REPORT - ALLOY ANALYZER SHUTTER FAILURE The following report was received from the Commonwealth of Pennsylvania via fax: "Notifications: A letter from the Radiation Safety Officer dated May 17, 2010 was received May 21, 2010 by the Department of Environmental Protection explaining the event. Note: an initial review of the letter by PaDEP [Pennsylvania Department of Environmental Protection] and NRC Region I noted this was a 30-day NMED reporting [only] per 10CFR30.5(c)(5), but upon further review of 10CFR31.2 and 30.5(b)(2)(ii), it was concluded this event is a 24-hr report. "Event Description: On May 14, 2010, Harsco Metals identified a failure of the shutter mechanism on a generally licensed portable alloy analyzer during the semi-annual test. The analyzer was a Niton model XLp818 (ser# 6500) with approximately 30 mCi (1.11 GBq) of Americium-241. A licensed contractor attempted to provide a radiation exposure survey and found the device could be operated without utilizing the [trigger switch] safety mechanism. No individuals were in contact with or exposed to the direct beam during this procedure. "Cause of the Event: Equipment failure "Actions: The device has been taken out of service and Harsco Metals will contact the device manufacturer for instruction on returning the instrument for repair or replacement. PaDEP considers this a closed incident at this time." Event Report ID No: PA100006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-05-28
45954 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-05-21 | 2010-05-25 18:37 | 2010-05-25 | AGREEMENT STATE REPORT - LOST SOURCE FOUND IN SCRAP METAL The following information was received by fax: "On Friday May 21, 2010 radiation detectors alarmed due to a device containing 200 mCi of Americium [Am]-241 detected at the ATI [Allegheny Technologies Incorporated] Midland [Pennsylvania] facility prior to a charge being loaded into the furnace. On Monday May 24, 2010 an employee from Allegheny Raw Materials (ARM) saw part of a radiation symbol in the off-loaded metal scrap and contacted AHP [Applied Health Physics] when they got high radiation level readings. The scrap metal had passed thru two sets of radiation detection monitors prior to being detected by a rail detection system. When AHP responded, production was stopped at ATI (which uses an electric arc furnace), and AHP checked the three charge buckets, and other areas. The Am-241 gauge was reading about 150 mR/hr on contact. The manufacturer of the device is NDC systems, serial # 295. The device was sold to Magla Corp (NC) [in] January of 1976. "The device [is] onsite and has been wrapped in lead by AHP. AHP and ATI have labeled the device with a 'caution radioactive material' sign and stored it in a secured room with two chains and two locks." Pennsylvania Event Report ID No: PA100007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-05-28
45953 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-05-24 | 2010-05-25 18:37 | 2010-05-25 | AGREEMENT STATE REPORT - LOST AND RECOVERED TROXLER NUCLEAR GAUGE MODEL 3411; S/N 6343 The following report was received via fax: "Event Description: On May 24, 2010, the licensee's nuclear gauge operator was working on the road leading to the Pinegrove State Correctional Institution (PSCI). The gauge operator left the jobsite and pulled onto Route 286. While the gauge operator was sitting in traffic, it was noticed that the tailgate was open and the gauge was gone. The gauge operator and local highway construction workers looked for the gauge. "A guard from PSCI left work at 1400hrs. While traveling on SR 286 in Indiana County. The guard noticed the yellow transport box with radiation symbols along side of the roadway. The guard loaded the box onto a truck and took it to the Pennsylvania State Police (PSP) barracks in Indiana, PA. The label noted it contained Cesium-137, thus the PSP requested a local Hazardous Material Team come to the barracks and survey the container. "Radiation levels appeared normal. The evening of May 24th the PSP, the licensee and a gauge service provider were contacted by DEP [Department of Environmental Protection] Bureau of Radiation Protection [BRP] to assess the situation at the barracks, secure the nuclear gauge, and arrange for the licensee to meet DEP/BRP staff at the PSP barracks the next day to examine the gauge and move it to the licensee's PA facility. Regional DEP staff met the licensee on [May 25th] to perform a radiation survey and conduct an interview. The gauge was released to the licensee by PSP. "Cause of the Event: The gauge was not secured in the vehicle, and the tailgate was left open as the operator drove the vehicle. "Actions: DEP performed an investigation on May 25, 2010. After the investigation, the PSP returned the gauge to the licensee. DEP will continue to review the licensee's actions related to this event." Event report number: PA100005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-05-28
45952 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-05-25 03:14 | 2010-05-25 06:50 | 2010-05-25 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "During a normal plant power increase following a refueling outage on Unit 2, a reactor trip occurred at approximately 32% power. This reactor trip was the result of a turbine trip. The cause of the turbine trip is unknown at this time, however, a lock out trip occurred on the only running main feed water pump (21 main feedwater pump) at the time of the turbine and reactor trip. An investigation is ongoing. "The reactor trip first actuated indication was a turbine trip. An automatic start of both Auxiliary Feed Water pumps occurred following the trip. "The operating crew responded to the reactor trip utilizing emergency operating procedures for reactor trip and reactor trip recovery and transitioned into a normal shutdown procedure. "All rods inserted as expected and all other systems operated as expected with the exception of a positive displacement charging pump that lifted a relief that failed to reclose." The positive displacement pump relief valve stuck open and the pump was shut down which isolated the relief valve. Decay heat was initially being removed to the main condenser however, steam leak by was causing a plant cooldown therefore the Main Steam Isolation Valves were shut. Decay heat is being removed using the steam generator atmospheric relief valves. There is no known primary to secondary leakage. The plant is in its normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-25
45951 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-05-24 17:25 | 2010-05-24 21:40 | 2010-05-24 | TECHNICAL SUPPORT CENTER DECLARED INOPERABLE "The Technical Support Center (TSC) emergency ventilation system was declared inoperable when the acceptance criteria of a periodic surveillance test related to outside air flow was not met. "The loss of TSC Emergency Ventilation Function represents a loss of emergency preparedness capability. "Actions to restore the TSC Emergency Ventilation system operability are in progress. "This event is being reported under 10CFR50.72(b)(3)(xiii). "The Senior Resident Inspector has been informed of the event [by the licensee]." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-24
45950 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-05-24 15:20 | 2010-05-24 19:24 | 2010-05-24 | OFFSITE NOTIFICATION - OIL SHEEN AT INTAKE FOREBAY "Browns Ferry Nuclear Plant (BFN) is notifying state and local agencies of an oil sheen at the Intake Structure Forebay of approximately 1 gallon. The sheen came from a center motor oil leak on Intake Structure Gate #3. Leak has been secured and oil sheen Is being cleaned up. "BFN Procedure RWI-007, Spill Prevention Control and Countermeasure Plan requires the National Response Center as well as other state and local agencies be notified of any oil sheen on the water. "This event is reportable as a 4-hour Non-Emergency Notification report in accordance with 10CFR50.72(b)(2)(xi) Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-05-24
45949 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-05-21 13:00 | 2010-05-24 12:05 | 2010-06-15 | AGREEMENT STATE REPORT- CALIBRATION SOURCE NOT RETURNED TO ITS STORAGE HOLDER The following information was received by e-mail: "About 0930 Weatherford International, LTD. (ND Lic # 33-45901-01) reported that at about 1500, May 21, 2010, in Williston, Williams County, ND, a well logging tool was [returned to] the truck with the calibration source still in the tool. The calibration source is Cs-137, strength about 55.5 GBq. This error was discovered about 1500, May 21, 2010. The source, when in the tool is highly collimated, restricting significant potential dose to a limited volume. The dosimeter badges for those working in the vicinity of the truck and those in an adjacent office have been sent in to Landauer for analysis. Drawings and estimated doses will be forwarded to NRC as soon as received from Weatherford. "ND Incident #: ND10003" * * * UPDATE FROM NORTH DAKOTA (HARMAN) TO HUFFMAN (VIA E-MAIL) ON 6/15/10 * * * The information below is a summary of a report provided from Weatherford to the State of North Dakota. "On May 21, 2010, a 1.5 Ci [55.5 GBq] Cs-137 source was placed into a logging tool for calibrations. After calibrations were complete, the tool containing the source was placed into a logging truck and left for approximately 24 hours, potentially exposing two Well Logging Supervisors, one District Manager and one Well Logging Assistant. "On May 22, 2010 at approximately 1400 (MDT), one of the Well Logging Supervisors, while trying to perform after [job] calibrations for the job which he had returned, noted high gamma ray background readings and, using a survey meter, began searching the area looking for a reason why the background readings were higher than normal. At approximately 1600 (MDT), he began searching the shop and noted that the readings as he approached logging truck were extremely high. He and the Well Logging Assistant removed the density logging tool from the wireline unit and found that the density source was still in the tool. At this point, the 1.5 Ci Cs-137 source had been in the tool loaded on logging truck for 24 hours. "The facility employs twelve individuals, of which eight were not present at the facility during the period of 1600 on May 21, 2010 and 1600 May 22, 2010. On May 24, 2010, the dosimeters for the [two Well Logging Supervisors, the Well Logging Assistant,] one spare located in the office, one control and an employee's dosimeter, which was left on the desk, were sent to Landauer for analysis. It should be noted that one of the Well Logging Supervisors was not wearing his dosimeter during the incident. "The incident was reconstructed and surveys were taken to aid in identifying the possibility of excess exposure to the District Manager and the Well Logging Supervisor that were not wearing dosimeters. "The incident investigation uncovered many procedural issues including failure to document the removal of radioactive material (RAM) from storage (i.e., utilization records), failure to properly secure storage areas, failure to properly return RAM to storage and failure to establish a radiation area during calibration procedures. Because of not following proper procedures, [personnel actions were taken for one of the individuals involved]. [In addition], written corrective action has been given to one of the Well Logging Supervisors for not wearing a dosimeter while on duty and failure to notify management of an improperly secured storage area. All facility employees have been given a verbal corrective action on radiation procedures. "Although there were many procedural violations, after analysis of the dosimeters and incident reconstruction surveys, Weatherford has no reason to believe an overexposure incident has taken place. " Based on event reconstruction and available dosimeter readings, it is believed that none of the four employees exposed by this event received in excess of 18 mRem total effective dose equivalent. R4DO (Powers) and FSME EO (Watson) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2010-05-27
45948 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2010-05-24 07:45 | 2010-05-24 10:55 | 2010-05-24 | PACKAGE SURFACE CONTAMINATION IN EXCESS OF REPORTING LIMITS "[A representative] with the Department of Veterans Affairs, VHA National Health Physics Program provided the following report. This report involves NRC master materials license no. 03-23853-01VA. "[The VHA representative] called, as required by 10 CFR 20.1906(d), to report receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than reporting limits. "The package was received today (May 24, 2010) at around 7:45 AM CT by the Central Texas Veterans Healthcare System, Temple, Texas. "A wipe test performed on the external surface of the package indicated a removable contamination level of 562 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2. "Surveys inside the package did not indicate elevated contamination. "The package contained Tc-99m (Technetium) labeled radiopharmaceuticals and was shipped from Specialty Pharmaceutical Services, Inc., in Temple, Texas. The vendor/shipper also serves as the delivery carrier. The VA facility staff immediately notified Specialty Pharmaceutical Services, Inc. about the contaminated package at about 9:30 AM CT. "[The VHA representative] will notify the NRC Project Manager at NRC Region III of this event. "The permittee holds VHA Permit Number 42-10739-03." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2010-05-24
45947 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-05-23 16:30 | 2010-05-23 21:52 | 2010-05-23 | NONFUNCTIONAL TECHNICAL SUPPORT CENTER VENTILATION "The Technical Support Center (TSC) ventilation system was found to be non-functional on 5/23/10 at 1630 EDT. The system repair was complete at 1747 EDT on 5/23/10. The time period that the TSC ventilation system was non-functional exceeded the 30 minute time limit that is delineated in the Technical Requirements Manual section T 3.10.1. This event is reportable per 10 CFR 50.72 (b)(3)(xiii) as described in NUREG 1022 Rev. 1 since this issue affected an emergency response facility. Also, this 8 hour notification is being made in accordance with the Technical Requirements Manual section T 3.10.1.B.2. "The alternate TSC facility remained functional during this entire time period." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-23
45946 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-05-22 16:34 | 2010-05-22 19:10 | 2010-05-22 | MANUAL REACTOR TRIP DUE TO LOSS OF STEAM GENERATOR WATER LEVEL CONTROL "Unit 2 was operating at 100% power in the normal operating procedure, FNP-2-UOP-3.1, Power Operation, when multiple alarms were received associated with 2C Steam Generator (S/G) level, and a process cabinet failure. The control room team noticed there was no power or control capability on the 2C S/G Feedwater Regulating Control Valve (FRV), and 2C S/G level was decreasing. The control room team attempted to take manual control of the 2C FRV, which did not respond. The reactor was manually tripped when 2C S/G narrow range level reached 40%. The automatic trip set point for S/G level is 28%. All systems responded properly for the reactor trip and there were no complications. "The investigation indicates there was an Nuclear Controller Driver (NCD) card failure in Process Control Cabinet 8. The controller card controls the 2C S/G FRV controller, which prevented any automatic, or manual control of the 2C S/G FRV, or 2C S/G level." There were no safety or relief valves that lifted and decay heat is being removed via steam dump control valves. Auxiliary feedwater pumps are maintaining level in the steam generators. Electrical lineup is normal. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-22
45945 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2010-05-22 16:45 | 2010-05-22 17:46 | 2010-05-22 | MANUAL REACTOR TRIP DUE TO LOSS OF STEAM GENERATOR WATER LEVEL CONTROL "The licensee experienced a feedwater transient which initiated the event. All safety systems are available. All control rods fully inserted. The electrical lineup is normal. The decay heat path is through the condenser steam dumps. No relief valves or safety valves lifted during the transient. Primary plant temperature is 533 degrees Fahrenheit and primary plant pressure is 2256 psia. The licensee is investigating the cause of the feed transient. "The licensee notified the NRC Resident Inspector, the Waterford Dispatch, and the State Department of Environmental Protection." Earlier, the licensee was experiencing oscillations in the feedwater regulating valve (FRV) for the #2 steam generator when the valve was in automatic control. Troubleshooting planning was underway but no troubleshooting activities were in progress at the time of the trip. When the operator placed the #2 steam generator FRV in manual control, the steam generator water level began to increase and could not be recovered. The operator then manually tripped the reactor prior to reaching the high steam generator level trip setpoint. An Auxiliary Feed Water system actuation did occur during the transient. The trip and plant response was considered uncomplicated. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-22
45944 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-05-21 19:37 | 2010-05-21 22:57 | 2010-05-21 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP "At 1937 Eastern Daylight Saving Time (EDT), Watts Bar Nuclear Power Plant Unit 1 experienced a reactor trip due to a turbine trip. This caused an automatic AFW Pump start from P-4 coincident with Lo Tave signal. The cause of the turbine trip has not yet been identified, and is under investigation. "The plant is stable and is being maintained in Mode 3, at normal operating pressure and temperature, with steam generator and pressurizer levels normal. "Plant systems responded to return the plant to a stable condition without complication, and all systems performed as expected with one exception: "The 'B' Motor Driven Auxiliary Feedwater Backpressure Control Valve failed closed, but the Steam Driven Auxiliary Feedwater Pump provided sufficient feedwater so that all Steam Generators were provided sufficient feedwater to maintain cooling and normal steam generator level. "Plans for plant restart are pending awaiting the cause investigation. "All control rods inserted into the core. Plant decay heat removal is through the steam dumps to the main condenser. Offsite power is available and lined up to plant system loads. "Watts Bar [NRC] Resident Inspector has been notified of this event." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-21
45943 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-05-21 13:20 | 2010-05-21 18:48 | 2010-05-21 | OFFSITE NOTIFICATION TO CALIFORNIA DEPARTMENT OF PUBLIC HEALTH "On May 19, 2010, at approximately 1730 PDT, San Onofre Nuclear Generating Station (SONGS) was notified that scrap bushings from breakers in the Unit 2 switchyard had alarmed a radiation monitor at a metal recycling facility in Los Angeles County. The metal recycling vendor (Alpert and Alpert) shipped the bushings back to a Southern California Edison (SCE) facility in Orange County. On May 21, 2010, SONGS completed isotopic analysis of a sample of ceramic shards from six randomly selected bushings. The analysis confirms the presence of naturally occurring radionuclides (uranium and thorium series), but does not indicate the presence of licensed radioactive material. "On May 21, 2010, at approximately 1320 PDT, SONGS confirmed that on May 19, 2010, the metal recycling vendor had called the Brea branch of the California Department of Public Health, Radiologic Health Branch (Andrew Taylor) to obtain a special permit authorizing the return shipment to SCE. SONGS is, therefore, reporting this event in accordance with 10CFR50.72(b)(2)(xi) as an event related to the health and safety of the public for which notification to another government agency has been made. "At the time of this report, both Unit 2 and Unit 3 were operating at 100 percent power. "The NRC Senior Resident Inspector has been notified of this occurrence and will be provided with a copy of this report. " | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-05-21
45942 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-05-21 | 2010-05-21 12:50 | 2010-05-21 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON RONAN GAUGE The following report was received from the State of Texas via e-mail: "On May 21, 2010, the Agency [State of Texas] was notified by the licensee that while conducting a routine inspection of a Ronan Engineering model SA1-F37 nuclear gauge, the shutter failed to close. The gauge was installed in 1991 and contained a 20 millicurie Cesium (Cs) - 137 Source. The licensee conducted a radiation survey in the area of the gauge and found the dose rates to be normal. Open is the normal operating condition for the gauge therefore there is no additional exposure risk to their workers. The vessel the gauge is associated with has been posted to warn workers hat the shutter is not functioning properly. The licensee has contacted the manufacturer to schedule the repair. The licensee stated that the repair should be completed within the next 60 days." Texas Incident Number I-8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-05-26
45941 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-05-21 06:01 | 2010-05-21 07:01 | 2010-05-21 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the protected area. The incident appears to be unintentional with no malevolent intent involved. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-21
45940 | -1 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-05-20 19:56 | 2010-05-20 21:22 | 2010-10-14 | SAFEGUARDS REPORT - DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM "Discovered vulnerability in a safeguards system that could allow access to a controlled area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional information." * * * UPDATE AT 1559 EDT ON 10/14/10 FROM ED BENDIS TO S. SANDIN * * * The licensee is retracting this report after further review completed at 1430 CDT on 10/14/10. The licensee has concluded that this event is loggable and not reportable. The licensee informed the NRC Resident Inspector. Notified R3DO(Phillips) and 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-20
45939 | 0 | WATERFORD | 3 |  |  | [3] CE | 2010-05-20 15:35 | 2010-05-20 20:30 | 2010-05-20 | OFFSITE NOTIFICATION DUE TO TRANSPORTATION ACCIDENT "This is a Non-Emergency 4 hour notification being made in accordance with 10 CFR 50.72(b)(2)(xi), an Offsite Notification. On May 20, 2010, at approximately 1535 CDT Waterford 3 was notified by the Louisiana (LA) State Police that a transportation accident occurred involving a low level radioactive shipping container that was being carried by a tractor trailer truck located at mile marker 22 East on interstate highway I-12 near Walker, LA in Livingston Parish. The surface contaminated object (SCO) metal shipment container was being used by Miller Transfer Houston to transport a used Reactor Coolant Pump (RCP) motor from Waterford 3 nuclear plant in Killona, LA to Westinghouse Waltz Mill in Madison, PA. The shipment weighing approximately 145,000 pounds departed Waterford 3 at approximately 1230 CDT with identification number of 10-3044 and pre-shipment radiological survey information of contamination levels of less than or equal to 15,000 dpm/100cm2 and dose rates of less than or equal to 0.4 mR/Hr. The tractor trailer is on its side, just off the interstate, on the grass. The shipping container boxed cover lid has opened, exposing the RCP motor, showing that it is still wrapped with contamination protective covering and still fastened to the container base and trailer. The initial, basic radiological assessment performed by the LA State Police Hazmat technician supervisor resulted in no indication of hazardous levels of radiation dose rates. Waterford 3 dispatched a Radiation Protection field team who arrived at approximately 1840 CDT and surveyed the container and the contents. The survey results indicate no radiological breach, with smear results of contaminations no higher than background and radiation dose rates of no higher than 0.5 mR/Hr. "There was no report of other vehicles involved. The driver was contacted by cell phone, who reported that he has been transported to the hospital emergency room for a CAT scan. The failure mode has yet to be determined." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-05-20
45938 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-05-20 13:27 | 2010-05-20 17:11 | 2010-05-20 | OFFSITE NOTIFICATION - BETHEL FIRE DEPARTMENT RESPONDED TO GRASS FIRE NEXT TO PLANT "Notification [was made] to make the NRC aware of a call to Bethel Fire Department for assistance in extinguishing a grass fire on Catawba property. The fire was caused by an arc flash, resulting from a large bird coming in contact with a York cooperative power line. [The] fire is extinguished. Fire was outside the owner controlled area. [The area burned] is approximately 100' x 100'. [There was] no property damage [to the site]." Both units were unaffected by this event and maintained 100% reactor power. The fire was located in a brush field located in Catawba Park and took approximately 30 minutes to distinguish. The licensee notified the NRC Resident Inspector. The licensee also notified Mecklenburg, Gaston, and York counties as well as the state of North Carolina and South Carolina. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-05-20
45937 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-05-19 16:40 | 2010-05-20 01:24 | 2010-07-16 | BOTH TRAINS OF RESIDUAL HEAT REMOVAL (RHR) INOPERABLE "On 5/19/2010 at 1209 CDT, Unit 2 entered Mode 4 from Mode 5 and started realigning RHR from a shutdown cooling to an Emergency Core Cooling System (ECCS) lineup. During this transition, the suction check valves for the RHR pump are tested for safety function closed per the In-service testing program . The valves are closed to provide train separation for the RHR trains and to prevent diversion of flow from suction sources. "On 5/19/2010 at 1228 CDT, both Unit 2 trains of RHR were declared inoperable due to the failure of the pump suction line check valve for each RHR pump (2RH-3-1 and 2RH-3-2) to meet In-Service Testing (IST) acceptance criteria. Technical Specification 3.5.2 Condition A was entered for inoperability of the one required ECCS train (RHR) in Mode 4 with Reactor Coolant System (RCS) cold leg temperatures above safety injection pump disable temperature. "On 5/19/2010 at 1640 CDT, both RHR pit sump covers were opened to facilitate multiple entries into each sump while performing a revised test procedure to verify the operability of check valves 2RH-3-1 and 2RH-3-2. The pit sump covers are required to be closed in [Modes 1 through 4] for each operable RHR train. Since both trains of RHR were inoperable both covers were opened. "On 5/19/2010 at 1947 CDT the pit sump cover was closed for one train of RHR. "On 5/19/2010 at 2005 CDT the revised test procedure was approved and completed satisfactorily. The train of RHR with the pit sump cover closed was declared operable and Technical Specification 3.5.3 Condition A was exited. Both suction check valves passed the closed safety function and a loss of safety function did not occur as originally thought on 5/19/2010 at 1228 CDT. "On 5/19/2010 from 1640 CDT to 1947 CDT both trains of RHR were inoperable due to both pit sump covers open on both RHR trains. The inoperability of both trains of RHR represents a condition that prevented the fulfillment of the safety function of structure or systems that are needed to remove residual heat and mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. * * * UPDATE (RETRACTION) FROM STEVEN INGALLS TO JOHN KNOKE AT 1654 EDT ON 7/16/10 * * * "The purpose of this report is to retract the ENS report made on May 20, 2010 at 0124 hours [ET] (ENS #45937) under 10 CFR 50.72(b)(3)(v)(D), a condition that could have prevented fulfillment of a safety function. The pump suction line check valve for each Unit 2 RHR pump failed to meet acceptance criteria per the in-service testing program. A revised test was performed which demonstrated that the check valves could perform their safety function. The RHR pit covers were removed to facilitate this test. After test completion, it was identified that both trains of RHR were inoperable due to both pit covers being open. However, subsequent review has determined that the condition where pit covers were open did not impair the ability of the RHR system to meet its safety function. Also, there was not a loss of safety function due to the check valve testing issue. Thus, there was no safety system function failure of the RHR system. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Dickson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-05-20
45936 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-05-19 13:30 | 2010-05-19 16:27 | 2010-05-19 | AGREEMENT STATE REPORT - STUCK SHUTTER "On May 19, 2010 at 1620 CDT the agency [State of Texas] received a phone call from the licensee. The licensee stated that shutter on a fixed gauge had stuck at approximately 1700 CDT on May 18, 2010. The gauge houses a 50 milliCurie Cesium (Cs) - 137 source. The licensee stated that shutter failed in the open position, the normal operating position for the gauge, and that exposure rates in the area were normal. The gauge is located high above the ground, on the side of a water tank. The licensee stated that they had contacted the manufacturer and have scheduled a repair of the gauge within the next 30 days. The licensee stated that they were going to continue to use the gauge, as it was in its normal operating state. The agency reminded the licensee that their license specifically states that they are to take the gauge out of operation if it is in need of repair, and should they continue to use the gauge, they would need to request an exemption from the agency. The licensee agreed to request the exemption so that they would not be in violation of their license." The gauge is a Ronan Gauge S/N 936GG. Texas I - 8743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-05-24
45935 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2010-05-19 13:30 | 2010-05-19 15:13 | 2010-05-19 | POTENTIALLY TOXIC ATMOSPHERE IN AN ACCESS FACILIITY "At 1315 hours personnel performing repairs to an air conditioning system inside the Access Facility (AF) reported a Freon leak from a valve packing failure. All personnel were evacuated from the building. Radiation protection personnel entered the building and atmospheric sampling commenced. Sample results indicated a potentially toxic atmosphere in portions of the AF, and at 1330 hours an Emergency Plan Unusual Event was declared on EAL HU7, 'Hazards and Other Conditions Affecting Plant Security.' "The AF was locked down and plant access and egress have been halted pending the restoration of AF atmosphere. Required security compensatory measures are in place. "The Freon completely discharged from the affected air conditioner through the leak. Actions to establish a habitable atmosphere inside the AF continue. "Units 1 and 2 are unaffected by this event and continue to operate at full power." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MARK BRIDGES TO PETE SNYDER AT 1551 ON 5/19/2010 * * * "A habitable atmosphere has been re-established and conditions no longer meet an emergency action level. The Unusual Event was terminated at 1438 CDT on 5/19/2010." The licensee will notify the NRC Resident Inspector. Notified R3DO (Cameron), IRD (Gott), NRR (Ruland), DHS (Vestal), and FEMA (Barden). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-05-19
45934 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2010-05-14 04:20 | 2010-05-18 12:20 | 2010-05-18 | SAFEGUARDS REPORT - DISCOVERED VULNERABILITY Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-18
45933 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-05-16 | 2010-05-17 14:58 | 2010-05-17 | AGREEMENT STATE REPORT - POTENTIAL RADIATION UNDERDOSE The following report was received via email from the State of Nevada: "On March 16, 2010, during a prostate Brachytherapy procedure, 112 sources of I-125 (Model I125-SL[NIST 99]), were implanted into the prostate. The activity of each source was 0.342mCi. Total prescribed dose was 145 Gy. When the patient returned for follow-up, 1 to 2 months after the implant, CT images were imported into the treatment planning system and a post-plan was created to assist in quality assurance, to determine the actual dose to the prostate and to review the overall quality of the implant. "When the post-plan was created for this patient and reviewed, it was determined that the dose to the prostate was approximately 114 Gy, which was 79% of the prescribed dose. This exceeds the +/- 20 % limit set in 10 CFR 35.3045. The physician was notified and the dosimetry reviewed. The lower dose was in the middle, close to the urethra where there is a desire for dose sparing. The higher doses were on the periphery of where the dose was intended. Following normal protocol, the patient's blood work will be monitored to observe his PSA levels. The referring physician was contacted on May 14, 2010. The patient has not been informed. "Contributory Factors: Though not known as to why the dose was lower than prescribed, it appears that the seeds were implanted more in the periphery probably due to a desire to spare the urethra. This could have been due to the urethra-gram performed during surgery. "Consequences: The physician is of the opinion that the therapy will still be effective since the seeds were implanted where statistically the cancer resides. The patient's blood work will be monitored regularly and additional therapy given, if necessary. "Corrective measures: Care will be taken to ensure that the sources are evenly distributed throughout the prostate in the future. It was the physician's desire to spare the urethra. It will be under the discretion of the physician as to how to implant the prostate and still deliver the desired prescribed dose. "Notification: The patient's plan/dosimetry was presented to the Physicist and the Physician on May 13, 2010 at 3.00 p.m., the State of Nevada Radiation Control Program was contacted by phone on May 14, 2010 at 9.00 a.m." This is NV event #NV100010. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-05-23
45932 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-05-17 | 2010-05-17 10:20 | 2010-05-17 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGES "[The State of Florida] received a report from the company's RSO at 0945 that three soil moisture density gauges and cases were stolen. [A] Conex box at [the] site was locked and broken into. All three gauges were chained and locked to [the] interior of [the] Conex box. All three locks were broken. [The] cases were locked with the gauges inside when stored. [The] owner still has keys to the cases and gauges. [The] licensee will offer a reward. Local police have been notified and [the] licensee is currently awaiting their arrival." All three stolen gauges were Troxler Model 3430, Serial Numbers 31318, 25778, and 19575. Each gauge contained a 40 mCi AmBe source and a 8 mCi Cs-137 source. FL:10-067 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-05-20
45931 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2010-05-17 10:17 | 2010-05-17 12:27 | 2010-05-17 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "System Affected: RPS actuation and reactor trip. Actuation Initiation Signals: AFW auto initiation. Cause: Low level 'C' steam generator. Effect of event on Plant: Reactor and turbine trip. Actions taken or Planned: Standard post trip actions. Additional information: Plant stabilized at NOP/NOT." The licensee experienced a feedwater transient which initiated the event. All safety systems are available. All control rods fully inserted. The electrical lineup is normal. The decay heat path is through the condenser steam dumps. There were no relief valve or safety valve lifted during the transient. Primary plant temperature is 555 degrees Fahrenheit, and primary plant pressure is 2250 psig. The licensee is investigating the cause of the feed transient. The licensee notified the NRC Resident Inspector, the Waterford Dispatch, and the State Department of Environmental Protection, | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-17
45930 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-05-14 23:01 | 2010-05-15 01:17 | 2010-05-15 | MANUAL REACTOR SCRAM DUE TO INCREASING REACTOR WATER LEVEL "At approximately 2301 hours EDT on May 14, 2010, Susquehanna Steam Electric Station Unit One reactor scrammed while performing a condensate pump trip test. The reactor operator placed the mode switch in shutdown when reactor water level reached +51 inches and rising. The main turbine tripped due to high reactor water level. All control rods inserted and both reactor recirculation pumps tripped. Reactor water level lowered to -30 inches causing Level 3 (+13 inches) isolations. The Operations crew restored reactor water level to the normal operating band using RCIC [Reactor Core Isolation Cooling] and subsequently the feedwater system. All isolations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "The reactor is currently stable in Mode 3. An investigation into the cause of the shutdown is underway. Unit Two continued power operation. "The NRC Resident Inspectors were notified. A press release will occur." The licensee was performing testing on the digital feedwater control system which was installed during their recent refueling outage when the loss of level control occurred. It appears that the control system did not respond fast enough to control water level. This resulted in the reactor operator inserting a manual scram at +51 inches prior to reaching the reactor automatic scram setpoint of +54 inches for water level. Currently, the plant is removing decay heat via main steam line drains to the condenser. The plant is in its normal shutdown electrical lineup with all safety equipment available. The licensee has notified the Pennsylvania Emergency Management Agency. | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-15
45929 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2010-05-14 15:30 | 2010-05-14 17:56 | 2010-05-18 | TECHNICAL SUPPORT CENTER NONFUNCTIONAL "At 1530 on May 14th, 2010, Three Mile Islands Technical Support Center (TSC) ventilation, filtration and climate control system was identified as nonfunctional. Site emergency implementation procedures provide direction for performance of TSC functions in alternate locations. This failure affects the ability of the TSC ventilation to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities of the TSC are unaffected by this emergent condition. This condition is considered a major loss of emergency assessment capability and is reportable under 10CFR50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. * * * UPDATE FROM JEFF GOLDMAN TO JOE O'HARA AT 1934 ON 5/18/10 * * * The TSC ventilation system has been repaired and is fully functional as of 1100 on May 15, 2010. The NRC Resident Inspector has been notified. Notified R1DO(Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-14
45928 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2010-05-14 16:05 | 2010-05-14 17:10 | 2010-05-14 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the State of Oklahoma via e-mail: "On May 14, 2010, Oklahoma Department of Environmental Quality (ODEQ) received telephone notification from American Airlines Maintenance and Engineering Center (AA) that they had lost one (1) tritium (H-3) radioluminescent exit sign containing a maximum total of 3.5 Ci of H-3. At this time, no further information is available; however, updates will be made to NMED as ODEQ receives updates from AA." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www.pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2010-05-19
45927 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2010-04-15 | 2010-05-14 14:11 | 2010-05-14 | BENT FUEL SPACER FLOW WING "During inspection of GNF2 reload fuel, a spacer flow wing on the corner rod position was discovered to be deformed (bent). A review of this condition and the associated root cause evaluation has determined that it could be present in previously manufactured GNF2 fuel that has been shipped for Fitzpatrick Cycle 19, Pilgrim Cycle 18, Vermont Yankee Cycle 28, Vermont Yankee GNF2 Lead Use Assemblies and Grand Gulf Cycle 18. It is not known that this condition exists in the GNF2 fuel for these plants, but it cannot be ruled out. A conservative assessment of thermal hydraulic impact of this condition resulted in a 0.01 OLMCPR [Operating Limit Minimum Critical Power Ratio] impact for these plants. An OLMCPR impact of 0.01 is at the threshold for reportability." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-05-14
45926 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2010-05-13 12:33 | 2010-05-14 10:54 | 2010-05-14 | A VALVE CLASSIFIED AS AN ITEM RELIED ON FOR SAFETY FOUND CLOSED WHILE POSITION INDICATOR SHOWED OPEN "It was reported to EH&S [Environmental Health & Safety] Management that on May 13, 2010 that the XV-202-I valve actuator was showing open when the valve was closed. This valve is the Uranium Hexafluoride (UF6) eduction back-up emergency shut off valve and is credited as a protective feature for a high level condition in the hydrolysis column. This valve is a key component of an Item Relied On for Safety (IROFS) and is identified in the Integrated Safety Analysis (ISA) Summary for the conversion area of the Columbia Fuel Fabrication Facility. This IROFS designation is ADUVAP-110. No process upset occurred and the condition was discovered by the production staff during normal operation. "This notification is made based on 10CFR70 Appendix A (b) (2), 'Loss or degradation of items relied on for safety that results in failure to meet the performance requirements of 10CFR70.61.' The performance requirements for this accident sequence require the Overall Likelihood Index (OLI) be a -4, which corresponds to Highly Unlikely. With this control failure the sequence OLI is a -3 which corresponds to Unlikely. "Immediate Corrective Actions: - Upon identification of the issue on May 13, production shut down conversion line 2 and generated a 'red book' to inform EH&S. - Maintenance determined the valve actuator had been installed incorrectly. - Maintenance properly installed the actuator on the valve and demonstrated proper performance. - The event has been entered into the Corrective Action Process IR# 10-134-C001. - Conversion line 2 remains shutdown pending staff management authorization for restart. - For all modifications/maintenance activity on IROFS in safety significant systems, staff management approval is required for restart of the system." The licensee believes that the valve mis-position and indication issues occurred during maintenance on the valve approximately one week prior to discovery of the condition. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-05-14
45925 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-05-13 16:02 | 2010-05-13 19:43 | 2010-05-13 | NOTIFICATION OF OHIO ENVIRONMENTAL PROTECTION AGENCY DUE TO EXCEEDING NPDES DISCHARGE PERMIT VALUE "At 1602 hrs on 5/13/2010 the Plant Shift Superintendent's (PSS) office was notified by USEC Environmental Management that NPDES [National Pollutant Discharge Elimination System] permit maximum concentration limit for fecal coliform at the X-6619 (Sewage Treatment Facility) discharge (NPDES Outfall 003) was exceeded. Sample results from 5/12/2010 revealed the permit limit of 2000 colonies / 100 ml was exceeded which resulted in a notification to the Ohio Environmental Protection Agency (OEPA). "Procedure UE2-RA-RE1030, appendix D, Section Q (Miscellaneous) which states: 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been made or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials.'" The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2010-05-13
45924 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-05-13 13:32 | 2010-05-13 16:55 | 2010-05-13 | OFFSITE NOTIFICATION "At 1332 CDT, FCS [Fort Calhoun Station] control room received notification that a person inside the Protected Area appeared to be having a heart attack. EMTs were immediately paged/dispatched and the victim was transported offsite for emergency medical treatment via helicopter. "At 1415 CDT, FCS control room received notification that another person suffered a severe hand laceration due to the closing of a security gate. Again, EMTs were immediately paged/dispatched and the victim was transported offsite for emergency medical treatment via ambulance. "Neither of these individuals were radioactively contaminated." The licensee notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-05-13
45923 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-05-11 | 2010-05-13 16:04 | 2010-07-08 | AGREEMENT STATE REPORT - REPORT OF LEAKING SEALED SOURCE The following information was received by e-mail: "On Tuesday May 11, 2010, the licensee discovered during a routine leak test that a Ni-63 source in a Shimadzu GC-14A gas chromatograph was leaking, presenting 0.0142 microCi. The source was identified as an NRD model N-100, serial number 616355, with an original activity of 9.98 mCi on 3/23/03 and a current activity of 9.50 mCi. "A second leak test confirmed that this was not a false positive. Surveys of the instrument and area presented no evidence that contamination had spread. "The device containing the Ni-63 source was removed from service and taken to the licensee's radioactive waste storage facility." Ohio Report: OH100006 * * * UPDATE FROM STEPHEN JAMES TO CHARLES TEAL ON 7/8/10 AT 1128 * * * "The source has been removed and packaged for disposal with the licensee's next LLRW shipment." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-05-18
45922 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-05-13 05:00 | 2010-05-13 05:00 | 2010-05-13 | PARTIAL LOSS OF ERDS AND SPDS DUE TO PLANNED MAINTENANCE "A partial loss of ERDS [Emergency Response Data System] and SPDS [Safety Parameter Display System] capability will occur while a planned replacement of the site's plant process computer power supplies is performed: "The following is a list of the inputs to ERDS that will be lost: IRM 14 PERCENT OF RANGE SRM 24 NEUTRON FLUX TORUS WIDE RANGE LEVEL CORE SPRAY SYSTEM 1 AND 2 FLOWS MAIN STEAM LINE BAND C RAD LEVELS DW [Dry Well] WIDE RANGE PRESS STACK RAGEMS [Radioactive Gas Effluent Monitoring System] LOG LO RNG CH 2 "The following is a list of the SPDS inputs that will be lost: CORE SPRAY SYSTEM 1 AND 2 FLOWS EMRV [Electromatic Relief Valves] AND SAFETY VALVE INDICATIONS DW PRESSURE MS [Main Steam] A,B,C, AND D RAD MONITORS DW 02 CONCENTRATION "ERDS and SPDS are expected to be returned to full functionality by 2000 EDT" Emergency plan contingency measures are in place to transmit data should it be required during the maintenance period. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DENNIS MOORE TO DONALD NORWOOD AT 2152 EDT ON 5/13/2010 * * * ERDS and SPDS returned to service as of 2144 EDT. The licensee will notify the NRC Resident Inspector. Notified R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-13
45921 | 0 | DRESSER-RAND |  |  |  |  | 2010-05-12 | 2010-05-12 18:39 | 2010-05-12 | LUGS ON DIGITAL FILTER IMPROPERLY SOLDERED A faulty Digital Control System Output Filter was discovered at Farley Nuclear Power station while installing it on the emergency feedwater Terry Steam Turbine. The problem only affects two plants: Farley Nuclear Power Station and San Onofre Nuclear Power Station. Farley replaced the filter before use. San Onofre had installed and used the filter, but they are replacing it. "Description of Defect: "Eyelets inserted into the printed circuit (p.c.) board to make connections from one side of the board to the other side were not soldered on the top side where the terminal block is installed. This may result in the connection being broken during tightening of the wire lug on the terminal block or if other stresses are applied to the p.c. board or terminal block. This defect is limited to output filter serial numbers 10009, 10010, 10011, and 10012. "Engineering Evaluation and Recommendations: "Failure can occur during assembly. The results of a seismic event are unknown. All 4 filters must be recovered and repaired. Locations of the 4 filters include Dresser-Rand, Farley Nuclear Station, and San Onofre Nuclear Generating Station." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2010-05-13
45920 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2010-05-12 13:51 | 2010-05-12 15:35 | 2010-05-12 | RPS ACTUATION - LOAD REJECT "At 1351 hrs. EDT on May 12, 2010, a Calvert Cliffs Unit 1 Reactor trip was generated by a complete load rejection when a main generator output breaker opened while its redundant breaker was opened for planned maintenance. "The generator output breaker trip caused Reactor Coolant System (RCS) pressure to rise to the Reactor Protection System (RPS) High Pressure setpoint, which opened both Power Operated Relief Valves (PORVs). Both PORVs reclosed when RCS pressure was reduced to normal. "All Control Rods fully inserted on the trip. Normal heat removal methods are currently in progress." Unit 1 is in a normal shutdown electrical lineup and there was no impact on Unit 2. The NRC Resident Inspector has been notified by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-12
45919 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2010-05-12 12:20 | 2010-05-12 13:47 | 2010-05-12 | OFFSITE NOTIFICATION "On May 11, 2010, Westinghouse reviewed the vendor chemical laboratory analysis for the Total Suspended Solids (TSS) parameter result for the April 28, 2010, NPDES [National Pollutant Discharge Elimination System] liquid effluent 24-hour composite sample. The sample result indicated that the wastewater discharged from the Westinghouse Columbia plant to the Congaree River during the 24-hour period preceding the April 28th sampling contained 93.16 pounds of TSS, which exceeds the daily maximum permit limit of 64.0 pounds per day. The April 28, 2010 result also produced a monthly average of 46.39 pounds, which exceeds the monthly average permit limit of 32.0 pounds per day. [The] investigation regarding the cause of this high TSS result is still ongoing. "Liquid discharges from the Columbia Plant are regulated with regard to chemical pollutants through the SC-DHEC/EPA [South Carolina - Department of Health and Environmental Control/Environmental Protection Agency] administered NPDES permit SC#0001848. WEC [Westinghouse Electric Company] is required to notify SC-DHEC of non-compliance conditions which exceed any effluent limitation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2010-05-12
45918 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-05-11 23:18 | 2010-05-12 03:12 | 2010-05-12 | MANUAL REACTOR SCRAM DUE TO LOSS OF CONTROL ROD DRIVE CHARGING WATER HEADER PUMPS "On May 11, 2010, at approximately 2318 hours, a manual Reactor Protection System (RPS) actuation was initiated as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.5 'Control Rod Scram Accumulators.' Control Rod Drive (CRD) charging water header pressure was less than 1520 psig (i.e., no CRD pumps operating) and there were multiple accumulator faults on withdrawn control rods. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the core and the plant is currently stable, in Mode 3 (Hot Shutdown) with reactor pressure at approximately 930 psig. No Emergency Core Cooling Systems were required or utilized to respond to the event and there were no other 10 CFR 50.72 reportable actuations. Reactor coolant level is being maintained in its normal band by the feedwater system and decay heat is being removed by the condenser. The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available if needed. "The cause of the event initiator, an invalid Division 2 Loss of Coolant Accident (LOCA), i.e., High Drywell Pressure/Low Reactor Vessel Water Level, signal, is currently under investigation. Prior to the manual RPS Actuation, the invalid LOCA signal resulted in invalid actuations of Division 2 equipment and systems including, the Division 2 Emergency Diesel Generator (EDG), (which started but did not load onto the bus), Low Pressure Coolant Injection B and C subsystems (which started the pumps but did not inject into the vessel), discharge of the Suppression Pool Makeup subsystem B into the suppression pool, startup of the Control Room Emergency Recirculation subsystem B, and isolation of Group 2B Containment isolation valves which included the Nuclear Closed Cooling System Containment Return Isolation valve that was not already closed. The affected equipment is being restored in accordance with plant procedure. The NRC Resident Inspector has been notified." The licensee experienced an instrumentation rack loss of power which appears to have resulted in the inadvertent Division 2 initiation. The initiator of this event also and led to a loss of power to both control rod drive charging water header pumps resulting in charging water header pressure less than required and related accumulator faults which placed the licensee in a technical specification required shutdown condition. The action statement allows only 20 minutes to restore the condition which was insufficient time for the licensee to correct the condition so a manual scram was initiated from 100% power. The scram was characterized as an uncomplicated scram and all system responses (not related to the initial instrument fault) functioned as required. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2010-05-12
45917 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-05-11 17:09 | 2010-05-11 17:48 | 2010-05-11 | OFFSITE NOTIFICATION "[On] May 10, 2010 at 1710 hours a USEC (United States Enrichment Corporation) Protective Force Officer entered the X-104 Police Headquarters Weapon Cleaning Area to perform cleaning maintenance on his assigned weapon. The officer began to disassemble the weapon [while] pointing the weapon in a safe direction. He pulled the trigger to release the slide and the weapon discharged (this action is required to remove the slide from this type of weapon). The officer in question was the only person in the room at the time of the incident. The officer was not struck by the discharge, however he did sustain minor powder burns to his hand. The area and weapon was immediately secured by Protective Force Management personnel. USEC Fire/EMS were summoned to the incident scene where the officers injury was evaluated at which time the officer refused treatment. Personal statements were collected from all personnel in the immediate area. A critique was conducted. The Protective Force Manager has generated a Long Term Order to provide compensatory actions to prevent recurrence of an accidental discharge of a weapon due to the same or similar circumstances. An internal investigation as well as an independent investigation are currently in progress. "This event was reportable to the Department of Energy per XP2-RA-RE1001 6.2.1, which requires a formal notification. This formal notification constitutes the need to report this event to the Nuclear Regulatory Commission within four (4) Hours per criteria listed in procedure UE2-RA-RE1030, Appendix 'D', P." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2010-05-11
45916 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-05-11 09:30 | 2010-05-11 16:12 | 2010-05-11 | LOSS OF TECHNICAL SUPPORT CENTER "On 05-11-10 at 09:30 hours the Technical Support Center (TSC) ventilation, filtration and climate control system was identified as nonfunctional. The TSC was declared nonfunctional. A plan has been implemented for performance of TSC functions in alternate locations in accordance with site emergency implementation procedures. "At 13:00 hours on 05-11-10, the system was placed back in service but is still considered non-functional while additional trouble shooting is being performed and final repairs are made." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-11
45915 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-05-10 | 2010-05-11 12:15 | 2010-05-24 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of North Dakota via email: "T&K Inspections, Inc., reported the inability to retract a 3.55 TBq (96 Ci ) Ir-192 radiography source into the exposure device (Source Production & Equipment Company Model SPEC 150, serial number 295) on May 10, 2010. Operations were being performed approximately 2 miles south of Highway 2, on 94th street, south of Ross, ND about 9:00 am CDT. "After completing the exposure, the radiographer and assistant radiographer performed the routine procedure to retract the source into the camera. The survey meter registered no activity above background, so they believed the source had retracted. As the radiographer approached the camera, the survey meter registered off-scale. He immediately stepped away from the camera and attempted to check the cable and retract the source. At this time, his pocket dosimeter registered 3mR/hr. With the survey meter continuing to register activity, the President and assistant RSO of T&K Inspections, Inc. was contacted. He suggested working with the crank and they were able to retract the source into the camera. The camera was located near the vehicle. As the radiography crew placed the camera onto the end gate of the truck, the survey meter and his pocket dosimeter were off-scale. They immediately moved away from the camera and called the assistant RSO again. The cables were still connected to the camera, so the assistant RSO had the radiographer straighten the cable and try to retract the source. The source was successfully retracted into the camera housing. The camera was secured in the vehicle and the crew returned to the shop. "Prior to this incident, T&K Inspections, Inc. believed they had trouble with the lock mechanism on this camera. April 28, 2010, the camera was sent to SPEC for inspection and maintenance. Maintenance and inspection was performed on the camera May 3, 2010. SPEC replaced parts of the camera and returned it to T&K Inspection with a certification document. The camera was placed back into service and has been used prior to the incident. T&K Inspections, Inc. believes when the camera was returned to the vehicle the lock mechanism was not functioning properly. "The assistant RSO has sent the film badges overnight delivery to be evaluated. The radiographer and assistant radiographer will not perform radiography until return of the dosimetry reports. The assistant RSO will follow-up with a report of the incident, copy of the camera certification, copy of the film badge reports and any other pertinent information as needed. "The camera has been taken out of service and will be returned to SPEC. It will be determined if the camera or parts will be replaced." Camera source information: "Ir-192 SPEC G-60 Source, S/N RE0304, 96 Ci "State Action: "1. The North Dakota Department of Health (NDDOH) will maintain contact with T&K Inspections, Inc. to determine the root cause of the incident. "2. The NDDOH will receive a copy of the dosimetry reports and a copy of the certificate from SPEC from the camera maintenance and inspection that was performed prior to the incident. "3. The NDDOH will follow-up with the camera inspection that will be performed at this time." * * UPDATE FROM LOUISE ROEHRICH TO JOHN KNOKE AT 1547 EDT ON 5/20/10 * * The radiographer and assistant radiographer received 1181 mRem and 756 mRem respectively. Notified FSME (James Danna) and R4DO (Vivian Campbell) * * * UPDATE ON 5/24/2010 AT 1100 FROM LOUISE ROEHRICH TO MARK ABRAMOVITZ * * * The radiography camera was inspected in the field and the problem was replicated. The camera has been taken out of service, returned to the manufacturer for disposal, and replaced with a different camera. A calculation of the dose to the radiographer's hand estimated the dose at 12.3 REM. Analysis of the problem by the licensee revealed that procedures were not followed and the problem could have been prevented. The licensee is reviewing procedures with all personnel. Notified R4DO (Shannon) and FSME (McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2010-05-14
45914 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-05-11 06:45 | 2010-05-11 07:47 | 2010-05-11 | ACTUAL CONTRABAND ENTRY INTO THE PROTECTED AREA Actual entry of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-11
45913 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-04-16 05:21 | 2010-05-10 16:36 | 2010-05-10 | INADVERTENT STEAM ADMISSION TO AFW TURBINE During maintenance on sliding links, the steam admission valve (SA-48) for the Auxiliary Feedwater (AFW) turbine inadvertently opened. Inadequate isolation from the steam header allowed steam flow through SA-77 steam drain valve into the turbine. This small amount of steam caused the pump to rotate at approximately 1000 rpm for approximately 2 minutes. Due to the low discharge pressure, no water was injected into the steam generator during this actuation. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-05-10
45912 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2010-05-05 | 2010-05-10 09:37 | 2010-05-10 | AGREEMENT STATE REPORT - FOUND GENERAL LICENSE DEVICE The following information was received via facsimile: "On the afternoon of May 5, 2010, the Alabama Office of Radiation Control received a phone call from a representative of ELG Metals in Mobile, Alabama advising the [Alabama Office of Radiation Control] Agency of the discovery of a device containing Am-241. The Agency was advised that the device was in two pieces. A member of the Department's Expanded Radiological Emergency Response Team was dispatched to verify if the sealed source was intact. On the afternoon of May 5, 2010, a field leak test was performed and its was determined that the sealed source was intact. The device was isolated at that time. On the morning of May 7, 2010, a representative of the Alabama Office of Radiation Control visited ELG Metals in Alabama to determine the condition of the device and assist in identifying the source of radiation. The source of radiation was identified as a NDC model 102, serial number 3572 containing 150 millicuries of Am-241. The investigation determined that the device was last owned by United Nonwoven in Mobile and was originally distributed as a General License device to Stems Technical Textiles in Cincinnati, OH. United Nonwoven in Mobile is no longer in business. The source of radiation was isolated and preliminary leak test results in the field indicate that the source is not ruptured. "This is all the information that [Alabama Office of Radiation Control] Agency has at this time and is current as of 8:30 am central time, May 10, 2010." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-05-13
45911 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-04-29 | 2010-05-07 15:49 | 2010-05-07 | AGREEMENT STATE REPORT - POTENTIAL DOSE TO EMBRYO OR FETUS The State of Colorado provided the following information via email: "In accordance with [Colorado Code] 7.23.1 [similar to 10 CFR 35.3047], Mercy Medical Center, Durango, CO is reporting a dose to an embryo/fetus in excess of 5 mSv." "On March 16, 2010 1110 MBq (30 mCi) of I-131 was administered to a 31 [year old] female patient." "A serum blood [pregnancy] test was taken prior to administration and was negative. On April 26, 2010 the patient, thinking she might be pregnant, took a home urine [pregnancy] test that showed positive. Pregnancy was confirmed by blood serum test on April 27, 2010. Patients OB/GYN physician estimates conception occurred on March 13, 2010." "Fetal dose was estimated to be approximately 80 mGy (8 rem). At this dose level and administration time in relation to fetal development (still in blastogenesis), there will likely be no impact upon subsequent fetal development or subsequent health risks. The patient has been notified as such." The Department has begun an investigation of this incident and will keep the NRC informed of the status of our investigation. The licensee stated that all procedures to prevent this occurrence were followed. Human chorionic gonadotropin (Hcg) is not detectable in the blood until 7 - 12 days post conception. The licensee is considering including additional questions during the screening process. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-05-12
45910 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-04-23 14:45 | 2010-05-07 14:35 | 2010-07-16 | AGREEMENT STATE REPORT - EXTERNAL RADIATION LEVELS EXCEED LIMITS The following was received via email from the Commonwealth of Massachusetts: "Lantheus Medical Imaging (LMI) received a customer complaint on 4/23/10 from a customer (GE Healthcare in Tampa, FL) reporting a reading of 310 mR/hr on a Tc-99m generator that was manufactured on 4/22/10 at the facility in Billerica, MA. On 4/27/10, LMI was able to clarify that the reading was on the package surface rather than on the generator itself. "The customer reported the situation to the Florida Bureau of Radiation Control on 4/28/10. LMI has been investigating and have not yet found any evidence of a problem with this generator in their manufacturing records. LMI will continue to investigate and will be receiving the generator back from the customer in the next week or so. They will then examine it directly." The R1DO (Cook) and FSME (Suber) have been notified. * * * UPDATE FROM JOHN SUMARES TO JOE O'HARA VIA FAX AT 1041 ON 5/10/10 * * * The Commonwealth clarified their report that the TC-99m generator is actually a Mo-99 generator. Notified R1DO (Gray) and FSME (McIntosh). * * * UPDATE FROM JOHN SUMARES TO JOHN KNOKE AT 1213 EDT ON 7/16/10 * * * The following was received via fax from the Commonwealth of Massachusetts: "This updated information is taken from Lantheus Medical Imaging letter dated June 11, 2010. "Lantheus Medical Imaging received the generator back from the customer on 5/10/10 and performed tests and inspections on the unit. LMI found no evidence of any defect or condition that could have caused the high reading. Their radiation levels measured on 5/10/10 and back decayed for this generator on the day of manufacture was reported as 140 mR/hr. LMI reports there are only two scenarios to explain the high readings: "1, Migration of Tc-99m activity out to an unshielded section of the fluid path while the generator was in transit. LMI reports that this would involve an as yet unknown failure mode since all required fittings and plugs were in place at time of inspection of the returned generator. "2. The 310 mR/hr reading is in error, given that the customer reported a normal TI value, (i.e., 4.6 mR/hr measured vs. 5.2 mR/hr label value), a high reading Is difficult to explain, and the customer could shed no light on this apparent discrepancy. "Based on the reported measurements of the returned generator which were back decay calculated to 140 mR/hr, it appears that the labeled TI value was correct. The customer's TI measurements agreed with the labeled TI value. The Agency [Commonwealth] considers this event to be closed." Notified R1DO (Joustra) and FSME (Villamar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-05-12
45909 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2010-04-26 12:00 | 2010-05-07 09:10 | 2010-05-21 | AGREEMENT STATE REPORT - STUCK/DAMAGED RADIOGRAPHY SOURCE Received this report from the State of Louisiana via facsimile: "On April 26, 2010, at a temporary job site a field crew was performing an X-Ray on a pipeline when the X-Ray source could not be returned to the shielded position. Using their survey meters, the crew determined the source was exposed and could not be retrieved. They called the Assistant Radiation Safety Officer who came and did a source retrieval and [received] a 150 mrem exposure. With the source shielded, the licensee transported the camera to QSA Global in Baton Rouge, LA for analysis. The equipment was a Sentinel, model 660B, S/N 82187, loaded with 69.5 Ci of Ir-l92, S/N 60611B. QSA Global observed the source and performed further evaluation. The results were that the weld on the source cracked and the capsule was catching on the exit port of the camera. QSA Global put out a recall for that particular lot of sources and forwarded the damaged camera to QSA Global in Burlington, MA." This event is Louisiana report # LA1000004 * * * UPDATE FROM JOHN SUMARES TO CHARLES TEAL VIA FAX AT 1054 ON 5/21/10 * * * This report was received from the Commonwealth of Massachusetts via facsimile: "On May 3, 2010 an agency [Commonwealth of Massachusetts Bureau of Radiation Protection] inspector visited QSA Global in response to this event. The inspector observed the route cards for all 6 sources from this production lot of the problem source assembly, serial number 60611B, manufactured for H and H X-Ray of Louisiana only. All 6 sources were returned to QSA Global for analysis and the other 5 sources were found to be properly welded and wipe testing of all 5 sources indicated no sources were leaking. In addition, wipe test of the problem source indicated this source was not leaking. [The] inspector also observed the next day's test weld which was analyzed and deemed acceptable prior to welding sources for the next days source production. "[The] inspector observed the outer encapsulation of the source that caused this event. The outer capsule laser weld was not completed along the weld joint, but slightly below the weld joint, thus the capsule was not properly welded. At the time of manufacture, leak testing (vacuum bubble test) of the problem sources weld did not reveal an improperly welded capsule. The inner capsule was properly welded and sealed, Thus the leak test (wipe test) did not reveal contamination. QSA Global ascertained that human error allowed the improperly welded outer capsule to pass the vacuum bubble test. QSA assembled a test outer encapsulation in the same manner as the problem source (i.e. an improper weld, located below the weld joint) and found that the vacuum bubble test easily detects that the capsule was not properly welded. QSA Global committed to submit a final report to the agency within a few weeks." Notified R4DO (Pick) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2010-05-12
45908 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-04-29 | 2010-05-07 02:39 | 2010-05-07 | AGREEMENT STATE REPORT - POSSIBLE LOST X-RAY ANALYZER The following was received from the State of California via email: On May 5, 2010 the California Radiologic Health Branch (RHB) was informed by the alternate Radiation Safety Officer (RSO) of Chevron USA that they may have lost a Niton, XLP 818, S/N 13354, containing a 30 mCi Am241/Be sealed source. According to the alternate RSO, the Niton XLP was lost and was reported to him by the Material Inspection Group supervisor on April 29, 2010. This incident was not reported to RHB because the licensee was looking for the Niton XLP until the date of this report. CA Report #: 050610 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-05-11
45907 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-05-06 13:46 | 2010-05-06 16:19 | 2010-05-06 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER MALFUNCTION The following information was received from the State of Nebraska via facsimile: "The licensee uses fixed industrial gauges for measuring densities in fly ash hoppers at the station's precipitator building. The industrial gauges contain a Cesium 137 sealed source. The Cesium 137 sources were originally installed in 1975 and at the time contained 50 millicuries per source. "The sources were manufactured and installed by Kay Ray Inc. "The gauges are Model No. 7700-50. "The licensee was attempting to close the shutter on the fixed gauge prior to performing maintenance. One of the external closure cables was found to be slightly bound up and only partially closed the internal source shutter. The cable closure was reopened, which reopened the source shutter up at the sealed source. Closure was tried again. This time the cable, which connects the handle at the floor to the sealed source shutter mechanism 20 feet above, bent instead of sliding the cable to the closed position. "This event happened at 1346 [CDT] and was reported to the station's Shift Supervisor who in turn contacted the plant electricians to make repairs so the precipitator tag-out could continue. By 1353, the cable had been closed and the lab contacted to perform a survey to verify the source shutter was in the closed position. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-05-11
45906 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-05-06 14:40 | 2010-05-06 16:50 | 2010-05-06 | TECHNICAL SUPPORT CENTER NONFUNCTIONAL "On 05-06-10 at 1440 hours the Technical Support Center (TSC) ventilation, filtration and climate control system was identified as nonfunctional. The TSC was declared nonfunctional. A plan has been implemented for performance of TSC functions in alternate locations in accordance with site emergency implementation procedures. Site maintenance has initiated trouble shooting and repairs will be implemented." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-06
45905 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2010-05-06 12:00 | 2010-05-06 15:09 | 2010-05-07 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The following information was provided by the Commonwealth of Virginia via facsimile: "On May 6, 2010 the licensee reported a missing Troxler portable gauge, Model 3430, Serial Number 36089. The utilization log indicated that a user had returned the gauge to the storage facility on April 23, 2010. On the morning of April 24, 2010 the user found the gauge was no longer in storage and assumed it had been sent for routine maintenance and repair and did not report it missing to the RSO (Radiation Safety Officer) or management. They became aware it was missing on May 6, 2010 while routine leak testing was being performed. "The licensee's representative stated that procedures require the gauge to be secured by a chain with padlock inside a locked caged area in a warehouse. The chain was present with the open padlock and there was no reported vandalism or forced entry into the warehouse or caged area. "The circumstances regarding the gauge are under investigation by the Virginia Department of Health Radioactive Materials Program. The licensee has contacted the Loudoun County Sheriff's Office and is conducting interviews with the user and other staff to determine if additional information is available." This event is VA report #VA-10-03. * * * UPDATE FROM MIKE WISE TO DONALD NORWOOD ON 5/7/2010 AT 1844 EDT * * * The gauge was found in the trunk of an authorized user's car. The gauge is being returned to its normal storage location and will be secured there. Notified R1DO (Cook), FSME EO (Suber), and ILTAB (via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2010-05-11
45904 | -1 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2010-05-04 12:19 | 2010-05-06 00:57 | 2010-05-07 | SAFEGUARDS REPORT - DISCOVERED VULNERABILITY Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM DAVID LANYI TO ERIC SIMPSON ON 05/07/10 AT 1415 EDT * * * It has been determined that compensatory measures had in fact been employed for the vulnerability in question. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (O'Donohue). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-06
45903 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2010-05-05 15:10 | 2010-05-05 19:26 | 2010-05-05 | INJURED INDIVIDUAL HOSPITALIZED "On May 5, 2010 at approximately 1510 PDT, a notification was made to the Washington State Department of Labor and Industries regarding an in-patient hospitalization of an Energy Northwest employee as required by Washington Administrative Code. "On May 3, 2010 high wind conditions were occurring at the plant site. While this individual was outside, a high gust of wind occurred resulting in the individual falling and injuring himself. The individual received treatment from a local medical facility and was released that day. On May 5, the individual identified additional symptoms and was admitted to a local hospital which resulted in in-patient hospitalization and treatment." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-05-05
45902 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-05-05 11:44 | 2010-05-05 15:11 | 2010-05-05 | AUTOMATIC REACTOR SCRAM DUE TO REACTOR FEED PUMP TRIP "On May 5, 2010, at 1144 hours Eastern Daylight Time (EDT), an automatic reactor scram occurred on Unit 1 following a trip of the 1B Reactor Feed Pump (RFP). Following the 1B RFP trip, the reactor recirculation pumps did not run back as expected. The resulting water level shrink caused level in the Reactor Pressure Vessel (RPV) to drop to Low Level 1, causing the activation of the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS). All control rods properly inserted. "PCIS Group 2 (i.e., Drywell Equipment and Floor Drain, Residual Heat Removal (RHR) Discharge to Radwaste, and RHR Process Sample), Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems), and Group 8 (i.e., RHR Shutdown Cooling) isolation signals were received on Low Level 1. Actuations of the Primary Containment Isolation Valves (PCIVs) were completed and the affected equipment responded as designed. "Due to the expected RPV level reduction following a reactor scram, water level in the RPV momentarily reached Low Level 2. This initiated the High Pressure Coolant Injection (HPCI) System, the Reactor Core Isolation Cooling (RCIC) System, and a partial Group 3 PCIS (i.e., RWCU) isolation. The HPCI and RCIC systems did not inject. The 1-G31-F001 isolated (i.e., inboard isolation) but 1-G31-F004 (i.e., outboard isolation) did not automatically isolate. Based on a preliminary assessment, this response appears to be in accordance with plant design. Further assessments of plant response are on-going to validate plant response. "The licensee has notified the NRC Resident Inspector." The scram was uncomplicated. No SRVs lifted. Decay heat removal is via the 'A' feed water pump via the turbine bypass valves to the condenser. The electrical line-up of Unit 1 is normal. Brunswick Unit 2 was not affected. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-05-05
45901 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2010-03-15 01:38 | 2010-05-05 14:04 | 2010-05-05 | OPTIONAL 60-DAY REPORT OF INVALID SPECIFIED SYSTEM ACTUATION "This telephone notification is being provided in accordance with 10CFR50.73(a)(1) for an invalid actuation reportable under 50.73 (a)(2) (iv)(A). "On March 15, 2010 at 0138 hours, during full power operations, Division 2 Drywell Ventilation (VP) and Drywell Cooling (WO) Primary Containment Isolation Valves (PCIVs) closed for isolation Groups 11 and 17. The affected valves were inboard PCIVs 1VP005A, 1VP005B, 1VP014A, 1VP014B, 1WO001B, 1W0002B, 1WO551B and1WO552B. The shunt trip devices for the breakers for the following components were tripped: Drywell cooling fan 1B (1VP01CB), Drywell cooling fan 1D (1VP01CD), Drywell chiller 18 oil pump, DC Motor Control Center (MCC) 1B ground detection, DC MCC 1B ground detection, Drywell Chiller 1B(1VP04CB), and Drywell Chiller control panel 1B. "The cause of the isolation was determined to be that a Division 2 load driver card spuriously actuated all of its loads without a valid Loss Of Coolant Accident (LOCA) signal or a manual initiation signal present. A reset of the Group 11 and 17 isolations was completed at 0208; the shunt trips were reset at 0215; and Drywell Cooling was restored by 0259 on March 15. The load driver circuit remained in service until a replacement load driver card could be installed on March 19, 2010. The cause of the card failure could not be determined; however the most probable cause is either an intermittent failure of the card or an intermittent short of the output connectors. "The actuation of primary containment isolation Groups 11 and 17 was complete and the isolation/actuation was limited to only these two groups. "The NRC Resident Inspector was notified of this notification." | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-05-05
45900 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-05-05 05:00 | 2010-05-05 05:07 | 2010-05-05 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PREVENTIVE MAINTENANCE "On May 5, 2010, at 0500 hours EDT, Fermi 2 removed the Technical Support Center (TSC) from operation to facilitate routine preventive maintenance on the facilities' heating ventilation and air-conditioning system. During this work, which is expected to last approximately 12 hours, the TSC will be unavailable. In the event TSC activation is necessary, the Emergency Operations Facility (EOF) will be used for the TSC function. Activation and use of the EOF as a backup for the TSC is included in Fermi 2's Radiological Emergency Response Preparedness Plan. The Emergency Call Out System (ECOS) is designed to facilitate contacting TSC personnel to respond directly to the EOF in the event of an emergency. Fermi 2 is making this notification in accordance with 10 CFR 50.72(b)(3)(xiii). Fermi 2 will notify the NRC upon completion of this work. Fermi 2 has notified the NRC Resident Inspector." * * * UPDATE FROM JIM KONRAD TO PETE SNYDER ON 5/5/10 AT 1725 EDT * * * "Maintenance to restore ventilation has been completed. The TSC has been restored as an Emergency Response Facility." Notified R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-05-05
45899 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2010-05-04 18:50 | 2010-05-04 19:32 | 2010-05-04 | ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-04
45898 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2010-05-04 15:12 | 2010-05-04 16:56 | 2010-05-05 | DISCOVERY OF AFTER-THE- FACT EMERGENCY CONDITION - UNUSUAL EVENT DUE TO RCS LINEUP "On 5/4/2010 at 15:12 CDT when attempting to flush CH-1A charging pump, a loss of charging flow occurred. CH-193 discharge valve for CH-1A charging pump was found to be open. This resulted in a flow path to the auxiliary building sump tank when CH-356 charging pump CH-1A discharge drain valve to waste disposal system was opened. This resulted in an approximately 38 gpm leak from the reactor coolant system via letdown to waste. This leak was isolated within 1 minute." The site entered and exited the conditions for NOUE before the shift manager was able to make an E-plan call. There are currently no emergency conditions on site and an NOUE was never declared. The reactor continued to operate at 100% power throughout the event. The cause of this event is believed to be a valve line-up error. The NRC Resident Inspector has been notified. The site plans to notify the State of Nebraska. No other notifications are planned. * * * RETRACTION AT 1625 EDT ON 5/5/10 FROM MATZKE TO HUFFMAN * * * "The declaration of Unusual Event SU 5 EAL 2, RCS leakage, on 5/4/10 is being retracted, because the declaration was inaccurate. The leak was an intersystem leak of the CVCS, not RCS leakage, and the leak was isolated as previously noted. Therefore, the leakage did not meet the initiating condition for the EAL." The licensee has notified the NRC Resident Inspector and plans to notify the State of Nebraska. Notified R4DO (Farnholtz), NRR EO (Quay), and IRD (McDermott). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2010-05-04
45897 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-05-03 15:55 | 2010-05-04 09:43 | 2010-05-04 | AGREEMENT STATE REPORT - STUCK SHUTTER The State of Texas provided this information via email: "On May 3, 2010, the licensee discovered that the shutter of a nuclear gauge mounted on the Ryton Quench Salt Solution Tank was stuck in the 'Open' position. The gauge is an Ohmart-Vega Model SH-F1 serial #6966CN, with a 20 mCi Cesium (Cs)-137 source. Initial efforts were made to free the shutter mechanism with penetrating oil and hand pressure, with no results. The shutter mechanism has been tagged out and the manufacturer has been contacted. The gauge is stuck in the open position which is its normal operating position. The source does not present an increased exposure risk to personnel as there are no identified needs for entry/opening of the vessel which would require lockout of the gauge. "The licensee is working with the manufacturer to arrange for a field service engineer to evaluate/repair/replace the stuck shutter. This shutter had previously failed in October 2009 (EN45399, I-8675.) Repairs had been made and a protective cover for the gauge was installed at that time." Texas Incident Report # I-8737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-05-07
45896 | 0 | FOLA COAL COMPANY, LLC |  |  |  |  | 2010-04-30 12:00 | 2010-05-03 15:29 | 2010-05-03 | SOURCE HOLDER MALFUNCTION On Friday, April 30, 2010, at approximately 1200 EDT, while replacing sources in a Gamma-Metrics Model 2000 Bulk Material Analyzer, it was discovered that the right side source holder had dropped three Cf-252 sources back into the stored and shielded position. Two of the three sources have been recovered, but one remains in the body of the instrument inside the safe and shielded compartment. Exposure rate measurements have been taken and no exposure or safety hazards exist. Efforts to retrieve the remaining source will continue on May 6, 2010. Each Cf-252 source is 0.8 micrograms, which is approximately 4.3 mCi in activity. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-05-03
45895 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2010-05-03 | 2010-05-03 11:53 | 2010-05-03 | AGREEMENT STATE REPORT - LOSS OF RADIUM CHECK SOURCE The following information is a summary of a report provided by the State of North Carolina via facsimile: A state inspector performed an inspection on April 20, 2010, and learned that a radiation source (Ra-226, 20 microCuries) used in the facility's liquid scintillation counter, Packard Tri-Carb Model, was lost or missing. The RSO [Radiation Safety Officer] and inspector performed a survey of all the labs with a Ludlum Model 19 and were not able to find the source. In addition, it was found that no paperwork was available indicating proper source tracking, leak testing, or disposal of the source. A violation letter has been mailed to the RSO allowing the licensee thirty days to respond to the violation. NC Incident No. 10-22. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2010-05-06
45894 | 0 | WALTER REED ARMY MEDICAL CENTER |  |  |  |  | 2010-05-01 12:49 | 2010-05-03 11:27 | 2010-05-03 | MISPLACED RADIOACTIVE MATERIAL On 5/1/10, at 1249 EDT, a 2 Ci Mo-99 generator was delivered to the Walter Reed Army Medical Facility. An unauthorized person signed for the package and stored it in an improper location. On the evening of 5/1/10, the health physicist did not know the location of the package, because it was supposed to be delivered earlier in the day. The package was located at 0815 EDT on 5/3/10 at the facility. The licensee has now stored the package in proper location and is in process of conducting a dosage calculations for any individuals who may have been in the vicinity of the package where it was improperly stored. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-05-03
45893 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-05-02 08:58 | 2010-05-02 15:27 | 2010-05-02 | MANUAL ACTUATION OF AUXILIARY FEEDWATER SYSTEM IN RESPONSE TO LOSS OF ONE MAIN FEEDWATER PUMP "At 0858 [EDT] on Sunday, May 2, 2010, operators manually started all Auxiliary Feedwater (AFW) pumps in response to a loss of the East Main Feedwater Pump (EMFP). "Operators were responding to high bearing temperatures on the EMFP, and had entered the Rapid Power Reduction Procedure, when they received EMFP Hi and Hi-Hi vibration alarms and reports of oil leaking from the EMFP. Operators entered the procedure for Loss of One Main Feed Pump, which directs starting the AFW pumps, and removed the EMFP from service. The plant was stabilized at approximately 49% power. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(iv)(A) due to the valid actuation of the AFW system in response to equipment failure." | 49 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-05-02
45892 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-05-01 20:06 | 2010-05-01 21:00 | 2010-05-01 | SECURITY PRECAUTIONS TAKEN DUE TO SEVERE WEATHER Specific security measures have been suspended or modified due to severe/hazardous weather on site. Compensatory measures have been taken. Contact the Headquarters Operations Officer for additional details. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE FROM BILLY JOHNSON TO HOWIE CROUCH @ 2148 EDT ON 5/1/10 * * * Security measures have been restored to their normal posture. The licensee has notified the NRC Resident Inspector. Notified R2DO (McCoy) and the 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Under Construction |  | Power Operation | Under Construction |  | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-05-01
45891 | 0 | PARTICLE DRILLING TECHNOLOGIES |  |  |  |  | 2010-04-26 | 2010-05-01 16:28 | 2010-05-01 | GAUGE SHUTTERS STUCK OPEN On April 26, 2010, while the licensee, Particle Drilling Technologies out of Houston, Texas was performing a scheduled shutter operation check, the shutter on a Ronan Model SA1 nuclear gauge failed to close. They were at a remote drilling site in the Pinedale, Wyoming when this occurred and was using the gauge as generally licensed material under its Texas license. The gauge contains 20 millicuries of Cesium (Cs) 137 (S/N #6198CN). The gauge is in its normal operating position and a radiation survey conducted by the licensee indicated that radiation levels are normal. The gauge was leak tested and the test sent for analysis. The licensee stated that there is no risk of additional exposure to their workers. The licensee is working with the manufacturer to schedule the repair of the gauge on May 18, 2010. The licensee reported this incident to the NRC Operations Center on April 27, 2010, and it was logged until it could be determined whether this incident should be reported to the State of Texas or the NRC. It was determined that since the event occurred in Wyoming, it is an NRC report. On May 1, 2010, the licensee was performing shutter checks when they discovered two more shutters were stuck in the open position. These are also Ronan Model SA1 gauges that contain 20 mCi Cs-137 sources. Their serial numbers are 6115CN and 5808CN. The vendor is still scheduled for onsite repairs on May 18. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-05-01
45890 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-04-30 10:15 | 2010-05-01 08:46 | 2010-05-01 | TAR FOUND ON OVERPRESSURE RUPTURE DISCS POTENTIALLY CHANGING THE RELIEF SET POINT "On 04/30/10 the Plant Shift Superintendent (PSS) was notified that while performing maintenance on C-337 Unit 2 Cell 4 Odd R-114 rupture disc replacement, roofing tar was discovered in the upper rupture disc. C-337 U/2 C/4 Odd system was not in a mode of applicability according to TSR [Technical Safety Requirement] 2.4.3.4. The presence of the roofing tar on an operable R-114 coolant overpressure control system rupture disc would not allow the rupture disc to perform its intended safety function as required by TSR 2.4.3.4. The R-114 rupture disc is the primary component of the R-114 coolant overpressure control system. The R-114 coolant overpressure control system prevents excess coolant pressure from rupturing the coolant system and releasing coolant into the UF6 primary system that could result in the subsequent release of UF6 due to over pressurization of the UF6 system. TSR 2.4.3.4 and 2.3.3.2 require that the R-114 coolant overpressure control system be operable. An extent of condition inspection of in use R-114 rupture discs is in progress. Roofing tar was discovered on R-114 coolant overpressure control system rupture discs in the following locations: C-337 cells U/3 C/2 Odd, U/1 C/5 Odd, U/1 C/6 Odd, U/6 C/4 Odd, U/2 C/5 Even, U/5 C/4 Odd, U/5 C/6 Even, U/5 C/8 Odd, U/4 C/7 Even (Not in an applicable mode), U/2 C/4 Odd (Not in an applicable mode). U/6 C/7 Odd (Not in an applicable mode). C-331 U/1 C/4 (Not in an applicable mode). Buildings C-310 and C-335 R-114 coolant overpressure control system rupture discs were inspected and were free of any foreign material. Systems that are in an applicable mode according to TSR 2.4.3.4 and were discovered to have roofing tar on the rupture discs were declared inoperable and an operator was stationed to continuously monitor the R-114 pressure in order to take action according to TSR 2.4.3.4. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-l0-1131; PGDP Event Report No. PAD-2010-6" * * * UPDATE FROM JOE BARLETTO TO HOWIE CROUCH @ 2254 EDT ON 5/1/10 * * * "On 05-01-2010 at 2225 hours, extent of condition walk downs have been completed. Additional R-114 rupture disc locations were discovered with either roofing tar and/or shipping caps in the upper rupture disc. The presence of either would not allow the R-114 rupture disc to perform its intended safety function as required by TSR 2.4.3.4. Systems that are in an applicable mode according to TSR 2.4.3.4 and were discovered to have roofing tar and/or shipping caps on the upper rupture discs were declared inoperable and an operator was stationed to continuously monitor the R-114 pressure in order to take action according to TSR 2.4.3.4." The licensee provided a list of 28 cells that had shipping caps installed and 13 cells with roofing tar on the discs. "The NRC Senior Resident Inspector has been notified of this event." * * * UPDATE FROM ROD COOK TO JOHN KNOKE @ 1737 EDT ON 5/2/10 * * * "On 5/02/2010 at 0636 hours during a review of the extent of condition inspection notes, engineering identified that C-333 U/4 C/9 Even R-114 Over-pressurization system had been omitted from the report due to oversight. Engineering had identified a shipping cover with tar on it was present on the rupture disc. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-10-1141; PGDP Event Report No. PAD-2010-6. Responsible Division: Operations" Notified R2 DO (Randy Musser) and NMSS EO (Tim McCartin) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2010-05-01
45889 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-04-30 21:00 | 2010-05-01 02:01 | 2010-05-01 | INADVERTENT SYSTEM ACTUATION OCCURRED DURING A SURVEILLANCE TEST "Unit 2 was performing a planned refueling outage surveillance test, FNP-2-STP-40.0, Safety Injection with Loss of Off-Site Power. The system was being returned to normal following the actuation portion of the test. When the B2F Sequencer was reset, a loss of off-site power (LOSP) occurred, which caused a loss of the 'A' Train 4kV busses, and an LOSP signal was generated. The 1-2A Diesel Generator was already running at normal speed, and voltage. Therefore, the diesel generator output breaker opened, and then reclosed which then allowed the LOSP loads to automatically start. This included the 2A Motor Driven Auxiliary Feedwater Pump, and the 2A High Head Safety Injection Pump. Therefore, during the test, the system actuated in a way that was not part of the planned evolution. "The investigation indicated that a recent design change on the diesel generator output breaker circuitry had not been fully incorporated into the test procedure. The test procedure currently in progress was revised to provide guidance for operating the B2G Sequencer Test Trip Override switch. The restoration section for the 'B' Train was completed with no further complications when the B2G Sequencer Test Trip Override switch was operated before resetting the B2G Sequencer." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-05-01
45888 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-04-30 16:48 | 2010-04-30 22:31 | 2010-06-29 | LIGHT SOCKET SHORT CAUSES ISOLATION SYSTEMS TO ACTUATE "At 1648 CDT, while the Control Bay AUO [Auxiliary Unit Operator] was attempting to change a light bulb for 1-IL-99-1AA, 1A [Reactor Protection System] RPS [Motor Generator] MG Set available light, the light socket shorted causing the loss of 1A RPS. The loss of 1A RPS resulted in Groups 2, 3, 6, and 8 primary containment isolations and initiated Standby Gas Treatment and Control Room Emergency Ventilation. All systems responded as designed. The Control Room operators entered the appropriate abnormal operating instruction, 1-AOI-99-1, to restore the affected systems. Operations entered TS LCO 3.3.1.1 conditions A.1 (place channel in Trip in 12 hours) and C.1 (restore RPS trip capability in 1 hr). At 1734 CDT, Operations exited TS LCO 3.3.1.1 upon restoration of 1A RPS per 1-AOI-99-1. "This event is reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) 'Any event or condition that results in a valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) [b. General Containment Isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs)], except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' This event also requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." * * * RETRACTION FROM RAY SWAFFORD TO DONG PARK AT 1522 EDT ON 6/29/10 * * * "Retraction of an 8 hour non-emergency notification for invalid Primary Containment Isolation System (PCIS) actuation from a loss of power to the Reactor Protection System (RPS) 1A. "Browns Ferry Nuclear Plant (BFN) is retracting the 10 CFR 50.72(b)(3)(iv)(A) eight-hour non-emergency report made on April 30, 2010, at 2131 hours Central Daylight Time. "BFN's initial report was categorized as a valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B). The loss of power to RPS 1A resulted in PCIS Groups 2, 3, 6, and 8 primary containment isolations and initiation of Standby Gas Treatment and Control Room Emergency Ventilation. However, plant conditions which require PCIS actuations and system initiations (e.g., low reactor water level, high drywell pressure, abnormal area radiation level, high area temperature) did not exist, therefore, the actuation was invalid. As a consequence, TVA has concluded that this event does not meet the reporting requirements of 10 CFR 50.72. The event is reportable under 10 CFR 50.73(a)(2)(iv)(A). A 60-day phone call will be made in accordance with 10 CFR 50.73(a)(1). [See EN #46054] "TVA's evaluation of this event is documented in the Corrective Action Program (PER 227662). TVA has notified the NRC Resident Inspector." Notified R2DO (Desai). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-04-30
45887 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-04-30 | 2010-04-30 20:38 | 2010-04-30 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The State provided this information via email: "On April 30, 2010, at 1750 hours, the Agency [State] received a report from the licensee stating that a Troxler moisture/density gauge (Model 3430 - Serial # 31489) was missing from a construction site at 6185 Retail Road in Dallas, Texas. The gauge contains an 8 milliCuries Cesium (Cs) - 137 source serial # 750-6245, and a 40 milliCuries Americium - 241/Beryllium (Am\Be) source serial # 47- 5598. "The license reported that the gauge user (worker) had used the gauge earlier in the day and had secured and locked it in their storage trailer at the site around 1300. The worker left the site around 1400 for his lunch break. The worker returned to the site around 1500, and around 1630 he returned to the storage trailer. At that time, he discovered the trailer lock and gauge were missing. The worker informed the Apex Project manager and the company service manager. The worker was instructed to conduct a thorough site search and contact all of their personnel with access to the site to see if they could determine the location of the gauge. After a thorough search and numerous telephone calls to various Apex personnel to make sure the gauge in fact was missing and not inadvertently picked up by another employee, the Corporate Radiation Safety Officer, Apex President, and this Agency was contacted to report the gauge missing. "The licensee speculates that the gauge was stolen. They are not aware of any former employees who left under bad circumstances and would have reason to take the gauge as a prank or as a vehicle for reprisal against them. The licensee has spoken to others at the site and does not believe any one at the site is in possession of the gauge. "The licensee has stated that they are considering a reward for the gauges' return." Texas Incident Report # I-8738 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-05-05
45886 | -1 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2010-04-30 11:31 | 2010-04-30 17:05 | 2010-05-03 | AGREEMENT STATE REPORT - LEAKING SHIPPING CONTAINER IDENTIFIED AFTER SHIPMENT Energy Solutions notified the State of Tennessee about a shipping container that was found leaking radioactively contaminated liquid at their site. The container was part of a shipment of two containers containing radwaste shipped to Energy Solutions from Areva in Lynchburg, VA. After the shipment arrived onsite the containers were stored on a slope in a holding area for about fourteen hours. The State dispatched people to the site who conducted surveys. When the shipping container was opened a bag of freestanding liquid was found near the doors of the container inside. The liquid was surveyed and determined to contain Co-60 and Cs-137. Cs-137 was not manifested on the shipping manifest. The liquid's consistency was described as semi-viscous similar to hydraulic fluid. The State surveyed the area from where the containers came into the site gate to the area where they were stored with floor monitors and did not find radioactive contamination. The trailer and surrounding area were also surveyed with no contamination found. Tennessee contacted Areva - Lynchburg and was told that the shipping container that contained the leaking bag was stored for a long period of time on top of the other shipping container at Lynchburg. Tennessee representatives surveyed the top of the other shipping container but again no radioactive contamination was found. * * * RETRACTION FROM BILLY FREEMAN TO ERIC SIMPSON AT 1354 ON 5/3/10 * * * The State Radiation Health Department, upon consultation with Regional NRC representatives, has determined that this event does not meet the notification requirements of SA-300 and is retracting the event. Notified R1DO (Cook), FSME DEO (McIntosh), NMSS EO (McCartin) and R2DO (Musser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2010-05-05
45885 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-04-01 | 2010-04-30 17:33 | 2010-04-30 | ARKANSAS AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following was received from the State via email: "The Department [State] received notice on April 1, 2010 by telephone and a written report on April 30, 2010, from Shaw Environmental, Inc. of seven (7) missing Tritium (H-3) exit signs. "The signs were purchased and installed in a military recruiting center, located on University Avenue in Little Rock, Arkansas. The recruiting center was located in a mall complex that had been demolished and removed for the construction of a new shopping center. "The signs were installed sometime between March, 2004 and October, 2005. The signs are described as: "Manufacturer: SRB Technologies "Model: BetaLux-E "Activity: 10 Curies each "Serial numbers: 318671-318675 and 318887-318888 (7 signs total)" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2010-05-05
45884 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2010-04-29 13:04 | 2010-04-30 12:34 | 2010-04-30 | HOT OIL SYSTEM EMERGENCY SHUTDOWN FAILS ANNUAL PREVENTATIVE MAINTENANCE CHECK "It was reported to EH&S Management that on April 29, 2010, the annual preventative maintenance functional check on the hot oil system emergency shutdown system failed. This function is an Item Relied On For Safety (IROFS) and is identified in the Integrated Safety Analysis (ISA) Summary for the conversion area of the Columbia Fuel Fabrication Facility. This IROFS designation is ADUHOS-407 and this IROFS is a control applied to a fire related sequence. Information pertaining to the accident sequence can be found in the January 2010, ISA Summary 03 page 78. There were no actual fire incidents; there were no hazardous materials or special nuclear materials released. "Current plant status: This functional test requires the conversion lines and associated hot oil dryer be shut down. The conversion lines which utilize the hot oil system protected by this function were in normal shutdown at the time of the functional check was performed. The Columbia Fuel Fabrication Facility is currently shutdown for performance of the annual inventory and associated maintenance outage. "This notification is made base on 10 CFR 70 Appendix A (b)(2) 'Loss or degradation of items relied on for safety that results in failure to meet the performance requirements of 10 CFR 70.61.' The performance requirements for this accident sequence require the Overall Likelihood Index (OLI) be a -4, which corresponds to Highly Unlikely. With this control failure the sequence OLI is -3 which corresponds to Unlikely. "Corrective Actions: The corresponding conversion lines and associated hot oil dryer systems are currently in a normal shutdown mode, and will remain so until appropriated troubleshooting and repairs are conducted and the IROFS is restored to an operable status." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-05-07
45883 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2010-04-30 03:00 | 2010-04-30 05:26 | 2010-04-30 | LOSS SAFETY PARAMETER DISPLAY SYSTEM (SPDS) DUE TO COMPUTER PROBLEMS "At 0300 [CDT] on 04/30/2010, the Plant Computer Group identified that the SPDS stalled and was not updating data points as required. The SPDS also supplies data to several Emergency Response Data System (ERDS) points. Redundant, normal control room indications are still available to the operators. This is considered a Loss of Emergency Assessment Capability and therefore, reportable under 10CFR50.72(b)(3)(xiii). "SPDS was restored at 0356 [CDT] on 4/30/2010. "The licensee has notified the NRC Resident Inspector." | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-30
45882 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2010-04-29 18:30 | 2010-04-29 20:30 | 2010-04-29 | IDENTIFIED WIRING DISCREPANCY IN "B" EDG "While performing a walkdown of the 'B' emergency diesel generator remote shutdown circuitry, a wiring discrepancy was identified that could have disabled the Appendix R function of the circuitry. The wiring discrepancy could have prevented complete isolation of the 'B' emergency diesel generator breaker closure circuitry from a postulated fire in the Control Building. "This configuration causes the Appendix R function of the 'B' emergency diesel generator to be inoperable. "A roving firewatch has been established and a 7 day action statement has been entered in accordance with the applicable fire protection procedure. Corrective actions are being evaluated to resolve this issue." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-04-29
45881 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-04-29 07:45 | 2010-04-29 16:31 | 2010-04-29 | AGREEMENT STATE REPORT - SHUTTER ON GAUGES FAILS TO FUNCTION The following was received via email: "While doing the shutter checks it was discovered that the shutters were inoperable on the following fixed gauges: "Serial #1015GK, Cs-137, 50 mCi, Source holder SR-A, at the Pump House North Train; "Serial #1017GK, Cs-137, 50 mCi, Source holder SR-A, at the Pump House Center Train. "Density gauges are installed on the piping going to the tails impoundment. The pipes are in the pump house and are not readily accessible. [An] Ohmart representative will be there on 5/5/10 for the necessary repairs. "All personnel have been briefed about the safety implications. The area has been cordoned off. No concerns of exposure to anyone. This is an ongoing investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-05-04
45880 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-04-29 08:30 | 2010-04-29 08:31 | 2010-04-29 | PLANT INTEGRATED COMPUTER SYSTEM OUTAGE DUE TO SCHEDULED MAINTENANCE "Beginning at approximately 0830 hours EDT on April 29, 2010, Perry Plant personnel will be taking the plant Integrated Computer System (ICS) out of service for planned maintenance. During the time ICS is out of service, the Safety Parameter Display System (SPDS), the Emergency Response Data System (ERDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. The computer outage is scheduled for six hours. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Private Branch Exchange, Off-Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. A follow-up notification will be made when the maintenance activities are completed and the equipment is restored." The NRC Resident Inspector has been notified. * * * UPDATE AT 1036 EDT ON 04/29/10 FROM DOUGLAS SHORTER TO CHARLES TEAL * * * The plant ICS has been returned to service and the system is functioning normally. The NRC Resident Inspector has been notified. Notified R3DO (Hills). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-29
45879 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-04-28 14:00 | 2010-04-28 19:40 | 2010-05-28 | RCIC DECLARED INOPERABLE DUE TO OIL LEAK ON GOVERNOR SYSTEM "On 04/28/10, at 1400 EDT, with the reactor at 100% power, the Reactor Core Isolation Cooling (RCIC) system was declared inoperable by the Shift Manager (SM) due to an oil leak on the RCIC governor control oil system that could have impacted the system performance during the accredited 24 hour mission time. The fitting where the oil leakage was observed was tightened and the machine was placed in service with no leakage identified. Currently the system is operable and in its normal standby lineup. The system was available for use during this time. At no time was there an impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM JOHN WHALLEY TO HOWIE CROUCH @ 1300 EDT ON 5/28/10 * * * "On April 28, 2010, at 1940 hours, Pilgrim Nuclear Power Station (PNPS) made an 8-hour non-emergency 50.72 notification, Event Notification EN# 45879. The notification was made in accordance with 50.72 (b)(3)(v)(D), Accident Mitigation. Earlier on April 28, 2010, at 1400 hours, a minor oil leak had been identified on the Reactor Core Isolation Cooling (RCIC) system at a lubricating oil vent fitting. The leak was immediately repaired by properly tightening the fitting, then running RCIC to verify no active leak existed. However in the interim, the Shift Manager conservatively declared RCIC inoperable when the high standard for operability could not be assured by initial system engineering judgment for the impact of the oil leak on RCIC system performance in consideration of mission time. "Subsequent engineering evaluation concluded that the observed leak, conservatively assumed to be one drop per 3 minutes, would not have impacted RCIC operability for the duration of its required 24 hour mission time. All relevant technical information is documented in the PNPS corrective action system. "Therefore PNPS is retracting the event notification EN# 45879. The USNRC Resident Inspector Office has been notified of this retraction." Notified R1DO (Dwyer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-04-28
45878 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2010-03-05 05:39 | 2010-04-28 14:32 | 2010-04-28 | INVALID ISOLATION SIGNAL CAUSED MSIV'S TO CLOSE "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "On March 5, 2010, at 0539 hours, during the Unit 1 refueling outage (L1R13), the inboard and outboard Main Steam Isolation Valves (MSIVs) closed as a result of an invalid partial Group 1 PCIS (Primary Containment Isolation System) isolation signal generated during the performance of station surveillance LOS-TG-SR2 'Operability of Main Turbine Valves and Controls Following an Extended Outage.' "Investigation revealed that during the resetting of the main turbine, the Group 1 PCIS logic received a signal that one of the Turbine Stop Valves (TSVs) was open. This caused the logic for Group 1 PCIS logic to be made up and the MSIVs to shut. Review of the data indicates that at no time did any of the TSVs open during the testing. This issue occurred as a result of the vibration seen by the relays in the trip logic during the resetting of the main turbine. "The apparent cause of this event was attributed to a lack of questioning attitude during testing. The surveillance has multiple actions for cycling all the turbine valves, as well as performing various trips and resets of the main turbine. The surveillance has a prerequisite to ensure during performance of the various sections, that the MSIVs are shut or jumpers are installed to prevent an inadvertent closure of the MSIVs should the TSVs be cycled. The operating crew had concluded that the section of the procedure they were performing did not require the MSIVs to be shut or the jumpers to be installed. "When the turbine was reset, the Reactor Protection System (RPS) Channels A1 and B2 actuated. Based upon these actuations, plant response to the partial Group 1 PCIS isolation signal was as expected. This actuation was invalid since the conditions required to bypass the low condenser vacuum Group 1 PCIS isolation were all met. With the mode switch not in run, the condenser low vacuum bypass keys in bypass and the main stop valves not full open, the Group 1 PCIS isolation is bypassed. These conditions were all met when the partial Group 1 PCIS isolation was received. The TSVs remained closed as indicated on the Digital Electro-Hydraulic Control (DEHC) system. "Corrective actions include enhancements to the surveillance procedure and preparation of a case study on the circumstances, which led to this event. [Corrective actions also include presentation] to all operating crews in LORT [Licensee Operations Requalification Training] Cycle 10-4 and various site training advisory and curriculum review committees." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-04-28
45877 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-04-27 16:37 | 2010-04-27 18:44 | 2010-04-27 | REACTOR TRIP FOLLOWING A GENERATOR LOCKOUT DURING AUTOMATIC VOLTAGE REGULATOR TESTING "On 4/27/2010 at 1637 hours, during recovery from a refueling outage when the main turbines and exciter were replaced, Unit 2 experienced a generator lockout which caused a turbine trip. The turbine trip resulted in a reactor trip when the reactor was at 74% power. The generator lockout occurred while automatic voltage regulator testing was being performed. This event is reportable per 10CFR50.72(b)(2)(iv)(B) due to actuation of the Reactor Protection System. "The Auxiliary Feedwater Pumps (AFW) received an automatic start signal due to low/low level in the steam generators following the reactor trip. Steam Generator inventory was restored to normal operating level. The Steam Driven AFW pump experienced an issue with the lube oil system which resulted in some of the oil leaking onto the floor. An investigation into the oil leakage issue will be performed. The Steam Driven AFW pump was declared inoperable until this investigation is complete. The two motor driven AFW pumps automatically started and operated as designed. This event is reportable per 10CFR50.72(b)(3)(iv)(A) due to actuation of an ESF system. "All control rods inserted into the core following the reactor trip and decay heat is being removed using the normal steam dump system. Several secondary (feedwater) relief valves lifted and resealed during the event. Unit 2 is stable in Mode 3 at normal operating temperature and pressure." Unit 2 is in a normal shutdown electrical lineup and there was no impact on Unit 1. The NRC Resident Inspector has been notified by the licensee. | 0 | 0 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-04-27
45876 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2010-03-15 07:30 | 2010-04-27 12:04 | 2010-04-27 | RADIATION UNDERDOSE AT PRESCRIBED LOCATION The following information below is a summary of a facsimile provided by the State of Louisiana Department of Environmental Quality concerning a reported medical event: "A medical event occurred involving a patient under treatment for adenocarcinoma of the prostate gland. The patient involved received a prostate brachytherapy implant on March 12, 2010, using radioactive iodine-125 seeds [95 seeds of I-125 were implanted at 0.322 mCi/seed]. "The radiation oncologist with the assistance of the urologist inserted the needles through the appropriate holes in the needle template. During the procedure, the radiation oncologist used the ultrasound to guide the needle placement. However, the radiation oncologist and ultrasound technologist had difficulty seeing the balloon location (indicating the prostate base) clearly on the sagittal view of the ultrasound during the dispensing of the seeds from the needles. It was felt that it was possible that the patient may have moved during the procedure which may have caused the balloon and ultimately the base plane to have shifted. "A variance was suspected by the radiation oncologist after reviewing the post implant seed count x-ray. The patient was called to return for an early post-implant CT on March 22, 2010 to confirm the implanted seed locations. Using these images, a treatment plan was constructed using the treatment planning system's post-plan software. Based on this postoperative plan, it has been estimated that the entire implanted volume was shifted approximately 3.0-cm inferiorly, resulting in D90% of 12.88 Gy (dose that covers 90% of the prostate volume outlined on the post implant CT images). The prescription dose was 145.0 Gy. The post-implant planning results were referred to the Radiation Safety Committee (RSC) for review. After review, the RSC decided to interpret the implant as a medical event. This decision was made based on the fact that the V100 (volume of the prostate that received 100% of the prescribed dose) was less than 50% and the event classification was felt to be that of a wrong site. "The information provided to the patient was that a treatment delivery inaccuracy occurred on March 15, 2010. The radiation oncologist explained to the patient that the dose delivered was not as planned and that supplemental treatment is recommended to treat his prostate cancer. A waiting period is recommended to allow the sources to decay and to determine any possible complications." Louisiana Report # LA100003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2010-05-03
45875 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2010-03-23 | 2010-04-26 17:15 | 2011-04-01 | EMD JACKET WATER PUMP WITH INCORRECT IMPELLER ORIENTATION The following is a summary of a report received from Engine Systems, Inc. via facsimile: "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 03/23/10 following a corrective action request from Entergy - Grand Gulf. The request was written as the result of Grand Gulf having an EMD jacket water pump with an incorrect impeller. Specifically, the impeller installed in the pump was for rotation opposite of the pump housing. The evaluation was concluded on 04/26/10 and was determined to be a reportable defect as defined by 10CFR21. "EMD diesel engines utilized for emergency diesel generator sets use two engine jacket water centrifugal pumps (one for each bank) to circulate fluid throughout the engine for cooling. Each pump is mounted on the front of the engine and rotates in the opposite direction of the engine crankshaft. For single engine generator set applications (i.e. left hand rotation engine, viewed from the rear of the engine), the pumps used on each bank contain identical components; the only difference is the position of the impeller housing in relation to the pump shaft housing. When viewed from the front of the engine, these water pumps rotate counterclockwise (see Figure 1 below). "For tandem generator set applications, one engine is left hand rotation and the other is right hand rotation. For each engine, the pumps used on each bank contain identical components and the only difference is the position of the impeller housing in relation to the pump shaft housing. However, for a right hand rotation engine the water pumps rotate clockwise when viewed from the front of the engine In summary, because these pumps use impellers that rotate in both clockwise and counter-clockwise directions, it is possible that an impeller could be installed with a design rotation opposite that required for the associated pump housing. "A review has been performed to evaluate the impact on past supply of EMD water pumps. Historically, ESI has supplied a quantity of over 280 water pumps under 17 different EMD part numbers dating back to 1988. The pump returned by the customer [Grand Gulf] was supplied in January 1997. After reviewing the history of dedication activities performed on the water pumps it was found that dedication reports for EMD water pumps have always contained an inspection requirement to verify the correct operational rotation; however reports written prior to 2000 did not include a clear visual depiction of what the correct operational rotation is. It appears that this was an isolated incident where the inspector made an error when performing the inspection. Since April 2000, all EMD water pumps shipped were inspected to a dedication report that included a clear visual depiction of proper impeller geometry. This one incident is the only known instance of an EMD water pump with the incorrect impeller. "ESI recommends that as a precaution, all customers with an EMD water pump in stock which was supplied by ESI prior to April 2000 should perform a visual inspection to ensure the correct impeller is installed. A pump which has been installed on the diesel engine is considered acceptable based on successful operation of the diesel engine. The impeller inspection is easily performed, without disassembly, by looking into the inlet port of the pump to confirm the orientation of the impeller matches the pump housing. A listing of the various part numbers supplied prior to April 2000 is included in Table [below]. Listing of Water Pump P/Ns Supplied Prior to April 2000 Part Number Rotation Bank Type of Engine 40004235 LH RIGHT 16 & 20-645E4 & E4B 40004234 LH LEFT 16 & 20-645E4 & E4B 8347607 LH LEFT 16 & 20-645E4 & E4B 8364236 RH RIGHT 16 & 20-645E4 & E4B 8364237 RH LEFT 16 & 20-645E4 & E4B 8269664 LH RIGHT 12-645E4 & E4B 9336390 LH LEFT 12-645E4 & E4B 8269638 LH LEFT 12-645E4 & E4B 8324588 RH RIGHT 12-645E4 & E4B 8324589 RH LEFT 12-645E4 & E4B NOTE: The ESI report did not provide an information on specific nuclear power plant licensees that may possess these components. * * * UPDATE RECEIVED VIA FAX FROM TOM HORNER TO DONG PARK AT 1614 EST ON 04/01/11 * * * Two sentences were added to address the safety hazard which is created or could be created by this defect. "Installation of the incorrect impeller would result in considerable loss of engine cooling water flow. This would cause elevated engine cooling water temperature that could impact engine performance and/or load carrying capability with the possibility of eventual engine failure, thereby preventing the emergency diesel generator from performing its safety related function." Notified R1DO (Powell), R2DO (Sykes), R3DO (Peterson), R4DO (Lantz), PART 21 GROUP via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-04-26
45874 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2010-04-26 08:37 | 2010-04-26 11:51 | 2010-05-01 | TECHNICAL SUPPORT CENTER VENTILATION TAKEN OUT OF SERVICE FOR MAINTENANCE "On April 25, 2010, at 1130 EDT, the Control Room Emergency Ventilation system on St. Lucie Unit 1 was declared out of service due to removing both Control Room Booster fans from service in order to support charcoal absorber replacement in the common filtration train as part of scheduled outage maintenance. The Technical Support Center (TSC) ventilation system is part of the Unit 1 Control Room Emergency Ventilation system, therefore, the TSC ventilation system has been rendered non-functional during the course of the work activities. The TSC ventilation is expected to be returned to service on 4/26/10. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Should the TSC become uninhabitable, the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the potential loss of an Emergency Response Facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM FRED POLLACK TO DONG PARK AT 0321 EDT ON 5/1/2010 * * * "Charcoal absorber replacement and post maintenance testing has been completed satisfactorily and the Control Room Emergency Ventilation System, and thus the Technical Support Center Ventilation System, has been declared back in service at 0140 on 05/01/2010. "The NRC Resident Inspector has been notified." Notified R2DO (McCoy). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-26
45873 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2010-04-26 03:00 | 2010-04-26 05:18 | 2010-04-26 | MANUAL SCRAM DUE TO HIGH TURBINE VIBRATIONS "This report is being made under 50.72(b)(2)(iv)(B) for inserting a manual reactor scram due to rising vibrations on the #6 turbine bearing. A planned reactor shutdown was in progress with reactor power at 13.8% when turbine vibrations approached procedural limits which would require a manual scram of the reactor. "The scram was uncomplicated; all control rods fully inserted. The reactor is in Mode 3, Hot Shutdown. Cooldown has been established to the condenser using main steam line drains. The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 14 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-04-26
45872 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2010-04-26 | 2010-04-26 01:35 | 2010-04-26 | UNIT 1 EXPERIENCED AN AUTOMATIC REACTOR TRIP DURING AN NI CALIBRATION "This is a 4 hour Non-Emergency 10CFR 50.72(b)(2)(iv)(B) notification due to an Automatic Reactor Protection System (RPS) actuation (scram). At 2126 hours [CDT] on April 25, 2010, Unit 1 Reactor automatically tripped due to 2 of 4 Reactor Protection System (RPS) Channels tripped. At the time of the trip, reactor power, as indicated by heat balance, was ~20%, while excore Nuclear Instrumentation (NI) indicated ~30%. The RPS high reactor power trip setpoint was 50% power. An NI calibration initiated an automatic withdrawal command to the control rod drive system. The rod withdrawal, resulted in one RPS channel tripping on high reactor power and another RPS channel tripping on high reactor coolant system pressure. All control rods fully inserted into the core and no safety systems, other than RPS, actuated. Emergency feedwater did not actuate and was not needed. No primary safety valves lifted. Seven secondary safety valves lifted and subsequently reseated. The plant is currently stable in Mode 3. "The NRC resident has been notified." The licensee also informed the State of Arkansas and does not plan a press release. The Unit 1 reactor trip was uncomplicated. Current means of decay heat removal is normal feedwater to the Steam Generators with steam discharge to the Main Condenser through Main Steam Bypass. The Main Generator was online at the time of the trip and the plant is currently in a normal post trip electrical line up. There is no indication of primary-secondary tube leakage. All systems functioned as required. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-04-26
45871 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-04-25 18:05 | 2010-04-25 21:49 | 2010-04-25 | ONE ALARM SIREN INITIATED SPURIOUSLY "At 1805 on 4/25/2010, Surry Power Station (SPS) Operations department began receiving reports from individuals in Surry County that at least one Early Warning System (EWS) siren was sounding. A subsequent review has confirmed that, at a minimum, Siren # 18 spuriously sounded six times over a period of approximately 20 minutes. Station personnel contacted the Virginia State Emergency Operations Center (EOC), in addition to Surry County dispatch for confirmation. Surry County dispatch reported that a number of calls were received for a sounding EWS siren. Neither the Virginia State EOC nor SPS Security received an alarm indicating that the siren was spuriously sounding. The Virginia State EOC has notified its Public Information Officer of the spuriously sounding siren. All plant conditions/parameters are normal, and-no releases to the environment have occurred. "The site NRC Resident Inspector has been notified". The emergency siren was on for approximately three hours before being locally disabled. There is still 100% coverage in the areas requiring siren notification. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-25
45870 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2010-04-19 11:00 | 2010-04-23 09:51 | 2010-04-23 | AGREEMENT STATE REPORT - POSSIBLE LOSS OF CONTROL/DAMAGE TO PORTABLE GAUGE The following report was received from the State via e-mail: "At approximately 11 a.m. [EDT] on Monday, April 19, 2010, one of KeyTech's portable moisture density gauges (Troxler Model 4640B, Serial No. 2008, containing 9 mCi of Cs-137 and 44 mCi of Am-241) was struck by a steam-roller. The incident occurred at the intersection of Manchester Boulevard and Manchester Road in Manchester, NJ. On Wednesday, April 21, 2010, the licensee filed a report with the Manchester Police. The Manchester Police then contacted the Trenton Dispatch. At about 11 a.m., RMP [New Jersey Dept. of Environmental Protection Radioactive Materials Program] personnel were notified by Trenton Dispatch. "The RMP contacted Manchester Police and it was learned that KeyTech reported that while the gauge was damaged the radioactive material remained intact within the device. KeyTech's RSO [Radiation Safety Officer] and administrator were contacted. The RSO stated that only the keyboard portion of the gauge was hit and that there was no damage to the radioactive material within the gauge. When the gauge was hit, the source rod was extended. The technician was able to retract the source rod into the safe position. The gauge was moved to a safe location and away from the public. RMP personnel went to KeyTech on Thursday, 4/22/10, to speak with the licensee and to conduct an investigation. The investigation concluded that the material was intact within the gauge and determined the licensee took appropriate actions to protect personnel and the public." New Jersey Report #C348104 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2010-04-28
45869 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2010-04-23 08:07 | 2010-04-23 10:29 | 2010-04-23 | FATALITY OF LICENSEE EMPLOYEE "An FPLE Seabrook employee experienced a medical emergency on site and was transported offsite for care. Subsequent notification was received from the hospital that the employee had passed away. "OSHA [Occupational Safety and Health Administration] was notified at 0848 [EDT] on 4/23/2010, under 29 CFR 1904, of the fatality of an employee caused by an apparent heart attack while at work." The employee was entering into the Protected Area when she experienced the medical emergency, and as such the employee was not radiologically contaminated when transported offsite. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-23
45868 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2010-04-22 10:01 | 2010-04-22 15:57 | 2010-04-22 | FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2010-04-22
45867 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-19 05:03 | 2010-04-22 15:17 | 2010-04-22 | RPS AND AFW ACTUATION SIGNALS WHILE SHUTDOWN IN MODE 4 "Unit 2 was in Hot Shutdown [Mode 4] for a Refueling Outage. At 0503 [CDT] on April 19, 2010, a valid Lo-Lo Steam Generator level condition occurred during restoration of feedwater system testing. The feedwater test was a planned activity and included isolation of feedwater to the steam generators. During performance of the test, steam generator levels decreased and the Lo-Lo level setpoint was reached on the 2D steam generator. This generated a reactor trip signal and auxiliary feedwater system start signal. Since the Unit was in Hot Shutdown, the reactor trip breakers were already open, and the auxiliary feedwater system was already removed from service when the steam generator water level unintentionally reached the Lo-Lo level setpoint. Additionally, the open steam generator blowdown isolation valves closed as expected at the Lo-Lo steam generator level setpoint. Steam generator level was promptly restored above the Lo-Lo steam generator setpoint. There was no impact on the reactor cooldown that was concurrently in progress as part of the preparation for refueling. Initial screening of the condition determined as not reportable in accordance with 10 CFR 50.72(b)(3)(iv), however, based upon further review it has been determined the condition is reportable." At the time of the event, both trains of shutdown cooling were in service and there were no challenges to offsite power. The licensee was not required to enter any Technical Specification LCO action statements as a result of the event, and the licensee is still investigating the cause of the decrease in steam generator level below the Lo-Lo level setpoint. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-04-22
45866 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-04-22 10:51 | 2010-04-22 13:20 | 2010-04-22 | REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL DURING FEEDWATER INTEGRATED CONTROL SYSTEM TESTING "At 10:51 on 4/22/10, Susquehanna Unit 1 experienced an automatic reactor SCRAM on reactor low level, +13", during the initial testing of the Feedwater Integrated Control System. Following the SCRAM, reactor water level dropped to approx. -30", and the Reactor Core Isolation Cooling system initiated and injected into the vessel. Level was recovered by the Feedwater System and the RCIC system. Division 2 Alternate Rod Insertion unexpectedly initiated during the level transient. Due to scheduled maintenance activities, the 11B Aux Bus did not transfer to the off site power supply post SCRAM. The 11B Aux bus was restored at 12:17. There were no ECCS initiations and no challenges to containment. "This event is a Reactor Protection System (RPS) actuation when the reactor is critical, and is reportable as a four hour ENS Notification under 10 CFR 50.72(b)(2)(iv)(B). This event is also an unplanned actuation of a system used to mitigate the consequences of a significant event and is reportable as an eight hour ENS notification under 10CFR50.72(b)(3)(iv)(A)." The scram was described as uncomplicated. All rods fully inserted and all systems functioned as required. The initiation of the alternative rod insertion should not occur unless level drops below -38" but the initiation did not result in any complications. The offsite supply breaker to Aux bus 11B was under maintenance when the scram occurred and so the loss of power was expected. This bus supplies some balance of plant loads which were lost (recirculation pump, condensate pump, and circulating water pump) but the loss of these components had no impact on the transient. The NRC Resident Inspector has been notified. The licensee will notify State authorities and also plans a press release. | 0 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-04-22
45865 | 0 | HALLIBURTON |  |  |  |  | 2010-04-20 20:00 | 2010-04-21 16:36 | 2010-04-21 | ANTICIPATED LOSS OF RADIOACTIVE MATERIAL The licensee reported that two cementing densometers were aboard the Deep Water Horizon Oil Rig when the oil rig caught fire on the evening of April 20, 2010. The oil rig is located in Federal waters in the Gulf of Mexico (Mississippi Canyon Block 252). At the time of the report, the oil rig was sinking in 4000 feet of water. The two gauges on the oil rig were as follows: 1. Device 10SD, Device S/N: V32785, Source S/N: DA071, Isotope Products Model No. A-3906, Isotope: Cs-137, Current Activity: 8.3 mCi 2. Device 10SD, Device S/N: W25980, Source S/N: XA923, Gammatron Model No. GTGHP, Isotope: Cs-137, Current Activity: 8.2 mCi When brought onto the oil rig, both devices were high integrity sources inside a tungsten cavity, and further contained in steel. The licensee had no information whether or not the sources were compromised as a result of oil rig fire and sinking. Based on the depth of the water where the oil rig is sinking, the licensee does not anticipate that the devices will be recoverable. The licensee notified the Region IV office of the incident. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore, it is being categorized as a less than Category 3 source Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-04-21
45864 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-04-20 | 2010-04-21 12:00 | 2010-07-08 | AGREEMENT STATE REPORT - POSSIBLE OVEREXPOSURE TO A MEMBER OF THE PUBLIC "Ohio Department of Health (ODH), Bureau of Radiation Protection (BPR) was notified of a possible overexposures to a member of the general public which occurred on 4/20/10 at the Ohio State University located in Columbus, Ohio. "A patient received a temporary implant of Cs-137 and Ir-192 seeds on April 16-18, 2010. The patient's visitor (her fiancÚ) was instructed by the licensee that he could stay no longer than 2 hours with the patient in a twenty four hour period, and must stay behind the bedside shield during these visitations. On Tuesday, April 20, 2010, the licensee was informed by the Assistant Nurse Manager that the fiancÚ spent the night in the patient's room on two consecutive nights. In addition, the initial investigation by the licensee indicates that the visitor told the Assistant Nurse Manager that he slept in the same bed with the patient both nights. Nursing Management personnel are in the process of interviewing staff members that were involved directly with the care of the implant patient to verify that the fiancÚ was in the room overnight with the patient. "A preliminary and conservative worst case dose estimate for the visitor is 6 Rad (6 cGy) whole body exposure, based on a 16-hour stay time (8 hours each night for two nights). ODH BRP will continue to collect information of this event and conduct an investigation. The licensee has initiated an internal investigation." Ohio Report OH100005 * * * UPDATE FROM STEPHEN JAMES TO CHARLES TEAL ON 7/8/10 AT 1128 EDT * * * "After investigation by the licensee and ODH the revised calculations indicate a dose estimate to the visitor to be 1.25 Rem. The licensee has instituted major procedural changes and conducted training for medical staff involved with brachytherapy treatments." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-04-26
45863 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-04-20 | 2010-04-21 12:38 | 2010-04-21 | AGREEMENT STATE - STUCK SHUTTER "On April 21, 2010, the agency [Texas Department of Health] was notified by the licensee that while performing a scheduled shutter operation check, the shutter on a Ronan model SA1 nuclear gauge failed to close. The gauge contains five millicuries of Cesium (Cs) 137, and was installed in 1995. The gauge is in its normal operating position and a radiation survey conducted by the licensee indicated that radiation levels are normal. The gauge was leak tested and the test sent for analysis. The licensee stated that there is no risk of additional exposure to their workers. The licensee is working with the manufacturer to schedule the repair of the gauge during a shutdown starting on May 3, 2010." Texas Incident #: I-8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-04-26
45862 | 0 | WATERFORD STEAM ELECTRIC STATION |  |  |  |  | 2010-04-21 | 2010-04-21 10:35 | 2010-04-21 | HIGH FAILURE RATE OF NORMALLY ENERGIZED ELECTRO-PNEUMATIC TIME DELAY RELAYS The following was received via facsimile: "Waterford 3 has observed a higher than expected failure rate of normally energized Tyco model E7024PB electro-pneumatic time delay relays produced since 2007. Seven of the eight failures were observed on 2007 or newer date code relays and one was observed on a 2004 date code relay. Waterford 3 had 33 Tyco model E7024PB time delay relays installed in the plant. The Agastat E7000 series timing relay consists of two basic operating types, On-Delay and Off-Delay. The On-Delay models provide a delay period of contact re-positioning on energization and no time delay upon de-energization. The Off-Delay models provide a delay period of contact re-positioning on de-energization and no time delay upon energization. These relays may be ordered with various electrical characteristics suitable for use specific to each application. The early-in-life failures have been observed on Tyco model E7024PB relays designed as an Off-Delay, 4 pole double throw, 125 VDC operating coil, with a time delay range of 0.5 to 5 seconds. "All failed relays were replaced. Post failure bench testing at Waterford 3, Tyco, or independent Failure Analysis has not consistently repeated the failures." See EN #44684 for Part 21 reported by Tyco Electronics. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-04-21
45861 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-04-21 07:45 | 2010-04-21 08:46 | 2010-04-21 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM THAT COULD ALLOW POSSIBLE UNAUTHORIZED ACCESS TO SAFEGUARDS MATERIAL Discovered a vulnerability in a safeguard system that could allow access unauthorized or undetected access to safeguards material in the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-04-21
45860 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-04-20 11:03 | 2010-04-20 18:39 | 2010-04-20 | OFFSITE NOTIFICATION - SODIUM HYDROXIDE RELEASED INTO BERM "At about 0755 (PDT) on April 20, 2010, approximately 200 gallons of sodium hydroxide (caustic) was released into the SONGS Caustic Skid Berm. The release was fully contained within the bermed area and there was no release to the environment. The release is believed to have occurred from a Unit 2 caustic pump pressure safety valve (PSV) during the performance of condensate polishing demineralizer regeneration. The release has been secured and SONGS personnel have pumped the caustic to poly drums. "Between 1103 and 1125 (PDT) SONGS notified the San Diego Department of Environmental Health (DEH), the State of California Emergency Management Agency (CalEMA), and the National Response Center of the contained non-radioactive caustic spill within the protected area of the facility. Therefore, Southern California Edison is reporting this occurrence to the Nuclear Regulatory Commission in accordance with 10 CFR 50.72(b)(2)(xi). "SONGS Unit 2 is in Mode 1 at approximately 98% power and Unit 3 is in Mode 1 at approximately 50% power. The NRC Resident Inspector will be notified of this occurrence and will be provided a copy of this report. "Additional information regarding this event will be provided to one of the Resident Inspectors at the site." | 0 | 98 | 50 | 0 | 98 | 50 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-20
45859 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-04-20 13:07 | 2010-04-20 15:55 | 2010-04-20 | FIVE POTENTIAL ISSUES DISCOVERED DURING POST-FIRE SAFE SHUTDOWN REVIEW "While performing a post-fire safe shutdown (PFSSD) review per Enforcement Guidance Memorandum (EGM) 09-002, 'Enforcement Discretion for Fire Induced Circuit Faults', and Regulatory Guide (RG) 1.189, Revision 2, five issues were identified that could be potentially reportable. EGM 09-002 provides enforcement discretion for non-compliances related to fire-induced multiple spurious operations (MSOs). The enforcement discretion period allows 6 months from the date of issuance of RG 1.189, Rev. 2 to perform the following: - Identify noncompliances related to multiple fire induced circuit failures - Implement compensatory measures for the noncompliances, and - Place the noncompliances in the licensees' corrective action program "The five fire-induced issues that were identified are: - Three issues which could potentially prevent operation of the Residual Heat Removal Pump(s), - An issue where all four Reactor Coolant Pumps may not stop from the Control Room, and - An issue where a Centrifugal Charging Pump could spuriously start and fill the pressurizer solid. "RG 1.189 was issued on November 2, 2009. Therefore, the 6-month identification period ends on May 2, 2010. For issues identified during the 6-month identification period, enforcement discretion continues for an additional 30 months to resolve identified issues. "The 10 CFR 50, Appendix R Fire is not a Design Basis Accident. While Appendix R fires are postulated to cause a Technical Specification (TS) inoperability of a [System, Structure or Component] SSC, the failure to previously identify these issues does not constitute an actual TS inoperability. Rather, the issues identified during this MSO are noncompliances with the Current Licensing Basis (CLB). Therefore, the affected systems are considered operable but degraded or non-conforming as defined in Regulatory Issue Summary (RIS) 2005-20." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-04-20
45858 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-04-19 | 2010-04-20 15:06 | 2010-04-20 | TEXAS AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTERS STUCK OPEN The following information was obtained from the State of Texas via email: "On April 20, 2010, the Agency [Texas Department of Health] was notified by the licensee that on April 19, 2010, while conducting calibrations on two continuous density measurement detectors, the associated nuclear gauge shutters were found to be stuck in the open position. Open is the normal position for these gauges. The gauges are Ohmart gauges containing 100 millicuries each of Cesium-137 (original activity). The gauges are model SR-A serial numbers 7613 GK and 8150 GK. The Radiation Safety Officer (RSO) has placed notification tags on the gauges to warn workers of the problem. The manufacturer has been contacted to provide repairs to the gauges." Texas Incident # I-8732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-04-23
45857 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-04-19 | 2010-04-19 17:33 | 2010-04-19 | AGREEMENT STATE REPORT - LOST BRACHYTHERAPY SEEDS The following information was received from the State of Florida Bureau of Radiation Control via facsimile: "Licensee discovered 51 I-125 brachytherapy seeds missing on 13 April 2010. Initial notification to the state was on 16 April 2010, after working hours, to the [State of Florida] duty officer. A search of the premises and outside garbage containers was performed [with negative results]. The search is still on going. Investigation [of this incident has been] assigned to [the State of Florida Bureau of Radiation Control] Miami Office." Florida Incident #: FL10-056 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-04-22
45856 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-04-19 01:58 | 2010-04-19 06:20 | 2010-04-19 | TSC EMERGENCY VENTILATION SYSTEM DISCOVERED NON-FUNCTIONAL WHILE PLACING A CLEARANCE "At 0158 [CDT] on 4/19/2010, during implementation of clearance order activities, it was identified that the Technical Support Center (TSC) ventilation system would not transition to the emergency mode of operation. This condition is reportable under 10CFR50.72(b)(3)(xiii). "The TSC ventilation system consists of normal ventilation equipment, including a normal air supply unit OAF-1, and an emergency air supply unit OAF-2 which provides conditioned air with HEPA and charcoal filtration. The system is placed in the emergency mode as follows: "When TSC HEPA FILTER BYPASS switch is placed to EMER UP, the Energy Management System (EMS) receives an emergency signal and the following actions occur: 1. Air Dampers AD1443 and AD1445 close and cause OAF-1 to stop. 2. Air Dampers AD1442 and AD1444 open and cause OAF-2 to start. 3. Outside air to the TSC is routed through HEPA filter unit. "During the clearance order activities, the TSC HEPA FILTER BYPASS switch was placed to EMER UP, but the actions above did not occur. A second attempt was made to place the system in the emergency mode, without success. Based upon these indications, it is considered that the TSC ventilation cannot be placed in the emergency mode. This is reportable under 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability due to the loss of the emergency response facility. Per Emergency Plan Implementing Procedure 5.7.7 for Activation of TSC, personnel can relocate to the Alternate TSC (control room) and Alternate Operations Support Center (OSC) where the TSC functions will be performed. Both of these alternate facilities are equipped with emergency ventilation systems and are currently fully functional. "Troubleshooting of the TSC ventilation system discrepancy will commence today." This system was last tested successfully on 10/20/2008 and due for retest on 6/21/2010. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-19
45855 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-04-18 22:25 | 2010-04-19 03:12 | 2010-04-22 | LCO 3.0.3 ENTRY AND LOSS OF SAFETY FUNCTION DUE TO LOSS OF TURBINE BUILDING HIGH ENERGY LINE BREAK COMPENSATORY MEASURE "At 2225 CDT on 4/18/2010, Operations discovered that the Unit 1 Turbine Building Truck Aisle Rollup Door Security Fence was closed. This fence was to be maintained open as the truck aisle is a required drainage path from the Unit 1 Turbine Building to outside in the event of flooding resulting from a High Energy Line Break (HELB). With the expanded metal mesh door [fence] closed, turbine building debris could clog the drainage path and result in a higher than calculated water level being reached for this event. As the final water level cannot be predicted, this represented an unanalyzed condition. The higher water levels would be reached at least one hour after the postulated turbine building HELB event. High water levels could result in a Loss of Safety Function for Unit 1 Emergency Diesel Generators. Auxiliary Feedwater (both units) and DC Electrical Power (both units) if water levels exceed critical heights in the associated rooms. "The doors [fence] were reopened at 2227 CDT. Unit 1 entered LCO 3.0.3 for this two minute period. With the doors [fence] opened, Unit 1 and 2 LCO conditions were again satisfied. "The Unit 2 truck aisle was in the assumed condition, and Unit 2 is in Mode 5 so loss of AFW or DC power would not result in an LCO 3.0.3 entry. Unit 2 Emergency Diesel Generators are not affected as the Unit 2 truck aisle drain path would prevent water levels from reaching critical heights. "The initial investigation determined that a Security Officer had closed the gate at approximately 1855 CDT on 4/18/2010. "The NRC Resident Inspector has been notified. A press release is not planned." * * * RETRACTION AT 1454 ON 4/22/2010 FROM DARRELL LAPCINSKI TO MARK ABRAMOVITZ * * * "In reference to the 4/18/2010 discovery of the security fences (screen door) closed on the Unit One Turbine Building truck aisle door and the Tech Spec LCO 3.0.3 entry on Unit One, further analysis of HELB flooding scenarios in the plant configuration known to be in effect at that time has shown that the LCO 3.0.3 entry was not warranted. Engineering analysis demonstrates that water levels in the Unit One Turbine Building from a postulated worst case HELB flooding event would only have rendered the 12 Motor Driven Auxiliary Feedwater Pump inoperable. Thus TS LCO 3.7.5 Condition B would have been the only LCO action statement required to be entered. No loss of safety function existed." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Skokowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2010-04-19
45854 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2010-04-18 13:57 | 2010-04-18 18:04 | 2010-04-18 | MANUAL REACTOR TRIP DURING REACTOR STARTUP "This is a 4-hour Non-Emergency, 10CFR 50.72(b)(2)(iv)(B) notification due to an RPS actuation (scram). Arkansas Nuclear One Unit 1 was manually tripped from 11% power at 1357 hrs. CDT. The cause of the trip was operator judgment due to a small fire reported in the high pressure turbine enclosure at governor valve number 3 by a fire watch stationed at that location and an unrelated failure of P-32C Reactor Coolant Pump 3rd stage seal (upper seal) occurring earlier that afternoon. No additional equipment issues were noted. An extinguishing agent (CO2) was applied within approximately 30 seconds. All control rods fully inserted. No primary safeties lifted. No secondary safeties lifted. Emergency feedwater did not actuate and was not needed. No safety systems actuated. The plant will be cooled down to repair the P-32C Reactor Coolant Pump Seal. "The NRC Resident has been notified." There was no effect on Unit 2. The grid is stable with Unit 1 in a normal shutdown electrical lineup. Decay heat is being removed via the steam dumps to condenser using normal feed to the steam generators. The licensee will be notifying the Arkansas Department of Health. | 0 | 0 | 0 | 11 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-04-18
45853 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-04-18 13:00 | 2010-04-18 16:57 | 2010-04-18 | OFFSITE NOTIFICATION DUE TO LOSS OF CONDENSER TUBE CLEANING (AMERTAP) BALLS "During the auto shutdown process of TP 1539, Amertap Ball Check, an equipment malfunction occurred when the ball catching flap did not auto reposition to the 'catch' position. This resulted in a loss of amertap balls to the external circulating water system. The quantity of balls lost to the environment is unknown but could potentially be the entire quantity of 1500 balls. "The Xcel Energy Environmental Service informed the plant that a report will be made to the Minnesota Pollution Control Agency during business hours on 4/19/2010. "The NRC Resident Inspector has been informed. "A news release is not planned." The Amertap system is out of service until repaired. The licensee will also be notifying the Prairie Island Indian Nation and Goodhue County, MN of this incident. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-18
45852 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-04-18 07:50 | 2010-04-18 09:30 | 2010-04-18 | OFFSITE NOTIFICATION DUE TO FATALITY DURING MEDICAL TRANSPORT "On 4/18/10, Salem management was notified that a contract employee working 1R20 (Salem Unit 1 outage) was complaining of respiratory issues. Site protection was contacted at about 0700 hours and they immediately responded to the control point area where the employee was resting. The employee was evaluated by site protection and immediately sent via ambulance to Salem County hospital (0721 hours). While enroute to the hospital the contract employee died in the ambulance (0750 hours). "There were no other injuries associated with this event. "There were no affects on plant systems or safety features as a result of this event. "A notification has been made to the NRC Resident Inspector in accordance with 11.8.2.a." The contract employee was not working in a radiological control area (RCA) at the time and there was no personnel contamination associated with this incident. The licensee will inform local agencies (Lower Alloways Creek Township) and the states of New Jersey and Delaware including the New Jersey State Police. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-18
45851 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-04-16 22:37 | 2010-04-17 02:19 | 2010-04-17 | REACTOR TRIP DUE TO TURBINE TRIP "During a normal reactor shutdown for a refueling outage on Unit 2, a reactor trip occurred at approximately 13% power. This reactor trip was the result of a turbine trip due to high differential pressure between A & B condensers (greater than 2.5 inches). The cause for the vacuum difference between condensers is unknown at this time. "The reactor trip first actuated indication was a high flux rate trip and the turbine trip first out indication was not received. The reason for this difference is unknown at this time. "The operating crew responded to the reactor trip utilizing emergency operating procedures for reactor trip and reactor trip recovery and transitioned into normal shutdown procedures. "All rods inserted as expected and all other systems operated as expected." The licensee notified the NRC Resident Inspector. According to the licensee: The plant is in a normal post-trip electrical lineup. No automatic relief valve operations occurred. The motor driven auxiliary feed pump was manually started. The main steam isolation valves are open and decay heat is being removed by steam through the turbine bypass valves to the main condenser. | 0 | 0 | 0 | 0 | 13 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-04-17
45850 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-04-16 19:17 | 2010-04-17 01:29 | 2010-04-17 | LOSS OF COOLING ACCIDENT SIGNAL DUE TO HIGH DRYWELL PRESSURE SIGNAL "On April 16, 2010 at 1917 hrs., Unit 1 received an ECCS [emergency core cooling system] loss of cooling accident (LOCA) signal on high drywell pressure. Based on plant data, drywell pressure reached a maximum pressure of approximately 1.25 psig, which is below the LOCA and RPS [reactor protection system] signal actuation pressure of 1.85 psig. At this time, the cause of the drywell pressure increase is under investigation. RPS logic did not initiate due to drywell pressure not reaching the actuation setpoint of 1.85 psig. Although the ECCS logic prematurely actuated, the signal is being treated as 'valid' for the ECCS actuation until further investigation is completed. All expected ECCS actions occurred as a result of the signal. The LOCA logic has been reset and all affected systems have been returned to normal or standby configuration. "As a result of the LOCA system actuations, several cooling tower fans tripped and condenser vacuum began to decrease. Reactor power was reduced to approximately 86 percent as a result of decreasing condenser vacuum. Power is being maintained at approximately 86 - 88 percent at this time. There are no other plant issues or concerns at this time." The licensee notified the NRC Resident Inspector. According to the licensee, normal drywell operating pressure is .5 to 1.2 psig. Prior to the event, drywell pressure had been steady at approximately 1.0 psig. Current drywell pressure is .6 psig. According to the licensee, ECCS systems that started (but did not inject) included: Core Spray pumps, Residual Heat Removal pumps, High Pressure Coolant Injection pump, and the Diesel Generators. An event review team is assessing this event to determine the root cause. * * * RETRACTION FROM GRIFFIS TO KLCO ON 4/17/2010 AT 1719 EDT* * * "On April 16, 2010, Hatch Unit 1 received a LOCA ECCS initiation from a high drywell pressure signal. Based on the information available at that time, a notification was made to the NRC assuming the signal to be valid until further investigation could be completed. "After further review, the determination has been made that the initiation signal originated from a faulted ATTS [Analog Transmitter Trip System] card and not from a valid high drywell pressure condition. Based on this information, this condition did not require an NRC notification in accordance with 10CFR50.72 and, as such, is being retracted through this updated response." The licensee notified the NRC Resident Inspector. Notified the R2DO (Hopper) | 86 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-04-17
45849 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-04-16 20:30 | 2010-04-16 23:35 | 2010-04-17 | TECHNICAL SUPPORT CENTER INOPERABLE DUE TO HVAC FAILURE "At 2030 CDT [on 4/16/10], the Technical Support Center ventilation system was found not running. The cause for the failure of the Technical Support Center ventilation system is not known at this time. This condition renders the Technical Support Center unavailable for emergency planning responses. Alternate facilities are available. This condition is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for Loss of Emergency Preparedness Capabilities." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVID SPARGO TO HOWIE CROUCH @ 1321 EDT ON 4/17/10 * * * "As of April 17, 2010 at 12:00 CDT, the Technical Support Center is once again available for Emergency Planning Responses. The cause of the failure was a broken belt on the TSC Air Handling Unit. This belt has been replaced." The licensee notified the NRC Resident Inspector. Notified R4DO (Spitzberg). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-16
45848 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-04-16 16:41 | 2010-04-16 22:08 | 2010-04-16 | UNPLANNED EMERGENCY DIESEL GENERATOR START DUE TO LOSS OF A 4160 V BUS "At 1641 hours [EDT] on April 16, 2010, an [unplanned] automatic start signal was generated for the 1C Emergency Diesel Generator (EDG). Surveillance testing was being performed on the 1C 4160 volt bus to verify the ability to swap between the 13 and 14 Station Power Transformers (SPT) which are the offsite power in-feeds for the 1C 4160 volt bus. The [failure to] swap from the 13 SPT to 14 SPT resulted in a loss of power to the 1C 4160 volt vital bus generating the automatic start signal for the 1C EDG. The 1C EDG started but the output breaker did not close. Abnormal operating procedure S1.OP-AB.4KV-0003 was entered for loss of the 1C 4160 volt vital bus. Salem Unit 1 was in Mode 6 with core reload (fuel movement) in progress. Fuel movement was stopped as a result of the loss of the 1C 4160 volt bus. All fuel assemblies were placed in a safe position. There was no impact to shutdown cooling and no loss of spent fuel pool cooling. Core reload has been suspended until power is restored to the 1C 4160 volt bus. Initial investigations determined the suspected cause to be a failed auxiliary contact associated with a SPT in-feed breaker. This prevented the opposite in-feed and EDG breaker from closing. Extent of condition review and repairs are in progress." Fuel movement was suspended due to loss of the fuel handling building exhaust fan which is powered by the 1C 4160V bus. There was no further impact on any safety related equipment required in Mode 6. The license will notify the NRC Resident Inspector, Lower Alloways Creek Township, the State of New Jersey, and the State of Delaware. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-04-16
45847 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-16 16:49 | 2010-04-16 17:07 | 2010-04-16 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF DIESEL FUEL OIL IN A MONITORING WELL "At 1649 [EDT], on April 16, 2010, Salem Unit 2 notified the New Jersey Department of Environmental Protection [NJDEP] via the NJDEP hotline of the discovery of fuel oil from a sample well. At 1645 [EDT], a sample was pulled from a monitoring well on the north east side of the Unit 2 Auxiliary Building which contained approximately 1 pint of diesel fuel oil. This notification to the State of New Jersey is reportable in accordance with 10 CFR 50.72(b)(2)(xi)." The source of the diesel fuel oil is under investigation by the licensee. The licensee notified the NRC Resident Inspector and will notify the State of Delaware. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-16
45846 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2010-04-13 | 2010-04-16 17:02 | 2010-04-16 | AGREEMENT STATE REPORT - UNCONTROLLED CONTAMINATION EVENT On April 13, 2010, a student at the Georgia Institute of Technology (the licensee), under the supervision of an authorized user, was conducting an electroplating experiment, using Ni-63, under a fume hood in one of the licensee's RAM (Radioactive Material) rooms. During the experiment, the student noticed fumes outside the hood and ceased the experiment. She took a swipe outside the hood and found no contamination. On April 14, the licensee's Radiation Safety Officer took swipes of the room and found 22,000 DPM of contamination on the fume hood lip, 11,000 DPM on the RAM room floor, 1,200 DPM on a public hallway floor outside the RAM room, and contamination in an adjacent RAM room. All areas have been cordoned off to control access and cleanup is in progress. It is unknown whether the student had any uptake, was overexposed, or was contaminated during the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2010-04-21
45845 | 0 | MONTANA DEPARTMENT OF TRANSPORTATIO |  |  |  |  | 2010-04-15 14:10 | 2010-04-16 13:21 | 2010-04-16 | DAMAGED TROXLER MOISTURE DENSITY At 1410 MST on 4/15/10, a gauge operator was conducting a density reading near a culvert on Highway 28 in Hot Springs, MT. After placing the gauge at the target areas, the operator walked about twenty feet away. While he was away, a compactor that was compacting the road bed, slipped off the road near the culvert. When the compactor operator was backing up to get back on the road, he backed over the density gauge. The gauge operator immediately secured the area and contacted the Radiation Safety Officer (RSO). The RSO visually inspected the gauge and determined that both sources were retracted into the shielded position and appeared to be intact. He then surveyed the area and determined that no radiation release had occurred. The RSO conducted a wipe test and determined that no source leakage occurred. There were no personnel overexposures during this event. The gauge is currently in storage at the Montana Department of Transportation awaiting transport to Troxler for disposal. The gauge was a model 3440, serial number 36152. It contained a Cs-137 source (serial number 77-3287, 8 mCi on 11/8/04) and an Am/Be-241 source (serial number 78-1047, 40 mCi on 10/13/04). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-04-16
45844 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-04-15 11:19 | 2010-04-15 17:57 | 2010-06-02 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE DUE TO VOIDING IN DISCHARGE PIPING "The Unit 2 HPCI [High Pressure Coolant Injection] system was declared inoperable due to failure to meet acceptance criteria for air voiding in the discharge piping. UT [Ultrasonic Testing] inspection identified an air void of approximately 0.515 cubic ft. HPCI remains available and on-line risk remains green. "The HPCI discharge piping has been vented. Preliminary post venting UT inspections indicate current void volume is less than acceptance criteria. Certified UT inspectors have been dispatched to validate preliminary UT results. "The event is being reported under 10CFR50.72(b)(3)(v)(D). "The NRC Senior Resident Inspector has been informed of the event." The acceptance criteria for voids is less than or equal to 0.052 cubic ft. * * * RETRACTION FROM THOMAS DITCHFIELD TO JOE O'HARA AT 1431 ON 6/2/2010 * * * "Following the void identification, an engineering evaluation was initiated to determine the impact of the non-condensable gas pocket identified in the HPCI piping. The evaluation was completed and the following results were obtained. "The pocket of non-condensable gas in the HPCI discharge piping did not adversely affect the ability of the system to maintain peak cladding temperatures below required limits. "The pressure that would have been experienced during an initiation of the system was determined to be within the design pressure of the system. "Additionally, the potential force imbalances that would be experienced during a system initiation were determined to be within the piping design allowables. "Based on the engineering evaluation, the pocket of non-condensable gas did not have a detrimental effect on HPCI system operation. The ability of the HPCI system to perform its intended safety function was maintained throughout this condition. Therefore, the above notification is being retracted." The NRC Resident Inspector has been notified. Notified R3DO(Pelke) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-04-15
45843 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2010-04-15 15:39 | 2010-04-15 17:49 | 2010-04-15 | UNPLANNED MANUAL REACTOR TRIP "At 1539 [EDT], Unit 2 was manually tripped due to lifting of the 2B moisture separator reheater relief valve. The Unit commenced a rapid downpower and then a manual reactor trip was initiated at approximately 95% power. All CEA's [control element assemblies] fully inserted on the trip. Auxiliary feedwater automatically initiated on low steam generator level due the 2A steam generator 15% feedwater bypass not opening. No pressurizer power operated relief valves (PORVs) opened. RCS heat removal is now being maintained with auxiliary feedwater and the steam bypass control system. Main feedwater is available. All other systems functioned normally, and the plant is stabilized at normal operating temperature and pressure in Mode 3. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual RPS actuation and 10 CFR 50.72(b)(3)(iv)(A) due to auxiliary feedwater system actuation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-04-15
45842 | 0 | INDIANA MICHIGAN POWER |  |  |  |  | 2010-04-11 09:13 | 2010-04-15 15:44 | 2010-04-15 | FIRE DAMAGED A DEVICE CONTAINING LICENSED MATERIAL "On Sunday, April 11, 2010 at approximately 0813 hrs (CST), two of three dust collector ducts failed on Unit 2 at the Rockport coal fired electric power plant. This resulted in the release of boiler gas in excess of 800 F which caused several small fires of combustible equipment and material. Damage included the rubber sheath covering the remote control cable that opens and closes the level indicator, [which contains the licensed material], and is located in a nearby gas recirculation hopper. "On Wednesday, April 14, 2010 at 1400 hrs (CST), the three (3) shutters on each Unit's level indicators were inspected and found and verified to be in the closed position. The vendor indicates that the estimated shipping date for a replacement is June 18, 2010. An alternative source is being investigated. There was no exposure or injury to any personnel. The adjacent area has been cordoned off and access is restricted. The affected indicator has been tagged in accordance with company energy isolation procedures." The gas recirculation hopper level indicator device was manufactured by Texas Nuclear (device number 5197; serial number LE/LX 7015; source serial number B2628) containing 100 mCi of CS-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-04-15
45841 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-04-14 16:20 | 2010-04-14 21:00 | 2010-04-14 | OFFSITE NOTIFICATIONS DUE TO FISH KILL AND CHEMICAL RELEASE "The licensee notified the State of Minnesota Department of Natural Resources and the Minnesota Pollution Control Agency (MPCA) at 1620 CDT of a fish kill that occurred during a change to the plant circulating water system. Approximately 300-400 fish were found dead in the discharge canal during inspections related to a Zebra Mussel Treatment in progress. The fish included carp, green sunfish, bluegill, carpsuckers, and gizzard shad. The cause appears to be related to temperature changes in the canal as the external circulating water system was manipulated to achieve the 82-84 deg (F) condenser inlet temperatures needed for the treatment and a reduction in plant blowdown flow to the river required by the site discharge permit. The dead fish were contained in discharge canal due to a net that was deployed on Monday in preparation for zebra mussel treatment conducted today (treatment started at 1030 am). Fish in the discharge canal have been dead for 12 to 24 hours. The fish kill is unrelated to the zebra mussel treatment mulluscide addition and did not extend to state waterways. "During the Zebra Mussel treatment, detectable mulluscide was found at the sluice gates to the Mississippi River at 1607 and the chemical addition was stopped The chemical is normally neutralized by addition of clay prior to reaching the sluice gates. The 1607 and 1620 samples at the sluice gates showed 0.6 ppm and 0.8 ppm of CL-2005 mulluscide and the 1730 sample had returned to non-detectable. The plant notified the Minnesota Department of Emergency Management of the chemical release at 1856, event number 110570. The MPCA will be notified during business hours tomorrow. "A news release is not planned." The licensee notified the NRC Resident Inspector. | 0 | 83 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-14
45840 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-04-14 17:03 | 2010-04-14 20:54 | 2010-04-14 | LOSS OF EMERGENCY RESPONSE ORGANIZATION IN-PLANT NOTIFICATION SYSTEM "At 1703 EDT on Wednesday, April 14, 2010, the Pilgrim Nuclear Power Station (PNPS) determined that the in-plant paging/notification systems used to notify the Emergency Response Organization (ERO) were not functioning as designed or required by the Emergency Plan. Specifically, the in-plant notification system which is comprised of the Computerized Automated Notification System (CANS) and back-up system (BEEPS) could not be determined to function reliably or consistently during an Emergency Plan drill or event. "Compensatory measures exist to contact members of the ERO by procedure via call-trees through the operations and security organizations at the site. Immediate actions are being taken to restore the system to functional status working with the service provider for the in-plant paging/notification systems. "It cannot be determined at the time of this notification as to when the system will be restored to full, functional status. "The licensee has notified the NRC Senior Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-14
45839 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2010-03-09 | 2010-04-14 16:49 | 2010-04-14 | FAULTY MODULATION INDEX CONTROL CIRCUIT BOARD USED IN A POWER SUPPLY The following is a summary of information received via fax: "UCI [United Controls International] personnel witnessed system level functional testing of three [Modulation Index Control] MIC circuit boards in a spare unit on March 9-10, 2010 at the PSEG Nuclear LLC training center as part of the dedication process. Initially, the boards were accepted based on the test results but later irregularities were noticed on the output side of another card (reference oscillator) in the system. The Original Equipment Manufacture (Thomas & Betts) began troubleshooting the issue and determined that two resistors (R336 and R347) had one leg each terminated in the wrong location. Subsequent repair and testing confirmed this to be the issue and that once corrected, the irregularities were gone. "The affected licensees are PSEG Nuclear LLC - Salem and Hope Creek Nuclear Generating Stations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-04-14
45838 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2010-02-16 11:22 | 2010-04-14 15:49 | 2010-04-14 | INVALID ACTUATION OF A MOTOR DRIVEN AUXILIARY FEEDWATER PUMP "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1). "On 2/16/10 at 1122 EST, following maintenance activities on 'B' Emergency Safeguards Sequencer, Clearance Order 213623, was in the process of being lifted when an automatic start of 'B' Motor Driven Auxiliary Feedwater (MDAFW) pump occurred. Water flowed to all three Steam Generators resulting in an increase of reactor power by 0.1%. Isolation of Steam Generator Blowdown and Blowdown Sampling also occurred. The actuation occurred during work associated with replacement of relay 2-55/1163 which was installed incorrectly in the "B" Sequencer cabinet. At the time of the event, all Steam Generator levels were normal. No actual condition existed that would require an automatic start of the "B" MDAFW pump and therefore this event has been classified as an invalid actuation. "All equipment operated properly. The 'B' MDAFW pump was secured by operations at 1123 EST. "This invalid actuation was entered into the corrective action program as [Harris Nuclear Condition Report] NCR 381672. "The safety significance of this event is considered to be minimal. The 'B' MDAFW pump started and operated normally and the 'A' MDAFW and Turbine Driven Auxiliary Feedwater (TDAFW) pumps were available. "Immediate corrective actions were to secure the "B" MDAFW pump and restore Steam Generator Blowdown and Sampling." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-04-14
45837 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2010-04-13 12:00 | 2010-04-13 13:17 | 2010-04-20 | UNUSUAL EVENT DECLARED DUE TO AN IDENTIFIED LEAKAGE EXCEEDING 25 GALLONS PER MINUTE On April 13, 2010 at 1200 CDT, Callaway Unit 1 declared an Unusual Event due to identified leakage of greater than 25 gallons per minute (EAL SU6.1). During the flushing of the 'A' Chemical and Volume Control System mixed bed demineralizer, a leak occurred from the vent valve exceeding 25 gallons per minute for approximately 5 minutes. The leak was isolated and the Unusual Event was terminated at 1223 CDT. No personnel contamination or outside release occurred. The licensee has notified the State and local authorities and the NRC Resident Inspector. * * * UPDATE FROM WALTER GRUER TO DONG PARK AT 1614 EDT on 04/13/2010 * * * "Callaway Plant declared an Unusual Event at 1200 CDT on 4/13/2010. The cause of the event was Emergency Action Level (EAL) SU6.1, identified leakage greater than 25 gallons per minute (gpm). "When attempting to place the 'A' Chemical and Volume Control System (CVCS) mixed bed demineralizers in service, a drop in the Volume Control Tank (VCT) level was noted by the Reactor Operator (RO). Technical Specification (TS) 3.4.13 Condition A was entered at 1033 CDT upon identification of identified leakage of the Reactor Coolant System (RCS) greater than 10 gpm. "TS 3.4.13 Condition A requires reduction of leakage to limits within 4 hours. The leakage was verified to be stopped at 1038 CDT, at which time TS 3.4.13.A was exited. The system was restored to a normal alignment. "Upon review, it was determined that the VCT level dropped approximately 125 gallons in 5 minutes. EAL SU6.1 was declared at 1200 CDT and closed at 1223 CDT. "The state and local counties (Callaway, Gasconade, Montgomery, and Osage) were notified of the event at 1210 CDT and of the event closeout at 1227 CDT. "The NRC Resident Inspector was notified of the event. A news release will be made by Ameren Corporate Communications." Notified R4DO (Spitzberg), NRR EO (Nelson), and IRD (Marshall). * * * RETRACTION ON 4/20/10 AT 1417 EDT FROM DAVID HURT TO R. ALEXANDER * * * "The declaration of Unusual Event SU6.1, RCS leakage, on 4/13/10 is being retracted, because the declaration was inaccurate. The leak was an isolable intersystem leak of the CVCS, not RCS leakage, and the leak was stopped within the 15 minute time period allowed to determine EAL applicability. Therefore, the leakage did not meet the Initiating Condition for the EAL. "The NRC Resident Inspectors have been notified." Notified R4DO (J. Whitten). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | MO | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2010-04-13
45836 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2010-04-13 05:01 | 2010-04-13 12:12 | 2010-04-13 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE "During routine testing of the Technical Support Center (TSC) ventilation system, the charcoal filter emergency supply fan did not start as required. As a result, under certain accident conditions, the TSC may become uninhabitable because of the inability of the charcoal filtration unit to maintain environmental conditions within limits. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to radiological or other conditions. If relocation of the TSC becomes necessary, Operational Support Center (OSC) and TSC personnel will relocate to an alternate TSC location in accordance with applicable site procedures with primary TSC and OSC positions reporting to the Main Control Room (which is capable of supporting the additional personnel). "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an Emergency Response Facility (ERF). "Troubleshooting is in progress to determine the cause of the equipment failure. An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATE FROM TIM GATES TO CHARLES TEAL ON 1742 EDT 4/13/10 * * * The failure of the fan to start was caused by loose linkages for a limit switch. The problem has been repaired and the TSC has been returned to service. The NRC Resident Inspector has been informed. Informed R4DO (Spitzberg). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-13
45835 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-02-23 10:50 | 2010-04-13 09:40 | 2010-04-13 | INVALID ACTUATION OF STANDBY GAS TREATMENT SYSTEM "This report is being made under 10CFR50.73(a)(2)(iv)(B)(2). On February 23, 2010 at 1050 EST procedure 52PM-C71-001-0, RPS M/G Set System Preventative Maintenance, was being performed. During restoration of RPS Buses on Unit 1, only the Unit 1 required logic was reset. The Unit 2 logic was also required to be reset but was not. Procedure 52PM-C71-001-0, RPS M/G Set System Preventive Maintenance, did not clearly require the reset of both Unit 1 and Unit 2 logic. The procedure has been revised to make this requirement clear. Continuation of steps in the procedure required links to be closed which resulted in SBGT starting on Unit 1 and Unit 2 from Unit 2 logic. Unit 1 and Unit 2 Reactor Building ventilation isolated. This was not due to a valid signal. The automatic actuation of the standby gas treatment system (SBGT) and the isolation of Unit 1 and 2 secondary containment isolation dampers is considered an invalid actuation since the parameters that cause this actuation to occur had not been exceeded. For this reason the actuation is considered invalid and a report to the NRC is not required by 10CFR50.72(b)(3)(iv); however, because the secondary containment isolation signals affected containment isolation valves in more than one system (Unit 1 and 2 components affected) the event is reportable as required by 10CFR50.73(a)(2)(iv)(B)(2). A licensee event report (LER) is required, but can be a telephone notification as allowed by 10CFR50.73. In the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. "The four Standby Gas Treatment (SBGT) fans auto started and both Unit 1 and Unit 2 reactor building and refueling floor normal ventilation systems automatically shutdown and isolated. The SBGT Initiation and the ventilation system shutdown were both complete actuations." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-04-13
45834 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-12 19:20 | 2010-04-12 21:38 | 2010-04-12 | FITNESS FOR DUTY REPORT "A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2010-04-12
45833 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-12 07:21 | 2010-04-12 10:00 | 2010-04-12 | ACTUATION OF BLACKOUT SEQUENCERS DUE TO LOSS OF ONE OFFSITE POWER SOURCE "At 0721 [CDT] on 4/12/10 the Comanche Peak Nuclear Power Plant experienced a loss of 138 KV transformer XST1 due to a failed transmission line insulator. Unit 1 is currently defueled per 1RF14 refueling outage schedule. Unit 2 was subjected to actuation of both blackout sequencers causing an automatic start of both motor driven Aux Feedwater (AFW) pumps as well as the turbine driven AFW pump. "No emergency diesel generator started as per design. "Train B and the turbine driven AFW pumps have been returned to automatic. Train A AFW pump has been removed from service due to damaged pump packing. "Unit 2 is currently operating in Technical Specification (TS) 3.8.1, Condition A, for one required source of offsite power inoperable and in TS 3.7.5, Condition B, for one train of AFW inoperable. "With the exception of Train A AFW on Unit 2, all other safety systems functioned per design. "The licensee has notified the NRC Resident Inspector." The loss of power to 138 KV transformer XST1 resulted in loss of power to both safeguards busses on Unit 2. The busses performed a load-shed and slow transfer to power supplied from 138 KV transformer XST2 as designed and were re-energized and loads sequenced back onto the busses. The emergency diesel generators are not required to start unless the busses are not re-energized by the alternate offsite transformer. All electrical power related actuations functioned as designed. During this event, the A train AFW pump on Unit 2 started as expected but had to be removed from service due to a pump packing leak. There was no impact on Unit 1 because of its defueled condition. * * * UPDATE FROM PAT MINAHAN TO DONG PARK ON 1840 EDT 4/12/10 * * * "The faulted 138 KV [line] insulator has been repaired, and the Unit 2 safeguard busses have been transferred back to their normal power supplies. The 2-01 motor driven AFW pump has been successfully surveillance tested and is available. Unit 2 remains in TS 3.7.5 condition B pending the close out of an engineering evaluation. No further update notifications are planned." The licensee has informed the NRC Resident Inspector. Notified R4DO (Spitzberg). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-04-12
45832 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-04-12 05:00 | 2010-04-12 04:49 | 2010-04-12 | PLANNED MODIFICATIONS AFFECTING TECHNICAL SUPPORT CENTER VENTILATION "A planned modification at the James A. Fitzpatrick (JAF) Nuclear Power Plant will replace an air conditioning chiller unit located in the old administration building. The electrical isolations necessary to safely perform the modification will require tagging out a booster fan common to the chiller unit and the Technical Support Center (TSC) ventilation system. Therefore, the TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately 12 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the station Emergency Plant Manager will relocate the TSC staff to an alternate TSC location in accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM CHRIS SMOLINSKI TO CHARLES TEAL ON 1857 EDT 4/12/10 * * * Maintenance on the TSC is complete. The TSC has been returned to service. The licensee has informed the NRC Resident Inspector. Notified R1DO (Gray). | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-12
45831 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-12 04:00 | 2010-04-12 03:01 | 2010-04-12 | SCHEDULED MAINTENANCE ON THE TECHNICAL SUPPORT CENTER VENTILATION SYSTEM "At 04:00 on Monday, April 12, 2010, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 22:00 on Monday, April 12, 2010. "The licensee has notified the NRC Senior Resident Inspector. This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM SCOTT SCHNEIDER TO CHARLES TEAL AT 1545 EDT ON 4/12/2010 * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1415." The NRC resident inspector has been informed. Notified R3DO (Orth). | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-12
45830 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-04-10 08:00 | 2010-04-10 08:59 | 2010-04-10 | PLANT PHONE SYSTEM OUT OF SERVICE FOR PLANNED MAINTENANCE "On April 10, 2010, the Monticello Nuclear Generating Plant (MNGP) will be performing planned maintenance to upgrade the site phone system. The maintenance activity will result in the majority of commercial phone lines to the site and the onsite phone system being taken out-of-service for approximately two hours starting at approximately 0800 CDT. The site NRC Emergency Telephone System (ETS), phone lines (which includes ENS, HPN, and ERDS), auto ring lines between the site and the State of MN Emergency Operations Center, onsite radio communication systems, offsite radio communications systems, and the plant Gaitronics system will be unaffected by the maintenance activity. In addition, a commercial phone line in the Control Room and dedicated cellular phone for the Shift Manager will be available for off-site communications." The licensee notified the NRC Resident Inspector and will notify state and local agencies. * * * UPDATE FROM NICK KRAMER TO CHARLES TEAL AT 1604 EDT ON 4/10/2010 * * * "On April 10, 2010 at 1030 hours use of the commercial phone lines and the on-site phone system was restored to the Monticello Nuclear Generating Plant (MNGP). Testing activities are in progress/completed to verify the functionality of affected phones." The licensee has notified the NRC Resident Inspector. Notified R3DO (Peterson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-10
45829 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-04-09 | 2010-04-09 17:37 | 2010-07-08 | RADIOGRAPHY CAMERA SOURCE NOT FULLY RETRACTED The following information was received via email: "Radiographer failed to fully retract Se-75 source into QSA Model 880 camera while on a job site in Stratton, Ohio. No additional information regarding device or source is available at this time. "Radiographer did not 'bump check' the source after retraction to make sure that the source was locked in the camera. He stated that he was using a survey meter as he approached the camera, but it slipped from his hand during his approach and fell to the ground. He stated that he did not verify proper operation after picking up the meter. He was approaching the camera from the rear and stated that he had not observed any reading on the meter. As the radiographer disconnected the guide tube, he noted that the source cable was still sticking out of the camera with the source. He stated that he turned the crank handle about 3/4 of a turn, at which time the source was retracted. The radiographer stated that he could not hear his alarming rate meter due to loud noise in the power plant where the work was being done. The radiographers pocket dosimeter (0 - 200 Mr) was reported as having gone off-scale. "The licensee has estimated a whole body exposure of 1.8 R and an extremity dose to the radiographer's hand of between 3 R and 20 R. The licensee has shipped the radiographer's dosimeter for rush processing and expects to have results late Monday (4/12/10) or Tuesday. ODH [Ohio Department of Health] will conduct an investigation. "NOTE: This report is being made as a precaution until the actual dose received by the radiographer is confirmed." Ref: OH 2010-013 * * * UPDATE FROM STEPHEN JAMES TO PETE SNYDER AT 0950 ON 4/15/10 * * * The following information was received via email: "1. Camera was a QSA Model 880 Delta, S/N D6162. "2. Source was a QSA Se-75 source, 73 Curies on 4/9/10, S/N 2739. "3. Extremity exposure was to right hand. "4. The radiographer's dosimeter was processed and indicated a whole body dose (shallow) dose of 0.563 Rem for April 2010, through April 9, 2010. This is approximately four times higher than the radiographer received in March 2010 (0.147 Rem). "5. ODH [Ohio Department of Health] will investigate the week of April 19 to recreate event and verify dose estimates and events leading to the exposure. "NOTE: As of the current information, the exposure received by the radiographer would not require reporting of the event. Final determination will be made upon completion of investigation by ODH." Notified R3DO (Orth) and FSME (McIntosh). * * * UPDATE FROM STEPHEN JAMES TO CHARLES TEAL AT ON 7/8/10 AT 1128* * * "ODH investigation and recreation of event indicate that the radiographer did follow proper procedures and was exposed to [the] source for less than one (1) minute total. [The] radiographer had [a] stopwatch used for timing shots and he had failed to shut off the stop watch until he had removed himself from area of source, at which time the stopwatch indicated 5 minutes since the shot began. This exposure does NOT require notification and no further action to be taken at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MI | OTH | AGR |  |  |  |  | 0 | 2010-04-14
45828 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-04-08 16:22 | 2010-04-08 20:34 | 2010-04-09 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE STEAM GENERATOR INLET ISOLATION VALVE "At 1622 hours CDT, an electrical ground on 480 Volt Bus 1B3A was determined to be from a supply cable to Motor Control Center (MCC)-3A1. Isolating loads on this MCC required securing power to HCV-1385, Steam Generator RC-2B Inlet Isolation Valve. This condition results in the valve being unable to close on a Steam Generator Isolation Signal (SGIS), which requires entry into Technical Specification 2.0.1(1). This Technical Specification requires the plant to be placed in a Hot Shutdown condition within 6 hours. A plant shutdown to Mode 3 was commenced at 1740 hours CDT." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVID SPARGO TO DONALD NORWOOD AT 0036 EDT ON 4/9/2010 * * * "At 2123 hours CDT, the Reactor was manually tripped from 22% Reactor Power in order to meet the requirements of Technical Specification 2.0.1(1) and have the reactor in a hot shutdown condition. All systems functioned properly. "At 2124 CDT, the plant entered Mode 3 Shutdown Condition. AT 2235 CDT, HCV-1385, Steam Generator RC-2B Inlet Isolation Valve has been manually closed. Technical Specification 2.0.1(1) has been exited." The licensee is reporting the manual scram under 10CFR50.72(b)(2)(iv)(B). The licensee notified the NRC Resident Inspector. | 75 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | RPS ACTUATION - CRITICAL |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(2)(iv)(B) |  | 0 | 2010-04-08
45827 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-04-08 | 2010-04-08 17:26 | 2010-05-10 | DIESEL GENERATORS WIRED INCORRECTLY "Action F of LCO 3.8.1, 'AC Sources - Operating,' was entered at 20:57 EDT April 7, 2010 for the 2A-A and the 2B-B diesel generators (DGs) being inoperable. Action F has a two hour allowed outage time (AOT). The DGs were determined to be inoperable due to incorrectly implemented wiring changes made by personnel performing construction work on Watts Bar Unit 2. The impact of the change is that during [an] actual or simulated ESF actuation signal, if the diesel is in test mode, and the output breaker is closed in parallel with the board supply breakers, the DG would not return to a 'ready to load' state meaning the output breaker would not have opened as designed for this condition. This function is tested as required on an 18 month frequency as a part of Surveillance Requirement (SR) 3.8.1.17. "The wiring changes which affected the DGs were made in accordance with Unit 2 Work Order (WO) 09-954447 and 09-954448. The WOs as developed would not have an impact on Unit 1 operations. A review of the Unit 1 Operator Logs from January 1, 2010 to present, did not find any entries establishing the Unit 2 work had been authorized by Unit 1. The proper technical specification entry would have been Action 8 of LCO 3.8.1 for this activity. Entry into Action B of LCO 3.8.1 requires the implementation of several actions including a verification of the operability of the offsite circuits. Since these Technical Specification required actions were not complied with, WBN is providing this 24-hour notification in accordance with Section 2.G of the Watts Bar Unit 1 Facility Operating License. "During the review of work performed by Unit 2 it was identified that the wiring was initially lifted on January 6. 2010. At the time of this report, actions have been taken to restore the wiring to its appropriate configuration on both of the DG circuits. 2B-B DG wiring was restored at 22:18 on April 7, 2010 and the 2B-B DG was declared operable. Action F of LCO 3.8.1 was exited at this time and Action B was entered for the 2A-A DG (14 day AOT). 2A-A DG circuitry was restored at 00:37 on April 8, 2010, and all LCO actions were exited. This event has been entered into TVA's corrective action program and actions are being initiated to establish the reason the leads were incorrectly lifted and to verify that no other similar wiring issues exist." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM WES DANIEL TO PETE SNYDER AT 1646 ON 5/10/10 * * * "The Watts Bar Nuclear Plant (WBN) Unit 2 diesel generators (DGs) were not inoperable." "The Unit 2 DGs were initially declared inoperable because of an inappropriate wiring change that disabled a DG output breaker trip in the event of an actual or simulated ESF actuation signal while the DG is in test mode and the output breaker is closed in parallel with the board supply breakers. Because Surveillance Requirement (SR) 3-8.1.17 required verification of this function for the Unit 1 DGs, and TVA was uncertain of the impact of the loss of this function to the Unit 2 DGs, TVA conservatively declared the Unit 2 DGs inoperable because they would not be able to meet this SR. "Upon review TVA determined that it was proper to exclude this surveillance requirement for the Unit 2 DGs. Since SR 3.8.1.17 only applies to Unit 1 DGs, inability of Unit 2 DGs to meet this requirement is not a basis for inoperability. TVA has concluded that the Unit 2 DGs and offsite power sources were operable, and WBN was in compliance with its Technical Specifications throughout the period that the wiring change was installed. Therefore, this event was not reportable under WBN License (NPF-90) Condition 2.G, 10 CFR 50.72, or 10 CFR 50.73." The licensee notified the NRC Resident Inspector. Notified R2DO (O'Donohue). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2010-04-08
45826 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-04-08 | 2010-04-08 16:33 | 2010-04-15 | AGREEMENT STATE REPORT - POTENTIAL RADIOGRAPHER OVEREXPOSURE The following information was received via fax: "An employee's TLD recorded an overexposure of 6.8 rem. The date was 22 March 2010 when the overexposure occurred. The affected employee claims he left his leather pouch with the TLD [in it] in the exposure area for two shots. His pocket dosimeter reading was also off scale. The RSO originally calculated the employee's dose to be approximately 4 rem which is not required to be reported to the state. The RSO received Landauer's dosimeter report sometime after 22 Mar 2010 which showed a 6.8 rem dose. The licensee contacted Licensing and Materials on 7 April 2010. The Tampa Inspection Office will investigate." * * * UPDATE FROM STEVE FURNACE TO HOWIE CROUCH @ 1340 EDT ON 4/15/10 * * * A Florida Department of Health investigator made a site visit on 4/15/10 to investigate the circumstances of the event. After recreating the event, the investigator agrees that the overexposure to the TLD could have only occurred if the employee left his TLD in the test area. Florida considers this case closed. Notified R1DO (Gray) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-04-13
45825 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-04-06 | 2010-04-08 16:00 | 2010-04-08 | AGREEMENT STATE REPORT - LOSS OF TRAINING BUTTON SOURCE The following information was received via fax: "A Training button source was lost on 3/6/2010 during training in Alachua county. The training facility was searched and the source was not found. Corrective actions include additional source handling procedures, daily checklists for use of sources, and training on proper notification to RSO of all events regarding use of RAM. No further action will be taken on this incident." Florida Incident Number: FL10-049 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-04-13
45824 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-04-08 | 2010-04-08 15:35 | 2010-04-08 | STACK SAMPLE LINE SEPARATED AT FITTING "During the routine replacement of the stack sample flow transmitter, technicians in the area discovered the stack sample line had become separated at a SWAGELOK union at the 150 foot elevation. The sample line was reconnected and a visible count change was observed. At the time of discovery, the stack radioactive gas effluent monitoring system (RAGEMS) had been removed from service in accordance with the plant procedures and declared inoperable for performance of Surveillance Procedure 621.3.023 'Stack RAGEMS Sample and Effluent Flow Calibration.' Plant chemistry personnel are currently taking compensatory grab samples. "Engineering has determined that functionality of the stack radiation monitoring capability was degraded and therefore this notification is being made in accordance with 50.72(b)(3)(xii) as a condition that resulted in a loss of monitoring capability. Backup assessment capabilities were available for Reactor Building Ventilation Radiation Monitoring and the Off-Gas Sample Monitor." The NRC Resident Inspector will be informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-08
45823 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-04-08 10:15 | 2010-04-08 14:07 | 2010-04-08 | NOTIFICATION OF UNUSUAL EVENT DUE TO AN EARTHQUAKE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under reporting requirements of 10 CFR 50.73. "An Event Classification of Unusual Event (HU1.1) was declared at 10:15 MST for the Palo Verde Nuclear Generating Station because of an earthquake that originated in Baja California location 32.220 N, 115.276 W at 09:44 MST. Per the USGS website and via phone conversation at 1003, the magnitude of the earthquake was preliminarily 5.5 on the Richter scale. "Initial walk downs of plant equipment and review of plant parameters have found no unusual conditions or damage to plant equipment. No abnormalities caused by the seismic event were observed. No reactor protection system (RPS) or engineered safety feature (ESF) actuations occurred and none were required. "Palo Verde Unit 1 is in mode 6 for a scheduled refueling outage and Units 2 & 3 are at 100 percent power with all offsite power supplies available. Seismic Monitoring Instrumentation system is currently functional and did not indicate a seismic event. Currently based on the Modified Mercalli scale the seismic event was below the magnitude of the 0.10g spectra Operating Basis Earthquake (OBE) and the 0.20g spectra Safe Shutdown Earthquake (SSE)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JIM BLAZEK TO PETE SNYDER AT 1606 ON 4/8/10 * * * "Emergency classification termination was declared at 4/08/10, 12:54 MST. All required power block inspections were completed with no deficiencies noted. No other conditions required an emergency classification, there are no challenges to fission product barriers or radiological release, and plant conditions offer no possibility of adverse impact on health and safety of the public. "The NRC Resident Inspector has been notified of NUE termination." Notified R4DO (Proulx), NRR EO (Thorp), DPR (McDermott), DHS (McDonald), and FEMA (Hollis). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-04-08
45822 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-04-08 08:30 | 2010-04-08 11:51 | 2010-04-08 | PAGING SYSTEM OUTAGE "At about 0830 CDT on 4/8/2010, it was discovered that the station paging system was not operating. Repair efforts were initiated. The Control Room and station personnel were notified of the pager outage. The automated callout system is available to notify the emergency response organization during the pager outage if needed. "That pager system was returned to service at about 1005 CDT 4/8/10." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-08
45821 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-06 08:30 | 2010-04-07 21:11 | 2010-04-08 | STORM DRAIN SYSTEM TESTED POSITIVE FOR TRITIUM "On 4/06/10, Salem management was notified that samples taken from the Salem Unit 2 north storm drain system were positive for tritium. Two storm drain catch basin sample results were confirmed above 1 million pico Curies per liter. The affected area of the north storm drain system has been isolated. Samples upstream of the river outfall were less than the minimum detectable level for tritium. "NRC reporting criteria were reviewed and, although no direct reportable criteria were met, based on the public sensitivity to tritium issues, it was determined that a voluntary notification to the NRC was prudent. "Salem is taking action to mitigate, locate, and remediate the source of the tritium. In addition to isolating the affected portion of the system, the station has increased the sample frequency for the storm drain system and ground water wells in the affected area. "A voluntary notification has been made to the appropriate State agency and the NRC Resident Inspector." * * * UPDATE FROM TOM BYYKKONEN TO PETE SNYDER ON 4/8/10 AT 2025 * * * "Based on further evaluation, Salem officially notified the New Jersey Department of Environmental Protection of the above tritium spill on 4/8/10 at 2003. This notification to New Jersey is reportable in accordance with 10 CFR 50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. Notified R1DO (Trapp). | 0 | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-07
45820 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-04-07 16:10 | 2010-04-07 20:28 | 2010-04-07 | SPILL OF WATER CONTAINING TRITIUM "Browns Ferry Nuclear Plant (BFN) is notifying state and local agencies of a spill of water containing tritium as specified in section 2.2.a.iii, of Nuclear Energy Institute document NEI 07-07 entitled 'Industry Groundwater Protection Initiative.' On April 7, 2010 from 02:30 to 03:00, BFN operations personnel were transferring water from one Condensate Storage Tank (CST 3) to another Condensate Storage Tank (CST 5). At 08:25, an operator conducting rounds noticed water flowing from an open test valve near the top of CST 5. The estimated flow rate from the test valve was approximately two gallons per minute (gpm). Attempts to isolate the open test valve by plant operations personnel were unsuccessful. Plant operations personnel lowered level in CST 5 and water flowing from the test valve stopped at 10:35. "The volume of water spilled to ground is estimated to be approximately 1,000 gallons. At 16:10, laboratory analysis results indicated this water contained 2.05 E-03 uCi/ml tritium. Mitigative actions will be developed and implemented. BFN Procedure: SPP 5.14 requires that state and local agencies be notified within one business day of verification of a discovery when: ' the spill or leak has or can potentially migrate to groundwater: 1. An unmonitored and inadvertent contaminated leak or spill of liquids of unknown volume and reasonably determined to be greater than 100 gallons to the environment occurs ' "This event is reportable as a 4-hour non-emergency notification report in accordance with 10 CFR 50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.'" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Startup | Power Operation | Power Operation | Startup | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-04-07
45819 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-04-07 | 2010-04-07 19:10 | 2010-04-08 | AGREEMENT STATE - DEPLETED URANIUM FOUND IN SCRAP METAL A scrap yard located in Seguin, TX was processing a rail car loaded with scrap metal when their radiation detectors alarmed. When the load was investigated a Varian Linear Accelerator was found (serial number 71). The source of radiation was determined to be from approximately 100 lbs. depleted Uranium contained in the unit. The shipment originated from Austin, TX. * * * RETRACTION FROM RAY JISHA TO CHARLES TEAL ON 4/8/10 AT 1302 * * * Additional investigation determined that the Varian CLINAC 18 accelerator does not contain depleted Uranium. The shields in this model are made of tungsten. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-04-12
45818 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-04-07 | 2010-04-07 17:46 | 2010-04-07 | AGREEMENT STATE - RADIOGRAPHY TRUCK INVOLVED IN AUTO ACCIDENT "On April 7, 2010 at approximately 1430 CST the Incident Investigation Program was notified by the licensee's Radiation Safety Officer (RSO) that one of the licensee's trucks carrying a camera with a 24 curie Iridium (Ir) 192 source had been involved in a car accident around 1300 CST that same day. The RSO stated that the radiography truck had collided head on with a tractor-trailer on a highway approximately 8-10 miles east of Kosse, Texas. One of the radiographers was fatally wounded and the other was rushed to the hospital. Consequently, no one was able to perform a survey to verify the source was intact in the camera as well as secure the camera. The RSO stated that the Robinson County Emergency Management Coordinator was on the scene along with police and fire personnel, as well as Texas Department of Transportation. The RSO stated that none of the emergency personnel responding were equipped with a radiation survey meter to verify the source locale. The RSO stated that the Site Radiation Safety Officer was en route to the scene to perform a survey and retrieve the camera, but he was almost two hours away. The Emergency Management Coordinator had cordoned off the area around the radiography camera. I contacted an Agency investigator who was near the area performing field work, and he agreed to go by the location and perform a survey because he could be there within 45 minutes. At approximately 1630, the investigator arrived on the scene and performed his survey. The investigator stated that it appeared the source was still housed in the camera and that the highest dose rate was 2.2 millirems/hour near the camera. The site RSO arrived on the scene, and the investigator briefed him on the survey. The information was passed to the RSO and he agreed to submit a report to the Agency." Texas Incident #: I-8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-04-12
45817 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2010-04-07 10:00 | 2010-04-07 16:48 | 2010-04-07 | FITNESS FOR DUTY REPORT A non-licensed contract employee had a confirmed positive for alcohol during a fitness-for-duty test. The contractor's access to the facility has been terminated. Contact the Headquarters Operations Officer for further details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2010-04-07
45816 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2010-04-06 17:47 | 2010-04-07 00:33 | 2010-04-29 | INITIATION OF TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO CONTROL ROOM EMERGENCY FILTRATION SYSTEM BEING DECLARED INOPERABLE "At 1650 PDT Columbia Generating Station entered LCO 3.0.3 as required by LCO 3.7.3 for both divisions of Control Room Emergency Filtration (CREF) [being] inoperable. Entry into LCO 3.0.3 was required by Condition E of LCO 3.7.3, 'Two CREF subsystems inoperable in MODE 1, 2, or 3 for reasons other than Condition B' and has a Required Action to enter LCO 3.0.3 with an immediate Completion Time. Columbia commenced a plant shutdown at 1747 as required by LCO 3.0.3. "[Columbia Generating Station] entered into Condition E of LCO 3.7.3 when it was determined that Radwaste Building Outside Air Smoke Detectors WOA-SMD-1A and WOA-SMD-1B did not meet seismic qualifications. Actuation of these smoke detectors would cause Radwaste Building Mixed Air Fire Dampers WMA-FD-1 and WMA-FD-2 to close. These fire dampers shutting would cause all CREF airflow to cease, preventing the control room from achieving a positive pressure. Both divisions of CREF [being] inoperable is an unanalyzed condition requiring immediate entry into LCO 3.0.3. "This event is reportable under 50.72(b)(2)(i) due to the initiation of a plant shutdown as required by Columbia's Technical Specifications. This event is also reportable under 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "WMA-FD-1 and WMA-FD-2 have been deactivated in the open position for the smoke actuation function. [Columbia Generating Station] entered RFOLCS (Requirements for Operability of Licensee Controlled Specifications) 1.10.6 for these fire dampers [being] nonfunctional. [Columbia Generating Station] completed the required actions of LCS 1.10.6. "The CREF system remains inoperable pending completion of a TMR (Temporary Modification Request)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM QUOC VO TO CHARLES TEAL ON 4/7/10 AT 1957 * * * "Question posed by NRC at time of initial report: Have these smoke detectors been installed since startup? "Response: These smoke detectors have been installed since initial plant startup. "A temporary modification request was installed to de-energize the non-seismic detector logic that causes automatic fire damper actuation for the two dampers identified above. The alarm function of the smoke detectors remains active with this temporary modification. "Entry into this condition was made when it was determined that the smoke detectors were not seismically qualified and there is a possible failure mode that during an earthquake the detectors would actuate the electro-thermal link and cause the associated fire damper (WOA-FD-1 or WOA-FD-2) to close, hence impacting control room emergency filtration function. "With implementation of the temporary modification at 2218 PDT on 4/6/10, the CREF system is now considered to be in an 'operable but non-conforming' status. As such, LCOs 3.7.3 and 3.0.3 were exited at 2218 PDT on 4/6/10. "This event was initially reported pursuant to paragraph 50.72(b)(2)(i) as an initiation of a plant shutdown required by Columbia's Technical Specifications. Reporting pursuant to paragraph 50.72(b)(2)(i) is being retracted because negative reactivity was not inserted into the reactor prior to exiting the LCOs described above. Reporting pursuant to paragraph 50.72(b)(2)(i) would not be consistent with the guidance provided in NUREG-1022 in that no negative reactivity was inserted and the condition was corrected before exceeding the required action times." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM KYLE CHRISTIANSON TO PETE SNYDER AT 1550 EDT ON 4/29/2010 * * * "Subsequent to the April 7, 2010, event report (EN #45816), an Energy Northwest engineering evaluation concluded that the identified smoke detectors would not inadvertently actuate during a design basis safe shutdown earthquake (SSE). This conclusion is based on a seismic response spectrum test report for the smoke detectors. Therefore, since the safety function of the CREF system needed to mitigate the consequences of an accident would not be affected by an SSE, the event notification made pursuant to 10 CFR 50.72 (b)(3)(iv)(D) is hereby retracted." "The NRC Senior Resident Inspector (Cohen) has been notified." Notified R4DO (Clark). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-04-07
45815 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2010-04-05 22:50 | 2010-04-06 06:11 | 2010-06-04 | LOSS OF SAFETY FUNCTION TO CONTROL THE RELEASE OF RADIOACTIVE MATERIAL "At 2145 [EDT] hours on April 5, 2010, a loss of electrical power to the Division 1 Loss of Coolant Accident (LOCA) initiation logic occurred. Control room annunciators for 'Residual Heat Removal (RHR) Out of Service', 'Reactor Core Isolation Cooling (RCIC) Out of Service', and 'RCIC/RHR D2 to D1 00 File Power Loss' were received. At 2250 hours, the Control Room staff determined a loss of isolation function existed. The operators entered Technical Specification (TS) action statements for Emergency Core Cooling System Instrumentation (TS 3.3.5.1), RCIC Instrumentation (TS 3.3.5.2), and Primary Containment and Drywell Isolation Instrumentation (TS 3.3.6.1). The power loss was caused by a blown fuse which occurred during surveillance testing. The surveillance test was suspended and plant personnel commenced troubleshooting and investigation efforts. A recovery plan is being developed to back out of the surveillance test and replace the fuse to re-energize the logic, while ensuring the plant does not experience an undesirable actuation of the logic. "The power loss caused five containment isolation valves to lose automatic isolation function. These valves have no associated inboard automatic isolation valve powered by Division 2. As a result of the power loss, the valves cannot automatically close on demand to isolate and therefore cannot perform their automatic function to isolate the containment. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "The NRC Resident Inspectors have been notified." The licensee entered a 12-hour shutdown action statement for the loss of containment isolation function as a result of the power failure. * * * RETRACTION FROM LLOYD ZERR TO PETE SNYDER ON 6/4/2010 AT 1126 * * * "On April 6, 2010, at 0611 hours, notification was made to NRC Operations Center of an event that at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material [10 CFR 50.72(b)(3)(v)(c)]. A blown fuse during surveillance testing caused a loss of electrical power to the Division 1 Loss of Coolant Accident initiation logic. The power loss caused five containment isolation valves to lose their automatic isolation function. These valves have no associated inboard automatic isolation valve powered by Division 2. As a result of the power loss, the valves could not automatically close on demand and therefore, could not perform their automatic function to isolate containment. "Following further evaluation, it was determined that a loss of safety function of structures or systems that are needed to control the release of radioactive material did not occur. Based on review of valve leak rate test history and compliance with 10 CFR 50, Appendix A, General Design Criteria, the penetrations and Containment were capable of performing their intended design function. The associated inboard valves and/or water seals were capable of automatically isolating containment. Additionally, all required Technical Specifications Limiting Conditions for Operation were complied with for the identified issue, and therefore, no operation or condition prohibited by the plant's Technical Specifications existed. "Since the event or condition reported in Event Notification 45815 would not have prevented the fulfillment of the safety function needed to control the release of radioactive material, this event or condition is not reportable and the notification is retracted. Additionally, based on not meeting any 10 CFR 50.73 reporting criteria, no Licensee Event Report is required. The evaluation (i.e., Reportability Determination) for this event or condition is documented in Condition Report 10-74904. "The NRC Resident Inspector has been notified." Notified the R3DO (Pelke). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2010-04-06
45814 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2010-04-05 23:02 | 2010-04-06 02:42 | 2010-04-06 | TRANSPORT OF A CONTAMINATED INDIVIDUAL OFFSITE "On 4/5/2010, at 2244 [EDT], the Unit 1 Control Room was notified of an individual in the Unit 1 Containment Building complaining of chest pains. Offsite medical was contacted via 911 emergency call and the individual was transported, via ambulance, to Lawnwood Regional Medical Center at 2302. Radiation Protection personnel accompanied the individual to the hospital. The individual was admitted at 2335. Radiation Protection personnel determined that the individual was radioactively contaminated at a level of 3500 corrected counts per minute on his left ankle. The individual was successfully decontaminated. The transport of a radioactively contaminated individual to an offsite medical facility is reportable under 10CFR50.72(b)(3)(xii)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2010-04-06
45813 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-04-04 23:34 | 2010-04-05 16:25 | 2010-04-05 | LOSS OF EMERGENCY SIREN ACTIVATION CAPABILITY "At 1400 hours Eastern Daylight Time (EDT) on April 5, 2010, the Control Room was notified that the ability to activate the thirty-eight (38) emergency sirens within the 10 mile emergency planning zone (EPZ) radius of the plant had been lost for a period of 1 hour and 16 minutes from 2334 hours EDT on April 4, 2010, until 0050 hours on April 5, 2010. The event occurred when an Uninterruptible Power Supply (UPS), supplying radio repeaters used to activate the sirens failed. Inoperability of the repeaters impacts the ability to actuate the emergency sirens from the New Hanover County and Brunswick County Emergency Operations Centers (EOCs) as well as from the Brunswick Nuclear Plant Emergency Offsite Facility (EOF). "The failed UPS was reset and emergency siren activation capability was restored at 0050 hours EDT on April 5, 2010. "The reportability requirement associated with the inability to activate the emergency sirens was not recognized by personnel who responded to the failure and, as such, the failure was not communicated to the control room. Emergency Preparedness personnel, reviewing emergency siren computer event logs on April 5, 2010, became aware of the failure and understood its impact. This resulted in notification of the event to the control room. "The initial safety significance of the event is minimal. The Brunswick and North Carolina Emergency Response Plans include compensatory measures to provide warning to affected areas, if required, in the event of the loss of sirens. "The ability to activate the emergency sirens has been confirmed. Investigations into the cause of the UPS failure, as well as interim and long term corrective actions are in progress. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-04-05
45812 | -1 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-04-04 12:45 | 2010-04-04 20:56 | 2010-04-05 | BOTH TRAINS OF RESIDUAL HEAT REMOVAL (RHR) INOPERABLE "On 4/4/10 at 1245 [CDT], three RHR system snubbers were declared inoperable due to visual inspection identifying empty reservoirs for the snubbers. The inoperability of the snubbers rendered both trains of RHR cooling inoperable. On 4/4/10 at 1545, ultrasonic testing identified voided piping on the common RWST [Refueling Water Storage Tank] suction line to the RHR pumps. This condition also resulted in inoperability of both trains of RHR for the ECCS [Emergency Core Cooling System] mode of operation. "At the time of these discoveries, Unit 2 was in mode 4, proceeding to mode 5 for a refueling outage. The inoperability of both trains of RHR represents a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat and mitigate the consequences of an accident. Replacement of the snubbers is in progress. Following completion of snubber replacement, Unit 2 will proceed to mode 5 at which point ECCS capability is not required. Resolution of the voided piping will be accomplished following mode 5 entry." The snubbers are in containment and were last checked during the previous refueling outage. The voiding in the RHR suction line only affects suction from the RWST and not when suction is aligned to the Reactor Coolant System. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM DOUGLAS HOBSON TO DONG PARK AT 1604 EDT ON 4/5/10 * * * "An eight hour report (EN #45812) per 10CFR50.72(b)(3)(v)(B) and 10CFR50.72(b)(3)(v)(D) was conservatively reported because both trains of Residual Heat Removal (RHR) system were thought to be inoperable based on the initial visual inspection of three hydraulic snubbers. In addition, initial ultrasonic testing at the RHR suction line to the refueling water storage tank (RWST) identified what was thought to be voided piping. "Subsequent visual inspections and testing demonstrated that all three snubbers had adequate oil to ensure that the snubbers would perform their intended function. In addition, the ultrasonic testing was reviewed and determined that the technique for the coupling gel application between the ultrasonic detector and piping was not adequate for an accurate test. The ultrasonic inspection was performed again using the correct detector to piping coupling technique and it was determined that the RHR piping had adequate water level. Therefore, based on more accurate subsequent results of snubber and ultrasonic testing, the RHR system was never inoperable. "The three snubbers thought to be inoperable were removed and replaced with snubbers previously verified to be operable. After removal, the snubbers were visually inspected and tested. Two of the three hydraulic snubbers share a common oil reservoir. This common reservoir was found to be completely full of clear oil which made it difficult to determine reservoir oil level while installed in the plant. The third snubber oil reservoir was one-third full. The removed snubbers have been tested to confirm they would have operated as designed. "The ultrasonic testing of RHR piping was started as a result of SNC's response to NRC Generic Letter 2008-01. This testing requires a coupling gel to be used between the ultrasonic detector and the RHR piping to ensure accurate water level results. Based on the initial ultrasonic test results it was thought that the RHR piping had voids. However, when the coupling process was reexamined, it was determined that additional coupling gel was needed for accurate results. When the ultrasonic test was performed again with the proper coupling process, it was determined that the RHR piping had adequate water and that voiding did not exist. The second ultrasonic inspection technique was reviewed and confirmed the coupling process utilized was correct. "In summary, a loss of safety function on both trains of RHR did not exist and the 50.72(b)(3)(v)(B) and 50.72(b)(3)(D) report (EN # 45812) is retracted." The licensee notified the NRC Resident Inspector. Notified R2DO (Moorman). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-04-04
45811 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-04-04 15:42 | 2010-04-04 19:38 | 2010-04-05 | UNUSUAL EVENT DECLARED DUE TO AN EARTHQUAKE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "An Event Classification of Unusual Event (HU1.1) was declared at 1549 MST for the Palo Verde Nuclear Generating Station because of an earthquake that originated in Baja California, [Mexico] location 32.093?N, 115.249?W at 1542 MST. Per the USGS [U.S. Geological Survey] website, the magnitude of the earthquake was 6.9 on the Richter scale. Initial walkdowns of plant equipment and review of plant parameters have found no unusual conditions or damage to plant equipment. No abnormalities caused by the seismic event were observed. No Reactor Protection System (RPS) or Engineered Safety Feature (ESF) actuations occurred and none were required. Palo Verde Unit 1 is in mode 5 for a scheduled refueling outage, and Units 2 & 3 are at 100 percent power with all offsite power supplies available. "Initial analysis of the Seismic Monitoring Instrumentation system indicated a seismic event, below the magnitude of the 0.10g spectra Operating Basis Earthquake (OBE) and the 0.20g spectra Safe Shutdown Earthquake (SSE)." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM GORDON TIMOTHY TO VINCE KLCO AT 0003 EDT ON 4/5/2010 * * * "Emergency classification termination was declared at 4/4/10, 2045 MST. All required power block inspections were completed with no deficiencies noted. No other conditions require an emergency classification, there are no challenges to fission product barriers or radiological release, and plant conditions offer no possibility of adverse impact on health and safety of the public. NRC Resident Inspector has been notified of NUE termination." Notified the R4DO (Okeefe), NRR-EO (Bahadur), FEMA (Via), DHS (Wallace) and IRD via email (Gott). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-04-04
45810 | 0 | SAN ONOFRE | 1 | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-04-04 15:42 | 2010-04-04 19:07 | 2010-04-04 | NOTIFICATION OF UNUSUAL EVENT - EARTHQUAKE FELT ON SITE "Seismic Recording System activation with ground motion readily felt by control room personnel. Plant inspections performed to date show no observable damage to systems or structures." The seismic event was reported by U.S. Geological Survey as a magnitude 7.2 event occurring 26 km (16 miles) SW of Guadalupe Victoria, Baja California, Mexico. Initial ground motion analysis on site indicated 0.027 g acceleration in the transverse direction. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ROBERT MEYERS TO DONG PARK AT 2055 EDT ON 4/4/2010 * * * The Notification of Unusual Event classification was terminated at 1725 PDT on 4/4/2010 after completion of walk downs with no equipment issues being found. Notified R4DO (Okeefe), NRR EO (Bahadur), IRD (Gott), DHS (Vestal), and FEMA (Via). | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Decommissioned | Hot Shutdown | Power Operation | Decommissioned | Hot Shutdown | Power Operation | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-04-04
45809 | 0 | TYCO FLOW CONTROL |  |  |  |  | 2010-04-02 | 2010-04-02 17:12 | 2010-04-02 | POSSIBLE FAILURE OF SOLENOID VALVES WITH DUAL FUNCTION MAIN STEAM SAFETY VALVES The following information was received via facsimile: "Tyco Valves & Controls LP (TVC), a business unit of Tyco Flow Control, is a contractor to certain NRC licensees, and on behalf of itself and certain of its affiliates, hereby submits information in response to notification requirements of 10 CFR Part 21. TVC manufactures, sells, and services Pressure Relief Valves (PRVs) to NRC licensees for use in NRC licensed facilities. "On February 4, 2010, EPRI issued a notification of a potential 10 CFR Part 21 defect for Main Steam Safety Valves manufactured by Crosby Valve & Gage (Crosby). Crosby became a brand of TVC when they were purchased by them in 1998. The reported problem stems from an issue with the solenoid valve that controls the pneumatic actuator on certain main steam safety valves that were supplied during the early 1980's. "Following is a list of U.S. plants that may have been affected by this issue: "Utility Unit Start Up "PA Power & Light Susquehanna 1 & 2 1983 & 1985 "Exelon LaSalle I & 2 1984 "Energy NW Columbia 1984 "Entergy Riverbend 1986 "TVC continues to investigate the reported problem, but is requesting a 30 day extension to complete the evaluation due to the complexity of the situation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-04-02
45808 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-04-02 14:30 | 2010-04-02 16:59 | 2010-04-02 | CONTRACTOR FAILED FITNESS FOR DUTY TESTING A contract employee had a confirmed positive for a controlled substance during a pre-access fitness-for-duty test. The individual's access to the plant was not granted. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2010-04-02
45807 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2010-04-01 | 2010-04-02 12:17 | 2010-04-02 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED BY CONSTRUCTION EQUIPMENT The following information was received from the Commonwealth of Virginia via facsimile: "The licensee's portable density gauge (Troxler Model 3430 S/N 038435) was damaged on April 1, 2010 when it was struck by a piece of earth moving equipment. The accident occurred at a commercial construction site in Roanoke County, Virginia. The gauge operator secured the area of the gauge and telephoned the licensee's Radiation Safety Officer who performed an onsite investigation and a radiation survey. The source was in the shielded position at the time of the accident and the survey confirmed that it remained so. There was no damage to the source rod or handle and only minor damage to the gauge trigger and casing. The gauge was returned to the licensee's storage facility. There were no injuries or radiation exposures as a result of the accident." Virginia Event Report ID No: VA-10-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2010-04-07
45806 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2010-04-02 04:45 | 2010-04-02 07:28 | 2010-04-02 | UNIT COMMENCED SHUTDOWN AFTER DECLARING MOTOR-DRIVEN EMERGENCY FEEDWATER SYSTEM INOPERABLE "At 0445 [EDT], VC Summer Nuclear Station commenced a shutdown required by Technical Specification 3.7.1.2 Action b. FCV 03541-EF, emergency motor driven feedwater flow control valve 'B', was declared inoperable due to the failure of Surveillance Requirement 4.7.1.2.b at 0154 [EDT]. In accordance with 3.7.1.2 Action b, hot standby is required to be achieved within 6 hours (0754 EDT). At approximately 87% power, FCV 03541-EF was repaired and the associated Technical Specification was exited at 0608 [EDT]. The power descent has been stopped, and all systems are functioning as required." The licensee will inform state/local agencies and has informed the NRC Resident Inspector. | 87 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-04-02
45805 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-03-31 15:30 | 2010-04-01 15:12 | 2010-04-01 | FAILED ACTIVE ENGINEERED CONTROL ON A ULTRASONIC TESTING SMART CRANE "On March 29, 2010, Nuclear Criticality Safety (NCS) was notified that a UT Smart Crane had failed its functional test. The Smart Crane is an active engineered control that prevents simultaneous immersion in water of two fuel bearing components of concern in an Ultrasonic Testing (UT) tank. Earlier in the morning the crane tripped into fault mode while being moved to a storage position; there was no fuel bearing component attached to the crane at the time. Plant Maintenance personnel reset the crane's PLC [Programmable Logic Controller] and the required functional tests were performed per procedure prior to returning the crane to service. When the functional test was performed on Tank #3, the crane failed the test. Tank #3 was loaded with a component of concern (> 500 lbs) and the crane failed to prevent movement of a test weight into the tank's exclusion zone. The Smart Crane should have recognized Tank #3 as loaded and should have stopped the test weights at the edge of the tank's exclusion zone. "The crane's PLC was subsequently checked and it was determined that it did not indicate Tank# 3 as loaded with a component of concern. The PLC was manually set to identify Tank #3 as loaded with a component of concern and testing resumed. The crane then failed a test on Tank #1. The UT tank did not contain a component of concern (i.e., it weighed < 500 lbs). As such, the operator using the crane should have been able to transfer the test weights into tank's exclusion zone, but the crane's safety interlock stopped the weights at the zone boundary. "Initially, these failures were thought to be caused by errors in conducting earlier tests. If the weights are inadvertently released from the crane within the exclusion zone at the conclusion of a test, the tank status (loaded/unloaded) can be affected. As a result of an earlier corrective action, forklift barriers had been erected to limit the free space around the tanks. It was anticipated that these barriers were possibly interfering with the movement of the weights in/out of the exclusion zone during test. "Tank #1 was reset and all tanks successfully passed the required functional test. Since a definite cause could not be determined but the crane passed the functional test and operations continued. The operators were requested to log the status of the Smart Crane indicating lights as the crane moved from tank to tank. On the night of March 30, 2010, the indicating lights did not provide the correct indication of tank loaded/unloaded status. The operation was immediately shutdown and NCS was notified. On March 31, 2010, Plant Maintenance determined the crane's linear encoder was damaged and not accurately tracking the crane's position. This failure mode allowed the crane to move, but gave a false indication of crane position to the PLC. "This type of failure did not provide the PLC with accurate data to determine the crane's position. In this state, the Smart Crane would not prevent an operator from loading two items of concern in a single tank. This is a failure of the Smart Crane as an IROFS. This determination was reached at 1530 EDT on March 31, 2010. "There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. An operator never attempted to load two components of concern into a UT tank. However, with inaccurate position information, the Smart Crane could not be credited as an IROFS and double contingency could no longer be assured. A criticality was no longer highly unlikely. "Babcock & Wilcox Nuclear Operations Group, Inc. is making this 24 hour report in accordance with 10CFR70, Appendix A(b)(2) - Loss or degradation of items relied on for safety that result in failure to meet the performance requirement of 70.61. "An investigation of this event is ongoing. Corrective actions will be determined as a result of the investigation." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-04-03
45804 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-03-26 | 2010-04-01 11:55 | 2010-04-01 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCES IN GAS CHROMATOGRAPH The following information was obtained from the State of Iowa via facsimile: Two sealed sources in a gas chromatograph (electron capture device) were wipe tested and had removable contamination. The sources will be sent to the manufacturer for disposal. Manufacturer: Agilent Technologies Incorporated Model: G2397A Sources: Each source contained 15 milliCuries Ni-63 (1) Serial: U12585 Leakage: 0.028 microCuries (2) Serial: U12586 Leakage: 0.00549 microCuries Iowa incident number: IA100002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-04-06
45803 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2010-03-30 14:15 | 2010-03-31 16:44 | 2010-03-31 | AGREEMENT STATE REPORT - DAMAGED PORTABLE MOISTURE DENSITY GAUGE The following is a synopsis of information received via facsimile from the Commonwealth of Virginia: On Tuesday, March 30, 2010, a Virginia Department of Transportation (VDOT) employee was using a Model #3440 moisture density gauge (Serial #31899). This gauge was damaged when a compaction roller ran over it. The time of the incident was approximately 2:15 pm. The VDOT inspector had left the gauge unattended to go to her pick-up to get the gauge tools needed to perform a density test. Upon arriving back at the gauge, the inspector noticed that the gauge had been hit by the compaction roller. The location where this event occurred was at a construction site on route 696 in Selma, VA in the Staunton District area, on the South side of the bridge, at Abutment A, station number 101+ 75. The inspector roped off the area, stopped the compaction roller, and called the District RSO from the Staunton District. The District RSO arrived at approximately 4:15 pm. The District RSO took a survey of the area and recorded readings of 1.2 to 1.7 mr/hr. The District RSO checked the source rod and determined that it was still in the shield. The gauge was transported to VDOT's home office at 6200 Elko Tract Road and is now in storage. No personnel were injured as a result of this event. Virginia Event Report ID No.: VA-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2010-04-05
45802 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-03-29 | 2010-03-29 18:07 | 2010-03-29 | AGREEMENT STATE REPORT - FOUND PORTABLE DENSITY GAUGE The following information was received from the State of Colorado via facsimile: "On 3/29/10 this department was notified of a portable density gauge that had been left at a property that had been foreclosed on. We responded to the property and found a CPN MC-3 density gauge. The s/n M390304939. We have taken possession of the gauge and it is now being stored in a secure area. We have contacted the manufacturer who is attempting to track the serial number." According to the NMED database, this gauge was reported stolen in 1999. The gauge contained 50 mCi of Am-241/Be and 10 mCi of Cs-137. NMED Report #990562. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-04-01
45801 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-03-27 09:50 | 2010-03-29 16:06 | 2010-03-29 | AGREEMENT STATE REPORT - FIXED DENSITY GAUGE STUCK SHUTTER The following information was received from the State of Nebraska via facsimile: "The licensee uses fixed industrial gauges for measuring densities in fly ash hoppers at the stations precipitator building. The industrial gauges contain a Cesium-137 sealed source. The Cesium-137 sources were originally installed in 1975 and at the time contained 50 millicuries per source. The sources were manufactured and installed by Kay Ray, Inc. The gauges are Model No. 7700-50. "The licensee was attempting to close the shutter on the fixed gauge prior to performing maintenance. One of the external closure cables was found to be slightly bound up and only partially closed the 'internal' source shutter. The cable closure was reopened, which reopened the source shutter up at the sealed source. Closure was tried again. This time the cable, which connects the handle at the floor to the sealed source shutter mechanism 20 feet above, bent instead of sliding the cable to the closed position. The 'event' happened at 9:50 am and was reported to the station's Shift Supervisor who in turn contacted the plant electricians to make repairs so the precipitator 'tag-out' could continue. By 11:00 am the [shutter] had been closed and the lab contacted to perform a survey to verify the source shutter was now in the closed position. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-04-01
45800 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-03-29 08:08 | 2010-03-29 13:36 | 2010-03-29 | SAFETY EQUIPMENT FAILURE - PROCESS GAS DETECTION SYSTEM FOUND INOPERABLE "At 0808 CDT on 03-29-10, the Plant Shift Superintendent (PSS) was notified that C-333 Unit 5 Cell 6 Process Gas Detection System (PGLD) was found with the READY light not illuminated when Operations were performing the manual test firing required by TSR surveillance requirement SR 2.4.4.1-1. This PGLD System contains detectors that cover Unit 5 cell 6 cell housing and Section 3 of the cell bypass piping. At the time the READY light was discovered not illuminated, these areas were operating above atmospheric pressure. The PGLD System was declared inoperable, TSR LCO 2.4.4.1.A.1 and 2.4.4.1.C.1 were entered and a continuous smoke watch was put in place within one hour. The power supply module was replaced and the system was satisfactorily tested. The system was declared operable at 1030 CDT on 03-29-10. "TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell housing and in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 5 Cell 6 PGLD system inoperable, none of the required cell housing heads were operable. A PGLD head was manually actuated ('smoke tested') and the system would not alarm. Engineering has determined that the system would not have been able to perform its intended safety function. "This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2010-03-29
45799 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2010-03-28 18:52 | 2010-03-28 22:47 | 2010-03-28 | ALERT DECLARED DUE TO FIRE AFFECTING SAFETY RELATED EQUIPMENT "At approximately 1852 hours Eastern Daylight Time [EDT], on March 28, 2010, with the unit operating at approximately 99.5% power, the H. B. Robinson Steam Electric Plant, Unit No. 2, reactor protection system actuated resulting in an automatic trip of the reactor. At about the time of the reactor trip, there was indication of a loss of the power to the Train 'B' emergency bus. The Train 'B' Emergency Diesel Generator started and provided power to the Train 'B' emergency bus. The Reactor Coolant System pressure response after the reactor trip resulted in the actuation of the Safety Injection System. The reduction in Reactor Coolant System pressure allowed the safety injection system to provide flow to the reactor coolant system, although, there was no indication of conditions that would require the safety injection system to provide flow to the reactor coolant system. Specifically, diagnosis of the event determined that a loss of coolant event, steam generator tube rupture, or secondary system break were not occurring. The safety systems that actuated for this event included the Reactor Protection System, the Safety Injection System, both Emergency Diesel Generators started and the 'B' Emergency Diesel Generator provided power to the 'B' Train Emergency Bus, the Auxiliary Feedwater System actuated, and the three main steam isolation valves closed. The Steam Generator Power Operated Relief Valves are being used for decay heat removal because of the closure of the main steam isolation valves. The Startup Transformer is energized and providing power to the 'A' Train Emergency Bus. Investigation of the cause of the reactor trip and associated emergency system actuations is in progress. At the time of the event, it was noted that there was evidence of a fire condition at 4KV bus number 5 located in the Turbine Building. It is currently believed that this is the cause of the transient condition that resulted in the reactor trip and other emergency system actuations. The reactor is currently being maintained in MODE 3, Hot Standby, conditions." "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(A) for ECCS discharge into the RCS and (B) for RPS actuation, and 10 CFR 50.72(b)(3)(iv)(A) for specified system actuation as described. "Additionally, based on an inquiry from the local news media reporter, information regarding this event was discussed with the local media. This contact with the local news media is being reported in accordance with 10 CFR 50.72(b)(2)(xi)." All control rods fully inserted on the trip. Volume Control Tank [VCT] level was not dropping consistent with no reactor coolant system leakage. Pressurizer level and pressure drop was indicative of shrink associated with the Reactor Coolant Pump stoppage and cooldown in one loop. The licensee observed no indication of reactor coolant system leakage from the containment sump water level monitors. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 2340 EDT ON 03/28/10 FROM MIKE DONITHAN TO PETE SNYDER * * * The original Non-Emergency classification was reclassified as an ALERT based on the following: "A fire on 4kV Bus 5 affected 4kV Bus 4 which caused a loss of 'B' Reactor Coolant Pump which caused a Reactor trip and Turbine Trip. "That fire was extinguished without a required event declaration, but a subsequent fire on 4kV Bus 4 required declaration of an ALERT at 2300 [EDT] based on the fire affecting the safety-related 'A' and 'B' DC Buses. The fire was out at 2301 [EDT]. "The primary systems are available and control of the Reactor Coolant System has been maintained. The Safety Injection termination Emergency Operating Procedure has been performed and the general procedure for post-trip stabilization is being performed." The licensee informed state/local agencies and the NRC Resident Inspector. Notified R2DO(Guthrie), IRD(Gott), EO(Blount), ET(Leeds), and R2RA(Reyes). * * * UPDATE AT 0134 EDT ON 03/29/10 FROM BRYAN C. WALDSMITH TO CHARLES TEAL * * * "Event Termination Notice for Event 45799. ALERT declaration is no longer required. "Event Termination Notice: Current plant Conditions are stable and the conditions that required declaration of the ALERT are no longer present. The fire causing the ALERT classification was extinguished at 2301 [EDT]. There was no explosion or steam line break. The last safety-related DC bus ground was identified and cleared at 0001 [EDT]." The licensee informed state/local agencies and the NRC Resident Inspector. Notified R2DO(Guthrie), IRD(Gott), EO(Blount), DHS(Moore), FEMA(Casto), DOE(Moorone), USDA(Hovey), and HHS(Nunn). | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Standby | ALERT | 2 | SC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) | 0 | 2010-03-28
45798 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-03-28 | 2010-03-28 22:13 | 2010-03-29 | PRESS RELEASE DUE TO LUBE OIL FIRE AFFECTING REACTOR FEED PUMP "At 1818 , the control room was notified of a lube oil fire on Reactor Feed Pump Turbine B. The fire brigade was toned out, and the Perry Township Fire Department was notified for assistance. Reactor Feed Pump Turbine B was manually tripped to allow removing the turbine lube oil system from service. The Motor Feed Pump started as expected, and the Reactor Recirculation system lowered reactor power as designed. Currently the reactor is at 68% reactor power following rod line adjustments after the transient was complete. "The fire was reported to be out by the fire brigade leader at 2122. Damage assessment is currently in progress. Two fire brigade members were transported by ambulance to Tri-Point Medical Center with signs of heat exhaustion. Both individuals were verified to be free of contamination prior to transport. "A news release will be made due to local media interest for this event. The NRC Resident Inspector has been notified." * * * UPDATE FROM CHARLES ELBERFELD TO DONALD NORWOOD AT 1636 EDT ON 3/29/2010 * * * "The purpose of this call is to update Event Number 45798. In the notification made on 3/28/10, it was stated that a news release would be made due to local media interest for this event. After further review, it was determined that discussions with the media adequately addressed the interest and that a new release will not be made. The NRC Resident Inspector has been notified." Notified R3DO (Duncan). | 68 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-03-28
45797 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2010-03-27 15:31 | 2010-03-27 20:32 | 2010-03-31 | POTENTIALLY DEGRADED PRESSURIZER LEVEL TAP IDENTIFIED "Arkansas Nuclear One Unit 1 is currently shut down in Mode 6 for refueling outage 1R22. "On March 27, 2010 at 1531 CDT a visual examination of Unit 1 pressurizer level tap 1-RC-1001 A/B indicated evidence of past leakage from the nozzle bore. The leakage is indicated by a small trail of what appears to be dry boron on the lower portion of the nozzle bore accompanied by rust stains on the stainless steel nozzle." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVID THOMPSON TO DONALD NORWOOD AT 1558 EDT ON 3/31/2010 * * * "Update per 10CFR50.72(c). "During the visual examination of the bore of T1 pressurizer level tap nozzle RC-1001 after the inconel nozzle removal, it is evident that corrosion of the carbon steel base material is present. This nozzle location was identified as leaking during the bare metal visual examination." The licensee notified the NRC Resident Inspector. Notified R4DO (O'Keefe). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-03-27
45796 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-03-26 22:45 | 2010-03-26 23:31 | 2010-03-27 | UNUSUAL EVENT DECLARED DUE TO FIRE GREATER THAN 15 MINUTES IN TURBINE BUILDING "An Unusual Event was declared at 2259 EDT due to a fire in the Unit 1 Turbine Building lasting > 15 minutes. The fire was reported by field personnel working in the Unit 1 Turbine Building Condenser Bay at 2245. Smoke was observed coming from the overhead but no visible flames were evident. The source of the fire was from electric blankets used for post-weld heat treatment. The fire was extinguished when the blankets were de-energized. No off-site assistance was required. The Unusual Event was terminated at 2310." There were no injuries and no damage to plant equipment. The fuel for the fire was tape that was used to bind the blankets together. The licensee has notified State and local authorities and will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-03-27
45795 | 0 | DOW CHEMICAL COMPANY |  |  |  |  | 2010-02-26 | 2010-03-26 14:37 | 2010-03-26 | MISSING MATERIAL IDENTIFIED DURING ANNUAL INVENTORY A 5.862 mCi sample of C-14 in a dipropylene glycol propyl ether mix was identified as missing on 2/26/10 during the annual physical inventory of radioactive materials. The sample had been present in its approved storage location during the 2009 physical inventory. The material was lost sometime between March 2009 and February 2010. The licensee has taken the following actions to locate the material: - Spoke with all authorized users to identify location or usage within the last year; - Detailed search of all storage areas and radioisotope-approved labs; and - Checked waste disposal records. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-03-26
45794 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-03-25 11:35 | 2010-03-26 13:36 | 2010-03-26 | PROCESS GAUGE SHUTTER MALFUNCTION The following information was received from the State of Nebraska via facsimile: "The licensee uses fixed industrial gauges for measuring densities in fly ash hoppers at the station's precipitator building. The industrial gauges contain a Cesium 137 sealed source. The Cesium 137 sources were originally installed in 1975 and at the time contained 50 millicuries per source. "The sources were manufactured and installed by Kay Ray Inc. "The gauges are Model No. 7700-50. "The licensee was attempting to close the shutter on the fixed gauge prior to performing maintenance. One of the external closure cables was found to be slightly bound up and only partially closed the 'internal' source shutter. The cable closure was reopened, which reopened the source shutter up at the sealed source. Closure was tried again. This time the cable, which connects the handle at the floor to the sealed source shutter mechanism 20 feet above, bent instead of sliding the cable to the closed position. "This 'event' happened at 11:35 am and was reported to the station's Shift Supervisor who in turn contacted the plant electricians to make repairs so the precipitator 'tag-out' could continue. By 11:45 am the cable had been closed and the lab contacted to perform a survey to verify the source shutter was now in the closed position. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-03-31
45793 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2010-03-25 22:55 | 2010-03-26 03:05 | 2010-03-26 | STANDBY GAS TREATMENT DECLARED INOPERABLE AFTER DISCOVERY OF OPEN DEMISTER DOOR "System Affected: Standby Gas Treatment (SBGT) "Condition: Demister Door Discovered open rendering both trains of SBGT INOP "At 2255 [EDT] on 3/25/2010, a Demister Door on 'B' Train of Standby Gas Treatment (SBGT) was found open. The door was closed upon discovery. The door was opened during performance of a scheduled surveillance during the dayshift and it appears that the door was not closed at the completion of work. With this door being open the 'B' Train of SBGT was INOP. Due to the physical configuration of the SBGT System it cannot be immediately verified that the 'A' Train of SBGT would have been able to perform its Safety Related Function since there is a probability that it could have drawn suction through the demister door of the 'B' Train and a normally open crosstie between the Trains. A 10 CFR 50.72 notification is conservatively being made based on the information currently available. "This condition has no impact on the health and safety of the public. "Both trains of SBGT are currently operable." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-03-26
45792 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-03-25 22:39 | 2010-03-26 01:02 | 2010-03-26 | OFFSITE NOTIFICATION DUE TO PIPING LEAK THAT CANNOT BE CLEANED UP WITHIN 24 HOURS The licensee made a 15 minute notification to the New Jersey Department of Environmental Protection due to a piping leak that cannot be cleaned up within 24 hours. The leak is on piping from the steam generator blowdown system to the non-radioactive waste bin and is leaking onto the asphalt beneath the piping. The leakage rate was approximately 1/2 gal/minute upon discovery but has since been stopped. There is no known primary to secondary leakage through the steam generator. No contact with the groundwater is suspected. The licensee has taken actions to divert leakage to the waste holdup system. The licensee will be notifying authorities in the Lower Alloways Creek Township and the NRC Resident Inspector. | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-03-26
45791 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-03-25 15:40 | 2010-03-25 20:18 | 2010-04-23 | HIGH HEAD SAFETY INJECTION INOPERABLE DUE TO VOIDS IDENTIFIED IN PIPING "At 1540 on 3/25/2010, engineering identified a gas void in the Unit 4 B Cold Leg High Head Safety Injection (HHSI) pipe which exceeded the station's allowable gas accumulation acceptance criteria. This condition rendered the cold leg injection flow path inoperable and required entry into Technical Specification 3.0.3 at 1540. The void was immediately vented and Technical Specification 3.0.3 was exited at 1750." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0830 EDT ON 04/23/10 FROM MARK JONES TO S. SANDIN * * * The licensee is retracting this report based on the following: "At 2018 on 3/25/2010, an event notification (#45791) was reported to the NRCOC as follows: "'At 1540 on 3/25/2010, engineering identified a gas void in the Unit 4 B Cold Leg High Head Safety Injection [HHSI] pipe which exceeded the station's allowable gas accumulation acceptance criteria. This condition rendered the cold leg injection flow path inoperable and required entry into Technical Specification 3.0.3 at 1540. The void was immediately vented and Technical Specification 3.0.3 was exited at 1750 [on 3/25/2010].' "The decision to enter TS 3.0.3 was based on the plant procedural guidance and the results of ultrasonic testing. "Following the discovery of the void, the failure investigation process required that an engineering evaluation be performed. The evaluation performed calculations to determine if, during a hypothetical HHSI pump start with the measured gas void present, the resulting water hammer conditions would cause the Unit 4 HHSI piping design pressure or Unit 4 HHSI piping supports design loading to be exceeded, thereby challenging the integrity of the Unit 4 HHSI discharge flow path to the reactor coolant system (RCS). "The engineering evaluation determined that under the specific conditions in the Unit 4 HHSI piping on 3/25/2010: "(1) Unit 4 HHSI piping design pressure would not have been exceeded should the HHSI pumps have started. "(2) Unit 4 HHSI piping support design loading would not have been exceeded should the HHSI pumps have started. "Therefore, the analysis of the void concluded that both the pipe and the support structural integrity would have withstood the pressure and axial loads due to the gas void and the HHSI system would have continued to perform its safety related function. "The Unit 4 HHSI system discharge flowpath to the RCS remained operable at all times. Technical Specification 3/4.5.2, ECCS SUBSYSTEMS: Tavg GREATER THAN OR EQUAL TO 350 degrees F, Limiting Condition for Operation was satisfied at all times. Entry into Technical Specification 3.0.3 was not required at any time before or after the void discovery. The Unit 4 HHSI system remained capable of fulfilling the design safety function to mitigate the consequences of an accident on Unit 4, and an immediate notification to the NRCOC, discussed in 10 CFR 50.72(b)(3)(v)(D), was not required." The licensee informed the NRC Resident Inspector. Notified R2DO (Ayres). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-03-25
45790 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2010-03-25 10:28 | 2010-03-25 18:53 | 2010-05-24 | HIGH PRESSURE SAFETY INJECTION INOPERABLE DUE TO VOIDS IDENTIFIED IN SUCTION PIPING "At 1028 CDT today 3/25/2010, a rejectable void was found in one of the suction lines (cooled suction line) to the B HPSI [High Pressure Safety Injection] pump. The main suction line is water filled. The piping was declared inoperable and the appropriate technical specification was entered. At 1357 CDT the void was cleared from the cooled suction line and the piping was declared operable. Subsequently, at 1409 CDT a similar rejectable void was discovered in the other cooled suction line for HPSI pumps A and C. The piping was declared inoperable. The appropriate technical specification was entered. At 1447 CDT the void was cleared and the piping was declared operable. Due to the close proximity of these occurrences the station is conservatively reporting this as a safety system functional failure as it appears that both trains of HPSI cooled suction were inoperable at the same time." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO VINCE KLCO ON 5/24/10 AT 1517 EDT * * * "Subsequent to making this event notification a detailed analysis of the event was performed by FAUSKE / Westinghouse Engineering. This evaluation determined the quantity of gas voiding in the piping, the duration of time the pump(s) would be subjected to gas voiding and potential effects on the piping support design loading. The hydraulic data was then reviewed by the HPSI pump manufacturer (Sulzer) to determine the effect on pump performance. Based on these evaluations, it has been determined that the HPSI pumps were not degraded, and that they were capable of performing their design basis function at all times and were operable. Therefore, this event does not meet the 10 CFR 50.72 reporting criteria and the notification is being retracted." The licensee notified the NRC Resident Inspector. Notified the R4DO (Shannon). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-03-25
45789 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-03-25 16:27 | 2010-03-25 18:18 | 2010-03-25 | AUTOMATIC REACTOR SHUTDOWN DUE TO MAIN TURBINE TRIP "At 1627 EDT on 3/25/10, the reactor mode switch was taken to shutdown following an automatic scram due to a main turbine trip. The scram was uncomplicated, and all control rods fully inserted into the core. The lowest reactor vessel water level reached was 136 inches, and as expected, HPCI & RCIC did not actuate. No safety relief valves (SRV) actuated. Reactor water level is being controlled in the normal band using the control rod drive and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The cause of the Main Turbine Trip is under investigation. "At the time of the scram all Emergency Core Cooling Systems and [Emergency Diesel Generators] EDGs were operable, and no safety related equipment was out of service." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 63 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-03-25
45788 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-23 | 2010-03-25 15:27 | 2010-03-25 | AGREEMENT STATE REPORT - IMPROPER DOSAGE GIVEN DURING MEDICAL TREATMENT The following information was received by e-mail: "On March 25, 2010, Mayo Clinic notified the Minnesota Department of Health of an HDR [High Dose Rate After Loader] medical event. The patient was prescribed four fractions of 4 Gy for a biliary HDR treatment. The catheter had been placed and imaged. A dummy source was pushed into the catheter until it met resistance that was assumed to be the end of the catheter. In fact, the resistance was a tight bend approximately 17 centimeters (6.69 inches) short of the end. "The distance that was thought to be the end of the catheter was incorrectly used for the treatment distance and the patient was subsequently treated. Prior to treatment the following day, a dummy source was again inserted. That source extended beyond the programmed distance. An x-ray revealed that the end of the catheter was beyond the initial treatment location. "For the first two fractions, the HDR source was 17 cm from its intended treatment location. This resulted in the tumor receiving only 30 percent of the intended fractional dose and resulted in the duodenum (where the HDR source was located) receiving more than 50 rem and more than 50 percent of planned." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2010-03-31
45787 | -1 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-12-14 | 2010-03-24 12:30 | 2010-04-06 | AGREEMENT STATE REPORT - FETAL EXPOSURE IN EXCESS OF 500 MILLIREM DURING A PET/CT SCAN The following information was obtained from the State of Colorado via facsimile: "The Department received notification on March 23, 2010, of a fetal exposure in excess of 500 milliRem from a PET/CT Scan. The licensee, PET Imaging of Northern Colorado, License No. 1105-0, is located in Fort Collins, Colorado. The licensee reported that on December 14, 2009, a female patient received 17.4 mCi of F-18 and underwent a PET/CT scan. The patient had indicated that she was not pregnant on her medical history questionnaire and told the technologist she was not pregnant prior to the scan. Later, the patient's physician notified the licensee that the patient was indeed pregnant at the time of the scan. "A consulting medical physicist calculated the total dose to the fetus from the PET/CT scan as 2.6 Rem (26 mGy). However, the medical physicist did not report the individual dose from the F-18 component alone, and this information has been requested from the licensee. "The licensee's authorized user physician reported that the risk of abnormality for the fetus is considered to be negligible per the guidance from the American College of Radiology Practice Guidelines. "No other details are available at this time." * * * RETRACTION FROM ED STROUD TO PETE SNYDER AT 1550 ON 4/6/10 * * * The following information was obtained from the State of Colorado via facsimile: "Following a full investigation of the incident, the fetal exposure was determined to be below the NRC's reporting requirement of 5 REM." Notified R4DO (Proulx) and FSME EO (VonTill). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-03-29
45786 | -1 | WASHINGTON UNIVERSITY ST. LOUIS |  |  |  |  | 2010-02-04 | 2010-03-23 18:10 | 2010-07-02 | EXTREMITY OVEREXPOSURE TO FINGERTIPS The licensee's RSO reported that on March 9, 2010, a report was received from Landauer indicating that a technician that worked at the licensee's facility received a left hand ring dose of 11,900 millirem. The right hand ring dose was 4030 millirem. The licensee began an investigation into these readings and determined that the technician may have had a high extremity dose to the finger tips. After interviews with the technician and reconstruction of the event the licensee now believes that the technician may have received a dose between 50 rem and 400 rem over a 10 square-centimeter area of his fingertips as the result of improper handling of the radionuclide Bromine-76. The dose exposure to the fingertips was calculated using the Varskin computer code. The technician was handling 32 millicurie vials of Bromine-76 between February 4 and February 5, 2010, related to research activities at Washington University. Normally, the vials would be handled with a long-handled tool with shielding. For reasons uncertain, the technician is believed to have directly handled the vials on several occasions. The technician has approximately six years of work-history with this type of activity. The technician experienced no observable effects from the exposure. The technician has not worked with radioactive materials since mid-February. The Landauer whole-body deep dose badge reading for the period in question was 25 millirem. * * * RETRACTION FROM SUSAN LANGHORST TO PETE SNYDER ON 7/2/2010 at 1631 EDT * * * The licensee reconstructed the dose for the event after conversing with NRC Region 3. The licensees reconstructed dose estimate was 26 rem which is not over the dose limit of 50 rem. Therefore, this event is not reportable. Notified R3DO (Daley), FSME EO (Lueman). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2010-03-23
45785 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-03-22 09:30 | 2010-03-23 09:20 | 2010-03-23 | LOSS OF ONE OF TWO REQUIRED CONTINGENCY CONTROLS "At approximately 0930 [EDT] on Monday, March 22nd, an operator noticed that a waste collection bag in the dry conversion area had torn away from its receptacle as it is designed to do when the mass of waste exceeds the specified threshold. The operator lifted the bag up and found it to be heavier than normal. The operator then transferred the bag to the decontamination area to sort through the contents and determine what had been placed in the bag per procedure. During the sorting process, the operator found two vacuum cleaner bags that contained uranium. Upon discovery of the vacuum bags, the operator promptly notified Nuclear Safety staff, who further notified Operations Management and the EHS Manager. Upon investigation it was determined that 8.7 kg of UO2 was present in the two vacuum bags, which is less than the criticality safety limit of 25kg UO2 specified in the Criticality Safety Analysis. As a result, no unsafe condition existed. "Since uranium was placed directly into the waste collection receptacle, one of the administrative requirements for double contingency was violated. The second control functioned as designed and the mass of uranium within the waste collection receptacle was controlled to less than the safe mass limit. Therefore, this event resulted in a failure of an administrative requirement necessary to meet double contingency and is being reported per internal procedural requirements. "As an immediate corrective action, the material was transferred into a favorable geometry 3-gallon can per procedure. In addition, a stand down of DCP operations was promptly performed to inform operators of the issue and retrain on the waste collection control requirements. All subsequent shifts have been briefed of the issue and retrained on the control requirements prior to returning to work. "The double contingency controls required include (1) only contaminated items may be placed in a waste container. No uranium or containers with unknown uranium contents are allowed in the waste collection containers and (2) waste bags are designed to physically tear from their holders prior to accumulating greater than a safe mass in the bag. Material may not be placed in the bag after it has torn from the holder. "Uranium was removed from the waste collection bag and placed into a 3-gallon can, which is a favorable geometry. "Immediate corrective actions are complete. Investigation of the event and implementation of long term corrective actions are pending. "At no time did an unsafe condition exist as the mass of uranium within the waste collection receptacle was less than the safe mass limit." The licensee will notify NRC Region 2, and the North Carolina State Department of Radiation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.74 APP. A |  |  |  | 0 | 2010-03-23
45784 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2010-03-22 18:11 | 2010-03-22 22:05 | 2010-03-23 | NOTIFICATION OF UNUSUAL EVENT DUE TO UNIDENTIFIED LEAKAGE GREATER THAN 10 GPM "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirement of 10CFR50.73. "On March 22, 2010 at approximately 1756 MST, Palo Verde Nuclear Generating Station (PVNGS) Unit 1 identified a rising level and temperature trend in the Reactor Drain Tank (RDT). PVNGS Unit 1 was in Mode 1 (Power Operation) at 93% power with normal RCS temperature and pressure at the time of discovery. Containment temperature and humidity trends are normal. Technical Specification Limiting Condition for Operation 3.4.14 (RCS Operational Leakage), Condition 'A' was entered at 1811 due to unidentified leakage >10 gpm and the LCO allows 4 hours to restore leakage to <1 gpm. Also at 1811, a Notification of Unusual Event (NOUE) was declared due to unidentified leakage >10 gpm (MU5.1). PVNGS Unit 1 remains at power with all normal systems in operation; periodic pumping of the RDT is occurring. "No automatic or manual reactor protection system or engineered safety features actuations occurred and none were required. There were no other component failures, testing or work in progress that contributed to the leak. The leak is located within the containment building, therefore there is no release of radioactivity to the environment and no impact to the health and safety of the public. There is no elevated RCS activity and heat removal is via normal steaming to the main turbine condenser. The electric grid is stable. "Current plans are to enter containment and identify the source of leakage. State and Local authorities have been notified. The NRC Senior Resident Inspector has been notified." The licensee notified the following state and local agencies: Maricopa County Sheriff, Arizona Department of Public Safety, Buckeye Police Department, Arizona Radiation Regulatory Agency, Arizona Division of Emergency Management, and the Maricopa County Emergency Management Agency. * * * UPDATE FROM BRAD ROBINSON TO DONG PARK AT 0028 EDT ON 3/23/2010 * * * At 2112 MST, the shift manager advised that the Pressurizer Main Spray Valve, 100E, packing leakage has been manually isolated. As of 2125 MST, the level trend in the RDT has stabilized. The licensee is working to verify the leakage rate, and remains in an Unusual Event. The plant remains stable in Mode 1 at 93% power. The licensee has notified the NRC Resident Inspector, and the NRC Resident Inspector remains on site. * * * UPDATE FROM BRAD ROBINSON TO DONG PARK AT 0121 EDT ON 3/23/2010 * * * At 2146 MST, the licensee exited Technical Specification Limiting Condition for Operation 3.4.14, RCS Operational Leakage. At 2219 MST, the Unusual Event was terminated. The licensee will notify the NRC Resident Inspector. Notified R4DO (Deese), NRR EO (Brown), IRD (McDermott), DHS (Moore), and FEMA (Canupp). | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-03-22
45783 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2010-03-22 13:39 | 2010-03-22 20:50 | 2010-03-22 | FITNESS FOR DUTY REPORT - CONTRACT SUPERVISOR A contract supervisor had a confirmed positive for drugs as a result of a pre-access fitness for duty test. The individual's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 92 | 100 | 100 | 92 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2010-03-22
45782 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-19 | 2010-03-22 17:36 | 2010-04-22 | AGREEMENT STATE REPORT - WELL LOGGING TOOL EJECTED DURING WELL BLOW-OUT The following information was received from the State of Texas via e-mail: "Weatherford personnel were logging a well in Howard County, Texas when a blow out occurred. The logging tool was at 3500 feet when the tool and wireline were ejected from the well bore. The blow out preventer did not stop the tool and wireline from being ejected onto the surface. The crew evacuated the drilling rig due to the hazards associated with the high downhole pressure. Initially it was unknown whether the logging tool was still in the hole. A logging company manager conducted radiation surveys and found the tool, with the sources still in place near the logging truck. The sources were secured in their transport shields and returned to the company office for leak testing. At this point, there is no estimate of exposures to personnel at the well site." Texas Report # I-8726 * * * UPDATE ON 04/22/2010 AT 1524 EDT FROM A. TUCKER TO R. ALEXANDER * * * The following update was received from the State of Texas via e-mail: "The licensee notified the Agency [Texas Department of State Health Services] that leak test results on the cesium and the americium-beryllium sources were satisfactory. The licensee stated that a visual examination of the sources did not find any physical damage." Notified R4DO (J. Whitten) and FSME EO (C. Einberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-03-25
45781 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-19 23:20 | 2010-03-20 01:35 | 2010-03-26 | AGREEMENT STATE REPORT - THEFT OF LICENSED MATERIALS The following information was received by e-mail: "On March 19, 2010 at 2350 hours, the Agency [Texas Department of State Health Services-Radiation Branch] was notified by the licensee's Radiation Safety Officer (RSO) that 120 milliCuries of Iridium (Ir)-192 was stolen from one of their trucks parked at a Wal-Mart parking lot in Alice, Texas at about 2320 hours. The Ir-192 was contained in six, 20 milliliter vials each containing 20 millicuries (15 grams) of Ir-192 in the form of zero wash [isotope tracer]. Each vial was placed into a labeled lead pig and each pig was then shrink wrapped. The six pigs were then placed into a zip lock bag. The zip lock bag was placed into a tool box in the back of the pick up truck. The licensee stated that the employee had stopped at the Wal-Mart on their way to a job site in south Texas. The RSO stated that the tool box was not locked and other items were stolen from the tool box. The tool box did not have any labeling on it. The RSO stated that the employee did not perform a radiation survey of the pigs, but he estimated the dose rate to be about 100 millirem per hour on the outside of the tool box. Local law enforcement was notified of the theft. Additional information will be provided as it is received." Texas Incident Number: I-8730 * * * UPDATE FROM ART TUCKER (VIA EMAIL) TO HOWIE CROUCH @ 1017 EDT ON 3/26/10 * * * "At 1730 on March 24, 2010, Alice police department notified the Agency that they had information regarding the location of the radioactive material. The material was subsequently found at a private residence. The material was inspected, surveyed, and returned to the licensee. The shrink wrap around each of the lead pigs was still intact, indicating the glass vials containing the radioactive materials had not been accessed. The Agency is performing dose estimates for the individuals who lived in the home." Notified R4DO (Deese), FSME EO (McIntosh), and FSME (Mauer). Notified ILTAB via email and Mexico via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-03-24
45780 | 0 | SOURCE PRODUCTION & EQUIPMENT CO. |  |  |  |  | 2010-03-19 | 2010-03-19 15:15 | 2010-03-19 | SELENIUM-75 SOURCE MISSING FROM SHIPMENT A representative of Source Production & Equipment Company (SPEC) notified the NRC that an 8 curie Selenium-75 source was missing from a shipment of 6 sources received at SPEC sometime around March 12, 2010. The shipment of 6 total special form (solid) Se-75 sources were shipped from Gilligan Engineering in Prudoe, England on March 9, 2010 and 5 of the 6 sources were received by SPEC. The licensee considers the source missing at this time but has not exhausted its search. The State of Louisiana has been notified. In addition, SPEC has contacted the shipment carrier to investigate the shipment tracking and determine if the single missing source might have been misdirected. The shipment was believed to have entered the US in Memphis, TN via air freight from England. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | LA | MAT | [5 empty] | 0 | 2010-03-19
45779 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2010-03-15 12:43 | 2010-03-19 14:07 | 2010-03-19 | INADVERTENT START OF EMERGENCY DIESEL GENERATOR "At 12:43 on Monday, March 15, 2010, the 103 Emergency Diesel Generator (EDG) was inadvertently started during standby circuit checks. The standby circuit checks test was a planned evolution that was not intended to cause a start of the EDG. Following the start of the EDG, the standby circuit check test was stopped and the running checks for the diesel were completed satisfactory at 12:50. The EDG was secured at 13:03, after functioning successfully. "The EDG was not started by a valid initiation signal. A valid initiation signal is degraded or loss of voltage to the Power Board (PB) 103. Also, the EDG output breaker did not close since the PB 103 was not deenergized. "This event is not considered an LER. This report is being made under 10 CFR 50.73(a)(2)(iv)(A) (requires reporting within 60 days when a event or condition that resulted in manual or automatic actuation of the EDG AC Electrical Power Systems, including EDG System occurs.) "EDG 103 is the train that actuated. EDG 103 actuation was not complete since breaker did not close. EDG 103 started and remained operable throughout the event; output breaker would have closed and supplied PB 103 if required. "The event has been entered into the corrective action program. "There are no other adverse impacts to the station based on this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-03-19
45778 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-19 | 2010-03-19 12:50 | 2010-03-22 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED PROCESS GAUGE The following information was received via E-mail: "On March 19, 2010, at 1130 hours, the Agency [Texas Department of State Health Services] received a telephone call from the licensee [Structural Metals, Inc. DBA: CMC Steel Texas] stating that the shutter on one of their gauges was stuck. The gauge houses a Cobalt (Co)-60 source. The shutter stuck in the open position, [which is] the normal operating position. Dose rates taken in the area were normal, and the licensee has contacted a repair company to have the shutter fixed sometime next week. The licensee will not be using the gauge until it is fixed, and has agreed to update the Agency as information is received. "Texas Incident #: I-8725" * * * UPDATE ON 3/22/10 AT 1442 FROM TEXAS (ROBERT FREE) TO HUFFMAN * * * The following information was received from the State of Texas via e-mail: "A Co-60 gauge [was reported by the licensee to have been] damaged by molten steel during a pouring operation. The area was secured from personnel entry until the licensee authorized to conduct recovery operations arrives on site today to begin recovery operation. No model or serial number is available at this time. [The Texas Dept. of Health Radiation Branch] will provide an update as more complete information is available." * * * UPDATE ON 3/22/10 AT 1744 FROM TEXAS (ROBERT FREE) TO HUFFMAN * * * The following information was received from the State of Texas via e-mail: "The event description should indicate that there was molten metal splashed or poured over the gauge. The gauge shutter mechanism remained open. The company, Structural Metals (CMC), did not know the status of the gauge until today. The gauge was recovered by a licensed contractor and the shielding was found to be intact. The only damage to the gauge was the mechanism used to open and close the shutter. The gauge will be repaired or replaced." R4DO (Deese) and FSME EO (Luehman) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-03-24
45777 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-17 | 2010-03-19 12:26 | 2010-06-09 | AGREEMENT STATE REPORT - DISCOVERY OF A SEALED SOURCE IN A LOAD OF SCRAP METAL The following information was received via E-mail: "The following are the findings of the Arkansas Department of Health, Radioactive Materials Program, concerning Event Number 03-10-01 involving an unknown radioactive source at Nucor-Yamato Steel in Blytheville, Arkansas. The Department was contacted on March 17, 2010 indicating that a sealed source had been discovered in a load of scrap metal. The isotope/activity of the sealed source is unknown at this time. It was also stated that survey readings were 50 mR/hr. Health Physicists from the Arkansas Department of Health went to Nucor-Yamato Steel. [Upon discovery], the cylinder-shaped source had been placed in a metal bucket and then put in a 55 gallon metal drum. Readings inside the barrel with the survey meter probe close to the source, the actual readings were 100-140 mR/hr. After all the shielding was in place, a survey was taken with the highest reading being 0.7 mR/hr at the surface of the drum, and the T.I. index [transport index] was 0.2 mR/hr. The drum containing the source was secured in the back of the state vehicle and transported to the Arkansas Department of Health, Radiation Control in Little Rock, Arkansas. "The source is awaiting pickup by American Radiation Services for transport to their storage location in New Orleans, Louisiana. Further information and identification of the isotope and activity are pending the report from the vendor. "The State of Louisiana has been notified." * * * UPDATE FROM KAYLA AVERY TO HOWIE CROUCH VIA EMAIL @ 1627 EDT ON 6/9/10 * * * "An employee of American Radiation Services, Inc. (ARS) arrived in Little Rock on March 19, 2010 to retrieve the unknown source. The source was packaged and transported to Port Allen, Louisiana where ARS determined that it was a Cesium-137 source of approximately 0.61 mCi. The manufacturer, model number and serial number are still unknown. ADCO Services, Inc. picked up the source from ARS on April 30, 2010 and transported it to Tinley Park, Illinois where it is waiting disposal. "The Arkansas Department of Health considers this incident to be closed." Notified R4DO (Powers) and FSME EO (Mauer). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2010-03-24
45776 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2010-03-18 | 2010-03-19 08:37 | 2010-03-19 | DEFECT CONCERNING FAILURE OF RELAY TO RELEASE WHEN DE-ENERGIZED The following was received via facsimile: The defect prevents the relay contacts from changing state when required during postulated events. This failure could preclude components from going to their desired accident state upon receipt of an engineered safety features actuation signal. There have been no reports to date of relay contacts failing to properly change state when the relay goes from a deenergized to an energized state. Westinghouse shipped Palo Verde a total of 120 Cutler Hammer Type ARD 660UR DC Relays. Westinghouse Repair, Replacement and Automation Services (RRAS) has been working with Palo Verde and Eaton-Cutler Hammer to identify and correct the cause of these relay failures. POC: J. A. Gresham, Secretary Safety Review Committee Westinghouse Electric Company LLC Nuclear Services P.O. Box 355 Pittsburgh, Pennsylvania 15230-0355 (412) 374-4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-03-19
45775 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-03-18 18:16 | 2010-03-18 20:21 | 2010-03-25 | LOSS OF TONE ALERT RADIOS "At approximately 1816 EDT, loss of prompt notification system (tone alert radios) occurred. Security notified Jacksonville National Weather Service and Information Technology to investigate. Jacksonville National Weather Service determined a problem with their equipment and prompt notification system (tone alert radios) was returned to service at approximately 1845 eastern time. Security has notified state and local agencies of prompt notification system (tone alert radio) outage and return to service." The licensee has notified the NRC Resident Inspector. Licensee also notified State and local agencies. * * * RETRACTION FROM FRANK GORLEY TO PETE SNYDER AT 1535 ON 3/25/10 * * * "On 3/18/10 at approximately 11:40 am we started receiving an 'off-air' alarm for the Plant Hatch NOAA Weather Radio. Initially we determined that a loss of the prompt notification system had occurred due to the alarm and consultation with Jacksonville National Weather Service, Ref. 10 CFR 50.72 (b)(3)(xiii). "NOAA personnel subsequently provided information to Plant Hatch personnel at which time it was learned that even though 'off-air' alarms were received for the NOAA Weather Radio, the radio was never off the air. While NOAA personnel were troubleshooting the system the broadcast was switched over to a digital backup system that continued to have the capability to warn the public. There was a problem noted in the broadcast that was causing several seconds of silence in the broadcast signal. While on the digital backup, the notification capability was maintained. The broadcast had been returned to the primary system today. During the time these activities were underway, broadcast capability to the public was never lost. "Based on this information, Plant Hatch is entering a Notification of Retraction for the 8 hr. report documented to the NRC Event Number 45775, as entered on 3/18/10." The licensee will notify the NRC Resident Inspector. Notified R2DO (Franke). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Startup | Power Operation |  | Startup | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-03-18
45774 | 0 | TRIAD ENGINEERING |  |  |  |  | 2010-03-18 15:00 | 2010-03-18 17:24 | 2010-03-19 | FOUND TROXLER MOISTURE-DENSITY GAUGE At about 1500 EDT, while traveling on US Rt. 19 South of Arnettsville, an employee of Triad Engineering [license number 45-18209-02] found a Troxler 3430 moisture-density gauge (S/N 24513) on the highway. The employee moved the gauge out of traffic and flagged down a state police officer. The police officer made some calls in an attempt to determine if anyone had reported the gauge lost. After negative results, the police officer left the gauge in the care of the Triad Engineering employee. The employee called his supervisor and was told to bring the gauge into the office where it could be adequately secured. After arriving at the office, calls were made to Troxler to determine to whom the gauge belonged. Troxler listed the gauge as belonging to CTL Engineering in Morgantown, West Virginia. Triad Engineering called CTL Engineering to tell them they had found their gauge. About 1710 EDT, an employee of CTL Engineering arrived at the Triad Engineering office and took possession of the gauge. * * * UPDATE FROM TIM GOWARTY TO DONG PARK @ 1040 EDT ON 3/19/10 * * * CTL Engineering, Inc. confirmed that a Troxler 3430 moisture-density gauge fell out of the back of their truck at around 1500 EDT, 3/18/2010, while on US Rt. 19. After an employee from CTL Engineering picked up the gauge from Triad Engineering, the gauge was transported to their facility. The gauge did not appear to be damaged, and the gauge is scheduled to be inspected. The driver of the truck will be required to take the four hour Troxler refresher course. Notified R1DO (Burritt), FSME EO (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-03-18
45773 | 0 | ACCURATE NDE & INSPECTION |  |  |  |  | 2010-03-17 12:10 | 2010-03-17 14:35 | 2010-03-17 | LOSS OF SEVEN CURIE SOURCE FROM RADIOGRAPHY CAMERA The licensee was conducting non-destructive testing (radiography camera x-ray) on an oil platform in the Gulf of Mexico. While the radiography was taking place at night, over grating, the pigtail disconnected from the camera and dropped through the grating into the Gulf of Mexico. The area where the source fell is about 6 miles from shore, East Cam 33 CS, and the depth of the water was about 40 feet. Licensee is not going to try to retrieve the source. The camera source is 7 Ci of Ir-192, s/n QD-1302. The camera is a Spec 150, s/n 814. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-03-17
45772 | 0 | NJ DEPT OF ENVIRONMENTAL PROTECTION |  |  |  |  | 2010-03-11 06:15 | 2010-03-17 12:42 | 2010-03-17 | AGREEMENT STATE REPORT - CONTAMINATED PACKAGE The following information was obtained from the State of New Jersey via facsimile: "The licensee reported that a package containing 810 mCi of bulk F-18 was shipped in a Yellow II, Type 7A container (this was an ammo can) from Cardinal Health's East Rutherford, NJ facility at 0500 EST on March 11th (last Thursday) to their Plainview, NY facility. Licensee stated that when the shipment was received at 0615 EST, the package surface reading was 100 mR/hr, exceeding the limit of 50 mR/hr for a Yellow II labeled package. Licensee indicated that removable contamination of 300,000 cpm (estimated 1,500,000 dpm with 20% instrument efficiency) was identified on the outer handle of the package. "The driver (who is employed by the Plainview, NY facility) was found to have a contaminated left hand and some contamination in the vehicle. The licensee estimated the employee's highest exposure to be 4 rem to the left hand." New York State Department of Health was notified by the licensee. New Jersey will be conducting an investigation of this incident to validate the contamination and exposure levels. NJDEP Incident ID #343512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2010-03-22
45771 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2010-03-17 11:30 | 2010-03-17 12:27 | 2010-04-09 | ERDS AND SPDS OUT OF SERVICE DUE TO PROCESS COMPUTER UPGRADE "During the current Unit 2 refueling outage, the Unit 2 plant process computer system will be taken out of service for approximately three weeks to support a planned modification which will install a new (upgraded) plant process computer system. During this timeframe, ERDS [Emergency Response Data System] and SPDS [Safety Parameter Display System] will be unavailable on Unit 2 which will remain in a shutdown condition. The computer outage will have no impact on Unit 1. Should the need arise, plant status information will be communicated to the NRC using other available communication systems. The computer outage is expected to commence at 1130 CDT on 3/17/2010 and the process computer will be restored prior to Unit 2 startup, currently scheduled for 4/11/2010. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a Major Loss of Assessment Capability." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM KENNETH OHR TO CHUCK TEAL AT 1410 ON 4/9/10 * * * "U2 [Unit 2] ERDS and SPDS have been restored. Acceptance testing was completed on 4/8/2010." Notified R3DO (Peterson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-03-17
45770 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2010-03-16 15:50 | 2010-03-16 20:24 | 2010-03-16 | OFFSITE NOTIFICATION TO OSHA DUE TO DEATH OF A SUPPLEMENTAL EMPLOYEE "Today at approximately 1550 CDT, a supplemental worker collapsed. Supplemental personnel were gathering for a brief on an upcoming task to uncrate construction material outside the plant security area. Site personnel responded, provided first aid, and the individual was transported to a hospital for advanced medical care. Following treatment, he was pronounced dead at 1635 CDT of an apparent heart attack. [Occupational Safety and Health Administration] (OSHA) will be notified of this occurrence." The licensee has notified the NRC Resident Inspector. | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-03-16
45769 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-03-15 16:00 | 2010-03-16 19:01 | 2010-03-16 | AGREEMENT STATE REPORT - TWO PROCESS GAUGES WITH STUCK SHUTTERS The following report information was received from the State of Nevada Dept of Health via e-mail: "On March 15, 2010, at 1600 hrs, the [Nevada] Radiation Control Program was notified by phone of two stuck shutters on fixed gauges at the Round Mountain Gold Corporation Smoky Valley Common Operation Mill. [The gauges with the stuck open shutters] were identified during the 6 month inspection on March 10, 2010. Both sources are 15 feet overhead and functioning as normal. "The licensee indicated that the RSO was briefed about the situation, and he documented, conducted safety briefings for all who work in the area, and posted signs to keep staff away from the vicinity of the stuck shutters. "Manufacturer is scheduled to repair the stuck shutters. "The Radiation Control Program will investigate this further and update this report. Violations will be cited as appropriate." Ronan Engineering Model # SA1-C5; Serial #M4882; 1.0 Ci (37 GBq) Cs-137 Source # DE4220 Ronan Engineering Model # SA1-C10; Serial #JJ-593; 0.1 Ci (3.7 GBq) Cs-137 Source # DE4620 Nevada Event Report - NV100004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-03-19
45768 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-03-15 08:10 | 2010-03-15 14:45 | 2010-03-15 | EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE DUE TO COMPUTER FAILURE "On March 15, 2010, at approximately 0810 hours EDT, the plant computer system (ICS) was taken out of service for a planned outage to set the computer time to Eastern Daylight Time. During the time change adjustment, the ICS experienced a hard memory fault which required additional efforts to recover the ICS. At approximately 1205 hours EDT, the ICS was restored to normal operation. During the time ICS was out of service, the Safety Parameter Display System (SPDS), the Emergency Response Data System (ERDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) were unavailable. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-03-15
45767 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-03-15 09:46 | 2010-03-15 12:51 | 2010-03-15 | SECONDARY CONTAINMENT BYPASS LEAKAGE EXCEEDED TECHNICAL SPECIFICATION LIMIT "Appendix J Local Leak Rate Testing has determined that Secondary Containment Bypass Leakage (SCBL) has been exceeded for Unit 1. During performance of leak rate test SE-159-045, the combined SCBL limit of 15 scfh [standard cubic feet per hour] for as-found minimum pathway was exceeded as specified in Tech Spec SR 3.6.1.3.11. "Acceptance Criteria Test results were within Acceptance Criteria for the 10CFR50 Appendix J limits of 0.6 La [maximum allowed leakage rate]. "This event is being reported as a degraded or unanalyzed condition pursuant to 10CFR50.72(b)(3)(ii)(A)." The RHR system containment spray penetration isolation valve was being tested when the failure occurred. The valve will be repaired and re-tested. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-03-15
45766 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-03-14 10:27 | 2010-03-14 15:54 | 2010-03-14 | LOSS OF POWER TO EMERGENCY OPERATIONS FACILITY "Loss of electrical power at the Emergency Operations Facility (EOF) in Toms River, NJ. Electrical power was not restored within the 60 minute staffing requirement for the ERF as defined in NUREG-0654. The loss of power only affects the EOF. Full assessment and communications capabilities remain available in the main control room and technical support center. ERDS and the Health Physics Network remain available. "Power was restored to the EOF at 1530 EDT on 3/14/10." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-03-14
45765 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2010-03-13 18:25 | 2010-03-13 21:38 | 2010-03-13 | EMERGENCY DIESEL GENERATORS (EDGs) DECLARED INOPERABLE DUE TO SERVICE WATER TAGOUT "At 1825 EST service water to '22' and '23' EDGs was isolated while applying a protective tagout to the service water '1-2-3' header. Previously, the supply from the other service water header '4-5-6' was also isolated. '21' EDG was out of service on a tagout. "This resulted in a condition where no service water flow to the Emergency Diesel Generators was available for approximately three minutes. Service water flow was restored by opening the supply from the '1-2-3' service water header. During this condition, LCO 3.8.2 was not met. All required actions for LCO 3.8.2 were performed. LCO 3.8.2 was met when service water flow was restored to the Emergency Diesel Generators. "The Emergency Diesel Generators were required to support residual heat removal in the event of a loss of offsite power. At no time was residual heat removal lost." The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-03-13
45764 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2010-03-12 21:43 | 2010-03-13 04:45 | 2010-03-15 | CONTROL ROD DRIVE MECHANISM NOZZLE INDICATIONS "On March 12, 2010, during the Davis-Besse Nuclear Power Station Unit No. 1 (DBNPS) refueling outage, the documented results of planned ultrasonic (UT) examinations performed on the Control Rod Drive Mechanism (CRDM) nozzles penetrating the reactor vessel closure head (RVCH) identified that two of the nozzles inspected to date did not meet the applicable acceptance criteria. Each of these two nozzles have similar indications that appear to penetrate into the nozzle walls from a lack of fusion point at the outer diameter of the nozzle and the J-Groove weld. Leak path detection was performed on both nozzles with the results showing no leak path. Bare metal visual examinations are scheduled to be performed on all nozzles to determine if there is any pressure boundary leakage. Both indications will require repair prior to returning the vessel head to service. There are sixty-nine nozzles and all will be subject to these UT inspections. "It is important to note that this notification is being provided prior to the completion of all of the required UT and VT [Visual Tests] examinations for these two nozzles and the remaining nozzles. The indications were detected with a blade probe used to detect axially-oriented indications. The remaining probe that is used to complete the UT examination in each of these two penetrations is a blade probe that is used to identify circumferentially-oriented indications. "The examinations are being performed to meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to identify potential flaws/indications well before they grow to a size that could potentially affect the structural integrity of the reactor vessel head pressure boundary." The licensee notified the NRC Resident Inspector and will notify the State of Ohio and both Lucas and Ottawa Counties. * * * UPDATE ON 3/13/2010 AT 1903 FROM LARRY MEYERS TO MARK ABRAMOVITZ * * * "On March 13, 2010, additional Control Rod Drive Mechanism nozzles (4 and 59) were identified that did not meet the applicable acceptance criteria. The indications on these nozzles are similar in nature and location to the indications previously reported for nozzles 28 and 33. These indications will also require repair prior to returning the vessel head to service. "Like the two previously reported nozzles, this notification is being provided prior to the completion of all of the required examinations for the nozzle and the remaining nozzles. The indications were detected with a blade probe used to detect axially-oriented indications. The remaining probe that will be used to complete the examination in this penetration is a probe sensitive to circumferentially-oriented indications. "Additionally, during the bare metal visual examination of the outer surface of the reactor vessel closure head, boric acid deposits were found at CRDM nozzles 4 and 33 that are indicative of primary water leakage. The visual examination of the RVCH is continuing." The licensee notified the NRC Resident Inspector, State of Ohio, and local government. Notified the R3DO (Phillips). * * * UPDATE ON 3/15/2010 AT 0800 EDT FROM THOMAS PHILLIPS TO JEFF ROTTON* * * Update to Davis-Besse event #45764 initially reported 3/13/2010 at 0445 and adding an additional 10 CFR 50.72 reporting criteria. "On March 15, 2010, the FirstEnergy Nuclear Operating Company is issuing a press release regarding the Davis-Besse Nuclear Power Station Unit No. 1 reactor vessel head (RVCH) Control Rod Drive Mechanism nozzles that have indications that do not meet the applicable acceptance regulatory criteria. The results of the ongoing planned ultrasonic (UT) examinations performed on these nozzles penetrating the RVCH have identified indications that will require repair prior to returning the vessel head to service. Currently, there are twelve nozzles which will be repaired, two of which have evidence of primary water leakage found during the bare metal visual examination of the outer surface of the reactor vessel closure head. There are sixty-nine nozzles and all are subject to these UT inspections. "It is important to note that this media release is being provided prior to the completion of all of the required examinations for these and the remaining nozzles." The licensee notified the NRC Resident Inspector and will be notifying the State of Ohio and both Lucas and Ottawa Counties. Notified R3DO (Monte Phillips) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | OFFSITE NOTIFICATION |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(2)(xi) |  |  | 0 | 2010-03-13
45763 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-03-12 15:11 | 2010-03-12 18:11 | 2010-03-12 | AGREEMENT STATE REPORT - GAUGE SHUTTERS STUCK SHUT The following report was received via facsimile: On March 12, 2010, at 1511 hours, the Agency [State of Texas] received a request to perform work in the State of Texas under reciprocity from a nuclear gauge manufacturer [Ronan Engineering]. The request stated that the work was to repair two nuclear gauges with stuck shutters. The gauges are Ronan Engineering model SA1-C10 each containing 200 millicuries each of Cesium (Cs) -137. The Agency contacted the Radiation Safety Officer (RSO) for the licensee identified on the request and asked him if the events were reportable. The RSO stated that the two gauges had been removed from storage and installed on a piece of equipment for use. A service company was testing the equipment prior to placing it in service and found that the gauge shutters would not open. The licensee then contacted the gauge manufacturer to repair the gauges. The RSO stated that he was not aware of the reporting requirement and would submit a written report to the Agency. Additional information will be provided as it is received." Texas Event #I-8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-03-17
45762 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-03-09 10:00 | 2010-03-12 09:39 | 2010-03-12 | LOST METALLURGY LABORATORY SAMPLE "A metallurgy laboratory (Met Lab) sample was determined to be missing from its prescribed location on March 9, 2010. A search for the item was immediately initiated per requirements. As of 10:00am March 12, 2010, the item has not been located and as a result, formal notification of a missing item is being made to the NRC per 10 CFR 74.11. To date, no other indicator of intentional theft or diversion has been found. Both the search and the investigation are still underway. The missing item contains approximately 0.67 grams U and 0.65 grams U-235." The material was last accounted for on 10/26/2009. The licensee has notified the NRC Resident Inspector and will notify the state. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.11(a) |  |  |  | 0 | 2010-03-17
45761 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2010-03-11 17:45 | 2010-03-11 21:25 | 2010-03-11 | PRESS RELEASE CONCERNING A FORMER PLANT EMPLOYEE "This notification is being made pursuant to 10CFR50.72(b)(2)(xi) due to the issuance of a press release concerning an individual that previously performed work at Hope Creek Generating Station. "PSEG Nuclear provided the following statement to Channel 6 News, the ABC-TV affiliate out of Philadelphia, which read as follows: 'Sharif Mobley previously worked as a laborer at PSEG Nuclear for a variety of contractors from 2002 to 2008 mainly during refueling outages for several weeks at a time. This individual satisfied federal security background checks required to work in the US nuclear industry as recently as 2008. While working here, he did routine labor work carrying supplies and assisting maintenance activities. He also worked at other nuclear plants in the region. We are cooperating with law enforcement as part of their investigation as well as the Nuclear Regulatory Commission and other nuclear plant operators.' "Sharif Mobley has been the focus of recent news stories due to his activities in the country of Yemen. "Hope Creek Generating Station is currently operating at 100%. There is no indication that the individual compromised the security of the station." The licensee will inform the State of Delaware and New Jersey, the Lower Alloways Creek Township and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-03-11
45760 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-03-11 17:45 | 2010-03-11 19:00 | 2010-03-11 | PRESS RELEASE CONCERNING A FORMER PLANT EMPLOYEE "This notification is being made pursuant to 10CFR50.72(b)(2)(xi) due to the issuance of a press release concerning an individual that previously performed work at Salem Generating Station. "PSEG Nuclear provided the following statement to Channel 6 News, the ABC-TV affiliate out of Philadelphia, which read as follows: 'Sharif Mobley previously worked as a laborer at PSEG Nuclear for a variety of contractors from 2002 to 2008 mainly during refueling outages for several weeks at a time. This individual satisfied federal security background checks required to work in the US nuclear industry as recently as 2008. While working here, he did routine labor work carrying supplies and assisting maintenance activities. He also worked at other nuclear plants in the region. We are cooperating with law enforcement as part of their investigation as well as the Nuclear Regulatory Commission and other nuclear plant operators.' "Sharif Mobley has been the focus of recent news stories due to his activities in the country of Yemen." The NRC Resident Inspector has been notified and the Lower Alloways Creek Township will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-03-11
45759 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-03-11 | 2010-03-11 15:55 | 2010-03-11 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL OVERDOSE The following report was received via e-mail: "Patient was receiving the 2nd of 14 fractions of 250 centiGray treatments to the ear. The therapist accidently pushed the 'auto radiography' button rather than the 'treatment' button which delivered approximately 9 times the intended dose. The patient and doctor have been notified. No health effects are expected. Licensee will send a written report. Florida is investigating." Isotope: Ir-192, 5.7 Ci Maximum dose received: 2250 centiGray Device: HDR Surface Applicator manufactured by Nucletron Model V2 MicroSelectron Florida Incident Number: FL10-035 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-03-17
45758 | 0 | BOZEMAN DEACONESS HOSPITAL |  |  |  |  | 2010-03-10 12:00 | 2010-03-11 12:45 | 2010-03-11 | SAMARIUM-153 VIAL UNACCOUNTED FOR DURING INVENTORY The RSO was informed at approximately 1200 hours on 3/10/10 that a 30 mCi vial of Sm-153 could not be accounted for during an inventory conducted on 3/9/10. The vial was last logged in on 2/19/04. The licensee discussed this incident with R4 (Munoz). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-03-11
45757 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-03-11 05:45 | 2010-03-11 12:43 | 2010-03-26 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Troxler moisture density gauge was stolen from an open bed truck at the employee's residence. The gauge was chained in the back of the truck. The theft was discovered at 0545 PST on 3/11/2010. "RSO was notified at 0550 PST, Las Vegas Metropolitan Police (LVMPD) at 0555 PST and the Nevada State Health Division at 0556 PST. The State is following the incident and working with LVMPD. Follow-up information will be provided to the NRC on the situation and entered into NMED. LVMPD Event No.: 100311-0802." Troxler model 3440 Serial Number: 17916 Sources: Am-241:Be 40 mCi Be (Model No.47- Serial No.13357) and Cs-137 8 mCi 137 (Model No. 50,Serial No. 7401) Nevada Incident Number: NV100003 * * * UPDATE FROM SNEHA RAVIKUMAR TO PETE SNYDER ON 3/26/10 AT 1303 EDT * * * At 0900 PDT on 3/25/10, the RSO reported that the gauge had been found by local police. When the RSO examined the gauge on 3/26/10, he found that the gauge was undamaged, intact and in good condition with only the outer lock of the case broken. Notified FSME EO (McIntosh), R4DO (Deese) and ILTAB (Hahn). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-03-16
45756 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-03-10 09:00 | 2010-03-10 13:15 | 2010-03-10 | FITNESS FOR DUTY REPORT A contract supervisor tested positive for alcohol on a for-cause fitness for duty test. The contractor's access to the facility has been terminated. Contact the Headquarters Operations Officer for further details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2010-03-10
45755 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-03-10 | 2010-03-10 10:21 | 2010-03-10 | AGREEMENT STATE REPORT - POTENTIALLY LOST STATIC ELIMINATOR The following information was obtained from the State of Colorado via email: "A general licensee, Hach Company - Loveland Facility, has notified the Colorado Department of Health that it lost a Nuclestat (static eliminator) device containing 10 milliCuries of Polonium 210. The model number is P-2021, Serial Number A2FR969 which was shipped on May 17, 2007 from NRD, LLC. "The licensee states that the facility has been audited and personnel questioned. No other details are available at this time. "The Colorado Department of Health has initiated an investigation of this incident." Colorado Report Number: I10-03 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-03-15
45754 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-03-09 19:16 | 2010-03-09 23:39 | 2010-03-09 | POTENTIAL LOSS OF 1E PUMPS DUE TO DEGRADED VOLTAGE DURING POSTULATED ACCIDENTS "While attempting to analyze the consequences of scenarios (loss of coolant accident (LOCA) and loss of offsite power (LOOP)) postulated during the Component Design Basis Inspection (CDBI), PG&E concluded both units were in an Unanalyzed Condition that significantly degrades plant safety, and therefore, reportable under 10 CFR 50.72(b)(3)(ii)(B). "The postulated scenario could result in permanently connected class 1E pump motors tripping over current relays due to sustained degraded voltage on the startup offsite power source. "The scenario starts with a safety injection (SI) signal transferring 4160 volt vital buses from auxiliary power to the startup offsite power source. Following bus transfer, the startup source is postulated to degrade to a level above the first level under voltage relay (FLUR) setting of equal to or greater than 2583 volts and below the second level under voltage relay (SLUR) setting of equal to or greater than 3785 volts. Permanently connected class 1E pump motors would experience this degraded voltage for up to the SLUR time delay relay setting of equal to or less than 20 seconds. Prior to reaching the SLUR time delay relay setpoint and transferring loads to the onsite emergency diesel generators (EDGs), operating motors (e.g. auxiliary saltwater (ASW) pump and component cooling water (CCW) pumps) could trip on over current. Operators would be directed by procedures to re-start these motors on an operable power source (EDG). However, since this scenario has not been previously analyzed and could reasonably challenge containment pressure or peak clad temperature limits, it is considered unanalyzed. "The postulated scenario had previously been considered non-credible, and therefore, had not been analyzed. "PG&E considers this a nonconservative technical specification (TS) since the values in TS surveillance requirement (SR) 3.3.5.3 would not protect permanently connected class 1E loads from damage during degraded voltage conditions." The licensee has notified the NRC Resident Inspector. The condition was discovered by NRC inspectors while performing a CDBI inspection. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-03-09
45753 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2010-03-08 16:35 | 2010-03-08 19:47 | 2010-03-08 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR WATER LEVEL "An 'A' reactor feed pump trip occurred and initiated a recirculation pump flow control valve runback. During the flow control valve runback, the 'A' recirculation hydraulic power unit tripped causing an incomplete runback. "Reactor water level 3 (11.4 inches) was reached which is an RPS scram setpoint and also a setpoint for Group 2 (RHR to Radwaste) and Group 3 (Shutdown Cooling Isolation). No valves isolated in these systems due to [the valves] being in their normally closed position. The lowest reactor water level reached was -28 inches wide range. "Appropriate off normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached, and no ECCS or Diesel Generator initiation occurred. All safety systems performed as expected. "MSIVs remained open and no SRVs lifted. Main condenser and pressure control systems remained in service. Currently, reactor water level is being maintained by the condensate and feedwater system in the normal level band and reactor pressure is being controlled to limit cooldown." During the scram, all rods inserted into the core. The plant is in its normal shutdown electrical lineup. Decay heat removal is via the steam bypass valves to the condenser. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-03-08
45752 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-03-08 | 2010-03-08 20:03 | 2010-03-08 | POTENTIAL RELEASE OF CONTAMINATED MATERALS OFF-SITE "At 1705 hours on 03/08/2010, the USEC-GS Plant Shift Superintendents' (PSS) Office at Portsmouth was notified of an inadvertent release of radioactively contaminated materials to an off-site location in Pike County, OH. The contamination was the result of a contractor neutralizing a fluorine service pipe connecting the X-326 building with the X-760 building. The X-760 building has been "de-leased" by USEC back to the Department of Energy (DOE) and is being prepared for decommission and demolition. The contaminated items consisted of five (5) 5-gallon buckets containing some rusty solution. The highest contamination levels were on one (1) bucket with 14K Beta removable and 50K Beta fixed. All other tools and personal protective equipment were monitored and found to be uncontaminated. There is a filtering unit located in Atlanta, GA that remains to be surveyed. A team of USEC health physics personnel is preparing to travel to the contractor's facility in Atlanta to complete the surveys. "This event has been classified as reportable in accordance with procedure UE2-RA-RE1030, Portsmouth GDP SAR 6.9, and 10CFR76. No 10CFR20 exposure limits were reached or exceeded." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2010-03-08
45751 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-03-08 10:25 | 2010-03-08 16:31 | 2010-03-08 | FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 72 | 0 | 0 | 72 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2010-03-08
45750 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-11-08 | 2010-03-08 15:54 | 2010-03-08 | AGREEMENT STATE REPORT - BRACHYTHERAPY DOSAGE LESS THAN PRESCRIBED The following information was obtained from the State of Ohio via email: "ODH [Ohio Department of Health] received information on 3/3/10 of a unreported medical event that occurred at Mercy St. Vincent Medical Center in Toledo on 11/8/05. ODH performed an on-site investigation on 3/5/10 and confirmed the unreported medical event. On 11/8/05, the licensee performed a prostate seed implant with 67 I-125 seeds prescribed to deliver a dose of 160 Gray to the prostate. Thirteen seeds were removed from the bladder immediately after the procedure leaving 54 seeds in the patient. A post implant dose calculation showed an under dose to the prostate greater than 20% of the prescribed dose. The licensee then performed an external beam treatment with a linear accelerator to treat the tumor. "ODH is continuing the investigation of this event along with other brachytherapy cases performed by the licensee. ODH is also requesting assistance from the NRC's contract medical expert in evaluating the event." Ohio Report Number: OH100003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-03-14
45749 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-03-08 03:33 | 2010-03-08 05:46 | 2010-03-08 | MANUAL REACTOR TRIP DUE TO LOSS OF ALL MAIN FEEDWATER "Wolf Creek experienced an 'A' Main Feedwater Pump (MFP) trip at 0332 CST during a plant startup. Reactor power was 42% at the time of the manual reactor trip. The loss of the 'A' MFP resulted in no feedwater flow to the Steam Generators and a manual reactor trip was ordered due to the impending reactor trip on low-low Steam Generator level. "Post-trip decay heat was being removed by the Condenser and Auxiliary Feedwater System. Reactor Coolant System (RCS) temperature dropped below 550 degrees Fahrenheit, which required emergency boration to ensure shutdown margin was maintained. Emergency boration was secured at 0404 CST when RCS temperature was raised to greater than 550 degrees Fahrenheit. The lowest RCS temperature reached following the reactor trip was 544 degrees Fahrenheit. "The cause of the 'A' Main Feedwater Pump trip is not known at this time. "Primary to secondary leakage is less than 0.224 gallons per day. All systems functioned as designed. "The plant is being maintained at normal Mode 3 pressure and temperature. "The licensee has notified the Senior NRC Resident Inspector." All control rods fully inserted. The plant is in a normal post-trip electrical line-up. | 0 | 0 | 0 | 42 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-03-08
45748 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2010-03-07 11:24 | 2010-03-07 14:23 | 2010-03-07 | NOTIFICATION OF UNUSUAL EVENT DUE TO ELECTRICAL FAULT CAUSING DAMAGE TO EQUIPMENT "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 7, 2010, at approximately 1124 MST Palo Verde Unit 1 declared a Notification of Unusual Event (NOUE) due to an electrical fault (explosion) experienced on the 13.8 KV Non-Class busses being supplied from the Unit Auxiliary Transformer. The fault resulted in a minor explosion and damage to the bus work leading from NAN S03 to NAN S01. The fault resulted in the loss of the NAN S01, which caused a reactor trip due to the loss of 2 of 4 reactor coolant pumps. There was no fire detected after the initial event. The reactor trip (RPS actuation at 1117 MST) was from 100% rated thermal power due to low departure from nucleate boiling (DNBR) trips on all four channels of the core protection calculators (CPCs). The unit was at normal temperature and pressure prior to the trip. "All of the control rods fully inserted into the core. Four of eight steam bypass control valves quick opened, per design, directing steam flow to the condenser. No main steam or primary relief valves lifted and none were required. There was no loss of heat removal capability or loss of safety functions associated with the event. ESF Electrical buses remain energized from off-site power. "The Shift Manager determined this event was an uncomplicated reactor trip. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event nor contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. No ESF actuations [other than RPS] occurred and none were required. The event did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or health and safety of the public." Decay heat is being removed via the steam bypass valves to the condenser. The plant is in its normal shutdown electrical lineup with the exception of powering the NAN S01 bus. Unit 2 and Unit 3 were not affected by the transient on Unit 1. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ALFRED ERDELJI TO HOWIE CROUCH @ 1723 EST ON 3/7/10 * * * Palo Verde Unit 1 has terminated the NOUE at 1516 MST. The termination criteria was that the plant is stable, the area around the fault has been inspected and no other conditions exist that would prevent termination of the event. Decay heat path has been changed from steam dumps to condenser to atmospheric dumps due to difficulty in maintaining temperature. There is no known primary to secondary leakage. The licensee has notified the NRC Resident Inspector. Notified R4DO (Cain), NRR EO (Holian), IRD (Gott), DHS (Roper) and FEMA (LaForte). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2010-03-07
45747 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2010-03-05 13:25 | 2010-03-05 16:32 | 2010-05-03 | UNANALYZED CONDITION - STEAM SUPPLY VALVE CREDITED AS CLOSED IN FSAR ANALYSIS IS NORMALLY OPEN DURING OPERATIONS "Valve FBV0147, Boric Acid Batch Tank Auxiliary Steam Supply Isolation Valve, is credited with being closed in the Callaway FSAR. This eliminated the need to analyze lines FB-081-HBD and FB-082-HBD for high energy line breaks (HELB). However, FBV0147 was found to be kept normally open to allow steam service for the boric acid batching tank. This is contrary to the normal position assumed in the FSAR and HELB analyses. "With valve FBV0147 open, the lines must considered high energy lines. The lines are in the auxiliary building and they traverse rooms containing several components including the flow transmitters for Residual Heat Removal (RHR) to train `A' accumulator injection supply header, RHR train `A' and 'B' SIS hot leg recirculation supply header, and several safety related auxiliary feedwater components. These instruments are used to provide indications during post-accident conditions. This configuration is therefore outside of current HELB analysis and potentially represents a condition that significantly degrades plant safety. "The condition was identified to Operations at 0740. Valve FBV0147 was closed at 0810. At 1325 CST, the issue was determined to be reportable. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 1557 EDT ON 5/3/10 FROM HURT TO HUFFMAN * * * "On 03/05/2010, EN #45747 provided notification that valve FBV0147 was found to be kept normally open to allow steam service for the boric acid hatching tank. This configuration was not consistent with the normal position assumed in the FSAR and HELB analyses. "An engineering evaluation was subsequently performed for the auxiliary steam inlet and outlet piping for the boric acid batching tank. This valuation identified four postulated break locations which have all been analyzed. The analyses determined that all safety-related components in the affected rooms would be able to perform their safety functions in the event of a line break. Pipe whip, jet impingement, compartment temperature and over pressurization, flooding, and internal missiles resulting from a postulated line break would not prevent any safety-related equipment from performing its design function. "As supported by this evaluation, this condition does not meet the criteria for an unanalyzed condition that significantly degrades plant safety as stated in 10 CFR 50.72(b)(3)(ii)(B). Therefore, the notification made on 03/05/2010 is hereby retracted. "The NRC Resident Inspector will be notified." R4DO (Farnholtz) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-03-05
45746 | 0 | NASA AMES RESEARCH CENTER |  |  |  |  | 2010-02-03 | 2010-03-05 13:29 | 2010-03-05 | TWO MISSING TRITIUM EXIT SIGNS During their biannual inventory, the licensee could not account for two tritium exit signs. Both signs were accounted for in the previous inventory. The first sign was installed in a wind tunnel that was transferred to the Air Force in 2006. After obtaining the wind tunnel, the Air Force claims to have removed the sign and, after a period of storage, recycled the sign with the others that were removed from the tunnel. The sign was manufactured on 7/20/94 by SRB Technologies (serial number 174501). The initial tritium load was 20 Ci. Calculated content on 2/26/10 was 8.33 Curies. The second sign was installed in a building on Moffitt Field that is currently undergoing renovation. It is believed that the sign is under the control of the renovation contractor after is was removed during the painting process. The sign was manufactured on 5/1/91 by SRB Technologies (serial number 526854). The initial tritium load was 20 Ci. Calculated content on 2/26/10 was 6.95 Curies. Both signs have contact information for the licensee attached. The licensee is conducting a search for both signs. They have notified Region 4 (Campbell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-03-05
45745 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-03-05 00:07 | 2010-03-05 03:25 | 2010-04-29 | SPECIFIED SYSTEM ACTUATION - FEEDWATER ISOLATION DUE TO HIGH STEAM GENERATOR WATER LEVEL "A Turbine trip and Feedwater Isolation Signal was generated as a result of high level in 'A' Steam Generator. At approximately 0007 CST, a turbine trip and Feedwater Isolation Signal was generated when the level in the 'A' Steam Generator exceeded the initiation set point of 78%. Steam Generator level returned below the initiation setpoint at approximately 0008 CST. Steam Generator 'A' high level resulted from swell of the Steam Generator after opening the 'A' Main Steam Isolation Valve. Level was approximately 50% prior to the event and returned to approximately 50% within one minute. "The turbine was already in the tripped condition due to the plant trip that occurred at 1458 CST on 03/02/2010 (Reference EN# 45739). "Steam Generators are being fed with the motor driven startup Feedwater pump. Decay heat removal is via the Steam Generator Atmospheric Relief Valves and steam dumps. The plant is in Mode 4 with Reactor Coolant System pressure at approximately 500 psig and temperature at approximately 332 degrees F. "Two Main Feedwater isolation valves did not fully close but the actuators were being supplied with auxiliary medium (air) at the time of the actuation. Feedwater isolation valves are not required to be operable in Mode 4." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM RICK HUBBARD TO PETE SNYDER AT 1456 ON 4/29/2010 * * * "This event (Event Number 45745) is being retracted. A valid actuation of any systems listed in paragraph 50.72 (b)(3)(iv)(B) did not occur. The plant was in Mode 4 and neither a reactor trip nor an auxiliary feedwater system actuation signal occurred. Additional evaluation determined that the turbine trip and feedwater isolation signal are a function of the ESFAS [Engineered Safety Features Actuation System] instrumentation and does not result in an actuation of the RPS [Reactor Protection System] or other systems listed in paragraph 50.72 (b)(3)(iv)(B)." The licensee notified the NRC Resident Inspector. Notified R4DO(Clark). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-03-05
45744 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-03-04 11:20 | 2010-03-04 13:11 | 2010-03-04 | OFFSITE NOTIFICATION DUE TO DECEASED BIRDS ON SITE "On the morning of 03/04/2010, approximately 500 dead European starlings were found in the area surrounding the north part of the Turbine Building. Most of the dead birds were found around the main transformers. External examination of the dead starlings initially indicates the birds likely died from respiratory distress as a result of damage to their respiratory system. Initial indications are that the birds were somehow poisoned offsite, came to Wolf Creek to roost, and subsequently died while roosting. "Wolf Creek notified the Kansas Department of Wildlife and Parks and the U.S. Fish and Wildlife Service of this event. This is being reported per 10 CFR 50.72(b)(2)(xi) since Wolf Creek made a notification to other government agencies. "The Senior Resident Inspector was notified of this event." * * * UPDATE FROM LANCE LANE TO HOWIE CROUCH @ 1904 EST ON 3/4/10 * * * "Wolf Creek was informed that a bait/poison was applied under permit (USDA & USFWS) at a local dairy farm near Westphalia, KS. Poison was placed on Tuesday, which coincides with some birds in a weakened state Tuesday night and major die off Wednesday. The USDA has agreed to let Wolf Creek know if similar baiting is done in the future." The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Giessner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-03-04
45743 | 0 | ARCELORMITTAL |  |  |  |  | 2009-12-07 | 2010-03-03 17:30 | 2010-03-03 | UNABLE TO FULLY CLOSE A FIXED GAUGE SHUTTER During operation, the shutter for a fixed gauge had a build up of dust. When the shutter failed to close completely, the licensee called the manufacturer for repairs. After cleaning of the fixed gauge, the shutter closed satisfactorily. The fixed gauge is a K-Ray, model number 7064P, serial number 8318 with a Cs-137, 5 Curie source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-03-03
45742 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2010-02-23 16:35 | 2010-03-03 16:25 | 2010-03-03 | AGREEMENT STATE REPORT - DAMAGED TROXLER The following information was received from the State via facsimile: "A Troxler Electronic Laboratories, Inc. Model 3430, portable gauging device [serial number 17906, containing approximately 8.0 millicuries of cesium-137 (source serial number 750-7391), and approximately 40 millicuries of americium-241/beryllium (source serial number 47-13347)] was hit by an excavator at a temporary jobsite. The Cs-137 source was in the safe shielded position when it was hit and the source remained shielded after it was struck by the excavator. A leak test was performed and no leakage was detected from either source." Utah Event Number: UT-10-0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2010-03-08
45741 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-03-03 | 2010-03-03 12:24 | 2010-03-03 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATION DEVICE The following information was received from the State via facsimile: "The current general licensee, M/A-COM Technology Solutions, Inc., at the same location of the former, original general licensee, Tyco Electronics M/A-COM, at 100 Chelmsford Street, in Lowell, Massachusetts has no knowledge of the location of one static elimination device. The device had been used in a process that was terminated in 2007. The facility has been searched and employees and past employees have been questioned. The general licensee has declared the device as missing. The Agreement State has contacted the distributor and determined that the device was not returned to them. "Source: 10mCi, Po-210 "Manufacture: NRD, Inc. "Model Number: P-2021 "Serial Number: 114186" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-03-08
45740 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2010-03-03 07:55 | 2010-03-03 09:51 | 2010-03-03 | SECURITY REPORT INVOLVING UNAUTHORIZED ENTRY INTO THE PROTECTED AREA An actual entry of an unauthorized person into a protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-03-03
45739 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-03-02 14:58 | 2010-03-02 18:48 | 2010-03-02 | AUTOMATIC REACTOR TRIP CAUSED BY LOW STEAM GENERATOR WATER LEVEL "Wolf Creek experienced a reactor trip at 1458 CST. The first out annunciator was Steam Generator Level Lo Lo Reactor Trip. "The trip was caused by the loss of the 'A' Main Feed Pump. The cause of the loss of the feed pump was due to the loss of 120 VAC non-safety instrument inverter PN09. PN09 supplies the Main Feed Pump Speed Control Circuitry. "The loss of the PN09 also resulted in the loss of the ability to dump steam to the main condenser. Initial post trip decay heat was being removed with the Steam Generator Atmospheric Relief Valves and Auxiliary Feed Water. The Atmospheric Relief Valves cycled from approximately 1458 CST until approximately 1504 CST. Primary to Secondary leakage is less than 2.68 gallons per day. "PN09 was re-energized at 1554 CST. "All systems functioned as designed with the exception of the instrumentation powered by PN09. At the time of the trip the 'A' Emergency Diesel Generator and the 'A' Class IE Air Conditioning Unit were out of service for maintenance. "The plant is being maintained at normal Mode 3 pressure and temperature." The reactor trip was uncomplicated and decay heat is currently being removed by steam dumps to the main condensers. The licensee has notified the NRC Senior Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-03-02
45738 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2010-02-25 23:15 | 2010-03-02 16:40 | 2010-03-02 | DISCOVERY OF AN AFTER-THE-FACT UNUSUAL EVENT "This is a one-hour report for the discovery of a condition that briefly met the emergency action level (EAL) for an Unusual Event but did not warrant declaration of an emergency classification. A detailed review of the conditions that existed at approximately 2315 EST on February 25 during a winter storm determined that the winds reached a speed of approximately 94 miles per hour for approximately four seconds. This wind speed exceeded the EAL value of greater than or equal to 90 miles per hour. However, because the condition cleared within approximately four seconds, a declaration of an Unusual Event would not have been warranted. The information examined during this detailed review was not the wind speed indication displayed in the control room and used by the operators for evaluating Emergency Action Levels. The additional analysis, which was performed following the winter storm, used data obtained by Engineering. The control room indication remained below 90 miles per hour at all times. This event is a one-hour report based on the guidance in NUREG-1022 for a condition that met an emergency plan EAL and the basis for the emergency classification no longer existed at the time of discovery. The [NRC] Resident Inspector has been informed of this notification and good neighbor notifications will be made to [the State of] New Hampshire and Massachusetts." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NH | POW | [5 empty] | 0 | 2010-03-02
45737 | -1 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2010-03-02 07:30 | 2010-03-02 11:30 | 2010-03-15 | PRESSURIZER SAFETY NOZZLE WELD DEGRADATION "A Unit-1 Pressurizer Safety Relief Valve Nozzle to Safe-end Weld, (#4SR-1006-1) was discovered to have an indication not acceptable under ASME Section XI, IWB-3600. The weld is on a 4 inch diameter line to the pressurizer safety relief valve (RV-201). The weld is in our dissimilar metal weld inspection program and was scheduled to be examined this RFO [refueling outage] in accordance with MRP-139 requirements. Initial inspections on 3/1/10 found an indication and the indication was confirmed by a second NDE level 3 examiner. Indication is circumferential, initiated at ID and propagates approximately 1.8 inches circumferentially to about approximately 70% through wall. ASME IWB-3500 allows up to 12.5% through wall for class 1 welds. The defect was found using phased array Ultrasonic Testing (UT). The NDE report is being reviewed and characterized at this time. "At this time, we believe the most probable cause of the indication is primary water stress corrosion cracking. No active leaks have been identified, the defect is not through wall. "Unit 1 is in Mode 6. A team has been established and repair options are being investigated." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED AT 0922 EDT ON 03/15/2010 BY ROBERT MARTIN TO JEFF ROTTON * * * "On March 7, 2010, manually indexed phased-array ultrasonic examination of the U1 Pressurizer Safety Relief Valve Nozzle to Safe-end Weld was performed. Based on these inspections, it was determined on March 13, 2010 that the indication does not exhibit stress corrosion cracking characteristics and is not consistent with ultrasonic responses associated with inside diameter (ID) connected geometry. Therefore, the U1 Pressurizer Safety Relief Valve Nozzle to Safe-end Weld is acceptable from an ASME Code Section XI perspective. On this basis, the indication did not result in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded and the issue is not reportable under 10 CFR 50.72(b)(3)(ii)(A). "The NRC resident was notified of this retraction." Notified the R1DO (Chris Cahill) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-03-02
45736 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-02-16 | 2010-03-01 11:48 | 2010-03-01 | AGREEMENT STATE REPORT - SHUTTER FOUND STUCK CLOSED ON PROCESS GAUGE During the semi-annual inspection of the gasification facility's process gauges, a gauge was found with its shutter stuck closed. The gauge had not been used since the last licensee inspection so there would have been no indication from operation of the facility that there was a problem. The gauge was a Berthold Model P-2608-100 containing a 5 millicurie Co-60 source. The licensee has determined that the gauge is not really needed to support the process and has contacted Berthold to come to the facility and remove the gauge and take possession of it. The licensee has inactivated the gauge and, with the shutter stuck closed, considers that there is no risk to personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2010-03-04
45735 | 0 | COVIDIEN-MALLINCKRODT |  |  |  |  | 2010-03-01 09:15 | 2010-03-01 10:47 | 2010-03-05 | TECHNETIUM GENERATOR LOST IN TRANSIT Covidien was shipping a Molybdenum/Technetium generator to Bermuda on 2/12/2010. It was being transshipped in Atlanta for air delivery to Bermuda on one of Delta Airlines twice weekly flights. On 2/14/2010, the shipment was bumped to the next flight and on 2/18/2010 it was again bumped. The recipient was contacted and declined the shipment. Delta was contacted and stated that they could no longer locate the shipment. The initial activity was 3 Ci of Mo-99m which would have decayed to 41 mCi on 3/1/2010. * * * UPDATE ON 3/5/10 AT 1030 EST FROM DAN HOFFMAN TO PETE SNYDER * * * On March 3, 2010, Covidien was notified by Delta that they had located the package at their Bermuda Cargo Facility. Delta will return the package to Covidien. Notified R3DO (Giessner) and FSME (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-03-01
45734 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-02-28 01:45 | 2010-02-28 04:10 | 2010-02-28 | OFFSITE NOTIFICATION OF STATE AND TRIBAL AGENCIES "At 0145 Prairie Island Security personnel detected an unknown person within the Owner Controlled Area. The individual was walking from the area near the Mississippi River boat ramp West and was intercepted by Security personnel in the plant parking lot. He was then taken into custody by Prairie Island Police. "The event was determined to be media sensitive and courtesy notifications are being made to state, local and tribal agencies. No news release is planned and there was no effect on plant operations. "It was later determined the individual had fled from the Treasure Island Casino. Local police had been searching for him at the time plant Security stopped him." The individual had been detained at the casino due to suspected underage drinking and was being held for local law enforcement when he fled on foot. The licensee notified the NRC Resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-02-28
45733 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-02-26 18:40 | 2010-02-27 13:46 | 2010-02-27 | AGREEMENT STATE - POTENTIAL OVEREXPOSURE DURING RADIOGRAPHY A representative of the State of Nebraska has received preliminary information about a radiography incident that may have resulted in overexposures. The incident occurred during radiography of elevated piping at a pumping station. The radiographer and a contactor operating an aerial lift bucket had just completed a radiography shot on some overhead piping. The assistant radiographer was in a different location and had supposedly retracted the source into its safe position. Because the radiographer had his alarming rate meter under his clothing, and because there was significant ambient noise in the work area, the radiographer did not immediately hear that his rate meter was alarming as he and the aerial lift operator approached the radiography camera guide tube to set up for the next shot. When the radiographer heard the alarm, he checked his pocket dosimeter and found it off-scale. The radiographer had the assistant re-perform the source retraction and was subsequently able to confirm that the source was now fully retracted into the camera's safe position. Based on initial estimates by the radiographer, his worst case exposure could be as high as 7.1 REM. The best case scenario would put his exposure around 200 mREM. The aerial lift operator, who is not a radiation worker, is believed to have exposures less than the radiographer. The radiographer's TLD has been sent for immediate processing by Landauer. The State should have an inspector at the site on 2/28/10. This report will be updated and more details provided after the State completes its initial inspection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-03-03
45732 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-02-27 01:58 | 2010-02-27 07:37 | 2010-02-27 | REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM MANUALLY STARTED TO MAINTAIN REACTOR PRESSURE VESSEL LEVEL FOLLOWING A PRE-PLANNED REACTOR SCRAM "On February 27, 2010, at 0116 hours, as part of a pre-planned sequence of events, Unit 1 control room operators manually inserted a Reactor Protection system trip to shut down the reactor from approximately 21 percent of rated thermal power to begin a planned refuel outage. At 0158 hours, the Reactor Core Isolation Cooling (RCIC) system was manually started to maintain reactor pressure vessel (RPV) coolant level after the 1A Reactor Feedwater Pump (RFP) was shutdown due to high turbine casing drain level, and the 1B Reactor Feedwater Pump (RFP) had been removed from service and isolated to support maintenance activities. The Reactor Core Isolation Cooling (RCIC) system started and maintained reactor pressure vessel (RPV) coolant level until the 1B Reactor Feedwater Pump (RFP) could be returned to service at 0248 [hours]. The Reactor Core Isolation Cooling (RCIC) system was shutdown at 0306 [hours]. "The safety significance of this occurrence is considered minimal. The RCIC system is designed to operate either automatically or manually following RPV isolation, accompanied by a loss of normal coolant flow from the Reactor Feedwater system, to provide adequate core cooling, and control of the RPV coolant level. The function of the RCIC system is to respond to transient events by providing makeup coolant to the reactor. For this event, the RPV was not isolated, but there was a loss of normal coolant flow from the Reactor Feedwater System. The RCIC system was manually started and successfully controlled RPV coolant level for approximately 68 minutes until Reactor Feedwater system flow could be restored to the RPV. All emergency core cooling systems were operable and ready for use, if needed, during this event. This transient is bounded by the analyses in the Updated Final Safety Analysis Report." RPV level remained in the normal post-shutdown band of 170-200 inches during the transient. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-02-27
45731 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-02-26 08:30 | 2010-02-26 14:17 | 2010-02-26 | IN-PLANT PAGING SYSTEM OUT OF SERVICE "At about 0830 CST on 2/26/2010 , it was discovered that the station paging system was not operating. Repair efforts were initiated. The Control Room and station personnel were notified of the pager outage. The automated callout system is available to notify the emergency response organization during the pager outage if needed." * * * UPDATE FROM JOHN MUSSER TO JOE O'HARA AT 1556 EST ON 2/26/10 * * * The station paging system was restored to operable status at 1400 CST. The licensee will notify the NRC Resident Inspector. Notified the R4DO(Lantz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-26
45730 | 0 | ALPHA COAL WEST |  |  |  |  | 2010-02-26 10:20 | 2010-02-26 13:15 | 2010-02-26 | MISSING SHUTTER ON TEXAS NUCLEAR LEVEL GAUGE While on a routine inspection, a technician from Thermal Fisher notified the RSO that a shutter was missing from Texas Nuclear gauge #5202, s/n #B2302. The technician indicated he will try and get a replacement shutter for the gauge. This gauge is used for level indication in a coal hopper and the shutter is normally open. The gauge's source is 200 mCi of Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-02-26
45729 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2010-02-26 11:25 | 2010-02-26 11:48 | 2010-02-26 | MANUAL REACTOR TRIP DUE TO LOSS OF TWO CIRCULATING WATER PUMPS The "C" Circulating Water Pump tripped on high delta pressure across the screens. Another Circulating Water Pump was out of service for maintenance. This condition required a shutdown, therefore the reactor was manually tripped. This caused the steam generator level to reach the low level setpoint. There was a loss of Main Feedwater Pumps when breaking condenser vacuum. Auxiliary Feedwater Pumps started automatically upon low level in the steam generators. The letdown system was isolated post trip and the charging and letdown systems are restored to normal lineup. The plant is in Mode 3. All rods fully inserted. Decay heat is being removed via atmospheric dump valves. There are no known primary to secondary leaks in the steam generator tubes. The electrical lineup is normal with offsite power. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-02-26
45728 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-02-25 19:35 | 2010-02-25 23:37 | 2010-02-25 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO RHR INOPERABILITY "At 1840 on 2/25/10, Unit 2 RHR Division II became inoperable due to exceeding 260 degrees F on the injection line. The temperature is elevated due to leakage past the injection line check valve (2-CKV-74-68) and the inboard injection valve (2-FCV-74-67). The 260 degree F value is based on engineering calculations to ensure the injection line does not become steam voided. RHR Division I was already inoperable for scheduled maintenance when this condition occurred. Entered TS LCO 3.0.3 based on TS LCO 3.5.1 Condition H - Two or more Low pressure ECCS injection/spray subsystems inoperable for reasons other than Condition A. "Action was taken to lower power at 1935 when the conditions requiring entry into LCO 3.0.3 could not be corrected. "Tech Spec LCO 3.0.3 was exited at 2000 when RHR Loop II system pressure was raised using an alternate keep fill flow path to ensure that the injection line would remain filled. Power will be returned to 100%. "This event requires a 4 hour report in accordance with 10 CFR 50.72(b)(2)(i)." The licensee informed the NRC Resident Inspector. | 0 | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-02-25
45727 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-01-21 | 2010-02-25 18:54 | 2010-02-25 | AGREEMENT STATE REPORT - BRACHYTHERAPY IMPLANTS OUTSIDE OF THE INTENDED TREATMENT AREA The following information was received via fax: "Notifications: The licensee called the PaDEP Southeast Regional Office on the morning of February 25, 2010 to provide a 24-hour verbal notice of a possible Medical Event. The SERO and Central Office discussed the known facts around noon time, and understood the U Penn RSO would be providing more information via email. DEP also provided a verbal notice to NRC Region 1 regarding this possible ME on 2-25-2010. "On January 21, 2010 a patient was treated by brachytherapy for prostate cancer with sixty five (65) iodine-125 (I-125) seeds. The I-125 seeds were implanted using real time dosimetry under ultrasonic guidance. The written directive called for a therapeutic radiation dose of 145 gray (Gy) [14,500 rad] to the prostate volume, plus 5 millimeters of margin, using interoperative planning. On February 23, 2010, the patient returned for a 30 day post-implant CT. The scan showed that the implanted seeds were "in an appropriate pattern," but outside the intended target. On February 24th the licensee's Radiation Oncology group determined that an additional quality assurance review was warranted, but the RSO should notify PaDEP/BRP [Pennsylvania Department of Environmental Protection/Bureau of Radiation Protection] regarding the case. Based on the information known at this time, PaDEP/BRP believes this ME is reportable under 10CFR35.3045, and may be an Abnormal Occurrence (AO). The state will perform a reactive inspection next week, and coordinate with NRC Region I; because of their ongoing evaluation of pre-April 2008 brachytherapy implants at U Penn, and at the Philadelphia VA hospital. "Cause of the event: A new ultrasound unit that was used to place the I-125 seeds may have been malfunctioning. "Actions: There is a reactive inspection scheduled to investigate this apparent ME at U Penn on March 2, 2010. PaDEP/BRP will also ask U Penn to evaluate the need for FDA notification regarding the ultrasound unit." Event Report ID Number: PA100002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-03-03
45726 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-02-25 14:18 | 2010-02-25 16:20 | 2010-02-25 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "This 60-day notification is being made in accordance with 10 CFR 50.73(a)(1), which states that in case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv)(A), other than the actuation of the Reactor Protection System (RPS) when the reactor is critical, the licensee may provide a telephone notification to the NRC within 60 days after discovery of the event instead of submitting a written LER. Because plant conditions necessary to prompt a containment isolation were not present, this event constitutes an invalid system actuation under 10 CFR 50.73(a)(2)(iv)(A). The condition meets the criteria of 10 CFR 50.73(a)(2)(iv)(B)(2) because the loss of the Unit 1 'B' RPS bus affected containment isolation valves in more than one system. "On 1/4/2010 at 1418 hours, the Unit 1 'B' RPS bus was lost. This event resulted in a half scram and primary containment isolations. By design, when the RPS MG set output breaker trips, all EPA breakers downstream of the MG set also trip resulting in a half scram and primary containment isolation signals. "An event investigation found the Unit 1 'B' RPS MG set running with its output breaker tripped. The output voltage was indicating 120VAC, which indicates that the voltage regulator was operating properly. Upon removal of the MG set cover, the underfrequency relay (UFR) contacts were found to be chattering, with frequency steady at approximately 60 Hz. A review of plant drawings indicated that a chattering UFR could cause the MG set output breaker to trip. Voltage readings were taken and no additional electrical problems (other than the UFR) were identified. The affected RPS loads were subsequently powered from their alternate source and all actuations and isolations were reset. "Inspection and test of the failed UFR found that one leg of a capacitor on the UFR electronic board had broken adjacent to its solder joint connection on the board. It is suspected that the capacitor lead may have been flawed during manufacture of the board. The failure was accelerated by the constant vibration that the connection is subjected to, as the UFR is mounted on the MG set. "The failed UFR electronic board was subsequently replaced and successfully passed all functional tests. "There were no actual safety consequences associated with this event. Valves affected by the invalid signal fulfilled their isolation function by successfully closing. The RPS loads were transferred to their alternate power supply and the trips and isolations were reset. In addition, the Unit 1 'B' RPS bus did not experience an underfrequency condition." The licensee has notified the NRC Resident Inspector. | 94 | 94 | 0 | 94 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-02-25
45725 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-01-26 | 2010-02-25 14:13 | 2010-03-26 | AGREEMENT STATE REPORT - POTENTIAL SHALLOW DOSE EQUIVALENT OVEREXPOSURE "On 1/26/10, the Agency [State of Texas] received a report from the licensee's Radiation Safety Officer stating they had received a report from their dosimetry processor indicating one of their workers had received 230 rem to the badge worn on his left hand. The right hand badge read 1.420 rem for the same period. The RSO stated that the individual involved handled predominantly Fluorine (F)-18. His deep dose equivalent (DDE) for the same period was 439 millirem. The RSO stated that the typical exposure to the hands is between 500 and 1,200 millirem and that the DDE was about 250 millirem per exposure period. The RSO believed the exposure was to his badge only. The RSO stated that on December 23, 2009, the individual was involved in a spill of F-18 and his badge may have become contaminated causing the exposure. The RSO stated that he was waiting on a statement from the individual involved. "On February 25, 2010, the Agency received a written report of the event from the licensee. A review of the report indicated that the information provided did not appear to substantiate the conclusion made by the licensee that this was a badge only event. The Agency's position is that the actual shallow dose equivalent (SDE) is currently unknown, and may have exceeded the limit. The Agency has begun their investigation. Additional information will be provided as obtained." Texas Incident Number I-8707 * * * RETRACTION FROM ART TUCKER (VIA EMAIL) TO HOWIE CROUCH @ 0944 EDT ON 3/26/10 * * * "It was determined that the individual was involved in a spill of F-18 and his badge became contaminated causing the exposure. It is believed that the worker contaminated his badge when he removed his gloves after cleaning up the spill. Surveys of the room after the spill indicated that the door handle used to exit the room by the individual was contaminated. The individual performed a contamination survey of his hands after leaving the room and they were not contaminated. Calculations indicate that, based on the specific activity of the F-18 involved, a small fraction of a milliliter would be required to cause this dose to the badge. The Agency agrees that this was a badge only exposure. "This Agency is requesting that this event be retracted." Notified R4DO (Deese) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-03-03
45724 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2010-02-24 11:40 | 2010-02-24 18:10 | 2010-02-25 | AUXILIARY FEEDWATER PUMPS MAY EXPERIENCE RUNOUT AT LOW STEAM PRESSURES "At 1140 CST, both of the stations safety related auxiliary feedwater (AFW) pumps were declared inoperable. The AFW pumps were declared inoperable due to an evaluation that determined that the pumps may experience runout at low steam generator pressures during some design basis events. The stations Technical Specifications require that: 'With both AFW trains inoperable, then initiate actions to restore one AFW train to OPERABLE status immediately.' Technical Specification (TS) 2.0.1 and all TS actions requiring MODE change are suspended until one AFW train is restored to OPERABLE status. "The station is aggressively working to develop a solution to return at least one train of the AFW system to operability." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVID SPARGO TO PETE SNYDER AT 2323 ON 2/24/10 * * * "At 2133 CST, Steam Driven Auxiliary Feedwater Pump, FW-10, was declared operable based on an engineering evaluation that determined FW-10 will perform as required under all design basis conditions. "Motor Driven Auxiliary Feedwater Pump, FW-6, remains inoperable. [The licensee] exited Technical Specification 2.0.1 and 2.5(1)D, and entered TS 2.5(1)B, 24 hour LCO, effective as of 1140 CST." The licensee notified the NRC Resident Inspector. Notified R4DO (Lantz). * * * UPDATE FROM DAVID SPARGO TO DONALD NORWOOD AT 0435 ON 2/25/10 * * * At 0238 CST, Motor Driven Auxiliary Feedwater Pump, FW-6, was declared operable per an Engineering Operability Evaluation. [The licensee] exited Technical Specification 2.5(1)B. The licensee notified the NRC Resident Inspector. Notified R4DO (Lantz). * * * RETRACTION FROM ERICK MATZKE TO JOE O'HARA AT 1625 EST ON 2/25/10 * * * "Further review has determined that the auxiliary feedwater pumps are and have been fully capable of performing their required safety function. Therefore, this notification is being retracted." The licensee notified the NRC Resident Inspector. Notified R4DO(Lantz) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT RHR INOP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2010-02-24
45723 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2009-04-23 | 2010-02-24 16:42 | 2010-02-24 | FAULTY LOGIC BOARD FOR CYBEREX 20 KVA INVERTER MODEL AC The following is a summary of information received via fax: On or around April 23rd, 2009, PSEG Nuclear LLC at Hope Creek Nuclear Station notified United Controls International (UCI), that they had encountered a problem with a Logic Power Supply circuit board (p/n: 90-41-974313) after installing it in their safety related inverter. This circuit board was a Logic Power Supply printed circuit board used in a Cyberex 20 KVA Inverter model AC. Upon inspection, PSEG determined that a jumper was missing from the circuit board by comparison to the originally removed board. The cause of this issue was due to an incorrect bill of materials (BOM) for the circuit board at the manufacturing location. The affected facility is the Hope Creek Nuclear Power Station. Nine boards were all shipped to PSEG at Hope Creek Nuclear Power Station. Preventive Actions Taken: The manufacturer, Thomas & Betts, has corrected the Bill of Materials (BOM) to show the jumper installed on this circuit board. Additionally, UCI has enhanced its inspection schedule for these boards by performing a component level inspection of each board against the BOM. Corrective Actions Taken: Of the nine potentially affected circuit boards - Two circuit boards have been returned to UCI by PSEG and have had the jumpers added and retested. These two were returned to PSEG. Three circuit boards have been verified to have the jumper correctly installed. Corrective Actions to be taken: There are four suspect circuit boards that have been shipped to PSEG (Hope Creek Nuclear Station) that need to be inspected for the correct jumper. If found to be missing the jumper, then these boards need to be returned to UCI for jumper installation and retesting. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-02-24
45722 | 0 | OCONEE NUCLEAR STATION |  |  |  |  | 2010-02-17 06:32 | 2010-02-24 14:44 | 2010-02-24 | POTENTIALLY DEFECTIVE STUD ATTACHMENT TO EMBEDED PLATES "On February 17, 2010, Duke Energy (Duke) completed a reportability determination which concluded that a defect associated with Nelson Stud attachment to embed plates is reportable under Part 21. The embed plates with Nelson studs were procured safety-related from DuBose National Energy Services, Inc. (DuBose) on December 18, 2008. Receipt of the material began as early as August 1, 2009. When delivered to the on-site storage location, it was identified that a Nelson Stud was missing from one of the plates. Follow-up investigation and evaluation identified that automatically timed stud welding procedures/process control weaknesses in the areas of cleanliness and operator/equipment performance have resulted in cold weld joints and weld failures. Duke will provide follow up written notification within 30 days pursuant to Part 21.21(d)(3)(ii). "Initial Safety Significance: None. The potentially defective embedded plates installed in the Protected Service Water (PSW) Building prior to this discovery have not been placed into service. These plates will be removed, abandoned, or re-engineered prior to placing the system in service. However, the embed plates described were to be used for a variety of QA Condition 1 functions, including reaction points for PSW Building structural steel framing and support/restraint of PSW electrical equipment. Depending upon the installation location of these embedded plates and the number and location of ineffectively attached Nelson studs, this deviation could have created a substantial safety hazard were it to remain uncorrected. "Corrective Action(s): "1. Notified vendor (DuBose). "2. Re-work all embeds by installing a fillet weld on each stud. "3. Determine whether the installed embeds will be removed, abandoned, re-engineered. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-02-24
45721 | 0 | CHRISTIANA CARE HEALTH SYSTEM |  |  |  |  | 2010-02-23 11:00 | 2010-02-24 12:56 | 2010-02-24 | POTENTIAL MEDICAL EVENT FROM DOSAGE DELIVERED TO DIFFERENT LOCATION THAN PRESCRIBED "[The patient] completed her prescribed 5 day, 10fx [High Dose Rate] HDR Brachytherapy to the left breast on January 22, 2010, utilizing a multi-lumen mammosite catheter device. On Feb 22, 2010, in follow-up, the patient complained about skin reddening on the external breast, outside of the mammosite catheter insertion site. The medical physicist involved in the treatment planning process was notified about the unusual finding, who upon investigating the treatment and the plan used to deliver the radiation treatment, found that an incorrect measurement resulted in placement of the radioactive source 10 cm away from the intended position, thereby delivering the prescribed dose to a portion of the unintended area. Majority of the dose was delivered in air, but a significantly high dose was delivered to a small volume of the skin distal to the connector end of the catheter, which could have caused the skin reaction. "Description of circumstances that led to the event: On Thursday, January 14 at 1130, [the patient] was brought to the HDR suit for CT simulation and the needed measurements. Following the CT scan of the left breast, the physicist went in the room with the source position simulator (a dummy source wire with the exact length of the actual live source cable) to measure the treatment distance for each catheter (distance to the tip of the catheter). A transfer tube was connected to the proximal end of each catheter and dummy cable was fed through the same till it could not go any further. This point is understood as the tip of the closed end catheter. While the dummy cable was being fed, the physicist felt resistance at 115.2 cm, which he recorded as the distance to the tip of the catheter. He then repeated the same measurement for the other three catheters and found that the distance of resistance was the same. All four lumens were measured and the distances were recorded. This multi-lumen mammosite catheter was the first one to be used on a patient and therefore the physicist assumed that this is the correct distance for this device, although other devices similar to this device have different treatment distances. The physicist did not exert extra pressure on the dummy cable fearing the rupture /malfunction of the catheters. "There were two representatives from the manufacturer present, for proctoring, as this was the first case of the multi-lumen mammosite catheter. The physicist expressed his concern about the unusual treatment distance to one of the representatives, who said that the distance sounded right. "The measured distances were entered in the plan as the position of the first dwell position of the radiation source for each catheter. The treatment plan was generated and sent to the treatment console for storage and treatment execution that next week. The planning system cannot detect any errors in the treatment distance, as long as the distance is within the length of the closed system. "The patient returned for her first treatment on the morning of Monday, January 18, and started with treatments, twice a day for five days. There were no warnings or error messages from the treatment console and the treatments were delivered as planned. "The radiation oncologist reported that the mammosite multi-lumen catheter had no unusual aspects or appearance at either insertion at surgery or at extraction after the last treatment fraction. "Discovery of the error: Soon after the physician's follow-up meeting with the patient, Monday, February 22, 2010, the physicist was informed about the unusual skin reaction on the patient, on February 22, 2010. The physicist immediately began investigating the treatment records and the treatment plan. He then tried to measure the treatment distance on a sample mammosite multi-lumen device which the manufacturer had provided, as a test device, with the same source position simulator and encountered a similar resistance at the exact same distance. But when exerted more pressure on the source cable, it advanced further and the distance turned out to be 125.2, which was 10 cm longer than the measurement done on the patient. This observation led him to conclude that the patient did not receive the treatment at the intended area, but at 10 cm proximal to the catheter tip, which included some skin and tissue of the external breast medial to the entry point of the device where the skin reaction is. The physicist recalled similar resistance on the dummy source cable on other occasions, which leads to a possible fault with source position simulator assembly. It was also possible that the lumens were kinked at some point inside, where the housing of the lumens was bent (to facilitate wound dressing), thereby causing resistance for the advancing of the dummy source cable. "A treatment plan was generated that night representing what happened and the following conclusions were made upon review by physics staff that next morning, February 23, 2010, regarding the treatment of the unintended tissue and skin: "a. An average dose of 1700 cGy was delivered to approximately 100 cc of the unintended breast tissue. "b. About 7.5 cc of the skin and underlying tissue received a high maximum dose of 6800 cGy (possibly the area of skin reaction) "c. 35 cc of the intended breast tissue received an average dose of 340 cGy (10% of the total prescribed dose) "Recommendations: "1. The physicist should make a list of treatment distances for all standard applicators including partial breast treatment devices and catheters. "2. Include a therapist or a nurse in the process of all patient measurements and have them double-check the patient measurements. "3. Acquire a new source position simulator assembly and a set of transfer tubes. "4. Make a second measurement of the treatment distance on all patient catheters prior to the first treatment." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-03-02
45720 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-02-19 | 2010-02-24 11:11 | 2010-02-24 | AGREEMENT STATE REPORT - STUCK PROCESS GAUGE SHUTTER The following information was received from the State of Texas via email: "On February 23, 2010, at 1500 hours, the [State of Texas] was notified by the licensee that the operating mechanism for the shutter shielding device on a Thermo Fisher model 5201 nuclear gauge had failed. The gauge is normally operated with the shielding for the source in the open position. The licensee stated that the current condition of the gauge poses no additional health risk to individuals. The gauge contains a Cesium (Cs)-137 source with an original activity of 100 milliCuries. The gauge is located 10 feet off of the ground and is accessed using a ladder to a platform. The area has been posted to prevent anyone from performing maintenance in the area. The licensee has contacted the manufacturer to repair the gauge. [State of Texas] will provide additional information as it is obtained." TX Report I-8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-03-01
45719 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2010-02-23 15:12 | 2010-02-23 16:58 | 2010-02-23 | DEGRADED CONDITION - WELD LEAK DUE TO VIBRATING VALVE ATTACHMENT WIRE "On 2/22/10, we determined that there was pressure boundary leakage on Unit 2 from the leak off line associated with a pressurizer spray valve (2-RC-220). The source of leakage associated with a boron deposit discovered earlier on 2/18/10. The boron deposit formed based on a leak in a Class 1 manual valve packing leak-off line. The leak location was determined to be in the packing leak-off pipe fillet weld to the stem retaining structure of the valve in the packing gland area. The valve (2-RC-220) is a Class 1 pressure boundary. The packing leak-off line is considered an auxiliary connection in the stem retaining structure of the valve. "At this time, we believe the most probable cause of the 2-RC-220 leak-off line socket weld leak was based on two factors, a small pore in the original socket weld metal and the location of a valve tag attachment wire. The leak location coincided with the location where a valve tag attachment wire laid across the weld. It is possible this wire, vibrating against the weld, opened up a subsurface pore in the weld metal which began to leak sometime after startup from the 2009 RFO [Refueling Outage] (March 2009). Since the failure may have occurred due to a material problem that resulted in abnormal degradation of a principal safety barrier (i.e., it is necessary to take corrective actions to restore the weld's integrity), this event is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A). The valve was overhauled in the 2009 RFO and subsequently passed VT-2 inspection. The overhaul did not include any welding on the affected joint. "Unit 2 is in Mode 5 to allow repairs to be made to this weld." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-02-23
45718 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2010-02-23 01:00 | 2010-02-23 16:00 | 2010-02-25 | ERDS NOT AVAILBLE DUE TO PLANT COMPUTER MALFUNCTION "The Emergency Response Data System (ERDS) link from the Critical Function Monitoring System (CFMS) was lost at approximately 0100 hours on February 23, 2010 due to a malfunction of the plant computer. Other systems such as Safety Parameter Display System (SPDS), RECS, and ENS remain available. In accordance with the site reporting procedure, a loss of ERDS for greater than 16 hours is reportable as a major loss of emergency assessment capability. Troubleshooting is in progress." The licensee has notified the NRC Resident Inspector and will notify the state. * * * UPDATE FROM THOMAS RAS TO JOE O'HARA AT 1724 ON 2/25/10 * * * ERDS was restored to operable status at 1652 EST. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-23
45717 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-02-23 11:00 | 2010-02-23 14:05 | 2010-03-11 | UNANALYZED CONDITION - INCOMPLETE LIST OF SAFETY CONTROLS IN INTEGRATED SAFETY ANALYSIS SUMMARY "During a [Global Nuclear Fuel, Americas] GNF-A ongoing review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was discovered at 3pm yesterday (2/22/2010) that the list of safety controls associated with the handling of hydrofluoric material may be incomplete in the ISA Summary. "After further review, it was determined this morning that the list of Items Relied on for Safety (IROFS) was incomplete, and as a result, the UF6 conversion area has been shut down pending revision of the ISA to document IROFS for these processes. UF6 conversion will remain shutdown until IROFS have been identified and implemented. "While this discovery did not result in an unsafe condition, it is being reported on 2/23/2010 pursuant to the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours." The licensee notified NRC Region 2 (Rich) and will notify the state and local authorities. * * * UPDATE FROM PHILLIP OLLIS TO DONG PARK AT 0905 EST ON 3/11/10 * * * "During the GNF-A ongoing review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was determined at 10:30am yesterday (3/10/2010) that the list of IROFS associated with the storage of uranium hexafluoride cylinders may be incomplete in the ISA Summary. As a result, conservative compensatory management measures for UF6 cylinder storage have been implemented pending revision of the ISA to document IROFS for these areas. "While this discovery did not result in an unsafe condition, it is being reported as an addendum to event report 45717 pursuant to the requirements of 10CFR70 Appendix A(b)(1) within 24 hours." Notified R2DO (Nease) and NMSS EO (Benner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-02-23
45716 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2010-02-23 09:45 | 2010-02-23 13:56 | 2010-02-23 | AGREEMENT STATE REPORT - GAMMA KNIFE TREATMENT TO WRONG LOCATION A gamma knife treatment prescribed to be administered to the left side of a patient was instead administered to the patient's right side. The scheduled 30 minute, 90 Gray procedure was terminated after 1.4 minutes when the administering physician detected the error. It is estimated that 4% of the prescribed dose was administered to the wrong area. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2010-03-01
45715 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2010-02-19 21:45 | 2010-02-20 03:49 | 2010-02-20 | SPECIFIED SYSTEM ACTUATIONS DUE TO LOSS OF THE 'A' SAFEGUARDS TRANSFORMER "At 2145 CST on 2/19/2010, the Callaway Plant experienced a loss of switchyard bus 'A'. This resulted in a loss of off site power to 'B' train vital 4160 volt bus NB02. Technical specification LCO 3.8.1 was entered. The 'B' train emergency diesel generator started and the shutdown sequencer actuated for bus NB02. 'B' motor driven auxiliary feed water pump, 'B' centrifugal charging pump, and both 'A' and 'B' essential service water pumps started. The turbine driven auxiliary feed water pump actuated, and steam generator blowdown and sample isolation occurred. 'A' train offsite vital power and emergency diesel generator were available. The actuations that occurred were consistent with the loss of one vital AC train. All emergency systems responded as expected with the exception of steam generator blowdown valve BMHV0002 which was manually isolated when it failed to fully close. "The loss of switchyard bus 'A' was due to a fault on the 'A' safeguards transformer. The faulted transformer has been isolated, and switchyard bus 'A' was reenergized at 0132 on 2/20/2010. The 'B' train vital 4160 volt bus NB02 was tied to offsite power at 0222 on 2/20/2010, and the 'B' emergency diesel generator was secured at 0233 on 2/20/2010. Technical specification LCO 3.8.1 was exited. "Currently the plant is at 100% power. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-02-20
45714 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-02-21 08:00 | 2010-02-19 18:12 | 2010-02-19 | PLANNED POWER OUTAGE AT PRIMARY EMERGENCY OPERATIONS FACILITY (EOF) "Southern California Edison has planned work scheduled for the San Onofre Emergency Operations Facility (EOF), for Sunday, February 21, 2010. The work is being done in order to replace a faulty circuit breaker and will result in area lighting being out in the building from approximately 0800 through 1600. During the time that the lighting is out, the EOF will be considered non-functional. Should conditions occur that would merit activation, EOF responders would be directed to the alternate EOF located in Irvine, CA. "This planned EOF outage is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM TOM SIMMONS TO DONG PARK AT 2042 EST ON 2/21/2010 * * * "Follow up phone call to one made on 2/19/10 regarding planned power outage at normal EOF. Commenced 1145 [PST] today (2/21); restored 1715 [PST]." The licensee will notify the NRC Resident Inspector. Notified R4DO (Miller) | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-19
45713 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-02-01 | 2010-02-19 14:56 | 2010-06-10 | AGREEMENT STATE REPORT INVOLVING AN UNACCOUNTED FOR GENERAL LICENSE SOURCE The following information was received from the State of Mississippi Division of Radiological Health (DRH) via email: "Description of Incident: The licensee contracted with a disposal company to dispose of one (1) Industrial Dynamic Model C1-2C FILTEC source holder, Serial No. 555, source. During the disposal company's visit, it was discovered that the source was not in the source holder and could not be accounted for. The facility has changed ownership in the previous years and the records were not well maintained of receipt/transfer and leak tests. The Industrial Dynamic Model C1-2C FILTEC source holder, contained a 100 millicurie Americium-241 source, Serial No. not known. "Isotope(s): Americium-241 "Activity: 100 millicuries "Date of Incident : unknown "Date Reported To DRH: 02-01-10 "Mississippi Incident No.: MS-10001" * * * UPDATE FROM JAYSON MOAK TO PETE SNYDER ON 6/10/2010 AT 1109 EDT * * * The following information was received from the State of Mississippi Division of Radiological Health (DRH) via email: "The licensee performed an investigation into the missing source after receiving a notice of violation issued 03-03-2010. The licensee determined the following from their investigation: "(1) Records obtained from Industrial Dynamics, indicated that all sources were removed from the Filtec C1-2C gauges installed at the Vicksburg plant as well as replacement units recently removed. It appears that the source was removed in 1984 from one Filtec C1-2 gauge Ser. No. 00212, and the gauge remained at the plant. The Ser. No. 00212, for the Filtec C1-2C gauge was deciphered only from the inside cover of an instruction manual found at the plant. "(2) a sticker, SN:555, was found on or near equipment in storage, but the sticker referenced something manufactured by Nuclear Enterprises Incorporated. The licensee believes the sticker may be referencing a serial number to a machine part and not the source holder in question. This may be where the incorrect reference to a serial number came into question. The licensee believes the former RSO started leak testing the empty Filtec C1-2C gauge Ser. No. 00212, in 2004, and placed a radioactive material label on the empty gauge in 2005, due to the type of equipment it was. "(3) The only piece of equipment, a partially dismantled Industrial Dynamics/Filtec C1-2C gauge remaining at the facility may have at one time contained a sealed source. This equipment was inspected by Adco Services , the source holder was found to be empty, and a report issued to DRH on 1-12-2010. "(4) The licensee contacted Industrial Dynamics/Filtec and traced the history of source Ser. No. 555. The licensee reported Industrial Dynamics/Filtec claimed the source holder has never been installed in a gauge in Mississippi. "The licensee submitted their response and investigative report to DRH on 04-21-2010, and claims it no longer possess any sources of radiation in the state. The violation issued on 03-03-2010 has been rescinded along with termination of GL-154." Notified R4DO (Powers) and FSME (Mauer). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2010-02-24
45712 | 0 | SIKORSKY AIRCRAFT CORPORATION |  |  |  |  | 2010-01-22 14:30 | 2010-02-19 12:10 | 2010-02-19 | LOST NUCLEAR GAS LEAK DETECTOR On January 22, 2010, the Radiation Safety Officer discovered two missing Leakmeter 200 gas leak detectors during an inventory inspection. The Leakmeter 200 is manufactured by USON and each contain a 10 mCi Ni-63 source. After investigating the incident, one of the employees believes that these leak detectors were sent to a scrapping facility back in September of 2009. The licensee believes that the sources have been disposed of properly and does not pose a safety threat to the public. #1 Leakmeter Serial number/Source number: 2002053/977502 #2 Leakmeter Serial number/Source number: 2002054/977506 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-02-19
45711 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-02-19 11:11 | 2010-02-19 11:33 | 2010-02-19 | UNSUAL EVENT DUE TO CARBON DIOXIDE DISCHARGE IN THE HIGH PRESSURE COOLANT INJECTION (HPCI) ROOM The licensee reported that a CO2 discharge has occurred in the Unit 1 HPCI room. The cause and amount of CO2 released is not specifically known but the licensee judged that the room was not currently habitable based on the CO2. The licensee consequently declared an Unusual Event (UE) under EAL HU3.1 - "Toxic, Corrosive, Asphyxiant, or Flammable Material in Amounts That Could Adversely Impact Plant Operations. " The licensee stated that activities were in progress in the room at the time of the discharge. There is no indication of a fire in the room and there were no personnel injuries as a result of the discharge. The discharge also had no impact on plant operation. The licensee at this point plans to terminate the UE when the room is properly ventilated. The licensee has notified State and local authorities and the NRC Resident Inspector and does not plan a press release. * * * UPDATE FROM GARY ROBERTS TO DONG PARK @ 1354 EST ON 02/19/10 * * * At 1330 EST on 2/19/10, the Unusual Event was terminated. The atmosphere in the HPCI room is back to normal. The CO2 source was from cylinders located in the HPCI room which is part of the fire suppression system. The licensee has notified the NRC Resident Inspector. Notified IRD (Grant), R2DO (Bartley), NRR EO (Thorp), DHS (Vestal) and FEMA (Fuller). | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-02-19
45710 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-02-18 19:15 | 2010-02-18 19:42 | 2010-02-18 | RCS PRESSURE BOUNDARY LEAKAGE IDENTIFIED ON RTD WELD "Catawba Nuclear Station is making an 8 hour notification due to a pressure boundary leak on the A loop of the Unit 1 Reactor Coolant System. The leak was found to be originating from 1A Reactor Coolant System hot leg [Resistance Temperature Detector] RTD penetration. Since the allowance for pressure boundary leakage is zero, this is being considered a degraded principal safety barrier. No safety signals were received and no actuations occurred as a result of this leak. The amount of the leak is small and is contained inside containment. No release to the environment occurred and there is no danger to the public. Repair will require the plant to enter Mode 5." The pressure boundary leakage is 0.08 GPM. The licensee is in a 36 hour LCO 3.4.13(B)(2), and plans to be in Mode 5 this evening. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-02-18
45709 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-02-18 08:24 | 2010-02-18 11:47 | 2010-02-18 | DUAL UNIT AUTOMATIC REACTOR TRIPS DUE TO PARTIAL LOSS OF OFFSITE POWER "Both U-1 and U-2 automatically tripped due to valid actuation of the Reactor Protection Systems (RPS). U-1 due to loss of 12B Reactor Coolant Pump (RCP) which resulted in a RCS Low Flow RPS Trip. Cause for loss of 12B RCP is currently not known but is suspected to be related to the electrical transient that occurred on U-2. U-2 tripped due to Loss of Load RPS Trip when the main turbine tripped due to an electrical malfunction and partial loss of offsite power. The electrical malfunction resulted in loss of power to all 4 Kv buses on U-2 with the exception of 21 4Kv bus (ZA train power) (Lost 22-26 4Kv buses) and the loss of 14 Kv bus (ZB train power) on U-1. All the buses lost are powered from the same in house service transformer, P-13000-2, which was lost due to the electrical transient. Cause of the electrical transient is being pursued but is unknown at this time. Loss of the 14 4Kv bus on U-1 and the 24 4Kv bus on U-2 resulted in an Engineered Safeguards Actuation System (ESFAS) valid actuations on both units due to Under Voltage (UV) conditions on those buses. The 1B [Diesel Generator] DG started automatically due to the 14 bus UV and is carrying that bus. The 2B DG received an automatic start signal due to the 24 bus UV but failed to start as expected. No other system actuations occurred. Both units are currently stable in Mode 3 at normal operating temperature (532 degrees) and pressure (2250 PSIA) with no other significant equipment malfunctions. Due to the loss of P-13000-2 [transformer], U-2 sustained a loss of normal heat removal due to loss of the main condenser cooling and the loss of secondary pumps. U-2 is removing heat with auxiliary feedwater pumps and [Steam Generator] SG atmospheric dump valves without issues. Current plans are to cool U-2 down to 445 degrees to maintain RCP seals cool until RCP's can be restarted. A decision on U-1 cool down has not yet been made." There is no primary to secondary leakage. U-2 is currently in a 12 hour LCO due to the partial loss of offsite power and 2B DG failing to start. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  |  | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-02-18
45708 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-12-10 | 2010-02-18 10:58 | 2010-02-18 | AGREEMENT STATE REPORT - SOURCE STUCK IN CATHETER TUBE The following information was obtained from NMED: "The Methodist Hospital reported that a 1.91 GBq (51.57 mCi) Sr-90 source (BEBIG model Sr0.S03, serial #ZB523) became stuck in a catheter during a patient's treatment on 12/10/2008, using a Novoste Beta-Cath system (model A1732, serial 91277). The catheter was removed from the patient and placed into a bailout box. The bailout box was returned to storage and additional shielding was used to ensure dose rates in the area were ALARA. There was no additional exposure to any individual involved. A preliminary visual inspection of the device indicated that there may be a small kink in the capillary tube, which prevented the source from returning to its secured location. The source was returned to the manufacturer for further investigation. The manufacturer determined that the source became stuck due to kinks in the delivery catheter. They provided additional guidance to the hospital in the use of the system to help minimize recurrence." The State of Texas discovered that the event was reported to NMED but not to the NRC Headquarters Operations Center as required therefore they are making a late report. Texas Report Number: I-8590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-02-23
45707 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-02-12 | 2010-02-17 18:52 | 2010-02-17 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received via e-mail: "A CPN moisture density gauge (model MC3, serial # M330506989) was reported to have been stolen over the recent four day weekend from a construction site in Hesperia, between Main St. and Smoke Tree Lane. The gauge was reportedly taken with the transportation container, which was secured inside a locked construction trailer. The RSO believed that the authorized user had locked the transportation container [prior to] the period during which the gauge was stolen. "The [theft of the] gauge was reported to the Hesperia Police in San Bernardino County. The RSO was informed by RHB [Radiologic Health Branch] that a reward should be offered for the return of the gauge. The RSO indicated he would discuss posting of a reward with the company insurance carrier." The gauge contains a 10 mCi Cs-137 gamma source and a 50 mCi Am-241/Be neutron source. California Incident No: 5010-021710 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-02-22
45706 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-02-17 14:20 | 2010-02-17 16:24 | 2010-02-17 | NOTIFICATION TO PENNSLYVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION CONCERNING DRINKING WATER QUALITY "The following is a 4-hour non-emergency notification in accordance with 10CFR50.72(b)(2)(xi), Offsite Notification. "At 1420, February 17, 2010, Susquehanna LLC notified the Pennsylvania Department of Environmental Protection (DEP) of an issue with the domestic water supply system at the Susquehanna facility. This notification was made via telephone. "The notification to Pennsylvania DEP was in accordance with 25 PA Code 109.1307 due to circumstances that exist that adversely affect the quality of drinking water. Specifically, no residual chlorine was detectable in the domestic water system. The Pennsylvania DEP contact was the Pennsylvania DEP Sanitarian. "Required compensatory actions have been initiated, including planned repairs of the domestic water chlorination system." The licensee notified the NRC Resident Inspector | 86 | 94 | 0 | 86 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-02-17
45705 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-02-16 | 2010-02-16 22:18 | 2010-02-17 | SCHEDULED MICROWAVE RADIO UPGRADES IMPACT TO THE CONTROL ROOM AND EMERGENCY OPERATIONS FACILITY "This is an eight hour report per 10 CFR 50.72 (b)(3)(xiii). Calvert Cliffs will be implementing a scheduled modification to upgrade the microwave radio system to improve reliability of the system at the Emergency Operations Facility (EOF), State, and County facilities. "This work will require that the microwave radio system at the EOF be removed for a period of approximately 4 to 6 hours. During this time, the following systems will be impacted for the duration of the upgrade: "1. The plant's {e.g., Control Room, Technical Support Center (TSC), Simulator} Dedicated Offsite Agency telephones will be out of service. (EOF's system will continue to function) "2. 800 MHz desk set radios at the EOF only will be out of service. "3. 153.44 MHz frequency at the EOF only will be out of service. (backup for MEMA and MDE) "4. MIDAS Terminal (Meteorological Data) located in the Dose Assessment Office at the EOF will be out of service. "5. TSC Computer data transfer to the EOF only will be out of service. "Once the upgrade starts the systems (listed above) can be returned to service within the first 2 hours. After the 2 hour timeframe, the upgrade must continue until completed. "Should an emergency be declared during this period, the Control Room will continue to have the capability to make the notification to the offsite agencies using the direct line for the appropriate agencies. The emergency preparedness communications procedure provides a chart listing the communication devices available and the order in which the process is to be implemented. MIDAS (Meteorological Data) will continue to be operational at the site and can be obtained by contacting the Control Room or TSC. The ERPIPs also provide a backup process and the instructions necessary for the EOF Dose Assessment Office to obtain Meteorological Data. Plant data can be obtained from the CR or TSC and will continue to be downloaded from the plant computer to the ERO SharePoint site. "All work associated with this microwave radio system upgrade will be performed in an expeditious manner consistent with the goal of minimizing unavailability of the systems listed above. A test of all systems will be performed at the completion of the upgrade. "All EOF responders and Control Room personnel have been briefed on this work and expected contingent actions. "This job will start on Wednesday, February 17, 2010 at approximately 7:00 am. We anticipate that all work will be completed by 5:00 pm on the same day, including testing of the system. We will provide a notification update upon completion of the job." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TOM JONES TO DONALD NORWOOD AT 1217 EST ON 2/17/2010 * * * All communications systems were tested and returned to operable status as of 1200 EST. The licensee notified the NRC Resident Inspector. Notified R1DO (Jackson). | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-16
45704 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-02-11 | 2010-02-16 17:16 | 2010-02-16 | AGREEMENT STATE REPORT - FAILURE OF FIXED GAUGE SHUTTER MECHANISMS TO CLOSE The following excerpted information was received via e-mail: During shutter checks performed by the licensee, it was discovered that four of their fixed gauge shutter mechanisms were unable to be closed. The following is information on those gauges: (1) Berthold, Model LB-7440-D, source SN FR288, Cs-137, 30 mCi; (2) Berthold, Model LB-300-L, source SN 1080/1-05-98, Co-60, 1.16 mCi; (3) Berthold Model LB-7440-D, source SN 1080/2-05-98, Co-60, 1.65 mCi; and (4) Berthold, Model LB-7442-D, source SN 2572-8-90, Cs-137, 250 mCi. On gauge 1 the shutter handle broke off. On gauges 2, 3, and 4 the shutter stuck open. The licensee has requested service from the gauge manufacturer. Mississippi Incident Number: MS-10002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2010-02-19
45703 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2010-02-16 10:30 | 2010-02-16 17:53 | 2010-02-16 | FITNESS FOR DUTY EVENT - CONFIRMED POSITIVE FFD TEST A licensed, non-supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the facility has been suspended. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2010-02-16
45702 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-02-16 | 2010-02-16 16:16 | 2010-02-16 | AGREEMENT STATE REPORT - MISPOSITIONED DOSE DURING MEDICAL TREATMENT The following information was received from the State via e-mail: "The two reported cases are single channel MammoSite patients. The errors resulted from erroneously placing the dwell position approximately 2 to 2.5 cm proximal to the correct position. The error was not noticed until 2/14/10 during a document review for [the second] patient after [the eighth] fraction. The last two fractions for [the second] patient were corrected. It appears that about 50% of the correct treatment volume received at least 50% of the prescribed dose. Some parts of the planned volume received greater than 700%. Also there are volumes that are not included in the planned treatment volume that exceed approximately 300% to 400% of the prescribed dose. The proximal skin received a small sliver of dose at the 125% the prescribed dose. "First patient's treatment had been completed in January before the error was noticed. Probably 25% of the planned volume received the prescribed dose or higher. Probably 25% of the planned volume received 25% or less than of the prescribed dose. A large volume outside the planned treatment volume exceeded the prescribed dose. The maximum proximal skin dose was at approximately 220% of the prescribed dose. The desired dose was 340 cGy/fx * 10. Both doctors and patients have been notified. "Health effects, if any, are still being determined. The licensee will send a written report on this incident." The State of Florida is investigating. The isotope involved is 9.76 Curies of Ir-192. Florida Incident Number: FL 10-027. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-02-22
45701 | -1 | WATERFORD | 3 |  |  | [3] CE | 2010-02-15 19:15 | 2010-02-15 20:46 | 2010-04-19 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM THAT COULD ALLOW POSSIBLE UNAUTHORIZED OR UNDETECTED ACCESS Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTED ON 4/19/2010 AT 1701 EDT FROM MIKE MASON TO RYAN ALEXANDER * * * The licensee has retracted this notification on the basis that there was no uncompensated potential vulnerability in the safeguard system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R4DO (Whitten). Notified via email ILTAB and 73.71 via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-02-15
45700 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2010-02-15 09:05 | 2010-02-15 16:42 | 2010-02-15 | FITNESS FOR DUTY EVENT - CONFIRMED POSITIVE FOR CONTROLLED SUBSTANCE USE A non-licensed, contract supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 26.719 |  |  |  | 0 | 2010-02-15
45699 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-02-15 12:05 | 2010-02-15 15:28 | 2010-02-15 | FITNESS FOR DUTY EVENT - POSSESSION OF ALCOHOL INSIDE THE PROTECTED AREA A non-licensed, non-supervisory employee was found in possession of alcohol inside the protected area. For-cause fitness-for-duty testing was conducted with negative results. The individual's unescorted access has been prohibited pending further investigation. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2010-02-15
45698 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-02-15 09:30 | 2010-02-15 08:58 | 2010-02-15 | UNAVAILABILITY OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) DUE TO PLANT PROCESS COMPUTER (PPC) SCHEDULED MAINTENANCE "At 0930 on Monday, February 15, 2010, the Cook Nuclear Plant (CNP) Unit 2 Plant Process Computer will be removed from service for scheduled maintenance for data backup and preventative maintenance which will take ERDS out of service to the NRC Operations Center. The scheduled maintenance will affect the Safety Parameter Display System (SPDS) and the Real Time Data Repository (RDR), PPC data to Emergency Response Facilities at CNP. "The scheduled maintenance is expected to take up to 6 hours to complete. "Compensatory measures exist within the CNP Emergency Response procedure to provide plant data via the Emergency Notification System to the NRC Operations Center until the ERDS can be returned to service. "The licensee notified the NRC Resident Inspector 2/15/2010 at 8:45 a.m. "This notification is being made in accordance with NUREG 1022 Revision 2 for CFR 50.72 (b)(3)(xiii) due any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)." The unit is expected to be maintained at 100% during the maintenance evolution. PPC trending and indication and rod position monitor will be out of service (OOS) while the PPC is OOS. * * * UPDATE FROM BRAD LEWIS TO DONALD NORWOOD AT 1205 EST ON 2/15/2010 * * * The DC Cook U-2 Plant Process Computer was returned to service and a fully operable and available status at 1144 EST on 2/15/2010. The licensee notified the NRC Resident Inspector. Notified R3DO (Peterson) via E-mail. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-15
45697 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2010-02-12 | 2010-02-12 13:40 | 2010-02-16 | INTERIM REPORT CONCERNING AN ISSUE IN SUMP BLOCKAGE GENERIC TESTS Westinghouse is evaluating an identified inconsistency between test assumptions and the test rig configurations used for Generic Safety Issue (GSI) 191, "Assessment of Debris Accumulation on PWR Sump Performance," testing. Specifically, this issue is related to jet impingement zone-of-influence (ZOI) tests and it applies to testing done for coatings and insulation. Prior to discovery of the inconsistency, Westinghouse provided letters to the utilities to summarize the testing, analyze the test results, and propose acceptable ZOIs to support resolution of the ZOI aspect of GSI-191. The ZOI tests assumed the smallest diameter in the nozzle producing the jet to be at the nozzle. Westinghouse discovered however, that the inner diameter of an upstream component was smaller than the nozzle. This inconsistency may have resulted in undersized ZOIs being proposed in the letters. Westinghouse has not yet concluded its determination as to whether there is a defect as defined by 10 CFR 21. Westinghouse has been working with the Pressurized Water Reactors Owners Group and the NRC NRR Safety Issues Resolution Branch to resolve general test protocol issues and establish methods to evaluate the test results in terms of ZOIs. * * * UPDATE ON 2/16/2010 * * * Corrected the title of GSI-191 above and removed incorrect reference to NUREG/CR-6874 since it is not related to the Part 21. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-02-12
45696 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2010-01-06 | 2010-02-12 12:28 | 2010-02-12 | INSTALLATION OF INCORRECT TRANSFORMER ON A CONTROL BOARD FOR A BATTERY CHARGER On January 6, 2010, Thomas & Betts (TNB) informed United Controls International (UCI) that TNB's sub-contractor (RBB Systems) had installed the incorrect transformer on a sub-component (control board) of a Cyberex battery charger. During a review of the Bill of Material (BOM) and assembly documentation for the control board by TNB, it was discovered that the incorrect transformer was being installed on the board. The control board affected is designed for systems with a 120 VAC primary input voltage. The incorrect transformer installed is designed for systems with a 208 VAC primary input voltage. Subsequent testing and risk assessment performed by TNB's sub-contractor, RBB Systems, found that under nominal input voltage, the control card operated marginally. Under low input voltage, the card could fail to operate properly, which could cause a failure of its parent component, the battery charger. Per TNB, the only sale on record of the Cyberex battery charger is of eight units sold to Philadelphia Electric Company (now part of Exelon-Peach Bottom Nuclear Power Station) in 1993, which are designed for 120 VAC primary input voltage to the control board. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2010-02-12
45695 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-02-10 | 2010-02-12 10:45 | 2010-03-23 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT DUE TO UNDERDOSE GREATER THAN 50% The following was received from the Commonwealth of Massachusetts via e-mail: "On 2/12/10, licensee reported to this Agency [Commonwealth of Massachusetts] the 2/11/10 discovery of a medical event that occurred on 2/10/10. The situation [was] described as two treatment fraction underdoses, delivered on the same day to the same patient, that differed from the prescribed dose, per fraction, by more than 50%. Initial indication [is] that [the] event was caused by [an] equipment software bug. Two fractions of 0.4 Gy were delivered on the first day of treatment. The prescription was for two treatments of 4 Gy per fraction per day for two days and one final 4 Gy treatment on the third day. [The] prescribing physician and equipment manufacturer [were] notified. This is a preliminary report; investigation [is] ongoing; more information to follow. "The Agency considers this event OPEN and ONGOING." * * * UPDATE FROM TONY CARPENITO TO JOE O'HARA VIA E-MAIL AT 1007 ON 2/17/10 * * * "[The] equipment manufacturer found the software issue to be 'reproducible' and therefore may be classified as a 'potential' (patient) safety issue. "[The] suspect portion of software will not be used again until [the] program [is] debugged and documented to be correct. [The] suspect portion of the software had not been used in the past by the licensee; no previous patients were affected." The device has been identified as a Nucletron HDR V3, and the software program is named Oncentra. Event docket #02-8893. Notified R1DO(T. Jackson) and FSME EO(McIntosh) * * * UPDATE FROM TONY CARPENITO TO HUFFMAN VIA E-MAIL AT 1448 ON 3/23/10 * * * "The equipment manufacturer published a customer information bulletin describing the problem. The licensee submitted a formal follow-up report to this Agency [Commonwealth of Massachusetts] on 2/25/10. The licensee wrote that since the underdose could be made up there will be no effect on the treatment outcome. There is no radiation morbidity. Patient underdose on 2/10/10 was 90%. The Agency considers this matter to be closed." Notified R1DO(Caruso) and FSME EO(Kock). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-02-18
45694 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-02-11 13:10 | 2010-02-11 20:36 | 2010-02-11 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR DENSITY GAUGE The following report was received via e-mail: "At 1310 [PST] on February 11, 2010, the C.Y. Geotech Radiation Safety Officer [RSO] reported that one of the nuclear density gauges (CPN, MC-1DRP, MD90905316 containing 10 milliCurie of Cesium 137 and 50 milliCurie of Americium-241:Be) had been run over by a truck at a construction site. Los Angeles County Radiation Management responded to the scene and found that although the source rod was broken and the plastic case was broken into pieces, the Cesium 137 and the Americium-241:Be sources were still in the shielded body of the device and were intact. There was no contamination. The highest dose rate on the body of the device housing the sources was 9 mR/hr and at one foot was 0.9 mR/hr. The gauge was placed into 2 plastic bags and was placed into the transportation case. The licensee will deliver the gauge to Maurer Technical Services (a licensed CPN representative) who will then ship the gauge to CPN for disposal. [The RSO] reported the gauge user walked about 10 feet away from the gauge to report his test results to a job supervisor and this is when the gauge was run over. The RHB-Brea office will cite the licensee for failure to maintain adequate control over the gauge. The licensee has been instructed they need to provide [California Radiation Control Program] with a report within 30 days as required by regulation. The licensee states they will retrain all of the gauge users regarding the control of the gauge to avoid a similar incident in the future. "Event Location: 951 25th Street, Santa Monica, CA" California Event Number: 021110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-02-16
45693 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-02-11 08:00 | 2010-02-11 08:00 | 2010-02-11 | TECHNICAL SUPPORT CENTER EMERGENCY VENTILATION SYSTEM MAINTENANCE "On Thursday, February 11, 2010, the Limerick Technical Support Center (TSC) emergency ventilation system will be removed from service for planned preventative maintenance activities on the damper flow controller and air filtration charcoal system. During the maintenance, the non-emergency ventilation system will be functional. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 12 hours. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing EP [Emergency Planning] procedures and checklists. If radiological conditions require TSC facility evacuation during ventilation system restoration, the Station Emergency Director will evacuate and relocate the TSC staff in accordance with applicable site procedures." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BRANDON SHULTZ TO DONG PARK ON 2/11/10 AT 1721 EST * * * The maintenance on the Limerick Technical Support Center (TSC) emergency ventilation system has been completed and the TSC is available. The licensee has notified the NRC Resident Inspector. Notified R1DO (Powell) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-11
45692 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-02-09 18:00 | 2010-02-09 22:49 | 2010-02-09 | POTENTIAL POST FIRE SAFE SHUTDOWN UNANALYZED CONDITION "A potential Post-Fire Safe Shutdown issue associated with the 'B' Emergency Diesel Generator Voltage Control Circuitry has been discovered, should a Control Room fire cause a hot short in the 'B' EDG Voltage Control Circuitry. A fire in the control circuit that renders the 'B' EDG inoperable and is large enough to require the Control Room to be evacuated during a loss of offsite power is an unanalyzed condition. This condition was discovered during a planned maintenance outage for the 'B' EDG. Compensatory measures are being established for early detection and extinguishment of a fire associated with this circuit in the Control Room. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-02-09
45691 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-02-08 12:30 | 2010-02-09 10:54 | 2010-02-09 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO FULLY RETRACT "On February 9, 2010, the Agency [Texas Department of Health] was notified by the licensee that while performing radiography with a 22 curie Iridium (Ir)-192 source, the source could not be retracted into the camera. The device is an Amersham 660B camera. The radiographer noted that when he returned the source to the camera, the auto locking mechanism failed to activate. The radiographer then cranked the source back out and tried again to locked the source in the camera. The locking mechanism failed to lock. The source drive cable was left in the position where the source should be shielded. The radiographer performed a dose rate survey on the guide tube. He found the dose rates near the end of the guide tube were elevated. He contacted his Radiation Safety Officer. An individual listed on the license to perform source retrieval went to the location and retrieved the source. No over exposures were reported. An inspection of the source pig tail and drive cable found that the connection of the drive cable to the source pig tail failed because the ball on the drive cable side of the connection had broken off from the drive cable." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-02-12
45690 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2010-02-09 09:00 | 2010-02-09 09:57 | 2010-02-09 | OFFSITE NOTIFICATION TO SOUTH CAROLINA DHEC CONCERNING TRITIUM FOUND IN GROUND WATER "Event Description: Ground water monitoring wells were installed on the Oconee site and initially sampled in 2008 in support of the Nuclear Energy Institute (NEI) Ground Water Protection Initiative (NEI 07-07). As part of an on-going investigation, a number of new monitoring wells have been installed and additional wells are in progress at Oconee. On February 8, 2010, Oconee was notified by the Duke Energy Environmental Lab that samples taken on January 26, 2010, from monitoring wells GM-7R and GM-7DR displayed tritium levels of 24,400 pCi/l and 35,400 pCi/l respectively, triggering the communication protocol of the NEI initiative. The threshold for initiating the communication protocol is 20,000 pCi/l. There is no public or plant worker risk associated with the GM-7R and GM-7DR well samples. Wells GM-7R and GM-7DR are not drinking water sources and therefore, there is no potential dose to the public or plant workers. Samples from surrounding monitoring wells indicate that tritium in ground water has not migrated off the plant site. Duke is continuing to investigate the source of tritium in wells GM-7R and GM-7DR. Tritium levels in samples from the remaining wells are below the communication protocol threshold. The licensee plans to notify the South Carolina DHEC state officials and local stakeholders of the sample results. "Initial Safety Significance: There is no safety significance due to the tritium identified in ground water at Oconee. The subject wells are not drinking water sources, and there is no indication tritium has migrated off the Oconee site in the ground water. "Corrective Action(s): The source of tritium in the ground water at Oconee is not understood at this time. Duke is continuing an investigation to identify the source and implement a corrective action plan." The licensee will issue a press release and has informed the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-02-09
45689 | 0 | AMERICAN ELECTRIC POWER |  |  |  |  | 2010-02-08 10:30 | 2010-02-09 09:50 | 2010-02-09 | SHUTTER ON NUCLEAR GAUGE FAILED TO CLOSE "Ash hopper nuclear level detector (NLD) on Unit 2 hoppers 9 and 13 (dual source) has its shutter failed in the open position. The gauge is a TN 5197, serial number B8031. The gauge manufacturer (Thermo Electron) had been notified and requested to assess and repair the gauge." "Isotope: Cs-137 "Activity: 100 mCi" No exposure to personnel occurred during this event and the detector is not easily accessible. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-02-09
45688 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-02-08 18:03 | 2010-02-08 19:52 | 2010-02-08 | SAFEGUARDS REPORT - UNAUTHORIZED ENTRY INTO THE PROTECTED AREA Actual entry of an unauthorized person into a protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-02-08
45687 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-02-08 12:00 | 2010-02-08 18:52 | 2010-02-09 | FITNESS FOR DUTY - CONFIRMED POSITIVE ALCOHOL TEST FOR A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access has been suspended. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM RAY SWAFFORD TO DONALD NORWOOD AT 1556 ON 2/9/2010 * * * Updated information provided by the licensee. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2010-02-08
45686 | 0 | ABB INC. (MEDIUM VOLTAGE SERVICE) |  |  |  |  | 2010-02-08 | 2010-02-08 16:38 | 2010-03-08 | POTENTIAL FAILURE OF A BREAKER COMPONENT TO COMPLY WITH DESIGN SPECIFICATIONS The following information was received via facsimile: A breaker failed during operation at Plant Vogtle during operation. A failure analysis indicated that the resistors on the electronic board fail to an open circuit status. On January 14, 2010, a failure analysis indicated that the resistors fail to a short circuit status prior to failing open. In this failure mode, the internal temperature increases to a point where the plastic core melts and thereby can potentially block the operation of the internal plunger. In such a case, the breaker remains closed, but if the breaker is opened then a new closing command is not possible. ABB is taking, or has taken, the following corrective actions: A. As noted above, the only affected customer with a failed breaker is Southern Company's Nuclear Plant Vogtle, and ABB has discussed this issue with Southern Company. An interim report was issued on 1-18-2010. B. As an interim solution, ABB will provide a standard close coil. This solution will be limited to applications that do not require the low impendence in the close coil for lamp applications. C. An alternate solution is to add 'b' contact (normally closed) in series with the existing close coil. While not having a history of failure, it is noted that similar breakers are used at Plant Hatch. Given the large number of applications for the affected circuit breakers, ABB (Medium Voltage Service) cannot determine if the potential for a substantial safety hazard exists at any licensee's facility if a similar failure of the close coil occurs. As noted above, the failure has been limited to applications that require continuous close coil duty. No failures have been reported or produced in testing in applications with intermittent use of close coil duty. Licensees are requested to evaluate the application of affected breakers to determine priority of close coil replacement. * * * UPDATE FROM JAY LAVRINC TO CHARLES TEAL @ 1323 EST ON 3/8/10 * * * The identification of the subject component is as follows: ABB PIN ISDA055274Rl Close Coil x Lamp. These close coils are used in Sace EMAX breakers exclusively provided to Southern Nuclear Company plant Vogtle for safety related applications. The close coils are used to release stored energy that in turn closes the breaker. The failure is limited to applications with constant voltage applied to the close coil. Intermittent use of the close coil has not resulted in any failures. ABB Sace EMAX circuit breakers procured from ABB between 2006 to present for Vogtle may have suspect close coils installed where the particular application requires constant control voltage to be applied to the close coil. ABB is taking, or has taken, the following corrective actions: a. As noted above, the only affected customer is Southern Company's Nuclear Plant Vogtle, and ABB has discussed this issue with Southern Company. An initial notification letter was issued on 2-18-2010. b. ABB will provide a standard close coil 1SDA0383013R1. This part number has been updated from the 2-8-2010 notification and is based on ABB Sace input. This solution will be limited to applications that do not require the low impedance in the close coil for lamp applications. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-02-08
45685 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2010-02-08 | 2010-02-08 15:00 | 2010-02-08 | AGREEMENT STATE REPORT - FIXED GAUGE STUCK SHUTTER The following information was received via e-mail: "The Plant Manager called the [Illinois Emergency Management] Agency to advise that a shutter on a gauge had failed. When staff went to close the shutter, [while performing] work in the immediate vicinity, the handle used to close the shutter, 'twisted off'. The shutter remained stuck in the open position. Radiation levels near the gauge did not change from the previous configuration. The area was posted to warn of the hazard and system maintenance personnel changed work procedures to account for the failure. No work is scheduled to be completed within the beam fan area in the lower portion of the vessel. "The company's radiation safety officer confirmed the steps taken and applied additional shielding to the front of the gauge to effectively render the gauge 'off' until such time as the vessel is once again filled with product to reduce the radiation levels or the manufacturer can be on-site. Current weather predictions are such that it may be a couple of days until a field engineer can be dispatched to the site. "This item remains open and may be further investigated depending on response by the manufacturer. This device experienced similar problems in October of 2009 which were addressed by the manufacturer. In that case, the gauge was 'upgraded' to include additional seals and replacement of others to prevent the infiltration of water which lead to corrosion of the shutter causing it to 'stick' in the open position unless sufficient force was applied to the handle." The fixed gauge was manufactured by Ohmart Corp.; model number SH-F2; serial number 74932. The sealed source radionuclide is CS-137 with an activity of .08 Ci (2.96 GBq). Illinois Event Number: IL10010. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2010-02-11
45684 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-02-08 00:10 | 2010-02-08 05:33 | 2010-02-08 | EMERGENCY SIREN SPURIOUS ACTUATION "Emergency offsite siren, SC-11, in the City of San Clemente inadvertently activated for [approximately] 20 seconds. (Similar to 1/19/10 event) [EN #45636] "Notification of California Office of Emergency Services and FEMA may occur." The licensee is investigating the cause of the alarm. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-02-08
45683 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-02-06 09:28 | 2010-02-06 13:16 | 2010-02-07 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER CONDITIONS "At 0928 hours on February 6, 2010, 38 of 119 offsite sirens were determined to be unavailable primarily due to power outages from heavy snowfall. As of 1100 hours, 27 of 119 offsite sirens remained unavailable. Furthermore, 4 of the available sirens are currently on back-up battery power and are being monitored. Sirens will be recovered when power is restored. "This event is being reported as a Loss of Emergency Preparedness Capabilities pursuant to 10CFR50.72(b)(3)(xiii). Beaver Valley Power Stations Units 1 and 2 are operating at 100% power with required safety related equipment operable and no other equipment problems due to the adverse weather. "The NRC Resident Inspector has been notified." Per the licensee, the applicable county Emergency Management Agencies are aware of this situation and are prepared to implement alternate notification measures if needed. * * * UPDATE FROM JIM DAUGHERTY TO DONG PARK AT 0829 EST ON 2/7/10 * * * As of 0800 EST, power to 14 offsite sirens have been restored. 13 of 119 offsite sirens remained unavailable. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Jackson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-06
45682 | 0 | SINAI - GRACE HOSPITAL |  |  |  |  | 2010-02-05 | 2010-02-05 21:16 | 2010-02-05 | LOST I-125 MEDICAL IMPLANT SEEDS While performing a medical procedure for treatment to a patient's prostate, several I-125 seeds were spilled onto the operating room floor. Using a Geiger counter, some seeds were recovered. However, five (5) seeds were not located. The seeds had been calibrated today and each seed contained .336 milliCi of I-125. The seeds were sealed sources and no loose contamination was detected in the operating room. The patient received the prescribed dose and post-procedure review of the patient determined that the lost seeds were not in the patient. The Radiation Safety Officer is returning to the hospital to continue searching for the missing seeds. * * * UPDATE FROM TIM APPLEGATE TO DONALD NORWOOD AT 2316 EST ON 2/5/2010 * * * At this time the RSO has been able to locate four of the five missing seeds. He is planning on continuing his search until approximately midnight tonight. Notified R3DO (Hills), FSME EO (Shaffer), and CNSC via Fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-02-05
45681 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2010-02-04 14:20 | 2010-02-04 18:30 | 2010-03-03 | AGREEMENT STATE REPORT - FAULTY SHUTTER ON FIXED GUAGE Licensee, Georgia Pacific Toledo, notified the Agency [Oregon Department of Health and Radiation Protection] that the 6 month inspection on their K-Ray fixed gauge (model 7062B) revealed the shutter would not close correctly. The gauge was still able to perform it's function as a level indicator on a coal bin. Licensee called the manufacturer for repairs. Source is 50 mCi of Cs-137. Incident Report # 10-0005 * * * UPDATE FROM DARYL LEON TO VINCE KLCO ON 3/3/10 AT 1154 EST* * * On February 10, 2010 the licensee's RSO (Radiation Safety Officer) and the vendor technician verified the fixed gauge shutter functioned correctly. It was observed that the time constant on the detector was quite long. The RSO and the vendor determined that the initial report of a shutter malfunction was in error because personnel did not wait long enough to see the result of closing the shutter on the control system. The licensee will add a note to the inventory form for this source as to the name of the control tag for the detector in order to verify the closed/open shutter transition and to see an adequate response. No other action is required on this incident and the State of Oregon recommends that that the incident be closed. Notified the R4DO (Cain) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2010-02-09
45680 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-11-12 | 2010-02-04 18:17 | 2010-02-04 | AGREEMENT STATE REPORT - FIXED GAUGE EXPOSURE INCIDENT The following information was received via E-mail: "On November 12, 2009, two Public Service Company of Colorado (PSCo) employees removed a fixed gauge (including the source and detector) that was mounted on a pipe to measure scrubber slurry flow. The detector was not working correctly and needed to be repaired. During the process, the employees left the shutter on the source open and received a radiation exposure. Removing the source from the pipe and leaving the shutter open are not allowed by company procedures or the radioactive materials license. "The Colorado Department of Public Health and Environment (CDPHE) was contacted about the November 12, 2009 incident by the PSCo Radiation Safety Officer (RSO) on November 12, 2009. At the time CDPHE was contacted it was believed that the shutter had been closed during the work and that there was no unplanned employee exposure. CDPHE was informed that PSCo employees would perform no further work on the source holder and that it was secured at the location where it was taken down. Also, any further work to reinstall the source would be performed by an NRC certified entity. Public Service Company of Colorado (License #032-01) is a specific licensee of the State of Colorado Agreement State Program. "On January 29, 2010 while talking to the instrument and control technician employees that had performed the (November 12, 2009) gauge removal, the PSCo RSO learned that the shutter had in fact been open during the work, and the shutter was locked after the source was taken down from its operating location. This was the first time the employee working on the gauge had informed anyone about the shutter being open while the employees removed the detector. On the afternoon of January 29, 2010 the PSCo RSO notified CDPHE via email to provide initial notification of the potential radiation exposure incident. "On February 4, 2010 the RSO for PSCo submitted additional information to CDPHE regarding the incident including exposure estimates for the employees involved. The licensee estimated that employee #1 received an exposure of approximately 25 mrem, while employee #2 received an exposure of approximately 0.9 mrem. "The gauge involved in the incident was an Ohmart model SR-A, Source Holder Serial #2690CG, containing approximately 50 mCi (1.85 GBq) of Cs-137 (source mfg date is April 2002). The gauge was originally installed in the licensee's facility in October, 2002. "The Colorado Department of Public Health and Environment has assigned incident number I10-02 to this incident and is continuing to investigate. The licensee (PSCo) has started an incident investigation to evaluate the incident and determine appropriate corrective actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-02-09
45679 | 0 | GENERAL ELECTRIC OF PLEASANTON |  |  |  | 0 KW GETR (TANK) TEST REACTOR | 2010-02-03 21:41 | 2010-02-04 15:32 | 2010-02-04 | SAFEGUARDS EVENT - PARTIAL LOSS OF SECURITY SYSTEM COMPUTER Discovered vulnerability in a safeguard system that could have allowed access into a controlled access area for which compensatory measures have not been employed. There is no NRC Resident Inspector at the site. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CA | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2010-02-04
45678 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-02-03 | 2010-02-04 11:53 | 2010-02-04 | SAFEGUARDS REPORT - UNAUTHORIZED PERSON ENTERED THE CONTROLLED ACCESS AREA Discovered vulnerability in a safeguard system that allowed access into a controlled access area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 90 | 94 | 0 | 90 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-02-04
45677 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2010-01-14 | 2010-02-04 10:12 | 2010-02-04 | LAW ENFORCEMENT INTERACTION WITH SUSPICIOUS INDIVIDUALS Law enforcement interaction with suspicious individuals. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-02-04
45676 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2010-02-03 11:00 | 2010-02-03 17:11 | 2010-02-03 | FEEDWATER CHECK VALVE LEAK RATE EXCEEDED TECHNICAL SPECIFICATION REQUIREMENT "At 1100 [CST] on February 3, 2010, it was discovered that a primary containment local leak rate test performed on feedwater check valve 1B21-F032B exceeded its acceptance criteria. Technical Specification Surveillance Requirement (SR) 3.6.1.3.11 requires that the combined leakage rate for both primary containment feedwater penetrations to be less than or equal to 2 gallons per minute. The measured leakage for 1B21-F032B was reported to be 2.5 gallons per minute (gpm). Operations immediately declared 1B21-F032B inoperable and initiated action to close the feedwater inlet shutoff valve 1B21-F065B to isolate the affected penetration. At 1136 [CST], 1B21-F065B was closed and its breaker was turned off to comply with TS 3.6.1.3, Condition C required actions. "At 1447 [CST], the Feedwater Leakage Control System (FWLCS) was declared inoperable in accordance with LCO 3.6.1.9 and the plant entered a 30-day action to restore FWLCS to an operable condition. "After performance of a line flush, plans are underway to attempt to re-perform the local leak rate test for the feedwater check valve, 1B21-F032B. If unsuccessful, further corrective actions will be taken. "The NRC Senior Resident has been informed." | 4 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2010-02-03
45675 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-02-03 13:44 | 2010-02-03 16:38 | 2010-02-05 | TECHNICAL SPECIFICATION SHUTDOWN REQUIRED DUE TO CONTROL ROD OUT OF ALIGNMENT "A shutdown of South Texas Project Unit 1 was initiated at 13:44 hours [CST] on February 3, 2010. When in Action b.2. of Technical Specification (TS) 3.1.3.1, 'Moveable Control Assemblies Group Height,' a second control rod, B-12, in Shutdown Bank A was declared inoperable when the rod came out of alignment with the remainder of the rods within its bank. The second control rod came out of alignment during the performance of Surveillance Requirement 4.1.3.1.2; a surveillance to determine operability by movement of the rod. "For the above condition, Action c. of TS 3.1.3.1 was entered. When the requirements of the action could not be met, South Texas Project Unit 1 entered TS 3.0.3. and a plant shutdown was initiated. "Prior to initiation of this event, South Texas Project Unit 1 was in Action b.2 [of TS 3.1.3.1] with rod C-5 of Shutdown Bank D trippable but inoperable due to causes other than addressed by Action a. The inoperable rod, C-5, was aligned within 12 steps of the remainder of the rods within its group and the rod sequence and insertion limits as specified in the Core Operating Limits Report were being maintained." At the time of this report, South Texas Project Unit 1 was at 30% power and decreasing. The plant will enter Mode 3, Hot Shutdown, at approximately 1800 CST. Shutdown was initiated when rod B-12 could not be aligned within 12 steps of the remainder of rods within its bank as specified in Action c. of TS 3.1.3.1. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BOB SCARBOROUGH TO HOWIE CROUCH @ 2220 EST ON 2/03/10 * * * "At 1730 [CST] during performance of the Unit 1 shutdown, control rod H-2 in Bank 1C inserted from 246 steps, as indicated by the digital rod-position indication system, to 234 steps indicated without a demand signal applied to the control bank. The group step counter remained at 249 steps with no other rods in Bank 1C indicating movement. "The shutdown continued normally from that point. Control rod H-2 stepped with the rest on the rods in the bank down to zero steps. All control rods in Unit 1 are at zero steps. The shutdown rods are currently withdrawn." The licensee has notified the NRC Resident Inspector. Notified R4DO (Gaddy). * * * UPDATE FROM KEN TAPLETT TO DONALD NORWOOD AT 1700 EST ON 2/5/2010 * * * "This update corrects information provided earlier at 2230 EST on February 3, 2010 after reviewing post shutdown data. During the performance of the Unit 1 shutdown, control rod H-2 in Bank 1C inserted upon demand, as indicated by the digital rod-position indication system, but did not withdraw upon demand, as indicated. This occurred when controlling Bank 1C between 249 and 242 steps by alternating insertion and withdrawal demand signals to control reactivity. At approximately 1731, the shutdown continued normally from that point. Control rod H-2 stepped in with the rest of the rods in the bank down to zero steps. All control rods and shutdown rods in Unit 1 were subsequently driven in to zero step position." The licensee notified the NRC Resident Inspector. Notified R4DO (Gaddy). | 30 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-02-03
45674 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-02-03 15:25 | 2010-02-03 15:56 | 2010-02-03 | ACTUAL ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-02-03
45673 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-02-02 20:15 | 2010-02-03 03:14 | 2010-02-03 | TWO OF THREE TRAINS OF AUXILIARY FEED WATER DECLARED INOPERABLE "On 2/2/10, at 1615 [CST], the Unit 1 TDAFW [Turbine Driven Auxiliary Feed Water] Pump was declared inoperable due to a high temperature identified on an electrical cable in the TDAFW UPS [Uninterrupted Power Supply]. The 1B Diesel Generator had previously been removed from service for scheduled maintenance. As required by the Diesel Generator LCO Required Action Statement, the Unit 1 'B' MDAFW [Motor Driven Auxiliary Feed Water] Pump was declared inoperable at 2015 [CST], on 2/2/10, due to the combination of its inoperable emergency power supply and inoperable redundant equipment. This resulted in two of three trains of Auxiliary Feed Water being inoperable. Because two out of the three trains of AFW [Auxiliary Feed Water] are required to meet flow requirements for limiting design basis accidents, this represents a condition that could have prevented the fulfillment of a safety function. "Repairs to the electrical cable were immediately initiated. At 2216 [CST], on 2/2/10, the Unit 1 TDAFW Pump was returned to operable status, allowing the 1B MDAFW Pump to be declared operable, and restoring the safety function." The licensee determined that the high temperature in the electrical cable was caused by a high resistance between the lug and cable connection. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-02-03
45672 | 0 | WATERFORD | 3 |  |  | [3] CE | 2010-02-02 14:00 | 2010-02-02 20:37 | 2010-02-02 | PRIMARY EOF UNAVAILABLE DUE TO FAILURE OF VENTILATION DAMPER POSITION INDICATION "On February 2, 2010, at approximately 1400 CST, Entergy personnel manually switched the Emergency Operations Facility (EOF) Ventilation System Panel to the isolation mode. This manual switching to the isolation mode will cause the isolation dampers to close and the movement of the dampers closing can normally be heard. An indication light on the ventilation panel will illuminate when the dampers close. For the manual isolation on February 2, 2010, these indications did not occur. Waterford 3 personnel have made a judgment that the isolation dampers may not be closed due the lack of the aforementioned indications. The EOF ventilation system is not able to perform its isolation function if the dampers are not closed. The ventilation system and associated dampers are designed to provide protection from radiological and toxic chemical release. This report is being made because the time to restore the ventilation system to functional status is indeterminate at this time, until the actual condition of the ventilation system can be established. "The back up EOF facility is judged to be functional based on January 12, 2010 communications check and facility readiness verifications on January 28, 2010." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-02
45671 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2010-02-01 19:13 | 2010-02-01 22:39 | 2010-02-04 | TSC UNAVAILABLE FOR PLANNED HVAC MAINTENANCE "At 1913 on 02/01/2010, the Technical Support Center (TSC) was removed from service for planned maintenance. This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). Maintenance will include replacement of carbon filter media in the TSC HVAC system. The total duration of the maintenance activities is expected to be approximately 24 hours. The Emergency Response Organization has been notified of the outage and provided instructions for responding if needed. No other emergency response facilities are impacted by this maintenance work. The NRC Resident Inspector has been notified. A follow up notification will be made when the maintenance work has been completed." * * * UPDATE FROM RICK GARCIA TO DONALD NORWOOD ON 02/04/2010 AT 1211 EST * * * Maintenance was completed and the TSC returned to service at 2328 PST on 02/03/2010. The NRC Resident Inspector has been notified. Notified R4DO (Gaddy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-02-01
45670 | 0 | WATERFORD | 3 |  |  | [3] CE | 2010-02-01 10:15 | 2010-02-01 21:05 | 2010-02-01 | FITNESS FOR DUTY TEST FOR AN ILLEGAL SUBSTANCE A contract supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2010-02-01
45669 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-01-31 01:30 | 2010-02-01 13:07 | 2010-02-01 | RADIOGRAPHY SOURCE FAILED TO FULLY RETRACT INTO CAMERA "On January 31st, two different radiography crews working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on the same INC IR-100 exposure device (serial number 6621). "During the night shift, the locking mechanism tripped prematurely [approximately 1/4 inch before the retracted lock position]. A survey of the exposure device did not reveal any abnormal readings. When the crank assembly was disconnected, it was noted that the pigtail was not in the proper position. A trained technician removed the locking assembly and cleaned dirt and ice from the assembly. The exposure device was reassembled with the source in the safe and secure position. "The day shift utilized the same device and experienced the same situation. When the lock was removed to be cleaned, there was a build up of ice in the locking assembly. The exposure device was reassembled with the source in the safe and secure position. "Exposure Device: Industrial Nuclear IR-100; Device S/N: 6621; Source S/N: O835; Source Activity: 85 curies; Source Type: Ir-192. "The weather was minus 15 degrees with a wind speed of 18 knots. "There was no exposure to the crew or the General Public during this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PROTECTIVE ACTION PREVENTED | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(a) |  |  |  | 0 | 2010-02-01
45668 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-31 10:42 | 2010-01-31 14:34 | 2010-01-31 | TEMA NOTIFIED OF A LOSS OF EMERGENCY SIRENS "At 1100 EST on 1/31/10, the Sequoyah Nuclear Plant Shift Manager was made aware of notifications made to an outside government agency regarding Loss of Offsite Response Capabilities. Specifically, on 1/30/10 at 1826 EST, the Operations Duty Specialist made a Courtesy notification to the Tennessee Emergency Management Agency (TEMA) of 9 offsite sirens which had failed their polling test. This is well below the normal reporting criteria for the Emergency Plan. Subsequently, on 1/31/10 at 1042 EST, TEMA was notified that 4 of the sirens had been repaired, and only 5 sirens are still not responding to the polling test." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1636 EST ON 1/31/2010 FROM MIKE BRUBAKER TO MARK ABRAMOVITZ * * * "This amendment is being provided to clarify that a loss of offsite notification capabilities did not occur. At 1100 EST on 1/31/10, the Sequoyah Nuclear Plant Shift Manager was made aware of a courtesy notification made by the TVA Operations Duty Specialist to TEMA regarding loss of a small number of sirens due to inclement weather conditions. The courtesy notification was made on 1/30/10 at 1826 to inform TEMA that 9 offsite sirens had failed their polling test. A loss of 9 sirens does not constitute loss of emergency preparedness capability. This amends the original report which was made within 4 hours of the shift manager's notification." The licensee notified the NRC Resident Inspector. Notified the R2DO (Widman). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-31
45667 | 0 | US ARMY |  |  |  |  | 2010-01-27 | 2010-01-28 15:20 | 2010-01-28 | MOSITURE DENSITY GAUGE RECEIVED WITH INOPERABLE LOCKING MECHANISM The Army Depot in Stockton, CA received at 1401 PST on 01/27/10 a CPN Moisture Density Gauge shipped from a field unit. Upon receipt inspection, they identified that the locking mechanism was separated from the guide tube. The source was in the shielded position at the time of discovery. The field unit which shipped the device on 01/26/10 was contacted and asserts that the unit was intact at the time of shipment. The device is a CPN, Model MC-1, S/N M1712089, manufactured in the 1970's containing two sources; 10 millicuries Cesium-137 and 50 millicuries Americium-241/Be. The damaged device is currently in secure storage and scheduled for disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-01-28
45666 | 0 | SULZER PUMPS INC |  |  |  |  | 2010-01-27 | 2010-01-27 16:28 | 2010-01-27 | DEFECT IN PUMP SHAFT JOURNAL COATING CAUSED SERVICE WATER PUMP (2E) FAILURE AT FARLEY NUCLEAR STATION The following was received via fax: "1. Name and address of the individual or individuals informing the Commission: Response: General Manager, Nuclear Services 4126 Caine Lane Chattanooga, TN 37421 "2. Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains defect: Response: Facility: Farley Nuclear Plant; Basic Component: Unit 2 Service Water Pump (2E) "3. Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: Response: Sulzer Pumps (US) Inc, Chattanooga Nuclear Service Center "4. Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: Response: Defect of pump shaft journal coating resulting in failure of basic component (Service Water Pump 2E) . "5. The date on which the information of such defect or failure to comply was obtained: Response: December 5, 2009 "6. In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part: Response: Sulzer Pumps (US) Inc, Chattanooga Service Center received Farley Purchase Order QP060449 for eleven (11) Service Water Pumps. The following table outlines current status of the pumps on this order: Serial Number Status Ship Date Location 08C02139 Shipped 12/18/07 Farley 08C02140 Shipped 5/19/08 Farley 08C02141 Shipped 11/5/08 Farley 08C02142 In Manufacturing N/A Sulzer Chattanooga 08C02143 In Manufacturing N/A Sulzer Chattanooga 08C02144 In Manufacturing N/A Sulzer Chattanooga 08C02145 Failed in Plant - Originally Shipped 11/14/06 for evaluation to Sulzer Chattanooga 08C02146 Shipped 8/3/07 Farley 08C02147 Shipped 7/30/08 Farley 08C02148 In Manufacturing N/A Sulzer Chattanooga 08C02149 In Manufacturing N/A Sulzer Chattanooga "7. The corrective action which has been, is being , or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: Response : A joint root cause evaluation has been completed by Sulzer Pumps (US) and Farley. Corrective actions will include replacement parts with updated and corrected design. Sulzer is developing a manufacturing schedule to implement the corrective actions (estimated completion for schedule, 1st Quarter 2010). "8. Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been. Is being or will be given to purchasers or licensees: Response: A comprehensive root cause report has been jointly developed and accepted by Sulzer and Farley." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21 |  |  |  | 0 | 2010-01-27
45665 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-01-27 | 2010-01-27 15:39 | 2010-01-27 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT INVOLVING A BRACHYTHERAPY UNDERDOSE EVENT The following was received via e-mail: "The BRP [Bureau of Radiation Protection] was informed on January 26, 2010 of a medical event that occurred at The Jewish Hospital of Cincinnati on December 28, 2009. A patient received a prostate I-125 seed implant on December 28, 2009. The post implant CT showed no problems but a follow-up CT performed on January 26, 2010 showed that the patient only received 75% of the prescribed dose to the prostate." The intended dose was 144 Gy (14400 rad) and the actual received dose was 108 Gy (10800 rad). I-125 activity was 0.032 Ci per seed. The total dose delivered differs from the prescribed dose by twenty five percent. The state is investigating the matter. Item Number: OH100002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-02-02
45664 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2010-01-27 07:30 | 2010-01-27 07:39 | 2010-01-27 | ELECTRICAL POWER TEMPORARILY REMOVED FROM THE EMERGENCY OPERATIONS FACILITY FOR MAINTENANCE "This is an eight hour report per 10 CFR 50.72(b)(3)(viii). Seabrook Station will be implementing a modification to improve reliability of the electrical system serving the Emergency Operations Facility (EOF). Specifically, the existing manual transfer switch between the backup power diesel generator and the EOF building will be replaced with an automatic transfer switch. "This work will require that the main power feed to the EOF building be removed for a period of approximately 3 hours today. During this time, a secondary power feed will remain in service which can supply some building loads. A second 3-hour period of 'partial power' may be necessary to complete the job; it is currently anticipated that this second 'partial power' period, if needed, will occur tomorrow, January 28. "Power to all EOF loads will be available in between the two 3-hour periods discussed above. In addition, should an emergency be declared during one of the 3-hour periods, full power to the facility can be restored within approximately 2 hours. As a compensatory measure, the TSC will perform the key planning standard functions assigned to the EOF during the two 'partial power' time periods should the EOF be unable to do so; this includes offsite dose projections, development of protective action recommendations and offsite notifications. Emergency plan implementing procedures for the TSC contain the instructions necessary for TSC responders to perform functions. "During the 2-day period that this work is being performed, there will be no backup power source for the EOF. "All work associated with this switch upgrade will be performed in an expeditious manner consistent with the goal of minimizing EOF unavailability. "All EOF responders have been briefed on this work and expected contingent actions. "This job will start at approximately 0730 am this morning. We anticipate that all work will be completed by sometime tomorrow afternoon. We will provide a notification update upon completion of the job." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MIKE TAYLOR TO JOE O'HARA AT 1738 ON 01/27/10 * * * "Seabrook station has completed the installation of the automatic transfer switch at the Emergency Operations Facility (EOF). There is no planned work affecting EOF availability." Notified R1DO(Hansell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-01-27
45663 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-01-26 15:25 | 2010-01-26 17:29 | 2010-01-26 | ENTRY INTO TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "While operating in mode 1 at 100% power, [the licensee] identified [a] failure to comply with Technical Requirements [TR] Manual 3.7.20, Snubbers, Condition C. [The] required action C.1 requires the performance of an inspection of required snubbers affected by transient in accordance with Table TR 3.7.20-1 within 6 months of the event. WCNOC [Wolf Creek Nuclear Operating Corporation] determined that a portion of the required inspections was not completed for transients that occurred during Refueling Outage 16 (Spring 2008). TR 3.7.20, Snubbers, Condition D requires affected systems to be declared inoperable immediately. No major equipment was out of service prior to the event. "At 1525 CST, TS [Technical Specification] LCO [Limiting Condition of Operation] 3.7.8, Essential Service Water (ESW) System, was declared not met, [and therefore], both trains of ESW [were declared] inoperable. With both trains of ESW inoperable, TS LCO 3.0.3 was entered and preparations for unit shutdown commenced. Additionally, with both trains of ESW inoperable both Emergency Diesel Generators were declared inoperable. TS LCO 3.8.1, AC Sources - Operating, Conditions B and F were entered. "Actions to complete required inspections per TR 3.7.20 Table TR 3.7.20-1 have been initiated. "Shutdown was commenced at 1618 CST. "NRC Senior Resident was notified 1/26/2010 15:30 CST regarding entry into TS LCO 3.0.3." * * * UPDATE FROM RICK HUBBARD TO JOHN KNOKE AT 2206 EST ON 1/26/10 * * * The licensee completed inspection of Train "B" snubbers, and at 2013 CST, the licensee exited TS LCO 3.0.3 based on restoration of Train "B" of Essential Service Water System to operable status. Licensee is still inspecting Train "A" snubbers. The licensee has notified the NRC Resident Inspector. Notified R4DO (Greg Pick) | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-01-26
45662 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-01-22 | 2010-01-26 14:34 | 2010-01-26 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECT "On January 26, 2010, [The Texas Department of Health] was notified by the licensee that a source disconnect had occurred on January 22, 2010. A radiographer was cranking a 26 curie iridium (Ir) - 192 source from the camera when he began having difficulty driving the source. He decided to retract the source back into the camera when the source disconnected at the drive cable. The source was driven into the collimator at the end of the guide tube. The radiographer contacted his Radiation Safety Officer (RSO) and informed him of the event. An individual qualified for source retrieval was sent to the location. The source was returned to the camera, and the camera was returned to the licensee's facility. The individual performing the source retrieval received 120 millirem as indicated by his pocket dosimeter. The RSO stated that the failure appeared to be caused by a failure of the connector on the drive cable. The RSO stated that it was a result of normal wear on the device. [The Texas Department of Health] has requested copies of the last three maintenance records for the device. The source serial number is QH2505 manufactured by Spec. The camera serial number is 1203. Additional information will be provided as it is received." Texas Incident #: I - 8706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-01-29
45661 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-04-11 | 2010-01-25 22:37 | 2010-01-25 | AGREEMENT STATE REPORT - DOSE TO AN EMBRYO / FETUS The following excerpted information was received by facsimile: "Notifications: DEP [PA Department of Environmental Protection] received a letter dated May 1, 2009; Received May 8, 2009 from St. Luke's describing the incident, corrective actions, effects and notification to the patient. "A patient was administered a therapeutic dose of 134 mCi of I-131 for thyroid carcinoma on April 11, 2008. She had previous negative pregnancy tests on April 6, 2008 and April 10, 2008. Following treatment the patient suspected she was pregnant and returned to the hospital an April 28, 2008. Subsequent testing indicated she became pregnant approximately 4 to 6 days following her treatment. Calculated dose to the fetus was 35 rad, whole body dose. Patient and referring physician both notified. The event occurred because the patient didn't follow the contraceptive plan outlined in the procedure she signed prior to treatment. The hospital staff followed procedure for therapeutic administration of I-131, however corrective actions involve procedure modifications such as over-emphasizing the risks associated with becoming pregnant following administration of radioiodine to prevent further occurrence." Event Report ID No: PA080016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-31
45660 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-05-18 | 2010-01-25 22:30 | 2010-01-25 | AGREEMENT STATE REPORT - DIFFICULTY RETRACTING GAMMA SOURCE The following excerpted information was received via facsimile: "Notifications: A letter dated June 6, 2009 was received by DEP [Department of Environmental Protection] on June 15, 2009 that described the incident. "Radiography crew was performing their 7th exposure at a location within the FCC Scrubber Unit (PV-7923). Upon completion of the exposure time (2 minutes), the crew attempted to retract the gamma source to its shielded / safe position. It was during the retraction sequence that the crew had difficulty returning the source to the shielded position. Both individuals made several attempts to retract the source. The crew re-established the posted radiation boundary to where the radiation levels were at or below regulatory limits for this situation (2 mR/hr), and implemented their source recovery procedures." Event Report ID No: PA090025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-28
45659 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-04-18 | 2010-01-25 22:21 | 2010-01-25 | AGREEMENT STATE REPORT - LEAKING WELL LOGGING SOURCE The following excerpted information was received via facsimile: "Notifications: Phone call made to South West Regional Office on April 18, 2009 to notify PA DEP of the situation. "The PA DEP SWRO [Pennsylvania Department of Environmental Protection Southwest Regional Office] was notified on Friday, April 18, 2008, by Weatherford International, who were doing reciprocity work in western PA, of a leaking well logging source containing 1.5 Ci of Cs-137. A rag used to clean of the tool was surveyed and was found to contain elevated radiation levels. The tool was removed from service and further leak tests were done, confirming the presence of contamination. It was found that the tool was leak tested in March 2008 and found to be contaminated then (at approximately 0.04 microcuries). No reason given why it was kept in service. On Saturday April 19, 2008 all likely areas of contamination were surveyed, with none showing higher than the 0.005 microcuries limit. Weatherford them contacted NSSI of Huston TX, and asked them to verify the test results and to inspect the tool itself. The source was packed and shipped to NSSI in Texas the week of April 20 for evaluation. NSSI conducted surveys and collected wipe samples of the facility before leaving and found no evidence of contamination at the facility other than the known area on the logging unit. The contamination on the logging unit was cleaned and re-wiped and showed no evidence of removable contamination after the clean-up. Urine samples for bioassays were collected from facility employees and sent to GEL Laboratories for analysis. Bioassay results for the employees were returned and showed no evidence of Cs-137 above the minimum detection limit of 10 pCi/L." Event Report ID No: PA080008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-28
45658 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-02-19 | 2010-01-25 22:12 | 2010-01-25 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE / RADIOGRAPHY SOURCE DISCONNECT The following was received from the Commonwealth via e-mail: "DEP [Department of Environmental Protection] received a letter dated March 9, 2009 from Acuren describing the incident. It was received March 16, 2009. "Event Description: A technician was performing radiography in Erie, PA (Booth #2) at 8:55am. A few seconds after his fourth exposure, the technician heard the spool piece fall off the table. He immediately tried to retract the source but was unsuccessful. The RSO traveled to the facility, calculated the exposure rates and executed a safe retrieval of the source. He received 35 mrem of exposure during the retrieval. The damaged guide tube was disposed. A 1.75" lead sheet was used to shield the source while the guide tube was reshaped to allow a safe retrieval to the secured position. A whole body dose of 32 mrem was received by retrieval technician. "Causes of the event: Spool piece was not properly secured in a safe position on the table. Piece was not properly blocked or braced, and located too close to the end of the table, so any movement would result in a fall. The jack stands that were available were not used, nor was shooting the parts on the floor considered. Guide tube and camera were not properly positioned to avoid contact with falling spool piece." Event Report ID No, PA090016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-28
45657 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-09-23 | 2010-01-25 22:09 | 2010-01-25 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE / RADIOGRAPHY SOURCE DISCONNECT The following information was received via fax: "Notifications: DEP [Department of Environmental Protection] received a phone call September 24, 2009 about the incident. "On Wednesday, September 24, 2008 the PA DEP SWRO [Pennsylvania Department of Environmental Protection Southwest Regional Office] received a telephone call from TEI Analytical Services in Washington, PA notifying them of a source disconnect at a facility in Houston, PA. At approximately 1005 pm, Tuesday, September 23, 2008, a 99 curie Ir-192 source became disconnected from the cable while performing radiography on a gas extraction facility along PA Route 519. The source became separated from the guide tube and could not be returned to the camera. The company was notified and sent a rescue team to assist in the recovery and control of the source. No overexposures occurred and the team managed to get the source back into its camera via tongs. This operation was concluded at 12:08am. Doses are as follows: radiographer 51 millirem whole body; assistant 25 millirem; rescue radiographer 42 millirem whole body, 800 millirem extremity; second member of rescue team 160 millirem whole body, no extremity dose. The cause was found to be limitations of the work environment, i.e., the positioning of the exposure device was very limiting and darkness reduced visibility. No modifications in operating procedures to prevent a re-occurrence were mentioned." Event Report ID No: PA080025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-28
45656 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-07-17 | 2010-01-25 22:01 | 2010-01-25 | AGREEMENT STATE REPORT- MEDICAL OVEREXPOSURE EVENT The following information was received via fax: "On July 17, 2008 the PA DEP SERO [Pennsylvania Department of Environmental Protection Southeast Regional Office] was notified of a medical event at Lehigh Valley Hospital. Two patients were scheduled for different I-131 therapy doses and the doses got switched. The first patient was prescribed 20 mCi but was administered 75 mCi. The event took place on July 17, 2008. Both the patient and the physician were informed. The patient was given a blocking agent of 130mg SSKI approximately 1 hour after uptake of the I-131. Next day measurements indicated 2 mCi uptake to the thyroid and 10 mCi whole body retention. A procedure modification has been put into place to prevent this from occurring again. Also a Notice of Violation was sent to the hospital." Event Report ID No: PA080021 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-31
45655 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2010-01-25 11:30 | 2010-01-25 18:33 | 2010-09-30 | UNANALYZED CONDITION - OVERFLOW OF URANIUM BEARING AMMONIATED WASTEWATER "It was reported to the EH&S Management that on January 24, 2010 a spill of approximately 200 gallons of uranium bearing ammoniated (5-7%) wastewater overflowed from the 'Q' tanks into the diked area below the tanks. These tanks are the final filtration prior to transfer of this liquid effluent to the outside treatment facility. Operators received a high level alarm and responded by shutting down the process in accordance with the operational procedure, with the overflow occurring for approximately six minutes. This event was the result of a pump failure in the tank discharge line. Notification was made to the on duty Health Physics (HP) staff and the on duty Incident Commander. Health Physics staff responded within minutes and used a Drager counter to determine the ammonia concentrations present. Readings in the immediate area of the dike were as high as 256 ppm ammonia. Readings in adjacent areas of the facility were approximately 150 ppm ammonia. Non-essential personnel were evacuated and essential personnel were instructed to don PPE-respirators with ammonia cartridges. "Operations cleanup of the area was completed and with normal plant ventilation running the ppm ammonia concentrations were returned to < 25 ppm within approximately two hours. The failed pump has been repaired and returned to service. Based on the quick response of the HP staff, evacuations and appropriate use of PPE, no workers were exposed to significant concentrations and no medical attention was necessary. "Notification is made based on 10CFR70 Appendix A (b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10CFR70.61.' The potential for a loss of containment was recognized and evaluated in one of the Process Hazards Analysis (PHA) which constitutes the Integrated Safety Analysis for this system. The PHA identified several initiating events which could lead to a high level and loss of containment event. The appropriate safeguards were identified, including the procedural responses, the evacuation during such an emergency of the workers in the enclosed chemical area, and the use of appropriate PPE. The consequences of the event were identified as a potential for personnel inhalation and exposure hazard from the uranium bearing ammoniated wastewater. However, the PHA did not specifically indentify that the potential existed for the consequences to exceed the Intermediate Consequence criteria for credible events. In accordance with SNM-1107 License Requirements for the Columbia Plant Intermediate Consequences are those that have the potential for a worker to receive greater than or equal to ERPG-2 chemical exposures. (ERPG-2 value for ammonia is 150 ppm.) Since the Q-Tank contains comingled uranium and chemicals, the Intermediate Consequences of 10CFR70.61 apply. Failure to identify that an Intermediate Consequence event was credible led to that event not being included in the Conversion ISA Summary ISA-03 and not designating Items Relied on For Safety (IROFS) for that accident sequence. "Corrective Actions: As stated previously, the pump which failed has been repaired and returned to service. Actions taken by the staff to mitigate the event were appropriate and in accordance with approved procedures. Normal ventilation system operation reduced the concentrations to acceptable levels. [These actions are] complete. "The safeguards identified in the PHA will be evaluated in the ISA and appropriate selections of IROFS will be made based on that evaluation and included in the ISA summary. [These actions are] in progress." * * * UPDATE AT 1053 ON 9/30/2010 FROM GERARD COUTURE TO ERIC SIMPSON * * * "Time and Date of Event: September 30, 2010, 0800. "Previously Westinghouse had reported to the Nuclear Regulatory Commission (NRC) in Licensee Event Report #45655, that the conversion Integrated Safety Analysis (ISA) did not specifically indentify that the potential existed for the consequences of overflows or spills in the conversion wastewater system to exceed the Intermediate Consequence criteria for credible events based on chemical exposure. In accordance with SNM-1107 License Requirements for the Columbia Plant intermediate consequences are those that have the potential for a worker to receive greater than or equal to ERPG-2 chemical exposures. In the required written follow up to that event (LTR-RAC-10-16, February 23, 2010). Westinghouse committed to perform an extent of condition review of other chemical release scenarios and designate necessary Items Relied On For Safety (IROFS). Westinghouse further provided NRC the casual analysis related to that event, (LTR-RAC-10-28, April 6, 2010) which identified the need to quantitatively evaluate chemical release scenarios. Westinghouse has completed the necessary evaluations and determined that additional scenarios exist which have the potential to exceed the performance requirements of 10 CFR 70.61. EH&S Management has now determined that these analyses, the necessary ISA and ISA Summary revisions, and the identification of appropriate IROFS are complete. For these new ISAs the necessary controls, procedures and equipment are in place and the performance requirements are met in a fully compliant manner taking into account the newly identified IROFS. "The extent of condition review identified additional areas within the facility where chemical releases have the potential to exceed consequence thresholds for facility workers. There is one area where potential consequences could challenge off-site receptor chemical consequence criteria. The areas covered by the extent of condition review impacted by this updated chemical analysis are Conversion, the Scrap Uranium Processing, the Solvent Extraction System, and the facility Wastewater Tanks. "Notification is made based on 10CFR70 Appendix A (b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10CFR70.61.' The potential for a loss of containment was recognized and evaluated in the applicable Process Hazards Analysis (PHA) which constitutes the Integrated Safety Analysis. The PHAs identified initiating events which could lead to loss of containment. The appropriate safeguards were identified, including the procedural responses, the evacuation during such an emergency of the workers in the enclosed chemical area, and the use of appropriate PPE. Failure to identify in the areas mentioned above those chemical release consequences could exceed 10CFR70.61 criteria led to these events not being included in the applicable ISA Summary and not designating Items Relied on For Safety (IROFS) for these accident sequences. "Corrective Actions: As stated previously, the associated Integrated Safety Analysis, Integrated Safety Analysis Summaries, and designation of IROFS to ensure the performance requirements are satisfied is complete for the extent of condition reviews previously committed to by Westinghouse. "Full implementation of the revised ISA Summaries, to include all required procedure revisions and appropriate training will be completed by October 30, 2010." Notified R2DO (Lesser) and NMSS EO (Rubenstone). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2010-01-26
45654 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-01-22 | 2010-01-25 10:01 | 2010-01-25 | AGREEMENT STATE REPORT - POTENTIAL OCCUPATIONAL OVEREXPOSURE The following report was received from the State of Florida Bureau of Radiation Control via facsimile: "Employee's TLD recorded an overexposure of 6.261 rem. Date [of potential overexposure] was between 10 Dec 2009 to 9 Jan 2010. Affected employee claims he left his leather pouch with TLD [and pocket dosimeter] in work bucket over night, second shift used bucket not noticing TLD pouch at bottom. Pocket dosimeter reading was also off scale. Other employees who worked with him during same time period have no excessive exposures. RSO calculates dose should be approximately 195 mr during month as per records. RSO believes [that this exposure is] not an occupational overexposure. RSO contacted Licensing and Materials office on 22 Jan 2010. RSO received Landauer's dosimetry report on 21 Jan 2010. [The State of Florida] Tampa Inspection Office will investigate." FL report #FL10-009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-01-28
45653 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-01-25 09:30 | 2010-01-25 09:09 | 2010-01-25 | EMERGENCY RESPONSE DATA SYSTEM UNAVAILABLE DUE TO PLANT PROCESS COMPUTER MAINTENANCE "At 0930 on Monday, January 25, 2010, the Cook Nuclear Plant (CNP) Unit 1 Plant Process Computer (PPC) will be removed from service for scheduled maintenance which will take the Emergency Response Data System (ERDS) out of service. The scheduled maintenance is planned from 0930 hours EST until 1530 hours EST. Personnel will be performing computer system backups and maintenance. "Compensatory measures exist within the CNP Emergency Response procedure to provide plant data via the Emergency Notification System until the ERDS can be returned to service. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with NUREG 1022 Revision 2 for CFR 50.72(b)(3)(xiii) due to any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)." * * * UPDATE FROM RICH KRESS TO JOE O'HARA AT 1207 EST ON 1/25/10 * * * "The Unit 1 Plant Process Computer and the Emergency Response Data System (ERDS) were returned to functional Status at 11:35 on Monday, January 25, 2010. "This follow up notification is being made to provide closure from the initial notification under CFR 50.72 (b)(3)(xiii) due to any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)." The NRC Resident Inspector has been notified. Notified R3DO(Lipa) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-01-25
45652 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-01-22 18:27 | 2010-01-23 12:32 | 2010-01-23 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-01-23
45651 | 0 | ABB INC. (MEDIUM VOLTAGE SERVICE) |  |  |  |  | 2010-01-23 | 2010-01-23 10:35 | 2010-02-05 | CIRCUIT BREAKER CHARGING MOTOR CRANK DOES NOT MEET HARDNESS SPECIFICATIONS The following information was received via facsimile: "This letter provides notification of a failure to comply with specifications associated with ABB P/N 716532C00 Motor Crank procured as a commercial grade item from Sims Machining, and dedicated by ABB from a production run of 105 pieces produced October 21, 2009. These motor cranks are used in K-Line electrically operated circuit breakers with Ryobi or Wuxi motors. The motor crank is attached to the end of an electric charging motor. When the motor rotates the crank moves the charging pawl assembly in a cyclical manner. The cyclical movement of the charging pawl assembly in turn works with the ratchet pawls and converts the rotational torque produced by the charging motor into linear spring displacement. The linear spring displacement is used to charge the closing springs in the breaker mechanism. "Myers Control Power LLC notified ABB Florence on November 25, 2009 of a hardness test failure of motor cranks supplied by ABB for commercial applications. An evaluation was performed by ABB and noted that the required heat treatment process was not performed on a lot quantity of 105 motor cranks received October 24, 2009 from Sims Machining. Of the 105 non-heat treated motor cranks, 100 have been accounted for. Five K-Line circuit breakers procured from ABB between 10/24/2009 and 1/06/2010 may have non-heat treated motor cranks installed. Work process errors allowed non-heat treated motor cranks to be used in manufacture of K-Line circuit breakers. The motor crank is heat treated to prevent the premature wear of the crank as the roller on the crank turns around the output shaft during the charging cycle. The failure to heat treat the motor crank can cause the output shaft of the crank to wear. This will result in the misalignment of the spring charging components or ultimate failure of the spring charging system during the charging cycle, leading to the inability to close the breaker more than once. "ABB is taking, or has taken, the following corrective actions: a. Notification of the potential existence of this deviation to affected customers (to complete 1/31/2010). b. Review historical procurement and inspection records associated with the subject part, vendor and similar machined parts requiring heat treatment. (Action complete - no previous heat treatment process errors identified for both commercial and safety-related applications.) c. Follow-up with Sims Machining to determine how future incidents can be prevented and other actions warranted to prevent recurrence. (Action complete - Vendor requires certificate of heat treatment prior to sending to approved supplier for plating services.) d. Remove all non-heat treated motor cranks from inventory and work in progress for rework. (Action complete - 99 of 105 affected motor cranks reworked and 1 motor crank maintained for life cycle testing resulting in 5 suspect motor cranks escaping facility.) e. Revise inspection process instructions to ensure heat treatment is identified as a critical characteristic for verification (to complete by 1/25/2010). f. A cycle test is being performed to determine level of premature wear due to non-heat treatment. Results expected to be complete by 1/31/2010. "Given the large number of applications for the affected circuit breakers, ABB (Medium Voltage Service) cannot determine if the potential for a substantial safety hazard exists at any licensee's facility if premature failure of the motor crank occurs. Licensees are requested to evaluate the history of circuit breaker operating cycles to determine if the circuit breaker motor crank should be replaced immediately, or to perform the replacement at the next convenient maintenance opportunity." The HOO spoke to the point of contact for ABB on this issue and determined that the only two reactor licensees likely to have one of these discrepant breakers are Palo Verde and Surry. * * * UPDATE FROM VICTOR ROMANO TO JOHN KNOKE AT 1344 EST ON 2/5/10 * * * "ABB has taken the following corrective actions: "a. Notification of the potential existence of this deviation to affected customers. (Action complete - notification letters sent 2-1-20 I0) b. Review historical procurement and inspection records associated with the subject part, vendor and similar machined parts requiring heat treatment. (Action complete - no previous heat treatment process errors identified for both commercial and safety-related applications) cycle testing resulting in 5 suspect motor cranks escaping facility) e. Revise inspection process instructions to ensure heat treatment is identified as a critical characteristic for verification. (Action complete) f. A cycle test is being performed to determine level of premature wear due to non-heat treatment. (Action complete) "Mechanical life testing of two non-heat treated motor cranks for premature wear was completed. The first crank was measured prior to being installed on the breaker. The output shaft of the crank was measured and found to be 0.370/0.371 before the test began. The breaker was stopped and the crank was removed after 2500, 7500, 10,000 and 12,500 operations. The output shaft was measured and the threaded end of the crank that screws onto the output shaft of the motor was inspected. There was no measurable/noticeable wear in either location. "The second crank was measured and installed on the breaker. The output shaft on the crank was measured and found to be 0.370/0.371 before the test began. The breaker was stopped and the crank was removed and measured after 2500,7500, 10,000, 12,500 and at 14,500 operations. No wear was measured during or after the test as a result of thee accumulated operations. The output shaft was measured and the threaded end of the crank that screws onto the output shaft of the motor was inspected. There was no measurable/noticeable wear in either location. After 10,000 operations, it was noted in both cases that the body of the crank showed signs of wear where it comes into contact with the charging assembly. This wear was present as a result of the lack of heat treatment. "The wear that was documented during the testing of the motor cranks should not be detrimental to the operation of the breakers. Both of the motor cranks completed the number of mechanical life operations required for certification to the ANSI standard, 12,500. It is recommended that the cranks in question be replaced during the next scheduled availability for the customers affected by this issue." Notified R4 DO (Vincent Gaddy), R2DO (David Ayers), Part 21 Group (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-01-23
45650 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-12-15 | 2010-01-22 18:34 | 2010-01-22 | AGREEMENT STATE REPORT - LOOSE SURFACE CONTAMINATION ON A SEALED SOURCE "On 12/15/09 an Electron Capture Detector (ECD) containing Ni-63 was discovered to have loose surface contamination in excess of 0.005 microcuries. This discovery was made while removing the ECD from a Gas Chromatograph (GC) used by Energy Northwest. The ECD was removed to prepare the GC for transfer from Columbia Generating Station to the Applied Physics and Engineering Laboratory in Richland, WA. During removal, the ECD was surveyed for loose contamination by Radiation Protection staff. Analysis of the swipes obtained during the survey was completed on 12/17/09 and indicated 0.02 microcuries on the swipe of the makeup gas adapter between the ECD and GC." Washington State Item: WA100008 Current source activity 12.3 milliCi ECD model: G2397 A; Serial Number: U2055 GC Model: 6890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2010-01-27
45649 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-01-21 | 2010-01-22 15:44 | 2010-01-22 | AGREEMENT STATE REPORT - BRACHYTHERAPY UNDERDOSE The following was received via E-mail: "On January 22, 2010 the BRP [Ohio Bureau of Radiation Protection] was notified of a medical event that occurred at the Jewish Hospital of Cincinnati on January 21, 2010. The patient received 67% of the prescribed dose to the prostate implant with I-125 seeds. The physician is attempting to contact the patient. The BRP will investigate the event." The prescribed dose was 144 Gy and the actual dose delivered was 96.48 Gy Ohio Incident: OH100001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-01-28
45648 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-01-22 | 2010-01-22 11:39 | 2010-01-25 | FAILURE TO FULLY RETRACT THE SOURCE OF A RADIOGRAPHY CAMERA On January 22, 2010, a radiography crew working the Alpine Oil Field on the North Slope of Alaska had a camera source that failed to fully retract back into the camera. The technician was able to restore the source to the shielded position and the camera has been returned to the vault. The locking mechanism will be repaired later today. At the time of this report it is believed that the camera contains a 70 Ci Iridium-192 source. * * * UPDATE ON 1/23/2010 AT 1255 FROM KEENAN REMELE TO MARK ABRAMOVITZ * * * "On January 22nd a radiography crew working the Alpine Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an INC IR-100 exposure device. "When preparing to perform the second exposure of the shift (Ir-192, 84 curies) the locking bar deployed prematurely. The crew reset the locking bar and the locking mechanism tripped again when the cranks were rotated. The exposure device was surveyed, no abnormal readings noticed, and prepared for disassembly. When the crank assembly was removed it was noted that the pigtail was not in the proper position, approximately 1/4 inch further inside the camera than normal. The shipping plugs were placed appropriately and the exposure device was tagged out and transported back to the storage vault. "When the trained technician attempted to remove the locking assembly, one set screw could not be removed. The remaining set screws were replaced and the camera will be shipped back to the manufacturer for repair. "The weather was minus 17 degrees with a wind speed of 18 knots. "There was no exposure to the crew or the general public during this incident." Notified the R4DO (Werner) and FSME (Camper). * * * UPDATE ON 1/25/2010 AT 1058 FROM KEENAN REMELE TO DONALD NORWOOD VIA E-MAIL * * * The report is being updated to provide source and exposure device information. Exposure Device: Industrial Nuclear IR-100 Device S/N: 6761 Source S/N: 0820 Source Type: 82.4 curies, IR-192 Notified R4DO (Pick) and FSME Daytime EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-01-22
45647 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-21 18:20 | 2010-01-21 21:36 | 2010-01-21 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "On January 21, 2010, at 1820 hours, Salem Unit 2 had an Automatic Reactor Trip due to low steam generator (SG) water level in the 22 SG. Prior to the reactor trip, the 21 SG feedwater pump tripped due to low oil pressure. A turbine runback was in progress and SG levels failed to recover. [Also at the time of the reactor trip], the 22 SG feedwater pump tripped on overspeed. "All rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the Steam Dump system, with condenser vacuum maintained. All three AFW Pumps auto started due to low Steam Generator level. Following the trip, the 22 Reactor Coolant Pump (RCP) flange vibration level spiked to approximately 9 mils and returned to a normal value of 2.6 mils. 22 RCP remained in service following the trip. The 21RS12 low pressure turbine intercept valve failed to indicate closed following the turbine trip but was locally verified closed. "Salem Unit 2 is currently in mode 3. The Reactor Coolant System temperature is 547 degrees F with pressure at 2235 psig (NOT and NOP). All ECCS and ESF Systems are available and no ECCS systems actuated during the event. No personnel injuries occurred as a result of the trip." There is no primary to secondary leakage. The electrical shutdown configuration is normal. There was no impact on Unit-1. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-01-21
45646 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-12-07 10:15 | 2010-01-21 15:05 | 2010-01-21 | AGREEMENT STATE REPORT - LEVEL GAUGE SOURCE DISCONNECTED The following excerpted information was received by facsimile: Licensee employees went to the High Pressure Separator Bay to remove a point level gauge so weld repairs could be made to the vessel. "The source was a 3M, Model 4D6L, Cs-137 5000 mCi isotope, Serial Number 71150 in a Ronan SA-10 holder. "The retracting rod was retracted and the shutter was closed. Wanting to be sure the shutter was fully closed, the retracting rod was pushed in and stopped at the shutter. The retracting rod was again retracted, however this time the rod came completely out of the holder. The source capsule was not attached. It appeared that the pins securing the source capsule to the rod had corroded and failed. The retracting rod was reinserted and a survey was done. All present came down from the vessel, barricaded the entry point to the separator bay to prevent access and contacted Thermo-Fisher to have the source removed from the vessel. Radiation readings at the barricaded entry way were 0.1 mR/hr." Representatives from Thermo-Fisher and the Louisiana Department of Environmental Quality arrived on site in order to oversee recovery of the source. On December 11, 2009, the source capsule was removed from the holder and placed into a "capture Type A container" for shipping and disposal. Louisiana Incident Number: LA100002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2010-01-26
45645 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-12-04 | 2010-01-21 14:52 | 2010-01-21 | AGREEMENT STATE REPORT- RADIOGRAPHY SOURCE DISCONNECTED The following information was received by facsimile: "On December 4, 2009, the screwed connection on the source guide tube became disconnected from a radiography camera. The radiographer turned the crank handle too far out. The handle on the crank would not turn in either direction. The Radiation Safety Officer was then contacted. The camera was an AEA 660B serial # B2326. The source was an Ir-192 sealed source, model # A424-9, serial # 57864B. The activity of the source was 78.2 Curies. The crank cable was a QSA model SAN882 with serial # 10465. The source guide tube does not have a model and serial number. While stationed outside of the x-ray cell, the crank assembly hose connections were removed from the crank assembly handle and freed up by pushing the cable back into the crank handle assembly. The sealed source was then slowly cranked back into the shielded position. The camera was surveyed, locked, and returned to storage. The crank assembly was cleaned and had maintenance performed on it the following day. There was no overexposure. The crank assembly worked properly not allowing the cable to slide out of the cranking assembly. Training will be given to make sure and check that the source guide tube is properly tightened during initial assembly. The incident is being investigated [by the Louisiana Department of Environmental Quality]." Louisiana Incident Number: LA100001. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2010-01-26
45644 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-01-21 11:06 | 2010-01-21 15:00 | 2010-01-22 | AGREEMENT STATE REPORT - POTENTIAL LOSS OF AN X-RAY FLUORESCENCE DEVICE SOURCE Thermo-Niton Analyzers LLC was expecting the delivery of an X-Ray Fluorescence device. The carrier was contacted and no delivery was scheduled for that location. The carrier is reviewing records to ascertain where the package is and whether it was delivered to the licensee's previous address. The state did not know the model number of the device or if there was a radioactive source in this device. Thermo-Niton has two Massachusetts licenses: 55-0238 and 53-0388 * * * UPDATE ON 1/22/2010 AT 1129 FROM TONY CARPENITO TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On 1/8/10, Thermo-Niton Analyzers LLC (Thermo) of Billerica, MA, shipped a Niton Portable XRF Analyzer (Model XL-801S, SN U1834, Source IPL Model XFB Series) to REM Aerospace of Fort Lauderdale, FL. On 1/12/10, REM Aerospace informed Thermo the device not yet been received. Subsequent communications determined that REM Aerospace had relocated and the device had been inadvertently shipped to REM Aerospace's previous address. Thermo contacted [the carrier] who returned to the original address on several occasions to recover the package. These attempts to recover the package were unsuccessful. On 1/21/10, Thermo contacted the MA and FL Radiation Control Programs and the Fort Lauderdale Police Department." The XRF Analyzer contains a 10 milliCi Cadmium-109 source. Notified FSME (Camper) and R1DO (Bellamy) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-01-26
45643 | -1 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-13 11:20 | 2010-01-21 10:44 | 2010-01-27 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM TED LOWERY TO JOE O'HARA AT 1719 EST ON 1/27/10 * * * The licensee has retracted the event based upon subsequent information learned during their investigation, a review of NRC written guidance, consult with other security professionals in the nuclear industry, and discussions with NRC Region II security personnel. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO(Widmann) and 73.71 group via e-mail. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-01-21
45642 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2010-01-20 19:35 | 2010-01-20 20:16 | 2010-03-18 | POTENTIALLY OVERPRESSURIZED UF6 CYLINDERS "UF6 cylinders are in storage. The cylinders consist of 1s/2s, hoke tubes, and 5A cylinders. The UF6 is contained in the cylinders, which are in DOT shipping containers (20PF1 and 6M containers). Calculations were performed that indicated that the theoretical pressure in some of the cylinders exceeds the service pressure (200psi) and some exceed the hydrostatic test pressure (400psi). DOE literature indicates that the burst pressure for a 5A cylinder is [approximately] 8,000 psi. The age of the cylinders is 1950s [to] 1980s. The potential pressure in the cylinders is estimated to be by liberation of fluorine gas in the cylinders. Access to the areas has been restricted. The path forward consists of further analysis, evaluation, and understanding of the issue. The cylinders potentially contain fluorine gas. "There were no actual safety consequences to workers, the public, or the environment. The potential consequences are minimal due to restricted access to the areas and the stable condition of the cylinders (i.e., cylinders, shipping containers, building containment). "UF6 cylinders, shipping containers, building containment provide mitigation. Area sprinklers and smoke detection also provide mitigation. Area security cameras provide assistance for monitoring. Security fire patrols [have been] implemented. Other compensatory measures are being considered that include providing uncharged fire hoses to the areas." Licensee has informed the NRC Resident Inspector. * * * UPDATE FROM RANDY SHACKELFORD TO DONG PARK @ 2231 EST ON 01/20/10 * * * "These are additional compensatory actions that have been and will be put in place: "1. Verified operability of smoke detection 2. Verified operability of sprinkler system 3. Established fire patrol inspection. (minimum of 1 inspection per hour) 4. Restricted access 5. Hot work restriction in the restricted areas 6. Verified Fire Brigade members on each shift. (minimum of 5 members each shift) 7. Staging one (1) 150 pound dry chemical extinguisher 8. Staging a fire response vehicle 9. Briefing plant superintendent on status with a superintendent turnover each shift." The licensee has informed the NRC Resident Inspector. Notified R2DO (Sykes), NMSS EO (Smith), and IRD (Gott). * * * UPDATE ON 1/22/2010 AT 1609 FROM RIK DROKE TO MARK ABRAMOVITZ * * * "With regard to the compensatory actions listed in the e-mail dated January 20, 2010, Nuclear Fuel Services, Inc. (NFS) is modifying its commitment to have at least five Fire Brigade members on each shift. Thus, compensatory action No. 6 is being replaced with the following compensatory action: "NFS has developed a specific pre-fire response plan for the areas where the UF6 cylinders are stored. This plan has been reviewed with the Erwin City Fire Chief. NFS plans to provide one trained Fire Brigade member on each shift who will coordinate the Erwin Fire Department response to a fire incident involving a UF6 cylinder." Notified R2DO (Sykes), NMSS EO (Smith), and IRD (Gott). * * * UPDATE ON 3/18/10 AT 1559 EDT FROM JENNIFER WHEELER TO DONALD NORWOOD * * * Following an extensive review by both NFS and independent experts, the analysis of the issue of UF6 cylinders in storage is now complete. The analysis concluded that the likelihood of a release from the cylinders is low, but even if a release were to occur, the consequences to workers, the public, and the environment would be low. Therefore, the additional compensatory actions that have been in place since January 20, 2010, are being discontinued. The licensee notified the NRC Resident Inspector. Notified R2DO (Franke), NMSS EO (McCartin), IRD (McDermott), and Fuels OUO Group via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2010-03-18
45641 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-01-20 13:17 | 2010-01-20 17:10 | 2010-01-20 | OFFSITE FIREFIGHTING ASSISTANCE FOR FIRE IN A NON-SAFEGUARDS DIESEL GENERATOR "While testing, a fire occurred in the D3 Non-Safeguards Diesel Generator at 1317 [CST]. CO2 was applied and at 1337 [CST], the fire was extinguished. A re-flash occurred at 1413 [CST] requiring further fire brigade and fire department action and was extinguished at 1455 [CST]. "No injuries resulted from this fire and it was contained to the D3 Building. The D3 Building is not adjacent or contiguous to any vital areas, and therefore, entry into Emergency Action Levels was not required. This fire did not pose a threat to the safe operation of the plant. "The Red Wing Fire Department was called and arrived on site to assist the plant fire brigade. This resulted in declaring a media sensitive event requiring government agency notifications, and therefore, the need for this report. "The investigation of the cause and extent of damage is ongoing. The [NRC] Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-20
45640 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-01-18 | 2010-01-20 14:52 | 2010-01-22 | AGREEMENT STATE REPORT - POTENTIAL GAUGE SHIELDING FAILURE The following information was received via e-mail: "On January 20, 2010, the Agency [Texas Department of State Health] was notified by the licensee that while conducting routine surveillance on a Texas Nuclear Model 5192 level gauge, dose rates were measured to be greater than 200 millirem per hour (mr/hr). This is the highest reading obtainable with the instrument they [licensee] used. The initial survey for this device was done in November 1981 and indicated a reading of 40 mr/hr at the same location on the gauge. The licensee measured the highest dose rates in any area that could be occupied by company personnel at 0.3 mr/hr. On the ground below the gauge was measured at 0.02 mr/hr. The gauge is located 15 feet above the ground and is attached to the side of the vessel. The dose rates were taken on the outside of the gauge on the top of the gauge casing. The licensee stated that the gauge does not pose any additional exposure risk to their workers. The gauge contained an initial activity of 100 millicuries of cesium (Cs) - 137. The current decay corrected activity is 52.2 millicuries. The licensee has contacted the manufacturer and requested assistance in repairing or replacing the gauge. This is not a shutter failure, but appears to be a shielding failure. The licensee stated that the gauge is not used in an area where temperatures are elevated. "The Agency will perform an onsite investigation on January 21, 2010. The Agency will provide a dose rate instrument capable of measuring the dose rate at the gauge." Texas Incident Number: I-8703. * * * UPDATE ON 1/22/2010 AT 1630 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "On 1/21/10 an Agency [Texas Department of State Health] inspector met with the RSO at the licensee's security office to perform an on-site investigation. He found that the gauge is located below a large tank, which normally contains hydrofluoric acid. There is very limited space between the top of the gauge and the bottom of the vessel. The gauge did not have any buildup of material on it nor were there any streaks on it that would indicate that liquids had leaked on to it. The RSO stated that the gauge is not subjected to high temperatures and that on the day of the event, the temperature at the gauge was about 110 degrees Fahrenheit. The area where the gauge is located requires special training in addition to special protective clothing and monitoring devices to enter. A licensee employee took an Eberline RO-2 instrument provided by the Agency into the area to perform a radiation survey. The dose rate on the top of the gauge was measured at 120 mr/hr. The instrument could not be placed on the very top of the gauge due to the space limitation. The dose rate taken on the side of the gauge was 10 mr/hr. A dose rate taken at the side of the road next to the boundary chain was <0.2 mr/hr. It appears that there may be some type of degradation of the shielding in the gauge. The RSO stated that he was trying to contact the manufacturer for assistance on determining the cause for the increase in dose rates on the gauge. "The licensee has been instructed to notify this Agency when the arrangements are completed for the inspection of the gauge." Notified R4DO (Werner) and FSME (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-01-25
45639 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-01-20 | 2010-01-20 13:22 | 2010-02-16 | AGREEMENT STATE REPORT- STOLEN TROXLER MOISTURE DENSITY GAUGE According to the Radiation Safety Officer, the operator was at a Kinko's store making copies. The Troxler gauge was locked in a case which was locked and chained to the truck in the parking lot. The chain was cut and the gauge was stolen. The licensee will offer a reward. The theft has been reported to the local police department. The incident has been assigned to the Miami Inspection Office for investigation. The gauge is a Troxler model 3430, serial number 34898, containing 40 mCi of Am-241/Be and 8 mCi of Cs-137. Florida Incident Number FL10-007. * * * UPDATE FROM STEVE FURNACE TO JOE O'HARA AT 0935 ON 2/16/10 * * * "[The] gauge [was] found on 2/15/10 in Miami, FL. The gauge will be operationally checked and leak tested. This office [state] will take no further action on this incident." Notified R1DO (Jackson), FSME Day EO(McIntosh), and ILTAB(Pearson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-01-25
45638 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-12-16 09:00 | 2010-01-20 12:20 | 2010-01-20 | POSSESSION OF ALCOHOLIC BEVERAGE IN PROTECTED AREA "At approximately 0900 on December 16, 2009, a PPL employee, located within the Susquehanna protected area, received a gift package from a vendor that contained a bottle of an alcoholic beverage. The individual immediately notified his supervision and Susquehanna Security personnel who took possession of the bottle. The bottle was still sealed with the original seal. The NRC [Resident Inspector] and Regional Security Inspectors were informed on the day of the event. "The individual who received the package was a non-licensed employee. "This event was originally not recognized as being reportable as a 24 hour call." | 94 | 94 | 0 | 94 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2010-01-20
45637 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-01-18 10:30 | 2010-01-19 16:00 | 2010-01-19 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK IN OPEN POSITION The shutter for a fixed nuclear gauge located 30 feet off the ground was attempted to be closed. The handle sheared off and the shutter remained stuck in the open position. The repair facility has been contacted and repairs are expected to be made in 5-7 days. No exposures resulted from this incident. The gauge was from Ohmart/VEGA Corporation containing a 375 milliCurie Cesium (Cs) - 137 source. Texas Incident: I-8702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-01-22
45636 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-01-19 04:30 | 2010-01-19 11:20 | 2010-01-19 | EMERGENCY SIREN SPURIOUS ACTUATION "On January 19, 2010, at about 0445 PST, the SONGS Control Room was notified of a spurious actuation of a SONGS emergency response siren located in the city of San Clemente. "The actuation occurred on January 19, 2010 at about 0430 PST for a duration of approximately 30 minutes. Upon investigation the siren was put into a silent test mode and technicians were able to duplicate the sounding. The siren was subsequently put into an inoperable status pending investigation and the cause of the actuation is unknown at this time. "SCE [Southern California Edison] personnel notified Orange County, the City of San Clemente and the City of Dana Point regarding the inadvertent actuation of part of the public notification system. "In compliance with 10CFR50.72(b)(2)(xi), requiring licensees to report any event that results in notification to other government agencies, SCE is providing this notification to the NRC. "At the time of this occurrence, Unit 2 was shutdown for a Steam Generator Replacement Outage and Unit 3 was operating at about 100 percent power. SCE will notify the NRC Resident Inspectors about this occurrence and will provide them with a copy of this report." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-19
45635 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2010-01-19 05:53 | 2010-01-19 08:35 | 2010-01-19 | OFFSITE FIRE DEPARTMENT ASSISTANCE REQUIRED FOR A FAILED RESIDENTIAL TRANSFORMER "At 0553 hours on 01/19/2010, plant personnel noted smoke emanating from a residential transformer within the Protected Area which was not affecting plant operation. The on-site fire brigade was dispatched to investigate. Rochester Gas and Electric Corporation (RG&E) was notified to isolate the off-site power supply to the transformer. While awaiting the arrival of RG&E personnel, the on-site Fire Brigade noted that the transformer smoke was worsening along with increased noises from the transformer. The Ontario Fire Department was notified at 0715 hours to provide off site assistance. "Ginna remains at 100% power, normal operating temperature of 574 degrees, and normal operating pressure of 2235 psig." The transformer supplies power to office trailers. The licensee notified the state and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-19
45634 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-01-18 19:50 | 2010-01-18 23:43 | 2010-01-21 | EMERGENCY OPERATIONS FACILITY INACCESSIBLE DUE TO ROAD FLOODING "On January 18, 2010, at about 1950 PST, the access road to the SONGS MESA facilities became flooded after a day of rain. The San Onofre Emergency Operations Facility (EOF) is located at the MESA and because of the flooding, is inaccessible to passenger vehicles. While the EOF itself is operable, in the event of an emergency at San Onofre, SCE [Southern California Edison] would direct EOF emergency responders to the alternate EOF located in Irvine, California. SCE is reporting this occurrence to the NRC in accordance with 10CFR50.72(b)(3)(xiii). "At the time of this occurrence, Unit 2 was shutdown for a Steam Generator Replacement outage and Unit 3 was operating at about 100% power. SCE will notify the NRC Resident Inspectors about this occurrence and will provide them with a copy of this report." * * * UPDATE FROM GEOFF COOK TO DONG PARK @ 1208 EST ON 01/19/10 * * * "On January 18, 2010 at about 2101 PST, the MESA road flooding had dissipated sufficiently for car traffic to be passable. In the event of an emergency at San Onofre, there is no longer a need to redirect emergency responders to the alternate EOF located in Irvine, California. This report is to advise the NRC of this change in EOF access status. Also note that it is expected that rain will continue in the SONGS area during the week of January 17, 2010 and this status is subject to change. "At the time of this occurrence, Unit 2 was shutdown for a Steam Generator Replacement Outage and Unit 3 was operating at about 100% power. SCE will notify the NRC Resident Inspectors about this occurrence and will provide them with a copy of this report." Notified R4DO (Werner) and NSIR (Kahler). * * * UPDATE FROM GEOFF COOK TO PETE SNYDER @ 1232 EST ON 01/21/10 * * * "On January 20, 2009, at about 2107 PST, the access road to the SONGS MESA facilities again became flooded after a day of rain (reference NRC Operations Log Number 45634). The San Onofre Emergency Operations Facility (EOF) is located at the MESA and because of the flooding, is inaccessible to passenger vehicles. While the EOF itself is operable, in the event of an Emergency at San Onofre, SCE would direct EOF emergency responders to the alternate EOF located in Irvine California. SCE is reporting this occurrence to the NRC in accordance with 10CFR50.72(b)(3)(xiii). "At the time of this occurrence, Unit 2 was in a Steam Generator Replacement Outage and Unit 3 was operating at about 100% power. SCE will notify the NRC resident inspectors about this occurrence and will provide them with a copy of this report." Notified R4DO (Werner) and NSIR/EP. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-01-19
45633 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2010-01-18 15:00 | 2010-01-18 23:03 | 2010-01-20 | MISSING RADIOACTIVE SOURCES GREATER THAN 10 TIMES THE LIMIT "In 2009, a radioactive source inventory was conducted by a Prairie Island Radiation Protection Specialist. During the inventory, it was determined that two sources were missing that are greater than 10 times the quantity specified in 10CFR20 Appendix C. These two sources include a 0.07 [micro]Ci U-234 radiation monitor detector and a 0.2 [micro]Ci mixed gamma standard that contains 0.09 [micro]Ci of Am-241 (a 60 ml vial used for HPGe calibration.) The U-234 source is normally stored in the Hot I&C Shop and the mixed gamma standard with Am-241 is normally stored in the Hot Chemistry Lab. The inventory, that concluded on December 18, 2009, listed these sources as lost. Four other sources, that do not exceed 10 times any quantity specified in 10CFR20 Appendix C, were also unaccounted for during this inventory. Radiation Protection is still in the process of locating the missing sources that were identified during this inventory." The licensee will provide information on the four other sources to the Operations Center on 1/19/2010. The licensee has informed the NRC Resident Inspector. * * * UPDATE FROM STEVE INGALLS TO DONG PARK @ 1547 EST ON 01/19/10 * * * "The four sources that do not exceed 10 times any quantity specified in 10CFR20 Appendix C: "Isotope Ci Content "C-14 TLD check source 0.5 [micro]Ci "Cs-137 check source 8.8 [nano]Ci "mixed gamma calibration source 1.9 [micro]Ci "mixed gamma calibration source 2.0 [micro]Ci "The 2.0 [micro]Ci mixed gamma source (previously reported as 0.2 [micro]Ci) that contains 0.09 [micro]Ci of Am-241(60 ml vial used for HPGe calibration) has been located in the Hot Chemistry Lab. Investigation into the five remaining sources continues." The licensee has informed the NRC Resident Inspector. Notified R3DO (Pelke), NRR EO (Cunningham), FSME EO (Camper), and Canada via fax. * * * UPDATE FROM JOHN KEMPKES TO VINCE KLCO @ 2039 EST ON 01/20/10 * * * "Current status update on the sources that exceed 10 times any quantity specified in 10CFR20 Appendix C: "The 2.0 [micro]Ci mixed gamma source - located and properly stored. The source was within the controlled area. (Previously reported) "The 0.07 [micro]Ci U-234 radiation monitor detector - installed in Containment (located by maintenance documentation review). (Previously reported) "While conducting a verification of all sources, a different 0.07 [micro] Ci U-234 radiation monitor detector was discovered to be missing. This detector is the same design as the originally reported U-234 detector but a different serial number. (New item) "The station has completed a verification of all sources; the results are undergoing management review. Search for the missing sources continues. "The Resident Inspector has been notified." Notified R3DO (Pelke), NRR EO (Cunningham), FSME (Camper), and Canada via fax. THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-01-18
45632 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-01-14 14:45 | 2010-01-14 19:28 | 2010-01-14 | AGREEMENT STATE - MISSING MOISTURE DENSITY GAUGE "Zell's former consultant HP (Health Physicist) informed DEP (Department of Environmental Protection) that [a] nuclear gauge was discovered [to be missing] while performing a 6-month inventory on January 13. An unsuccessful search for the missing nuclear density gauge (Humboldt Model 5001 EZ122; Ser. No. 5375) was concluded on January 14. The licensee notes the gauge cannot be accounted for at this time. Gauge contains about 10 milliCuries Cs-137 and 40 milliCuries Am-241 (as an Am/be neutron source)." PA Event #: PA100001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-01-19
45631 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-07-07 21:47 | 2010-01-14 17:59 | 2010-01-14 | LOSS OF FIRE SUPPRESSION CAPABILITY "This is an 8-hour notification being made in accordance with 10CFR 50.72(b)(3)(ii)(B) for an event or condition that results in the plant being in an unanalyzed condition that significantly degrades plant safety. "This notification is being made as the result of the re-review of a July 7, 2008 occurrence which resulted in an inadvertent isolation of a large portion of the [fire suppression] ring header affecting all Unit 2 fire suppression and a portion of Unit 1 fire suppression. The Unit 1 ring header isolation did not have an affect on the fire safe shutdown capability of Unit 1. However, three areas in Unit 2 which credit the availability of fire suppression to assure that the safe shutdown capability could have been achieved did not have fire suppression for approximately 3 hours. "A Licensee Event Report will be submitted within 60 days." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-01-14
45630 | 0 | QHG OF INDIANA |  |  |  |  | 2010-01-14 14:00 | 2010-01-14 16:00 | 2010-01-14 | INCORRECT DOSE ADMINISTERED TO PATIENT Two patients were to receive hyper thyroid therapy on 1/14/10, and the hospital prepared written directives for each patient. One patient was prescribed 25 milliCurie of I-131. The second patient was prescribed 30 milliCurie of I-131. The first patient arrived and the technician assayed and administered the 30 milliCurie dose for the patient who was to receive 25 milliCurie. The tech administered 31.4 milliCurie to the patient. This is a 25.6% difference than prescribed in the written directive for the patient. The patient and prescribing physician have not been informed. The hospital does not believe there is any long term medical consequence to the patient. The hospital management team is reviewing protocols to prevent recurrence of this event. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-01-20
45629 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-01-13 08:50 | 2010-01-14 08:50 | 2010-01-14 | PROCESS GAS LEAK DETECTION SYSTEM INOPERABLE "At 0850 CST, on 1-13-10 the Plant Shift Superintendent (PSS) was notified that the C-333 B-Booster UF6 Release Detection (PGLD) system was inoperable due to loss of power to the system. The purpose of the PGLD System is to detect a UF6 release and alert operators in the ACR by sounding an alarm. At the time this was discovered, some areas covered by this PGLD system were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the areas covered by this PGLD system are operable during steady state operations above atmospheric pressure. With the B-Booster PGLD system inoperable, none of the required heads were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.D.1 and 2.4.4.1.E.1 were entered, and a continuous smoke watch was put in place within one hour. An investigation was initiated and it was determined that power was interrupted during planned maintenance activities and there was a failure to identify that the power supply to this PGLD system would be impacted prior to performing the maintenance. Power was restored and the system was tested and declared operable at 1542 hours. This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2010-01-14
45628 | -1 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-01-13 11:25 | 2010-01-13 22:43 | 2010-01-19 | WRONG TRAIN OF EMERGENCY CORE COOLING SYSTEM REMOVED FROM SERVICE "On January 13, 2010, at about 1125 PST, Train A suction piping from the SONGS Unit 3 Refueling Water Storage Tank (RWST) was determined to be inoperable following detection of weld flaw indications during ultrasonic testing. Due to miscommunication, operators mistakenly declared the Train B Emergency Core Cooling System (ECCS) header inoperable at about 1125 and removed DC control power to the Train B ECCS pumps. This resulted in both trains of Unit 3 ECCS being inoperable and entry into the Technical Specification (TS) 3.0.3 one-hour shut down action. At 1140 PST, the DC control power was restored to the Train B ECCS pumps, Train B ECCS was declared operable, and TS 3.0.3 was exited. SCE is reporting this in accordance with 10 CFR 50.72(b)(3)(v) as an event that could have prevented the fulfillment of a safety function. "SCE is further evaluating the indications found on Train A piping to determine if the piping is capable of performing its safety function. At the time of this occurrence, Unit 2 was in a Steam Generator Replacement Outage, and Unit 3 was at approximately 100% power." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY LEE KELLY TO DONG PARK AT 1402 EST ON 1/19/10 * * * "On January 13, 2010, SCE reported that both trains of Unit 3 Emergency Core Cooling System were inoperable for approximately 15 minutes because Train B ECCS was mistakenly taken out of service when weld flaw indications were found on Train A ECCS piping. This resulted in a condition that could have prevented the fulfillment of a safety function. Consequently, both trains of ECCS in Unit 3 were declared inoperable and the unit entered into Technical Specification 3.0.3 at 1134 PST (Time of Discovery). At 1140 PST, Train B ECCS was declared operable and TS 3.0.3 was exited. "Event Notification 45628 was conservatively made because, although Train A ECCS piping remained capable of performing its safety function, this was not yet formally documented at the time the 8-hour report was due. Subsequently, an engineering evaluation was completed at 2308 PST on January 13, 2010, that demonstrates the as-found condition of the Train A ECCS piping was operable because the flaw meets the evaluation criteria of ASME Boiler and Pressure Vessel Code Case N-513-2. Since Train A ECCS piping was operable, this event did not constitute a condition that could have prevented the fulfillment of a safety function and is not reportable under 10 CFR 50.72(b)(3)(v)(D). "Consequently, SCE is retracting the phone report to the NRC on January 13, 2010. The NRC Resident Inspector will be informed of this report." Notified R4DO (Werner). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-01-13
45627 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-13 01:59 | 2010-01-13 02:24 | 2010-01-13 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO CONTROL ROOM CHILLERS OUT OF SERVICE "The A-YC chiller [was] shutdown and tagged for yearly inspection and work. The B-YC chiller has developed a refrigerant leak and has been declared inoperable. This places both Unit 1 and Unit 2 in Tech Spec 3.0.3. Both units will have to be in Mode 3 within 7 hours; Mode 4 within 13 hours; and 37 hours to be in Mode 5. 3.0.3 was declared at 2332 on 1/12/2010. The event time is when Unit 1 began load reduction. Unit 2 will commence load reduction at 0230." The licensee notified the NRC Resident Inspector. | 89 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) |  |  | 0 | 2010-01-13
45626 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-01-09 | 2010-01-12 16:10 | 2010-01-12 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECTED "On Saturday, January 9, 2010, the Radiation Safety Officer (RSO) of IESCO, LLC, contacted the California Office of Emergency Services to report that a Selenium 75 (27.5 Curies) industrial radiography source disconnected from the drive cable during radiography operations at the Chevron, El Segundo Refinery. During the first exposure, the source disconnected from the drive cable. This was discovered during the radiographer's confirmatory survey, as required after the source is cranked back in the shielded position. It was discovered that the source was disconnected near the collimator and when the drive cable was retracted, the source would slide back a couple of inches and the pigtail would be caught at a bend in the guide tube, allowing the source to be partially removed from the collimator. The radiographer placed lead shielding over the exposed source to minimize radiation exposure. The radiographer then contacted the RSO. Upon arrival at the site, the RSO disconnected the guide tube from the exposure device and then assessed the situation. He placed more lead shielding on the camera until the dose rate at 6 feet was at 20 Mr/hr. He returned the drive cable to the guide tube, reinserted the drive cable into the guide tube and removed the guide tube from the collimator. The RSO was then able to connect the drive cable to the pigtail and crank it back into the exposure device. The RSO stated that the reading taken from the Direct Reading Pocket Dosimeter (DRPD) of the radiographer was 9 Mr and the DRPD of the RSO was 25 Mr. "After inspecting the equipment and interviewing the radiographer and assistant, the RSO concluded that the source disconnect occurred due to dirt on the shutter of the drive cable preventing the cover on the pigtail from closing, preventing a secure connection. The RSO has scheduled a safety meeting to ensure that the radiographers are aware of the issue and instructed how to avoid another incident. Further investigation will be deferred until the 30 day report has been submitted and reviewed." California Report No: 5010-010910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-01-15
45625 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2010-01-10 08:30 | 2010-01-12 14:10 | 2010-01-12 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF TRITIUM IN WATER LEAKAGE ONSITE "At 8:30 a.m. on January 10, 2010, an operator on regular rounds discovered the underground Waste Neutralization Basin Flash Mixer Return Pipe had developed a leak. The eight-inch fiberglass pipe carries secondary plant and water treatment building waste water for chemical processing. Approximately 1,000 gallons of water containing a low level of tritium (5,590 picocuries per liter) leaked into the surrounding soil. The EPA Drinking Water Standard is 20,000 picocuries per liter. "Once the leak was discovered, the system was secured and the leak was isolated. Crews are repairing the pipe. The spill has been contained within the plant backfill and is unlikely to migrate off-site or reach the water table. The affected area is located within the plant's site boundary, approximately 15 feet west of the Water Treatment Building, and involves roughly 100 cubic feet of soil. Once repaired, the system will be tested and returned to service. "Immediate remedial actions involving the affected area include: pumping the water from the saturated ground back into the waste neutralization basin, removal of the tritiated soil and sampling soil in the area for tritium analysis. "The health and safety of the public are not affected by this event, based on the location of the leak and the low tritium levels. Harris Nuclear Plant is following the guidance in NEI 07-07 and has initiated this Event Notification as a result of our voluntary communication to State agencies in accordance with the Groundwater Protection Initiative." The licensee will be notifying North Carolina Divisions of Radiation Protection and Water Quality and has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-12
45624 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2010-01-11 15:59 | 2010-01-11 18:31 | 2010-01-11 | AUTOMATIC TRIP DUE TO MAIN GENERATOR ELECTRICAL TRIP "At 1559 on January 11, 2010, Indian Point Unit 2 tripped from 100% power due to a main generator electrical trip. The investigation into the generator trip is ongoing. All systems responded as expected. The auxiliary feedwater system responded as expected and is maintaining steam generator water levels. Decay heat removal is via the steam generators to the main condenser. Offsite power and plant electrical lineups are normal. No primary or secondary side relief valves lifted. The reactor plant is in mode 3 and stable. "Indian Point Unit 3 was not affected and remains at 100% power." The licensee notified the NRC Resident Inspector and the N.Y. State Public Service Commission. The licensee intends to notify the Mayor's Office and issue a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-01-11
45623 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-01-11 15:10 | 2010-01-11 16:53 | 2010-01-11 | OFFSITE NOTIFICATION DUE TO WATER SEEPAGE ON AN ONSITE STRUCTURE "A verbal report was made to the Federal Energy Regulatory Commission (FERC) Engineer on January 11, 2010 at 1510 hours pursuant to 18CFR12.10(a) for a condition affecting the safety of a project or works. A new wet area has been identified on the slope of Dike 6, approximately 25 feet from the top of the structure. Dike 6 was designed and created during original plant construction to support electrical towers and provide isolation between Lake Anna and the proposed Unit 3 & 4 intake structures. The Unit 3 & 4 intake area is currently being used as a settling pond. The settling pond is used to process storm water and other secondary water before the liquid is discharged from the station. "This minor seepage is located about half way down the slope to the settling pond. Water samples were obtained from the wet area and it was determined that the seepage was not ground water. The sample composition was similar to the water in Lake Anna. Currently, there is no threat to the public or North Anna Power Station. Engineering is investigating this issue and a corrective action plan will be developed to correct the minor seepage. "This issue is being reported pursuant to 10CFR50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector and the local government. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-11
45622 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-12-03 | 2010-01-11 15:37 | 2010-01-11 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING A GAMMA KNIFE "On December 2, 2008 Austin Headquarters IIP [Incident Investigation Program], was notified of a medical event with a Leksell Gamma Knife resulting in a dose of approximately 15 Gray (1,500 rad) to the wrong cranial nerve. The incident involved the use of a medical gamma stereotactic radio surgical device known as a gamma knife (GK). Essentially the wrong nerve was designated for treatment for a trigeminal procedure that typically calls for a 80 Gray dose within a 4 mm sphere. Treatment of trigeminal neuralgia can account for as many as 20% of the workload on GK facilities with a standard protocol of 80 Gray to the base of the 5th intracranial nerve yet in this case the 7th cranial nerve was mistakenly targeted. Fortunately, for a reason not clear, the authorized neurosurgeon instructed the Licensed Medical Physicist (LMP) to pause the treatment 9 minutes into a 45 minute regime. He then consulted again with the neuroradiologist on the case and they both determined that the slice used in the treatment plan was the 7th not the intended 5th cranial nerve some one centimeter [away]. The physicians on the case do not expect any untoward effect upon the patient who was notified of the mishap and actually resumed successful treatment on the same day. It was the conclusion of the clinical staff who participated on the case that the root cause was a misidentification of the anatomical target site as listed on the Written Directive (WD). The 15 day report by the RSO stated that he has implemented specific measures as corrective actions to prevent recurrence. These include: 1) a change in the written procedures to include a verification of the target site by the neuroradiologist for each case and 2) a modified WD to document the new procedural change to ensure that the correct treatment site is targeted and treated in each procedure. "The department will conduct a review of at least 20% of past cases to ensure that this error had not occurred before however the clinicians were of the opinion that such a dose to the wrong site would have pronounced and readily observable clinical manifestations. "On December 17, 2008 the Agency [State of Texas] received a fax from [the] licensee Radiation Safety Officer detailing the medical event. He noted that the Written Directive was complete and signed by all appropriate parties. The exposure to the 7th cranial never was precisely 9.17 minutes resulting in a dose to other tissue of 14.95Gy and to the 5th trigeminal nerve (targeted site) a negligible dose of 10-20 cGy while 80 Gy was intended. Therefore the patient had treatment continued on the correct anatomical site with apparent success. The authorized physicians attest that the misadministration will have no untoward effects upon the patient. For corrective action it will be documented that the neuroradiologist has provided precise information on the MRI slice of the 5th cranial nerve for Trigeminal Neuralgia treatments. "This event was reported to the Nuclear Material Events Database (NMED) (090019) instead of to the Headquarters Operations Officer as required. This file is closed in NMED." Texas Incident No. I-8585 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-01-17
45621 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-01-11 | 2010-01-11 15:00 | 2010-01-11 | AGREEMENT STATE REPORT - QSA GLOBAL REPORT OF DEFECT "On January 8, 2010, at 1552 hrs. EST, QSA Global, Inc. reported a product defect to the Massachusetts Radiation Control Program in accordance with 105 CMR 120.142(B)(2)(a). The affected equipment that was identified was the QSA Model 87703 source assembly for a QSA Global radiography camera. A customer had received a Model 87703 source assembly and reported problems with the assembly connection on October 21, 2009. The unit was returned to their Burlington office and QSA Global, Inc. performed an evaluation of the extent of the defect. The Model 55000-3 female connector sleeve was identified as the source of the problem. "The defect causes the male connector to not be fully seated in the sleeve of the connector and it was, therefore, not locking in. This could give the user the false impression that the source is connected to the drive cable when there is only a partial connection. The operations manual requires that the user visually check the connection prior to use. If the user does not do a full visual inspection of the connection, the source assembly may not be secure and could dislodge inside guide tube. "The manufacturer conducted a 100% search of a lot of 1,567 pieces in stock and found 5 to be defective. The manufacturer is sending out notice dated January 11, 2010 to all of their radiography customers describing this disconnect issue. There are 236 sources in the field with 29 different licensees that have not sent their units back to QSA Global in Burlington, MA at this time. They will continue to monitor this problem as assemblies are returned." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-01-14
45620 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-12 04:00 | 2010-01-11 14:00 | 2010-01-12 | UNAVAILABILITY OF TSC VENTILATION SYSTEM AND CHARCOAL FILTER FOR SCHEDULED MAINTENANCE "The Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system air conditioning and filtration systems are scheduled to be removed from service for scheduled preventive maintenance at 0400 on January 12, 2010. "Under certain accident conditions, the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system air conditioning and filtration systems are scheduled to be restored to service by 1400 on Tuesday January 12, 2010. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to unavailability of an emergency response facility." * * * UPDATE FROM BEN HUFFMAN TO HOWIE CROUCH @ 1420 EST ON 01/12/10 * * * "The TSC ventilation system and charcoal filter were returned to functional status at 1418 EST on Tuesday, January 12, 2010. "This follow up notification is being made to provide closure of the initial notification under 10 CFR 50.72 (b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-01-11
45619 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-01-11 10:55 | 2010-01-11 12:54 | 2010-01-11 | MANUAL REACTOR TRIP INITIATED DUE TO HIGH STEAM GENERATOR LEVEL "At 1055 on 1/11/2010, Turkey Point Unit 4 was manually tripped on high steam generator level. Steam generator level was high due to plant response to a turbine runback. The runback was manually initiated by stopping the 4A Steam Generator Feed Pump from the Control Room due to mechanical seal failure. "At the time of the trip, reactor power was 30%. Auxiliary Feedwater was not required since Steam Generator levels were maintained above the low level actuation setpoint. "Unit 4 has been stabilized in Mode 3 on normal off-site power. No significant equipment problems were encountered. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) - actuation of the Reactor Protection System with the reactor critical." All rods inserted during the trip. There were no relief or safety valves that lifted during the transient. Decay heat is being removed via steam dumps to atmosphere. There is no known primary to secondary leakage. Unit 4 is in a normal shutdown electrical lineup. Unit 3 was not affected by the transient. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-01-11
45618 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-09 19:51 | 2010-01-09 21:33 | 2010-01-09 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO A FIRE IN THE AUXILIARY BUILDING LASTING GREATER THAN 15 MINUTES "At 1925 [hrs. CST], the Main Control Room received a notification of smoke in the Auxiliary Building Ventilation Supply Plenum. Fire Brigade and the Incident Commander were dispatched. Once [they] arrived at the scene, they noted smoke in the area of the 0C VA Supply Fan and requested the fan be shutdown. The 0C VA supply fan was shutdown at 1933 hrs. The operators reported smoke and a small fire coming from the inboard bearing of the 0C VA supply fan. A CO2 fire extinguisher was used to put the fire out and cool the bearing. A total of 2 extinguishers were used. The fire was declared out at 1941 hrs. Both Units remained stable and at full power during the entire event. "There were no injuries, and no off site assistance was required." The licensee notified state and local authorities and the NRC Resident Inspector. * * * UPDATE FROM DEBOARD TO CROUCH @ 2231 CST ON 01/09/10 * * * "At 2111 CST [on] 1-9-2010, the Unusual Event was terminated. The fire is out. Both Units are stable. A fire watch is established. There are no signs of reflash. [Braidwood] no longer [meets the] Unusual Event action level threshold." The licensee has notified the NRC Resident Inspector. Notified IRD (Grant), R3DO (Stone), NRR EO (Giiter), DHS (Inzler) and FEMA (Casto). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-01-09
45617 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-01-09 10:28 | 2010-01-09 12:14 | 2010-01-09 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON SUDDEN PRESSURE IN OUTPUT TRANSFORMER "At 1028 CST on the 9th of January, Unit 1 tripped due to turbine trip greater than 50% reactor power. The turbine trip was caused by a sudden pressure fault of the Unit 1 main generator output transformer (1MT1). "All systems operated as designed. All three auxiliary feedwater pumps auto-started as required. There were no complications noted on the reactor trip. "Current status: Holding in mode 3 and shutting down secondary equipment. Decay heat removal is via auxiliary feed and main condenser steam dumps." All rods inserted during the trip. No relief or safety valves lifted during the transient. The electrical grid is stable and Unit 1 is in its' normal shutdown electrical lineup. Investigation of the transformer fault is underway. Unit 2 was unaffected by the transient. The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-01-09
45616 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2009-12-23 10:14 | 2010-01-08 18:15 | 2010-01-08 | LOSS OF RHR COOLING CAPABILITY DUE TO ISOLATION OF THE SPENT FUEL POOL COOLING HEAT SINK "This is a late eight hour report submitted under 10CFR50.72(b)(3)(v), 'Loss of Safety Function to (B) Remove Residual Heat' "On December 23, 2009 at about 0957 PST, with SONGS Unit 2 defueled for the Cycle 16 refueling outage, a decrease in salt water cooling flow to the Train A Component Cooling Water Heat Exchanger indicated debris was entering the system. The loss of flow appears to have been caused by debris entering the system through a failed pump suction screen. At 1014 PST operators removed the heat exchanger from service for approximately one hour to reverse the salt water cooling flow though the heat exchanger and clear the debris. The Train B cooling system had previously been removed from service for scheduled maintenance, relying on the single Train A heat exchanger to supply cooling to the Spent Fuel Pool cooling system. "Salt water cooling flow was fully restored at approximately 1118 PST. Operators conservatively declared the Spent Fuel Pool Cooling System inoperable and maintained compliance with the conditions of Licensee Controlled Specification 3.7.106. Time to exceed the 160 degree Fahrenheit allowable pool temperature was estimated at over twenty three hours. "It has been determined that the temporary isolation of the heat sink from the spent fuel pool constituted a loss of safety function for residual heat removal. Therefore SCE is reporting this occurrence as a loss of safety function in accordance with 10 CFR 50.72(b)(3)(v). "The safety significance of this event was minimal. Flow reversal to clear ocean debris from the heat exchangers is a routine procedurally controlled evolution and bounded by design calculations which consider post-accident heat loads with a full core offload in the spent fuel pool. These actions are within the limits of both the Technical Specifications and Licensee Controlled Specifications." The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-01-08
45615 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-01-08 13:29 | 2010-01-08 15:00 | 2010-01-11 | EMERGENCY SIRENS MAY BE IMPACTED BY EXTREME WEATHER CONDITIONS "The current NOAA weather forecast for the station is predicted to be about -25 degrees Fahrenheit [on the morning of January 9, 2010]. Based on this forecast, the station reviewed the impact of these temperatures on the 101 sirens in the Fort Calhoun Station 10-mile Emergency Planning Zone (EPZ). The siren manufacturer's and the FEMA approved siren design report information states that the sirens (Federal Signal model 2001) are designed for operation between the temperature readings of -22 degrees Fahrenheit and +140 degrees Fahrenheit. "Event Numbers 44782 and 44783, on a similar condition at another utility having the same sirens, were reviewed. It was noted that the reports documented discussion with the manufacturer's technical representative confirming that the sirens are operational and no special testing is required when the temperature goes below and then returns within the operating temperature limits. "The current temperature at the station is within the operational limits. Therefore, the 101 sirens are considered functional at this time. "The following agencies were notified that if the temperature falls below a negative twenty-two degrees Fahrenheit, the established process of back-up route alerting is to be used notifying the public in the event of a nuclear emergency where the sirens are activated but fail to respond: -Washington County, NE Emergency Management -Pottawatomie County, IA Emergency Management -Harrison County, IA Emergency Management "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). No media press release is being made." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ERICK MATZKE TO HOWIE CROUCH AT 1513 EST ON 1/11/10 * * * "A review of area temperature indicates that the siren design was not exceeded." The licensee will be notifying the NRC Resident Inspector. Notified R4DO (Hagar). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-01-08
45614 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-01-07 13:00 | 2010-01-07 16:57 | 2010-01-07 | OFFSITE NOTIFICATION DUE TO THE DISCOVERY OF CONTAMINATED DOLLAR BILLS "An individual entered the plant access and alarmed [the] portal radiation monitor. Upon investigation the individual's wallet contained three contaminated one dollar bills. The individual had processed out of similar monitors the previous day without indication of contamination. The three one dollar bills were surveyed and it was determined that they contained only I-131. The individual was interviewed and it was determined that the contaminated money was likely obtained at a local merchant. The individual is not aware of anyone undergoing iodine therapy. I-131 is used for therapy and diagnostic medical practices. The Corporate Health Physicist called the Nebraska Department of Health and Human Services, Radiological Health Division about the incident and location. The bills are contaminated above levels acceptable for the plant. The conclusion is that someone not associated with the power plant had iodine treatment, contaminated the bills, used them at the store and the individual received those bills as change. "There is no reason to believe that contamination has any connection to the operation of power plant." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-07
45613 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2010-01-07 15:30 | 2010-01-07 16:55 | 2010-01-07 | OFFSITE NOTIFICATION TO STATE AND LOCAL AGENCIES CONCERNING RESULTS OF QUARTERLY GROUND WATER ANALYSIS "On January 6, 2010, Vermont Yankee (VY) was notified that the results of fourth quarter 2009 ground water sampling, performed as part of the voluntary ground water monitoring program, identified a very low concentration of tritium in one well that is used to monitor station ground water. VY has notified state, local and other government agencies of this condition. Since no other wells indicated the presence of tritium and the concentration detected is below the reporting threshold identified in the Off-site Dose Calculation Manual, notifications were considered voluntary consistent with NEI 07-07 'Industry Ground Water Initiative - Final Guidance Document.' This report is being made in accordance with 10 CFR 50.72(b)(2)(xi) to notify the NRC of these voluntary notifications. There is no impact on public health and safety as a result of this event. "The NRC Resident Inspector has been notified." | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-01-07
45612 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2010-01-07 01:00 | 2010-01-07 04:38 | 2010-01-07 | AUTOMATIC REACTOR SCRAM DURING TRANSMITTER VENTING "At 0100, Nine Mile Point Unit 2 reactor scrammed [on low reactor water level]. The cause is currently under investigation. Maintenance activities were in progress on Residual Heat Removal (RHR) B & C systems. It is suspected that transmitter venting is the most probable cause of the trip. Reactor core isolation system (RCIC) injected on invalid level 2 signal. No safety relief valves (SRV's) actuated. B and C Residual Heat Removal systems (RHR) remain inoperable. All other ECCS systems and Emergency Diesel Generator are currently operable. Reactor water level is normal. No emergency core cooling system injection was required. The plant is currently in the hot shutdown condition. No emergency plan activation is required. Activation of forced outage plan is in progress. "Lowest reactor water level reached during the transient was 140 inches. This is less than the reactor water level scram set point of 159.3 inches. "Reactor pressure before scram was 1020 psig, current reactor pressure is 530 psig and reactor coolant temperature is 470 degrees F. Plant stack monitor is not available. Last grab sample reading at time 0257 is 857 micro-curies/sec. "All systems functioned as required. All rods fully inserted on trip." Decay heat is being removed by steaming to the main condenser. The plant is in its normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-01-07
45611 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-12-31 20:28 | 2010-01-06 21:26 | 2010-01-06 | ACTUAL ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-01-06
45610 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-01-04 | 2010-01-06 11:56 | 2010-01-11 | AGREEMENT STATE - MOISTURE DENSITY GAUGE FOUND IN SCRAP METAL "The department received an email on January 4, 2010 from Miller Compressing, Milwaukee, WI, describing a load of scrap metal received on December 24, 2009 that set off the radiation detector. On January 4, 2010, they isolated a damaged Seaman Nuclear Model R-75 moisture density gauge containing 4.5 mCi of Radium-226, serial number 3276. Miller Compressing placed the device in a locked storage area. Seaman Nuclear has agreed to conduct a leak test to ensure source integrity and transport the device back to their facility in Oak Creek, WI this week." WI Report No.: WI100001 * * * UPDATE FROM SHUNLAI ZHU TO JOE O'HARA VIA E-MAIL ON 1/11/10 AT 1115 * * * "Seaman Nuclear conducted a leak test on January 8, 2010 and found the radioactive source was shielded and no removable contamination. They transported the device back to their facility in Oak Creek, WI." Notified R3DO(Stone) and FSME EO(McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-01-11
45609 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2010-01-06 01:50 | 2010-01-06 11:41 | 2010-01-06 | FAILURE TO FULLY RETRACT THE SOURCE OF A RADIOGRAPHY CAMERA "On January 6th a radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an INC IR-100 exposure device. "When returning the source (Ir-192, 108 curies) the locking bar deployed prematurely. The crew reset the locking bar and was able to return the source to the safe and secure position. The crew was working a remote location using a Tucker (tracked machine for traveling over snow) and called for the night foreman. They met at a drill site where the exposure device was reconnected to the drive cables. The source was extended and then retracted. It was noticed that on the return the crank assembly became hard to turn. After the locking bar tripped, the exposure device was surveyed with no noticeable indication that the source was not in the safe and secure position. When the crank assembly was disconnected it was noted that the pig tail was not in its proper position. The exposure device was transported back to the main office. "When the lock was disassembled there the technician noted: 'The lock chamber had a reasonable amount of grit coated to the internals.' It should be noted that the exposure device had just been received the day prior. "The weather was minus 10 degrees with a wind speed of 10 knots. The lock assembly was cleaned and reassembled as was the crank assembly. There was no exposure to the crew or the general public during this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-01-06
45608 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2010-01-05 15:20 | 2010-01-05 17:09 | 2010-01-14 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO A PROTECTED AREA Attempted introduction of contraband into a protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION PROVIDED BY JIM PETERSON TO JOE O'HARA AT 1509 ON 1/14/10 * * * Licensee retracted the event. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R3DO(Lipa) and 73.71 group via e-mail. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-01-05
45607 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-01 07:30 | 2010-01-05 14:53 | 2010-01-05 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-01-05
45606 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-12-27 | 2010-01-05 12:57 | 2010-01-05 | AGREEMENT STATE REPORT - LOST Mo-99 ISOTOPE GENERATOR "On January 5, 2010, at 0740 hours, the Agency [Texas Department of State Health Services] received a phone call from the United States Department of Transportation (USDOT) informing them that on December 27, 2009, 38 molly generators containing various activities of molybdenum (Mo) 99 were shipped to the Dallas/Forth Worth Airport. Some of the generators were to be delivered to various surrounding states and 24 were intended for delivery to licensees in the State of Texas. "The shipper was Lantheus and they are located in N. Billerica, Massachusetts. The shipper stated that the number of units shipped was verified at the airport prior to shipping. The number of generators arriving in Texas was not verified by the shipping company according to USDOT. A device containing four curies of Mo-99 for the National Central Pharmacy in Abilene, Texas was not found. "USDOT has contacted all companies who received generators from this shipment, and none of them indicated that they had received the generator that is missing. The consultant for the shipping company stated that during transit the devices were flown from Massachusetts to Cincinnati, Ohio, and then to Dallas/Fort Worth, where they were removed from the plane. A search of all transportation vehicles used to transport the devices was conducted, but the device was not located. "The consultant stated that the shipping company also contacted each company who received a device and confirmed that they had not received any additional material. The consultant stated that there may be some discrepancies in the shipping documents and that it could be a clerical error and not a missing source. The shipping company is currently conducting a document review. Additional information will be provided as it is obtained." Texas Incident #: I-8696 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-01-08
45605 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-04 09:30 | 2010-01-04 13:38 | 2010-01-04 | POSSESSION OF ALCOHOLIC BEVERAGE IN PROTECTED AREA "At approximately 0930 on January 4, 2010 a gift package was brought into the protected area that contained a bottle of an alcoholic beverage. The individual that brought the package into the protected area was unaware that a bottle of an alcoholic beverage was in the gift package. The gift package was delivered to the intended individual. As the individual was reviewing the contents of the package, the bottle of alcoholic beverage was identified as part of the package. Security was immediately contacted and took possession of the bottle. The bottle was still sealed with the original seal. The gift package was always attended while inside the protected area. A fitness for duty evaluation of the personnel involved was conducted with no concerns identified." The individual was a non-licensed licensee supervisor. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2010-01-04
45604 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-01-03 08:04 | 2010-01-03 11:52 | 2010-01-03 | MANUAL REACTOR TRIP DUE TO LOSS OF CIRCULATORS AFTER UPTAKE OF RIVER ICE "A manual trip of Salem Unit 2 was initiated due to a loss of 4 circulators due to an excessive uptake of river ice. Strong northwest winds, freezing temperatures and abnormally low tide levels contributed to the ice formation on the river. The operating crew entered EOP-TRIP-A, appropriately transitioned to EOP-TRIP-2 and stabilized the plant at no load conditions (MODE 3 Hot Stand-by). "All rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the Steam Dump system, with condenser vacuum maintained. All three AFW Pumps auto started due to low Steam Generator level due to closure of 21-23CN27, low pressure feed water heater inlet isolation valves. There were no other significant equipment challenges associated with the reactor trip. "Salem Unit-2 is currently in mode 3. The Reactor Coolant System temperature is 547 [degrees] F with pressure at 2235 psig [NOT and NOP]. All ECCS and ESF Systems are available and no ECCS systems actuated during the event. No personnel injuries occurred as a result of the trip. [The Unit 2 reactor trip recovery is uncomplicated.]." Unit 1 power was also reduced to 80%. Although the combination of strong northwest winds, freezing temperatures and an abnormally low tide contributed to the ice formation on the river, operators foresee no further complication due to the ice conditions. The licensee has notified the NRC Resident Inspector and will notify the States of Delaware and New Jersey. | 0 | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-01-03
45603 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2010-01-01 23:10 | 2010-01-02 04:12 | 2010-01-02 | DIESEL GENERATOR AUTO START DUE TO FAILED LINE ARRESTOR IN SWITCHYARD "This report is being made under 10CFR50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in Paragraph (b)(3)(iv)(B) of this section' due to an auto start of the 'A' Standby Diesel Generator. "The auto start of the 'A' Standby Diesel Generator occurred on a valid bus undervoltage condition caused by a momentary fault on the 161 kV Vinton line. Switchyard inspection revealed a failed 161 kV line arrestor [on] one of the phases of the Vinton line. The 'A' Standby Diesel Generator supply breaker was not required to close onto its respective essential bus as it remained powered from its normal power supply, 1X003 Start-up Transformer, during and after the event. Offsite power remained fully operable during and following the event. The 'A' Standby Diesel Generator has been returned to the standby/readiness condition. "As designed, the 'A' Emergency Service Water systems auto started when the 'A' Standby Diesel Generator started. The Emergency Service Water systems have been returned to the standby/readiness condition. "The 'B' Well Water Pump tripped as a result of the electrical transient. The 'A' Well Water pump and 'B' Emergency Service Water pump were manually started by operators in accordance with Abnormal Operating Procedure 408, Well Water System Abnormal Operation. "The in-service Reactor Water Cleanup pump tripped which removed RWCU from service. The RWCU system has been returned to service. "The in-service Spent Fuel Pool Cooling pump tripped as a result of the electrical transient. Spent Fuel Pool Cooling has been returned to service. Spent fuel pool temperature rose 0.7 [degrees] F while the pump was out of service. "All ECCS systems were available before the event and have remained available following the event." The licensee is not in any Technical Specification LCO's as a result of this event. The in-service Spent Fuel Pool Cooling pump was OOS for approximately 58 minutes. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-01-02
45602 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2009-12-30 | 2009-12-31 12:18 | 2009-12-31 | UNDERDOSE TO PATIENT The Richard L. Roudebush VA Medical Center holds VHA Permit Number 13-00694-03 under the VA's Master Material License (NRC License Number 03-23853-01VA). "For a patient treatment on December 30, 2009, involving Yttrium-90 microspheres, the medical center discovered (on same date) that the total activity delivered to the treatment site was less than 80% of the total activity documented in the written directive. "The medical event was discovered when a waste container, which contained used catheters, lines, gloves, tongs, tape, etc., from the treatment were assayed. The waste materials indicated a higher than expected residual activity equal to about 25 percent of the activity that was in the source vial prior to treatment. Examination of the waste materials revealed that nearly all of the residual activity was distributed somewhat uniformly along the length of the approximately 100 cm microcatheter tubing. "The current estimate is that about 47.03 millicuries were delivered to the patient, and 15.67 millicuries were in the wastes. The prescribed activity was 63.2 millicuries. Therefore, the patient was under-dosed by about 25.6%. Because this deviation exceeds 20%, a medical event is considered to have occurred per 10 CFR 35.3045(a)(1). "Although a lower-than-intended activity was administered, the permittee estimates that the absorbed dose to the target organ was around 109 gray and was within the therapeutic target range of 100 to 150 gray. Therefore, no adverse biological effects to the patient are expected." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient.test | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2010-01-06
45601 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-12-31 05:17 | 2009-12-31 05:17 | 2009-12-31 | TEMPORARILY SUSPEND CERTAIN PROCESS AREAS A press release is being issued by NFS [Nuclear Fuels Services]. NFS is implementing organizational, facility and management changes that will ensure an even more stringent level of safety controls and processes at the facility. During the implementation, NFS will temporarily stand down certain process areas. NFS developed these changes following consultation with the Nuclear Regulatory Commission (NRC), to ensure that the highest levels of safety commitment, culture and compliance are in place for licensed operational processes. NFS is making these specific changes following a recent NRC review. Suspended operations include production operations, the Commercial Development Line and the down blending facility. These facilities will be brought back on line pending a third-party review and NRC review of the safety improvement implementations. Other areas of the plant will continue to operate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2009-12-31
45600 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-12-30 22:10 | 2009-12-30 22:45 | 2009-12-30 | OSHA CONTACTED DUE TO ON-SITE FATALITY "A non-contaminated individual was transported by ambulance from the Catawba Nuclear Station parking lot to a local hospital due to a personal illness. The individual was pronounced dead at the hospital. Catawba Nuclear Station is notifying [Occupation Safety Health Administration] OSHA of an on-site fatality." Licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-30
45599 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-12-30 | 2009-12-30 19:02 | 2010-03-01 | AGREEMENT STATE - STUCK SHUTTER ON FIXED DENSITY METER The following was received via email: "A fixed gauge licensee operating a paper mill in Camas, Washington, reported that the shutter mechanism of an Ohmart Vega fixed gauge, Model Number SH-F1B-0, containing a 100 mCi sealed source of Cesium 137 failed to close during a routine six-month shutter check. "The Radiation Safety Officer reported the gauge is mounted on a vertical section of six-inch piping and is still functioning correctly as a density meter. The device is not part of any lockout or confined space entry permit and there is currently no safety hazard potential for exposure to radiation associated with the failure of the shutter mechanism. "The environment where the gauge is mounted is susceptible to messy process conditions which allows water and lime-mud to accumulate on the fixed gauge. This appears to have contributed to the failure of the shutter mechanism. The manufacturer's representative was called by the licensee and has scheduled a visit to the facility to make corrective repairs." Report #: WA090097 * * * UPDATE FROM BRANDIN KETTER TO HOWIE CROUCH VIA EMAIL ON 3/1/10 @ 1526 HRS. EST * * * "On February 25, 2010, service representatives from Ohmart Vega replaced the shutter mechanism with a new shutter closing this incident." Notified R4DO (Cain) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2010-01-04
45598 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-12-30 12:03 | 2009-12-30 14:55 | 2009-12-30 | UNUSUAL EVENT DUE TO EARTHQUAKE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "An Event Classification of Unusual Event (HU1.1) was declared at 12:03 MST for the PVNGS (Palo Verde Nuclear Generating Station) site because of an earthquake that originated in Baja Mexico location 32.467 N, 115.195 W at 10:48:57 local time. Per the USGS (United States Geologic Survey) website, the magnitude of the earthquake 5.8 on the Richter scale. Initial walk downs of plant equipment and review of plant parameters have found no unusual conditions or damage to plant equipment. There was no automatic initiation of the Reactor Protection System or Emergency Safety Function System and none were required. The units are all at 100 percent power and all offsite power supplies are available. "The earthquake didn't register on plant seismic monitoring equipment, but was felt by plant personnel." * * * UPDATE FROM BRIESE TO TEAL AT 1722 ON 12/30/2009 * * * "The Notification of Unusual event classification was terminated at 15:15 MST on 12/30/2009 after completion of walk downs of the protected area, ISFSI, cooling towers, switchyard, Station Blackout Generators and water reclamation with no equipment issues being found. " Notified R4DO (Farnholtz), NRR EO (Evans), IRD (McDermott), FEMA, DHS | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-12-30
45597 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2009-12-30 04:37 | 2009-12-30 08:24 | 2009-12-30 | AUTOMATIC REACTOR TRIP DUE TO TURBINE STOP VALVES CLOSING "At 0437 hours [the] Turbine Stop Valves closed causing an automatic Reactor Trip. Auxiliary Feedwater Pumps automatically started as expected during the transient and operated normally. All control rods inserted on the reactor trip. Reactor Coolant System temperature and pressure are stable at 547 degrees and 2235 psig. The cause of the Turbine Stop Valve closure is under investigation." The pressurizer relief and safety valves did not lift. Decay heat is being removed via the Auxiliary Feedwater Pumps and the Atmospheric Relief Valves. There is no primary to secondary leakage in the steam generators. Electrical lineup is normal, and the EDG's are available if required. The licensee has notified the State and the NRC Resident Inspector | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-12-30
45596 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2009-12-28 18:15 | 2009-12-29 19:36 | 2009-12-29 | AGREEMENT STATE REPORT- DAMAGE TO PORTABLE GAUGE The following was received via email: "At 6:15 PM, on 12/28/09, the Nevada Radiation Control Program (RCP) received a phone call from NHP [Nevada Highway Patrol] and was informed that a nuclear density gauge [model CPN MC3 Am-241/Be 50 mCi and Cs-137 10 mCi nominal] had fallen out of a truck in Las Vegas and that the gauge had been destroyed. "At 6:35 PM, NHP, Las Vegas, contacted [the Nevada RCP Senior RSO] and reported that a nuclear density gauge had fallen from a truck at I-15 and 215 and that his initial instrument reading was 415 micro R/hr at 10 feet. The instrument was destroyed; however the source tube was not ruptured. The NHP was also on the line with [RCP] who was arranging for Metro All Regional Multi-Agency Operations and Response (ARMOR) to respond with other instruments. [The RCP] coordinated from that point with subsequent calls to [the Nevada RCP Senior RSO] to discuss how to proceed. The subsequent instrument readings received from Metro ARMOR indicated that the surface of the device case was 600 mR/hr. "On the morning of 12/29/09, RCP learned that Instrotek was on the way to the licensee to conduct wipe tests and determine if the gauge could be shipped for repair. "RCP also took measurements on December 29, 2009 with a calibrated Victoreen 451 P. The measurements were 70 mR/hr at contact with the outside of the shipping container that held the gauge pieces. It was indicated that the licensee was to call the program [State] on 12/29/09 to report the incident. As of this writing the program is awaiting contact from the licensee. "The state has an inspector in the area, and will continue to keep the NRC informed of the status of our investigation." The RCP stated that both sources were recovered, intact, and leak tested satisfactory. Nevada Event #: NV-01-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-01-01
45595 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-11-19 | 2009-12-29 17:09 | 2009-12-29 | AGREEMENT STATE REPORT - BRAYCHYTHERAPY DOSE DIFFERED FROM THE PRESCRIBED DOSE BY MORE THAN 20% The following was received via facsimile: "During a prostrate brachytherapy procedure using a Mick applicator and I-125 sources, 41 of 41 sources were implanted into the patient's perineal soft tissue, inferior to the prostrate [resulting in:] 1. Dose was greater than 5 rem effective dose equivalent, and/or 50 rem to an organ or tissue and 2. the total dose delivered differs from the prescribed dose by 20% or more. "Explain the effect, if any, on the individual who received the administration: Possible perineal soft tissue fibrosis. The patient is currently without symptoms six weeks following the implant. "Additional notes: "Licensee's evaluation of why the event occurred: Visualization of the prostrate was difficult on ultrasound due to poor image quality, leading to needle placement inferior to the prostrate. "What actions, if any, have been taken or are planned to prevent recurrence: Discontinuation of the procedure if the locations of the needles are not known to relative certainty. "The patient and the referring physician were notified [of this event]. "No follow-up is required." NC Incident Report Number: 09-63 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2010-01-04
45594 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-12-29 15:00 | 2009-12-29 15:57 | 2009-12-30 | AGREEMENT STATE - LOST SOURCE The following is a summary of information received via fax: The licensee reported a lost 189 micro-Curie Cs-137 source at 1500 [EST] on 12/29/09. Also missing was the certificate for the source. Miami Inspection Office will investigate. The incident occurred at the Miami Diagnostic Interventional Center located in Miami Lakes, FL. * * * UPDATE FROM FURNACE TO TEAL AT 1631 ON 12/30/2009 * * * "[An] investigator determined that source became missing sometime between December 8th to the 23rd. [As a] corrective action [the] licensee will restrict who has possession of Hot Lab keys to, the owner, office manager, and nuclear medicine technologist. Incident referred to Materials and Licensing for any further investigation. This office will take no further action on this incident." FL Incident #: FL09-088 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-01-01
45593 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2009-12-28 15:15 | 2009-12-28 17:33 | 2009-12-28 | OFFSITE NOTIFICATION FOR ELEVATED TRITIUM LEVELS "On 12/23/09, station management was notified that a sample taken from [James A. Fitzpatrick] JAFs west storm drain was positive for tritium. The sample results were confirmed at 984 pCi/L. The sensitivity of the analysis is 800 pCi/L. The Offsite Dose Calculation Manual (ODCM) lower limit of detection (LLD) requirement for tritium is 3,000 pCi/L with a reporting level of 30,000 pCi/L. Comparing the confirmed activity level in the sample with the reporting criteria, there is little environmental impact, as the sample is more than an order of magnitude below the reporting criteria. "Although no regulatory limit was exceeded these results were evaluated against the NEI 07-07 guidance for voluntary informal communication of state/local authorities. Since the storm drains communicate with native soil and Lake Ontario, it has been determined that the voluntary informal communication criteria applies. That determination was made at 1515 [EST] on 12/28/09. "Since the state and local agencies will be notified of the slightly positive indication in the storm drain sample, reporting criterion 10 CFR 50.72(b)(2)(xi) was reviewed and based on the public sensitivity to tritium issues, it was determined that a notification to the NRC should be made. "The site has developed an action plan to address locating the source of the tritium [including] potential remediation actions, inclusion in the annual Radiological Environmental Monitoring Program (REMP) report, and evaluation for inclusion as an NRC IN 80-10 pathway. In the interim, both the reactor building perimeter sump and west storm drain have been placed on an increased sampling frequency. The storm drain will be sampled weekly and the reactor building perimeter sump will be sampled daily. "Background: On 11/03/09 station management was notified that a sample from the reactor building perimeter sump was positive for tritium at 1474 pCi/L. The reactor building perimeter sump was placed on increased monitoring frequency due to the positive indication. Since the sump only communicates with the environment, through the west storm drain, and there was no positive indication of tritium in the west storm drain or in the ground water monitoring wells, it was determined that no 'voluntary informal communication' criteria applied, at that time." The licensee has notified the NRC Resident Inspector. The licensee will notify the state, local, and other government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-28
45592 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-11-06 15:32 | 2009-12-28 12:35 | 2009-12-28 | INVALID START OF THE UNIT 2/3 EMERGENCY DIESEL GENERATOR "On November 6, 2009, at approximately 1532 CST, Dresden Unit 3 manually tripped the main turbine due to an Electro-Hydraulic [Control] Fluid leak. Following the turbine trip, electrical busses automatically realigned breakers which transferred power from the unit auxiliary transformer to the reserve auxiliary transformer. During this transfer, the Unit 2/3 Emergency Diesel Generator (EDG) automatically started. The power source transfer occurred as designed within 0.2 seconds. None of the electrical busses experienced an under-voltage condition. Therefore, the [Unit] 2/3 EDG start signal was invalid. However, the Unit 2/3 EDG started due to a 4 Kv bus breaker interlock. Both the main feed breaker and the reserve feed breaker were open concurrently for approximately 73 milliseconds, which resulted in the invalid Unit 2/3 EDG start signal. "Following the start, the Unit 2/3 EDG operated as expected and no abnormalities were observed. Since there was no under-voltage signal experienced, the EDG output breaker did not attempt to close onto the associated bus. "The breakers associated with the EDG interlock are scheduled to be inspected during the next refuel outage to verify proper EDG interlock interface. "Since this ESF actuation was caused by an invalid signal, it is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as specified by 10 CFR 50.73(a)(1), which allows a telephone notification in lieu of a written licensee event report within 60 days." The licensee notified the NRC Resident Inspector. | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-12-28
45591 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-12-25 15:40 | 2009-12-25 19:18 | 2009-12-25 | EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE "On December 25, 2009, at approximately 1540 hours EST, the plant computer system (ICS) experienced a lockup due to a loss of electrical power to the meteorological tower. This resulted in a loss of most Emergency Response Data System (ERDS) information points, the Safety Parameter Display System (SPDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP). The Computer Aided Dose Assessment Program remained available in manual data entry mode. "At 1758 hours, the ICS computer system operation was restored to normal. All SPDS and ERDS information points are now functioning properly. Power restoration activities to the meteorological tower are in progress. This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii) as a condition that results in a major loss of emergency offsite communications capability. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-25
45590 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-12-24 05:14 | 2009-12-24 09:08 | 2009-12-24 | OFFSITE NOTIFICATION RESULTING FROM AN INADVERTANT ACTIVATION OF A SIREN "Prairie Island Nuclear Plant was notified by Goodhue County Dispatch that a public alert notification siren inadvertently activated at 0430 hours. Local law enforcement officials deactivated the siren at 0500 hours. [Greater than] 70% of sirens remain functional in the 10 mile EPZ [Emergency Planning Zone]. The communications company has been contacted to investigate the cause of the false activation." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-24
45589 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-12-23 | 2009-12-23 18:57 | 2009-12-23 | AGREEMENT STATE - RADIOGRAPHY SOURCE FAILED TO RETRACT The following was received via email: "The 48 Ci Iridium-192 source in an INC IR-100 radiography camera, sn 6617, failed to retract in that the safety latch popped up prematurely, locking the source in the un-captured position outside of the radiography camera. The radiographer approached and surveyed the radiography camera, depressed the latch, returned to the cranks and returned the source to the safe position. Upon examination of both the radiography camera and the cranks, no damage or excessive dirt was detected that could explain this type of failure. The radiographer and assistant did not pick up any excessive radiation exposure as a result of this incident. Note: the operations manual for this instrument indicates that this type of failure could occur and instructs the user/radiographer in the steps to take to correct the problem. These steps, mentioned above, were taken by the radiographer." This event occurred at Shell Oil Refinery in Martinez, California. California report number 122309. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-12-28
45588 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-12-23 15:25 | 2009-12-23 17:18 | 2009-12-23 | MANUAL RPS ACTUATION DUE TO LOSS OF INSTRUMENT AIR "At 1525 EST, Vogtle Unit 2 was manually tripped from 100% power due to a loss of instrument air to the turbine building. "System operators were releasing a tagout and restoring one of two instrument air dryers that had been isolated for maintenance. Instrument air low pressure alarms were received in the control room and secondary side valves were responding to the loss of instrument air. Control room operators responded according to procedures. Main feed pump 'B' tripped on a loss of suction pressure and operators manually tripped the reactor. "The reactor was manually tripped in anticipation of a loss of feed water to the steam generators. All systems responded as required. AFW [Auxiliary Feed Water] actuated as required for loss of feed water. All control rods fully inserted on the reactor trip. Instrument air has been restored to the turbine building and steam dumps are controlling RCS temperatures. "Cause of the loss of instrument air is being investigated. "[The NRC] Senior Resident [Inspector] was notified." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-23
45587 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-12-23 06:56 | 2009-12-23 12:21 | 2009-12-23 | WINTER STORM POWER OUTAGES CAUSE ALERT SIREN INOPERABILITY "On December 23, 2009, at 0656 hours, 40% of the alert sirens in the Quad Cities Station Emergency Planning Zone were determined to be inoperable for greater than 60 minutes. This is considered a major loss of the Quad Cities offsite notification capability. The alert sirens were disabled due to power outages caused by a winter storm. Efforts are underway at the time of this notification to restore the sirens. "This report is being made due to the reduction in public notification capabilities in accordance with 10CFR50.72(b)(3)(xiii). As of 1100 hours, all but 6 EPZ sirens (12%) have been restored. "A follow-up notification will be provided when the sirens have been restored." * * * UPDATE FROM DEWEERTE TO TEAL AT 1707 ON 12/23/2009 * * * "Repairs to the emergency sirens were completed as of 1456 CST hours. All sirens are restored." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-23
45586 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2009-12-22 08:45 | 2009-12-22 16:30 | 2009-12-22 | LOSS OF WATER SEAL TO SECONDARY CONTAINMENT "On December 22, 2009, at 0845 hours, with the reactor at 100% core thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNPS) declared Secondary Containment inoperable due to the loss of a water seal on two 14 inch drain lines in the Torus Compartment designed to mitigate the consequences of a flood in the Reactor Auxiliary Bay. An initial assessment of the condition indicates that the cross-sectional area of pipes, as found, have the potential to exceed the analytical value of allowable Secondary Containment leakage pathway size documented in the design calculations. The Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.7.C.2.a, was immediately entered at 0845 until the condition was corrected. The TS LCO was subsequently exited at 0945 hours at which time Secondary Containment was declared operable. "As background, each Reactor Auxiliary Bay (2) is equipped with a sump containing two 14 inch drain lines that discharge into separate trough in the Torus Compartment in the event of a flooding condition. The trough is approximately 4 feet by 4 feet by 4 feet deep and is equipped with a high and low level alarm which annunciates in the Control Room. One of the functions of the alarm is to indicate a low level condition prior to the pipes losing their water seal which maintains Secondary Containment for those penetrations. When the water level in the trough dropped below the low level setpoint, the alarm failed to annunciate. This condition was discovered during an engineering walk down of the Torus Compartment. "Immediate actions taken were to refill the trough to the correct level, initiate repairs to the level switch, which was found to be defective, and to enhance the weekly tour requirement of the Torus Compartment performed by plant operations. "This notification has no impact on the health and safety of the public. "The NRC Resident Inspector is onsite and has been notified. "This is an 8 hour notification made in accordance with 50.72(b)(3)(v)(C)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2009-12-22
45585 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-11-21 21:13 | 2009-12-22 11:14 | 2009-12-22 | UNEXPECTED AUTOMATIC START OF THE 2-1 EMERGENCY DIESEL GENERATOR (EDG) "This notification is being made in accordance with 10 CFR 50.73(a)(i), which states, in part; that in case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv)(A), other than the actuation of the Reactor Protection System when the reactor is critical, the licensee may provide a telephone notification to the NRC within 60 days after discovery of the event instead of submitting a written Licensee Event Report. "On November 21, 2009, at 2113 PST, EDG 2-1 automatically started, but did not load, due to an attempted replacement of an indicating light that caused a control circuit electrical short and opening the power supply fuse. EDG 2-2 and EDG 2-3 were unaffected by this event. Plant operators entered TS 3.8.1, AC Sources - Operating, due to the loss of the Startup Feeder indication circuit. No actual condition requiring the start of EDG 2-1 existed. "The EDG 2-1 4kV Bus Start up Transfer Feeder Undervoltage Relay was placed in bypass (knife switch #10 for relay 27 HGU opened), the EDG was shutdown at 2147 PST and placed in standby operation at 2148 PST. This inadvertent start relay input is not a required safety function, but provides an anticipatory start of the EDG. The actuated relay input is not required for operability, thus the EDG was operable at 2148 PST. "Electrical Maintenance replaced the affected sensing relay circuit fuse (52HG14 "UA" fuses), tightened the indicating light socket for SUT 2 2 Potential C A Phase, and reset 27HGU (Startup Feeder UV for 4kV Bus G). On November 22, 2009, at 0729 PST, TS 3.8.1 was exited. "The consequences of this event were limited to the unplanned start of EDG 2-1. The EDG started and functioned in accordance with its design. Since no valid signal which required the EDG to start, and since the start occurred inadvertently as the result of a known maintenance action (resulting in a single component failure, a protective fuse opening), this event has been classified as an invalid actuation. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-12-22
45584 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-12-21 13:37 | 2009-12-21 20:17 | 2009-12-21 | HPCI DECLARED INOPERABLE "High Pressure Coolant Injection [HPCI] system was declared inoperable due to failure of the turbine governor valve to open with the Auxiliary Oil Pump [AOP] running. The AOP had been started to obtain oil samples for routine maintenance. The turbine was not expected to roll since there was no initiation signal, but the HPCI governor valve was expected to open to try to raise HPCI speed. Failure of the governor valve to open would prevent HPCI from achieving rated system flow and pressure. HPCI is also considered unavailable. All remaining ECCS systems and RCIC are operable. Cause of the condition is currently unknown. Troubleshooting activities are being planned. "HPCI is a single train system. This report is submitted in accordance with 10 CFR 50.72(b)(3)(v) as a condition that at time of discovery could prevent the fulfillment of the safety function of an SSC [Structure, System and Components] needed to mitigate the consequence of an accident. "The NRC Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-12-21
45583 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2009-12-19 22:53 | 2009-12-20 00:06 | 2009-12-20 | AUTOMATIC REACTOR TRIP CAUSED BY A TURBINE/GENERATOR ELECTRICAL FAULT An automatic reactor trip occurred due to a turbine trip caused by a generator electrical fault trip. The cause of the electrical fault is under investigation. All rods fully inserted into the reactor. The auxiliary feedwater pump started and is maintaining steam generator level. The reactor is NOP and NOT. The post trip electrical line-up is being back-fed from off-site power through the RSST transformer. All other post trip actions are standard and all systems are operating as expected. There was no affect on Unit-2. The licensee will contact the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-20
45582 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-11-26 | 2009-12-18 13:47 | 2009-12-18 | AGREEMENT STATE - LOST LEVEL INDICATOR The following was received via email: "General licensee (GL) reported to BRP (Bureau of Radiation Protection) on 12/18/09 that a generally licensed device was unaccounted for. The device has been identified as an Industrial Dynamics FilTech FT-50 [fixed gauge] level indicator, serial number 113216, containing 100 mCi of Am-241. "The licensee last reported that the device was in their possession with the annual GL registration to BRP on 10/11/02. The device was not listed on the next GL registration submitted by the licensee on 11/26/03. During an internal audit by the licensee it was determined that a report of disposition of the device had not been submitted to BRP. The device had been installed in a process line which was decommissioned and dismantled in June 2003. As the licensee investigated the matter they determined that they could not account for the current location of the device. The manufacturer had no record of receipt of the device and the licensee could not locate the device anywhere within their facility. Additional investigation and information is being requested by BRP. " Ohio Report #: OH090012 Source Model #: 06110 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-12-23
45581 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-12-15 | 2009-12-18 11:36 | 2010-02-08 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA The following report was received via email: "The department received a notification from a radiography company [on 12/16/09] located in Kent, Washington, about an event [that occurred] while performing radiographic operations in a fabrication shop in Sedro Wooley, Washington. A 2 inch pipe fell onto the source guide tube and the radiography crew was unable to retract their source past the damage. The crew called the company's Radiation Safety Officer who sent an assistant to the site with lead blankets. The assistant was able to normally retract the source through the damaged area and into the shielded safe storage position of the radiographic exposure device. The dose to the assistant RSO was reported as 480 mRem. No other individuals were reported to have received an elevated dose. A full report from the company's RSO will be made after they perform a reenactment of the incident." WA Incident Number: WA-09-093 Source material: 80 Ci, Ir-192 * * * UPDATE FROM BRANDIN KETTER TO VINCE KLCO ON 2/8/10 AT 1857 VIA EMAIL* * * "A full report was received from the company on 12/18/09. TLD's worn by the three individuals involved in the incident were processed the next day by Landauer. Two of these individuals were the radiography crew who were working with the equipment when the source failed to retract. Their doses were reported as 79 mRem and 261 mRem. It was also reported that most of this exposure could probably be attributed to the previous 14 and 1/2 days of radiography work. The third person receiving a dose from this incident was the assistant RSO. This person received a dose of 22 mRem. Three other people in the company who responded to the incident site were reported to have received no dose. The damaged equipment was tagged and taken out of service." Notified R4DO (Jones) and FSME (Shaffer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-12-23
45580 | 0 | FMC CORPORATION |  |  |  |  | 2009-12-17 08:30 | 2009-12-17 16:12 | 2009-12-17 | UNABLE TO SHUTTER OR SHIELD FIXED NUCLEAR DENSITY DEVICE DURING MAINTENANCE ACTIVITIES "At approximately 1:00 PM MST today (12/17/09), . . .FMC personnel notified Mr. Richard Leonardi at the NRC Region 4 Office of the following incident. Mr. Leonardi requested that we report the incident to the Operations Center . . .. "Incident: At approximately 8:30 AM MST, on 12/17/09, the FMC radiation worker was approaching the location of a Berthold fixed source device, for the purpose of performing some maintenance functions. The Berthold device is mounted approximately 12 ft. above the floor, and meters flow of a sodium-based slurry @ 98 degree Centigrade through an 8 [inch] diameter Stainless Steel pipe. The radiation worker approached the device to see if they could close the shutter and upon nearing the device (via ladder), the meter pegged at 200 millirems. The radiation worker could not get the reading to change by moving the shutter actuator, and retreated from the device within [approximately] 2 minutes. "The RSO and assistant then flagged the area to establish a perimeter at which readings of 2 millirems or less are detected. "Pertinent Facts: This Device, Berthold Model LB-7440, S/N 226-1-91, containing a 150 millicurie source, Cesium 137, was subjected to routine shutter test in September 2009, per standard license protocol. The device passed that shutter test without issue. "This same device was subjected to routine 'leak test' per standard license protocol in June of 2009, without issue. "The Manufacturer of the device, Berthold, has been notified . . . , and a qualified Berthold technician has been dispatched via automobile from Tennessee, with a replacement shield, to address and contain the device, such that the unit is rendered safe for appropriate repair/replacement. "We have committed to update Mr. Leonardi of Region 4, as soon as the Berthold technician has inspected the unit. We have also understand that FMC has an obligation to tender a written report of this incident and its resolution to Mr. James Thompson of the Region 4 NRC Office. "FMC's RSO and Radiation Worker verified the readings, using two other metering devices." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-12-17
45579 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2009-12-15 | 2009-12-17 10:59 | 2009-12-17 | AGREEMENT STATE REPORT - POSSIBLE MISADMINISTRATION OF RADIOACTIVE MEDICAL TREATMENT The following report was received via facsimile: "[Tennessee Division of Radiological Health] TN DRH was notified on 12/15/09, by the medical physicist at Cookeville Regional Medical Center, of a possible therapeutic misadministration that occurred the morning of 12/15. A patient was being treated with three sealed sources of cesium-137 (total activity of 70 mg Ra-equivalent) contained in a vaginal applicator. The patient was elderly and heavily sedated. The applicator was inserted and after twenty minutes of treatment, the nurse came into the room to check on the patient and noticed the applicator outside the treatment area. The applicator was removed and placed in a lead pig. The patient may have received a maximum dose of 76 Rem to the thigh area. A written report will be submitted by the licensee." Tennessee Report Number: TN-09-155 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2009-12-23
45578 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-12-17 | 2009-12-17 09:13 | 2010-06-02 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received via facsimile: "[A] technician contacted this office at approximately 0810 [EST] to report that a Troxler gauge was stolen. The gauge was stored in the truck bed inside the case. The case with locked gauge inside was chained to the truck. The office compound has a locked gate and fence. The gate was found to be open upon his arrival, the supervisor was there but was not aware of the missing gauge until informed by [the technician]. The truck that had the gauge was parked in the back parking lot. [The] Miami office will investigate." Florida Incident Number: FL09-086. Troxler Model Number: 3411-B Serial Number: 7648 * * * UPDATE FROM STEVE FURNACE TO HOWIE CROUCH @ 1419 EDT ON 6/2/10 * * * The missing Troxler gauge has been recovered and returned to the owner. The owner is conducting a leak test and will be sending the gauge to the vendor for an operational check. Notified R1DO (Dentel), FSME EO (McIntosh) and ILTAB (English) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-12-22
45577 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-12-16 14:15 | 2009-12-16 17:30 | 2009-12-16 | MANUAL REACTOR TRIP FOLLOWING A FAILURE OF THE STEAM DUMP SYSTEM "VC Summer Nuclear Station (VCSNS) was performing a preplanned turbine shutdown in order to perform maintenance on a faulty turbine control valve. After the manual turbine trip, the steam dump system failed to operate and the crew manually tripped the reactor. The cause of the failure of the steam dump system is unknown, and is currently being investigated. Both motor driven Emergency Feedwater pumps were manually started at 40% Steam Generator Level. Preliminary review indicates all other primary and secondary systems responded as required. The plant is in mode 3 at normal RCS [Reactor Coolant System] pressure and temperature. Decay heat is being removed by dumping steam via the secondary [steam generator] power operated relief valves. The station will remain in mode 3 until repairs are complete. Estimated restart date has not been determined." All rods fully inserted. There is no known primary to secondary leakage. Off site power supply configuration is normal. The turbine trip was performed at 45% power due to a stuck open turbine control valve. The licensee has notified the NRC Resident Inspector and will notify state and local contacts. | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-16
45576 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-12-16 10:39 | 2009-12-16 17:30 | 2009-12-17 | FITNESS FOR DUTY - LICENSED OPERATOR A licensed operator supervisor had a confirmed positive for alcohol during a "for cause" test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ELKINTON TO ABRAMOVITZ AT 1637 ON 12/17/2009 * * * The licensed operator was not a supervisor. Notified the R4DO (Whitten) via e-mail. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2009-12-16
45575 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-12-16 06:11 | 2009-12-16 17:30 | 2009-12-16 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR A non-licensed supervisor had a confirmed positive for alcohol during a "for cause" fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2009-12-16
45574 | 0 | HYDROAIRE |  |  |  |  | 2009-09-29 09:02 | 2009-12-16 17:11 | 2010-02-22 | PART 21 INVOLVING A PUMP SHAFT COUPLING FAILURE A service water pump failed during operation on 9/29/2009. Upon disassembly it was detected that a shaft coupling installed on a repaired service water pump failed while in service. The failed coupling was replaced with a new coupling of a different heat code. According to the manufacturer, the threaded coupling design was only supplied for Palisades. * * * UPDATE FROM SESHA GIRI TO PETE SNYDER AT 1529 ON 2/22/10 * * * HydroAire conducted a root cause analysis on the issue. They and their heat treat vendor, BodyCote, reviewed all of their safety related work records for the past three years and monitored heat treating of recent orders. "Records showed that this anomaly occurred only on one piece and it is a random isolated incident." The vendor believes that corrective actions that they and BodyCote have taken "should remove concerns in the future heat treatments and past review of records confirms adequacy of the heat treat at least for the past three years." Notified R3DO (Stone) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2009-12-16
45573 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-12-16 | 2009-12-16 10:45 | 2009-12-22 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received via e-mail: "On December 16, 2009, at 0729 hours, the licensee notified the [Texas] agency that sometime during the previous night, a company truck containing a Humboldt model 5001 EZ moisture density gauge serial # 3566 was stolen from an employee's home. The gauge contains a 10 millicurie Cesium (Cs) -137 source and a 40 millicurie Americium-241 /Beryllium (Am/Be) source. Local law enforcement was notified and a report filed. The employee is on his way to the company's office to file a complete report. The [Texas] agency has notified the Texas Association of Pawnbrokers of the theft. The company is licensed in the State of Illinois (IL-01828-01) and operating in Texas under reciprocity. It is unknown at this time how the gauge was stored in the vehicle or the address where the vehicle was located when it was stolen. This [Texas] agency will supply additional information as it is obtained." * * * UPDATE FROM A. TUCKER TO P. SNYDER AT 0926 ON 12/22/09 * * * The following report was received via e-mail: "On December 22, 2009, at 0809 hours, the license notified the agency that on the evening of December 21, 2009, the stolen truck was located in an impound yard. The gauge was still on the truck. The gauge was inspected and was undamaged. The gauge has been returned to storage. No additional information is available at this time. The licensee stated that a written report will be provided within the next week." Notified R4DO (Walker), FSME (Villamar), and ILTAB (e-mail). The Texas agency notified the State of Illinois. Texas Incident Number I-8693. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-12-21
45572 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-12-15 22:07 | 2009-12-16 00:01 | 2009-12-16 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-12-16
45571 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2009-12-15 14:30 | 2009-12-15 18:37 | 2010-01-21 | HELB CONFIGURATION CALCULATIONS NOT CONSISTENT WITH PREVIOUS HELB ANALYSIS "During a review of a High-Energy Line Break (HELB) calculation, valve FBV0146 on a 3" Auxiliary Steam line, FB-093-HBD-3", was found to be kept normally open. This is not consistent with HELB analysis, which assumes flow in line FB-093-HBD-3" is restricted by an orifice plate or isolated by FBV0146. This HELB analysis classified FB-093-HBD-3" as a moderate-energy line downstream of FBV0146 as a result of line isolation. "No orifice plate was installed, and line FB-093-HBD-3" downstream of the FBV0146 is considered a high-energy line if FBV0146 is open. A room containing line FB-093-HBD-3" downstream from FBV0146 includes several components, the most critical of which are two RCS [Reactor Coolant System] pressure transmitters in one train which are used to provide indications during post-accident conditions. This configuration is therefore outside of current HELB analysis and potentially represents a condition that significantly degrades plant safety. "Valve FBV0146 was closed at 1522. The NRC resident inspectors have been notified." * * * RETRACTION FROM KEITH CRIBLEZ TO VINCE KLCO ON 1/21/2010 AT 1739 * * * "On 12/15/2009, EN #45571 provided notification that valve FBV0146 on Auxiliary Steam line FB-093-HBD-3 was found to be kept normally open. This configuration was not consistent with High Energy Line Break (HELB) analysis which assumes flow beyond this valve to be restricted or isolated. "An engineering evaluation was subsequently performed for the rooms containing this line downstream of FBV0146. This evaluation has determined that all safety-related components in the affected rooms would be able to perform their safety functions in the event of a line break. Pipe whip, jet impingement, compartment over pressurization, flooding, and internal missiles resulting from a postulated line break would not prevent any safety-related equipment from performing its design function. "As supported by this evaluation, this condition does not meet the criteria for an unanalyzed condition that significantly degrades plant safety as stated in 10CFR 50.72(b)(3)(ii)(B). Therefore, the notification made on 12/15/2009 is hereby retracted. "The [NRC] Resident Inspectors have been notified." Notified the R4DO (Werner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-12-15
45570 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-12-14 19:00 | 2009-12-15 16:45 | 2009-12-16 | AGREEMENT STATE REPORT - IRRADIATOR SAFETY INTERLOCKS BYPASSED While engaged in production, the irradiator source was brought down due to an electrical fault. To verify the source was in the shielded position, an operator was sent to the roof and verified that there was no slack in the cables and the position of the cables indicated the source as in the shielded position. The interlocks were bypassed and an operator entered the cell. A damaged wire was discovered and repaired. Operators did not receive any radiation dose from this event. Previously, a flex conduit was discovered with damaged insulation that had caused a short (Ref: EN # 45486). * * * UPDATE ON 12/16/09 AT 1724 FROM TRUDY HILL TO MARK ABRAMOVITZ * * * The Nebraska item number for this event is NE090018. Notified the R4DO (Whitten). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | PAR |  |  |  |  | 0 | 2009-12-15
45569 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-12-15 07:55 | 2009-12-15 12:39 | 2009-12-15 | FITNESS FOR DUTY - SUPERVISOR TESTED POSITIVE FOR ALCOHOL An employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the site has been denied. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2009-12-18
45568 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-12-15 | 2009-12-15 10:03 | 2009-12-15 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following report was received via facsimile: "Soil moisture density gauge stolen. Storage facility at jobsite broken in to. Owner has possession of keys. Owner will submit a reward for $500. Incident referred to Miami Inspection Office for investigation. No further action will be taken on this incident." Gauge is a Troxler model 3440, serial number 35908, containing 40mCi of Am-241/Be and 8mCi of Cs-137. Miami Police Department Case #PD091215549153. Florida Incident Number FL 09-084. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-12-18
45567 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2009-12-14 12:00 | 2009-12-14 17:20 | 2009-12-14 | UNANALYZED CONDITION RELATED TO CERTAIN FIRE CONDITIONS "During review of the safe shutdown strategies for NFPA 805 in Fire Area 32, it was identified that fire induced damage to cable 1C-333 could cause a spurious lockout of 1RY transformer. The Appendix R Safe Shutdown Compliance assessment for Fire Area 32 credited the 1RY transformer source to safeguards 4kv bus 16 for safe shutdown. Cable 1C-333 was not previously identified as a required cable for the 1RY source in the Appendix R circuit analysis. "It was determined that D2 Emergency Diesel Generator could be credited as the safe shutdown power source to safeguards 4kv bus 16. Cabling required to support D2 Emergency Diesel Generator passed through Fire Area 32 but should be protected with a thermal shield as approved by the 5/4/1983 NRC Fire Protection Safety Evaluation Report. While inspecting these thermally shielded cables, it was identified that they are not wrapped after leaving the cable tray and prior to entering the bus room located above. "A fire watch was established in Fire Area 32 as a compensatory measure. Actions to ensure a power source remains available to achieve safe shutdown have been initiated. "The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B). An hourly fire watch has already been in place for Fire Area 32 as a compensatory measure for other issues identified in this fire area." The licensee notified the NRC Resident Inspector of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-12-14
45566 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2009-12-09 | 2009-12-14 01:40 | 2009-12-14 | AGREEMENT STATE REPORT - Cs-137 BRACHYTHERAPY SOURCE LEAKING The following information was communicated to the NRC via a telephone notification on December 14, 2009: On Wednesday, December 9, 2009, Bionomics personnel were at McLeod Regional Medical Center in Florence, SC to package several old sources for disposal. These packages remained at McLeod until the following day when Bionomics personnel picked them up for transport to the Bionomics facility in Oak Ridge, TN. On Friday, December 11, 2009, a Bionomics worker reported that he had radioactive contamination on his clothing. On Sunday, December 13, 2009 it was ascertained that this radioactive contamination had come from the sources picked up at McLeod. A brachytherapy source containing 38 mCi of Cs-137 was found to be leaking. Bionomics contacted an HP consultant from the University of SC to have him perform radiation surveys at the McLeod facility. Radiation surveys found contamination in treatment areas, supply rooms, offices, and hallways. Highest contact readings were localized and were approximately 100 mR/hr. At this time it is believed that no radioactive contamination had been tracked outside of the McLeod facility. The McLeod Radiation Safety Officer has surveyed all staff personnel - except for two individuals - that had been in the contaminated areas. No radioactive contamination was found on any of these individuals. The other two individuals will be surveyed today, Monday, December 14, 2009. Bionomics personnel are presently on-site at the McLeod Medical Center performing decontamination. The Medical Center has closed the area to personnel and patients until decontamination is completed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2009-12-16
45565 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-12-12 18:45 | 2009-12-12 20:44 | 2009-12-12 | UNUSUAL EVENT DECLARED DUE TO A FIRE IN THE CCW HEAT EXCHANGER The licensee declared an Unusual Event at 1845 CST due to a fire greater than 15 minutes in the CCW heat exchanger room. The fire suppression system actuated as designed and the site fire brigade responded . There were no injuries or equipment damage. The fire is out and the licensee is monitoring the area. The licensee reduced power per their plant response procedures. The plant is stable and remains in Mode 1. The licensee has notified the State and local authorities and the NRC Resident Inspector. * * * UPDATE FROM BRANNON PAYNE TO JOHN KNOKE AT 2243 EST ON 12/12/09 * * * The licensee exited the Unusual Event at 2036 CST, based on the fact that no equipment was damaged. The fire was believed to be from some hot work in the area igniting combustible material. The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Nease), NRR EO (McGinty) email only, DHS (Kettles), FEMA (Casto). | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-12-12
45564 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-12-12 01:26 | 2009-12-12 04:48 | 2009-12-12 | UNUSUAL EVENT DECLARED DUE TO BOTH EMERGENCY DIESEL GENERATORS BEING INOPERABLE A declaration of Unusual Event per EAL D.1-1 was made at 0126 PST on 12/12/09 due to both EDGs being inoperable. This condition places the Unit in a required Technical Specification Shutdown condition and the Unit is proceeding to shutdown. Train "B" EDG was declared inoperable at 0025 PST on 12/11/09 due to annunciator issues associated with the EDG. The cause of the annunciator issues has still not been identified. This placed the licensee into the Action Statement for LCO 3.8.1 that required verification of operability of the Train "A" EDG within 24 hours. During the operability test of the Train "A" EDG, the diesel failed to reach voltage and frequency (the EDG tripped on startup) and it was also declared inoperable. As a result, the licensee entered Action F of LCO 3.8.1 and is required to be in Mode 3 within 6 hours and Mode 5 within 36 hours. The licensee declared the UE at 0126 and commenced power reduction. Mode 3 must be reached by 0625 PST on 12/12/09 and Mode 5 must be reached by 1225 on 12/13/09. Besides the EDGs, all other safety related systems are operable. The licensee has notified State and local authorities and the NRC Resident Inspector. * * * UPDATE FROM GEOFF COOK TO DONALD NORWOOD AT 0918 EST ON 12/12/2009 * * * "On December 12, 2009, at about 0025 PST, SONGS Unit 3 Emergency Diesel Generator (EDG) 3G002 was determined to be inoperable. EDG 3G003 had been declared inoperable prior to this, resulting in both Unit 3 EDGs being inoperable. "At about 0025 on December 11, 2009, EDG 3G003 (Train 'B') was declared inoperable as a result of work being done on an annunciator power supply. SONGS Technical Specifications (TS), section 3.8.1.B, requires that the associated EDG, 3G002 (Train 'A') be tested within 24 hours to ensure that the EDG was also not inoperable due to a common cause. On December 12, 2009, at about 0025, EDG 3G002 was declared inoperable when it did not achieve required voltage and frequency during an attempted start. "SCE is reporting this occurrence as a loss of safety function in accordance with 10 CFR 50.72(b)(3)(v). "The loss of both EDGs on Unit 3, per TS 3.8.1.E, requires restoration of one EDG within 2 hours. This action was not met, and as a result TS 3.8.1.F required the unit to be shutdown to Mode 3 within 6 hours. This shutdown action began at 0126 PST. Also, pursuant to the SONGS Emergency Plan, the shutdown of Unit 3 under TS 3.8.1.F required declaration of an Unusual Event. Both the TS required shutdown action and the declaration of the Unusual Event were reported to the NRC pursuant to 10CFR50.72 in an earlier notification (same NRC Operations Log #45564). "SCE is taking actions to restore one of the EDGs to operability. At the time of this occurrence, Unit 2 was in a Steam Generator Replacement Outage, and Unit 3 was at approximately 100% power proceeding to a Mode 3 shutdown. "The NRC Resident Inspector has been notified of this occurrence and will be provided with a copy of this report." Notified R4DO (Spitzberg). * * * UPDATE FROM DOUG KNUDSON TO BILL HUFFMAN AT 1021 EST ON 12/12/2009 * * * The licensee exited their Unusual Event [and TS required shutdown] at 0645 PST based on restoration of operability of the "B" Train EDG. The "B" Train EDG annunciator issue was repaired and the EDG started and load tested per Technical Specification requirements. The EDG was declared operable at 0511 PST. The licensee is currently holding at 40% and planning to return to full power. Investigation into the starting problem of the "A" Train EDG is still ongoing. The licensee has notified the NRC Resident Inspector, State and local authorities. R4DO(Spitzberg), NRR(McGinty), and IRD MOC (Grant) notified. Also notified DHS (Inzer) and FEMA (Via). | 0 | 0 | 90 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD |  | IMode3: Power Operation; FMode3: Power Operation | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) |  | 0 | 2009-12-12
45563 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-12-11 | 2009-12-11 18:40 | 2010-02-23 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "Medi-Physics [PA license PA-0515] prepared a 30 ml kit of Myoview at approximately 2:30 a.m. on December 11, 2009. The radiochemical purity was determined to be 91%. They consider 90% on the center as passing. "On December 11, 2009, Grand View Hospital reported a problem with a nuclear medicine scan. Medi-Physics confirmed with BRP [Pennsylvania Bureau of Radiation Protection] that they dispensed 50 doses from the vial of Myoview in question. They believed 13 of these doses were administered to patients in PA and NJ. They thought the doses that were administered were resting doses of 8 to 10 mCi each. They assured BRP that they have a system in place to track their doses and contacted all the recipients once they were notified of the problem. "Initially, Grand View, one of the hospitals that received a Myoview dose, called Medi-Physics to advise them they saw thyroid and no cardiac uptake in a patient they injected with Myoview. This suggests free 99mTC04. Therefore, at approximately 8:30 a.m., they repeated [the quality check] on the Myoview left in the vial and determined the tag was less than 1%. Medi-Physics is still investigating the problem and will send the vial to the United Kingdom for chemical analysis once it is no longer radioactive. BRP feels this is an [abnormal occurrence] because there was (fundamentally) the wrong radiopharmaceutical given to a patient. "BRP has been in contact with all parties, will continue to investigate and enter in NMED." PA Report ID No.: PA090035 * * * RETRACTION FROM DAVID ALLARD TO DAN LIVERMORE AT 1601 ON 02/23/2010 * * * The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "Retraction of A.O. [abnormal occurrence]. Licensee calculations note patient dose below reporting / A.O. criteria. There will be no external NMED report." Notified R1DO (Schmidt) and FSME EO (Chang) A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-12-17
45562 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2009-12-11 | 2009-12-11 14:46 | 2009-12-12 | SECURITY SUSPENDED SAFEGUARDS REQUIREMENTS DUE TO SUDDEN SEVERE WEATHER Security suspended safeguards requirements due to sudden severe weather. Compensatory actions were taken. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JEFF LAMB TO DONALD NORWOOD AT 0525 EST ON 12/12/2009 * * * Security Operations returned to normal at 0510 EST. The licensee will notify the NRC Resident Inspector. Notified R1DO (Holody). Notified 73.71 Group via E-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 1 | 2009-12-11
45561 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-11-03 | 2009-12-10 21:29 | 2009-12-10 | INSTRUMENT LINE DETERMINED TO HAVE INADEQUATE STRUCTURAL SUPPORT "At 1700 on 12/10/09, an operability evaluation determined that an instrument line within the primary containment did not have adequate structural support during the previous operating cycle. The evaluation determined that the instrument line would have failed during a Safe Shutdown Earthquake (SSE). This would have resulted in reactor coolant leakage within the primary containment that could not be isolated. "The condition was identified and repaired during the recent refueling outage and full qualification and operability was restored prior to return to service." The condition was discovered on November 3, 2009 during the Unit 2 refueling outage. The operability determination was completed on December 10, 2009. It is unknown at this time if the condition exists in Unit 3 due to inaccessibility of the drywell during power operations. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-12-10
45560 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-12-10 13:00 | 2009-12-10 16:37 | 2009-12-10 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY "A mechanical maintenance employee died this afternoon from an apparent heart attack. The individual was not actively working at the time and lost consciousness in a shop area. The individual was treated by onsite EMT's who administered CPR and AED (automatic external defibrillator). The death was not the result of any industrial safety issue and did not occur in a contaminated area. He was transported via ambulance to Salem Memorial hospital where he was pronounced dead." The licensee notified the NRC Resident Inspector and local authorities in Lower Alloway Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-10
45559 | 0 | BELLEFONTE | 1 | 2 |  | [1] B&W-R-LP (205),[2] B&W-R-LP (205) | 2009-12-10 | 2009-12-10 16:23 | 2009-12-10 | CONTAINMENT VERTICAL TENDON FAILED "Inspection of failed Unit 1 Reactor Building Containment Vertical Tendon V9 coupling indicates a potential for an unknown common mode failure mechanism for BLN Containment vertical tendon rock anchor couplings. Unit 1 Reactor Building Containment Vertical Tendon V9 experienced a failure of the rock anchor/tendon anchor coupling on August 17, 2009 at approximately 1400 CDT. The time of failure was identified based on a loud noise bang reported by several individuals. Initial investigation failed to reveal the source of the noise. The failed tendon was discovered on August 24, 2009 during a tour of U1 Tendon Gallery, elevation 607. Unsafe conditions previously precluded an inspection of the failed coupling for proper installation or component specific damage. The failed tendon coupling was inspected on 11/23/2009 and showed no signs of component specific damage or improper installation creating the potential for an unknown common mode failure. "Safety significance: Until the mechanism of failure is identified the extent of condition will not be known. If multiple containment tendons are found to be losing the capability to carry tendon design force and this condition was left uncorrected, this could jeopardize the ability of the containment structure to perform its design function. "Causes of deficiency: The cause of this deficiency is unknown at this time. Further analysis is in progress and when completed, an update to this report will be provided. "Interim progress: Grease from the lower anchor head can has been analyzed for moisture content. Results were within vendor specifications. Additional samples have been sent for further analysis as described in Regulatory Guide 1.25 'In-service Inspection of Ungrouted Tendon in Prestressed Concrete Containments.' "After successful safe securing of the tendon load, the failed coupling was visually inspected. The visual inspection of the failed coupling did not indicate a component-specific failure mechanism or indication of visually apparent common mode failure mechanism. Based on this inspection visual inspection of additional tendon coupling tendon couplers is not warranted at this time. The coupling has been removed from both the tendon anchorhead and the rock anchor tendon anchorhead and sent to the TVA Central Lab for metallurgical analysis. "Records are being reviewed to identify previous non-conformance reports and certificates of compliances for the coupler. An extent of condition and extent of cause investigation will apply to vertical tendons are similar in design, these tendons do not utilize an anchorhead coupler in the design. However, these tendons will be considered in the analysis. "Future updates: TVA plans to provide an update to this report by March 31, 2010 following the completion of the metallurgical analysis." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 2 | AL | POW |  | 50.55(e) |  |  |  | 0 | 2009-12-10
45558 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-12-10 10:35 | 2009-12-10 12:48 | 2009-12-10 | BEARING COOLING WATER DISCHARGED INTO LAKE "On December 9, 2009, at 1423 hours, Unit 2 tripped offline due to the loss of 'C' Reserve Station Service Transformer. This resulted in a loss of power to one of the bearing cooling system level control valves (LCV). The affected LCV failed open, which caused the bearing cooling tower basin to overflow and release bearing cooling water to Lake Anna. By approximately 1530 hours, plant personnel had manually isolated the bearing cooling water system and the flow to the lake stopped shortly afterwards. Based on the duration of the event (approximately 70 minutes) and the maximum discharge flow rate of a bearing cooling water make-up pump (850 gpm), no more than 59,500 gal. of water were discharged to the lake. Based on visual observation of the actual flow going to the lake, it was estimated that approximately 35,000 gal. were discharged. The bearing cooling water was sampled on 12/09/09 by the Chemistry Department as part of their routine chemistry surveillance. All chemical parameters analyzed were within VPDES (Virginia Pollutant Discharge Elimination System) permit limits. There was no violation of permit parameters from this discharge and no adverse impact to the environment was observed. Bearing cooling system chemistry is maintained to meet VPDES discharge limits. "At 1035 hours on December 10, 2009, a 24-hour notification of the unusual discharge was made to the Virginia Department of Environmental Quality in accordance with the North Anna VPDES permit. "This issue is being reported per 10CFR50.72(b)(2)(xi) as an event where notification of other government agencies has been made. "The NRC resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-10
45557 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-12-09 23:10 | 2009-12-10 01:38 | 2009-12-10 | MANUAL SCRAM FOLLOWING HIGH TURBINE VIBRATION "At 2310 EST, Vogtle Unit 1 was manually tripped from 24% reactor power while the main turbine was rolling at 1800 rpm, preparing for synchronization to the grid. "As Vogtle 1 was preparing to bring the Unit 1 generator on line following a forced outage, high vibration levels were experienced on the HP turbine bearings while the Turbine was at rated speed and synchronization preparations were in progress. The Turbine was manually tripped in accordance with plant procedures. Vibrations continued to increase as the Turbine began to coast down, warranting that vacuum be broken in accordance with procedures. "The reactor was manually tripped in anticipation of trip of the main feedwater pump (due to loss of condenser vacuum) and condenser vacuum was broken to slow the turbine. When condenser vacuum was broken, the in-service Main Feedwater Pump auto tripped as expected, causing an automatic actuation of the Motor Driven Auxiliary Feedwater system. "The cause of high vibrations on the Turbine is being investigated. "All systems responded as expected on the trip." All control rods fully inserted into the core following the reactor trip. Atmospheric relief valves are being used to remove decay heat. There is no known primary to secondary leakage. The plant is in a normal post-trip electrical line-up. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-10
45556 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-12-09 14:23 | 2009-12-09 17:15 | 2009-12-09 | AUTOMATIC REACTOR TRIP ON UNIT 2 AND EDG START ON BOTH UNITS DUE TO INADVERTENT LOSS OF "C" RESERVE STATION SERVICE TRANSFORMER "At 1423 hours on 12/9/2009, electrical supply breaker L102 was inadvertently opened which caused electrical Bus 3 and the 'C' Reserve Station Service Transformer to de-energize. This caused the loss of 'F' Transfer Bus which resulted in a loss of power to the 1H and 2J Emergency Busses and an automatic start of the 1H and the 2J Emergency Diesel Generators. Both emergency diesel generators started and re-energized their associated emergency bus as designed. "The Unit 2 'G' Bus, which supplies power to the Unit 2 Circulating Water Pumps, did not automatically transfer to the 'B' Reserve Station Service Transformer in a sufficiently short time to prevent the loss of the Unit 2 Circulating Water pumps. The loss of the Unit 2 Circulating Water pumps resulted in an automatic low vacuum turbine trip and a subsequent [Unit 2] reactor trip due to the turbine trip. "The 2 'G' Bus did automatically transfer to the 'B' Reserve Station Service Transformer and is currently energized. The Unit 2 Auxiliary Feedwater pumps automatically started and provided flow to the steam generators. There were no issues with the Auxiliary Feedwater System operation. "The Unit 2 'A' Charging Pump and the Unit 2 'A' Component Cooling Water pump automatically started as designed due to the loss of power. The Unit 1 'B' Charging Pump and the Unit 1 'B' Component Cooling Water pump automatically started as designed due to the loss of power. The Unit 2 'C' Station Service Bus was lost following the trip when the electrical system automatically transferred to the Reserve Station Service transformers. With the 'C' Reserve Station Service Transformer de-energized the 'C' Station Service Bus was unable to transfer to an energized transformer. This resulted in the loss of the Unit 2 'C' Reactor Coolant Pump. The 'A' and 'B' Reactor Coolant Pumps remain in service at this time. "The reactor trip is reportable per 10CFR50.72(b)(2)(iv)(B). "The Auxiliary Feedwater system, Emergency Diesel Generator system, Charging system actuations are reportable per 10CFR50.72(b)(3)(iv)(A). "The electrical system is being returned to a normal lineup. The condensate and feedwater system remained in service to provide flow to the steam generators. Steam Dump operation to the condenser is not available due to low condenser vacuum, therefore steam is being released to the atmosphere from the Steam Generator Power Operated Relief Valves." The licensee suspects that switchyard maintenance activities caused the L102 trip which initiated the chain of events. All rods inserted into the core during the trip. During the transient, some secondary relief valves lifted and properly reseated. There is no known primary to secondary leakage. During the event call, the licensee reported that the 'C' Reserve Station Service Transformer was returned to service. The licensee notified the NRC Resident Inspector and will be notifying the Louisa County Administrator. | 100 | 0 | 0 | 100 | 97 | 0 | -1 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-09
45555 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-12-09 11:17 | 2009-12-09 17:04 | 2009-12-10 | WINTER STORM POWER OUTAGES CAUSE ALERT SIREN INOPERABILITY "On December 9, 2009, at 1117 hours, 27% of the alert sirens in the Quad Cities Station Emergency Planning Zone were determined to be inoperable for greater than 60 minutes. This is considered a major loss of the Quad Cities off site notification capability. The alert sirens were disabled due to power outages caused by a winter storm. Efforts are underway at the time of this notification to restore the sirens. "This report is being made due to the reduction in public notification capabilities in accordance with 10CFR50.72(b)(3)(xiii). "A follow-up notification will be provided when the sirens have been restored." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MIKE MACLENNAN TO DONALD NORWOOD AT 0849 EST ON 12/10/2009 * * * "Follow-up Notification - Repairs to the emergency sirens were completed as of 0100 hours. All sirens are restored." The licensee notified the NRC Resident Inspector. Notified R3DO (Phillips). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-09
45554 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-12-09 12:31 | 2009-12-09 16:48 | 2009-12-09 | BLIZZARD RESULTS IN SPURIOUS ACTUATION OF EMERGENCY SIREN "At 1231 CST on 12/09/2009 Emergency Siren P-007 located in Mishicot, WI area inadvertently actuated. This siren accounts for a population coverage of 2.3%. Therefore, the KPS (Kewaunee Power Station) emergency siren coverage remains acceptable with P-007 non-functional. "Point Beach Nuclear Plant notified the Manitowoc County Sheriff department of the actuated siren [See EN# 45553]. At 1350 CST Point Beach performed a siren test and reset the siren. The siren is no longer alarming. A repair team has been sent to the siren location to determine the cause of the actuation." The NRC resident inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-09
45553 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-12-09 12:31 | 2009-12-09 16:22 | 2009-12-09 | NOTIFICATION OF LOCAL LAW ENFORCEMENT DUE TO A SINGLE EMERGENCY SIREN ACTUATION "At 1231 emergency siren P-007 located in the Mishicot, WI area inadvertently actuated. The siren covers 0.9% of total EPZ population. Severe weather, snow, ice and wind is occurring at this time. "At 1340 siren actuation was verified and Manitowoc County Sheriff was notified of the sounding siren. At 1350, Point Beach performed a siren test, reset the siren and it is no longer alarming. Repair team has been dispatched to the siren location to troubleshoot and determine the cause of the actuation. "The population coverage for siren P-007 is 0.9% and the siren malfunction is not reportable due to loss of population coverage. However, based on actuation and notification of the Manitowoc County Sheriffs Department, the event is reportable." The NRC resident inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-09
45552 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-12-09 11:01 | 2009-12-09 14:55 | 2009-12-09 | EMERGENCY SIRENS FAILED TO ACTIVATE "On December 9, 2009, at approximately 1101 EST, as a result of a scheduled full-volume test of the Indian Point Energy Center (IPEC) Alert Notification System (ANS), using microwave/radio activation pathway only, 37 of 172 sirens did not pass the test. The siren system was then configured to the normal configured (TCP/IP and microwave/radio activation pathways) and the siren system retested successfully following a silent test at approximately 1147 EST. The system is capable of being used to notify the public in an emergency. Prior to the full volume test today, a previous silent test using the radio/microwave pathway was successful. As a result of the 37 sirens that did not pass the test today, a press notice was provided. This courtesy notification is being provided under 10CFR50.72(b)(2)(xi). "The condition was recorded in the IPEC corrective action program. The event remains under investigation." The licensee notified the NRC Resident Inspector and FEMA. Additionally Westchester, Orange, Putnam, and Rockland counties were notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-09
45551 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-12-09 08:00 | 2009-12-09 10:34 | 2009-12-09 | BLIZZARD RESULTS IN GREATER THAN 50% SIREN COVERAGE LOSS "On December 9 at 0800 CST, seven emergency notification system sirens in Kewaunee Power Station Emergency Planning Zone were reported out of service. It is expected the cause of the sirens to be out of service is the severe winter weather. The loss of these emergency notification sirens results in a lost population coverage of 56%. As a result, this event is being reported under 10CFR50.72(b)(3)(xiii) and guidance in NUREG-1022 as a major loss of off-site communications capability. "It is unknown, at this time, when the sirens will be returned to service." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-09
45550 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-12-08 13:28 | 2009-12-08 14:56 | 2009-12-08 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 1328 [CST] on Tuesday, December 8, 2009, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system was removed from service for planned preventative maintenance activities on the damper flow controller and air filtration charcoal system. During the maintenance, the non-emergency ventilation system will be functional. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 48 hours. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing EP [Emergency Planning] procedures and checklists. If radiological conditions require TSC facility evacuation during ventilation system restoration; the Station Emergency Director will evacuate and relocate the TSC staff in accordance with, EP-AA-112-200-F-01." The licensee notified the NRC Resident Inspector. | 0 | 83 | 99 | 0 | 83 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-08
45549 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2009-12-08 08:42 | 2009-12-08 12:19 | 2009-12-08 | MANUAL REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL CAUSED BY LOSS OF MAIN FEED WATER PUMP "Arkansas Nuclear One - Unit 2 experienced a high temperature on the 'A' Main Feedwater Pump thrust bearing which required the pump to be manually tripped . Steam Generator levels lowered as a result of the Main Feedwater Pump trip to the point that operators initiated a manual reactor trip. The Emergency Feedwater System automatically actuated on low Steam Generator level as a result of the Steam Generator level transient. "The manual reactor trip requires 4-Hr non-emergency notification IAW 10CFR 50.72(b)(2)(iv)(B). "The automatic actuation of Emergency Feedwater requires 8-Hr non-emergency notification IAW 10CFR 50.72(b)(3)(iv)(A)." All rods fully inserted. After the trip, decay heat was being removed using steam dumps to the condenser. Steam generator level was being maintained with the emergency feedwater pumps. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-08
45548 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2009-12-08 | 2009-12-08 11:22 | 2009-12-08 | WOODWARD GOVERNOR SERVO FAILURE DUE TO SILVER SULFIDE CORROSION OF SURFACE MOUNT RESISTORS "Woodward failure analysis report #85572-R001, dated 10/9/09, addressed two separate [model] PGPL remote servo failures. The failure analysis report discusses a silver sulfide corrosion issue with surface mount resistors used in the PGPL remote servo feedback transmitter circuitry. Woodward part number 9903-539 consists of a PGPL actuator and a remote servo. The PGPL actuator is mounted on the turbine's governor drive and the remote servo (Woodward part number 5296-044) is mounted at the steam valve. Hydraulic lines interconnect the PGPL to the remote servo. The PGPL actuator and remote servo was supplied by Engine Systems, Inc. (ESI) to the Callaway and Vogtle nuclear plants as part of a digital governor upgrade (Woodward 505 control) on their steam turbine generators. These are the only nuclear plants that use the P/N 9903-539 actuator remote servo assembly. "LISTING OF WOODWARD PIN 9903-539 PGPL ACTUATORS WITH SUSPECT RESISTORS "Serial Number Born Date Shipped to 12369963 Nov 2000 Callaway 13305595 July 2002 Callaway 13798414 May 2004 Vogtle 13798415 May 2004 Callaway 14141720 Feb 2005 Vogtle 14409400 Sep 2005 Vogtle "Note: Serial numbers 12369963 and 13798414 recently had the feedback board replaced during the failure analysis; these require no further corrective action." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-12-08
45547 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-12-07 18:01 | 2009-12-07 20:07 | 2009-12-07 | AUTOMATIC REACTOR TRIP DUE TO A TURBINE TRIP CAUSED BY LOW CONDENSER VACUUM "Vogtle Unit 1 tripped from 100% power due to a [turbine trip/ reactor trip] RPS [reactor protection system] actuation. The turbine tripped due to low condenser vacuum. Initial investigation indicates that a loss of a non-1E electrical switchgear initiated the event. "All systems responded as expected. The AFW [auxiliary feedwater] systems responded as required. "Reactor temperature [and decay heat removal] is being maintained on SG [steam generator] ARVs [atmospheric relief valves]. "Both NRC Resident Inspectors were notified of the trip." There were no complications. All rods inserted during the trip and there was no primary to secondary leakage. There was no impact on Unit 2. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-12-07
45546 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-12-07 11:18 | 2009-12-07 19:48 | 2009-12-07 | AGREEMENT STATEMENT REPORT - STOLEN NUCLEAR GAUGE FROM A DELIVERY TRUCK The following notification was received via email: "On December 7, 2009, CPN Instrotek, California License CA1100-07, reported that a MC-3 gauge was stolen from a delivery truck while it was being transported to CPM Instrotek. The gauge is Serial Number M36046710. The gauge contains 10mCi of CS 137 and 50mCi of Am/Be. "This theft was reported by CPN Instrotek on Monday, December 07, 2009 1118 AM by email. The report was made by [the] Radiation Safety Officer [RSO] for CPN Instrotek. [The RSO] reported that CPN Instrotek had received a call on the morning of December 7, 2009 from the transport company that was transporting the gauge from the airport to CPN Instrotek (both in Concord California). The transport company stated that the gauge was stolen from one of their trucks between the evening of December 4th and the morning of December 7, 2009. The truck was locked. The transport company had picked up the gauge at the airport and it was being delivered to CPN Instrotek in Concord. The gauge was being returned to CPN Instrotek for disposal. The loss was reported to local law enforcement. " California Event Number: N/A THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-12-10
45545 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2009-07-14 | 2009-12-07 16:26 | 2009-12-07 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILS TO FUNCTION The following information was received by email: "On 07-14-09 while conducting a biannual inventory of gauges, licensee discovered that shutter on the Ronan X92-SA-1, Serial No. 74584, was not functioning. The licensee contacted Ronan, who repaired the shutter on 08-05-09. Although the necessary repairs were made, it was found that future service of the shutter would require replacing the current shutter with a new shutter. "DRH was notified of the incident on 11-04-09 while doing a routine inspection of the licensee. DRH closed out with the licensee and received documentation of the incident." The gauge contains the isotope Cs-137 with an activity of 20mCi. Mississippi Incident Number: MS 09007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2009-12-10
45544 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2009-12-07 04:30 | 2009-12-07 16:42 | 2009-12-07 | FAILURE TO FULLY RETRACT THE SOURCE OF A RADIOGRAPHY CAMERA Technicians were performing radiography when the source in an Industrial Nuclear Corporation (INC) IR-100 radiography camera was unable to be fully retracted. This was caused by a frozen lock on the device which occurred due to freezing weather conditions. A certified technician serviced the lock. The lock was returned to a fully functional condition, and the source was returned to the safe and secure position. No personnel over exposure occurred. The licensee could not provide the source number of the Ir-192 source at the time of the report. The camera number is 4812. Similar events: EN #45384, 45469, 45524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-12-07
45543 | 0 | US ARMY CECOM |  |  |  |  | 2009-11-30 | 2009-12-07 15:33 | 2009-12-09 | LOSS OF CONTROL OF A NUCLEAR GAUGE On November 30, 2009, the US Army Communications and Electronics Command (CECOM) discovered that a licensed nuclear scanning device was missing. [The device location is REDACTED]. The device is an Ohmart VM00055 that is a part of a mobile vehicle and cargo system made by Science Applications International Corporation (SAIC). The source is a 1.6 Ci, CS-137 source with a source number: 3231CG. * * * UPDATE FROM BARRY SILBER TO DONG PARK AT 1422 ON 12/8/09 * * * A request made by Headquarters Department of Army Radiation Safety Officer was processed. Notified R1DO (Schmidt), R3DO (Phillips), FSME (Burgess). * * * UPDATE FROM BARRY SILBER TO VINCE KLCO AT 1625 ON 12/09/09 * * * The licensee called to clarify that on November 30, 2009, Fort Drum discovered the device was missing and then an investigation ensued. On December 7, 2009, Fort Drum successfully notified the US Army CECOM Life Cycle Management Command that a licensed nuclear scanning device was missing. The device is postulated to be located on a maritime security vessel. Notified R1DO (Schmidt), R3DO (Phillips), FSME (Einberg) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-12-09
45542 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-09-11 | 2009-12-07 11:47 | 2009-12-07 | AGREEMENT STATE REPORT- POTENTIAL LOSS OF RADIOACTIVE MATERIAL The following information was received from the Commonwealth of Massachusetts via facsimile: "On 9/11/09 a package containing 1 mCi of P-32 was received by the licensee Radiation Safety Office, [who then] opened the package to confirm RAM [radioactive material] was in the box, surveyed the package, and then delivered [the package] to the research lab. The research lab signed for the package. One week later the research lab reported to the RSO that the package did not contain the ordered P-32. A search of lab, adjacent labs, and waste removed from the lab did not locate the missing radioactive material." MA Docket Number: 10-8699 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-12-10
45541 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-12-05 10:59 | 2009-12-05 17:48 | 2009-12-05 | HPCI OUT OF SERVICE DUE TO THE LOSS OF THE SUCTION AUTO-SWAP FUNCTION "On 12-04-09 at 16:00, condensate storage tank (CST) level switch [2E41 N002], was declared inoperable due to not actuating at the correct set point. A RAS [Required Action Statement] was entered to align high pressure coolant injection (HPCI) suction to the suppression pool within 24 hours as required by Tech Spec [Technical Specification] action statement 3.3.5.1.D 2.2. The switch was found stuck and was freed up after manual manipulation and tripped correctly during a functional test. It was decided on 12-05-09 to perform a calibration on the level switch prior to declaring it operable. "During performance of calibration procedure 57CP-CAL-012-2 at 1059 EST on 12-05-09, a jumper was installed that rendered the HPCI and reactor core isolation cooling (RCIC) auto-transfer suction swap from CST to suppression pool inoperable. This is a loss of function for the initiation capability of HPCI and RCIC CST low level suction swap instrumentation. This loss of function was not discovered until 1330 on 12-05-09, at which time TS [Technical Specification] 3.3.5.1.D was entered for HPCI and TS 3.3.5.2.D for RCIC, until HPCI and RCIC suction were manually aligned to the suppression pool which allowed the plant to exit the required actions to declare HPCI and RCIC inoperable within 1 Hour. HPCI and RCIC were aligned to the suppression pool at 1341 EST. "The RCIC suction was realigned to the suppression pool as required by the Tech Specs in order to restore its operability. It should be noted that no credit is taken for RCIC in the safety analysis nor is this system considered an ESF system. For this reason there are no reporting requirements associated with the inoperability of RCIC. HPCI was declared inoperable in accordance with the instrumentation Tech Specs, but during this time frame HPCI was capable of performing its safety function. However- additional review will be needed to confirm that HPCI could have operated for the duration of its mission time of 4 hours while aligned to the condensate storage tank. Absent that information this report is being made due to HPCI being declared inoperable until its suction was realigned to the suppression pool. This assumed loss of function for HPCI is being reported in accordance with 10CFR50.72(b)(3)(v)(D) since a final determination has not been made that HPCI would have continued to perform its safety function for the required mission time while aligned to the CST." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-12-05
45540 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-09-02 | 2009-12-03 17:19 | 2009-12-03 | AGREEMENT STATE REPORT - MEDICAL DOSE DIFFERENT THAN PRESCRIBED The following information was received via facsimile: "This incident was reported to the DEP [Pennsylvania Department of Environmental Protection Bureau of Radiation Protection] Eastern Regional Office by the licensee via a phone call on September 3, 2009, but wasn't considered a ME [Medical Event] by DEP at the time. On September 2, 2009 a patient was prescribed a dose of 150 millicuries (mCi) of radioactive iodine-131 (I-131) for a therapeutic treatment of thyroid cancer. The nuclear medicine technologist took the 150 mCi dose to the patient's room in a lead container and made the appropriate tube connections. The connections were checked with water prior to administration of the I-131 and no leaks were present. The dose was administered. During the flushing process, the technologist noted some leakage of liquid on the absorbent material that was placed under the tubing. The syringe, tubing, and absorbent material were immediately removed and assayed in the dose calibrator. It was determined that 57.6% of the prescribed dose had been administered to the patient. A second written directive for an additional dose prescribed by the authorized user was delivered to provide assurance that the patient received the appropriate complete amount of radioactive iodine for treatment of the thyroid cancer. "During an inspection of Fox Chase on December 1, 2009, this incident was reviewed by the DEP. At this point the licensee informed DEP that they considered this a ME, had notified the patient, thus, the reason for this fax ME notification to the NRC HOO [Headquarter Operation Officer] at this point in time. Additional details will be provided in the NMED report." Pennsylvania Event Report: PA090034. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-12-09
45539 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-05-15 | 2009-12-03 15:20 | 2009-12-03 | AGREEMENT STATE REPORT- RADIOGRAPHY CAMERA SOURCE FAILED TO FULLY RETRACT The following report was provided by the Arkansas Department of Health via facsimile: "On October 26, 2009, during a routine inspection of Desert Industrial X-Ray, ARK-1010-3320, in Beebe AR it was discovered that an INC IR-100 exposure device (SN#4772, Source Model#32, SN#N475, Ir-192, 32 Ci) had failed to retract the source to the fully shielded position. The failure to retract had occurred on May 15, 2009. The Radiation Safety Officer for the location was properly trained and had to disassemble and clean the locking mechanism in order to retract the source to the fully shielded position. INC informed Desert Industrial X-Ray that this failure to retract occurs when the exposure devices are getting dirty. The licensee reports that corrective actions have been taken to that there have been no further problems with this device. Desert Industrial X-Ray personnel reported no unusual survey readings, and no personnel exposures occurred during this incident. "The Department [Arkansas Department of Health] has concluded that the root cause of this incident is improper maintenance of the INC IR-100 exposure device. The licensee has implemented corrective action by introducing an enhanced maintenance program. The Department considers this incident to be closed." See similar report EN#45538. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-12-08
45538 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-06-16 | 2009-12-03 15:18 | 2009-12-03 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO FULLY RETRACT The following report was provided by the Arkansas Department of Health via facsimile: "On October 26, 2009, during a routine inspection of Desert Industrial X-Ray, ARK-1010-3320, in Beebe AR it was discovered that an INC IR-100 exposure device (SN#4520, Source Model#32, SN#N478, IR-192, 26 Ci) had failed to retract the source to the fully shielded position. The failure to retract had occurred on June 16, 2009. The Radiation Safety Officer for the location was properly trained and had to disassemble and clean the locking mechanism in order to retract the source to the fully shielded position. INC informed Desert Industrial X-Ray that this failure to retract occurs when the exposure devices are getting dirty. The licensee reports that there have been no further problems with this device. Desert Industrial X-Ray personnel reported no unusual survey readings, and no personnel exposures occurred during this incident. "The Department [ Arkansas Department of Health] has concluded that the root cause of this incident is improper maintenance of the INC IR-100 exposure device. The licensee has implemented corrective action by introducing an enhanced maintenance program. The Department considers this incident to be closed." See similar report EN#45539. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-12-08
45537 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2009-12-03 04:30 | 2009-12-03 09:14 | 2009-12-03 | MANUAL REACTOR TRIP AFTER LOSS OF INSTRUMENT AIR TO CONTAINMENT "On December 3, 2009 at approximately 04:30 Mountain Standard Time (MST) Palo Verde Unit 3 operators manually tripped the reactor from approximately 100% rated thermal power due to loss of Instrument Air (IA) to Containment. This loss was apparently caused by a failure (closed) of the outboard IA Containment Isolation Valve (CIV) solenoid valve. Loss of IA to Containment resulted in closure of the inboard Reactor Coolant Pump (RCP) controlled seal bleedoff CIV. The RCP seal bleedoff was then being diverted via relief valve to the Reactor Drain Tank (RDT) inside Containment. "Following the manual reactor trip all CEAs [Control Element Assemblies] fully inserted into the reactor core. All 4 RCPs were stopped to allow for isolation of bleedoff to the RDT. Upon completion of Standard Post Trip Actions, the crew entered the Optimal Recovery Procedure for Loss of Forced Circulation. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. LCO 3.6.3 was entered due to failure of the IA CIV. No major equipment was inoperable prior to the event which contributed to the need for manual reactor trip." The reactor was manually tripped for equipment preservation. No safety or relief valves lifted other than noted above. After the trip, decay heat was being removed using the turbine bypass valves and steam generator level was being maintained with the auxiliary feedwater pumps. The licensee also entered LCO 3.4.5, "RCS Loop Operability" because the RCPs were stopped. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-12-03
45536 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-12-02 13:41 | 2009-12-02 17:25 | 2009-12-02 | POTENTIAL FIRE PREVENTING REDUNDANT CHILL WATER PUMP FROM OPERATING "During reconstitution of the post fire safe shutdown analysis, it was noted that conditions exist whereby the requirements of the Hope Creek fire protection program (BTP CMEB 9.5-1) for the required degree of separation for redundant safe shutdown trains may not be met. "A postulated fire in one of the reactor building fire zones (RB1 or RB2) may affect the ability to operate a required chilled water circulating pump due to the logic interrelationships between the cooling fans and their associated chilled water pump. Specifically, a fire in one area may affect cooling fans from each division and the fan failures could either trip or prevent the redundant chilled water pump from operating. This has the effect of removing the fire barrier between redundant safe shutdown trains. As such, this event is reportable under 10CFR50.72(b)(3)(ii)(B) for the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "Fire watches have been implemented in accordance with our approved fire protection program as an interim compensatory measure. All required safe shutdown systems remain operable. No systems or safety-related equipment actuations occurred or were required or expected as a result of this condition. All systems and safety-related equipment affected by this condition remain operable and functional. Nothing has been noted as unusual or not understood. The only system affected is the chill water system. There were no actuations or initiating signals, nor effects of the event on the plant. No personnel have been injured." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-12-02
45535 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-12-02 13:45 | 2009-12-02 17:09 | 2009-12-02 | NOTIFICATION TO KANSAS DEPARTMENT OF HEALTH "Notification to State agency due to sample exceeding limits. "On 12/2/09, Wolf Creek received lab results for Wastewater Treatment Basin samples. The sample taken on 11/14/09 exceeded the National Pollutant Discharge Elimination System (NPDES) daily limit of 15 parts per million (ppm) for oil and grease. The result was 18.3 ppm. Exceeding this limit required notification to the State. The Kansas Department of Health and Environment, Bureau of Water was notified on 12/2/2009 that our NPDES limit was exceeded." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-02
45534 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-12-01 18:00 | 2009-12-01 21:53 | 2009-12-01 | ONSITE FLOODING CAUSED BY MAKE-UP SUPPLY LINE FAILURE "The following transmission was made as a voluntary notification at 1800 EST: On 12/01/09 at 1410 [EST], due to a Unit 2 cooling tower make-up supply line failure, a valve vault was flooded and overflowed at several thousands of gallons per minute flow. The local fire company was contacted to provide equipment assistance in pumping out the vault. The river water overflowing the vault entered nearby storm drains and a nearby building housing non-safety related equipment. There are no injuries or an emergency of any kind. The water entering the storm sewer does not constitute a reportable spill. Unit 2 reactor power was reduced to 80% to minimize cooling tower impact. The Pennsylvania Emergency Management Agency was notified at 1800 EST. Various other local and state agencies have been advised of the event. "Subsequently, notifications were made to the following agencies: "Salem Township Supervisor Chairman "State Senator Baker "State Rep. Boback "Columbia County Commissioner Soberick "Federal Affairs to notify US Rep. Kanjorski's staff. "Although the impact of this make-up supply line failure to the environment is insignificant (Radiological levels are less than lower limit of detection), its occurrence coupled with subsequent notifications to aforementioned agencies is likely to cause heightened public or government concern. Thus, Susquehanna Steam Electric Station is making a four hour ENS notification pursuant to 10CFR50.72(b)(2)(xi). A press release is not planned at this time." The licensee has notified the NRC Resident Inspector. | 94 | 79 | 0 | 94 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-12-01
45533 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-12-01 15:00 | 2009-12-01 17:37 | 2009-12-01 | CONTAMINATED PERSON REPORTS TO OFFSITE HOSPITAL "On November 26, 2009, at 2330, it was determined that a machinist who was working on reactor coolant pump (RCP 3A) seal was contaminated on his left hand index finger. The contamination level was 1500 net counts per minute (CPM). Upon exit, the individual alarmed monitors and decontamination was attempted. Decontamination for the next two shifts included wrapping of the hand, waiting 2 hours, rechecking and repeating 2 hours later. However, decontamination was unsuccessful. The individual was conditionally released and allowed to leave the site with his hand wrapped. "On December 1, 2009, at approximately 1500, the Fort Calhoun Station Health Physics and Radiological Protection Personnel met the machinist at the University of Nebraska Medical Center (UNMC) for further treatment." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2009-12-01
45532 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-02-04 10:00 | 2009-12-01 14:45 | 2009-12-01 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR GAUGE NOT INITIALLY REPORTED The following report was received via e-mail: "On Monday, February 4, 2008, a technician was attempting to load a gauge on a truck when he dropped the gauge on the tailgate whereupon the index probe broke off and the Cs-137 probe became extended and failed to retract to the shielded position. The gauge was then loaded into the cab of the truck and was delivered to the local site office less than ten minutes from the work site. A service company was notified and within an hour, the source rod was safely retracted into the shielded position. The gauge sources were satisfactory leak tested. No overexposures occurred in this event. The licensee required all gauge users to attend refresher training on nuclear gauge safety and procedures. The licensee was cited for a related violation. "During a record review, it was discovered that this event was reported to the NRC using the Nuclear Materials Event Database (080192) instead of to the Headquarters Operations Officer. "Texas Incident #: I-8494" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-12-04
45531 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-11-30 14:27 | 2009-12-01 12:23 | 2009-12-01 | FITNESS FOR DUTY NON-LICENSED SUPERVISOR A non-licensed contractor supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2009-12-01
45530 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-12-01 12:00 | 2009-12-01 11:08 | 2009-12-03 | IPCS SYSTEM OOS FOR SECURITY MODIFICATION "Beginning December 1,2009, at approximately 1200, the Fermi 2 Integrated Plant Computer System (IPCS) will be removed from service to support installation of a Cyber Security Modification. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the PCS platform and will be out of service when the PCS is removed from service. These systems will be unavailable to the Control Room and all other Emergency Response Facilities (ERFs) for approximately six hours. By 1800, it is planned to restore IPCS, including SPDS and ERDS, to the Control Room, Operational Support Center, and the Technical Support Center. The IPCS will remain unavailable to the Emergency Operations Facility (EOF) as well as alternate EOF. On December 2, at approximately 1600, IPCS will be restored to the EOF but will remain unavailable to the alternate facilities. On December 3, 2009, at approximately 1600, IPCS will be restored, including alternate facilities. "During this entire duration dose assessment capability will only be available in the manual data input mode. A follow-up notification will be submitted when the PCS is completely restored. For the first six hours of the PCS outage, the emergency assessment capability of all Fermi 2 ERFs will be degraded by the loss of IPCS and SPDS. During this period the ERDS function will also be lost. For the following 24 hrs., the EOF will have no IPCSs capability, which includes the SPDS function. Based on the aggregate effect of these losses, this notification is being made per the requirements of 8 Hour Non-Emergency Notification 10CFR,50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1753 EST ON 12/3/09 FROM MATUSZAK TO HUFFMAN * * * "On December 3, 2009, at 1530, emergency assessment capability has been restored to all on site emergency response facilities." The licensee will notify the NRC Resident Inspector. R3DO (Riemer) notified. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-01
45529 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-12-01 09:18 | 2009-12-01 08:57 | 2009-12-01 | HEALTH PHYSICS CONTROL POINT AND CHEM LAB HVAC OUT OF SERVICE FOR PLANNED MAINTENANCE "On 12/1/2009 the emergency HVAC [heating, ventilation, and air conditioning] for the Hatch Nuclear Plant's Health Physics (HP) Control Point/Chemistry Lab area will be removed from service for preventative maintenance, planned corrective maintenance and glycol addition to the cooling coil. The Technical Response Manual (TRM) section 3.10.1 lists the HP Control Point/Chemistry Lab area emergency HVAC system as being required for functionality of the Operations Support Center [OSC]. This area is normally utilized by HP/Chem for analysis of radiological samples during normal as well as emergency conditions. These work activities are planned to be performed and completed within a 12 hour work shift. During the time these activities are being performed the HP emergency HVAC and filter train will not be available for operation for approximately eight (8) hours. As such the OSC will be rendered non-functional during the performance of this work activity. The OSC facility working area itself, however, does not lose EP functionality throughout this evolution. "If an emergency were to occur, plans are to continue utilize the Health Physics Control Point/Chemistry Lab areas during the time required to restore the HVAC system, as long as environmental and radiological conditions allow. Habitability surveys will be performed in the areas while they are being utilized. If required respiratory protection equipment can be utilized as appropriate for emergency responders utilizing this area until such time as the emergency HVAC is returned to service. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-12-01
45528 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-11-29 10:45 | 2009-11-29 13:31 | 2009-11-29 | TRIP FROM INTERMEDIATE RANGE DUE TO ROD GROUP DEMAND COUNTER DISCREPANCY "During startup physics testing, the reactor operator identified a discrepancy between Group 1 & Group 2 Step Demand Counters for control bank 'B'. Research identified the issue to be associated with failure of a card in the rod control power cabinet. Failure of the card impacts group step counters for control bank 'B', control bank 'D' and shutdown bank 'B.' "Inoperability of more than one group step counter per bank placed Unit 2 in a 6-hour clock to hot shutdown as of 0808 hrs 29 November 2009. Consequently, at 1045 hrs, the decision was made to trip Unit 2 reactor. The decision was based on time required to make repairs, complete post maintenance testing requirements, and maintaining proper control of reactivity. "All systems functioned as required on the trip and initiation of any auxiliary or emergency systems was not required. Current heat removal is via normal plant alignment following refueling outage activities: steam generator blowdown, main feedwater, and steam generator PORV." All control rods fully inserted on the manual trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-11-29
45527 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-11-28 18:50 | 2009-11-29 13:01 | 2009-11-29 | SAFETY EQUIPMENT DISABLED DUE TO A GROUND IN THE AREA CONTROL ROOM ALARM "At 1850 CST, on 11/28/09 the Plant Shift Superintendent (PSS) was notified that the C-333 Unit 6 Cell 5 UF6 Release Detection (PGLD) System was inoperable due to loss of power to the Area Control Room (ACR) alarm for this system. The purpose of the PGLD System is to detect a UF6 release and alert operators in the ACR by sounding an alarm. At the time this was discovered, G-333 Unit 6 Cell 5 was operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell are operable during steady state operations above atmospheric pressure. With the Unit 6 Cell 5 PGLD system inoperable, none of the required heads were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.B.1 was entered and a continuous smoke watch was put in place within one hour. "Troubleshooting was initiated, a ground was discovered on the alarm circuit, the ground was isolated, and the system was tested and declared operable at 2305 [CST]. This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2009-11-29
45526 | -1 | WATERFORD | 3 |  |  | [3] CE | 2009-11-28 23:44 | 2009-11-29 05:08 | 2009-12-02 | CONTAINMENT MINIMUM PATHWAY LEAK RATE WAS EXCEEDED "10CFR50 Appendix J Local Leak Rate Testing determined the total 'as-found' containment minimum pathway leak rate exceeded the maximum allowable containment leak rate per the Containment Leakage Rate Testing Program. This was primarily due to three penetrations that could not be pressurized to full test pressure. The maximum allowable leakage was assigned to both valves in each penetration since the valves can not be tested individually. "This condition is reportable as a condition of the nuclear power plant, including its principal safety barriers, being seriously degraded per 10CFR50.72(b)(3)(ii)(A). The condition was discovered with the plant in Mode 5. Corrective actions have already been completed and all penetrations, as well as total containment leakage, is well within limits established by the Containment Leakage Rate Testing Program." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM JIM POLLOCK TO PETE SNYDER AT 1711 EST ON 12/2/09 * * * "On November 29, 2009, Waterford 3 reported that the total as-found containment minimum pathway leak rate exceeded the maximum allowable containment leak rate per the Containment Leakage Rate Testing Program. This was primarily due to three penetrations that could not be pressurized to full test pressure. The maximum allowable leakage was assigned to both valves in each penetration since the valves could not be tested individually. This condition was determined to be reportable as a condition of the nuclear power plant, including its principle safety barriers, being seriously degraded per 10CFR72(b)(3)(ii). "Subsequently, Waterford 3 has evaluated the leak rates for all three penetrations and determined that as-found leakage rates assigned to the penetrations should not have been recorded at 630,000 sccm each, but should have been recorded at lower values. "After one valve was re-worked in Penetration number 48, a Local Leak Rate Test (LLRT) was completed. With the new information from the second LLRT, a revised as-found leak rate of 97 sccm was assigned to the un-worked valve. "For Penetration number 10, an Engineering evaluation of the test results was completed. The evaluation determined that the as-found leakage from this penetration was 191,000 sccm. This was based on calculating the maximum air flow capacity that could be obtained from the Leak Rate Monitor test equipment and using the first LLRT's penetration only reaching a test pressure of 43 psig instead of the 44 psig full test pressure. "For Penetration number 11, troubleshooting activities determined that one of the valves had no detectable leakage; however, a leak rate of 9,100 sccm was assigned based on its previous as-left leakage value. "With the lower leakage rates, the total as-found containment minimum pathway leak rate is calculated to be 230,682 sccm, which is within the limit of 630,000 SCCM. Since Waterford 3 had not exceeded the maximum allowable containment leak rate, EN #45526 is being retracted." The licensee notified the NRC Resident Inspector. Notified R4DO (Deese). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-11-29
45525 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-11-27 22:05 | 2009-11-28 03:15 | 2009-11-28 | TURBINE VALVE TRIPS DID NOT MEET TECH SPECS "At 2205 on Nov 27, 2009, at the Dresden Nuclear Power Station (DNPS) it was determined that Technical Specification RPS functions 8 and 9, 'Turbine Stop Valve - Closure' and 'Turbine Control Valve Fast Closure, Trip Oil Pressure - Low' are susceptible to single point vulnerability due to a nonconformance to a design standard (IEEE- 279 1968). Based on this single point vulnerability, these RPS functions could potentially have prevented the fulfillment of their respective safety function and therefore this event is reportable per 10 CFR 50.72(b)(3)(v)(D), 'an event or condition that could have prevented the fulfillment of a safety function-mitigate the consequences of an accident.' The station has performed an operability determination, and the safety function remains operable. Actions to restore compliance to referenced design standard are in progress." The licensee has informed the NRC Resident Inspector. | 0 | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-11-28
45524 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2009-11-27 08:00 | 2009-11-27 15:36 | 2009-11-27 | FAILURE TO FULLY RETRACT THE SOURCE OF A RADIOGRAPHY CAMERA Technicians were performing radiography when the source in an Industrial Nuclear Corporation (INC) IR-100 radiography camera was unable to be fully retracted. This was caused by a frozen lock on the device which occurred due to freezing weather conditions. A certified technician serviced the lock. The lock was returned to a fully functional condition, and the source was returned to the safe and secure position. No personnel over exposure occurred. The licensee could not provide the serial number of the camera at the time of the report due to the remote location where the radiography was taking place. Similar events: EN #45384, 45469, 45496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-11-27
45523 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2009-11-27 07:34 | 2009-11-27 08:40 | 2009-11-27 | ACCIDENTAL DISCHARGE OF A SECURITY OFFICER'S PISTOL "On November 27, 2009, at approximately 0734 hours, an accidental discharge of a security officer's sidearm occurred at the Davis-Besse Nuclear Power Station (DBNPS) resulting in a leg injury to the officer. The accidental discharge occurred in the Primary Access Facility. The onsite DBNPS first aid team and the Caroll Township Emergency Medical Services responded to the Primary Access Facility. The injured officer was in stable condition and transported off site [at 0800] to St. Vincent Hospital [in Toledo, OH]. "Both the Ottawa County Sheriffs Office and the Caroll Township Police Department responded to the DBNPS site to obtain information. "The Ottawa County Emergency Management Agency (EMA), the Lucas County EMA, and the Ohio EMA were notified of this incident. The NRC Resident Inspector has been notified. "Plant operation was not affected by this incident. [The plant has received calls from the media however,] no press release is planned at this time." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-11-30
45522 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-11-26 23:40 | 2009-11-27 05:00 | 2009-11-27 | TWO SHUTDOWN BANK RODS WERE DROPPED FROM FULLY WITHDRAWN POSITION "With Unit 4 borated to a cold shutdown condition following the Unit 4 Cycle 25 refueling outage, post-modification acceptance testing was being performed on the Rod Position Indication System prior to reactor startup. While performing this test, two shutdown bank rods showed indication of being fully inserted from a fully withdrawn position. Off-normal procedures were entered and the Reactor Protection System (RPS) was subsequently manually actuated. All remaining rods were fully inserted in accordance with plant procedures. Investigations are in progress to determine and repair the cause of the dropped rods." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-11-27
45521 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-11-26 13:28 | 2009-11-26 14:52 | 2009-11-26 | OFFSITE NOTIFICATION DUE TO CUBAN NATIONALS LANDING ON OWNERS CONTROLLED AREA "At 1328 [EST] on 11/26/09, the Turkey Point Nuclear Power Station Control Room received a call from an individual stating that he was a member of a group of Cuban nationals that had landed in the Turkey Point cooling canals. The individual reported that 33 Cuban nationals total (29 adults and 4 children) were in the cooling canal system. The Turkey Point Nuclear control room notified Turkey Point Nuclear Security, who located and assumed control over the Cuban nationals without incident. Turkey Point Nuclear Security notified local law enforcement agency (Miami-Dade Police), requesting assistance. At 1425 [EST], Miami-Dade Police arrived on site. United States Border Patrol and Immigration and Customs Enforcement (ICE) were notified by Miami-Dade Police. "This event is being reported under 10CFR50.72(b)(2)(xi), for an event requiring notification to a government agency." The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-11-26
45520 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-11-26 02:42 | 2009-11-26 04:00 | 2009-11-26 | MANUAL TRIP DUE TO LOSS OF VACUUM ON TURBINE DRIVEN FEEDWATER PUMP "At 0242 EST, 11/26/2009 Unit 2 reactor was manually tripped based upon indications that the 2A Main Feedwater Pump Turbine was losing vacuum. Prior to the trip, the reactor was at 30% RTP and ascending following completion of a scheduled refueling outage. 2A Main Feedwater Pump was in service; preparations were in progress to start 2B Main Feedwater Pump to support continued power ascension. Subsequent to the trip, the Auxiliary Feedwater Pumps (motor-driven and turbine-driven) started as expected in response to the trip of both main feedwater pumps following receipt of a normal feedwater isolation signal. No primary or secondary plant safety valves operated during the transient. All plant system responses to the trip were as expected. An investigation will be conducted to identify the cause of the indicated loss of vacuum and the required corrective actions. Expected restart date to be determined." All control rods fully inserted. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-11-26
45519 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-11-23 18:45 | 2009-11-24 15:14 | 2009-11-24 | AGREEMENT STATE REPORT - FAILURE OF SOURCE UP INDICATOR SWITCH The following report was received via E-mail: "At or around 6:45 PM on November 23, 2009 the irradiator at Becton Dickinson in Broken Bow, NE experienced a box jam. The master timer timed out and sent the source into the pool as normal. The source movement bell continued to ring beyond the normal time. The operator on duty entered the control room and noted that the fault indicator lights for source switch, source pass time out were activated. Both source up and source down indicator lights were on. The operator went to the source cylinder room on the roof and verified that physically the cylinder had traveled to the full down position. The source cable was determined to be tight as normal. The area was also surveyed for any radiation above background. None was noted. "The operator then called the RSO and informed him of the situation. The RSO came to the plant. Since the source up indicator was activated, the area monitor was disabled. The cell door was manually opened and the air to the source cylinder disabled. Two operators along with the RSO slowly entered the cell with two survey meters. No radiation above background was detected. "It was determined that the source up switch plunger had become stuck in the closed position. This plunger was removed, cleaned and lubricated. No other machine issues were noted and normal operation ensued. "Reporting Requirement: 30.509(b)(2) - events involving failure or disability to function when equipment is required to be available and operable and no redundant equipment is available and operable, includes source disconnection and failure to retract source." Nebraska Item Number: NE090017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-11-27
45518 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-10-19 11:05 | 2009-11-24 14:19 | 2009-11-24 | AUTOMATIC CLOSURE OF PRIMARY CONTAINMENT ISOLATION VALVES DUE TO INVALID SIGNAL "On Monday, October 19, 2009, Limerick Unit 1 was operating at 100% power. At 1105 hours, an invalid actuation of the 1B Reactor Enclosure Ventilation Exhaust Radiation Monitor occurred. The actuation caused a Division 2 Group 6C isolation signal, which caused primary containment isolation valves (PCIVs) to automatically close on the Containment Leak Detector Radiation Monitor (10-S182) and the Drywell Hydrogen/Oxygen Analyzer (10-S205). The 1A, 1C, and 1D channels were unaffected and indicated normal ventilation exhaust radiation levels during the event. "The cause of the event was a failure of a fuse holder in the 1B Reactor Enclosure Ventilation Exhaust Radiation Monitor. The radiation monitor is designed to fail-safe on a loss of power. The automatic closure of the PCIVs placed them in their fail-safe position. The failed fuse holder has been replaced and the radiation monitor was declared operable on Tuesday, October 20, 2009 at 1348 hours. "The portion of the primary containment isolation system that received an actuation signal functioned successfully. All of the affected open isolation valves automatically closed. The only equipment malfunction during the event was the failed fuse holder. The Division 2 Group 6C isolation was a partial actuation. "This event is reportable per 10CFR50.73(a)(2)(iv)(A) since isolation valves for the Containment Leak Detector Radiation Monitor and Drywell Hydrogen/Oxygen Analyzer automatically closed due to an invalid signal." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-11-24
45517 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-11-24 03:05 | 2009-11-24 03:40 | 2009-11-24 | UNUSUAL EVENT - REACTOR COOLANT SYSTEM LEAKAGE GREATER THAN 25 GPM "Beaver Valley Unit 2 declared an unusual event due to reactor coolant system unidentified leakage greater than 25 GPM into the pressurizer relief tank. Leakage occurred during shutdown of the residual heat removal system Train-A. The Train-A suction relief valve lifted due to pressure from the in-service Train-B residual heat [removal] system. The leakage has been stopped by isolating Train-A RHR from Train-B RHR. The duration of relief valve lifting was about 9 minutes. The pressurizer relief tank remained intact. All other systems functioned as designed and the plant is stable. Containment was closed at time of the event. No radioactive release occurred." The licensee terminated the unusual event at 0404 EST. The licensee notified the NRC Resident Inspector. * * * UPDATE BY DAVID HASER TO VINCE KLCO ON 11/24/2009 AT 0707* * * Licensee clarified that the event was due to identified leakage not unidentified leakage as stated in the paragraph above. Notified R1DO. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-11-24
45516 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2009-11-17 | 2009-11-23 11:36 | 2009-11-23 | AGREEMENT STATE REPORT - REPORT OF FOUND Cs-137 SOURCE The following report was received via facsimile: "On the morning of November 17, 2009, the Alabama Office of Radiation Control received a phone call from a representative of US Steel in Fairfield, Alabama advising the Agency [Alabama Office of Radiation Control] of the discovery of radiation levels in a load of scrap metal. The entire load of scrap was set aside and isolated. On the morning of November 20, 2009, a representative of the Office of Radiation Control visited the USA Steel facility in Fairfield to assist in locating and identifying the source of radiation. The source of radiation was identified as a stainless steel rod approximately 12 inches in length and 3/4 inches in diameter. Maximum radiation levels of 150 millirem/hour were noted at close proximity to one end of the rod. Preliminary field analysis identified the isotope as Cs-137. Based on the configuration and isotope, the source of radiation may be a source rod from a moisture density gauge. The source of radiation was isolated and preliminary leak test results in the field indicate that the source is not ruptured. The Alabama Office of Radiation Control is currently investigating where the source of radiation originated. "This is all the information that this Agency [Alabama Office of Radiation Control] has at this time and is current as of 10:30 am central time, November 23, 2009." Alabama Incident 09-43. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2009-11-26
45515 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-11-22 16:00 | 2009-11-22 16:31 | 2009-11-22 | FIRE IN THE 1A SWITCHGEAR ROOM The licensee declared a Notice of Unusual Event (NOUE) condition onsite per Emergency Action Level HU2.1 'Fire within the Protected Area not extinguished within 15 min. of detection or explosion within the Protected Area.' The fire is in the [non-safety] 1A 7.2 kV switchgear room. Both Engineered Safety Features buses are being supplied by offsite power. The plant remains shutdown and stable in mode 5. Offsite assistance was called to fight the fire. The licensee confirmed the fire as extinguished at 1640 EST and is monitoring the area. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM WILLIAMSON TO SNYDER AT 1906 ON 11/22/09 * * * The licensee terminated the NOUE at 1855 EST. Upon inspection of the area the licensee noted that 3 areas of non-safety switchgear were affected. Offsite assistance was used in fighting the fires and has since been released. Notified R2DO (Bartley), NRR EO (Lee), IRD (McDermott), DHS (Vestal), and FEMA (Burckhardt). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-11-22
45514 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2009-11-21 22:45 | 2009-11-22 01:13 | 2009-12-18 | RADIATION RELEASE IN CONTAINMENT ASSOCIATED WITH STEAM GENERATOR REMOVAL "This event is being reported via the ENS to the NRC Operations Center within four hours after notifications were made to the Pennsylvania Emergency Management Agency and local counties for an event of potential public interest. This notification was made at 22:45 on November 21, 2009, after the occurrence of an event related to the safety and health of onsite personnel for which a press release has been made. The press release was made following the event of potential public interest notifications. This report is being made under 10 CFR 72.75(b)(2). "At approximately 16:00 on Saturday November 21, 2009, low levels of radiation activity were measured on radiation monitors installed in the TMI-1 reactor building. Personnel were directed to immediately leave the reactor building until the source of the activity could be identified. Surveys directly outside of the reactor building construction opening indicated a slight increase in activity. Levels have returned to normal. No contamination was identified outside of the reactor building. Approximately 150 workers were monitored for exposure to the radiation activity. No worker approached or exceeded any exposure limits. The sources of the activity are believed to be from maintenance tasks related to cutting lines in preparation for removal of the 'B' Steam Generator." The licensee is still investigating the cause of the event but indicated that the radiation release is no longer in progress. Containment Ventilation is established to provide an inflow into containment to the extent possible (considering the openings in containment). The licensee contacted state and local authorities and the Pennsylvania Emergency Management Agency (PEMA). The licensee notified the NRC Resident Inspector. The licensee has also issued a press release. * * * UPDATE FROM NEFF TO TEAL AT 1824 EST ON 12/18/2009 * * * "This provides an update to notification EN #45514 that reported a non-emergency offsite notification for an event on November 21, 2009, at the Three Mile island Nuclear Station. "Updated news release and notifications to local, state and federal elected and regulatory officials were performed today, December 18, 2009, that provide an outage update as well as communication the results of analysis of Offsite Environmental Monitors following the November 21, 2009 event." The licensee notified NRC Region I. Notified R1DO (Barkley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-11-22
45513 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-11-21 | 2009-11-21 16:02 | 2009-11-21 | NOTIFICATION OF RESCUE SQUAD FOR OFFSITE INJURY OF HUNTERS "On 11/21/2009 at 14:27, two individuals arrived at the Surry Power Station Security Checkpoint with an accidental gun shot victim. The three individuals were hunting approximately one mile offsite when one individual was accidentally struck by gun fire. The other two individuals transported the injured individual to the Security Checkpoint at the station. Station personnel contacted the local Sheriff's Department, local Volunteer Rescue Squad, Virginia State Police, and Air Ambulance for assistance. Wounds do not appear to be life threatening, and the individual is being transported offsite via Air Ambulance. "The site NRC Resident has been notified. "This notification is being transmitted due to notification of other Government Agencies in accordance with 10CFR50.72(b)(2)(xi)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-11-21
45512 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-11-21 05:00 | 2009-11-21 05:58 | 2009-11-22 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED ELECTRICAL MAINTENANCE "On November 21, 2009, Fermi 2 [removed] the Technical Support Center (TSC) from operation to facilitate maintenance on the facilities' 480-volt AC power supply. This work affects TSC lighting, computers, and ventilation. During this work, which is expected to last over 8 hours, the TSC will be unavailable. In the event TSC activation is necessary, the Emergency Operations Facility (EOF) will be used for the TSC function. Activation and use of the EOF as a backup for the TSC is included in Fermi 2's Radiological Emergency Response Preparedness Plan. The Emergency Call Out System (ECOS) is designed to facilitate contacting TSC personnel to respond directly to the EOF in the event of an emergency. Fermi 2 is making this notification in accordance with 10 CFR 50.72(b)(3)(xiii). Fermi 2 will notify the NRC upon completion of this work. Fermi 2 will notify the NRC Resident Inspector." * * * UPDATE FROM GREG MILLER TO VINCE KLCO ON 11/22/2009 AT 0036 EST * * * The planned maintenance has been completed and the TSC has been restored as an Emergency Response Facility. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-11-21
45511 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-09-27 16:48 | 2009-11-19 16:45 | 2009-11-19 | OPTIONAL 60-DAY TELEPHONIC NOTIFICATION FOR INVALID SPECIFIED SYSTEM ACTUATION "[This is a] telephone notification made under 10 CFR 50.73(a)(2)(iv)(A) in lieu of submitting written Licensee Event Report. "On September 27, 2009, following reactor shutdown and cooldown for a planned refueling outage, 4160 VAC Safeguard Bus 5 was being restored to normal electrical lineup. Emergency Diesel Generator (EDG) A was powering Bus 5 following successful completion of planned testing to satisfy Technical Specification requirements for testing of EDG automatic start, load shedding, and restoration, initiated by a simulated loss of all normal AC power. "At 1648, while restoring Bus 5 to normal electrical lineup, breaker 1-503, Tertiary Auxiliary Transformer (TAT) supply to Bus 5, reopened after being closed. EDG A continued to supply Bus 5 without interruption. The following equipment tripped when breaker 1-503 opened: Residual Heat Removal (RHR) Pump A, Containment Fan Coil Units (CFCUs) A & B, Shield Building Ventilation (SBV) Fan A, and Service Water (SW) Pump A1. Auxiliary Feedwater (AFW) Pump A, Component Cooling (CC) Pump A, and SW Pump A2 were tripped and restarted by the blackout sequencer. All actuations were completed as designed and the components started and functioned successfully. AFW Train A had been properly removed from service for the EDG test and operated on minimum recirculation following AFW Pump A start. "The equipment actuations resulted from an invalid signal caused by an electrical jumper for the blackout signal remaining installed during Bus 5 restoration. The jumper continued to inject a simulated loss of voltage (blackout) signal, causing the TAT supply breaker opening and load shedding and sequencer operation as designed. "Inspection of breaker 1-503 was completed with no abnormalities noted. The jumper was removed and Bus 5 was restored to normal lineup. Corrective actions were initiated to revise the test procedure to more appropriately control bus restoration. "Although the actuating signal that caused this event was invalid and the electrical bus had been appropriately aligned for the EDG test, this event is being reported because of the multiple and diverse components that were inadvertently actuated." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-11-19
45510 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2009-11-19 13:00 | 2009-11-19 13:59 | 2009-11-19 | OFFSITE NOTIFICATION DUE TO LOW LEVEL RADIOACTIVE SPILL "The New York State Department of Environmental Conservation and other State and Local officials were notified today, November 19, 2009, that there had been a spill of low level radioactive material at an excavation site at the facility. "Workers were conducting planned modification activities, replacing a section of piping, when sediment fell from the pipe to the ground and localized water at the excavation site. Samples of the localized water in the excavation after the sediment had fallen in exceeded the limit of the site procedure for notifying State and Local officials for a groundwater spill. No elevated levels have been detected in the nearest plant monitoring well. Therefore, we have no indications that there has been a release beyond the site from this source. Cleanup activities are currently in progress. "The licensee notified the NRC Resident Inspector." The section of piping being replaced was between the plant storm drain system and the discharge canal. The radioactive material was identified as Cs-137 but was not quantified at the time of this report. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-11-19
45509 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-11-18 08:30 | 2009-11-19 08:58 | 2009-12-22 | AGREEMENT STATE REPORT INVOLVING A STOLEN/RECOVERED TROXLER MOISTURE DENSITY GAUGE The following information was received via email: "At approximately 0830 on the morning of November 18, 2009, the RSO (Radiation Safety Officer) of Terracon Consulting Inc. (ARK-0820-03121) reported the theft of a Troxler 3440 Moisture Density gauge (SN#27140) from a construction site at the Two Pines landfill in Jacksonville, Arkansas. The gauge contained an 9 mCi Cesium-137 source and a 44 mCi Americium-241/Beryllium source. According to the RSO, the gauge had been secured with two independent chains to the rear rack of an all terrain vehicle (ATV), which in turn was locked inside of a cargo shipping container after work was halted on November 17, 2009. When personnel arrived at the construction site at approximately 0700 on the 18th, they noted that the lock on the cargo container had been cut and that the ATV and gauge were missing. Local and state law enforcement were notified. "At approximately 1340 on that same day, the Jacksonville Police Department reported that the gauge had been found along a roadside in Pulaski County. The gauge was examined by Department personnel and appeared to be undamaged, wipes tests were taken to further verify that the sources were not leaking. Terracon personnel were then allowed to take possession the gauge. "The [Arkansas Department of Health] will keep this incident open pending the receipt of a report and corrective actions from the licensee." Arkansas Incident Number: 11-09-01 * * * UPDATE FROM ROBERT PEMBERTON TO DONG PARK AT 1621 ON 12/22/09 * * * The following report was received via e-mail: "The following are the findings of the Arkansas Department of Health, Radioactive Materials Program, concerning event Number 45509 involving the theft and recovery of a Troxler 3440 moisture/density gauge from Terracon Consulting Inc. From information provided by Terracon Consulting Inc. the Department has determined that the gauge was apparently undamaged and the sources were not leaking. The Department has received corrective actions from Terracon Consulting Inc., dated December 18, 2009, and found them to be adequate. The Department considers this incident to be closed." Notified R4DO (Walker), FSME (Villamar), and ILTAB (e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | PAR |  |  |  |  | 0 | 2009-11-19
45508 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-12-12 | 2009-11-18 15:09 | 2009-11-18 | AGREEMENT STATE REPORT - BACKSCATTER PROBE READING ERRATICALLY The following report was received via e-mail: "On December 14, 2008, the Agency received notification that while restarting the line production the operator noted that a NDC model 103 backscatter probe was reading erratically. An operator standing on the first leveled looking up at the probe, which was located on the second level thought he saw a piece of tape on the end of the probe. Upon closer inspection, the operator believed that the probe had been damaged and requested assistance. The facility Radiation Safety Officer had the area around the probe evacuated. Further investigation determined that the probe shutter was in the closed position. The probe was removed by the facilities Hazardous Material Team and placed in a locked storage location. A technician from the manufacturer inspected the probe and determined that the shutter mechanism was operating properly. He removed the shutter and installed it on a spare probe. The old probe was sent to the manufacturer for inspection and repair. The manufacturer inspected the probe and performed a leak test of the source. The source did not appear to have been damaged, and the leak test results were satisfactory. The probe was returned to the facility after some routine repairs." Texas Incident: I-8463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 0 |  | OTH | AGR |  |  |  |  | 0 | 2009-11-23
45507 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-10-15 | 2009-11-18 14:46 | 2009-11-18 | AGREEMENT STATE REPORT - DENSITY GAUGE SHUTTER STUCK IN OPEN POSITION The following report was received via e-mail: "On November 26, 2007, the Agency received a letter from the licensee notifying them that while conducting a routine inventory and shutter inspection of a density gauge, the shutter was found stuck in the open position. The licensee contacted a vendor to repair the gauge. The vendor determined that a bolt on the shutter had broken preventing the shutter from closing. The shutter could not be repaired. The shutter is normally open so there was no increased risk of additional radiation exposure to the workers at the facility. A new device was ordered and the old gauge was disposed of when the new one was installed. "The gauge was an Ohmart/VEGA Corporation model SH-F1, serial number 8622 K containing a 50 milliCurie Cesium (Cs) - 137 source." Texas Incident: I-8456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-11-23
45506 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-04-12 | 2009-11-18 13:52 | 2009-11-18 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE SHUTTER FAILURE The following report was received via e-mail: "On April 19, 2007, the Agency was notified of a generally licensed device malfunction. The general licensee reported that the 'on-off' shutter mechanism failed on a frame beta gauge, designed for measuring mass per unit area of thickness of sheet material. The device was removed from operation, repaired, and put back into operation. The failure was determined to be caused by the lack of maintenance on the device. "The device is a General License device, a Frame Beta Gauge, Model BG-V, serial no. 940331001, with two Krypton-85 sources of 0.2 Ci each, Model KAC.D3, serial no's. KS429 and KS430." Texas Incident: I-8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-11-23
45505 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-11-17 20:34 | 2009-11-18 03:19 | 2009-11-18 | INADVERTENT HPCI ISOLATION "On 11/17/09 a 2034 [CST], while performing 2-SR-3.3.6.1.3(3DFT) HPCI Steam line space high temperature functional test, HPCI isolated due to B2 and A1 PCIS Channels picking up. A1 was the channel under test at the lime the isolation occurred. Following the immediate investigation it appears the isolation was due to test equipment configuration failure. This test equipment is still under investigation. "This incident is reportable as an 8-hour ENS notification under 10CFR 5O.72 (b)(3)(v) as 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: "d. Mitigate the consequences of an accident.' "It also requires a 60 day written report in accordance with 10CFR50.73(a)(2Xvii). "The NRC Resident Inspector has been notified. "SR number associated with this report: 93270." The HPCI system has been restored to operable status. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-11-18
45504 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2009-11-17 17:40 | 2009-11-17 21:35 | 2009-11-18 | LOSS OF NATIONAL WEATHER SERVICE TONE ALERT RADIO SYSTEM "At 1819 on November 17, 2009, with James A. FitzPatrick (JAF) nuclear Power Plant operating at 100% power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 1740. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8-hour reporting criteria per 10 CFR 50.72(b)(3)(xiii). "The National Weather Service is currently working to determine the cause of the failure and time frame for system restoration. "The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local law enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program and the NRC Resident Inspector has been briefed and the state PSC will also be notified." See EN# 45503 for Nine Mile Point Nuclear Plant. * * * UPDATE FROM THOMAS YURKON TO JOE O'HARA AT 0456 ON 11/18/09 * * * "Notified by Oswego County 911 operator that the Tone Alert radios were restored at 0318 on 11/18/09." The NRC Resident Inspector was notified. Notified R1DO(McKinley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-11-17
45503 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2009-11-17 17:40 | 2009-11-17 21:20 | 2009-11-18 | LOSS OF NATIONAL WEATHER SERVICE TONE ALERT RADIO SYSTEM "At 1819 on November 17, 2009, with Nine Mile Point Unit 1 and Unit 2 operating at 100% power, [Nine Mile Point was] notified via the RECS Line by Oswego County Warning Point, that the National Weather Service Tone Alert Radio System for Nine Mile Point and James A. Fitzpatrick Nuclear Power Plants has been out of service for greater than 1 hour as of 1740 on 11/17/2009. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the Nine Mile Point and James A. Fitzpatrick Nuclear Power Plants. This failure meets the NRC 8-hour reporting criteria per 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens, which also function as part of the Public Prompt Notification System, remain operable. "The loss of the National Weather Service Tone Alert Radio System constitutes a significant loss of emergency off-site communications capability. Compensatory measures were verified to be available should the Prompt Notification System be needed. This includes the use of the hyper-reach system, which is a reverse 911 feature, available from the Oswego County 911 center. Local law enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the site's corrective action program and the NRC Resident Inspector has been notified." See EN# 45504 for James A. Fitzpatrick Nuclear Plant. * * * UPDATE FROM DON SHEEHAN TO JOE O'HARA AT 0432 ON 11/18/09 * * * "At 0318 on November 18, 2009, notified via the RECS [Radiological Emergency Communication System] Line by Oswego County Warning Point that the National Weather Service Tone Alert Radio System for Nine Mile Point and James A. Fitzpatrick Nuclear Power Plants has been returned to service." The NRC Resident Inspector has been notified. Notified R1DO(McKinley) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-11-17
45502 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-10-26 | 2009-11-17 13:50 | 2009-11-17 | AGREEMENT STATE REPORT - MEDICAL EVENT The following report was received via facsimile: "Patient liver is being treated by thera sphere procedure. First dose was intended to be for left lobe but was delivered to right lobe on 10/26/09. The second treatment was going to be for the right lobe. The window for the right lobe dose was 90-115 grays, but what actually delivered was 18-51 % low. Error was discovered 10/30/09. The patient will be retreated to bring dose up to required level. The patient and doctor have been notified. In the future the radiologist will submit a written statement on the treatment to be preformed before it is accomplished. Licensee will submit a written report. No further action will be taken on this incident." Source: 1.27 GBq Y-90 Florida Incident: FL09-077 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-11-23
45501 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-11-12 | 2009-11-16 15:53 | 2009-11-16 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE DURING RADIOGRAPHY The following report was received via facsimile: "On November 13, 2009 the RSO [Radiation Safety Officer] for Owensby & Kritikos (O & K), contacted LDEQ [Louisiana Department of Environmental Quality] to report an excessive exposure. O & K had a radiography crew x-raying a pressure vessel. The radiographers believed that they had cranked the source in the camera. One of the radiographers went to the camera without a survey meter to remove the source guide tube. He was trying to put the safety plug on the end of the camera, but it would not go on. At this point, he realized that the source was not in the shielded position. Instead of roping off the area and calling the RSO per their procedures, they got the source in the shielded position themselves. This occurred on November 12, 2009 and the radiographers did not tell the RSO until November 13, 2009. Both of the pocket dosimeters were off scale. The radiographers said they where wearing their rate alarm meters. The personnel monitors were sent to Landauer for emergency processing. One of the radiographers had a dose of 5.57 rem for November with a year dose of 6.67 rem. The other radiographer had a November dose of 0.45 rem and a year dose of 1.00 rem. At this time, LDEQ believes these exposures to be true exposures to the radiographers. The crew had an AEA 660B camera, s/n B1495, that had a 79 Ci Ir-192 source, s/n 57338B. The last leak test was on October 12, 2009. LDEQ has begun an investigation and will report any new information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-11-19
45500 | 0 | WARTSILA FRANCE S.A.S |  |  |  |  | 2009-11-16 | 2009-11-16 14:27 | 2009-11-16 | PART 21 NOTIFICATION - POTENTIAL FAILURE IN EMERGENCY DIESEL GENERATOR BEARINGS The following report was received via facsimile: "PART 21 involving Wartsila type SACM UD45 Emergency Diesel Generating [EDG] set big end bearings installed in the US nuclear power stations of Constellation Energy at Calvert Cliffs and Xcel Energy at Prairie Island. "COMPONENT: Big end bearing DLT141885 all batches & DLT123351 batches A2, F2, J2 on Wartsila type SACM UD45 [EDG] sets. "DISCUSSION: Three of four incidents which have been reported to Wartsila France are related to UD45 diesel engines operating at 1500 rpm in nuclear installations. Big end bearing damage can result in non-availability of the diesel engine. Wartsila France has been working on the root cause analysis after the first reported failure and has given an overall recommendation in October 2009 regarding the risks of using the above mentioned big end bearings on diesel engines running at 1500 rpm (50 Hz applications). An additional technical evaluation has been issued in November 2009 after testing a new big end bearing. The evaluation has determined that this is potentially a reportable defect as defined by 10CFR21. "AFFECTED USERS: UD45 engines "CORRECTIVE ACTION: Being unable to predict the occurrence of such a random event, Wartsila France has advised its customers to: identify the [EDG] sets equipped with big end bearings above referenced in COMPONENT, stop the utilization of big end bearings above referenced in COMPONENT, replace all above referenced in COMPONENT big end bearings by a new reference PAAG129161 which has been qualified after extensive running tests on a 1500 rpm engine. Wartsila has not recorded such a situation on other UD45 diesel engines running at a lower speed of 1200 rpm (60 Hz applications) which are installed as Emergency Generating sets in nuclear power plants. Nevertheless Wartsila France recommendation if components have also been identified in 1200 rpm units installed in US nuclear power plants or if such components are held in stock, is to replace them with the new reference big end bearing PAAG129161." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2009-11-16
45499 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2009-11-15 22:42 | 2009-11-16 02:24 | 2009-11-16 | MANUAL REACTOR TRIP DUE TO MAIN GENERATOR OIL LEAK "At 2242 [EST] on 11/15/09, the reactor was manually scrammed from 100% power due to a large oil leak on the main generator seal oil system. Condenser vacuum was broken immediately following the reactor trip, and the main turbine stopped rotating at 2324 [EST]. Following the reactor trip, the 'B' steam generator Main Steam Isolation Valve (MSIV) failed to fully close on demand, but was closed due to field actions at 2303 [EST]. The reactor remained stable at NOP/NOT following the reactor trip. Offsite power remained available throughout the event. "This condition is being reported as actuation of the reactor protection system in accordance with 10CFR 50.72(b)(2)(iv)(B)." All control rods fully inserted and decay heat is being removed through the S/G relief valves to the atmospheric dumps. No known primary to secondary leakage exists. The plant remains stable in Mode 3. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-11-16
45498 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2009-11-15 08:26 | 2009-11-15 08:57 | 2009-11-15 | UNIT 2 DECLARED AN UNUSUAL EVENT DUE TO A LOSS OF ANNUNCIATORS At 0826 EST, Millstone Unit 2 declared a NOUE, due to a loss of power to the control room main board annunciators. Power was lost to the non-vital power supply, VR-11&21, during heater drain pump post maintenance testing, which caused the loss of power to the main control board annunciators. Charging and letdown systems are secured. Additional watchstanders were stationed during the annunciator outage. Power was restored to the main control board, and the licensee is in the process of terminating the NOUE. The NRC remained in Normal Mode. The NRC Senior Resident Inspector has been notified. The State of Connecticut has been notified. * * * NOTIFIED BY BRIEN STRIZZI TO DONG PARK AT 0922 EST ON 11/15/09 * * * Millstone Unit 2 terminated the NOUE at 0859 EST after power was restored to the main control board annunciator. Notified R1DO (Cahill), R1RA (Roberts), IRD MOC (Grant), NRR ET (Boger), NRR EO (Bahadur). The NRC Senior Resident Inspector has been notified. The State of Connecticut has been notified as well as DHS and FEMA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  |  | Hot Standby | Hot Standby |  | Hot Standby | Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-11-15
45497 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-11-14 07:30 | 2009-11-14 18:43 | 2009-11-18 | FIRE IN PROCESS GLOVE BOX "On Saturday November 14, 2009 at approximately 0730 there was a heated high pressure release from the 5A/5B UF6 cylinder in the CDL facility Sublimation Station 3. At the time of the upset, the operators were in the process of preparing the cylinder for sublimation. They had just satisfactorily performed the valve leak checks (SOP 409 Section 56 step 5.3) and were performing the cylinder pressure test (SOP 409 Section 56 step 5.4). The cylinder was not being heated. The upset occurred when the cylinder valve was opened (step 5.4.7) to vent the cylinder to column 1D01. The release ruptured the connective teflon tubing that was enclosed in braided stainless steel. When flame was observed the operator actuated the CO2 release valve and extinguished the flame. The subsequent damage appears to be limited to: 1). Braided teflon tubing, 2). Singed area on lexan cover of the enclosure, 3). Possible leak on the inlet and outlet side of the eductor. "Of note, column 1D01 was filled with DI water in preparation for startup. The solution should have a clear appearance but has been discolored by the upset. It appears to have been blackened, possibly from burning Teflon. "As of 1200 PM the following actions have been taken to place the system in a safe condition: 1. Building 333 personnel were notified of the event and the 301/333 door was posted with caution. 2. Immediate area is roped off. 3. All involved personnel have received incident report forms for completion. 4. A firewatch has been posted (ISA requirement as cylinder contains >7.2 kgs UF6) 5. Supervisor verified valves on UF6 cylinder are shut. 6. Nasal smears taken on all affected personnel (7 dpm max; below action limit of 90). 7. High volume air sample taken with no elevated activity identified. 8. Area sampled for HF with a Draegor Tube (negative). 9. Verified no increase on room CAM [continuous air monitor]. 10. Subsequent NCS [nuclear criticality safety] evaluation identified no concerns or NCS reportability issues. 11. System has been locked out of service with operational locks and appropriate signage placed on sublimation station #3. 12. Solution on the floor from the enclosure P traps has been cleaned up. 13. The enclosure overflow traps have been filled. 14. The CO2 gage has been verified functional and operations personnel are in the process of replacing the spent CO2 cylinder. 15. NDA has scanned the NaF trap (no elevated levels found). 16. Plant Superintendent took photos of equipment damage. 17. HP verified no damage to gloves. 18. Sublimation station #1 & 2 have been tagged 'Not Authorized for Use.' 19. All proper notifications made. 20. Plant Superintendent is in the process of developing a timeline of events. "No actual exposures occurred to the workers, the public, and environment. Potential UF6 exposure to workers. However, no loss of containment occurred. "No other structures, systems, or equipment components in the area were affected. Safety systems are operational. "All sublimation stations have been taken out-of-service pending investigation results. "The event is terminated. No declared emergency class. "Notifications were made to the local county Emergency Management Coordinator and the Town of Erwin Fire Department. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2009-11-19
45496 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2009-11-12 15:30 | 2009-11-13 10:30 | 2009-11-14 | FAILURE TO FULLY RETRACT THE SOURCE OF A RADIOGRAPHY CAMERA Technicians were performing radiography at the Kuparuk Oil Field in Prudhoe Bay, Alaska when the source in an Industrial Nuclear Corporation (INC) IR-100 radiography camera, serial number 6643 was unable to be fully retracted. This was caused by a frozen lock on the device which occurred due to weather conditions of blowing snow and freezing rain. A certified technician serviced the lock. The lock was returned to fully functional condition and the source was returned to the safe and secure position. The device has a 101 Ci Ir-192 source. No personnel over exposures occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-11-14
45495 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-11-13 06:58 | 2009-11-13 09:22 | 2009-11-13 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-11-13
45494 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-11-12 17:11 | 2009-11-12 22:36 | 2009-11-12 | HPCI INOPERABLE DUE TO EXCESSIVE WATER IN STEAM DRAIN "The HPCI [High Pressure Coolant Injection] system was declared inoperable after completion of a scheduled surveillance due to an excessive amount of water in the turbine exhaust line. The line was being drained in response to the alarm 'HPCI TURB EXH DRAIN POT LEVEL HIGH', indicating that there was a high level in a drain pot attached to the turbine exhaust line. An investigation is in progress to determine the source of the water in the turbine exhaust line. "This event is reportable within 8 hours in accordance with 10CFR 50.72(b)(3)(v) as an event or condition that at the time of discovery could have prevented the fulfillment of a safety function. It also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(vii) "The NRC Resident Inspector has been notified. "SR number associated with this report: 91546." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-11-12
45493 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-11-12 19:00 | 2009-11-12 22:00 | 2009-11-12 | NOTIFICATION TO US COAST GUARD AND COMMONWEALTH OF VIRGINIA OF HAZARD TO NAVIGATION "Surry Power Station maintenance activities at the James River intake structure were supported with a barge from Crofton Industries using stop logs (referred to as caissons, each with dimensions of 24'x6'x3'and weighing 11,000 pounds empty) to seal water ingress into intake bays. On November 12, 2009, due to the potential for damage from high winds and tide, the barge and four of the caissons were towed by tug boat from the intake structure, across the James River, to Fort Eustis. At 1650 hours, mid-way across the river, one of the caissons broke free from the tug. The tug operator attempted to secure the partially submerged caisson, but was unsuccessful. The tug operator noted the location and completed the transfer of the barge and caissons to Fort Eustis. "At approximately 1900 hours, Crofton Industries informed Surry Power Station that in accordance with the Marine Safety Office Notification Procedure, they communicated with the US Coast Guard, notifying them of the incident and the approximate location of the caisson. In addition, at 2030 hours, Surry made a courtesy notification of the incident to the Virginia Department of Emergency Services. This report is being submitted due to the notification of other government agencies under 10CFR50.72(b)(2)(xi). In addition, the Site NRC Resident was also notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-11-12
45492 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-11-12 11:15 | 2009-11-12 16:09 | 2009-11-12 | VIOLATION OF A NUCLEAR CRITICALITY SAFETY CONTROL "At 1115 CST on 11/12/09, abandoned cell piping was reported in C-331 and C-335 cell housings. The 16-inch abandoned piping is from the cell recycle line that was replaced in the mid 1970s. NCS [Nuclear Criticality Safety] controls require that equipment openings with unknown uranium deposits shall be covered with water-proof covers that are fire resistant. Since the piping contains an unknown uranium mass, and was discovered without water-proof covers, the NCS control was violated. "Since moderation is the primary criticality control, and where double contingency cannot be re-established within 4 hours, this is being reported to the NRC as a 4-hour Event Report in accordance with NRC BL 91-01 Supplement 1. "The NRC Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-09-2781; PGDP Event Report No. PAD-2009-19. "Safety significance of events: Although the NCS control to cover the pipe openings was violated, it was not exposed to a liquid moderator. The geometry of the pipe is safe for a maximum enrichment that may be in the pipe. During the plant modifications that replaced the cell recycle lines, the maximum plant enrichment was 2.0 wt. % U235. There are no indications, based on quarterly NDA scans, that the piping contains greater than a safe mass of uranium. Therefore, the safety significance of the event is low. "Potential criticality pathways involved: The maximum plant enrichment at the time the piping was in operation was a maximum 2.0 wt. % U235. The piping is contained in housing without fire suppression. The single parameter pipe diameter for that enrichment is greater than 16 inches. In order for a criticality to be possible, the pipe would have to contain greater than a critical mass. A large amount of moderator would have to enter the horizontal pipe opening. Greater than a critical mass would then have to be washed from the pipe due to the unlikely moderator release at the pipe opening. The washed material would then have to accumulate in an unsafe geometry. "Controlled parameters: Moderation. "Estimated amount, enrichment, form of licensed material: The assay of any material is less than or equal to 2.00 wt. % U235. "Nuclear Criticality safety control(s) or control systems(s) and description of the failures or deficiencies: The first leg of double contingency relies on control of moderation. Moderator intrusion associated with sprinkler activation is controlled by limiting fire sprinkler head activation temperatures at the ceiling and bypass heights. The analysis also determined that significant moderator intrusion into open fissile piping due to inadvertent spills, RCW/oil line leaks, or other mechanism is unlikely. These controls were not violated and an unlikely moderator release event has not occurred at the pipe opening. The second leg of double contingency is also based on moderation. Piping exceeding 10.25 inches that contains an unknown or greater than safe mass deposit is required to have openings covered with fire resistant waterproof covers. Since the piping is nominal 16 inches in diameter, contains an unknown uranium mass, the NCS control was violated. Since the openings are not covered resulting in a loss of NCS control and there are two controls on one parameter, the process condition was not maintained. "Corrective actions to restore safety systems and when each was implemented: Control access to the area. Exempt the pipe from NCS controls based on enrichment determination, cover the pipe openings, or quantify the uranium mass in the pipe." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2009-11-12
45491 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2009-11-11 15:00 | 2009-11-12 11:47 | 2009-11-12 | INCOMPLETE DOCUMENTATION OF CRITICALITY SAFETY CONTROLS IN INTEGRATED SAFETY ANALYSIS SUMMARY "During a GNF-A ongoing review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was discovered at 3pm yesterday (11/11/09) that there may be an incomplete list of criticality safety controls associated with the Pellet and Rod Load Fabrication areas in the ISA Summary. "At 7pm, it was determined that the list of Items Relied On For Safety (IROFS) was incomplete and the affected equipment was shut down pending revision of the ISA to document IROFS for these processes. Notwithstanding the documentation deficiency, the controls associated with moderator intrusion and geometry remained in place, functional, and maintained with appropriate management controls. "While this discovery did not result in an unsafe condition, it is being reported on 11/12/09 pursuant to the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours. "Safety Significance of Events: Low safety significance - All process criticality safety controls remained intact and functioning for this processes. "Safety Equipment Status: Pellet and Fuel Load fabrication areas are shutdown and will remain shutdown until the ISA review is completed. "Status of Corrective Actions: Pellet and Rod Load Fabrication areas will remain shutdown pending final investigation results and identification of additional IROFS." The licensee notified NRC Region 2 Inspector (Crespo) and will notify state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2009-11-12
45490 | -1 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-11-12 08:11 | 2009-11-12 10:05 | 2010-04-22 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM SCOTT BUTLER TO JOE O'HARA AT 1704 ON 11/12/09 * * * The vulnerability to the safeguard system has been corrected. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. Notified R3DO(Orth) and ILTAB (Whitney) * * * RETRACTION AT 1701 ON 4/22/2010 FROM RYAN WITCOTSKI TO MARK ABRAMOVITZ * * * "It has subsequently been determined that the November 12, 2009 event is a security loggable event, but not reportable. "Evaluation of this event notification is documented in the corrective action program. "The NRC Resident Inspector has been notified of this retraction." Notified the R3DO (Skokowski), ILTAB (English via e-mail), and 73.71 Group (via e-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-11-12
45489 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-11-11 17:43 | 2009-11-11 22:34 | 2009-11-11 | MANUAL REACTOR SCRAM AFTER A TURBINE HYDRAULIC FLUID LEAK "On November 11, 2009, at 1743 CST the reactor was manually scrammed following a manual trip of the main turbine due to an un-isolable leak on the Turbine High Pressure Fluid System (TGF) governor valve 3. Initial power level when the leak was identified was approximately 70%. Power was lowered commencing at 1405 in accordance with shutdown procedures. The reactor operator scrammed the reactor at 17:43 from approximately 15% power when directed by the shutdown procedure to place the reactor in a condition to support repairs to the TGF system. In preparation for the scram, level was raised to the range specified in the shutdown procedure (approximately 46 inches). Following the scram, reactor vessel water level lowered to approximately 15 inches on the narrow range instruments, and was subsequently recovered to normal post scram range (approximately 40 inches) using the reactor feedwater system. All control rods fully inserted. No group isolations occurred since level did not reach the isolation setpoint (3 inches). At 1920, the inboard MSIVs were manually closed to stabilize plant cool down and maintain the plant in mode 3. The main condenser remained available throughout the evolution and condenser vacuum is currently being maintained by the mechanical vacuum pumps. Pressure is being controlled using the steam line drains to the main condenser. "All equipment operated as expected and there were no difficulties encountered during the evolution. "The TGF System has been secured and is in the process of being tagged out for repair. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) due to a non planned reactor scram while critical. The licensee has notified the NRC Resident Inspector." The plant is in its normal shutdown electrical lineup. | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-11-11
45488 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-11-11 12:38 | 2009-11-11 18:41 | 2009-11-11 | DEGRADED TSC EMERGENCY VENTILATION "At 1238 hours on November 11, 2009, during performance of the Technical Support Center (TSC) ventilation pressure test, it was determined that the TSC could not be maintained at a positive pressure in the emergency mode due to the failure of an outside air intake damper to fully close. At this time, troubleshooting is being performed on the damper. "If an emergency is declared requiring TSC activation, the TSC will be staffed and activated using existing procedures. In the event TSC evacuation is warranted due to radiological conditions, key Emergency Response Organization members would be relocated in accordance with existing procedures. "This event is reportable per 10 CFR 50.72 (b)(3)(xiii) given the impact on the emergency response facility. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-11-11
45487 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-11-10 | 2009-11-10 07:36 | 2009-11-11 | LOSS OF TSC DUE TO PLANNED MANTENANCE "At 0425 on 11/10/09, the Technical Support Center (TSC) was removed from service for planned maintenance. This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(xiii). Maintenance will include replacement of a heating element in the HVAC system and replacement of an iodine radiation sampling instrument. The total duration of the maintenance activities is expected to be approximately 20 hours. Direction has been provided to the ERO (Emergency Response Officer) that should the TSC need to activated, TSC staff should report to the main control room in accordance with established procedures. No other emergency response facilities are impacted by this maintenance work. The [NRC] Resident Inspector has been notified." * * * UPDATE FROM FRED SCHILL TO JOHN KNOKE AT 1845 EDT ON 11/11/09 * * * Licensee stated that the Technical Support Center (TSC) is now back in service. Licensee has notified the NRC Resident Inspector. Notified R4DO (Jeff Clark) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-11-10
45486 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-11-07 | 2009-11-09 16:54 | 2009-11-09 | AGREEMENT STATE REPORT - IRRADIATOR SAFETY INTERLOCKS BYPASSED A fuse blew during operation of an irradiator facility in Broken Bow, NE. This affected: the source up or down indication, the roof plug switch, the high temperature sensor, and the source movement light. The system could not be reset manually with the key. To verify the source was in the shielded position, an operator was sent to the roof and verified that there was no slack in the cables and the position of the cables indicated the source was in the shielded position. The interlocks were bypassed and an operator entered the cell. It was determined that there was a blown fuse and faulty wiring which were replaced. Operators did not receive any radiation dose from this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-11-12
45485 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2009-08-28 | 2009-11-09 10:50 | 2009-11-09 | AGREEMENT STATE REPORT - BRACHYTHERAPY PATIENT RECEIVED MORE THAN PRESCRIBED DOSE The following information was received via NMED report #090706: "Hardin Memorial Hospital reported that a patient received 26.9% more dose than prescribed during prostate seed implant procedure on 8/28/09. The patient received I-125 brachytherapy seeds with a total activity of 1.26 GBq (34.054 mCi) instead of the prescribed 0.99 GBq (26.825 mCi). It is believed that the medical physicist calculated dose to the prostate using air kerma instead of milliCurie. All physicians and the patient have been notified of the mistake." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2009-11-13
45484 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-11-07 07:25 | 2009-11-07 12:57 | 2009-11-07 | MANUAL REACTOR SCRAM DUE TO A MAIN TURBINE DIGITAL ELECTRO-HYDRAULIC CONTROL SYSTEM LEAK "At 0725 hours, a manual scram was inserted due to a Main Turbine Digital Electro-Hydraulic (DEH) control system leak and anticipated turbine trip on loss of DEH tank level. Initial investigation identified a DEH leak at the area of the Quad-Voter hydraulic trip subsystem on the high pressure turbine. "All rods fully inserted, main steam isolation valves (MSIVs) remained open, no safety/relief valves (SRVs) opened, and all other safety systems operated as designed. Reactor water level was restored and maintained with the Reactor Feedwater and Condensate systems during the post-scram transient within normal operating bands. Reactor pressure was controlled using main steam drain lines. A normal cooldown to the condenser is in progress. Offsite power is available. All three emergency diesel generators are operable and available." The plant was operating at 52% for planned maintenance. All safety systems remain available. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 52 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-11-07
45483 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2009-11-06 22:02 | 2009-11-06 23:36 | 2009-11-06 | MANUAL REACTOR TRIP DUE TO FEED REG VALVE CLOSURE "A Manual Reactor Trip was initiated due to closure of Main Feedwater Regulating Valve 'A' with Steam Generator 'A' Level at 35% narrow range and lowering with a Steam Flow / Feed Flow mismatch present. Both Motor Driven Auxiliary Feedwater Pumps (MDAFW) and the Steam Driven Auxiliary Feedwater Pump (SDAFW) auto-started as required based on low Steam Generator Water Levels. All systems responded normally and plant operators have stabilized the unit in Mode 3." There were no complications. All rods inserted during the trip. Decay heat is being removed via steam dumps to condensers. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-11-06
45482 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-11-06 19:30 | 2009-11-06 23:22 | 2009-11-06 | MANUAL REACTOR SCRAM DUE TO AN UNISOLABLE LEAK ON THE TURBINE HIGH PRESSURE FLUID SYSTEM "On November 6, 2009, at 1930 CST the reactor was manually scrammed following a manual trip of the Main Turbine due to an un-isolable leak on the Turbine High Pressure Fluid System (TGF). The RO [Reactor Operator] scrammed the reactor when [reactor vessel water] level lowered below 12 inches on the Narrow Range Instruments. All Control Rods fully inserted and a Group 2 Isolation occurred when level reached 3 inches on the Narrow Range Instruments. Reactor level lowered to approximately 22 inches on the Wide Range Instruments and was recovered in a slow and deliberate manner in order to minimize the effect on the cool down rate because of low levels of decay heat in the fuel. The Reactor Feed System was used to initially recover level. At 2043, the plant was in Mode 3 with the inboard MSIVs manually closed and level and pressure being controlled by RCIC. The MSIVs were closed to minimize the cool down rate and RCIC was started manually for level and pressure control. The Main Condenser remained available throughout the evolution and condenser vacuum is currently being maintained by the Mechanical Vacuum Pumps. "The Group 2 Isolation was verified with no discrepancies and was reset at approximately 2010. "All equipment operated as expected and there were no difficulties encountered during the evolution. "The TGF System has been secured and is in the process of being tagged out for repair." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-11-06
45481 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-11-06 | 2009-11-06 23:27 | 2009-11-06 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following notification was received from the state via e-mail: "A Troxler moisture density gauge (model 3411, serial # 7078) was stolen from an open pickup truck sometime between 7 am and noon on 11/6/09. The gauge was taken out of the transportation container, which was secured in the back of the open pickup truck. The RSO does not know if the transportation container was locked. "The lost gauge was reported to the Riverside Sheriff's Department. The RSO was informed that a reward should be offered for return of the gauge. He indicated he will discuss posting of a reward with the company owner. " THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-11-11
45480 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2009-11-03 | 2009-11-06 15:03 | 2009-11-06 | AGREEMENT STATE REPORT INVOLVING LEAKING IRRADIATOR SOURCE New York does not publish the name, address or license number of its licensees in incident reporting to the NRC. The following information was received via e-mail: "Event description: Best Theratronics was performing a security upgrade (hardening) on an AECL Gamma Cell 40 irradiator, containing AECL Model Number C-161 cesium-137 sources, and discovered radioactive contamination indicating a 'leaking' source. Coincidently, [Department of Health representatives] arrived at the licensee's facility for a planned site visit at noon on 11/03/09, and were able to assess the situation with the vendor and Radiation Safety Officer (RSO). "The engineers noticed that one of the pneumatic source drive mechanisms moved noticeably slower than the other. They removed the pneumatic drive assemblies and manually moved the source drive rods. They noted excessive resistance to movement and noticed corrosion (rust) on the source rod. They wiped the rusty material and measured the wipe with a thin-window GM detector, which indicated radioactive contamination. Further sample analysis confirmed removable cesium 137 (isotopic analysis) in excess of the leak test limit. The contamination is limited to the areas of the source drive components only. Radiological surveys were performed on personnel, tools, the room, etc. with negative findings. In consultation with the service engineers, the RSO, and [Department of Health representatives], the decision was made to abandon the hardening procedure. The unit was reassembled and taken out of service. DOH will work with the licensee to determine what options, if any, exist for disposal of the unit. DOH will also follow-up with Best Theratronics in regard to their procedures for PM (i.e., is leak testing performed in areas such as the drive mechanism during routine PM service or during hardening). Also, we will inquire about actions such as a notice to owners and/or assessment of other licensee's units, etc. "Contamination on both source rods may indicate a generic source integrity issue." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2009-11-11
45479 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-11-06 | 2009-11-06 14:31 | 2010-01-14 | AGREEMENT STATE REPORT - LOST AND RECOVERED TROXLER MOISTURE DENSITY GAUGE On November 6, 2009, the State of Texas reported that a Troxler moisture density gauge was lost and recovered by the Troxler Electronic Laboratories, Inc. The event occurred approximately one to two years ago. The density gauge was recovered two days after it was lost. The State of Texas will provide updates as more information is available. The gauge contained an 8 mCi Cs-137 and a 40 mCi Am/Be-241 source. Texas Incident # I-8686 * * * UPDATE FROM ART TUCKER TO CHUCK TEAL AT 1730 EST ON 1/14/10 * * * "On November 4, 2009, while conducting a routine inspection, an agency inspector found an event that involved a Troxler moisture/density gauge model # 4640 containing one 8 millicurie Cesium (Cs) - 137 source, which was lost during shipment and returned to the licensee the next day, intact and with no damage. The gauge did not contain an Americium source. The case did not have any scuff marks on it. Neither the licensee or the shipper had notified the agency of the event. They believed that it was not reportable since there was no chance that someone could have received an exposure from it and it was lost for only one day. The licensee also believed that the shipper would be required to make any required notifications. The licensee was informed that they would have been required to notify the agency of an event [and it] would have been reportable. The licensee stated that they believed the gauge had fallen off of their truck. The truck used had a faulty latch mechanism on the door. The driver received additional instruction on securing the door." Notified FSME (Lewis) and R4DO (Hagar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-11-11
45478 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-11-06 | 2009-11-06 13:26 | 2009-11-06 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER MALFUNCTION The following information was obtained from the State of Texas via email: "On November 6, 2009, the [State of Texas] was notified that the shutter on a Ronan Engineering level gauge containing 2,000 millicuries of Cesium (Cs) - 137 failed to operate properly. The gauge is installed on the top of a vessel that is 16 feet high. The vessel had been taken out of service and the Radiation Safety Officer (RSO) went to the location to perform a shutter operation check. He found that the shutter could not be fully closed. Dose rates in the area were normal. Lead shielding was placed in front of the gauge as shielding. The RSO believes that as many as four people may have entered the vessel while the shutter was not fully closed. The licensee intends to repair the gauge during their next scheduled outage. The RSO was not certain on what day the event occurred, but believed it was about two weeks ago. The licensee stated that he was not aware of the reporting criteria until he received a letter sent out by [the State of Texas] regarding the reporting requirements for this type of event. The licensee is continuing their investigation. Additional information will be provided as it is received." Texas Incident # I-8685. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-11-11
45477 | 0 | FLOWSERVE |  |  |  |  | 2009-11-06 | 2009-11-06 11:34 | 2009-11-24 | PART 21 REPORT - POTENTIAL FAILURE OF BONNET VALVE The following is quoted selectively from the text of the original Part 21 notification received from Flowserve via fax: "On September 8, 2009, Flowserve Corporation was notified by Exelon-LaSalle Nuclear Power Station of a failure which occurred and was initially communicated via Flowserve Complaint Report #4914. "The Referenced Complaint Report describes an anomaly with a Size 3/4 Figure 848Y bolted bonnet valve at the LaSalle Nuclear Power Station. "The subject valve was in service at the time of disassembly. The disassembly revealed that the disk nut, which captures the valve stem in the valve main disk, had separated from the main disk. "The valve in question is a manually operated, non-active valve. The safety function of this valve is to retain system pressure. This safety function was not affected by separation of the stem nut from the valve disk. "However, other Figure 848 valves may have different safety related functions that could be affected by this type of failure. "[Flowserve has determined that] the Nuclear Industry needs to be notified concerning the potential defect and encouraged to inspect the operation of their valves, especially if they have a safety-related function in the plant that may be adversely affected. "The valves affected are Size 2 and smaller Edward Figure 848 valves manufactured by Rockwell International at the Sulphur Springs, Texas, and the Raleigh, North Carolina, manufacturing facilities prior to 1991. These valves may be tagged 'Rockwell', 'Rockwell Edward' or 'Edward'. The valves affected have the old design stem/disk assembly. "Valves with Figure Number A848 incorporate the new design stem/disk connection and are not affected. The total number of valves affected and their installed locations are not known." The original report contains more technical details and information. * * * UPDATE FROM ROBERT BERRY TO PETE SNYDER AT 1454 ON 11/24/09 * * * "Upon further investigation, Flowserve has become aware that additional Figure Numbers, 849, 828, and 829 may also be affected by the deviation reported herein, as they share the OLD Stem/Disk Assembly Design." Notified R1DO (Ferdas), R2DO (Sykes), R3DO (Peterson), and R4DO (O'Keefe). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-11-06
45476 | 0 | WATERFORD | 3 |  |  | [3] CE | 2009-11-03 19:03 | 2009-11-03 23:32 | 2009-11-03 | FITNESS FOR DUTY - EMPLOYEE TESTED POSITIVE FOR ALCOHOL. An employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2009-11-03
45475 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-11-03 06:09 | 2009-11-03 14:23 | 2009-11-03 | DEGRADED CONDITION DUE TO WELD ISSUE "On 11/3/09 a walkdown of the Unit 2 Drywell identified a leak on a 3/4" ASME Code Class 1 pipe weld near the 2-0202-5B valve, 2B Recirc Pump Discharge valve. The weld is at an elbow in the pipe leading to the 2-220-35B valve. Unit 2 is currently in Mode 5. The weld will be repaired prior to unit startup." No safety function was lost due to this weld issue. The estimated restart date is 11/26/2009. The licensee has notified NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-11-03
45474 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2009-11-02 22:41 | 2009-11-02 23:55 | 2009-11-03 | REACTOR TRIP DUE TO TURBINE TRIP CAUSED BY A GENERATOR LOCK-OUT RELAY ACTUATION "At 2242 on November 2, 2009 Indian Point Unit 2 reactor tripped from 100% due to a turbine trip. The turbine tripped due to a generator lockout relay actuation. The investigation into the relay actuation is ongoing. All systems responded as expected. Auxiliary feed water is providing steam generator feed and levels are being maintained. No steam safeties opened and no coolant system relief or safety valves actuated. The reactor plant is in mode 3 and stable. Unit 3 was unaffected and remains at 100%." The trip was characterized as uncomplicated. All rods fully inserted and stabilized at the normal mode 3 no-load Tave and pressure. The shutdown electrical lineup is normal and the unit was not in any significant LCOs at the time of the trip. The licensee stated that they were not performing any maintenance or surveillances at the time of the trip. Initial investigation has not revealed any obvious generator electrical system issues but a detailed investigation is ongoing. The licensee has notified State and local authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-11-03
45473 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-11-01 14:00 | 2009-11-02 17:44 | 2009-11-02 | AGREEMENT STATE REPORT INVOLVING A PROCESS GAUGE SHUTTER MALFUNCTION The following information was received from the State of Texas via email: "On November 2, 2009 at 1037 CST the [Texas Department of Health] was notified by [All Star Metals LLC] that they had discovered the shutter operation failure of a Thermo Niton gauge [Model XLp 818] on November 1, 2009 at 1400 CST. The licensee has notified the manufacturer and has sent the gauge to the manufacturer for service and repair. The licensee will send a formal report to the Agency within 30 days." The gauge contains a 30 mCi source of Am-241. Texas Incident # I-8684. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-11-05
45472 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-11-02 07:12 | 2009-11-02 14:23 | 2009-11-02 | LOSS OF SHUTDOWN COOLING "On 11/2/09 at 0712 shutdown cooling (SDC) was lost on Dresden Unit 2 when a recirculation loop temperature element (2-0260-13B) failed upscale. Unit 2 was in the process of initial cooldown for entry into a refueling outage. Recirculation loop temperature was approximately 224 degrees F based on alternate indications. The circuitry was jumpered out and SDC was restarted at 0748. The Recirculation loop temperature was at 260 degrees F upon restart. At 0835, the reactor entered Mode 4 (i.e., Recirculation loop temperature less than or equal to 212 degrees F and Mode Switch in Shutdown). This event is reportable under 10CFR 50.72(b)(3)(v)(B). This event is being reported based on lessons learned from industry experience and is undergoing further review. "The licensee notified NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2009-11-02
45471 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-09-22 | 2009-10-30 14:26 | 2009-11-06 | AGREEMENT STATE REPORT - STUCK SHUTTER ON GAUGE The following was received via e-mail: "On October 30, 2009, the Agency [Texas Department of State Health Services] was notified by the licensee that they were reporting a stuck gauge event. The licensee stated that they realized that they needed to report the event after they reviewed a letter sent out by this Agency regarding the reporting of stuck shutters on gauges. The stuck shutter was found during a routine inspection on September 22, 2009. The gauge is stuck in the open position, which is the normal operating position for this gauge. Dose rates in the area were measured and found to be normal. The gauge is a Thermo Fisher model SH-F2 containing a 100 millicurie Cesium (Cs) - 137. The gauge is installed on the side of a vessel and does not pose any additional risk to their workers. The Licensee has contacted a repair service to repair the shutter. This Agency will provide additional information as it is received." Texas Incident number I-8683 * * * UPDATE AT 1116 EST ON 11/06/2009 TO SIMPSON FROM ART TUCKER * * * The following update was provided by the State via e-mail: "The gauge manufacturer was incorrectly identified as Thermo Fisher. The manufacturer is Ohmart/VEGA." The R4DO (Hay) and FSME (McIntosh) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-11-04
45470 | 0 | SOUTH CAROLINA DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-27 14:00 | 2009-10-28 11:20 | 2009-10-28 | AGREEMENT STATE - MOISTURE DENSITY GAUGE DAMAGED AT CONSTRUCTION SITE The following was received from the state via fax: "The SC [South Carolina] Department of Health and Environmental Control (SCDHEC) was notified Tuesday, October 27, 2009 at 2:10 p.m. that a Humboldt Model 5001 portable moisture density gauge had been damaged on a job site in North Charleston, SC. The gauge contained 11 milliCurie maximum of Cesium 137 and 44 milliCuries maximum of Americium 241/Be. [The] F&ME employee notified the department (SCDHEC) that a gauge technician had been in the process of performing a standardization test with the gauge when it was hit by a motor grader. [The company representative] was present at the job site when the event occurred. [The company representative] informed SCDHEC that the area had been secured with both the gauge and motor grader within the perimeter. [The company representative] was advised to maintain surveillance of the gauge until SCDHEC personnel could respond. "Once on site, SCDHEC personnel determined there was no release of radioactive material and that the Cesium 137 source was still in the locked position. The gauge was placed in its storage container and secured. The licensee informed SCDHEC that he would transport the damaged gauge back to the home office in Columbia, SC that same evening and secure it until the manufacturer could be contacted on Wednesday, October 28, 2009. The licensee would then follow the manufacturer's instructions for the disposition of the device. As more information is available, this notice will be updated. The licensee was advised that a written report detailing this event must be submitted to the department (SCDHEC) within 30 days. The event is open and pending further investigation by the licensee and the department (SCDHEC). Updates will be made through the NMED (Nuclear Materials Event Database) system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2009-11-02
45469 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2009-10-27 00:45 | 2009-10-27 15:59 | 2009-10-27 | RADIOGRAPHY SOURCE UNABLE TO FULLY RETRACT On October 27, 2009, at approximately 0045 hours local time, in the Kuparuk Oil Field in the North Slope Borough, Alaska, the source in an Industrial Nuclear Corporation (INC) IR-100 radiography camera, serial number 6620 was unable to be fully retracted. This was judged to be due to a frozen lock on the device which occurred due to weather conditions of blowing snow and freezing rain. A certified technician serviced the lock. The lock was returned to fully functional condition and the source was returned to the safe and secure position at approximately 0130 hours. The device has a 60 Ci Ir-192 source. No personnel over exposures occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-10-27
45468 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-10-26 10:50 | 2009-10-26 16:50 | 2009-10-26 | STATION PAGING SYSTEM OUT OF SERVICE "At about 1050 CDT on 10/26/2009, it was discovered that the station paging system was not operating. Repair efforts were initiated. The Control Room was notified of the pager outage. The automated callout system was available during the pager outage. "Investigation determined that the paging system was nonfunctional as early as 0900 the same day. "Repair efforts were successful and the pager system was returned to operation about 1230 CDT." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-10-26
45467 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2009-10-26 10:50 | 2009-10-26 12:47 | 2009-11-18 | PRESSURIZER AND FEEDWATER STORAGE TANK LEVEL INDICATIONS DO NOT MEET APPENDIX R REQUIREMENTS "During a review in preparation for converting from 10 CFR 50 Appendix R to NFPA 805, it was discovered that all of the cables for pressurizer and emergency feedwater storage tank level indications did not meet Appendix R cable requirements. A fire in Corridor 4, Corridor 26, or in Room 6 could result in a failure of level indication for these critical components. Corridors 4 and 26 were adequately addressed by existing fire watches. A fire watch was established for Room 6 upon discovery of this condition. Pressurizer level and emergency feedwater storage tank level indicators currently meet their requirements, with the established fire watches." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO DONALD NORWOOD AT 1507 ON 11/18/2009 * * * "On October 26, 2009, Fort Calhoun reported the [above event]. "During the course of the subsequent evaluation it was determined that the pressurizer level indications do meet the 10 CFR 50 Appendix R separation requirements. There is sufficient redundancy of emergency feedwater storage tank level indications to allow proper operator response to potential plant fires. Therefore, this event is not reportable." The licensee notified the NRC Resident Inspector. Notified R4DO (Proulx). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-10-26
45466 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-10-24 13:20 | 2009-10-24 17:07 | 2009-10-24 | OFFSITE NOTIFICATION OF MINOR OIL SPILL "A light film of oil was discovered on the recycle canal of the plant water ways. The source was from residual oil on the deck of a small barge parked on the canal. Snow melt-off carried the oil into the canal. The barge is being used to dredge the canal. The quantity was estimated at less than 1/2 cup [of oil]. The oil is being cleaned up with oil absorbent booms and pads. The oil was contained to the plant water ways and was not discharged to the Mississippi River. "Xcel Energy Services was notified. Xcel notified the National Response Center (Rpt #921543) and the Minnesota Division of Emergency Management (Rpt #107021). The licensee has covered the barge to prevent any further spill and will continue to monitor conditions." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-24
45465 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2009-10-24 | 2009-10-24 12:11 | 2010-01-14 | POTENTIAL AGGRESSIVE WEARING OF ROD CLUSTER CONTROL ASSEMBLY GUIDE CARDS "Aggressive wearing of the RCCA [Rod Cluster Control Assembly] guide card has been observed at an international plant. Such aggressive wear has not been observed in any US plants. If this issue were to remain uncorrected, it is possible for enough wear to occur during the life of the plant that the RCCAs could become unguided and may not properly insert into the core. It has not been concluded whether there is a safety hazard which would result from this deviation." * * * UPDATE FROM GRESHAM TO CHUCK TEAL VIA FAX AT 1213 EST ON 1/14/2010 * * * "Aggressive wearing of the Rod Cluster Control Assembly (RCCA) guide card has been observed at an international plant. Such aggressive wear has not been observed in any other plants. If this issue were to remain uncorrected, it was postulated that enough wear could occur during the life of the plant that the RCCAs could become unguided and may not properly insert into the core. "With the exception of the one international plant in which abnormal excessive wear has been found, the conclusion from the analysis of the collection of wear data and the analysis of rodlet insertion with worn guide cards is that there is no concern for safe operation of any plant regarding guide tube wear for the 40-year design life. The engineering analysis supports this conclusion regardless of the type of RCCA guide tube or the RCCA rodlet material currently in use. For the international plant with the excessive wear, years of continued safe operation is available, and a justification for continued operation has been provided to the utility. Directives in Materials Reliability Program (MRP 227) will necessitate guide tube inspections as part of life extension licensing. "Concerning AP 1000, a guide tube wear analysis has been performed. The analysis demonstrates operability for the 60-year design life for the shutdown control rods. "Based on the above evaluation results, it has been determined that this issue does not represent a substantial safety hazard pursuant to the requirements delineated in I0CFR Part 21 ." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-10-24
45464 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2009-10-23 17:41 | 2009-10-23 22:23 | 2009-12-11 | STEAM GENERATOR SAFETY RELIEF VALVES DID NOT OPEN AT REQUIRED SETPOINT "Online testing of the secondary side pressure relief valves revealed that 3 valves did not open at the required pressure set point on the initial tests. All valves did open on subsequent tests at a higher pressure and have been restored to operable status. These 3 valves and 3 other similar valves were installed during the last refueling outage and it is concluded that all 6 valves have the same set point drift failure mechanism. All 6 valves are assumed to have been inoperable at some time during the last operating cycle. The steam generator design analysis specifies a minimum pressure relief capability to prevent a failure of the steam generator and subsequent potential loss of decay heat removal capability. This condition could have prevented the fulfillment of the safety function needed to remove residual heat. An engineering analysis is in progress to determine the actual impact on the safety function. "Per Technical Specifications 3.4.1.2.3, reactor power was reduced to below 66.3% due to the remaining 3 inoperable relief valves." The licensee notified the NRC Resident Inspector. * * * EVENT RETRACTION FROM ADAM MILLER TO DONALD NORWOOD AT 1130 EST ON 12/11/2009 * * * "In addition to the 6 valves discussed in EN 45464, an additional valve was found to be inoperable. Thus, it is assumed that 7 of the 18 secondary side pressure relief valves were inoperable at some time during the last operating cycle. An engineering analysis has determined that the inoperable secondary side pressure relief valves did not result in a condition that could have prevented the fulfillment of the safety function needed to remove residual heat. The impact of the inoperable secondary side pressure relief valves on the steam generators and associated secondary side piping integrity was assessed by comparison to an existing analysis. A qualitative assessment of that analysis indicates that with the reduced steam relief capacity, the pressure in the steam generators and associated secondary side piping would remain below the ASME code allowable. Thus, there would have been no failure of the steam generators and no subsequent potential loss of decay heat removal capability. Therefore, this event does not meet the criteria of 50.72(b)(3)(v)(B) and is being retracted. This event will be reported as a 60 day LER in accordance with 10CFR50.73(a)(2)(i)(B)." The licensee notified the NRC Resident Inspector. Notified R1DO (Holody). | 60 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2009-10-23
45463 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-10-23 17:00 | 2009-10-23 20:20 | 2009-10-23 | SMALL CIRCUMFERENTIAL INDICATIONS FOUND ON TWO REACTOR VESSEL HEAD PENETRATIONS "On October 23, 2009 during the Beaver Valley Power Station Unit No. 2 (BVPS-2) refueling outage, it was determined that the results of planned ultrasonic (UT) examinations performed on two penetrations of the reactor vessel head would not meet the applicable acceptance criteria. Both require repair prior to returning the vessel head to service. Each of these penetrations has a small circumferential indication near the toe of the J-groove weld. The indications are not through wall and there was no evidence of leakage based on inspections performed on the top of the reactor vessel head. The examinations were being performed to meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to find potential flaws/indications well before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. Currently 43 of 66 penetrations have been examined; all of the penetrations will be examined during the current refueling outage. "The plant is currently shutdown and in an undefined mode as the fuel has been offloaded from the reactor to the spent fuel pool. The reactor vessel head is not currently installed. Repairs are currently being planned and will be completed prior to startup. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) since the as found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-10-23
45462 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-10-23 12:05 | 2009-10-23 17:46 | 2009-10-23 | LOSS OF EMERGENCY PREPAREDNESS CAPABILITIES "On Friday October 23, 2009, at approximately 1205 PDT, Southern California Edison (SCE) evacuated Building E-50, which includes the SONGS [San Onofre Nuclear Generating Station] Emergency Operations Facility (EOF). This Building is located outside of both the Protected Area and the Owner Controlled Area. The evacuation was initiated due to personnel reports of a smoky odor in Building E-50. SONGS Fire Department responded to the incident and, at approximately 1222 PDT, the majority of Building E 50, including the EOF, was cleared for personnel to re-enter the building. SCE is continuing to investigate the source of the smoky odor. The EOF was considered unavailable (but fully functional) for approximately 17 minutes. The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-10-23
45461 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-10-23 08:00 | 2009-10-23 17:44 | 2009-10-23 | POST LOCA RECIRCULATION VALVE POSITION INTERLOCKS "During the current Unit 2 fifteenth refueling outage (2R15), with the core off-loaded to the spent fuel pool, the containment recirculation sump valve interlock position switches were found not to perform correctly. Initial investigation has determined that the valve position sensing interlock switches were left incorrectly set during the Unit 2 fourteenth refueling outage (2R14). "In the event of a Loss of Coolant Accident, (LOCA) this condition would have prevented Residual Heat Removal (RHR) flow from reaching containment spray, high head and intermediate head safety injection pumps following alignment to long term recirculation from the containment sump without additional operator action. "The RHR function, including the long term recirculation from the containment sump, was not adversely affected by this condition. Also, containment spray, high head and intermediate head safety injection from the refueling water storage tank (RWST) was not adversely affected by this condition. "Unit 2 containment recirculation sump valve interlock position switches have been correctly set and are being retested during the current 2R15. "Unit 1 containment recirculation sump valve interlock position switches have been verified as correctly set to be capable of performing their design function by testing performed during the last refueling outage. "This condition will be reported in a Licensee Event Report (LER) within 60 days in accordance with 10 CFR 50.73(a)(2)(ii)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-10-23
45460 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-10-23 16:34 | 2009-10-23 17:34 | 2009-10-23 | PLANT SHUTDOWN DUE TO EXCESS LETDOWN HEAT EXCHANGER TUBE LEAK AND AFTER-THE-FACT UNUSUAL EVENT "On 10/23/09 at 1633, North Anna Unit 1 was placing Excess Letdown in service per 1-OP-8.5 due to a small unquantifiable throughwall leak on 1-CH-TV-1204B. At 1634 [the licensee] entered action of TS 3.4.13 due to what appears to be an Excess Letdown Heat Exchanger tube leak. The Component Cooling Water Head Tank [level] increased from 59% to 79% and the VCT [Volume Control Tank] level dropped 20 % indicating approximately 260 gallons of RCS had flowed into the Component Cooling Water System. At 1638 Excess Letdown was removed from service and the leak was terminated. At 1718 [the licensee] commenced ramping Unit 1 from service [TS Required Shutdown] to comply with TS 3.6.1, 'Containment Integrity' due to the throughwall leak on 1-CH-TV-1204B." The licensee has placed the normal letdown system back in service while the plant is being shut down. The throughwall leak on 1-CH-TV-1204B is relatively small and unquantifiable compare to the tube leak on the excess letdown heat exchanger. The licensee plans to proceed to Mode 5 to repair both the Letdown valve and the Excess Letdown Heat Exchanger tube leak. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM COUNTS TO HUFFMAN AT 1831 EDT ON 10/23/09 * * * The licensee determined that it exceeded EAL SU6.1, Unidentified or Pressure Boundary Leakage greater than 10 gpm, for 4 minutes but currently does not meet the EAL Criteria. This requires the licensee to make a 1-hour notification that it has classified the event after-the-fact as an unusual event but did not actually declare the unusual event. The licensee will notify the NRC Resident Inspector and has notified the Virginia Department of Emergency Management. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-10-23
45459 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2009-08-24 | 2009-10-23 16:32 | 2011-12-01 | INTERIM REPORT ON THERMOSTATIC VALVE FAILURE ON PALO VERDE EDG "This interim report is being issued because Engine Systems, Inc. (ESI) is not able to complete an evaluation of an identified deviation within the 60 day requirement of 10CFR21.21. The evaluation is expected to be completed no later than November 30, 2009. "ESI began an evaluation of a thermostatic valve element failure on August 24, 2009. Palo Verde Nuclear Plant notified ESI of the failure as a result of a failure analysis they were performing on a thermostatic valve that had been removed from the lube oil system of their 2A-EDG. The element was in service since April 2008 and Palo Verde verified operation of the element prior to installation. "The Palo Verde failure analysis determined that one of two elements within the valve was defective. The element failure was attributed to wax leakage past the diaphragm seal on one of two power pills within the element. Evidence of mechanical binding of the piston is believed to have caused the wax leakage. If the piston was jammed, the expanding wax could have over pressurized the diaphragm seal leading to wax leakage. The failure analysis noted the following to support piston binding: - The piston was initially difficult to remove from its guide tube. - A gouge was observed on the piston surface. - The rubber plug within the power pill exhibited brass machining chip debris. "ESI has been coordinating with Palo Verde and the manufacturer (AMOT) to complete our evaluation and to determine if this is a generic issue or if it is an isolated incident. "To date, no other similar failures with AMOT thermostatic valves have been reported to ESI." Palo Verde has Cooper Bessemer KSV-20T diesel engines that use one 6" thermostatic valve in the engine jacket water system and one in the engine lube oil system to regulate system temperatures during engine operation. The thermostatic valve is an AMOT model 6HAS. The AMOT thermostatic valve element (P/N 9760X) is the defective part. ESI did not provide any information on other nuclear power plants that have EDGs that utilize this model thermostatic valve. * * * UPDATE RECEIVED VIA EMAIL FROM PAUL STEPANTSCHENKO TO DONG PARK AT 1642 EST ON 12/01/09 * * * "This report is a follow-up to an interim report (10CFR21-0098-INT) issued by Engine Systems, Inc. (ESI) on 10/23/09 which identified a deviation with an Amot thermostatic valve element. The interim report was issued because ESI was not able to complete the evaluation within the 60 day requirement of 10CFR21. The evaluation was completed on 11/30/09 and the deviation was determined be a reportable defect as by defined by 10CFR21. "The Exelon analysis also reports that similar brass machining debris was observed on the plugs from the other three power pills to varying degrees. None of the stems of these pills displayed evidence of gouging or binding. "To date, no other similar failures with Amot thermostatic valves have been reported to ESI. "ESI has contacted the valve manufacturer (Amot) to discuss these findings. A copy of the Palo Verde failure analysis and eleven (11) element assemblies from ESI inventory were sent to Amot for evaluation. The following elements were sent to Amot for evaluation: "Qty. 8: PIN 9760 X-170' (CES PIN 2-05V-419-107) "Qty. 3: PIN 9760 X-160' (CES PIN 2-05V-419-109) "Both part number elements are the same except for the temperature setting ('-170' indicates 170?F nominal and '-160' indicates 160?F nominal). "Upon completion of their evaluation, Amot has reported the following: "Fine shavings/powder of brass was observed in some of the element pills. "None of the pill stems had any evidence of gouging. "The pills used in the 9760X elements are made by converting another part number pill. This conversion consists of removing the stem from the pill and performing some machining. Amot believes the brass debris may have entered the pill as a result of this conversion process. "Amot has not made any changes to this conversion process in recent history and has not had reports of similar problems with these elements. "Machining debris, while undesirable, was evident in other pills which did not exhibit any operability issues; therefore this is not believed to be the cause of the pill failure. "The primary cause of the failure is believed to be the gouge found in the pill stem. The gouge could have occurred during the conversion process as the stem is removed and handled at that time. "As a precaution, Amot has made changes to their conversion process for this pill. The drilling fixture was modified to eliminate the possibility of chips entering the pill during the machining operation. This change was made effective 10/22/09. "A listing of users with the thermostatic valves that contain the Amot 9760X element is provided in the table below. "Site - Thermostatic Valve - System: "Braidwood - 6HAS - Lube "Byron - 6HAS - Lube "Nine Mile Point - 6HAS- Lube "Oconee - 4HAS & 6HAS - Water "Palo Verde - 6HAS - Lube & Water "South Texas Project - 6HAS - Lube & Water "Susquehanna - 6HAS - Lube & Water "Waterford - 5HAS & 6HAS - Lube & Water "Corrective Action: The element failure at Palo Verde is considered to be an isolated incident related to a gouge in the pill stem. Thus, there is no recommended corrective action for users of the Amot 9760X element. The evaluation also indicated a weakness in Amot's manufacturing process for the element pill which introduced machining debris. While not believed to be the cause of the Palo Verde element failure, machining debris within the element pill is undesirable and increases the potential for failure in the future. Users with thermostatic valves containing Amot PIN 9760X elements should be aware of this issue so that they can monitor their systems for any indications of thermostat element problems. Notified R1DO (Holody), R2DO (Guthrie), R3DO (Riemer), R4DO (Deese), NRR (Thorp) via e-mail, NRO (Tabatabai) via email. * * * UPDATE RECEIVED VIA FAX FROM TOM HORNER TO DONG PARK AT 1613 EST ON 04/01/11 * * * Two sentences were added to address the safety hazard which is created or could be created by this defect. "This defect could affect operability of the thermostatic valve within the diesel engine cooling water and/or lube oil system, resulting in elevated fluid system temperatures during engine operation. Engine performance and/or load carrying capability could be impacted with the possibility of eventual engine failure, thereby preventing the emergency diesel generator from performing its safety related function." Notified R1DO (Powell), R2DO (Sykes), R3DO (Peterson), R4DO (Lantz), PART 21 GROUP via e-mail. * * * UPDATE RECEIVED VIA FAX FROM TOM HORNER TO VINCE KLCO AT 1611 EST ON 12/01/11 * * * The report was updated to revise part numbers for Oconee, Waterford and Laguna Verde (Mexico). Affected users added include the following: Susquehanna 5th EDG and Ergytech/Iberdroia (Spain). Notified R1DO (Schmidt), R2DO (Desai), R3DO (Riemer), R4DO (Farnholtz) and PART 21 GROUP via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-10-23
45458 | 0 | HILTI INC. |  |  |  |  | 2009-10-23 | 2009-10-23 14:18 | 2009-10-23 | POTENTIAL DELIVERY OF NONCONFORMING WASHERS Hilti provided notification of a potential delivery of nonconforming washers supplied with expansion anchors type Hilti Kwik Bolt KB3 SS316, 1/4" and 3/8" diameters, all lengths. Chemical analysis of provided samples showed the nonconforming washers were made of grade SS430Ti stainless steel instead of the specified grade SS316. Potentially affected utilities or plants are: PSE&G Nuclear; Pilgrim; Brunswick; Arizona Public Service; Waterford 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | OK | OTH | PAR | 21.21 |  |  |  | 0 | 2009-10-23
45457 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-20 15:00 | 2009-10-23 11:18 | 2010-06-09 | AGREEMENT STATE REPORT - RADIUM SOURCE FOUND IN SCRAP METAL The following information was received from the state via e-mail: "Nucor-Yamato Steel in Blytheville, Arkansas reported to the Arkansas Radiation Control Program on October 20, 2009, that they believed a source had been found in a load of scrap metal received at their facility. The shipper for this load of scrap metal was Southern Scrap, Baton Rouge, Louisiana. "Radiation surveys conducted by steel mill personnel indicated an on contact reading of 5.0 mR/hr. "Health Physicists from the Arkansas Radiation Control Program responded to Nucor-Yamato Steel in Blytheville, Arkansas on Tuesday, October 20, 2009 arriving at 3:00 p.m. "The device is 20 inches long and 6 inches square. The only identifying marks are a plate labeled 'MFD BY S.H. COUCH CO INC' and appears to be a type of selector switch containing a Radium-226 backlight. The switch can select 'AFT STA' or 'WHEEL HSE.' "Survey readings at the selector switch were 5.5 mR/hr. Removable contamination (not quantified) was found on smears of the device taken in the field. "The device was packaged and transported to the Arkansas Department of Health and is currently in a secured storage area. The Department continues to investigate this incident to determine the identity of the device as well as the owner." * * * UPDATE FROM KAYLA AVERY TO HOWIE CROUCH VIA EMAIL AT 1627 EDT ON 6/9/10 * * * "An employee of American Radiation Services, Inc. (ARS) arrived in Little Rock on March 19, 2010 to retrieve the unknown source. The source was packaged and transported to Port Allen, Louisiana where ARS determined that it was a Radium-226 source of approximately 2.4 mCi. The manufacturer, model number and serial number are still unknown. ADCO Services, Inc. picked up the source from ARS on April 30, 2010 and transported it to Tinley Park, Illinois where it is waiting disposal. "The Arkansas Department of Health considers this incident to be closed." Notified R4DO (Powers) and FSME (Mauer). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-10-28
45456 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-10-22 17:39 | 2009-10-22 19:14 | 2009-10-23 | UNUSUAL EVENT DECLARED DUE TO INOPERABLE DIESEL GENERATORS WHILE DEFUELED "While the reactor was defueled as part of a refueling outage the 'A' Emergency Diesel was declared inoperable due to a failed speed switch. 'A' Emergency Diesel was the required emergency power source while the 'B' Emergency Diesel and its associated safeguards buss, NB02, were inoperable for scheduled maintenance. With both emergency diesels inoperable a Notification of Unusual Event was declared on the 'Loss of Electrical Power/Assessment Capability'. "Technicians are currently replacing the failed speed switch. It is estimated that the 'A' Emergency Diesel will be restored to operable status by 2200 CDT." The licensee notified the State and local authorities and the NRC Resident Inspector. The licensee also stated a press release will be issued. * * * UPDATE AT 0456 ON 10/23/2009 FROM MARK JENKINS TO MARK ABRAMOVITZ * * * Additional problems were found during troubleshooting and a power supply is being replaced. This should be completed about 0600 CDT followed by a diesel test. Notified the R4DO (O'Keefe) and NRR (Lee). * * * UPDATE ON 10/23/2009 AT 0907 FROM RICK HUBBARD TO JOE O'HARA * * * The "A" EDG has been returned to service. The licensee exited the Unusual Event at 0740 CDT. The licensee notified the NRC Resident Inspector. Notified the R4DO (O'Keefe), NRR (Lee), IRD (McDermott), DHS (Kettles), FEMA (Biscoe). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-10-22
45455 | 0 | PORT HURON HOSPITAL |  |  |  |  | 2009-10-22 11:40 | 2009-10-22 17:34 | 2009-10-22 | PACKAGE EXTERNAL CONTAMINATION ABOVE LIMITS At 1140 EDT, the Port Huron Hospital received a shipment of Technetium-99m from Lake View Diagnostic (also located in Port Huron) that had excessive surface contamination levels. The shipment contained a 250 millicurie dose of Tc-99m and a 10 millicurie dose of Tc-99m (Mag3). The shipment was wipe surveyed and contamination of 568,000 dpm was discovered along a vertical edge of the shipping package. The surface radiation level was measured at 15 mRem/Hr. The hospital isolated the package and did not attempt to use the Tc-99m doses. The licensee stated that there was no evidence of damage to the package. The personnel that handled the package and all hospital locations where the package was handled were surveyed but no other contamination was found. Lake View Diagnostic was contacted and retrieved the package from the Port Huron Hospital. The licensee noted that the delivery carrier of the package was also Lake View Diagnostic. There was no information on whether the carrier vehicle or any Lake View Diagnostic personnel were contaminated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2009-10-22
45454 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-10-22 00:01 | 2009-10-21 23:39 | 2009-10-22 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR VENTILATION SYSTEM AND CHARCOAL FILTER MAINTENANCE "At 0001 on Thursday, October 22, 2009, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system air conditioning and filtration systems will be removed from service for a scheduled maintenance activity. The Motor Control Center providing electrical power to several TSC ventilation components will be de-energized to facilitate replacement of the U1 CD Emergency Diesel Generator room ventilation supply fan starter (1-88X-DGS-2). "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system availability is scheduled to be restored at 0800 on Thursday, October 22, 2009. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the unavailability of an emergency response facility." * * * UPDATE AT 1008 ON 10/22/2009 FROM DAN KURTH TO MARK ABRAMOVITZ * * * The TSC ventilation was restored to service at 0937 EDT. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Kozak). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-10-22
45453 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-10-21 17:55 | 2009-10-21 21:29 | 2009-10-21 | FATALITY AND TRANSPORT OF A POTENTIALLY CONTAMINATED INDIVIDUAL OFFISTE "At approximately 1755 CDT on 10/21/09, control room personnel were notified of a potentially contaminated individual suffering from a personal medical emergency inside the containment building. The individual was treated by the onsite first responders who administered CPR and AED (Automatic External Defibrillator). At 1816 [CDT], Coffey County medical personnel arrived on site. The individual was transported via ambulance to the Coffey County Hospital where the individual was pronounced dead at approximately 1900 [CDT] from an apparent cardiac arrest. A WCNOC [Wolf Creek Nuclear Operating Corp.] health physics technician accompanied the individual to the hospital and determined that the individual was not contaminated. The individual was a supplemental employee supporting refueling activities. "OSHA will be notified of the work place fatality. State and Local Government Agencies will be notified. No news release is planned." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-21
45452 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-10-21 | 2009-10-21 21:21 | 2009-10-21 | FITNESS FOR DUTY NON-LICENSED SUPERVISOR A non-licensed contractor supervisor refused to take a random drug and alcohol test. The individual's unescorted access was immediately terminated and the individual removed from the site. Contact the HOO for additional details. The licensee notified the NRC Resident Inspector. | 28 | 100 | 0 | 28 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2009-10-21
45451 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-21 | 2009-10-21 19:18 | 2010-01-08 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION ON A PACKAGE Packaged vials of Sulfur-35 were delivered to the University of Texas with an indicated removable contamination of 10,000 dpm per swipe on the outside of the package. The vials of sulfur were reported as frozen with 1600 dpm per swipe. A lead pig located in the package indicated 600 dpm per swipe. There was no other reported contamination on the package. A Texas incident report number will follow. * * * UPDATE AT 1136 EDT ON 10/22/2009 TO PARK FROM TUCKER * * * The following report was provide by the State via e-mail: "On October 21, 2009 at 1735 [CDT] the Agency [Texas Dept of State Health Services] received a telephone call from [Redacted] the Radiation Safety Officer [RSO] for the University of Texas. [The RSO] stated that a package had arrived at the University of Texas facility in Port Aransas, Texas, and was found to have removable contamination on the outside of the package. The package was shipped as expected and contained vials of Sulfur-35, and did not appear to be damaged. The vials that contained the radioactive material were packed in dry ice and were still frozen when the package was opened. Swipes taken on the outside of the package, as part of the arrival survey, indicated contamination of 10,000 disintegrations per minute (dpm). Contamination levels on the vials in the package were 1,600 dpm. The contamination level on the lead pig shielding the vials was 600 dpm. Removable contamination on the inside of the package was between 1000-2000 dpm. All contamination levels are reported as per swipe, but [the RSO] was unsure of the areas that were swiped. No contamination was detected on personnel involved at the receiving facility. [The RSO] was not convinced that the contamination came from the package because none of the vials appeared damaged, and the highest contamination levels were located on the outside of the package. He stated that they are still investigating and may request assistance from the Agency to identify the radionuclide. It was shipped by [a common carrier] from PerkinElmer, but [the RSO] was unaware of the location it was shipped from. The common carrier tracking number given was [provided], but when tracked online using the [common carrier] website, the package was not in the system. The Agency is awaiting further information from the licensee's investigation." Notified the R4DO (O'Keefe) and FSME (McIntosh). Texas Incident Number: I-8680 * * * RETRACTION FROM ANNIE BACKHAUS TO HOWIE CROUCH VIA EMAIL AT 1639 EST ON 1/08/10 * * * "On November 2, 2009, [the RSO] concluded, through his investigation, that the initial readings were false-positives. He concluded this after he conducted two independent surveys of the package and detected nothing above background. [The RSO] concluded the false-positive was due to chemiluminescence and ionizing radiation. Therefore, the State of Texas would like to retract this report from the Nuclear Materials Events Database." Notified the R4DO (Shannon) and FSME EO (McConnell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-10-26
45450 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-08-04 | 2009-10-21 16:44 | 2009-10-21 | AGREEMENT STATE REPORT - UNAUTHORIZED ORDER OF TRITIUM GAS "Event location: Customs and Border Protection in Cleveland, OH "Notifications: [The Pennsylvania Department of Environmental Protection] DEP got a phone call from the RSO [Radiation Safety Officer] on October 6th, 2009, that there was a suspicion of unauthorized order of radioactive material. Confirmation phone call [was made] from the RSO to the DEP on October 21, 2009, after a full internal investigation to confirm suspicion of unauthorized order of tritium gas. "Event description: On August 4,2009, an unauthorized researcher from University of Pittsburgh placed an order with 'Microtek AG' for 11.88 Curies of tritium. The order was shipped on September 11, 2009 and inspected by Customs & Border Protection (CBP) at Cleveland, OH. CBP contacted the RSO to verify the license, and the Univ. of Pittsburgh advised CBP that the shipment was an unauthorized order. The order was returned to [the] shipper (Microtek AG of Switzerland)." Event Report ID No: PA090033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-10-26
45449 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-10-21 09:52 | 2009-10-21 10:45 | 2009-10-21 | UNINTENTIONAL ATTEMPTED INTRODUCTION OF CONTRABAND INTO A PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1545 EDT ON 10/21/09 FROM GEORGE ROBERTSON TO S. SANDIN * * * After further review the licensee concluded there was no malevolent intent and is, therefore, retracting this report. The licensee will inform the NRC Resident Inspector. Notified R2DO (Henson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-10-21
45448 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-10-20 07:10 | 2009-10-20 17:36 | 2009-10-20 | RANDOM FITNESS FOR DUTY FAILURE A non-licensed contract supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employees access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2009-10-20
45447 | 0 | BASIN ELECTRIC POWER COOPERATIVE |  |  |  |  | 2009-10-19 | 2009-10-20 11:05 | 2009-10-20 | SHUTTER ON NUCLEAR GAUGE STUCK OPEN During an inspection on October 19, 2009, a process nuclear gauge was found to have a stuck open shutter. The gauge is a Kay Ray Model 7062P, serial number 5757, containing 100 milliCurie Cs-137 source. It was mounted 20 feet above the floor and no exposure to personnel occurred. "At this time it appears that Radiation Technology, Inc. of Austin, TX will provide repair service at a date yet to be determined. In the meantime, the crusher is in service and the gauge is in use with no plans to work on associated equipment. As the gauge is located about 20 feet above the floor with no immediate access, it is not likely to present a hazard. A notification of hazard will be placed in the operations log to prevent any unintentional access until the gauge can be repaired." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | OTH | GEN | 30.50(b)(2) |  |  |  | 0 | 2009-10-20
45446 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-10-13 | 2009-10-19 17:00 | 2009-10-22 | NITROUS OXIDE (NOx) GENERATION RATE HIGHER THAN EXPECTED AFTER ALUMINUM FINES WERE INTRODUCED "Bldg 333's U-Aluminum Bowl Cleaning system is designed to remove uranium from centrifuge bowls by circulating nitric acid through the bowls. The system has historically produced NOx (nitrous oxide, etc) during the nitric acid dissolution process. Safety controls designated as Items Relied On For Safety (IROFS) include a NOx detection system (IROFS BPF-43) with sensors located at the nitric acid knockout column's siphon break potential NOx release point if process ventilation fails and at employee working level. "On October 13, 2009, NFS began using the Bowl Cleaning system to dissolve U-Al fines (very small particles of U-AI) rather than adding them to the normal dissolver column. The fines were loaded into strainers and placed directly into the bowls to be dissolved with nitric acid. After the dissolution process began, the Operator noticed that the temperature of the system was increasing and that NOx (in the form of a brown cloud) was beginning to form inside the Bowl Cleaning station containment vessels. The system was shutdown. The Nox detector designated as an IROFS alarmed and the facility was evacuated. Immediate corrective actions included building, and health and safety personnel re-entry in SCBA to validate shutdown conditions and remote monitoring of Nox levels in Bldg 333. Based on re-entry data and remote Nox detector readings, Nox levels inside the building (outside of containment) were not significant. "Laboratory analysis of similar U-AI fines material was conducted October 14-October 16. It behaved in the laboratory in the same manner as what was observed during the operational event. Based on the lab testing, a Nox generation rate specific for the fines material was estimated. Based on engineering calculations, it was determined that the Nox generation for the fines was significantly higher than the previously analyzed Nox generation for the U-AI ingots. The previous Nox evaluation for the U-Al Bowl Cleaning station resulted in an intermediate occupational consequence. Using the generation rate specific for the fines results in high occupational consequences. "On October 19, 2009, based on the revised Nox generation rate, it was determined that insufficient lROFS were in place and that the performance criteria of 10 CFR 70.61 were not met. "a) Radiological Hazards involved including: High- enrichment Uranium: quantity Approx 1,000 g; Isotope: U-235 quantity Approx 710 g "b) Chemical Hazards involved including: Chemical: Nox gas; Quantity: Approx. 1.85 lbs. "c) Discuss the actual or potential health and safety consequences to the workers, the public, and the environment, including relevant chemical and radiation data for actual personnel exposures to radiation or radioactive materials or hazardous chemicals produced from licensed materials. Include in the discussion below the concentration of chemicals and duration of exposure, if any: Potential worker and public exposure to Nox. Process ventilation and Nox detection worked as designed. No actual exposure to workers or the public were recorded. "d) Discuss the sequence of occurrences leading to the event, including degradation or failure of structures, systems, equipment, components and activities of personnel relied on to prevent potential accidents or mitigate their consequences: See above. "e) Discuss whether the remaining structures, systems, equipment components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences are available and reliable to perform their function: IROFS BPF-43 is in place and functioned correctly during the event. Operating personnel responded to the alarm as specified in the operating procedure and evacuated the facility. "External conditions affecting the event: None. "Additional actions taken in response to the event: Discussed situation with Operations, Safety management and with the NRC Resident Inspector. The U-Al Bowl Cleaning system is currently not operating." * * * UPDATE FROM JENNIFER WHEELER TO DONG PARK AT 1005 EDT ON 10/22/09 * * * The "(nitrous oxide, etc)" in the first paragraph of the original report is updated to state "(NO, NO2, etc)." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Henson) and NMSS EO (Rubenstone) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2009-10-21
45445 | 0 | WATERFORD | 3 |  |  | [3] CE | 2009-10-19 09:44 | 2009-10-19 14:13 | 2009-10-19 | MANUAL REACTOR TRIP FOLLOWING STUCK OPEN MOISTURE SEPARATOR HEATER RELIEF VALVE "At approximately 0915 CDT on 10/19/09 a Waterford 3 Moisture Separator Heater shell-slide relief valve (RS-203B) inadvertently opened, causing reactor power to increase from 100% to approximately 100.27% Rated Thermal Power (RTP). Operations reduced Main Turbine-Generator load by approximately 26 megawatts to restore reactor power to less than 100% RTP. At approximately 0942 CDT, Operations commenced a rapid plant shutdown because the relief valve would not re-close. At approximately 0944 CDT, Operations manually tripped the reactor due to a low condenser hot well level, just prior to reaching the Condensate Pumps Trip setpoint, to avoid a loss of Main Feedwater event. The Plant Protection System (PPS) responded as designed, resulting in an uncomplicated reactor trip. "Emergency Feedwater Actuation Signal (EFAS) was received on low Steam Generator level as expected from reactor trip at or near full power. Steam Generator levels remained above the EFAS injection level setpoint so that actual injection of Emergency Feedwater did not occur. No other PPS actuation occurred. The plant is currently being maintained in Mode 3. "Waterford 3 plans to commence refueling outage (RF16) at this time, approximately 1 - 2 days earlier than scheduled. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-10-19
45444 | -1 | DEFENSE DISTRIBUTION CENTER |  |  |  |  | 2009-10-16 | 2009-10-19 10:13 | 2009-11-02 | STRONTIUM-90 PRESSURE INDICATORS MISSING DURING AN ANNUAL INVENTORY "While conducting the Annual Radioactive Inventory [of pressure indicators], a discrepancy was noted in the on-hand balance of the subject NIIN (National Item Identification Number). The current electronic inventory balance was 138 ea, but a physical check of the location could only locate 136 for a shortage of 2 ea. An initial search of the Radioactive Materiel Storage Area did not locate the item. The Service Provider and Continuing Government Activity personnel will begin a review of all transaction since the last reconciled inventory in an attempt to identify potential transaction errors. "The pressure indicator in its shipping container is authorized to ship as an expected package with an external dose rate of less than 0.5 mrem /hr on contact." The pressure indicators contained 500 microcuries of Sr-90. * * * RETRACTION FROM D. COLLINS TO E. SIMPSON ON 11/02/09 AT 1336 EST * * * The inventory items that were previously thought to be lost or stolen were subsequently located during a more comprehensive search of the warehouse. "A number of potential process weaknesses lead to the initial report of the inventory discrepancy. While available, handheld Radiofrequency transmitters were not used for all transactions, causing delay in inventory balance updates (issues and re-warehousing not immediately accounted for), [and] similar packaging were found to contain either one or two items per packaging. "DDC Inventory Control [licensee] canceled the current electronic inventory, processed all open transactions and ran an updated inventory. Physical inventory and verification of serial numbers accounted for all sources identified in electronic inventory system. "Hand-held Radiofrequency devices will be used in the future for all inventory transactions to alleviate delay in transaction processing. Also, items were repackaged to ensure that only one device was in each package." Notified R1DO (Barkley), R4DO (Hay), FSME EO (White) and Mexico via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | CA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-10-19
45443 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-10-14 17:00 | 2009-10-16 15:57 | 2009-10-16 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED CONTRACT SUPERVISOR A non-licensed contract employee supervisor failed to disclose derogatory information as required by the fitness-for-duty program. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2009-10-16
45442 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-15 | 2009-10-16 14:15 | 2009-10-16 | AGREEMENT STATE REPORT INVOLVING POTENTIAL LOSS OF RADIOACTIVE MATERIAL DURING SHIPMENT The following information was received from the State of Texas via email: "On October 16, 2009, at 11:35 AM, the licensee notified the Agency [State of Texas] that a 1.78 curie Cesium (Cs)-137 sources, and a 10.8 millicurie California (Cf) -252 source was lost in transport. The sources were picked up by a common carrier on October 14, 2009, for delivery to their facility in Oklahoma City, Oklahoma. At 1600 on October 15, 2009, the licensee was informed that the sources had not arrived in Oklahoma City. The RSO contacted the shipper and was informed that they believed that the sources had been placed on a truck going to Albuquerque, New Mexico. At about 3:00 AM on October 16, 2009, the licensee was notified that the sources were not on the truck going to Albuquerque. The shipper stated that they would contact all of their facilities (290 of them) to look for the packages. The Cs-137 source is in a container that weighs 320 pounds and labeled as Yellow II with a TI of 0.2. The Cf-252 source is in a container that weighs 185 pounds, is labeled as a Yellow II and a TI of 0.6. The RSO went to the shippers facility in Houston and searched for the packages. He did not find them. The shipper will contact the licensee as soon as the sources are located. The license will provide additional information as it is received." The State of Oklahoma was informed of the missing shipment. Texas Incident No.: I-8679 * * * UPDATE AT 1951 EDT ON 10/16/09 FROM ART TUCKER TO S. SANDIN * * * The following update was received from the State of Texas via email: "On October 16, 2009, at 1715 CT, the licensee contacted the Agency and informed them that at 1657 CT, the licensee was contacted by the shipping company and informed that the two sources had been located at their facility in Kansas City, Mo. The shipping company will deliver the sources to the licensee's facility in Oklahoma City on October 17, 2009." Notified R4DO (Cain) and FSME EO (Delligatti). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-10-21
45441 | 0 | BASIN ELECTRIC POWER COOPERATIVE |  |  |  |  | 2007-02-16 | 2009-10-16 13:43 | 2009-10-16 | COAL BUNKER FIRE DAMAGED DENSITY GAUGE CONTAINING 50 MILLICURIE CS-137 Subsequent to discussions with NRC Region IV (J. Thompson), the licensee is reporting a fire in one of their coal bunkers in late February 2007 damaged a Texas Nuclear Model 5192 density gauge (S/N B4745) containing 50 milliCurie Cs-137. The gauge was fix mounted in Unit 2 approximately 20 feet above the floor. After the fire was extinguished, a radiological survey of the gauge indicated that the source was still in the gauge. The licensee hired a contractor who removed and disposed of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-10-16
45440 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-10-16 00:48 | 2009-10-16 01:48 | 2009-10-16 | MANUAL REACTOR SCRAM DUE TO REACTOR RECIRCULATION PUMP TRIP "On October 16, 2009 at 0048 a manual reactor scram was inserted at the Perry Nuclear Plant. "The plant was conducting a planned shutdown due to the Division 2 Emergency Service Water inoperability. While shifting reactor recirculation pumps to slow speed the 'A' pump failed to transfer and tripped off. Following stabilization from this event a manual reactor scram was inserted from approximately 30% power. This was different from the initial planned shutdown sequence. "Following the scram all systems operated as expected. The plant is stable in Mode 3. The plant will transition to Mode 4 in accordance with Technical Specification 3.7.1 (Emergency Service Water Inoperability) required actions." All control rods fully inserted and the plant electrical power is in a normal line-up. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-10-16
45439 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-14 | 2009-10-15 18:04 | 2009-10-16 | AGREEMENT STATE REPORT INVOLVING A RADIOGRAPHY CAMERA SOURCE DISCONNECT Received a call from State of Texas concerning an incident that occurred 10/14/09 at a temporary jobsite in Texas (location unknown). The company (not identified in the call) is located in Pasadena, TX. The State of Texas representative said that the Radiographer failed to follow procedures and connect the guide tube before cranking out the source. The source subsequently struck the wall and disconnected. The company RSO who is qualified for source retrieval recovered and secured the source. His extremity dosimetry indicated 57 mrem with a whole body dose of about 90 mrem. Details of the incident including licensee name and license number will be provided by update. * * * UPDATE FROM ART TUCKER TO VINCE KLCO AT 1049 ON 10/16/2009 * * * The following information was received by e-mail: "On October 15, 2009, the Agency [State] was notified by the licensee that on October 14, 2009, they experienced a source disconnect while using an Amersham model 660 radiography camera containing a 45.3 curie Iridium (Ir) 192 source. The Radiation Safety Officer (RSO) stated that two radiographers were setting up for their first shot of the day. The guide tube they had was too short, so one of the radiographers connected an additional guide tube to the end of the existing guide tube, while the other radiographer prepared to perform the shot. Neither of the radiographers attached the guide tube to the camera. They then cranked the source out of the camera to perform their first shot. This caused the source to be pushed out of the camera, onto the floor of the shooting bay, and against the wall of a shooting bay. The camera operator felt that he had cranked the source out farther than it should have traveled for the shot and stopped cranking the source. He then tried to return the source to the camera. When the radiographer retracted the drive cable, the source was left loose on the shooting bay floor. The radiographer approached the shooting area with his dose rate meter and found the dose rates were elevated. The radiographer then secured the area and notified the RSO, who is specifically authorized on the license for source retrieval. The RSO developed a strategy to reconnect the source, and then successfully cranked the source back into the camera. No one involved with this event received an exposure exceeding any regulatory limit. "The RSO stated that their investigation into the event determined that the root cause for the event was the failure of the two radiographers to follow procedure. He also noted a failure of the two radiographers to communicate adequately. The RSO stated that they will retrain all of their radiographers regarding their procedures for the proper connecting and disconnecting of equipment to their exposure devices. He also stated that this training would be repeated in their annual training in 2010." Texas Incident: I-8678 Notified R4DO(Cain) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-10-20
45438 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-10-15 12:04 | 2009-10-15 18:11 | 2009-10-15 | MOMENTARY LOSS OF SHUTDOWN COOLING WITH AUTOSTART OF EMERGENCY DIESEL GENERATOR "At 1204 power was lost to Safeguards Bus '5' and Emergency Diesel Generator 'A' started and re-energized Bus '5.' "Event was caused by starting SI Pump 'A' to fill SI Accumulator 'A' which resulted in a Tertiary Auxiliary Transformer trip and lockout. At the time RHR Pump 'A' was in operation and tripped, RHR Pump 'B' was started within 2 minutes using the Abnormal Operating Procedure and flow restored to the RCS. RCS temperature decreased initially due to an increase in service water cooling and actions were taken to stabilize RCS Temperature. "All equipment operated as expected for the voltage restoration to Safeguards Bus '5.' "Both trains of RHR were declared inoperable as of 1204 [CDT] due to the loss of normal power supplies per Technical Specification 3.7. Emergency Busses were energized and both trains of RHR remained available for decay heat removal during this event." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | VALID SPECIF SYS ACTUATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-10-15
45437 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-10-15 14:49 | 2009-10-15 17:13 | 2009-10-15 | OFFSITE NOTIFICATION DUE TO MINOR OIL SPILL TO THE MISSISSIPPI RIVER An oil spill of less than 1/2 of a cup to the Mississippi River occurred while preparing for Intake Structure dredging activities. Hydraulic oil leaked out of a fitting for the dredging pump and entered the Mississippi River side of the Intake Screenhouse. A small oil sheen was noticed and collected using the pre-deployed absorbents. The fitting was repaired and no more oil is currently leaking. The Minnesota Pollution Control Agency and the National Response Center were notified. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-15
45436 | 0 | UNIVERSITY OF MICHIGAN HOSPITAL |  |  |  |  | 2009-10-14 17:00 | 2009-10-15 16:42 | 2009-10-15 | PATIENT RECEIVED APPROXIMATELY 76% OF THE PRESCRIBED DOSE A three year old boy was undergoing a palliative treatment for a cancer related illness with I-131. The boy was prescribed 180.5 milliCuries of I-131 by his physician. During the treatment, a technician noticed that there were air bubbles in the intravenous tubing leading to the boy and stopped the treatment. Upon subsequent investigation, it was revealed that the patient only received 138 milliCuries of the prescribed 180.5 milliCuries of I-131, which is approximately 76% of the prescribed dose. The patient's physician has been notified, and is making a decision whether to inform the boy's parents. The licensee is investigating the cause of the incident. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-10-21
45435 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-15 14:15 | 2009-10-15 15:55 | 2009-10-15 | POTENTIAL LOST SEALED SOURCE CONTAINING 1.8 CURIES TRITIUM The following information was received from the State of Texas via email: "On June 29, 2009 Hotwell US LTD received a new shipment of two tritium well logging tools from their manufacturer in Austria. The tools each contain a 1.8 Curies (Ci) tritium sealed source inside a 15,000 psi pressure housing. These tools were slated for sale and delivery to Competition Wireline (NRC License No. 25-27802-1) out of Billings, Montana. After arriving at the facility in Houston, Texas, the tools were checked and shipped via [common carrier] to Competition Wireline. One tool (No. 33264) arrived at Competition Wireline on July 1, 2009. On July 6, 2009, Competition Wireline verified to Hotwell US LTD that the other tool (No. 33284) had been received. On October 13, 2009 Competition Wireline reported to Hotwell US LTD that after a general inventory of equipment, they could not locate one of the tools (No. 33284). The licensee has alleged that [the common carrier] never delivered the tool and found that it was last tracked to Memphis, Tennessee. [The common carrier] now shows the package as 'In Transit'. Competition Wireline has notified [the common carrier], and [the common carrier] is conducting an investigation into the location of the package. The missing tool is described as follows: " Tool No. 33284 Monoblock No.: 99448 Model No.: ING-10-50-120-TBT Description: 84 x12 x8 Black Crate "Texas Incident Number I-8677." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-10-20
45434 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-10-15 12:25 | 2009-10-15 14:47 | 2009-10-15 | UNIT COMMENCED SHUTDOWN DUE TO INOPERABLE DIVISION 2 EMERGENCY SERVICE WATER SYSTEM "This event is being reported in accordance with 10CFR50.72(b)(2)(i). On October 15, 2009, at approximately 1225 hours, the Perry Nuclear Power Plant commenced a Technical Specification required plant shutdown. "On October 14, 2009, At 1747 hours, the Division 2 Emergency Service Water (ESW) system was declared inoperable and unavailable for planned work. The plant entered Technical Specification (TS) 3.7.1 Action A for one inoperable ESW Division. Other supported TSs were also entered (TS 3.8.1 for the Division 2 diesel generator, TS 3.6.1.7 for Containment Spray 'B', TS 3.6.2.3 for Suppression Pool Cooling 'B', TS 3.7.10 for Emergency Closed Cooling 'B', TS 3.5.1 for LPCI 'B' & 'C', among others). "On October 15, 2009, at 0601 hours, the ESW 'B' pump was started for a planned pump run. At 0718 hours, the ESW 'B' pump tripped for unknown reasons. The determination was made to commence a controlled plant shutdown and power reduction commenced at 1225 hours. This decision was based on the anticipated investigation and repair time of ESW 'B' pump exceeding the TS 3.7.1 Action A 72 hour LCO completion time, and therefore, Action B requires the plant to be in MODE 3 within 12 hours and in MODE 4 in 36 hours. The TS 3.7.1 Action A 72 hour LCO completion time coincides with October 17, 2009, at 1747 hours. "Currently, the plant is expected to be in MODE 3 at approximately 2300 hours on October 15, 2009. "The NRC Resident Inspector has been notified. The State and Counties will also be notified." | 75 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-10-15
45433 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-10-15 05:37 | 2009-10-15 09:06 | 2009-10-15 | MANUAL REACTOR SCRAM DUE TO REACTOR RECIRCULATION PUMP TRIP "At 0537 hours on October 15, 2009, the 'B' Reactor Recirculation pump tripped. The reactor mode switch was placed in shutdown due to rising reactor water level (approx. 49 inches) prior to the Level 8 automatic scram setpoint (52 inches). All controls rods inserted as a result of the manual scram. All systems performed as expected. Reactor water level is being controlled by the motor driven feedwater pump. Main steam isolation valves were manually closed and decay heat was initially controlled through the main steam line drains to the main condenser via the main turbine bypass valves. Reactor Core Isolation Cooling (RCIC) was manually placed into service (tank-to-tank) to assist in RPV pressure control. RCIC is currently being used for decay heat removal. Investigation is underway to determine the cause of the Reactor Recirculation pump trip." The licensee will be contacting the state, and issuing a press release. The NRC Senior Resident Inspector has been notified. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-10-15
45432 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-10-14 15:00 | 2009-10-14 17:09 | 2009-10-14 | SAFETY SYSTEM FUNCTIONAL FAILURE - ALTERNATE SAFE SHUTDOWN SOURCE RANGE NEUTRON MONITOR INOPERABLE "At 1500 hours on October 14, 2009, the power supply for neutron source range detector N-38 was determined to be unable to provide reliable power to detector N-38 and the detector was declared inoperable. Technical Specification (TS) 3.3.4 (Remote Shutdown) Basis Table 3.3.4-1, Function 1.a requires one channel. Technical Requirements Manual (TRM) 3.3.D (Appendix R Alternate Safe Shutdown Instrumentation) requires entry into the condition referenced in TRM Table 3.3.0-1 and entry into the applicable related TS referenced in TRM Table 3.3.D-1 when one or more required functions with one or more required instruments in Table 3.3.D-1 [are] inoperable. TRM Table 3.3.D-1, TRO 3.3.D1, neutron flux (source range only) lists and specifies detector N-38 only and references TS 3.3.4 Basis Table 3.3.4-1, Item 1a. Although there is an operable redundant source range neutron detector N-39, the only source range detector which has indication remote from the control room is N-38. Therefore, the safety function for safe shutdown remote from the control room for reactivity control in accordance with TS Basis Table 3.3.4-1, Function 1a can not be met with N-38 inoperable. The inability to meet the TS condition is a safety system functional failure. Actions are in progress to provide a reliable power supply for N-38. Unit 2 is at 100% and is not affected by the condition." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2009-10-14
45431 | 0 | OHIO DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-12 | 2009-10-14 09:12 | 2009-10-14 | AGREEMENT STATE REPORT - LOST GAUGE FOUND WITH SHUTTER STUCK OPEN The following event was received from the state via e-mail: "A radiation alarm was tripped at PSC Metals from a load of scrap metal coming from Polk Metal and Iron located in Zanesville, Ohio. The load of scrap metal was returned to Polk Metal and Iron. The BRP [Bureau of Radiation Protection] was informed on October 12 and dispatched an inspector to Polk Metal and Iron on October 13. Based on the information on the device [Texas Nuclear model # 5190 SN B5283 containing 200 mCi of Cs-137] the BRP contacted the manufacturer and learned that the device was initially distributed to Producers Service Corporation, also located in Zanesville. "The Producers Service Corporation was contacted and sent a representative to meet the BRP inspector at the Polk site to retrieve the gauge. The inspector surveyed the gauge and found that the shutter was stuck open with an in-beam dose rate of 200 mR/hr at six inches. The shutter mechanism was freed and verified closed by the inspector. The device was transported less than a mile to the Producers Service Corp facility and is now secured in a vacant office in a secured building. The inspector wipe tested the device and found it to be free of contamination. Producers Service Corporation is in the process of contacting the device manufacturer to make disposal arrangements. The device was a generally licensed device distributed on September 9, 1986. "The inspector determined that the device was inadvertently sent to the scrap yard and that Producers Service Corporation was not attempting to illegally dispose of the device. "Device Name: Fixed Gauge Manufacturer: Texas Nuclear Model Number: 5190 Serial Number: B5283" Ohio Report No. OH09-031 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | MAT | [5 empty] | 0 | 2009-10-14
45430 | 0 | INDIANA DEPT OF TRANSPORTATION |  |  |  |  | 2009-10-13 07:00 | 2009-10-13 08:33 | 2009-10-13 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM OFFICE A Troxler Model 3440 (S/N 18635) containing two sources, i.e., 8 millicuries Cs-137 and 40 millicuries Am-241/Be, was stolen from the Indiana Department of Transportation field office in Elkhart, Indiana. The field office was broken into during the weekend and Troxler gauge was found missing from a locked closet. The licensee will conduct an investigation and inform their local law enforcement. The licensee notified the NRC Region 3 Office (Jim Lynch). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Less than Cat 3" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-10-13
45429 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-10-13 07:44 | 2009-10-13 08:20 | 2009-10-13 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PLANNED MAINTENANCE "At 0744 [EDT] on Tuesday, October 13, 2009, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems were removed from service for scheduled maintenance. Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. TSC ventilation system maintenance is scheduled to be completed at 1500 [EDT] on Tuesday, October 13, 2009. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an emergency response facility." The licensee notified the NRC Senior Resident Inspector. * * * UPDATE FROM BUD HINCKLEY TO DONALD NORWOOD AT 1336 EDT ON 10/13/09 * * * "The CNP TSC ventilation system was returned to functional status following scheduled maintenance at 1333 [EDT] on Tuesday, October 13, 2009. "This follow-up notification is being made to provide closure from the initial notification under 10CFR50.72.(b)(3)(xiii) due to the loss of an emergency response facility. The licensee has notified the NRC Senior Resident Inspector of the return to service of the TSC Ventilation System." Notified R3DO (Eric Duncan) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-10-13
45428 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-10-12 16:03 | 2009-10-12 17:22 | 2009-10-12 | NOTIFICATION OF UNUSUAL EVENT DUE TO SMALL FIRE LASTING GREATER THAN 10 MINUTES "At 1551, [the control room] received a 911 notification of a fire in the Condenser area. Entered abnormal procedure 5.1 Incident [and the] fire brigade was dispatched. Follow-up reports indicated that the fire was in the Heater Bay area in the vicinity of B2/B3 heaters. 'At 1556, the Control Room received a report via the Work Control Center from a qualified fire watch on the scene that the fire had been extinguished. "At 1603 the Emergency Director declared a NOUE, on EAL 5.1.1, due to a fire in the Protected Area that takes longer than 10 minutes to extinguish. At the time of the declaration, a six sided search had not yet been conducted in accordance with procedural requirements. "At 1613, the Fire Brigade Leader reported a six sided search of the Heater Bay area was complete, and the fire was declared OUT. "At 1619 the 'all clear' alarm sounded. "At 1638, the Emergency Director terminated the NOUE. "The actual location of the fire was in a pipe chase between B-4 and B-3 Heaters and was caused by hot ceramic pellets from a heating blanket that was above the area of the location of the fire. The heating blankets were being used to pre-heat the piping in preparation for welding. A pigtail that feeds the blanket failed and some of the hot ceramic pellets from inside the blanket dropped down on to the plastic protecting the area below from foreign materials. The hot ceramic pellets on the plastic caused a small (approx. 3 inch diameter) fire. The active fire only lasted for approximately five minutes. "All required notification were completed in a timely manner." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-10-12
45427 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2009-10-12 04:00 | 2009-10-12 12:00 | 2009-10-12 | EMERGENCY OPERATIONS FACILITY INOPERABLE DUE TO LOSS OF VENTILATION "Loss of ventilation to an emergency response facility: Emergency Operations Facility (EOF). "During performance of the EOF diesel generator operability test, the EOF ventilation system was placed in filtration mode. The air conditioning unit and air return fan did not run. Emergency Preparedness personnel evaluated the habitability of the EOF and determined that the filtration mode of the ventilation system was not functional. Because of the loss of the ventilation function for the EOF, the facility was not functional. "The EOF is available for emergency response purposes unless the temperature could not be maintained or a release is in progress. The backup EOF is available for use if needed. Repair of the EOF's ventilation system is in progress. This is reported per 10CFR50.72(b)(3)(xiii)." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM STEVE SAMPLE TO DONALD NORWOOD AT 1620 10/12/09 * * * The EOF was restored to operable status at 1247 CDT. The licensee notified the NRC Resident Inspector. Notified R4DO (Campbell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-10-12
45426 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2009-10-12 03:33 | 2009-10-12 05:33 | 2009-10-12 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO UNIDENTIFIED LEAKAGE FROM RCS "This notification is being provided in accordance with 10CFR50.72(b)(2)(i), plant shutdown required by Technical Specifications. "At 0300 [CDT] on 10/12/09, LaSalle Unit 2 commenced a plant shutdown. At 2333 [CDT] on 10/11/09, LaSalle Unit 2 exceeded the 2 gpm increase in unidentified leakage within the previous 24 hour period of Technical Specification [TS] LCO 3.4.5.d. per required action B.1, unidentified leakage increase was required to be restored to within limits within 4 hours. At 0333 [CDT] on 10/12/09, TS 3.4.5 required action 8.1 was declared not met, and TS 3.4.5 condition C was entered which requires the unit to be in mode 3 within 12 hours and mode 4 within 36 hours. TS LCO 3.4.5, RCS operational leakage requires the plant to be in mode 3 by 10/12/09 at 1533 [CDT] and mode 4 by 10/13/09 at 1533 [CDT]. "The unidentified leakage is currently at 2.3 gpm. Although not physically verified, the source of the leakage is suspected to be from the 2B21-F016, Inboard Main Steam Line drain valve packing. Other primary containment parameters - Drywell Air Temperature, Drywell and Suppression Chamber Pressure, Suppression Pool Average Temperature - remain within TS limits." The licensee expects to enter mode 3 by 1200 CDT on 10/12/09 and mode 4 by 0000 on 10/13/09. The licensee suspects the leakage to be from the Inboard Main Steam Line Drain Valve packing due to an earlier maintenance requiring cycling of that valve. All safety-related systems required for plant shutdown and cooldown are operable. The licensee has notified the NRC Resident Inspector. | 0 | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-10-12
45425 | -1 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2009-10-11 04:50 | 2009-10-11 15:26 | 2009-10-23 | REACTOR WATER LEVEL INDICATION INOPERABLE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS (Emergency Notification System) or under the reporting requirements of 10CFR50.73. "On 10/11/2009 at 0450 MST Palo Verde Nuclear Station Unit 1 declared both trains of the Qualified Safety Parameter Display (QSPDS) inoperable due to the discovery that an installed temporary modification (TMOD) impacted the reactor vessel level indication parameter in a non-conservative manner. The modification jumpered failed heater junction thermal connections (HJTC) at the heated and unheated HJTC points. Unit 1 has two failed detectors with TMODs installed. During a design event where these detectors would be needed, these detectors will not alarm at the correct vessel levels. "The emergency operating procedures use this indication and pressurizer level indications (which are unaffected by this condition) to throttle safety injection flow during certain accidents. With the TMOD providing incorrect indication the operators could throttle flow when full flow should be maintained. "In addition the QSPDS reactor level indication is used in the Emergency Plan to classify emergencies. The standard Appendix 101 to Palo Verde emergency procedures provides guidance for an alternate method for determining reactor vessel level when RVLMS (Reactor Vessel Level Monitoring System) is out of service. This alternate method determines level by manually determining sub-cooled, saturation or superheated conditions based upon input of reactor vessel pressure and the "raw" QSPDS - RVLMS thermocouple temperature indications. This compensatory measure ensures that classification of events can continue to be completed in a timely manner. "Unit 1 has entered the LCO (Limiting Condition of Operation) required action for this condition which requires at least one channel be restored to operable status within 7 days. Unit 2 is in a refueling and is not impacted at this time. Unit 3 does not have the TMOD installed. " According to the licensee Train A TMOD which was installed 2/3/08 and the train B TMOD which was installed 12/12/08. The licensee checked the installation of these TMODs after reviewing operating experience reports from Calvert Cliffs. The licensee has notified the NRC Resident Inspector. * * * RETRACTION AT 1916 EDT ON 10/23/09 FROM BUZARD TO HUFFMAN * * * "On 10/11/2009 at 12:26 MST Palo Verde Nuclear Station Unit 1 reported the inoperability of both trains of the Qualified Safety Parameter Display System (QSPDS) due to the discovery that an installed temporary modification impacted the reactor vessel water level indication parameter in a non-conservative manner. After further Operations and Engineering review it was concluded that the modification, installed due to one inoperable heated junction thermal couple (HJTC) in each train, does not result in the inoperability of either train of QSPDS since the Technical Specification required number of heated junction thermal couples (HJTC) (two each in the upper and lower level indication) remain operable with the temporary modification installed. In addition, the Control Room operators would understand the QSPDS indication and would correctly control the plant per the emergency operating procedures using this indication along with pressurizer level indication to throttle safety injection flow during certain accidents. "The QSPDS reactor level indication is also used in the Emergency Plan to classify emergencies and the modification would not impact this function. "Unit 1 has exited the LCO Condition for two inoperable QSPDS reactor vessel water level instrument channels." The licensee has notified the NRC Resident Inspector. R4DO (Okeefe) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(xiii) |  |  | 0 | 2009-10-11
45424 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-10-10 13:21 | 2009-10-10 14:34 | 2009-12-04 | CONTROL ROOM FILTRATION OUT OF SERVICE FOR MAINTAINANCE "Post maintenance operability testing of the 'A' CREF (Control Room Emergency Filtration) subsystem will result in a planned potential loss of safety function for the CREF for a brief period of time when the 'B' CREF subsystem is simultaneously made inoperable during the testing. Clear guidance for timely restoration of the 'B' CREF subsystem, and therefore, CREF safety function is included in the test procedure. An operator will be dedicated to the testing to ensure that the CREF will perform its safety function if required." The licensee will notify the NRC Resident Inspector. * * * RETRACTION AT 1525 EST ON 12/04/09 FROM COOK TO HUFFMAN * * * "Monticello is retracting the event reported based on further evaluation. An investigation of the event found the removal of the [CREF] system from service was part of a planned evolution for maintenance or surveillance testing and done in accordance with an approved procedure and the plant's TS [Technical Specifications]. In addition, the event would not have prevented the completion of the fulfillment of a safety function since an operator was stationed and briefed that in the event of the start of any transient, the CREF system would be immediately restored to operability and thereby ensure the train would have been available to perform its safety function In its required timeframe. The licensee has notified the NRC Resident Inspector." R3DO (Riemer) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-10-10
45423 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-10-09 15:44 | 2009-10-09 18:07 | 2009-10-09 | OFFSITE NOTIFICATION DUE TO A SPILL OF HYDRAULIC FLUID "On October 9, 2009, at approximately 1544 hours EDT, notification of an oil spill was made to the U.S. Environmental Protection Agency (EPA), National Response Center. At the time of the event, the plant was in Mode 1 at 100% power. The oil spill was the result of delivery activities related to a backhoe that was delivered to the Perry Nuclear Power Plant in the owner controlled area. The spill was initially estimated to be approximately 3 to 5 gallons of a red colored oil resembling hydraulic fluid. With current rainy weather conditions, the resultant sheen covered an area of approximately 20 to 25 feet by 100 feet of gravel and asphalt. The spill drained into two storm drains. The backhoe was moved inside of a building with a concrete floor. Absorbent material and oil selective soak mulch were placed on the area of the spill. Clean Harbors Incorporated (CHI) was contacted for clean up assistance. CHI representatives are providing assistance for clean-up remediation. "Additionally, the Ohio EPA: State Emergency Response Commission, Perry Township Fire Department, Lake County Emergency Planning committee, and the U.S. Coast Guard were notified in accordance with plant procedures. This event is also being reported in accordance with the Operating License, Appendix B, Environmental Protection Plan, which states in part, 'Any occurrence of an unusual or important event that indicates or could result in significant environmental impact causally related to plant operation shall be recorded and reported to the NRC within 24 hours followed by written report. Specifically, unanticipated or emergency discharge of waste water or chemical substances.'" The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-09
45422 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-10-09 03:20 | 2009-10-09 07:17 | 2009-10-09 | OFFSITE NOTIFICATION - SOUTH CAROLINA DEPARTMENT OF LABOR "On October 9, 2009 at approximately 2:30am [EDT] a Wackenhut security services employee was found unconscious and unresponsive within the protected area of V. C. Summer Nuclear Station (VCSNS). On site Medical Emergency Response Team (MERT) responded and administered CPR, oxygen and AED. The non-contaminated patient was transported via ambulance to the Fairfield Memorial Hospital and was pronounced dead at approximately 3:20 am from an apparent pulmonary embolism. The event is reportable per 10CFR50.72(b)(2)(xi). "South Carolina Department of Labor, OSHA, and NRC Senior Resident Inspector are being contacted." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-09
45421 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2009-10-08 14:20 | 2009-10-08 18:06 | 2009-10-08 | AUTOMATIC REACTOR SCRAM DURING TESTING "This report is being made under CFR 50.72(b)(2(iv)(B) for a automatic reactor scram which is preliminarily believed to have been caused while restoring reactor pressure vessel level/pressure instrumentation to service during performance of surveillance test 3.3.3.2-09 Reactor Water Level and Pressure Instruments Calibration . "In addition, this report is being made under CRF 50.72(b)(3)(iv)(A) due to PCIS (Primary Containment Isolation System) Groups 2, 3 and 4 being received when reactor water level dropped below 170 due to the expected level shrink immediately following a reactor scram. All isolations went to completion. Reactor water level was recovered to normal vessel level as expected under post scram conditions. "The following Technical Specification LCOs (Limiting Conditions of Operation) were in affect at the time of the reactor scram: "TS 3.7.5, Required Action A.1, 30 day completion time for 'B' Control Building Chiller; TS 3.7.2, Required Action A.1, 7 day completion time for 'B' River Water Supply loop; TS 3.3.3.1, Function 6, Required Action A.1, 30 day completion time for position indication of MO-1949B, 'B' Residual Heat Removal Heat Exchanger Vent; TS 3.7.1, Required Action A.1, 30 day completion time for 1P22D, 'D' Residual Heat Removal Service Water Pump. "All rods fully inserted during the scram. The plant is in a normal shutdown electrical lineup with offsite sources powering the safety busses. No safety or relief valves lifted during the transient. Decay heat is being removed via the steam bypass [valves to the] condenser. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-10-08
45420 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-10-07 16:41 | 2009-10-08 13:39 | 2009-10-08 | FITNESS FOR DUTY - REPORT OF FAILURE OF RANDOM DRUG TEST NON-LICENSED CONTRACTOR A non-licensed contractor had confirmed positive for illegal drugs a random fitness for duty test. The contractors access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2009-10-08
45419 | 0 | RANCHO SECO |  |  |  |  | 2009-10-08 08:00 | 2009-10-08 11:25 | 2009-10-08 | DISCOVERY OF SITE ACCESS VULNERABILITY A safeguards system degradation was discovered related to site access. Compensatory actions were taken. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 73.71(b)(1) |  |  |  | 1 | 2009-10-08
45418 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-09-23 05:45 | 2009-10-07 21:49 | 2009-10-07 | AGREEMENT STATE REPORT - DEPARTMENT OF ENERGY TRUCK WITH LOW LEVEL WASTE OVERTURNED "On September 23, 2009, at about 5:45am, a truck with a container of building demolition debris waste from the DOE/Navy Knolls Atomic Power Laboratory site in Kesselring, New York overturned near Wilkes Barre, Pennsylvania at mile marker 147.9 on southbound lane of Interstate 81 (I-81), spilling its contents on the median. The debris consisted primarily of concrete, metal with low levels of radioactivity (approximately 50 micocuries of cobalt-60, strontium-90, americium-241, and plutonium-238). The shipper noted the package was below the limits for labeling and placarding as Class 7 hazardous material set by the U.S. DOT in their hazardous material regulations in 49CFR. The 'low-level waste' was being shipped to the Savannah River Site for disposal. "The final field radiological surveys and labs tests of soil samples support the conclusion that no measurable radioactivity remains at the scene and that all equipment used in the response and recovery were free of detectable surface contamination prior to release from the scene. All final surveys after clean-up were less than the investigation level." PA incident #PA090030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-10-13
45417 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-10-01 | 2009-10-07 19:46 | 2009-10-07 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The following report was received via e-mail: "An exit sign containing tritium was discovered missing from the MEDRAD facility located at 150 Victory Road in Saxonburg, PA (Butler County) on the evening of October 1, 2009. The sign was an Isolite product with 11.5 curies of H-3; two were purchased less than a year ago. The company interviewed employees and conducted an internal investigation to determine what happened to the sign; they are still uncertain about how it was lost. MEDRAD plans to return the other sign to Isolite. "MEDRAD contacted Isolite and they could not find any record of the tritium exit signs in their database. MEDRAD had received the two tritium exit signs via an electrical contractor, who in turn installed the exit signs at MEDRAD. "The State will continue to keep NRC informed of the status of our investigation." PA incident # PA090031 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-10-13
45416 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2009-10-07 19:30 | 2009-10-07 19:33 | 2009-10-07 | DISCOVERY OF A CONTAINMENT SEPARATION "Crystal River Unit 3 is currently shutdown for a planned refueling and steam generator replacement outage. During containment building concrete removal activities to create a construction opening to support steam generator replacement, a separation in the concrete was discovered in the vicinity of the construction opening near the periphery of the containment. The Crystal River Unit 3 containment is a steel lined, post tensioned concrete structure nominally 42 inches thick. Post tensioning is achieved utilizing an outer array of horizontal tendons immediately adjacent to an inner array of vertical tendons. The separation is generally in the plane of the horizontal tendons. Inside the separation is 30 inches of concrete and the steel liner plate. This condition has been evaluated relative to current plant conditions and found to represent no degradation in safety. Crystal River Unit 3 personnel in conjunction with industry experts are currently performing a detailed analysis of this separation to determine the cause, extent of condition, the impact on the containment building function and any required repairs prior to plant restart. Operating experience reports are being prepared to share our information with the industry. The station will provide updates as we gain more information concerning this issue." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2009-10-07
45415 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2009-10-07 03:20 | 2009-10-07 04:36 | 2009-10-07 | OFFSITE NOTIFICATION TO THE STATE OF FLORIDA AND THE NATIONAL RESPONSE CENTER "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to notification of other government agencies at 0320 EDT on 10/7/09. "Florida Power and Light Company (FPL) has identified a Sodium Hypochlorite spill within the protected area at Plant Saint Lucie. The spill has been terminated and it is estimated that up to 240 lbs of Sodium Hypochlorite was spilled past the secondary containment of the hypochlorite tank. The precise volume of the spill is indeterminate at this time. "This event poses no health or safety consequences to either on site personnel or the general public. Notification to the State of Florida Emergency Response Commission and the National Response Center was made in accordance with the Plant Saint Lucie hazardous material spill response procedure." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-07
45414 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-05 10:30 | 2009-10-06 11:11 | 2009-10-06 | AGREEMENT STATE REPORT - INDUSTRIAL RADIOGRAPHY SOURCE RETRACTION INCIDENT The following event was received from the state via e-mail: "On October 5, 2009 at approximately 1030, radiographers working for Stork Twin City Testing in a tunnel at a steam plant in St. Paul, Minnesota were unable to retract the 75 curie Iridium-192 source (serial number 56177B) of their AEA Model 660B exposure device (serial number 2657). The radiographers had the device placed on a ladder approximately six feet off the ground during this and two previous exposures. Following several attempts to retract the source the device fell from the ladder landing on the control cable. The Radiation Safety Officer was contacted at approximately 1045. The radiographers established boundaries of approximately 2 mR/h and maintained control over the area. The Radiation Safety Officer placed several layers of lead over the device and the cable to reduce the exposure levels, but he still considered the levels too high to safely work on releasing the source. Minnesota Department of Health (MDH) Radioactive Materials Unit was notified at approximately 1215. The University of Minnesota's Health Physics staff was contacted and offered to bring additional lead shielding to the area. MDH and University of Minnesota staff arrived at the location at approximately 1250. Following placing additional shielding around the device the Radiation Safety Officer made another attempt to release the source, but was unable to get the source back into the device. QSA Global was contacted for technical support at approximately 1430. At approximately 1530 the Radiation Safety Officer removed two pins from the back of the exposure device and was able to manually pull the cable and secure the source in the device. Following surveys of the device to determine the source was in the device, the control cable was examined. Damage to the cable at the point where the metal tip connects to the cable was discovered. The exposure device was transported back to Stork Twin City Testing and will be inspected and tested October 6, 2009. The Radiation Safety Officer will submit a complete report to MDH within 30 days. Personal dosimetry readings were 90 mR for the Radiation Safety Officer and approximately 80 and 30 mR for the radiographers." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2009-10-09
45413 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-10-04 15:00 | 2009-10-05 15:55 | 2009-12-03 | UNPLANNED CONTAMINATION DURING STARTUP "On 10/04/2009 at 1500 C-331 unit 2 cell 2 was being charged and placed on stream and had just gone above atmospheric pressure when a Maintenance Mechanic observed smoke coming from the cell instrument cubicle and determined it to be UF6 outleakage from cell process instrumentation. To stop the release the cell was immediately taken back below atmospheric pressure. Investigation revealed that a UF6 release had occurred inside the instrument cubicle. The amount of material released has not yet been determined. Decontamination is underway but has not been completed inside the cabinet. The area outside the cabinet has been decontaminated. No injuries or personnel exposure occurred as a result of this event. This is being reported based on 10 CFR 76.120(c)(1)(i) (unplanned contamination event). "PGDP Problem Report Nos. ATRC-09-2435; PGDP Event Report No. PAD-2009-016. Responsible Division: Operations "PGDP Assessment and Tracking Report No. ATR-09-2435; PGDP Event Report No. PAD-2009-16; Worksheet No. Responsible Division: Operations "The NRC Senior Resident Inspector has been notified of this event." Decontamination is expected to be completed on 10/6/2009. * * * RETRACTION FROM CALVIN PITTMAN TO VINCE KLCO ON 12/03/09 AT 1551 EST* * * "After further review, it was determined that the amount of contamination was significantly less than five times the lowest annual limit on intake specified in Appendix B to Section 20.1001-20.2402 of 10CFR20 for the material." The licensee notified the NRC Resident Inspector. Notified the R2DO (Guthrie) and NMSS (Whaley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2009-10-05
45412 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2009-10-05 11:58 | 2009-10-05 14:41 | 2009-10-05 | MANUAL SCRAM AND HIGH PRESSURE COOLANT INJECTION FOLLOWING A LOSS OF FEEDWATER LEVEL CONTROL "At 1158 on Monday, October 5, 2009, Nine Mile Point Unit One was manually scrammed from approximately 100% rated power due to failure of the Feedwater Level Control System, in anticipation of a reactor scram. Following the manual scram insertion at 11:58, High Pressure Coolant Injection (HPCI) System automatically initiated on low Reactor Vessel (RPV) level. At 11:59, RPV level was restored above the HPCI System low level actuation setpoint, and the HPCI System initiation signal was reset. At Nine Mile Point Unit One, a HPCI System actuation signal on low RPV level is normally received following a reactor scram, due to level shrink. "Unit 1 has commenced cooldown, in preparation for the forced outage to commence repairs. Reactor water level is being controlled in the normal operating band; reactor temperature is 450?F and reactor pressure is approximately 500 psig. "10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours when any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical. "10 CFR 50.72(b)(3)(iv)(A) requires reporting within 8 hours when a valid actuation of the High Pressure Coolant Injection System occurs." All control rods fully inserted. All systems functioned as required following the reactor scram. The reactor is currently stable in Mode 3. HPCI has been secured. Makeup water is being provided by the Reactor Feedwater System and decay heat removal is through the bypass valves to the condenser. There was no impact on Unit 2 and the plant is in a normal post-scram electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-10-05
45411 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-08-03 | 2009-10-05 10:06 | 2009-10-05 | AGREEMENT STATE REPORT INVOLVING SEVENTEEN LOST TRITIUM EXIT SIGNS The State of Nebraska was notified by a Bed Bath & Beyond representative that they are unable to account for a total of 17 tritium exit signs (which are general licensed materials). These 17 signs were part of an order that went to three separate Bed Bath & Beyond store locations in the Omaha, NE area. The Bed Bath & Beyond representative informed the state that Bed Bath & Beyond has performed an extensive search and considers the signs not to be present at the stores. - Sixteen (16) signs are Safety Light Corporation Model SLX60 and contain 11.5 Ci/each H-3. The serial numbers of these 16 missing signs are as follows: 302790, 302792, 302793, 283015, 302799, 302800, 302810, 302803, 397719, 397720, 397721, 397722, 397725, 397726, 397728, and 397730. - One (1) sign is Safety Light Corporation Model 2040 and contains 11.5 Ci H-3. The serial number for this sign is #257964. NE Item Number NE090012 (Store #771-GL0634), NE090013 (Store #1021-GL0654) and NE090014 (Store #1184-GL0605). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-10-08
45410 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-10-03 14:00 | 2009-10-04 02:23 | 2009-10-05 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE At approximately 1400 CDT on 10/3/09, a Terracon Consultants Ford Ranger pickup truck was stolen from the Powell Replacement Elementary School construction site in Chicago, IL. In the bed of the truck was a Troxler Model 3430 Moisture Density Gauge. These gauges typically contain two (2) radioactive sources; 8 millicuries Cs-137 and 40 millicuries Am-241:Be. The Chicago Police Department was informed of the theft and subsequently located the abandoned vehicle approximately two (2) miles away from the construction site at about 2300 CDT on 10/3. The vehicle had been ransacked and both the storage container and gauge were missing. The Illinois Emergency Management Agency informed the Illinois State Police (ISP) Statewide Terrorism and Intelligence Center (STIC) and will followup with additional details as they become available. * * * UPDATE FROM PAUL EASTVOLD TO JOE O'HARA AT 0934 ON 10/05/09 * * * The serial number of the missing Troxler Model 3430 Moisture Density Gauge is S/N 32686. The state also confirmed the quantities of material in the gauge. Notified R3DO(Daley), FSME(Villamar), and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-10-07
45409 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-10-03 17:34 | 2009-10-03 20:26 | 2009-10-03 | AUTOMATIC REACTOR SCRAM FOLLOWING MSIV CLOSURE "On 10/03/09 at 1734 CDT, Unit 3 scrammed due to a Group 1 MSIV closure. The cause of the event is being investigated. The 2/3 Emergency Diesel Generator also auto-started during the event. The cause of the auto start is also being investigated." All rods fully inserted. The reactor is currently stable in Mode 3 with makeup water coming from the control rod drive system and decay heat removal from the isolation condenser. All systems functioned as required with the exception of the unexplained MSIV closure and the auto start of the 2/3 EDG. There was no impact on Unit 2 and the plant is in a normal post-scram electrical lineup. There was no need for the 2/3 EDG to auto-start and it did not load. Group 2 and 3 isolations were also received during the transient which is expected and normal. Reactor water level is being maintained between 8 and 48 inches and pressure between 800 and 1060 psi. Investigation of the cause of the MSIV closure is in progress The licensee stated that there were no activities or surveillances in progress at the time that could have caused the MSIV closure. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-10-03
45408 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-10-02 08:00 | 2009-10-02 18:00 | 2009-10-02 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received from the State of California via e-mail: "On October 2, 2009, the California Radiologic Health Branch was contacted by Romig Engineers, Inc. Radiation Safety Officer via California Department of Public Health duty officer at 09:30 am. The call was to report that one moisture density gauge which belongs to Romig Engineers, Inc, License # 7223-41, office and storage location at San Carlos, CA, was stolen. "The Radiation Safety Officer stated that on October 1, 2009, the gauge user checked out CPN, model MC1-DR, S/N 30807119, containing a licensed material Cs-137, 10 mCi and Am/Be 15 mCi, moisture density gauge from the storage location, and transported using his personal vehicle to his residence at San Jose , CA, to be used in San Jose area the following day. "On October 2, 2009, as the gauge user was going to his parking garage he found out that his personal vehicle containing the CPN moisture density gauge was stolen. The gauge user contacted the Radiation Safety Officer and the San Jose Police Department. Police report case number is 09-275-026. Reward to retrieve the gauge is going to be posted in local newspaper and Craigslist. RHB will perform a follow-up on this matter." CA Report 100209 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-10-07
45407 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2009-10-02 13:30 | 2009-10-02 17:14 | 2009-10-02 | 24 HOUR REPORT ON PROCESS EXHAUST HEPA FILTER DAMAGE "At approximately 1330 hours on 10/1/09 during a follow-up investigation of an event which occurred at mid-day on 9/27/09, conditions were discovered that may have met the criteria for reporting in accordance with 10 CFR 70.50.b.2. "The incinerator was shutdown on 9/25/09 in preparation for performing dioctyl sebacate (DOS) efficiency testing on 9/27/09 of the final HEPA filters in K50 Solid Waste Uranium Recovery (SWUR) exhaust gas treatment system. At approximately noon that Sunday, an event occurred that, in hindsight, was a probable fire in the packed column scrubber in the exhaust gas treatment system. This event was terminated in a timely fashion by reinitiating water flow to the packed column. Indications of high heat and possible fire in the packed column included high temperatures and observed 'smoke' from mechanical flanges on the downstream ducting of the packed column. Subsequent to the observed high heat event in the packed column, high temperatures of the downstream north HEPA housing (in-service) were observed. The high temperatures in the HEPA housing were believed to be from the high heat event in the packed column. The continuous airborne effluent sample for the K50 stack (downstream of HEPA filters) was counted to evaluated whether a release had occurred. The results of the sample were at the low end of the normal range for this stack, indicating no active release had occurred. "Continuous monitoring of the system assured the termination of the packed column and HEPA housing high heat events. The systems were continuously monitored and cooled down to near ambient conditions on Monday, 9/28/09. On Monday morning a valve was removed between the quench column and the packed column of the scrubber system. The valve on the packed column side showed high heat damage. A visual inspection on the bottom of the packed column indicated significant degradation of the internals, including the lower fiberglass distribution plate and high surface area polypropylene balls. This evidence points to a high heat event/fire within the packed column. The ignition source is still under investigation as the furnace was completely cold. There is an electric re-heater mounted immediately above the packed column which may have been the ignition source. Disassembly of the packed column is awaiting access platform construction. "Continuing the investigation on 10/1/09 at approximately 1330 hours the HEPA filter housing was opened for inspection. This inspection found significant deterioration of one of the two HEPA units in each of the primary and final banks. The loss of both the primary and final HEPA units constituted a loss of equipment in accordance with 10 CFR 70.50.2. "A Condition Report in the Corrective Action Program has been initiated and a causal analysis is being performed. The system continues to be in a shutdown condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2009-10-02
45406 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-10-02 11:49 | 2009-10-02 15:14 | 2009-10-02 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTIVATION OF EMERGENCY SIRENS "At approximately 1149 CDT, on October 2, 2009, a Goodhue County Dispatch Supervisor inadvertently activated the Red Wing [Minnesota] sirens from the backup unit during conduct of a silent siren test. The backup unit was being tested to ensure proper siren function prior to work on the primary unit. "Twenty-six of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for less than 10 seconds. No press release is planned by Goodhue county or Xcel Energy. "The NRC Resident Inspector was notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-10-02
45405 | 0 | TENNESSEE VALLEY AUTHORITY |  |  |  |  | 2009-10-02 | 2009-10-02 12:53 | 2009-10-02 | SHUTTER ON NUCLEAR GAUGE FAILED TO CLOSE "It was discovered on October 1, 2009, that a twenty-four hour event notification was not reported. The notification was required per 10 CFR 30.50(b)(2) due to [the] inability to close a fixed gauge shutter at TVA's (Tennessee Valley Authority) Widows Creek Fossil Plant. The gauge is a Texas Nuclear unit and contains 100 mCi of Cesium-137. The gauge is used to monitor the slurry surge tank in the U7 and U8 Limestone Ball Mill Building." This gauge is used under an NRC license to TVA at the Widows Creek Fossil Plant in Stevenson, Alabama. "The shutter failure discovery was made during a routine shutter check on August 4, 2009. Corrective actions were taken to repair the shutter and the shutter check was successfully completed on August 17, 2009. No personnel radiation exposure was received. These corrective actions were reported in the Corrective Action Program." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | TN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-10-02
45404 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-10-02 06:49 | 2009-10-02 10:28 | 2009-10-02 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP POSSIBLY CAUSED BY A FAULTED MAIN GENERATOR BREAKER "At 0649 [EDT] The VC Summer Nuclear Station automatically tripped due to a turbine trip. The cause of turbine trip is under investigation. Preliminary review indicates a possible failure of one phase of the main generator breaker. The three emergency feedwater pumps automatically started on Lo-Lo steam generator level. Preliminary review indicates all primary and secondary systems responded as required. "The plant is in mode 3 with normal RCS pressure and temperature. Decay heat is being removed by dumping steam to the condenser. The station will remain in mode 3 until repairs are complete. Estimated restart date has not been determined." All control rods fully inserted. The plant is in a normal post-trip electrical lineup with the exception of the balance of plant buses which are on the alternate electrical source. The licensee will inform State and local agencies and has informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-10-02
45403 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2009-10-01 22:39 | 2009-10-02 04:18 | 2009-10-02 | UNIT EXPERIENCED A VALID RPS ACTUATION DURING PLANT COOLDOWN ON LOW STEAM GENERATOR LEVELS "On Thursday, October 1, 2009 @ 2239 hrs EDT Seabrook Station Unit 1 was in Mode 4 in the process of removing feedwater heating and raising steam generator levels during a plant cooldown. A valid actuation of the reactor protection system occurred when both the A and C steam generator [SG] levels were reduced to the SG low level reactor trip setpoint of less than 20%. This occurred twice on both the A and C steam generators approximately 10 minutes apart. Steam generator levels have since been restored to normal operating levels and plant is now in Mode 5. "This is reportable under 50.72 (b)(3)(iv) as an event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. The reactor trip breakers were open and the emergency feedwater system removed from service when the event occurred. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-10-02
45402 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2009-09-30 19:10 | 2009-10-01 19:49 | 2009-10-01 | 24 HOUR REPORT ON PROCESS EXHAUST HEPA FILTER DETERIORATON "On September 30, 2009 at approximately 1910 (PDT) an Air Balance Tech at AREVA NP's Richland fuel fabrication plant discovered that the primary and secondary HEPA filters servicing the ammonium diuranate (ADU) area showed visible signs of deterioration. The apparent deterioration is being reported in accordance with 10CFR70.50.b.2. "The K32A HEPA filters were examined at approximately 1910 PDT on September 30, 2009 based on a request to follow up on some observations the previous day of a dusting of powder and very low contamination downstream of the filters. Air flow was diverted to HEPA filters in a parallel upper housing in order to check the filters in the lower housing. Investigation showed apparent deterioration, cracked creases, of both the primary and final HEPA's. "At approximately 2030 PDT the same day EHS&L personnel were informed of the event. The only processes running at the time were the Mop Water Furnace and Cylinder Wash. EHS&L ordered that these be shut down. Air monitor samples were pulled on the K-32A system. Air monitoring samples showed negligible release levels. A Health Safety Technician survey of the downstream side of the final HEPA housing of K-32A revealed no contamination. "Potential dose to a member of the public and the effect on the environment are essentially negligible. External conditions are not known to have affected the event. "A Corrective Action Report was written on October 1, 2009. The cause of the apparent deterioration is under active investigation. Steps to prevent recurrence will be developed as appropriate." The licensee stated that records indicate that the primary filter was changed out in August and the final filter was changed out in March. The licensee will notify the State and the NRC regional contact. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2009-10-01
45401 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-10-01 | 2009-10-01 18:11 | 2009-12-08 | AGREEMENT STATE - ADMINISTERED RADIATION TREATMENT TO WRONG AREA The following was received via email: "On October 1, 2009, the Agency was notified by the licensee that a patient had received 13 of 25 fractions to the wrong breast. The patient received 2,340 centigrays by the time the error was discovered. The Radiation Safety Officer stated that he had just fount out about the event and no additional information was available. Additional information will be provided as it is obtained." Texas Incident #: I-8676 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM ART TUCKER TO DAN LIVERMORE ON 12/08/2009 AT 1705 * * * The following was received via email: "This event involved an exposure to a patient from a linear accelerator and should not have been reported to the NRC; therefore, the Agency [Texas Department of Health] is retracting this report." Notified R4DO (Spitzberg) and FSME EO (Einberg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-10-07
45400 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-09-30 | 2009-10-01 16:19 | 2009-10-01 | AGREEMENT STATE REPORT - SHUTTER ON NUCLEAR GAUGE FAILED TO CLOSE The following information from the State of Illinois Emergency Management Agency via e-mail: "On September 30, the facility's radiation safety officer contacted the Agency to advise that a fixed gauge had failed to operate as intended. While performing routine safety and shutter condition checks, attempts to close the shutter on the level gauge were not successful. The gauge is operated in an elevated, open environment on a polymer process vessel and there are no occupiable workstations in the area. The safety officer reports that they believe the shutter could be rotated to the closed position if additional force were applied to the shutter arm. However, previous experience has shown such actions could result in the arm becoming sheared from the shutter. Attempts to apply additional lubricant and remove debris from the pathway not otherwise readily observed, did not improve the extent of closure. "The process vessel involved is continuously operated and not scheduled for any routine maintenance at this time. The licensee continues to operate the line at this time with the shutter open. Warning notices have been posted near the gauge regarding the shutter operation and all operational supervisors and personnel responsible for the line have been made aware of the condition. Should an emergency condition exist the licensee is prepared to remove the gauge from the vessel and apply additional shielding. Arrangements are pending with the manufacturer to come on-site to perform an evaluation of the three year old device and make the necessary repairs or replace the device as necessary. Similar failures of this device have been noted in the past. The manufacturer states the common cause for those failures is poor or non-existent maintenance, operation of the gauge outside of its approved conditions and/or attempting to force operation of the shutter handle. "The licensee indicated the necessary written report would be filed within the next 30 days. " The gauge involved is an Ohmart Model SHF2 (S/N 74932) with a 80 millicurie Cs-137 source. See similar event report EN#45399 involving an Ohmart gauge with a stuck open shutter. Illinois Report Number IL0900075. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-10-06
45399 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-09-30 18:00 | 2009-10-01 15:43 | 2009-10-01 | AGREEMENT STATE REPORT - SHUTTER ON NUCLEAR GAUGE FAILED TO CLOSE The following was received via E-mail: "On October 1, 2009, the Agency [TX Dept. of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) that while conducting a routine shutter check on an Ohmart/Vega Corp. SHF1 nuclear gauge containing 20 millicuries of Cesium (Cs) 137, the shutter failed to close. The RSO stated that the gauge had been installed on the vessel in June of 2009. He was performing the check now to get this gauge into the same inspection schedule as the other gauges they use. He stated that the gauge is stuck open in the normal operating position and a survey conducted in the area indicated that dose rates were normal. He stated that there was no other damage to the gauge. He stated that he thought the mechanism may have become fouled from work conducted on a piece of equipment in the area. The manufacturer was contacted and is scheduled to perform repairs and training on October 21, 2009. The gauge is currently tagged 'Do Not Operate.' Additional information will be provided as it is received." See similar event report EN# 45400 involving an Ohmart gauge with a stuck open shutter. Texas Incident #: I-8675. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-10-06
45398 | 0 | TRANSNUCLEAR INC |  |  |  |  | 2009-10-01 | 2009-10-01 14:13 | 2009-10-01 | FASTENERS ON SPENT FUEL STORAGE DEVICES DID NOT MEET STANDARDS "In accordance with 10 CFR 21.21, Transnuclear, Inc. is reporting a potential Part 21 violation. Transnuclear, Inc. has reason to believe that Hwa Shin Bolt Ind. Co. provided unsubstantiated certified material test reports (CMTR's) for certain small parts utilized in products fabricated in accordance with the requirements of 10 CFR 72 under general certificates 1004 and 1030. Transnuclear is in the process of performing a 10 CFR Part 21 [evaluation] but does not believe that this issue has safety significance. TN [Transnuclear] is reporting this issue because Hwa Shin may have supplied parts to others that may have safety significance. "The parts were provided by Hwa Shin Bolt Ind. Co., Ltd. Having offices in Busan, Korea under subcontract to Hitachi Zosen Corporation, Ariake Works located in Kumamoto, Japan. Hitachi Zosen fabricated the components under contract to Transnuclear, Inc. "A preliminary review of the fabrication records at Hitachi Zosen indicate that shipped components have parts supplied by Hwa Shin Bolt Ind. Co. as indicated in Attachment 1. "No [dry storage canister] loadings have occurred at Cooper or Ginna. We are not certain of which [dry storage] canisters have been loaded, if any, at the other plants. "All Hwa Shin material at the Hitachi Zosen facility has been identified and placed under the control of the Hitachi Zosen NCR system. No material received from Hwa Shin is being released for further use in fabrication of Dry Storage Canisters (DSCs) or other components subject to the requirements of 10 CFR 72. Nonconformance Reports (NCRs) are being issued for all components that contain Hwa Shin Material." The licensee reported affected plants include Millstone, Susquehanna, Oyster Creek, Ginna, Brunswick, and Cooper. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MD | OTH | PAR | 21.21 |  |  |  | 0 | 2009-10-01
45397 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-09-21 | 2009-10-01 13:04 | 2009-10-01 | AGREEMENT STATE REPORT - DOSE TO EMBRYO GREATER THAN 5 REM The following was received via E-mail: "On September 30, 2009 the licensee's radiation safety officer contacted the Agency [Illinois EMA] to advise that a dose to an embryo likely to have exceeded 5 Rem occurred as a result of an administration of I-131 to a mother under going thyroid treatment. Twenty five milliCi of I-131 was administered on September 21, 2009. As per hospital protocol, the patient had undergone [pregnancy] screening consisting of interviews and a urine based pregnancy test with negative results. Eight days subsequent to the administration, the patient missed an expected [menstrual] cycle and conducted a home based [pregnancy] test with positive results. Those test results were confirmed with a positive serum based test on that same day administered by her physician. "The authorized user estimates the embryo would potentially have progressed as much as 3 weeks at that time. TEDE estimates are roughly 6.7 Rem to the embryo, with no thyroid likely to have developed at this stage of pregnancy. The confirmed presence or absence of permanent functional damage is unknown, but the expectation is that there would no effect on the embryo. The patient was advised of this information the same day and further advised that a spontaneous termination was still a potential due to the early developmental stage involved although the radionuclide would not likely play a role in that outcome. "As a matter of practice, the radiation safety office is investigating details regarding this specific event to ensure all expected procedures were followed. Based on the initial report, no apparent violations are noted, nor any failures made that would have prevented the event from occurring. A formal report will be submitted within the required 15 days. At this time, no general corrective measures are anticipated but the event will be used as an opportunity for refresher training and a risk audit." Illinois Report #: IL-0900074. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-10-06
45396 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2009-09-30 | 2009-09-30 15:41 | 2009-09-30 | AGREEMENT STATE REPORT - PATIENT GIVEN A THERAPEUTIC DOSE VICE A DIAGNOSTIC DOSE The following information was received from the Commonwealth of Virginia by facsimile: "On September 30, 2009 a patient was given a therapeutic dose of I-131(100 mCi) instead of a diagnostic dose as prescribed (4 mCi). The patient was previously given a therapeutic dose in August of 2008 and a follow up diagnostic visit was scheduled for September 30, 2009. During scheduling, the dose was incorrectly entered as therapeutic instead of diagnostic. The licensee notified the patient's physician and consulted with the patient. The licensee notified their risk management group and has begun an investigation into the event. The licensee was informed to provide RMP [Radioactive Materials Program] with a written report within 15 days. "Event Report Number: VA-09-04." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2009-10-06
45395 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-09-30 15:21 | 2009-09-30 15:38 | 2009-09-30 | OFFSITE NOTIFICATION TO VARIOUS GOVERNMENT AGENCIES "Voluntary notifications, a press release, and a webinar are being made to various government agencies and the media to provide information regarding the installation of temporary structures on top of earthen embankments of the Fort Loudoun, Tellico, Cherokee and Watts Bar dams. These dams are on the Tennessee River System. Recent upgraded flood modeling indicates that there is a possibility for overtopping to occur on these dams during a hypothetical extreme flooding scenario in the winter/spring period. As a precautionary measure, TVA is effectively raising the height of some of the dams in certain areas. These precautionary measures ensure that the TVA nuclear sites (Sequoyah, Watts Bar and Browns Ferry) will remain within their original licensing basis. "Currently, Sequoyah Units 1 & 2 (DPR-77 & 79) and Browns Ferry Units 1 & 3 (DPR-33 & DPR-68) are operating at 100% power, Browns Ferry Unit 2 (DPR-52) is in Mode 4. Watts Bar Unit 1 (NPF-90) is shutdown for refueling." The licensee has notified the NRC Resident Inspectors at each of these sites. The licensee's corporate management is issuing a press release. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-30
45394 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-09-30 11:09 | 2009-09-30 14:11 | 2009-09-30 | MANUAL REACTOR SHUTDOWN DUE TO HYDROGEN IN-LEAKAGE TO STATOR WATER COOLING SYSTEM "At 11:09 EDT 09/30/09, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to hydrogen gas in-leakage into the stator water cooling system from the main turbine generator. The scram was uncomplicated, and all control rods fully inserted into the core. The lowest reactor vessel water level reached was 122 inches, and as expected, HPCI & RCIC did not actuate. No safety relief valves (SRV) actuated. Reactor water level is being controlled in the normal band using the control rod drive and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The cause of the increased hydrogen gas in-leakage into the stator water cooling is under investigation. At the time of the manual scram all Emergency Core Cooling Systems and Emergency Diesel Generators were operable, and no significant safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-09-30
45393 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-08-25 | 2009-09-30 09:41 | 2009-09-30 | AGREEMENT STATE REPORT - POTENTIAL EXCESSIVE EXPOSURE This information was received from the State by facsimile "On September 23, 2009, Accurate NDE reported an over-exposure to an industrial radiographer. On August 25, 2009, Accurate NDE was informed by Landauer that an employee's badge showed a dose of 4990 mrem for the July 2009 wear period. This put the radiographer's yearly dose up to 6243 mrem for 2009. The employee stated to Accurate NDE that there was no equipment malfunctions or unusual circumstances during the month of July. The radiographer also stated that his pocket dosimeter did not go off scale during radiographic operations. A review of the daily radiation dose revealed nothing abnormal according to Accurate NDE. This incident is under investigation." Louisiana Incident Number: LA090018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-10-05
45392 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-09-20 18:00 | 2009-09-30 04:30 | 2009-09-30 | INVALID ACTUATION FROM A SURVEILLANCE ACTIVITY TEST SIGNAL "On Sunday September 20, 2009 @ 1800 hrs EDT the Vogtle Electric Generating Plant Unit 1 was in Mode 5 and performing testing for Containment Ventilation Isolation. A jumper was installed per operations procedure 14238-1 for this testing. The jumper was inadvertently dislodged resulting in a B Train Containment Ventilation Isolation (CVI). There was not a valid radiation alarm signal present; only a test signal. Per Technical Specification 3.3.8 this function is applicable in MODES 1, 2, 3 and 4. The actuation occurred during a maintenance activity and was not from a valid signal. "This is reportable under 50.73 (a)(2)(iv) based on the following: Per 50.73(a)(2)(iv)(A), 'Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, except when: (1) The actuation resulted from and was part of a pre-planned sequence during testing or reactor operation; or (2) The actuation was invalid and: (i) Occurred while the system was properly removed from service; or (ii) Occurred after the safety function had been already completed.' "The event occurred during a surveillance activity and resulted in an invalid actuation from a test signal. The actuation was invalid and the system was not removed from service during this activity. The actuation was considered complete and successful. The CVI signal for Train B automatically isolated the containment ventilation system as designed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-09-30
45391 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-09-29 23:23 | 2009-09-30 04:09 | 2009-09-30 | UNIT 2 MANUALLY SCRAMMED AFTER TRIP OF AN OPERATING CONDENSATE PUMP AND RAPIDLY LOWERING RVWL "On 9/29/09, at 2323 [hours] Unit 2 was manually scrammed due to loss of one of the remaining two Condensate Booster Pumps due to low pump suction pressure. The cause for the Condensate Booster Pump low suction pressures is unknown at this time, but is under investigation. The operating crew was removing feedwater pump 2B from service when the condensate booster pump tripped. The condensate booster pump 2C was already out of service to support maintenance. After the reactor was scrammed manually, reactor water level lowered below the automatic scram set point (+2 inches) and below the automatic start for HPCI and RCIC (-45 inches). All expected Primary and Secondary Containment Isolation valves operated as required, isolation groups 2, 3, 6 and 8 were actuated. Both reactor recirculation pumps tripped due to the low reactor water level. HPCI and RCIC actuated as expected to restore reactor water level. Reactor pressure control was maintained on the turbine bypass valves, and no Main Steam Relief Valves (MSRVs) were opened as a result of the transient. "At this time the unit is stable in mode 3. Reactor water level is being controlled using one Reactor Feedwater pump. HPCI and RCIC have been returned to standby readiness. Reactor pressure is being automatically maintained by the main turbine bypass valves. "This event is reportable as a 4 hour non-emergency report due to 10CFR50.72(b)(2)(iv)(A) and (B) (ECCS discharge to the reactor and Reactor Protection System (RPS) actuation) and as an 8 hour non-emergency report due to 10CFR50.72(b)(3)(iv)(A) (specified system actuations)." Lowest observed Reactor Vessel Water Level (RVWL) was -50 inches. Following actuation of HPCI level recovered to +51 inches and then returned to the normal operating band of +33 inches. Safety-related equipment out-of-service prior to the scram included Core Spray Loop 1. All control rods fully inserted. Unit 2 is in a normal post scram electrical lineup. The licensee informed the NRC Resident Inspector and does not plan a press release. * * * UPDATE FROM MIKE HUNTER TO JOE O'HARA AT 1508 ON 9/30/09 * * * "The initial notification made at 0409 hours ET on September 30, 2009, reported that the RCIC system actuated as expected in conjunction with the HPCI to restore Reactor Pressure Vessel (RPV) water level. However, during a review of plant data, BFN [Browns Ferry Nuclear] determined that after receiving a valid actuation signal, RCIC failed to inject to the RPV. The cause of the failure is under investigation. "The licensee informed the NRC Resident Inspector of the update and does not plan a press release." Notified R2DO(Ernstes). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ECCS INJECTION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(A) |  | 0 | 2009-09-30
45390 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-09-29 18:50 | 2009-09-29 20:46 | 2009-09-29 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO UNIDENTIFIED LEAKAGE FROM RCS "At 1850 hours CDT, operators initiated a plant shutdown required by Technical Specification 3.4.5, Reactor Coolant System (RCS) Operational Leakage, due to a greater than 2 gpm increase in unidentified leakage within the previous 24 hours in MODE 1. "At 1544 hours CDT, a control room operator noticed drywell pressure increased from 0.68 to 0.81 psig. At 1552, the drywell cooler differential temperature alarm actuated, drywell cooling HVAC chiller amps increased from 50 amps to 56 amps, and the Fission Product Monitor particulate and iodine indications were trending up. At 1555, operators entered the abnormal coolant leakage procedure and evacuated containment. At 1615, drywell floor drain leakage rate alarm actuated. At 1616, plant entered the 4-hour Technical Specification action to verify the source of the unidentified leakage source is not due to service sensitive type 304 or type 316 austenitic stainless steel. "At 1730, operators started a power reduction in an attempt to verify the source of the leak. At 1850, the leakage source could not be verified to not be service sensitive stainless steel; entered TS Required Action to be in MODE 3 within 12 hours and MODE 4 within 36 hours. A reactor shutdown has been initiated. At 1930 floor drain leakage (unidentified leakage) was 3.3 gpm and stable. MODE 3 is expected to be entered by 0350 hours on 9/30/09." The licensee has notified the NRC Resident Inspector. | 53 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-09-29
45389 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-09-29 15:09 | 2009-09-29 20:09 | 2009-09-30 | TECHNICAL SUPPORT CENTER UNAVAILABLE FOR EMERGENCY PLANNING RESPONSES "At 15:09 CDT, today the Technical Support Center ventilation system stopped running. The cause for the failure of the Technical Support Center ventilation system is suspected to be an interlock between the fire detection system and the ventilation unit. The cause of the this condition renders the Technical Support Center unavailable for Emergency Planning Responses. Alternate facilities are available. This condition is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for Loss of Emergency Preparedness Capabilities." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JULIE BISSEN TO JOHN KNOKE AT 1314 EDT ON 9/30/09 * * * Technical Support Center ventilation system is now functional and is available for Emergency Planning Responses. The licensee has notified the NRC Resident Inspector. Notified R4DO (Mike Shannon) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-29
45388 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2009-09-29 11:27 | 2009-09-29 16:19 | 2009-09-29 | LOSS OF WATER FROM UPPER REFUEL POOL "On 9/29/2009, at 1127 hours, with the plant in Mode 5, Refuel, upper pool filled for refuel activities, and no fuel handling or control rod movement activities in progress, River Bend Station operators manually started Low Pressure Coolant Injection Pump Charlie to facilitate filling of the upper pool. This action was necessary to offset a loss of upper pool water through a main steam line and into the drywell. Approximately 5000 gallons of water drained from the upper pool into the drywell. Initial investigation found that the leakage was past a partially de-flated main steam line plug, through Safety Relief Valve flanges, which were not fully torqued at the time. The steam line plug became deflated during ECCS testing when service air isolated to containment. The service air system provides a backup to the mechanical seal. The drywell was evacuated and actions were initiated to close containment. The steam line plug was re-inflated which stopped leakage to the main steam line and drywell. At no time during the event was River Bend Station out of compliance with Technical Specification requirements for the upper pool. River Bend personnel are performing further investigations into the cause of the event." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-09-29
45387 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2009-09-14 | 2009-09-29 15:00 | 2009-10-01 | MISSING SHIPMENT OF GENERAL LICENSED DEVICES This information was received from the State via facsimile: "On the afternoon of September 28, 2009 at approximately 12:15 pm CDT, the Alabama Office of Radiation Control received a phone call from a representative of the Kentucky Radiation Health Program advising the Agency [Alabama Office of Radiation Control] of the discovery of two missing general licensed devices containing radioactive material. The representative of the Kentucky Radiation Health Program indicated that he was advised from Ronan Engineering representatives that two Ronan model RLL-1 source holders each containing 0.63 millicuries of Cs-137 were lost in transit by a commercial carrier. The shipment originated at Southfresh Feed, Demopolis, Alabama on September 14, 2009 with destination to Ronan Engineering, Florence, Kentucky scheduled for delivery on September 17, 2009. The carrier is YRC [Yellow Transportation Inc]. "According to Ronan Engineering representatives, the RLL-1 source holders are bolted to a pallet. The devices are eight inches wide, including mounting flange and twelve inches long. The housing is 4" x 4" x 12" long. Radioactive material labels, UN identification labels, and Ronan address labels are on the skid and devices. "According to YRC representatives, YRC has sent out notifications to over 30 dispatch centers and are contacting customers in an attempt to locate the shipment. The shipment was last accounted for on September 18, 2009 at the YRC, Nashville, TN terminal. "This is all the information that this Agency [Alabama Office of Radiation Control] has at this time and is current as of 2:00 pm CDT, September 29, 2009." * * * UPDATE AT 0926 EDT ON 10/01/09 FROM DAVID TURBURVILLE TO S. SANDIN * * * At 0750 CDT on 10/01/09, the Alabama Office of Radiation Control was informed that the missing shipment had been misrouted to the YRC Columbus, OH terminal. The shipment is currently enroute to its final destination, i.e., Ronan Engineering located in Florence, KY. Notified R1DO (Miller), FSME (Villamar) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2009-10-02
45386 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-09-28 07:54 | 2009-09-28 15:55 | 2009-09-28 | PLANT PROCESS COMPUTER OUTAGE RESULTING IN A LOSS OF ERDS AND SPDS "At 07:54 hours EDT, on September 28, 2009, the Plant Process Computer (PPC) was removed from service to replace the Intelligent Remote Control Units (IRCUs). The expected duration of PPC inoperability is approximately 16 to 24 hours. The PPC provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS). The loss of PPC requires alternate methods, as described in plant procedures, to be used for the above described functions. Therefore, appropriate assessment of plant conditions, notifications and communications can still be made, if required, during the time that the PPC is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii) which is any event that results in a major loss of emergency assessment capability, offsite response capability or offsite communications capability. As previously stated, alternate means remain available to assess plant conditions, make notifications and accomplish required communications, as necessary. An additional notification will be provided when the PPC operability is restored." The licensee notified the NRC Resident inspector. * * * UPDATE AT 2309 ON 9/28/2009 FROM JOSHUA SISAK TO MARK ABRAMOVITZ * * * "At 2255 hours EDT on Sept 28, 2009, the Plant Process Computer was restored to service. Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS) were returned to service. All offsite communication capabilities and all emergency assessment capabilities have been restored." The licensee notified the NRC Resident Inspector. Notified the R1DO (Miller). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-28
45385 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-09-25 13:00 | 2009-09-28 12:14 | 2009-09-28 | AGREEMENT STATE REPORT - SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA The following agreement state report was received via e-mail: "On September 25, 2009 (at approximately 14:45 MDT), the Colorado Department of Public Health and Environment was notified by the RSO for Team Industrial Services that a source disconnect had occurred within the prior 1-2 hours at a temporary jobsite located in Rifle, Colorado. The source remained disconnected at the time the RSO made the notification to the Department as no personnel working in the area were trained for source recovery operations. Once the radiographer in charge at the jobsite realized that a disconnect had occurred and the source could not be returned to the radiography device, the source was cranked/pushed out to the collimator to provide additional shielding. "The RSO reported that the radiographer and radiographer assistant involved in the source disconnect had received approximately 1 mrem up to and including the time of the source disconnect. According to the RSO, the temporary jobsite was located adjacent to an oil or gas drilling rig site, but radiography operations were located at a sufficient distance so as not to impact other non-radiography personnel (members of the public) working in the vicinity. Additional (licensee) radiography crews working in the Rifle, CO area were dispatched to the jobsite where the disconnect had occurred to provide additional support and access control. "On September 26, 2009 (at approximately 11:08 am MDT), the licensee notified the Department that the source recovery had been successfully completed by the RSO at about 1:30 am MDT that morning. The personnel involved in the source recovery - including the RSO - had received approximately 8 mrem each based upon pocket dosimeter readings. "The event involved a radiography device containing 35.6 curies of Ir-192. The source had been in use for several months and the source was nearing the end of its useful life. The radiography device involved in the disconnect was a Sentinel Delta 880 (Serial #D4309) containing approximately 35.6 Ci of Ir-192. The Ir-192 source was a Model 424-9, Serial #53922B. "The Department [Colorado Department of Health] recommended to the licensee that the device and source be returned to the manufacturer for further evaluation. The licensee is expected to submit a written report to the Department within 30 days of the incident. "Colorado Incident #I09-19" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-10-01
45384 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2009-09-27 02:00 | 2009-09-27 12:30 | 2009-09-27 | RADIOGRAPHY CAMERA SOURCE FAILS TO FULLY RETRACT INTO CAMERA Technicians were performing radiography at the Kuparuk Oil Field in Prudhoe Bay, Alaska. The IR-100 camera experienced a lockout with the source within the camera but not fully retracted. The technicians were trained on this problem and were able to reset the lockout and fully retract the source. No exposure resulted from resetting the lockout. The IR-100 camera contains less than 100 Ci of Ir-192. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-09-27
45383 | 0 | VETERANS ADMINISTRATION SAN DIEGO |  |  |  |  | 2009-09-21 | 2009-09-26 16:31 | 2009-09-26 | MEDICAL EVENT - PATIENT UNDER DOSE "This is a notification, pursuant to 10 CFR 35.3045, of a medical event that occurred at the VA San Diego Healthcare System in San Diego, California. "A dosage of 194 millicuries of I-131 sodium iodide was administered to a patient through a feeding tube on September 21, 2009. The patient was kept in a shielded room at the facility. Daily measurements of the exposure rate at one meter from the patient showed only a small decrease, consistent with radioactive decay, but not the expected biological elimination. The feeding tube was replaced on September 25, 2009. The activity in the feeding tube after removal from the patient was estimated as over 80 millicuries. At this time, it is estimated that the patient received less than half of the administered dose. "The basis for the medical event is that the total dosage delivered differs from the prescribed dosage by more than 20 percent. The facility has notified the patient of the medical event and is in the process of notifying the referring physician. The facility is in the process of assessing any possible medical effects on the patient. "The NHPP will perform a reactive inspection regarding the medical event. A 15-day written report for the medical event will be submitted to NRC Region III. National Health Physics Program will notify the NRC Project Manager, Cassandra Frasier, NRC Region III, of the medical event. Additional information "The Department of Veterans Affairs holds NRC License No. 03-23853-01VA, a master materials license. Permits are issued under the license to Veterans Health Administration facilities. The VHA permit number for the facility involved in this medical event is 04-15030-01. National Health Physics Program makes required notifications to NRC." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | CA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-10-02
45382 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-09-25 12:45 | 2009-09-25 14:50 | 2009-10-16 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE OF TRITIUM "On September 1, 2009, the Agency [Texas DEH] received a call from the Florida Bureau of Radiation Control notifying them that during a routine inspection of a facility in Florida, they found tritium contamination on and outside of a container that contained a prototype tritium battery sent to them by a company in Alvin, Texas. The Radiation Safety Officer (RSO) at the Texas facility was contacted by this Agency [Florida]. The RSO stated that the facility had shipped two of the six batteries they had made from their facility to Florida. He stated that they had not had contamination issues in the past with these batteries and he believed the contamination event was caused by the testing facility when they opened the outer battery housing to determine the cause of a failure. He stated that they had not experienced any significant contamination issues at their facility. "On September 18, 2009, in response to additional information provided by the State of Florida, an Agency [Texas DEH] inspector conducted an onsite investigation at the facility in Alvin. The inspector performed a removable contamination survey in the area where the batteries are handled and stored. During his investigation of the event, the inspector learned that the seven batteries were manufactured in a city outside of the State of Texas. One was shipped to the facility in Florida directly, and six were shipped to the facility in Alvin, Texas. "On September 24, 2009, the Agency [Texas DEH] received notification that the results of the tritium survey done at the facility indicated all swipes exceeded the limit for unrestricted use. The Agency [Texas DEH] contacted the licensee and informed the licensee of their results. Documents regarding previous radiological surveys for the battery storage area, leak test of the 3D diodes, receipt survey on the six 3D diodes that were sent from the manufacturer, and any Bioassays that have been performed on their staff were requested from the licensee. "On September 25, 2009, at 12:45 PM (local) the Agency [Texas DEH] was notified by the licensee that the area had been isolated and that decontamination work would go on for an undetermined period of time. The licensee has begun providing the requested information. Updates will be provided as additional pertinent information is obtained." Texas Incident #I-8668. See also Event Notification #45358 for the notification made by the State of Florida on the same event. * * * UPDATE AT 1745 EDT ON 10/16/09 FROM ART TUCKER TO S. SANDIN * * * The following update was received from the State of Texas via email: "On October 13, 2009, the Agency received copies of surveys performed by BetaBatt at their Texas facility. These surveys indicated contamination levels of tritium to be between 8,000 dpm and 300,000 dpm after the first decontamination effort, and between 51,325 dpm and 16,500 dpm after the second decontamination effort. The licensee is considering additional decontamination techniques to reduce the activity. The report also indicated that two individuals had received bioassay analysis. The results indicated that the two individuals had received small body burdens. The licensee has contacted Rice University and REAC/TS for assistance." Notified R4DO(Cain) and FSME EO(Delligatti). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-09-30
45381 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-08-31 | 2009-09-24 17:46 | 2009-09-24 | AGREEMENT STATE REPORT - MISSING RADIOACTIVE MATERIAL The following report was received from the state via facsimile: "On September 21, 2009 the Radiation Safety Officer for a Colorado Licensee - Colorado State University (CSU), provided verbal notification of a past error in its inventory of unsealed radioactive materials used in one of its laboratories on campus. The specific laboratory had been using unsealed radioactive materials since the 1980's and accumulated numerous containers of improperly characterized and labeled waste materials. The licensee followed up the verbal report with a written report dated September 18, 2009 that was received via fax by the Colorado Department of Public Health and Environment on September 22, 2009. Colorado State University is a broad scope non-human use research licensee and has approximately 150 labs using unsealed radioactive materials. The reported inventory discrepancy applies to only one of these labs. "In accordance with Section 4.51.1.2 (equivalent to 10 CFR 20.2201) of the Colorado Rules and Regulations Pertaining to Radiation Control, within 30 days the licensee is required to report to the Colorado Department of Public and Health and Environment (CDPHE) any lost, stolen, or missing radioactive materials exceeding 10 times the Appendix 4C (equivalent to 10 CFR Part 20 Appendix C) quantities. "Following completion of an in-depth, multi-year radioactive materials inventory review that was first initiated in 1997, re-established in 2004, and ultimately concluded in August 2009, CSU reported an inventory discrepancy of radioactive materials in one of its laboratories. The inventory review consisted of evaluation of thousands of records, and collection and analysis of greater than 1000 samples from greater than 700 vials, test tubes, and bottles of unknown substances potentially containing radioactive materials that had accumulated over many years in the specific laboratory. Upon completion of the data and inventory review in August 2009, the licensee reported that it could not account for approximately 24 milliCi of H3 (tritium), based upon an accounting evaluation of incoming radioactive materials and outgoing radioactive materials (disposal records). The licensee however, believes that the radioactive material was in fact disposed of properly with other waste materials, but cannot necessarily provide the records to demonstrate this. The licensee has stated that they do not believe the radioactive materials have been stolen, but rather the discrepancy is attributed to poor inventory and waste disposal records by the laboratory personnel over many years and personnel changes." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-09-29
45380 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2009-09-24 01:30 | 2009-09-24 03:45 | 2009-09-24 | OFFSITE NOTIFICATION OF INADVERTENT SIREN SOUNDING "At time 0130 CDT the Louisiana Governor's Office of Homeland Security and Emergency Preparedness was notified of an inadvertent sounding of one siren (WF39) at River Bend Station. The Louisiana Governor's Office of Homeland Security and Emergency Preparedness initiated their procedure for inadvertent siren sounding which includes a broadcast of an EAS [Emergency Alert System] message of the inadvertent sounding. West Feliciana Parish Sheriff Office 911 center was also contacted." The cause of the siren actuation is under investigation and the siren has been disabled until the problem is identified and repaired. The licensee has notified State and local authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-24
45379 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-09-23 | 2009-09-23 19:05 | 2009-09-23 | AGREEMENT STATE REPORT - LEAKING SOURCE The following information was provided from the State of California via email: "J.L. Shepherd & Associates (JLS&A) performed a source exchange on a Model 44, serial number 7079, category 1 panoramic irradiator of their own manufacture. "The source is identified as JLS&A Type 7810 capsule, manufactured by General Electric Company, Nuclear Center. The serial number is GEC-05-04. CA Sealed Source & Device registry: CA0598S122S "At the time of source exchange, the Co-60 source was estimated to have [approximately] 250 Ci of activity. Wipe tests were taken at the location of the resourcing and showed no indication of leaks. The source holder rod was discolored and had evidence of corrosion. Source assembly was shipped to JL Shepherd's facility in San Fernando, CA. "On September 22, 2009, the source was removed from the transport container in their hot cell with remote manipulators. The source was wiped and determined to have 0.0688 microCi of removable contamination. The source was decontaminated to between 0.001 - 0.0025 microCi level on smears, and placed into a stainless steel pipe and sealed with caps. This will remain in storage at their facility until disposed of in a proper manner." California reference number: 092209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-09-28
45378 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-09-21 | 2009-09-22 18:32 | 2010-01-27 | AGREEMENT STATE REPORT- PATIENT RECEIVED IMPROPER DOSAGE On September 21, 2009, a patient undergoing mammosite brachytherapy did not receive the proper dose administration due to the Ir-192 (9.6 Ci) source failing to retract. The administering physician retrieved the source from the patient and placed it back in the device. A dose estimate is in progress, however, the licensee does not expect the dosage to exceed 50 percent of the prescribed dose. The afterloader was cleaned recently and the licensee does not expect any debris from the device. The State will report any results of the dose assessment. Texas Incident Number: #8673 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 1/27/2010 AT 1703 FROM ANNIE BACKHAUS TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On September 22, 2009, the Agency [Texas Department of Health] was notified of an incident that occurred on September 21, 2009 involving a patient undergoing mammosite brachytherapy. The patient did not receive the proper dose due to the Iridium (Ir)-192 (9.6 Curies) source failing to retract back into the High Dose Rate after-loader unit. The administering physician retrieved the source from the patient and placed it in a shielded container. An investigation by the Agency was performed on September 29, 2009 and it determined that this was not a reportable event because the fractionated dose delivered differed from the prescribed dose, for a single fraction, by less than 50 percent or the total dose for the prescribed treatment differed from that prescribed by less than 20 percent. Because this does not meet the criteria for a reportable medical event, the State of Texas would like to retract this report." Notified the R4DO (Pick), and FSME (Thaggard). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-09-28
45377 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2009-09-22 13:29 | 2009-09-22 15:11 | 2009-09-22 | UNANALYZED CONDITION RESULTING FROM AN UNLATCHED DOOR SERVING AS A HIGH ENERGY LINE BREAK BARRIER "Based on the results of a past operability evaluation completed on 1329 [CDT], 9/22/2009, it appears that an unanalyzed condition existed intermittently for short periods of time in which a door that serves as a High Energy Line Break (HELB) barrier may have been unlatched. With the door not latched, an engineering evaluation concluded that a critical crack (HELB) in the Main Feedwater pipe traversing the south penetration room would force the door (DR-19) open, creating a harsh environment in the adjoining Emergency Feedwater (EFW) pump room. Because the EFW pump room is not evaluated for harsh conditions, it must be conservatively assumed that both pumps may fail to operate following this HELB event. Therefore, this condition is being reported in accordance with 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety." The licensee informed the Arkansas Department of Health. The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-09-22
45376 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2009-09-22 05:11 | 2009-09-22 13:46 | 2009-09-22 | LOSS OF POWER TO THE EMERGENCY OPERATIONS FACILITY "The normal power supply to the Emergency Operations Facility (EOF) was lost due to thunderstorms in the area. Support personnel were dispatched to assess the EOF. The facility has a diesel generator that should supply power to the facility. However, electricians discovered the generator degraded and non-functional. By 0511, 9/22/2009, electricians determined that they were unsuccessful at immediately restoring the generator. It is estimated that the EOF was degraded for approximately 5 1/2 hours. "Following restoration of normal power, Computer Support personnel discovered that the Safety Parameter Display System (SPDS) at the EOF was not functioning. SPDS is a computer based system designed to monitor and display a concise set of parameters from which the safety status of the plant can be readily and reliably determined. "The normal power supply was eventually returned [to service] by Entergy Arkansas Transmission and the EOF was restored at 0420 and SPDS terminals were subsequently restored at 0815, 9/22/2009. Due to the time that the EOF was degraded, this is considered a major loss of assessment, communications, and response capability." The licensee informed the Arkansas Department of Health. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-22
45375 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-09-21 14:46 | 2009-09-21 19:02 | 2009-09-21 | REACTOR PROTECTION SYSTEM AND PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION AFTER PLACING HPCI SYSTEM INSERVICE "On September 21, 2009, at 14:46 EDT, Unit 1 received valid actuations of the Reactor Protection System (RPS) and the Primary Containment Isolation System. Unit 1 was non-critical, operating in Mode 3, when a RPS actuation occurred. Operators were placing the High Pressure Coolant Injection (HPCI) system in service for reactor pressure control, when a resulting water level shrink caused level in the Reactor Pressure Vessel to drop to Low Level 1 causing the actuation of RPS and the Primary Containment Isolation system. The HPCI system was secured, and level stabilized in the normal band. "Primary Containment Isolation system Group 2 (i.e., Drywell Equipment and Floor Drain, Residual Heat Removal (RHR) Discharge to Radwaste, and RHR Process Sample), Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems), and Group 8 (i.e., RHR Shutdown Cooling) isolation signals were received. RHR was not in shutdown cooling at the time of the isolation signal. Actuations of the Primary Containment Isolation Valves (PCIVs) were completed and the affected equipment responded as designed, with the following exceptions: Two Group 2 valves (1-G16-F003 and 1-G16-F019) and two Group 6 valves (1-CAC-V6 and l-CAC-V9) did not automatically isolate and were manually isolated from the control panel. Investigation is under way to determine why these valves did not automatically close. "Unit 1 was non-critical, in Mode 3, with all rods inserted at the time of the event. The four primary containment isolation valves that did not automatically close did not create an unisolated primary containment penetration. The Emergency Core Cooling System (ECCS), along with Reactor Core Isolation Cooling (RCIC), were operable and available." "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-09-21
45374 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2009-09-21 13:34 | 2009-09-21 16:05 | 2009-09-21 | UNPLANNED MANUAL REACTOR TRIP DURING REACTOR STARTUP "At 1227 EDT, a reactor startup was commenced on Unit 2. Mode 2 was entered at 1325 EDT. At 1333, a Reactor Control Operator noted that Primary Safety Valve V1202 had indications that it was leaking past its seat. Plant procedures required reducing RCS [Reactor Coolant System] pressure in 100 psi increments until the safety reseated. This event required the plant pressure to be reduced to 200 psi below Normal Operating Pressure. Prior to commencing the depressurization, a manual reactor trip was ordered by the Unit Supervisor as discussed in the pre-evolution brief. The unit was in Mode 2 approaching criticality at the time of the trip. The unit is currently stable in Mode 3, Hot Standby. "The reactor trip was uncomplicated. All equipment operated as expected. Main feedwater remained available during the entire event. Auxiliary Feedwater and Atmospheric Dump Valves remained in service during the entire event. "Unit 1 was unaffected by the event and remained at full power. "The grid remained stable throughout the event." All control rods fully inserted. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-09-21
45373 | 0 | BAYER CROPSCIENCE |  |  |  |  | 2009-09-18 | 2009-09-21 14:07 | 2009-09-24 | GAUGE SHUTTER STUCK OPEN "On Sept 21, 2009, [the licensee discovered] a stuck shutter on an ammonia tank (top) in the catalyst area. The gauge is an Ohmart Model SH-F2, Serial 64692, containing 800 millicuries of Cesium-137. The gauge was originally installed in 2006. The stuck shutter was discovered during a routine 6 month shutter check on Sept 18, 2009. The technician tried to electrically close the shutter, but was unable to do so. [The licensee has] scheduled a service provider for repair within the week. The source is safely mounted on the side of a tank, [and the licensee] expects no exposure to occur. The Ohmart manufacturer was contacted." * * * UPDATE ON 9/24/09 AT 0930 EDT FROM GAZDIK TO HUFFMAN * * * An Ohmart service representative responded to the site to repair the gauge. It was determined that a fuse had blown in the gauge actuating circuit and that the shutter was not mechanically stuck. The gauge has been repaired and returned to service. R1DO (DeFrancisco) and FSME EO (McIntosh) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | OTH | GEN | 30.50(b)(2) |  |  |  | 0 | 2009-09-21
45372 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-09-21 05:51 | 2009-09-21 12:54 | 2009-09-21 | TRANSPORT OF A POTENTIALLY CONTAMINATED INDIVIDUAL OFFSITE "Earlier this morning, a contract worker fell from a ladder inside the Unit One Containment. The distance fallen is estimated to be eight and one half feet. First Responders arrived at the individual and after examining him secured him to a backboard, after which he was carried from [the] containment. Health Physics Technicians were not able to survey the individual's back since he was strapped to the back board. The ambulance containing the individual exited the PA [Protected Area] at 0551 and a Health Physics Technician accompanied the individual to the hospital. Upon arrival at the hospital and examination by a physician, the Health Physics Technician was allowed to fully check the individual and determined that there was no contamination present. "This report is being made under 10CFR50.72(b)(3)(xii) since it could not be positively determined that the injured individual was not contaminated when he was transported off site." The individual has been released from the hospital. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2009-09-21
45371 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-09-21 08:30 | 2009-09-21 10:45 | 2009-09-21 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PLANNED MAINTENANCE "Planned preventive maintenance and testing activities are being performed on the Hatch Nuclear Plant's Technical Support Center (TSC) HVAC system on September 21, 2009. These maintenance activities include the performance of preventive maintenance on the TSC air handling unit, condensing unit and fan and testing of the filter train. These work activities are planned to be completed within the (12) hour day shift on 9/21/2009. "During the time these activities are being performed, the TSC air handling unit, TSC condensing unit, TSC filter train and the fan unit for the TSC filter train will not be available for operation. As such, the TSC HVAC will be rendered non-functional during the performance of this work activity. If an emergency condition occurs during the time these work activities are being performed which requires activation of the TSC, the contingency plan calls for utilization of the TSC, as long as radiological conditions allow for habitability of the facility. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM URQUHART TO PARK AT 1704 EDT ON 9/21/09 * * * Maintenance to the TSC has been completed and the TSC is fully functional. The licensee notified the NRC Resident Inspector. R2DO (Bonser) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-21
45370 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-09-20 18:26 | 2009-09-21 01:44 | 2009-09-21 | MAJOR LOSS OF COMMUNICATIONS DUE TO LIGHTNING STRIKE "At 1826 on Sept 20, 2009, a lightning strike caused a disruption of power to offsite communications. At 1853, ENS communications from Sequoyah Nuclear Plant to the NRC were verified. At 2129, Sequoyah Nuclear Plant was notified the ERDS was not linked to the CECC (Offsite Emergency Operating Facility) or the NRC. At 2218, it was discovered the NRC could not contact Sequoyah Nuclear Plant by the ENS, but Sequoyah Nuclear Plant could still contact the NRC using ENS. At 2240, backup phone communications with satellite phone and cell phones were established between Sequoyah Nuclear Plant and the NRC. Efforts are in progress to restore power to the communications NODE building to restore normal communications." At 0155 the NRC verified 2 way communications via ENS with the licensee. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-21
45369 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2009-09-20 17:47 | 2009-09-20 21:32 | 2009-09-20 | MANUAL SCRAM DUE TO REACTOR RECIRC PUMP TRIP "At 1747 hours on September 20, 2009, at River Bend Station, during plant shut down for a planned outage, an unplanned manual reactor scram was initiated by plant operators. As part of the planned shutdown, the reactor recirculation pumps were being transferred from fast to slow speed. This transfer did not occur as expected. Instead, the pumps tripped to off. After this occurred, the operators entered the manual reactor scram. Power level was approximately 23 percent at the time of the scram. All other plant equipment and systems performed as expected. Plant personnel are investigating the cause of the pump trip. The plant is proceeding with planned outage activities." All rods fully inserted. Decay heat is being removed via main steam drains and bypass valves to the condenser. Reactor pressure is at 200 psig. The electrical lineup is normal and all safety related equipment is available if required. No safety or relief valves lifted during the manual scram. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-09-20
45368 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-09-20 14:00 | 2009-09-20 17:08 | 2009-09-20 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABILITY OF DIESEL GENERATOR "Event reportability, is in accordance with 10 CFR 50.72(b)(2)(i), Technical Specification Required Shutdown, due to inoperability of Diesel Generator #4 extending from planned maintenance. "Brunswick Nuclear Plant Units 1 and 2 are initiating unit shutdowns in anticipation of Technical Specification Required Shutdown as required by Technical Specification 3.8.1, Condition H due to the inoperability of Diesel Generator #4 lasting longer than seven (7) days. Power reduction commenced at 1400 on Unit 1, and is scheduled to commence at 2200 09/20/2009 on Unit 2 in accordance with site procedures. Both units will continue the shutdown to Mode 4 or until the emergency diesel generator is declared operable following appropriate repairs and testing." The licensee has notified the NRC Resident Inspector. | 40 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-09-20
45367 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2009-09-20 05:11 | 2009-09-20 13:17 | 2009-09-20 | UNPLANNED EMERGENCY DIESEL AUTO START DURING SURVEILLANCE TESTING "This report is being made due to an auto start of the Red Train Emergency Diesel Generator (2K-4A) which was the result of an unplanned loss of power to the Red Train 4160 Volt Electrical Bus (2A3) during surveillance testing. Concurrent with the loss of power, Shutdown Cooling Flow was temporarily lost. "This condition occurred with the unit in Mode 5 during a refueling outage. The Reactor Coolant System (RCS) Pressurizer level was 85 percent and RCS temperature was 139 degrees Fahrenheit. During the momentary loss of power, 2A3 automatically shed its loads as designed. This caused the running Shutdown Cooling Pump (Low Pressure Safety Injection Pump 2P-60A) to secure which resulted in a loss of Shutdown Cooling Flow to the RCS for approximately three and a half minutes. Shutdown Cooling was restored using the applicable Abnormal Operating Procedure. RCS temperature rose approximately five degrees Fahrenheit. "During the performance of planned surveillance testing, 2K-4A was unexpectedly auto started. An Offsite Power Transfer Test was being performed to test automatic transfer from Startup 3 Offsite Transformer to Startup 2 Offsite Transformer. The transfer was initiated by momentarily bypassing (jumpering) a relay. When the test was initiated, a slow transfer of the Red Train 4160 Volt Electrical Bus (2A1) occurred instead of the expected fast transfer. The slow transfer of 2A1 resulted in a momentary loss of power, for approximately two seconds, to the Red Train 4160 Volt Electrical Bus (2A3) which is supplied from 2A1. The under voltage condition on 2A3 caused 2K-4A to auto start, as designed. 2K-4A did not power 2A3, since 2A3 was powered from 2A1 after the slow transfer completed." The cause of the slow transfer versus a fast transfer is under investigation. The licensee notified the Arkansas Department of Health and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-09-20
45366 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2009-09-20 01:30 | 2009-09-20 05:50 | 2009-09-20 | EMERGENCY SIRENS INOPERABLE "At 0130 the 800 MHZ radio [control] system failed to the 'fail soft' mode rendering all [73] emergency notification sirens inoperable. At 0305 courtesy call notifications were made to the county control centers (Calvert, Dorchester, St. Mary's and MEMA). "The backup system was placed in service and 800 MHZ radio and ENS sirens restored to operable status at 0526 9/20/09." Maintenance work to restore the primary system will occur today. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2009-09-20
45365 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-09-19 13:23 | 2009-09-19 21:04 | 2009-09-23 | HIGH VOLTAGE PROCESS GAS LEAK DETECTOR RENDERED INOPERABLE "At 1323 CST, on 09-19-09 the Plant Shift Superintendent (PSS) was notified that C-315 (Tails Withdrawal facility) High Voltage Process Gas Leak Detector (PGLD) YE-10-2-6 was rendered inoperable during asbestos abatement activities. This PGLD system contains detectors that cover the C-315 UF6 condensers, accumulators, and piping heated housing. At the time of this failure, these areas were operating above atmospheric pressure. TSR 2.3.4.4 requires that all detector heads in this system be operable during operations above atmospheric pressure. This PGLD System was declared operable and returned to service at 1359 hours, which is within the one hour required by TSR LCO 2.3.4.4.A.1 to enter a continuous smoke watch. This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). "This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. Once the reason for the failure was identified, the detector was repaired, the C-315 High Voltage PGLD system was tested and declared operable. "The NRC Senior Resident Inspector has been notified of this event." PGDP Assessment and Tracking Report No. ATR-09-2284 PGDP Event Report No. PAD-2009-15 * * * RETRACTION FROM DERRICK WARFORD TO DONG PARK ON 9/23/2009 AT 1553 EDT * * * "After review, it was determined that a redundant operable PGLD detector was available to perform the intended safety function. Therefore according to 10CFR76.120, this event is not reportable. The NRC Resident Inspector has been notified of this retraction. " Notified the R2DO (Rudisail) and NMSS (Waters). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2009-09-19
45364 | 0 | HILLIS-CARNES ENGINEERING ASSOC |  |  |  |  | 2009-09-18 16:50 | 2009-09-18 17:03 | 2009-09-19 | TROXLER MOISTURE DENSITY GAUGE DAMAGED A Hillis-Carnes operator was conducting a density test along a portion of the Fairfax County Parkway project on Fort Belvoir property when the gauge was backed over by a pick-up truck. Hillis-Carnes technician was 10-15 feet from the gauge when the incident occurred but could not get the driver's attention in time for him to stop. The gauge (Model No. 3411-B, Serial No. 15826) with 8 mCi of Cs-137 (Serial No. 50-4850) and 40 mCi of Am 241:Be (Serial No. 47-11222) was hit by the under carriage of the vehicle while in the testing mode with the source rod extended to a depth of 8 inches. The depth rod was snapped off the gauge and the source rod remained intact. However, the source rod was slightly bent which prevented the rod from being lifted to the shielded position. The area was immediately cleared to a minimum distance of 30 feet. Local emergency responders were the first on the scene and surveyed the area. The RSO was not on site at this time but was informed that survey readings were taken, and the levels indicated the sources were not leaking. The responders recommended the area remain cleared until personnel arrived that could address removing the gauge properly. Hillis-Carnes attempted to contact their 24-hour emergency response service without success. The RSO was also informed by the NRC that the emergency contact numbers did not work. Subsequently, U.S. Army Corps of Engineers (USACE) representative was contacted by Fort Belvoir representatives to come to the site. Upon arrival, USACE surveyed the area. No readings were recorded at 30 feet from the gauge (established safe zone), however a reading of 10mR/hr was obtained at contact with the gauge. The RSO and USACE discussed opinions for temporary packaging of the device. It was determined that the gauge would be placed in a 55 gallon drum, sandwiched in soil. The NRC was contacted on this course of action and it was subsequently approved. The drum was partially filled with soil, then the gauge was lifted from its test location and immediately embedded into the loose soil with the source rod down the center of the drum. Additional soil was placed over the gauge. Survey readings over the soil in the drum and around the perimeter of drum were 8 mR/hr each. Additionally, the in-place soil was surveyed with 12 to 14 microRem obtained at the test location and background noted to be 10 microRem. Only individuals with personal monitoring badges were permitted within the 30 foot safety area during the packaging of the gauge. The drum was transported and placed in an on-site storage container and subsequently surveyed again by USACE. Readings at this point were taken at 30 cm from the container and noted to be 2 mR/hr. The storage container is labeled with radiation placards and labeling was added to the drum. The container was locked and the door barricaded with construction equipment. Today [9/19/09], the RSO contacted Northeast Technical Services in Westminster, Maryland. They indicated that they could be on-site today to take care of properly packaging and shipping the gauge. It is to be transported to their facility. The RSO contacted others involved in the on-site activities from last evening and it was determined that the USAG [United States Army Garrison] Fort Belvoir Army Radiation representative has not been involved in the actions to date. Army representative wanted the removal of the gauge to be postponed until midday on Monday, September 21st, until the representative could be involved. Northeast Technical has subsequently been scheduled for midday Monday. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-09-19
45363 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2009-07-21 | 2009-09-19 09:49 | 2009-09-19 | AGREEMENT STATE - POTENTIAL EXTREMITY OVEREXPOSURE A licensee radio-pharmacist was preparing Flourine-18 (F-18) doses for use, when a manipulator malfunction occurred. The radio-pharmacist continued to prepare the F-18 manually instead of securing the process. This led to a potential dose to the radio-pharmacist's right hand of greater than 50 rem. This dose is a rough estimate from whole body dose values and reconstruction of the event due to the fact the radio-pharmacist was not wearing any dosimetry on the extremity. The State will continue to investigate this event and provide additional information as it become available. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2009-09-23
45362 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-09-18 14:50 | 2009-09-18 16:38 | 2009-09-18 | FITNESS FOR DUTY - NON-DISCLOSURE OF INFORMATION BY A NON-LICENSED CONTRACTOR A non-licensed contractor failed to report derogatory information to the licensee at the time of processing. Upon discovery of the discrepancy, the contractor's plant access was terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2009-09-18
45361 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-09-18 10:30 | 2009-09-18 16:29 | 2009-10-01 | INOPERABILITY OF BOTH EDG'S DUE TO VALVE FOUND OUT OF POSITION "At 02:00 on Friday, September 18, 2009, the Unit 2 AB Emergency Diesel Generator (EDG) Air Jet Assist Control Air Shutoff valve, which is required to be open, was discovered closed. At 10:30 on Friday, September 18, 2009, it was determined that with the valve closed, the EDG Air Jet Assist may not be able to support the EDG fast speed start to meet the EDG's Operability requirements. This condition renders the Unit 2 AB EDG inoperable. The valve was repositioned and verified open at 02:15 on Friday, September 18, 2009, restoring the EDG to operable status. Similar valves were verified to be in the correct position on all other EDGs in both Units. "The Unit 2 AB Emergency Diesel Generator Air Jet Assist Control Air Shutoff valve was last confirmed open on July 21, 2009. The time the valve became closed is not known. Since July 21, 2009, there have been 3 periods of inoperability for Unit 2 CD EDG, the redundant Emergency Diesel Generator. During each of these periods, both of the Unit 2 EDGs are assumed to be inoperable. The periods are as follows: "August 10, 2009 at 09:31 until August 10, 2009 at 23:00 August 11, 2009 at 07:30 until August 11, 2009 at 23:16 September 9, 2009 al 00:02 until September 9, 2009 at 04:40 "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(ii)(B) due to the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety." The licensee has notified the NRC Senior Resident Inspector. * * * RETRACTION ON 10/01/2009 AT 1634 EDT FROM JAMES SHAW TO DONALD NORWOOD * * * "At 02:00 on Friday, September 18, 2009, the Unit 2 AB Emergency Diesel Generator (EDG) Air Jet Assist Control Air Shutoff valve, which is required to be open, was discovered closed. At 10:30 on Friday, September 18, 2009, it was determined that with the valve closed, the EDG Air Jet Assist may not be able to support the EDG fast speed start to meet the EDG's Operability requirements. This condition renders the Unit 2 AB EDG inoperable. The valve was repositioned and verified open at 02:15 on Friday, September 18, 2009, restoring the EDG to operable status. "Since the last time the Turbocharger Air Jet Assist Control Air Shutoff valve was confirmed open, July 21, 2009, there were three periods where the redundant EDG was inoperable for planned maintenance and surveillance testing. During each of these periods, both of the Unit 2 EDGs are assumed to be inoperable. As such, Cook Nuclear Plant (CNP) submitted Event Notification 45361 in accordance with 10CFR50.72(b)(3)(ii)(B) due to the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "On September 25, 2009, CNP conducted two EDG fast speed starts, one with the Turbocharger Air Jet Assist Control Air Shutoff valve closed, and one with the valve open. Based on a review of the data collected and observed performance of the EDG, the determination has been made that having the Turbocharger Air Jet Assist Control Air valve closed does not adversely impact operability of an EDG. "The circumstances discussed in the notification did not result in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Lara). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-09-18
45360 | 0 | US ARMY |  |  |  |  | 2009-09-16 | 2009-09-17 17:15 | 2009-09-17 | FOUR DEFECTIVE MOISTURE DENSITY GAUGES As part of the pre-operational check at the Defense Distribution Depot in Tracy, CA, operators discovered that four of their CPN Model MC-1 Moisture Density Gauges were defective. The 4 moisture density gauges were manufactured approximately 30 years ago and each contains two sources; 10 mCi Cs-137 and 50 mCi Americium-241/Be (nominal). These gauges will not be returned to the manufacturer for evaluation and repair, but rather disposed of at an approved facility. The 4 units are currently locked in their storage containers, and those containers are locked inside another locked cabinet at the Defense Distribution Depot in Tracy, CA. The four gauges serial number and the reason for being defective are as follows: 1) s/n M17092033 - Locking mechanism does not work. 2) s/n M17112087 - Locking mechanism does not work. 3) s/n M17092041 - Handle broken. 4) s/n M17071988 - Broken guide tube. The licensee notified NRC Region 3 Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-09-17
45359 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2009-09-17 13:00 | 2009-09-17 16:16 | 2009-09-17 | EMERGENCY RESPONSE DATA SYSTEM INOPERABLE FOR GREATER THAN EIGHT HOURS "At 1300 hrs. on Thursday, September 17, 2009, TMI Unit 1 determined that there had been a degradation of the emergency preparedness response capabilities when a loss of the Emergency Response Data System (ERDS) was identified. While preparing for a future job in the same cabinet where the ERDS modem is located, technicians identified that the phone line for the ERDS modem was not connected. "At 1400, the phone line was reconnected to the modem. After coordination with the NRC Operations Center testing personnel, a test of the ERDS system was initiated. At 1414, an active link was established. A successful ERDS link was confirmed with the NRC Operations Center. At 1426, the ERDS link was terminated. "Work was performed on different equipment in the cabinet containing the ERDS modem on approximately September 1, 2009. It is probable that the phone line was inadvertently disconnected from the ERDS modem at that time. The last scheduled quarterly test was successfully completed on July 9, 2009. TMI 1 has determined that this event is reportable to the NRC as an 8-hour non-emergency report in accordance with 10 CFR 50.72 (b)(3)(xiii). " The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-17
45358 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-09-17 | 2009-09-17 16:03 | 2009-09-17 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE OF TRITIUM The following report was received from the State via facsimile: "Leaking sealed source containing tritium was discovered by state inspector during routine inspection. Lab technician was bio assayed (urine) and an activity level of 1.25 E5 p/Ci per liter was reported. REAC/TS has been notified. [The device containing the tritium source] belongs to a company in Texas, BetaBatt, [whose] license number is L05961. This office [State] is still investigating." Florida report number - FL09-064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-09-22
45357 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-09-17 11:30 | 2009-09-17 15:25 | 2009-09-17 | OFFSITE NOTIFICATION TO MINNESOTA POLLUTION CONTROL AGENCY "Approximately one cup of hydraulic oil entered the plant waterway while operating the 122 Emergency Intake Bypass Gate. While troubleshooting a limit switch issue with the bypass gate, a leak developed on the lower seal for the hydraulic cylinder. An oil sheen was noticed on the plant side of the Intake Screen House and has been cleaned up with absorbents. No oil sheen was detected on the Mississippi River side of the Intake Screen House or in the plant discharge canal. The Minnesota Pollution Control Agency and the National Response Center were notified." The licensee has notified the NRC Resident Inspector. Licensee will be contacting local and other government agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-17
45356 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-09-17 13:52 | 2009-09-17 14:01 | 2009-09-18 | TECHNICAL SUPPORT CENTER FUNCTIONALITY OUT OF SERVICE "A condition is being reported per Technical Requirement Manual 13.13.1 Emergency Response Facilities Action B.2. The backup power supply functionality of the Technical Support Center (TSC) will be out of service due to planned maintenance on the SAS Battery. Pre job briefings and steps for restoration in case of emergency have been included in the work plan. Alternate facilities are available to provide emergency response functions. A 10CFR50.54(q) evaluation has been performed for this planned Maintenance activity." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0355 EDT ON 9/18/09 FROM SWEAT TO HUFFMAN * * * "In reference to EN# 45456, Plant Vogtle Technical Requirement Manual 13.13.1 Emergency Response Facilities Action B.2 has been exited. The backup power supply for the Technical Support Facilities (TSC) has been returned to service and is now fully functional." R2DO (Bonser) notified. | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-17
45355 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2009-09-15 | 2009-09-17 12:11 | 2009-09-17 | AGREEMENT STATE REPORT - PATIENT GIVEN WRONG DOSE The following information was faxed in by the State: "The South Carolina Department of Health and Environmental Control was notified on September 17, 2009, by the licensee, that a medical event occurred. A patient who was scheduled for a Yttrium-90 Microsphere therapy was given the wrong dose. The patient was scheduled for 25.38 millicuries but was administered 45.9 millicuries according to the initial report by the licensee. "The event took place on the 15th and was verified by the licensee on the 17th of September. The referring physician has been notified as well as the patient. The licensee knew no additional details at this point. The licensee will provide additional information in a written report within 15 days. Updates to this event will be made through the NMED system as further information is received." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2009-09-23
45354 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-09-16 10:36 | 2009-09-16 17:10 | 2009-09-17 | EMERGENCY SIRENS OUT OF SERVICE "On September 16, 2009, at approximately 1036 hours, as a result of a regularly scheduled test of the Indian Point Energy Center (IPEC) Alert Notification System (ANS) 18 of 172 sirens did not pass the test. The sirens were not tested and declared as functional within one hour and in accordance with the reporting guidelines the event is reportable under 10CFR50.72(b)(3)(xiii) as a major loss of offsite response capability (i.e., a loss of 10% or more of the total number of sirens for more than one hour). "Preliminary investigations and troubleshooting determined 14 sirens failed to indicate via the ANS computer system successful siren activation due to an incorrect software data adjustment for these 14 sirens. ANS technicians corrected the software error for these 14 sirens and are continuing to investigate the cause of the failure of the remaining 4 sirens to activate. To validate that the software error for the 14 sirens was corrected, a functional test of 1 of the 14 sirens was conducted. The test indicated the siren was functional but investigation and troubleshooting is continuing to validate this. "Reverse 911 has been and remains available to alert the public should there be an actual event requiring the ANS. The condition was recorded in the IPEC corrective action program. The event remains under investigation." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BRIAN ROKES TO JOHN KNOKE AT 1435 ON 09/17/09 * * * Two sirens were repaired making a total of 156 sirens operable. No further reporting is forthcoming. Licensee has notified the NRC Resident Inspector. The R1DO (Don Jackson) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-16
45353 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-09-16 12:20 | 2009-09-16 15:59 | 2009-09-16 | OFFSITE NOTIFICATION MADE AFTER DISCOVERY OF AN OIL SHEEN "A voluntary notification to the National Response Center was made on Sept. 16, 2009 at 1220. The purpose of the notification was to inform the National Response Center of an oil sheen on a concrete pad at the inlet of the diffuser pond. The diffuser pond is classified as waters of the U.S. There was no observable oil sheen on the pond." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-16
45352 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2009-09-16 01:39 | 2009-09-16 10:09 | 2009-09-16 | LOSS OF COMMUNICATIONS "At 0139 on 9/16/2009, LaSalle Main Control Room was contacted by IEMA (Illinois Emergency Management Agency), stating that they have lost contact with LaSalle via the modem from IDNS (Illinois Department of Nuclear Safety) building. It was subsequently discovered that there was a site telephone equipment malfunction. This issue has affected the Emergency Response Data System, Emergency Notification System, Health Physics Network and the ability to receive phone calls from off-site. "The Emergency Notification System and the Health Physics Network phones are currently not functioning. The NRC has been successfully contacted via commercial line. The NRC has been unable to contact the station directly via the commercial line. The NRC has been capable of contacting the station by relaying the information going through the radio from the Transmission System Operator. "Repairs to the phone system are currently in progress." Communications have been established with the site by cell phone. Alternate communications paths exist through the Dresden and Braidwood sites who can use their ENS lines to communicate with the site and also through the Load Dispatcher. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-16
45351 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2009-09-15 | 2009-09-15 10:14 | 2009-09-15 | AGREEMENT STATE - POTENTIAL OVEREXPOSURE EVENT The following was provided by the State via e-mail: "A radiographer assistant employed by the company for about ten months may have been overexposed. The licensee processes dosimetry every two weeks. The employee's badge for 8-1 to 8-15 returned a reading of 3.077 rem deep dose for the two week period. This placed the employee's total exposure for the calendar year at 3.93 rem. The licensee removed the worker from being involved with licensed materials and initiated an investigation. The worker's badge for 8-16 to 8-31 had already been submitted for processing. On 9/3/09, the licensee was contacted by the dosimetry provider and informed that the worker's deep dose for 8-16 to 8-31 was 12.542 rem. This placed his total annual dose at 16 rem. No unusual exposures on the worker's pocket dosimeter had been recorded at any time. The dosimetry provider indicates the badge exposures are 'irregular'. "The licensee contacted Oklahoma DEQ and initiated a thorough investigation. During the period in question, the radiographer assistant had worked with only one radiographer. All work was done at temporary job sites at industrial facilities. The radiographer and assistant insisted that there had been no unusual events or possibility of exposure, that the worker's alarming rate meter had not alarmed, and that pocket dosimeter readings for the period had been normal. The worker insisted he had not been exposed, and he believed someone else had exposed his dosimetry. The company does not allow assistant radiographers to have keys to cameras, and the worker is not approved for unescorted access to IC quantities of radioactive material. Both workers agreed that the assistant radiographer had never had a key to a camera, but investigation revealed that the assistant radiographer had left the worker alone with the unlocked camera while he went to the restroom. The licensee has counseled the radiographer not to do this, and has informed all radiography staff that assistant radiographers must not be left alone with unlocked radiography cameras. The licensee has contacted local medical assistance, and is told that because of the (relatively) low level of the exposure, and it being spread into at least two components, locally-available blood testing will not reliably detect the exposure. "Since receipt of the dosimetry report, the licensee is not allowing the worker to work near radioactive materials or x-ray. The licensee does not believe the worker was actually exposed to radioactive material, and wants to use chromosome analysis to test this theory. The State has encouraged the licensee to take steps to investigate whether the exposure was to the badge only, or to the worker." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2009-09-18
45350 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2009-09-14 16:15 | 2009-09-14 17:40 | 2009-09-14 | FISH KILL REPORTED TO THE FLORIDA FISH AND WILDLIFE CONSERVATION COMMISSION "On September 14, 2009, Progress Energy Environmental Services determined that approximately 200 deceased or stressed Ladyfish (Elops saurus) were observed near the banks of the Crystal River Energy Complex (CREC) discharge canal. Only Ladyfish were found stressed or deceased. Three of the stressed fish were sampled and examined by the CREC Mariculture Center to evaluate potential causes of these fish mortalities. Of the three fish examined, the only item of note was that the stomach and intestinal tracks were empty. It is likely that the runoff from recent heavy precipitation, coupled with summertime warm water temperatures and rapid salinity changes, resulted in a localized area of low dissolved oxygen and physiologic stress that affected this population of Ladyfish. There were no unusual conditions or factors associated with CREC operations that would have contributed to this event. Notification to the Florida Fish and Wildlife Conservation Commission will be made. This is reportable per 10CFR50.72(b)(2)(xi) as an event for which notification to other government agencies will be made." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-14
45349 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-09-14 08:57 | 2009-09-14 14:57 | 2009-09-14 | FITNESS FOR DUTY - LICENSED EMPLOYEE TESTED POSITIVE FOR ALCOHOL A licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 26.719 |  |  |  | 0 | 2009-09-14
45348 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2009-09-13 22:44 | 2009-09-14 01:49 | 2009-09-14 | MANUAL REACTOR SCRAM DUE TO SHORT PERIOD DURING PLANT SHUTDOWN "During the scheduled shutdown to commence the Peach Bottom Unit 3 refueling outage, Unit 3 was manually shutdown using the mode switch in accordance with GP-3, 'Normal Plant Shutdown,' when reactor period lowered below 50 seconds as indicated on the WRNM [Wide Range Nuclear Monitoring] system. The Feedwater Startup Level Controller was in automatic set at 23" when a small addition of cold water added enough positive reactivity to cause reactor period to be less than 50 seconds. The shortest period observed was 44 seconds. The WRNM system RPS [Reactor Protective System] automatic SCRAM setpoint is 19 seconds." All control rods inserted into the core. Decay heat is being removed by shutdown cooling. The plant is continuing into its scheduled refueling outage. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-09-14
45347 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2009-09-13 12:43 | 2009-09-13 16:12 | 2009-09-13 | AUTOMATIC REACTOR TRIP FOLLOWING TURBINE TRIP FOR LOSS OF CONDENSER VACUUM "The SONGS Unit 2 reactor automatically tripped from approximately 94% power at 1243 PDT due to loss of turbine load caused by lowering main condenser vacuum. Prior to the reactor trip, personnel were attempting to conduct a heat treat on Unit 2. During this evolution, Gate 5 in the main circulating water system was being repositioned when it stopped moving at 45 percent. This resulted in a recirculation and subsequent increase in circulating water temperature, a lowering main condenser vacuum, a loss of load on the main turbine, and an associated automatic reactor trip. "All rods inserted on the automatic reactor trip and the electric grid is stable. "This event report is being made under 10CFR50.72(b)(2)(iv)(B) as a valid Reactor Protection System actuation." Decay heat is being removed via normal feedwater to steam generators steaming through the condenser bypass valves to the main condenser. "At the time of this event, SONGS Unit 3 was operating at approximately 99% power." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-09-13
45346 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-09-11 | 2009-09-11 19:05 | 2009-09-11 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS On 9/11/09 at 1246, the State of California was notified by Boeing that 15 tritium exit signs could not be accounted for in their Long Beach, CA location. The signs were manufactured by Safety Light Corporation and the serial numbers are as follows: 387873, 387874, 387875, 392809, 392810, 392811, 392812, 392813, 392814, 392815, 392816, 392817, 392818, 392819, 392820. The original activity of these signs is typically 11.5 Curies each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-09-16
45345 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-09-11 17:18 | 2009-09-11 18:08 | 2009-09-11 | TRANSPORT OF A POTENTIALLY CONTAMINATED INDIVIDUAL OFFSITE A potentially contaminated individual was transported offsite for medical treatment due to an injury in a normally clean area inside the site's radiologically controlled area (RCA). The individual was a contractor working for Bartlett Nuclear and initial indications are that a fall caused a back injury. The individual was transported to the Carolina Medical Center in Mecklenburg County, North Carolina. A site senior health physics technician accompanied the individual to the medical center. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM THAD REAMES TO PETE SNYDER ON 9/11/09 AT 1900 * * * The contract employee taken to the hospital has been confirmed not to be radioactively contaminated, nor is the Ambulance or other areas contaminated. Notified R2DO (Blamey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2009-09-11
45344 | 0 | HAWAII ADVANCED IMAGING INSTITUTE |  |  |  |  | 2009-09-11 09:00 | 2009-09-11 15:54 | 2009-09-11 | EXTERNAL CONTAMINATION ON RECEIVED SHIPMENT The Hawaii Advanced Imaging Institute received a daily shipment of F18 isotopes in two separate packages that indicated a contamination level of 5086 dpm/100 square centimeters on package #1 and 12936 dpm/100 square centimeters on package #2. The limit is 2200 dpm/ 100 square centimeters. The packages are currently stored in the hot lab at the Hawaii Advanced Imaging Institute. The carrier company (Queens Medical Center of Honolulu) was notified of the contamination event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2009-09-11
45343 | 0 | SARGENT & LUNDY LLC |  |  |  |  | 2009-09-11 | 2009-09-11 16:00 | 2009-09-11 | PROBLEM WITH SEISMIC SOIL STRUCTURE ANALYSIS SOFTWARE "ACS SASSI (Sargent & Lundy Program No. 03.7.848-2.21) by Ghiocel Predictive Technologies Inc. (GPT) is a program which performs seismic soil-structure interaction (SSI) analysis. Sargent & Lundy (S&L) purchased licenses to use ACS SASSI NQA Version 2.2.1 from GPT in 2008 and verified and validated the software under S&L's QA program. "S&L used ACS SASSI for seismic analysis activities for South Texas Project Units 3 & 4 (STP 3&4). "On July 14, 2009, during SSI analysis of the Control Building performed to address the STP 3&4 Shear Wave Velocity Departure, irregularities were observed in the results obtained using ACS SASSI and the analysis was halted. The irregularities in turn led us to question the results for the Ultimate Heat Sink / Reactor Service Water Pump House (UHS/RSWPH) completed earlier. "Our investigations, including a review of other uses of the software, indicate that numerical instability may occur with high numbers of soil layers, even when soil layer properties and number of soil layers (less than or equal to 100) are within the parameters stated in the User's Manual. Our investigations indicate that the results for the Control Building with 94 layers, the Reactor Building with 84 layers, and the UHS/RSWPH with 100 layers are not reliable. Some individual results are conservative, others are not. "S&L recommended to the South Texas Project Nuclear Operating Company (STPNOC) that the work performed using ACS SASSI NQA Version 2.2.1 relied upon to support licensing positions and to support the design basis be reanalyzed using SASSI 2000, Version 3.0. STPNOC accepted this recommendation. "S&L is no longer using ACS SASSI for production work. In addition, we have investigated whether SASSI 2000 has similar irregularities. We concluded that SASSI 2000 does not have this condition and is fundamentally sound." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2009-09-11
45342 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-09-11 05:30 | 2009-09-11 14:05 | 2009-09-11 | AGREEMENT STATE REPORT - CONTAMINATED PHARMACY SHIPMENT PACKAGE '[A] contaminated package [was] received at Mission Hospital from Cardinal Health - Asheville. The RSO [Radiation Safety Officer] of Mission Hospital received a shipment of Tc-99 unit doses from Cardinal Health pharmacy. The exterior of the box was contaminated to [approximately] 180,000 dpm/100 [square centimeters]. "Upon determination of the contamination, Mission Hospital contacted Cardinal Health pharmacy and they came and picked up the box. "Mission Hospital did not open the box. "After the box was picked up, a small spot of contamination was found on the absorbent paper that the box had been placed on. Mission Hospital removed the paper, which removed the contamination, and placed it as waste into their decay-in-storage area. This level exceeds the reportability limit of 22,000 dpm/100 [square centimeters] of 15A NCAC [North Carolina Administrative Code] 11.1627; which references 10 CFR 71.87; which references 49 CFR 173.443. "15A NCAC 11.1627(d) requires an immediate notification to the [North Carolina Radiation Protection Section] Agency." North Carolina Incident 09-43. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-09-16
45341 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2009-09-11 09:04 | 2009-09-11 13:52 | 2009-09-11 | TECHNICAL SUPPORT CENTER UNAVAILABLE "On September 11, 2009, while performing a quarterly surveillance on the Technical Support Center Emergency Diesel Generator, the automatic transfer switch failed to swap as required. This resulted in both the normal and emergency feed to the Technical Support Center losing power. At 1026, the automatic transfer switch was mechanically transferred to the normal feed, restoring the power to the Technical Support Center. "The Outage Control Center was staffed to prepare repair plans for the Automatic Transfer Switch. These repairs will restore backup power capability to the Technical Support Center. Actions are in progress to identify the necessary parts and generate the work packages to restore the backup power capability. "The licensee has notified the [NRC] Senior Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-11
45340 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2009-09-11 11:01 | 2009-09-11 12:40 | 2009-09-11 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO MAINTENANCE "At 1100 on Friday, September 11, 2009 a portion of the Duane Arnold Energy Center power plant (DAEC) Technical Support Center (TSC) ventilation system, Technical Support Center (TSC) air conditioning system, and Technical Support Center (TSC) computer system was removed from service for maintenance on Technical Support Center (TSC) electrical power supply. "The electrical power supply being removed supports air conditioning, filtration system and computers. "Under certain accident conditions the TSC may become unavailable due to the inability of the ventilation system to maintain a habitable atmosphere and loss of computer systems. Compensatory measures exist to rapidly restore power to the TSC if necessary based upon TSC activation requirements. "The TSC power supply maintenance is scheduled to complete at 1800 on Friday, September 11, 2009. The licensee has notified the NRC Senior Resident Inspector. This notification is being made in accordance with 10 CFR 50.72 (b) (3) (xiii) due to loss of an emergency response facility." * * * UPDATE FROM SCOTT AREBAUGH TO VINCE KLCO AT 1802 ON 9/11/2009 * * * The TSC power supply maintenance has been completed and the Technical Support Center(TSC) is now fully available. The licensee will notify the NRC Resident Inspector. Notified the R3DO(Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-11
45339 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2009-09-11 10:25 | 2009-09-11 11:32 | 2009-09-11 | SPDS REMOVED FROM SERVICE FOR MAINTENANCE "Arkansas Nuclear One Unit 2 is removing the Safety Parameter Display System (SPDS) from service for preventative maintenance and scheduled corrective maintenance. SPDS is a computer based system that is utilized by both Unit 1 and Unit 2 to provide critical information during an emergency. Unit 2 is currently in a refueling outage. Unit 1 is on line at 100% power. Compensatory measures are being taken to ensure that necessary backup monitoring is established on Unit 1. The maintenance window is scheduled to be open for 24 hours." The licensee notified the NRC Resident Inspector. The licensee made a courtesy notification to the Arkansas Department of Health. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-11
45338 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-09-10 09:13 | 2009-09-10 13:06 | 2009-09-12 | STATE OFFSITE NOTIFICATION DUE TO NOT MEETING PERMIT REQUIREMENTS "The Minnesota State Pollution Control Agency and State Department of Emergency Management were notified today, September 10, 2009, that Monticello did not meet the National Pollutant Discharge Elimination System (NPDES) Permit. "Samples from a new monitoring well near the reactor building showed low levels of tritium greater than normal background but below Environmental Protection Agency drinking water standards. The concentration of tritium is below any radiological reporting levels established in station procedures. No elevated levels have been detected in any of the other permanent plant monitoring wells. Therefore, we have no indications that there has been a release of tritium beyond the site from this source. The station will continue to monitor, sample and investigate the source of the tritium." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM B. CALLSTROM TO V. KLCO AT 1201 ON 9/12/2009 * * * "A subsequent water sample from a new monitoring well near the reactor building indicated a level of 21,300 picocuries/liter of tritium which is slightly above the Environmental Protection Agency drinking water standard for tritium of 20,000 picocuries/liter. No elevated levels have been detected in any of the other permanent plant monitoring wells. Therefore, [the licensee has] no indication that there has been a release of tritium beyond the site from this source. The station will continue to monitor, sample and investigate the source of the tritium. "This poses no immediate safety concern for plant employees or the general public." The licensee notified the NRC Resident Inspector. Notified the R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-10
45337 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-09-09 15:23 | 2009-09-09 17:15 | 2009-09-09 | OFFSITE NOTIFICATION DUE TO SOIL SAMPLE RESULTS IN EXCESS OF STATE REQUIREMENTS "At 1523 CDT, on September 9, 2009, the Wisconsin Department of Natural Resources (WDNR) was notified via electronic mail that laboratory analyses of soil samples collected from the catch basins surrounding the Unit 1 and 2 Main Power Transformers, 1X01, and 2X01, revealed polycyclic aromatic hydrocarbon (PAH) levels in excess of Wisconsin Administrative Code requirements. Remediation will be performed in accordance with Wisconsin Administrative Code requirements." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-09
45336 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-09-09 09:30 | 2009-09-09 16:40 | 2009-09-09 | EMERGENCY SIRENS OUT OF SERVICE "On Wednesday, Sept. 9 at 9:30 am EDT, all 76 emergency sirens that serve the communities within a 10-mile radius of the PPL Susquehanna nuclear power plant failed during their bi-weekly silent test. "The failed siren test was initiated by Columbia County at 9:30 am; Luzerne County was then asked to complete the test from its controller, but it experienced a similar failure. "The vendor that services the system was called in and is working to fix the problem, which is believed to be a fault in the system radio repeaters. "A backup emergency notification plan is in place with local emergency agencies. "A voluntary notification will be made to the Pennsylvania Emergency Management Agency." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RICH KLINEFELTER TO VINCE KLCO AT 1847 ON 09/09/2009 * * * All emergency sirens were restored to service and tested successfully as of 1742 on 09/09/2009. The licensee notified the NRC Resident Inspector. Notified R1DO(Powell). | 94 | 94 | 0 | 94 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-09
45335 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2009-08-14 | 2009-09-09 14:50 | 2009-09-09 | PART 21 INVOLVING WOODWARD GOVERNORS USING UNAPPROVED SUPPLIER INTEGRATED CIRCUITS The following information was provided via fax: "COMPONENT: Woodward 2301A and DRU with unapproved supplier IC P/N: 9903-303, 9903-337, 9903-444 & 9903-470 "DISCUSSION: Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 8/14/09 to evaluate the use of an integrated circuit (IC) used in some 2301A and DRU controls. The suspect IC was obtained by Woodward from an unapproved supplier. The evaluation was concluded on 09/08/09 and was determined to be a reportable defect as defined by 10CFR21. "On 8/14/09, Woodward confirmed that they had shipped ESI a total of thirty-four (34) 2301A and DRU controls with nuclear part numbers that contained an IC (Woodward P/N 1688-767) from a suspect lot. The lot was dated 12/12/08 and was received by Woodward from an unapproved supplier. Eight (8) of the 34 controls were subsequently shipped by ESI to nuclear customers (2 domestic plants and 3 foreign plants) before the issue was identified. To date, no operability issues have been reported or observed with 2301A and DRU controls containing the suspect IC. "In the DRU, the IC is used in the raise-lower circuit and in the ramp time circuit (the ramp time circuit controls the ramp rate of the DRU). The DRU is primarily used as the speed reference input signal to the 2301A and provides remote speed adjustment for the 2301A (similar to the function of a motor operated potentiometer - MOP). In some applications, the DRU has also been used as a replacement for the voltage regulator MOP; in this case, the DRU provides the voltage adjustment signal to the voltage regulator. Failure of this IC could impact speed (frequency) control (and in some cases voltage control) of the EDG. "In the 2301A, the IC is used in the start fuel limit circuit and in the speed signal input (magnetic pickup) circuit. The 2301A is the electronic governor used on many EDG's. It provides speed and/or load control of the diesel engine by communicating with the governor/actuator mounted on the diesel engine. Failure of this IC could impact speed (frequency) control of the EDG. "AFFECTED USERS: Thirty-four (34) controls were shipped to ESI containing IC's from the suspect lot. Twenty-six (26) of the suspect controls were in ESI inventory and have been returned to Woodward to have the suspect IC replaced. ESI shipped eight (8) controls with suspect IC's to nuclear customers as safety related items as identified in the tables below. "LISTING OF WOODWARD CONTROLS SHIPPED WITH SUSPECT IC's - (DOMESTIC PLANTS) McGuire - P/N # 9903-337, Customer PO # 00114776 Palo Verde - P/N # 9903-470 and # 9903-444, Customer PO # 500529186 "LISTING OF WOODWARD CONTROLS SHIPPED WITH SUSPECT IC's - (FOREIGN PLANTS) Korea-KHNP - P/N # 9903-470, Customer PO # K080553241 Almaraz - P/N # 9903-470 and # 9903-337, Customer PO # 2009/015 - ER09AT06805MA KRSKO - P/N # 9903-303, Customer PO # NEK-10271/309 "CORRECTIVE ACTION: The controls listed in the tables above should be returned to Engine Systems Inc. to have the suspect IC replaced as soon as possible. Contact ESI's Customer Service department with the part number and serial number of the control to be returned. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-09-09
45334 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-09-08 09:30 | 2009-09-09 14:53 | 2009-09-09 | DEFECT FOUND IN BUSSMANN FUSES "On September 8, 2009, Nebraska Public Power District (NPPD) completed a reportability determination which concluded that a Bussmann fuse with a batch code of R18 contained an underlying fabrication vulnerability consisting of a missing fuse link. NPPD has concluded this condition is reportable per 10 CFR Part 21. "This fuse is part of a batch of fuses purchased as Commercial Grade items and dedicated by NPPD for use at the Cooper Nuclear Station (CNS). The fuses are shipped directly from an authorized Bussmann facility to CNS. The fuse purchasing description is as follows: FUSE; 10 AMP; 250VAC; ONE-TIME; 50KA I.R. ; GENERAL PURPOSE; Manufacturer Part Number NON-10. The missing fuse link was discovered via destructive testing at CNS. The destructive test was prompted when the fuse failed a field continuity test prior to installation. The fuse had passed CNS dedication, which included a continuity test of 100% of the batch by the manufacturer. Although, none of the other fuses in this batch exhibited missing links via continuity testing, the fuse with the missing link is considered to be a continuation of quality problems previously reported to the Nuclear Regulatory Commission (NRC) per Emergency Notification Number 44634, as followed up by a written report from NPPD to the NRC dated December 2, 2008. That report identified that Several Bussmann fuses, Manufacturer Part Number NON-10, batch code J47, contained poor solder joints internal to the fuse assembly. "Bussmann NON-10 fuses are authorized by NPPD for use in both safety related and non safety related applications. The applicable dedication package identifies one of the safety functions as 'fuses are required to conduct the design basis load current without interruption.' If the fuses were installed without the condition being detected and failed upon valid demand of the associated circuit, the mission of the associated safety related equipment may not have been accomplished. Since the condition was found prior to installation, the safety function of the installed fuses remains unaffected and the supported equipment remains unaffected. Other locations where the batch R18 fuses are installed have been determined to be operable through actual circuit operation or measurements across the fuses. Therefore, this condition is NOT reportable under 10 CFR 50.72 or 50.73. "Vendor testing and current dedication practices should have precluded the possibility of placing a fuse with a similar condition into unrestricted spares. However, these barriers failed. This provided a potential for a Substantial Safety Hazard. This regulation does not credit pre-installation or post-maintenance testing for the detection of a defect. The dedication does not require CNS to perform a continuity check as credit is given to the vendor, per NUPIC survey, for performing the continuity check at the manufacturer's facility. "Since the fuses were stocked in unrestricted spares for essential applications, 10 CFR 21 applies, and the condition is reportable under 10 CFR 21.21. The responsible Corporate Officer has been notified of this condition per 10 CFR 21.21(d)(3)(i) on September 8, 2009 at approximately 0930 CDT. Pursuant to 10 CFR 21.21 (d)(3)(ii) written notification is due to the NRC within 30 days of this notification." The licensee will notify the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 21.21 |  |  |  | 0 | 2009-09-09
45333 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2009-09-08 20:10 | 2009-09-08 23:56 | 2009-09-09 | REACTOR SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO AN UNISOLABLE LEAK IN A CORE SPRAY MINIMUM FLOW LINE "On September 8, 2009, during performance of quarterly Core Spray (CS) system flow rate testing, a pinhole leak was identified in the 1B Core Spray Minimum Flow Line. The pinhole leak is located just downstream of the 1B CS minimum flow valve (1-1402-38B) and cannot be isolated from primary containment. "At 1935, hours it was determined that structural integrity of the piping could not be assured. Technical Specification 3.6.1.1, Required Action B.1, was entered and a plant shutdown was initiated at 2010 hours. "In addition, the 1B Core Spray system was declared inoperable. All other ECCS systems remain operable. The NRC Resident Inspector has been notified. "This event is being reported under 50.72(b)(2)(i) due to the initiation of a shutdown required by the plant's Technical Specifications." The licensee estimates reactor shutdown will be achieved at 0130 CDT. | 55 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-09-09
45332 | 0 | FLOWSERVE US INC. |  |  |  |  | 2009-09-08 | 2009-09-08 15:30 | 2009-09-08 | PART 21 NOTIFICATION - SOLENOID VALVE MAY NOT PERFORM ITS FUNCTION On July 13, 2009 Flowserve US Inc. Raleigh, NC was notified by Exelon - Byron Nuclear Power Station that they identified a potential problem with a Borg-Warner (BW/IP) Solenoid Valve (BW/IP Part No. 86868) received by Exelon as it was being tested by their Electrical Maintenance Technician. Flowserve conducted an evaluation of the issue. Flowserve's evaluation discovered that there existed dimensional deviations on the valve body parts that may cause the Solenoid Valve not to perform its intended function. Flowserve inventory discovered that the dimensional deviation also existed on 8 body parts in the current inventory and it was determined that this part was produced by the same subcontracted machining supplier since 2004. This renders the Solenoid Valve Body parts suspect from that time. This Solenoid Valve Body part is used in Solenoid Valve assembly models identified by the following Borg-Warner / Flowserve Part numbers: 86868 - Solenoid Valve Assembly - Normally Open; 86868-1 - Solenoid Valve Assembly - Normally Closed; 90628 - Solenoid Valve Assembly - Normally Open; 90638-1 - Solenoid Valve Assembly - Normally Closed. "Based upon Flowserve, Raleigh information, Solenoid Valve Assemblies with the above model / part numbers have been provided to the following licensees and purchasers as Safety - Related products: Exelon Company - Byron Station: P.O. 00000375 REL 13388 Qty.: 3 each; P.O. 00000375 REL 13573 Qty.: 3 each; P.O. 00000375 REL 13613 Qty.: 3 each; P.O. 00000375 REL 13650 Qty.: 2 each. Exelon Company - Braidwood Station: P.O. 00000375 REL 13439 Qty.: 1 each; P.O. 00000375 REL 13514 Qty.: 1 each; P.O. 00000375 REL 13522 Qty.: 1 each; P.O. 00000375 REL 13566 Qty.: 8 each; P.O. 00000375 REL 13661 Qty.: 2 each. Korea Hydro & Nuclear Power: P.O. U050425333 Qty,: 6 each. Control Components Inc.: P.O. 304835 Qty.: 2 each; P.O. 306820 Qty.: 6 each. "As Flowserve, Raleigh is not capable of determining if the defect could cause a substantial safety hazard based upon the service application which the Solenoid Valve Assembly may be used in. The licensees / purchasers of the subject Solenoid Valve Assembly will need to evaluate their applications to make this determination. "Flowserve, Raleigh is in the process of manufacturing the Solenoid Valve Assembly Bodies and will rebuild the Solenoid Valve Assemblies as they are returned by the licensees / purchasers. Please contact Gary Shaw (919-831-3331) or Edna Ulsamar (919-831-3331) to obtain a Return Material Authorization." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-09-08
45331 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-09-07 21:20 | 2009-09-07 22:02 | 2009-09-15 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION UNUSUAL EVENT "This report documents a condition in which WBN [Watts Bar Nuclear] Unit 1 met the criteria to declare a NOUE [Notification of Unusual Event] based on RCS [Reactor Coolant System] unidentified leakage. Prior to declaration, the event was terminated thus no declaration was made. This event is reportable within one hour as an acceptable alternative to reporting in accordance with 10CFR50.72(a)(1)(i) - declaration of any of the emergency classes specified in the licensees approved emergency plan. "During tagout installation in support of planned maintenance on the cation bed flush valve (1-FLV-62-921) in the CVCS/Letdown system, isolation boundary valve leakage of approximately 80 gpm was present for approximately three minutes. The leakage was terminated by reclosing opened vent (1-VTV-62-917) and drain valves (1-DRV-62-920). Cation Bed Inlet (l-ISV-62-915) and Outlet (1-ISV-62-916) and all other boundary valve isolations were verified to be in the correct, closed position per the tagout instructions. This RCS leakage was directed to the Tritiated Drain Collector Tank, thus all leakage was contained within plant systems and no radiological releases resulted. A work order will be initiated to troubleshoot and repair the faulty isolation valve. "This amount of leakage is in excess of the amount specified in WBN Emergency Plans for declaration of an NOUE based on >10 gpm unidentified leakage per EAL 2.5. Prior to declaration, the event was terminated, thus no declaration was made." The State of Tennessee and the NRC Resident Inspector has been notified. * * * RETRACTION ON 9/15/2009 AT 1113 FROM WES DANIEL TO MARK ABRAMOVITZ * * * "Event Notice 45331 reported a condition in which WBN Unit 1 conservatively determined it met the criteria to declare a NOUE based on RCS unidentified leakage. Prior to declaration, the event was terminated thus no declaration was made. "Based upon further review and discussion with others in the industry, the NOUE criterion cited, EAL 2.5, applies to specific sources of excessive RCS leakage. The source of the leakage discussed in the event has been confirmed as CVCS leakage, not RCS leakage. An action to clarify the basis and scope of this EAL is being pursued within TVA's Corrective Action Program. Therefore, Event Notice 45331 is being retracted. "The NRC resident has been notified." Notified the R2DO (Blamey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2009-09-07
45330 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2009-09-06 18:05 | 2009-09-06 20:17 | 2009-09-06 | OFFSITE NOTIFICATION DUE TO LOSS OF AMERTAP BALLS "Xcel environmental notified the State of Minnesota duty officer of the loss of approximately 1200 Amertap balls from the Unit 1 circulating water system. The Amertap balls are made of foam and are used for condenser tube cleaning. No further actions or notifications are required." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-06
45329 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-09-04 08:15 | 2009-09-04 14:46 | 2009-09-04 | FITNESS FOR DUTY - LICENSED EMPLOYEE CONFIRMED POSITIVE FOR ALCOHOL A licensed employee had a confirmed positive for alcohol during for-cause fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2009-09-04
45328 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-09-03 17:30 | 2009-09-03 23:18 | 2009-09-04 | OFFSITE NOTIFICATION TO LOS ANGELES COUNTY PUBLIC HEALTH RADIATION MANAGEMENT DIVISION "On September 3, 2009, at approximately 1730 PDT, Southern California Edison [SCE] was notified by a metal recycling vendor that a metal recycle load that was picked up at SONGS had been rejected at Terminal Island (Long Beach, CA) because it set off a radiation portal monitor as it was being processed through. The vendor (Alpert and Alpert) was requested to immediately ship the material back to SONGS. The County of Los Angeles Public Health, Radiation Management Division (Joji Ortego) called to confirm final destination, and a Special DOT Permit was issued to return the shipment to SONGS. "The truck is currently returning to San Onofre where SCE Health Physicists will evaluate the load. "SCE is reporting this event in accordance with 10CFR50.72(b)(2)(xi). SCE will provide an update to this report after the truck has returned to SONGS and the contents evaluated. "At the time of this report, Unit 2 and Unit 3 were operating at about 99 and 100 percent power respectively. "The NRC Resident Inspectors have been notified of this occurrence and will be provided with a copy of this report." * * * UPDATE FROM DAVID AXLINE TO CHARLES TEAL AT 1456 ON 09/04/09 * * * "The truck returned to SONGS site and SONGS has performed surveys on the contents of the truck cargo containers. SONGS' preliminary investigation did not identify any licensed radioactive material either internal or external to the containers. Surveys indicate that the source of the radiation appears to be boxes of ceramic tiles being removed from a storage area outside the Owner Controlled Area (OCA). Gamma isotopic analysis indicate the tiles appear to contain naturally occurring radioactive material (thorium byproducts). SONGS will continue to perform additional surveys to validate our initial conclusions. "The NRC Resident Inspectors have been notified of this occurrence and will be provided with a copy of this report." Notified R4DO (Farnholtz). | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-03
45327 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-09-03 15:25 | 2009-09-03 16:32 | 2009-09-03 | OFFSITE NOTIFICATION TO VIRGINIA DEQ "At 12:10 on September 3rd, 2009, the Surry Power Station Chemistry Department received the results from an offsite lab analysis of an Oil and Grease and Total Suspended Solids sample. This sample was taken from the discharge of the Surry Power Station Radiological Waste Facility on 8/11/2009. The results from the offsite lab indicated Oil and Grease results of 37 ppm, which exceeds the VPDES (Virginia Pollutant Discharge Elimination System) limit of 20 ppm. "This notification is being transmitted due to Notification of Other Government Agencies under 10CFR50.72(b)(2)(xi). The Virginia Department of Environmental Quality (DEQ) has been notified of this event. The Senior NRC Resident has been notified of this event. " | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-09-03
45326 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2009-08-17 | 2009-09-03 16:12 | 2009-09-03 | PART 21 - FAULTY EMERGENCY DIESEL GENERATOR START-UP SOLENOID VALVE The following is excerpted from a fax received from the reporting organization: "Engine Systems Inc. (ESI) began a 10CFR21 deviation evaluation on 08/17/09 after Brunswick Nuclear Plant (BNP) notified ESI of a failure of one of their air start solenoid valves. The valve failure reportedly occurred on 08/02/09 as indicated by a slow start of the safety-related emergency diesel generator during a surveillance run. This caused the diesel generator to be declared inoperable. Subsequently, ESI opened up an internal work order to receive back the failed valve (S/N 1230588) as well as two more valves believed to be suspect (S/Ns 1230583 and 1230586). Soon after, another internal work order was opened up to receive and evaluate 10 additional air start solenoid valves from BNP inventory. ESI completed the evaluation on 8/31/09 and determined the issue to be reportable in accordance with 10 CFR 21, 'Reporting of Defects and Non-compliance.'" The solenoid actuated valve in question opens when energized and closes when de-energized. "The valve is installed in-line with the starting air piping via 2" NPT connections in the valve body and is utilized for two applications on the Nordberg diesel engine. Upon receipt of a diesel generator start signal, the valve is energized and directs the starting air supply to either the starting air header of the diesel engine or turbocharger jet assist piping. Failure of the valve in these applications could result in a failure of the diesel engine to start and therefore prevent the diesel generator from performing its safety-related function. A total quantity of four valves are used per engine; one installed in the left bank starting air piping, one in the right bank starting air piping, and two in parallel supplying the turbocharger jet assist. "ESI's investigation determined that in failed valves, the upper DC sleeve had dislodged from the solenoid housing and slid down the bonnet, contacting the lower DC sleeve. This action disrupts the magnetic field to the extent that the valve will not function properly. "ESI has supplied a total quantity of 33 [of the affected] solenoid valves and all were supplied to BNP. There are only two utilities that use Nordberg diesel engines for safety-related power supply and BNP is the only nuclear site ESI is aware of that uses the [affected] valve." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-09-03
45325 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-09-01 | 2009-09-03 11:25 | 2010-03-19 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATOR DEVICES The following report was received via fax from the Commonwealth of Massachusetts: "In 2009, the Agency [Radiation Control Program of the Commonwealth of Massachusetts] billed the general licensee for the 2008 annual fee. The licensee was unresponsive and attempts to contact the licensee failed. On 9/1/09, the Agency discovered a published article in 'Business Week' that reported that the licensee, ACT Electronics, filed for bankruptcy in August 2008. Agency records indicate the licensee received these devices [static eliminators] in March 2007 and October 2007. The Agency contacted the manufacturer of the static eliminator devices, NRD Inc., and confirmed that the devices were not returned to the manufacturer. The Agency has declared the static eliminator devices as 'missing'." Manufacturer: NRD, Inc. Model #: P-2021 Serial Number: A2FL283, A2FW008, and AF2W009. Sources: (3) Polonium 210, 10 mCi each. MA Report No.: 09-8637 * * * UPDATE FROM JOHN SUMARES TO DONALD NORWOOD VIA FACSMILE AT 1409 EDT ON 3/19/2010 * * * "On 9/22/09, an Agency inspector visited the site of ACT Electronics, 2 Cabot Road, Hudson, MA. The building was empty and only a cleaning crew was present. The supervisor did not have any information on ACT Electronics. A 'for lease' sign was observed on the property and a real estate company's name, 'New Boston' and contact information was read. The inspector called the real estate company and was informed that the items in the building were auctioned off in April 2009, and that no one had any knowledge of radioactive material in any of the items. The inspector was given the name of the auction company, Branford Group of Philadelphia, PA, and a contact person name. The inspector sent an e-mail to the Branford Group requesting information on ACT Electronics. "The Agency received no response and [has had] no further contact with any person associated with ACT Electronics. The Agency considers this event to be closed." Notified R1DO (Burritt) and FSME DEO (McIntosh). Notified ILTAB (English) via E-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-09-08
45324 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2009-07-10 02:38 | 2009-09-03 09:04 | 2009-09-03 | ELECTRICAL SHORT CIRCUIT RESULTED IN PARTIAL HIGH PRESSURE INJECTION "This event is being reported via a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. In this case, the telephone report is not considered an LER. This report is being made under 10 CFR 50.73(a)(2)(iv)(A). "During a maintenance activity to replace an Engineered Safeguards Actuation System (ESAS) relay, one of the two High Pressure Injection (HPI) valves (MU-V-16C) in the 'B' train partially opened. The HPI system consists of the 'A' and 'B' trains, with each train containing two HPI valves. The cause of the partial opening of the HPI valve was inadvertent contact with adjacent energized circuits during the replacement of the ESAS relay. This resulted in a momentary short circuit, which bypassed the normal actuation logic, causing the HPI valve to open approximately 0.17 inches before blowing the control power fuse that stopped the valve movement. The event resulted in the inadvertent transfer of approximately 1000 gallons of water from the Make-up Tank into the Reactor Coolant System (RCS), before the valve could be restored to the closed position. No other valves or components actuated as a result of the inadvertent short circuit. RCS volume and pressure were stabilized and returned to normal. "The 'B' HPI train had been declared inoperable and the unit entered a 72 hour LCO at 1:03 AM on 7/10/2009 due to configuration requirements needed for the planned ESAS relay replacement. The inadvertent partial 'B' train HPI did not impact the 'A' HPI train, and the unit remained at full power during this event. Following troubleshooting and replacement of the control power fuse, MU-V-16C was tested and restored to OPERABLE at 4:59 AM on 7/11/2009. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-09-03
45323 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2009-09-02 08:30 | 2009-09-02 19:20 | 2009-09-10 | LOSS OF SPDS COMPUTER "This 8-hour non-emergency report is being made based upon requirements of 10CFR50.72(b)(3)(xiii) which states, 'The licensee shall notify the NRC as soon as practical and in all cases within eight hours of the occurrence of any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system).' An example of a major loss of emergency assessment capability is when the Safety Parameter Display System (SPDS) computer is unavailable for greater than eight hours. "At 0830 EDT on Wednesday, September 02, 2009 the SPDS Computer was found by the computer department to have one of three interface modules failed. The interface module transports data from the radwaste computer to SPDS. The failure resulted in a loss of 187 SPDS points. "All other SPDS points along with Plant Process Computer functions are available. Information Technology Department personnel are investigating the cause of the interface module failure, which is currently unknown. "No other control room emergency assessment capabilities have been adversely affected. All Control Room panel indicators and annunciators are responding properly." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 09/10/09 AT 1107 EDT FROM JASON SAWYER TO DONG PARK * * * "The Safety Parameter Display System [SPDS] was returned to service at 1030 EDT on 9/10/2009. Degraded SPDS components have been repaired and SPDS has been verified to be functional and capable of meeting all required design functions. "The licensee has notified the NRC Resident Inspector." Notified R1DO (Powell). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-09-02
45322 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-09-02 08:40 | 2009-09-02 10:43 | 2009-09-02 | AGREEMENT STATE REPORT - MOBILE SLURRY UNIT CAUGHT ON FIRE The following report was received via email from the State of Texas: "A mobile slurry unit (authorized under TX license G02259) in which a 200mCi, Cs-137, Thermo Fischer Scientific Model 5190 density gauge was mounted, caught fire. This occurred at an oil field temporary job site south of Fort Worth, TX. It was relayed that the fire had melted the lead at the top of the shield exposing the source as evidenced by elevated readings with a survey meter. It is believed that the source remains in the holder and has not been breached. Further, the gauge housing is still intact and [the] plan (already instituted) is to have the manufacturer remove the gauge for disposal at their facility. The device and source serial number are B7274 and CN-3171 respectively. "There was no exposure to anybody in excess of agency limits due to the manner in which the units were parked." Texas report # I-8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-09-07
45321 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-08-25 14:30 | 2009-09-01 22:28 | 2009-09-01 | AGREEMENT STATE - SURFACE CONTAMINATION LEVELS IN EXCESS OF LIMITS The following was received via facsimile: "An empty Type B, 30 gallon drum container was shipped on August 20, 2009 via public carrier from NSSI Sources and Services Inc. from Houston, Texas. It was delivered on August 25, 2009 to a Los Alamos National Laboratory (LANL) job site within a building at Penn State University in State College, PA. The shipping container was found to have external removable alpha contamination in excess of the US DOT limits noted in 49 CFR 173. LANL personnel informed their management and the carrier. Steps were also taken to verify that the contamination did not originate at Penn State. The individual truck that delivered the package to Penn State was surveyed by LANL personnel at about 2100 on 8/25/09. No contamination was found in the truck or the driver's area. There was no risk to any personnel at this facility due to this event. The first wipe found removable alpha contamination well in excess of the 2.2 dpm/centimeter squared DOT limit. After hours of decon, the removable contamination on the shipping containers was still over the limit. Onsite measurements noted little or no associated gamma radiation, and a sample was sent to LANL for alpha spectrum analysis. The material has been tentatively identified as curium-244 (Cm-244). "PA DEP (Department of Radiation Protection) Bureau of Radiation Protection (BRP) was initially notified August 26, 2009 and has continued to receive more complete information through September 1st. LANL will put a new lid on the drum, package up the waste, and get things ready for shipping on September 2, 2009. "The Commonwealth of PA has provided email notices of preliminary information related to this event to the NRC Region 1 State Liaison, and will continue to keep NRC informed of the status of our investigation." See also EN #45309 for the Texas report on the same event. State Event #: PA090028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-09-04
45320 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-09-01 16:09 | 2009-09-01 21:01 | 2009-09-01 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "Unit 1 High Pressure Coolant Injection (HPCI) system was declared inoperable after the 250V RMOV BD breaker 11A1 for the ECCS DIV II Inverter tripped. The cause for the breaker trip is currently being investigated. "This event is reportable within 8 hours in accordance with 10CFR 50.72(b)(3)(v) as an event or condition that at the time of discovery could have prevented the fulfillment of a safety function. It also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(vii). "Unit 1 remains at 100% power." NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-09-01
45319 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-08-31 21:55 | 2009-09-01 14:58 | 2009-09-01 | CONTROLLED SUBSTANCE DISOVERED ON SITE IN PROTECTED AREA Controlled substance discovered in protected area. Contact HOO for additional information. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2009-09-01
45318 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-08-31 | 2009-09-01 14:38 | 2009-09-01 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following notification was received via email: "Received call from licensee at 4:58 PM on 8/31/09, regarding a Troxler Model 3400 portable gauge containing 44 mCi of Am-241 and 9 mCi of Cs-137 which was damaged at a job site in Olmstead Falls, Ohio. Serial numbers and manufacturer of sources not currently available. Serial number of gauge not currently available. "The gauge user completed work with the gauge, locked the gauge, and then placed it on the ground under the tailgate of his truck. The user then went to the cab of the truck to perform some other tasks. While in the cab of the truck, the user noticed that heavy equipment operating at the job site was moving closer to his location, so he decided to move his truck. Forgetting that the gauge had been left outside the vehicle under the tailgate, the user backed over the gauge, causing damage to the case and shearing off the source rod at the case top. The portion of the rod containing the radioactive material remained inside the shielded body of the gauge. "The licensee's RSO immediately responded to the event and took readings to verify that the source was in the shielded case and that there was no contamination on the ground where the gauge was run over. The damaged gauge has been moved to the licensee's facility in Cleveland where it is in secure storage. The licensee intends to transport the damaged gauge to their licensed repair contractor's facility in Michigan. "ODH will be inspecting the licensee" Ohio Report No.: OH090009 Notified R3DO (Lipa) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-09-04
45317 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2009-08-31 14:45 | 2009-09-01 09:10 | 2009-09-01 | PART 21 REPORT - FAILURE OF A SPARE LIMITORQUE ACTUATOR MOTOR "On July 31, 2009, [Crystal River Unit 3] personnel performed a video probe inspection of a spare safety-related Limitorque SB-3/SMB-3 actuator motor magnesium rotor and end rings. Visual indications were observed in the outboard end of the motor which were cause for rejection based on specified acceptance criteria. The specific indication was a cracked weld with dislodged metal in the outboard end of the motor. "In 2007, the spare safety-related Limitorque SB-3/SMB-3 actuator motor (Motor Serial Number 7497004-001T1AL: Limitorque Part No. R-403-F04-0821) was purchased as safety-related Quality level 1 (QL-1) from AREVA under Purchase Order No. 337566. Limitorque purchased the motor from the Baldor Electric Company, doing business as the Reliance Electric Company, as commercial grade and dedicated the motor to safety related. "The above evaluation was completed on August 28, 2009. The FPC director/responsible officer was notified of the above determination on August 31, 2009. The vendor (Limitorque) and the NRC Senior Resident Inspector have been notified of FPC's intent to report this issue under 10CFR21.21." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 21.21 |  |  |  | 0 | 2009-09-01
45316 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2009-08-31 10:14 | 2009-08-31 18:16 | 2009-10-30 | SECONDARY CONTAINMENT BOUNDARY DOOR INOPERABLE "During normal entry / exit through secondary containment boundary door 1A401, it was discovered that the door would not latch closed due to interferences between the door and its frame. The door was unable to be latched closed for approximately 5 minutes which represented a possible path for uncontrolled release of radioactive material. No release of radioactive material occurred as a result of this event. "The time during which the door would not latch was spent diligently troubleshooting to determine why the door would not secure. When discovered, the interference was immediately removed and the door was secured (latched). Door 1A401 is now operable as a secondary containment boundary but is currently deactivated and posted by security to prevent use as a conservative measure until further inspection and maintenance can be preformed on the door to prevent this issue from reoccurring. "At this time secondary containment is operable with boundary door 1A401 closed and latched." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MICHAEL J. LARSON TO DONALD NORWOOD AT 1042 EDT ON 10/30/09 * * * "Retraction of Notification EN# 45316. "The event was reported by Grand Gulf Nuclear Station on 08/31/2009 at 1014 CDT. This update is being provided for the purpose of retracting that notification. "On August 31, 2009, during normal entry/exit through secondary containment boundary door 1A401, it was discovered that the door would not latch closed due to interferences between the door and its frame. The door was unable to be latched closed for approximately 5 minutes which represented a possible loss of safety function since it could have provided a path for uncontrolled release of radioactive material. No release of radioactive material occurred as a result of this event. "As part of the event investigation, the malfunction (inability to close and latch) of door 1A401 was simulated under controlled conditions. Data was obtained under normal ventilation conditions and under the condition with one train of Standby Gas Treatment System (SGT) operating. Analysis of the data determined that the SGT system was able to drawdown the secondary containment enclosure building pressure to greater than 0.311 inch of vacuum water gauge (for no assumed failures) which is above the Technical Specification (TS) 3.6.4.1 surveillance minimum requirement of 0.266 inch of vacuum water gauge (following a postulated accident with assumed failures) using one SGT subsystem. "Therefore, this event did not constitute a loss of the safety function of secondary containment and this event is not reportable." The licensee notified the NRC Resident Inspector. Notified R4DO (Powers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2009-08-31
45315 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-08-31 | 2009-08-31 18:03 | 2009-09-01 | EMERGENCY SIRENS INOPERABLE "At 1546 CDT the control room at the Fort Calhoun Power Station was notified that a siren test conducted at 1440 CDT had failed. At this time none of the station's emergency sirens are capable of being sounded. Utility personnel are troubleshooting the problem and expect to restore siren capability. Compensatory measures have been implemented. The NRC will be notified when siren capability has been restored." Harrison and Pattawattamie counties in Iowa, and Washington county in Nebraska have been notified. The NRC resident inspector has been notified. * * * UPDATE ON 08/31/09 AT 2055 EDT FROM ALAN PALLAS TO HUFFMAN * * * The licensee has reset a communications device that activates the sirens and restored operability to 38 out of the 103 total sirens around the site. To re-establish operability of the remaining sirens, the licensee will need to dispatch personnel to each siren to relink with the communications system. The time frame to complete this effort is estimated to be approximately 5 hours. The compensatory notification measures will remain in place until the sirens have been restored. The licensee will notify the Resident Inspector of this updated information. * * * UPDATE ON 09/01/09 AT 0236 EDT FROM ALAN PALLAS TO PARK * * * The licensee has restored 101 of 103 total sirens to service. Two sirens that are not in service are currently not accessible. They will be automatically restored to service at approximately 0330 CDT and verified in the morning. The licensee has notified the Resident Inspector of this updated information. Notified R4DO (Farnholtz). * * * UPDATE ON 09/01/09 AT 0943 EDT FROM ERICK MATZKE TO PARK * * * The licensee has restored all 103 of 103 total sirens to service. Harrison and Pattawattamie counties in Iowa, and Washington county in Nebraska have been notified. The licensee will notify the NRC Resident Inspector of this updated information. Notified R4DO (Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-31
45314 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-08-31 09:45 | 2009-08-31 16:04 | 2009-08-31 | FITNESS FOR DUTY - LICENSED EMPLOYEE CONFIRMED POSITIVE FOR ALCOHOL A licensed employee had a confirmed positive for alcohol during a fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2009-08-31
45313 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2009-08-31 09:44 | 2009-08-31 14:51 | 2009-08-31 | FITNESS FOR DUTY - SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 26.719 |  |  |  | 0 | 2009-08-31
45312 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2009-08-31 | 2009-08-31 12:29 | 2009-09-01 | AGREEMENT STATE REPORT - STOLEN RADIOGRAPHY CAMERA The following notification was received via fax: "Initial Notification: "Stolen Industrial Radiography Camera - contains approximately 18 Ci of Iridium-192. "Certified Testing Laboratories, New York State Department of Health (NYS DOH) radioactive materials licensee # C1920, had an Amersham model 660 industrial radiography device stolen early this morning (2-2:30 AM) from their facility at in the Bronx. The New York Police Department is investigating the theft." * * * UPDATE FROM ROBERT DESEREAU TO ERIC SIMPSON AT 1630 ON 08/31/09 * * * The following notification was received via fax: "The stolen unit is a QSA Global Model 660, S/N B1000 radiography exposure device (SS&D No. MA-1059-D-124-S) containing an approximately 18 curie Industrial Nuclear Company model 7, S/N N626, Iridium 192 sealed source (SS&D No. CA-384-S-102-U). Other radiography sources that were in the licensees possession at the same location were not affected and they remain under the licensee's control. The FBI is also on the scene." NYS DOH indicated that the reported source activity was decay corrected from the original source activity level. Notified R1DO (Dwyer), FSME (Suber) and DHS (Hill). Based on a phone update from NYC DOH at 1740, law enforcement is requesting that information related to this event be designated official use only - law enforcement sensitive. * * * UPDATE FROM ROBERT DESEREAU TO ERIC SIMPSON AT 1302 ON 09/01/09 * * * The following notification was received via fax: "The unit, with the source inside, has been recovered and it is in the licensee's possession. No additional details are available at this time. The police investigation is ongoing." Notified R1DO (Dwyer) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [10 empty] | 1 | NY | OTH | AGR |  |  |  |  | 1 | 2009-09-03
45311 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-08-31 07:21 | 2009-08-31 08:00 | 2009-08-31 | TSC POTENTIALLY OUT OF SERVICE "At 0721 on Monday, August 31, 2009, a portion of the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system and Technical Support Center (TSC) air conditioning system was removed from service for maintenance on the electrical power supply Motor Control Center (MCC). "The MCC being removed supports 3 of the 4 air conditioning units for the Technical Support Center, as well as the filtration system. The remaining air conditioning unit which is not supported by the MCC will remain in service. "Under certain accident conditions the TSC may become unavailable due to the inability of the ventilation system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system maintenance is scheduled to complete at 2100 on Monday, August 31, 2009. The licensee has notified the NRC Senior Resident Inspector. This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE AT 2147 EDT ON 8/31/09 FROM BRUCK TO HUFFMAN * * * "The TSC ventilation system air conditioning was returned to functional status at 21:37 on Monday, August 31, 2009. "This follow up notification is being made to provide closure from the initial notification under 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." The licensee has notified the NRC Resident Inspector. R3DO (Lipa) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-31
45310 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2009-08-29 06:15 | 2009-08-29 16:39 | 2009-08-29 | NUCLEAR CRITICALITY DETECTION SYSTEM INOPERABLE "On 08/29/2009 at 0615 PDT, during a scheduled testing of the Nuclear Criticality Detection [NCD] System, it was discovered that in one of the nine locations, two of three NCD units were non-functional. The two NCD units were non-functional apparently due to miswiring. This is still under investigation. "All movement of SNM [Special Nuclear Material] on site was suspended during the testing of the Nuclear Criticality Detection System. "This occurrence is reportable to the NRC in accordance with 10CFR70.50.b(2)(i). This is a 24 hour reporting requirement with a follow up 30 day written report. "Safety Significance of Event: "The safety significance is very low. Accidental nuclear criticality is highly unlikely. Only two of three NCD units in one of nine locations through out the plant were nonfunctional. The one deficient unit had one functional NCD that would have produced a trouble alarm if actuated. The remaining eight Criticality Detector systems were fully functional and covered the areas where SNM is processed." The licensee will be notifying their NRC Region II Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2009-08-29
45309 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-28 | 2009-08-28 18:22 | 2009-09-02 | AGREEMENT STATE REPORT - RADIOLOGICAL CONTAMINATION IN AN UNCONTROLLED AREA "On August 28, 2009, the [State] Agency was notified by the licensee that while performing radiological surveys in response to a shipping event, access to an area of their facility not normally controlled for radiological reasons was isolated due to the presence of radioactive contamination. The licensee believes that the radionuclide involved is Curium (Cm) - 244. The licensee is continuing their investigation and cleanup activities. The [State] Agency will provide updates when available." Texas report # I-8661 * * * UPDATE ON 09/02/09 AT 1436 EDT FROM ART TUCKER TO TEAL * * * "NSSI became aware of our contamination problem as a result of the shipment of an empty transport container in support of the DOE Offsite Source Recovery Program (OSRP) which operates from Los Alamos. The NSSI facility is used by OSRP as the primary consolidation facility for the Program. "NSSI shipped an empty 30 gallon 6M transport container to Penn State University at University Park, PA on August 20, 2009 by [a delivery company]. An attempt was made by the [delivery company] to deliver the package on August 24, but it was refused. The drum was accepted the morning of August 25, 2009. "On receipt, contamination was noted on the lid with another spot on the pallet and on the banding holding the drum to the pallet. OSRP personnel were at the site and confirmed the contamination. [The delivery company] was also notified and arrangements were made to survey the delivering vehicle. No contamination was found on the truck. "NSSI was notified midday and began to make measurements to determine if the contamination could be from the NSSI facility or whether it occurred during transit. NSSI tracked the drum back to its origination point in the NSSI facility and was able to confirm that the area immediately surrounding where the drum had been stored was contaminated. Further surveys and wipes showed activity across the storage area floor. Trace contamination was also found on the pallet banding equipment and on the OSRP source inspection and documentation table. Other spots of low contamination were found on a fork lift and a drum cart that was used to move the transport container that went to Pennsylvania. These areas were decontaminated so the equipment could be utilized. "As the radionuclide has not yet been identified, decontamination is being limited to small spots on the concrete outside the Longhorn building and on equipment or shields that may have been removed from the contaminated area. "NSSI has decided to delay any decontamination activities pending identification of the nuclide. Time will be required to get air sampling set up and operating and to coordinate with the decontamination personnel. "At the moment, the radionuclide, quantity, and physical/chemical form involved has not been specifically identified. Surveys tell us the radioactive material is an alpha emitter. Gamma spectrum tells us that the nuclide is not Am-241. Long term gamma spectrum counts of wipes collected also tend to indicate the absence of Pu-238 and Pu-239 as there is always some Am-241 present with these nuclides. Liquid scintillation identifies the alpha energy as being higher than the 5.4-5.5 MeV from Am-241, the 5.4-5.5 MeV for Pu-238 and the 5.1-5.2 for Pu-239. Polonium 210 would also appear to be excluded as it's alpha energy is only 5.3 MeV. In addition, NSSI handles almost no Po-210. At this time, the primary suspect at this time is Curium-244 which has an alpha energy of 5.7-5.8 MeV. We do expect to have nuclide confirmation within a few days as the State of PA and Los Alamos both have samples for evaluation. "At this point, we do not have any indication of personnel radiation exposure. We will be talking with Los Alamos internal dose assessment people early next week. "Until we have nuclide information and further evaluate the contamination present in the restricted area, the involved area will remain closed to all NSSI personnel. NSSI is currently in the process of contacting the decontamination experts that assisted NSSI several years ago with an Am-241 contamination incident. We expect to be ready to start the decontamination process within the next 2-3 weeks." See also EN #45321 for the Pennsylvania report on the same event. Notified R4DO (Farnholtz) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-09-02
45308 | 0 | KARMANOS CANCER CENTER |  |  |  |  | 2009-08-27 18:00 | 2009-08-28 17:05 | 2009-08-28 | MEDICAL EVENT - PATIENT RECEIVED 60% LESS DOSE THAN PRESCRIBED The licensee was performing reviews on past procedures when they discovered the following reportable event: On March 3, 2009, a patient received a permanent prostate implant with a prescribed D90 dose of 144 Gy. The implant used fifty-eight I-125 seeds. On April 3, 2009, the patient returned to the facility for a post-implant CT/dose reconstruction and it was determined that the D90 dose received by the patient was 85 Gy which is 60% of the prescribed dose. The patient and prescribing physician were notified and the patient underwent an external radiation treatment to compensate. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | OTH | AGR | 35.3045(a)(1) |  |  |  | 0 | 2009-09-04
45307 | -1 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-08-27 23:10 | 2009-08-28 01:13 | 2009-10-20 | NON-CONSERVATIVE TECHNICAL SPECIFICATION SETPOINTS DISCOVERED "Non-conservative Tech Spec setpoints were discovered that affected Steam Leak Detection for Unit 1 and Unit 2 [High Pressure Coolant Injection] HPCI room high differential temperatures. During a steam leak detection system design basis leak, the present temperature setpoint would not isolate the HPCI steam supply piping. "A calculation has been performed by engineering which demonstrates that, with both room coolers secured, a design basis steam leak will result in the room ventilation differential temperature exceeding the present Tech Spec setpoints. At this time, the room unit coolers have been secured and HPCI and the associated steam leak detection system remain operable. Calculations are in-progress by engineering for changes to the high differential temperature steam leak detection setpoint." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM J. BROILET TO P. SNYDER ON 10/20/09 AT 1154 EDT * * * "This is a retraction of the event notification made on 8/28/09 at 0113 EDT. This event (#45307) was initially reported as a condition that could have prevented fulfillment of a safety function under the requirement of 10 CFR 50.72 (b)(3)(v)(c). "A follow-up review of the HPCI equipment room steam leak detection system calculations determined that other HPCI equipment room ambient high temperature instruments would have automatically actuated a HPCI steam line isolation during a 25 gpm design basis HPCI steam line leak event. "Therefore, a condition did not exist at the time of discovery that could have prevented the fulfillment of the HPCI steam line isolation safety function." The licensee notified the NRC Resident Inspector. Notified R1DO (Doerflein). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2009-08-28
45306 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-08-27 19:45 | 2009-08-27 21:40 | 2009-08-27 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 1945 on 8/27/09 Indian Point Unit #3 automatically tripped due to a turbine trip signal. The cause for this automatic trip is under investigation. All auxiliary feedwater pumps started as expected. All control rods inserted as expected. Currently, Indian Point #3 is in Mode 3. The reactor coolant system is at Normal Operating Temperature, Pressure and Level. Offsite power is available and supplying all safeguards busses. Heat removal is to the main condenser via the steam dumps. Indian Point Unit 2 is unaffected and remains in Mode 1 at 100% power. The [NRC] Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-08-27
45305 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-08-27 09:20 | 2009-08-27 18:20 | 2009-08-27 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST BY NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness for duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2009-08-27
45304 | 0 | BANDMILL COAL CORPORATION |  |  |  |  | 2009-08-27 05:00 | 2009-08-27 12:51 | 2009-08-27 | FIRE INVOLVING RADIOACTIVE MATERIALS The licensee facility experienced a large fire on 08/27/09 starting at approximately 0500. The facility involved houses 4 devices containing radioactive materials. These devices are used for process control. Three (3) of the devices contain 200 milliCuries of Cs-137 (Texas Nuclear Model #5202) and one device contains 100 milliCuries of Cs-137 (Texas Nuclear Model #7062BP). Currently the floors that contain the devices are believed to be intact. This however may change as the condition of the building degrades. The Mine Safety and Health Administration (MSHA) is currently not allowing anyone into the facility due to the treacherous conditions. It is not known when the licensee will be able to determine the integrity of the sources. The Logan County, West Virginia Fire Department is responding to the fire, are aware of the sources, and are wearing appropriate personnel protective equipment. The firefighters have been using a Geiger counter to ensure radiological safety. Initial surveys of firefighters that entered the building were negative. The source of the fire is still under investigation, but the licensee does not believe the fire to be suspicious in nature. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2009-08-27
45303 | 0 | OHIO DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-25 | 2009-08-27 10:58 | 2009-08-27 | AGREEMENT STATE REPORT - DISCOVERY OF ABANDONED RADIOACTIVE SOURCE The following information was received from the State of Ohio via e-mail: "The Ohio Bureau of Radiation Protection was informed on 8/25/09 of the discovery of an abandoned radioactive source at the Meridian Automotive Systems, Inc. plant in Jackson, Ohio. Investigation on 8/26/09 revealed that the source is a 500 mCi Am-241/Be source in a generally licensed RMD Compuglass Analyzer. The EPA was notified and will pick up the source for disposal. The source is secure at the site." Ohio reference number: Ohio 2009-025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-09-01
45302 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-08-25 21:40 | 2009-08-26 16:19 | 2009-08-26 | AUTOCLAVE PRESSURE RELIEF SYSTEM INOPERABLE "On 08-25-09, the Plant Shift Superintendent (PSS) was notified that C-360 (Toll Transfer & Sampling Building) Autoclave #4 had a failure in the autoclave pressure relief system. The autoclave pressure relief system utilizes a rupture disc in series with a relief valve. A pressure indicator is located between the rupture disc and the relief valve to verify that the pressure between the two devices is less than 5 psig per TSR 2.1.3.2 Condition A. This pressure is limited to prevent any significant bias to the actuation pressure of the rupture disc. TSR 2.1.3.2 requires that the actuation pressure of the autoclave pressure relief system shall not exceed 157.5 psig. On 08-25-09 at 2140 CDT, an operator was preparing to place the #4 autoclave into service, per the proper operating procedure, when the pressure between the rupture disc and the relief valve was found to be 5.5 psig, a pressure which indicated a failure in this required safety system. The autoclave was in a mode where this TSR system is required to be operable. There is low safety significance to this failure as the TSR does allow the current operating cycle to be completed under this condition. "Since the operating cycle was just started and steam had not been applied to the autoclave, the operating evolution was abandoned and the autoclave was declared inoperable and taken out of service. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-09-2084; PGDP Event Report No. PAD-2009-12; Worksheet No. Responsible Division: Operations" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2009-08-26
45301 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2009-08-22 07:30 | 2009-08-26 16:00 | 2009-09-04 | AGREEMENT STATE REPORT - EXTERIOR ACCESS DOOR TO RADIOLOGY LAB FOUND OPEN While responding to an audible alarm, the Clayton County Police Department found an exterior door open to the Radiology Lab at the Kaiser Permanente Nuclear Medicine Clinic located in Jonesboro, Georgia. The Clayton County Police Department notified the Federal Bureau of Investigations and the Georgia Information Sharing and Analysis Center. The Georgia Information Sharing and Analysis Center then contacted the Georgia Radioactive Materials Program. The licensee is authorized to possess diagnostic imaging isotopes. At this time, no information is available whether radiological material is missing, or if the open door was the cause of the alarm. The investigation is ongoing. * * * UPDATE FROM IRENE BENNETT TO JOHN KNOKE AT 1036 EDT ON 09/04/09 * * * The State conducted an inspection at the licensee's facility and determined that no material was missing. A complete report will follow later. Notified FSME (Angela McIntosh), R1DO (James Dwyer), and ILTAB (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2009-08-31
45300 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-08-26 09:00 | 2009-08-26 09:20 | 2009-08-28 | LOSS OF RESPONSE CAPABILITY DUE TO MAINTENANCE RENDERING TSC NON-FUNCTIONAL "The TSC Air Handling Unit will be taken OOS to repair one of the two compressors. In order to perform this corrective maintenance, the TSC HVAC will be removed from service for [approximately] 1 hour to disconnect the compressor to be repaired and in doing so will render the TSC HVAC inoperable which renders the TSC as non-functional. The TSC HVAC will be restarted to return the TSC to an operable and functional status. The work to repair or replace the compressor is planned to be completed within (1-3 days). After the work is completed, the system will be taken out of service again to reconnect the compressor ([approximately] 1 hr) and return the TSC HVAC to service." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J.W. COVINGTON TO V. KLCO AT 1045 ON 8/28/2009 * * * Maintenance was completed and the TSC was restored to operable status. The licensee notified the NRC Resident Inspector. Notified the R2DO(Widmann). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-26
45299 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-08-25 19:35 | 2009-08-25 21:15 | 2009-08-26 | OFFSITE NOTIFICATION DUE TO A WATER LEAK CONTAINING TRITIUM "Oyster Creek Nuclear Generating Station notified the New Jersey Department of Environmental Protection of a leak of water containing tritium from an underground condensate transfer pipe at the turbine building penetration of less than 20 gpm and concentration of approximately 10 million picocuries/milliliter. "The leaking water is being pumped to storage drums and a plan is being developed to replace the six-inch condensate transfer piping which penetrates the turbine building inside a 42 Inch long sixteen inch diameter penetration sleeve. Previously, water was observed coming from the sleeve into the turbine building where it was draining to a sump. The leak coming out of the turbine building was uncovered during excavation to determine if the condensate was leaking to the soil." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY CALVIN TAYLOR TO JASON KOZAL AT 0907 ON 08/26/09 * * * The licensee corrected the reported concentration to 10 million picocuries/liter. Additionally, after closer examination the leak rate was determined to be approximately 5 GPM vice the initially reported less than 20 GPM. The licensee will be issuing a press release. Notified the R1DO (White). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-08-25
45298 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-08-25 | 2009-08-25 15:42 | 2009-09-01 | AGREEMENT STATE REPORT - X-RAY FLUORESCENCE ANALYZER REPORTED STOLEN The following information was received from the State of Florida via e-mail: "Licensee reports that a handheld x-ray fluorescence (XRF) analyzer [containing 30 mCi of Am-241] was stolen. The device was last seen when used on 7/5/09. The device was placed in the office of user and was noted missing when it was looked for on 8/11/09 to use for a job. On 8/24/09, after searching through the company office, the licensee determined that it was missing/stolen. The licensee reports that [the device] is password locked. Licensee is considering offering a reward. Licensee will submit a written report. Florida is investigating." Florida incident number: FL09-063 * * * UPDATE FROM STEVE FURNACE TO ERIC SIMPSON AT 1420 ON 09/01/09 * * * The following notification was received via phone: The handheld XRF analyzer was found by the licensee stored in a closet onsite. A member of the technical staff had placed the unit in a closet in order to move it out of the area where a cleaning crew was working. The analyzer is a generally licensed item. The State of Florida expects no further actions to be taken concerning this event. Notified R1DO (Dwyer) and FSME (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-08-28
45297 | 0 | USEC |  |  |  |  | 2009-08-10 | 2009-08-25 15:14 | 2009-08-25 | PART 21 REPORT - MISSING RETRACTING BALL IN BALL LOCK PINS ON URANIUM CYLINDER "On August 10, 2009, a failure to comply was identified during USEC's routine refurbishment of a UX-30 transportation overpack. The overpack was being prepared for shipment of a clean empty 30B cylinder to a Russian facility where the cylinder would be filled with enriched uranium hexafluoride and returned to the Paducah Gaseous Diffusion Plant (PGDP). The failure to comply involves a missing retracting ball in a ball lock pin that is designed with two required retracting balls. Ten of these ball lock pins are used to hold the top and bottom half of the UX-30 overpack together during transport. "The firm supplying the ball lock pins was Columbiana Hi Tech (CHT). USEC has received 3,732 ball lock pins from CHT since July 2008, in five separate purchase orders. This report is the only instance to USEC's knowledge that a ball lock pin has had a missing retracting ball. Six hundred eighty-six of these pins have been supplied by USEC to its shipping agent. "USEC Quality Control inspected approximately one thousand one hundred sixty-four ball lock pins currently on site, but not yet installed, to insure the pins had both balls installed and the pins functioned correctly. This was completed on August 24, 2009. Not additional defective pins were discovered. "The USEC shipping agent was ordered, on August 21, 2009, to return to PGDP the remaining uninstalled ball lock pins from the six hundred eighty-six supplied and in its possession. A USEC Quality Control inspection will verify both balls installed and the pins function correctly. "USEC intends to perform an assessment of the supplier (CHT) to ensure the supplier is adequately implementing its quality programs and is ensuring its sub tier suppliers are meeting established quality requirements. This assessment is scheduled to be conducted beginning September 28, 2009, barring any unforeseen circumstances." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2009-08-25
45296 | 0 | GENERAL ATOMICS |  |  |  |  | 2009-06-30 | 2009-08-25 15:17 | 2009-08-31 | PART 21 - RADIATION MONITOR DEFECT "The defect is contained in the General Atomics Electronic Systems, Inc (GA-ESI) radiation monitoring system model RM-80 firmware. The RM-80 firmware anomaly was initially identified at the St. Lucie Nuclear Power Plant. The radiation monitor was part of the control room outside air intake ventilation radiation monitors. "More specifically, if the radiation monitor is already in a high and or alert alarm state, and subsequently suffers a loss of power, then upon restoration of power to the unit, the RM-80 high and or alert alarm relays are not reenergized by the RM-80 firmware. This in turn prevents the relays that are located in the [RM]-80 from performing their safety related function. "This error in the firmware only affects those plant sites that connect annunciator panels or other safety related equipment to the RM-80 Alert and High Alarm relays. "Plant sites that use RM-80 radiation monitors will be advised to test their systems for this anomaly. When so requested, GA-ESI will provide all necessary information to plants on how to test their RM-80 radiation monitors, and how to receive firmware upgrades if the condition is found during testing." General Atomics will notify the following affected plants: Beaver Valley, Braidwood, Byron, Callaway, Indian Point 2 &3, Limerick, River Bend, Shearon Harris, South Texas, St. Lucie, Waterford, and Wolf Creek. * * * UPDATE FROM KEITH E. ASMUSSEN TO C. TEAL AT 1900 ON 8/31/2009 * * * "This notification is an update to a notification made on 1506 Hrs. EST on August 25, 2009 regarding the existence of a defect. This notification is being provided in compliance with the requirements of Title 10 Code of Federal Regulations Part 21.21. "In the initial notification, under the section titled 'Locations affected by the reported condition,' General Atomics Electronic Systems, Inc. (GA-ESI) provided a table (Table1) that listed sites and corresponding firmware sets having safety related RM-80 software that had been found to contain the reported firmware anomaly. GA-ESI has now identified one additional firmware set that should be included in Table 1. The site is Braidwood and the firmware set is bhr165/01. "Accordingly, Table 1 has been revised to include this firmware set for the Braidwood site. The revised Table 1 is attached to this update notification. "Also, please note that earlier today, August 31, 2009, GA-ESI emailed a notification letter to its customer contact at the Braidwood site. "All other information remains the same as was initially reported on August 25, 2009" Notified R3DO (Lipa). Also notified NRR and NRO via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-08-25
45295 | 0 | ALLEGIANCE HEALTH |  |  |  |  | 2009-08-24 13:47 | 2009-08-25 14:50 | 2009-08-25 | POTENTIAL MEDICAL EVENT - D90 DOSE LESS THAN PRESCRIBED DOSE On April 16, 2009, a patient received a permanent prostate implant of I-125 seeds. On August 24, 2009, post-implant dosimetry analysis, performed multiple times using multiple modalities, determined the D90 dose was 46.8% of prescribed dose. The prescribed dose was 145 Gy using 0.577 u/seed and 57 seeds. The referring physician and patient have been notified. The physician will be conducting a corrective implant. The licensee is conducting an investigation and will be determining corrective actions. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-08-31
45294 | 0 | ALLEGIANCE HEALTH |  |  |  |  | 2009-08-24 13:47 | 2009-08-25 14:50 | 2009-08-25 | MEDICAL EVENT - D90 DOSE LESS THAN PRESCRIBED DOSE On April 16, 2009, a patient received a permanent prostate implant of I-125 seeds. On August 24, 2009, post-implant dosimetry analysis, performed multiple times using multiple modalities, determined the D90 dose was 76.3% of prescribed dose. The prescribed dose was 145 Gy using 0.679u/seed and 54 seeds. The referring physician and patient have been notified. The licensee is conducting an investigation and will be determining corrective actions. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-08-31
45293 | 0 | HEARTS CLINICS NORTHWEST |  |  |  |  | 2009-08-24 16:00 | 2009-08-25 12:53 | 2009-08-25 | MEDICAL EVENT - ACTUAL DOSE LESS THAN SCHEDULED DOSE Two patients were scheduled for treatment using Tc-99m. One patient was scheduled to receive a dosage of 8 mCi and the other patient a 25 mCi dose of a different Tc-99m chemical make-up. However, the wrong patient was given the 8 mCi (versus the 25 mCi). Both the patient and physician were notified of the wrong dosage. The critical organ of concern is the upper intestine and the exposure is calculated to be 1.44 Rem which is below the administrative limit. There is no expected medical effects to the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-08-31
45292 | 0 | LOUISIANA DEQ |  |  |  |  | 2009-07-28 | 2009-08-25 10:56 | 2009-08-25 | AGREEMENT STATE REPORT - SOURCE DISCONNECT OF RADIOGRAPHY CAMERA The following is a summary of a fax received from the state of Louisiana: At approximately 10:30 p.m. on the night of July 28, 2009, a radiographer failed to connect the source tube to the camera before he cranked out the source. The cable stop that is attached to the worm cable did not work properly. After dismantling the crankout assembly, the source was hand retrieved and placed back into the camera using the worm cable. A survey was taken to verify that the source was stored safely. The total time of retrieval was approximately 2 minutes. No personnel were overexposed during this event. Louisiana Report #: LA090016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-08-31
45291 | 0 | LOUISIANA DEQ |  |  |  |  | 2009-07-09 | 2009-08-25 10:57 | 2009-08-25 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING RADIOPHARMACEUTICALS The following report was received from the State of Louisiana via facsimile: "On July 9, 2009, a facility reported a mislabeled unit dose from GE Healthcare nuclear pharmacy. Three 20 mCi unit doses of Tc-99m MDP (bone scans) were ordered by Ochsner [a medical facility]. Two patients were injected. After viewing the images, it was determined that the unit doses were mislabeled. An investigation of GE Healthcare was performed. A preliminary cause was determined to be a mix up of MDP cold vial with DTPA [renal scans] as they closely resemble each other with the same vial configuration and same color label. Contributing factors leading to the incident were Tc-99m/Mo-99 shortage, late arrival of generators, increased number of kits to prepare as a result of the shortage, and pharmacist working alone. Corrective actions involved reviewing procedures and discontinuing manual changes of inventory dispensed on prescription labels." Louisiana incident number: LA090017 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | GEN |  |  |  |  | 0 | 2009-08-31
45290 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-08-24 18:50 | 2009-08-24 23:38 | 2009-08-24 | CONDENSATE BOOSTER PUMP TRIP RESULTING IN A MANUAL REACTOR SCRAM "On 8/24/09, at 18:50 Unit 3 was manually scrammed due to loss of 2 of the 3 Condensate Booster Pumps due to low pump suction pressure. The cause for the Condensate Booster Pump low suction pressures is unknown at this time, but is under investigation. After the reactor was scrammed manually, reactor water level lowered below the automatic scram set point (+2 inches) and below the automatic start for HPCI and RCIC (-45 inches). All expected Primary and Secondary Containment isolation valves operated as required, isolation groups 2,3,6 and 8 were actuated. Both reactor recirculation pumps tripped due to the low reactor water level. HPCI and RCIC actuated as expected to restore reactor water level. Reactor pressure control was maintained on the turbine bypass valves, and no Main Steam Relief Valves (MSRVs) were opened as a result of the transient. "At this time the unit is stable in mode 3. Reactor water level is being controlled using one Reactor Feedwater pump, HPCI and RCIC have been returned to standby readiness. The 3B Reactor Recirculation Pump has been returned to service. Reactor pressure is being automatically maintained by the main turbine bypass valves. "This event is reportable as a 4 hour non-emergency report due to 10CFR 50.72(b)(2)(iv)(A) and (B) (ECCS discharge to the reactor and Reactor Protection System (RPS) actuation) and as an 8 hour non-emergency report due to 10CFR50.72(b)(3)(iv)(A) (specified system actuations)." All rods fully inserted on the SCRAM. The plant is in its normal shutdown lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2009-08-24
45289 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2009-08-24 14:15 | 2009-08-24 21:21 | 2009-08-24 | STATION SAFETY GRADE PNEUMATIC SUPPLY ISSUE "This event is being reported pursuant to the requirements of 10 CFR 50.72(b)(3)(v) as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of systems supplied by the station safety-grade pneumatic supply. The systems affected include the primary containment isolation valves (i.e., large primary containment isolation valve boot seals) and the reactor-building to suppression pool vacuum breakers. "On 8/24/09 at 1330, while troubleshooting the receipt of unexpected alarms during containment valve stroking the previous week, Exelon personnel discovered a valve closed instead of the expected open position. Licensed personnel concluded at 1415 that the out of position valve was restricting the Containment Atmospheric Dilution tank from supplying operating nitrogen to the Safety Grade Instrument Gas (SGIG) system headers for Peach Bottom Units 2 and 3. The valve was re-opened at 1445 (within the one hour action time required by Technical Specifications) and other system valves were verified to be in the required positions." The licensee notified the NRC Resident Inspector. | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-08-24
45288 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-06-01 | 2009-08-24 13:29 | 2009-08-24 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE STUCK OUTSIDE CAMERA "On June 1, 2009, licensee personnel were performing radiography when the projector fell on the guide tube while the source was exposed, preventing the source from being retracted into the shield. Licensee personnel tried to retract the source but were unsuccessful. The area was secured and monitored until a source retrieval team could be assembled and arrive on site. On June 2, 2009, the source retrieval team arrived and performed the source retrieval. The damaged guide tube was replaced and tested and the camera operates properly. The radiographer received 325 mRem by dosimeter and the radiographer's assistant received 38 mRem. No overexposure is anticipated. "The incident was reported to the Agency within the 30 day reporting time. However, the received report was misplaced until August 24, 2009. "Incident Number: 09-40 "NMED Number: NC090040" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-08-27
45287 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-08-24 09:00 | 2009-08-24 13:01 | 2009-08-25 | EOF BACKUP DIESEL FAILURE AND EOF OUTAGE "On August 24, 2009 at 0900 EDT the Fermi 2 Emergency Operations Facility (EOF) was declared unavailable due to failure of the EOF backup diesel generator to start during weekly testing. Fermi 2 is making this notification in accordance with 10 CFR 50.72(b)(3)(xiii). In the event that EOF activation is necessary, the alternate EOF will be utilized. Activation and use of the alternate EOF is included in Fermi's Radiological Emergency Response Preparedness Plan. The alternate EOF has been verified available. Investigation into the failure of the EOF backup diesel generator start failure is in progress. Fermi will notify the NRC when EOF availability is restored. " The licensee notified the NRC Resident Inspector. * * * UPDATE FROM GREG MILLER TO HOWIE CROUCH @ 1534 ON 8/25/09 * * * "Repairs have been made to the EOF backup diesel generator and it was successfully tested. The EOF is now available for use. The NRC Resident Inspector has been notified." Notified R3DO (Orth). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-24
45286 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2009-08-24 11:00 | 2009-08-24 12:48 | 2009-08-24 | MANUAL TRIP DUE TO LOSS OF POWER TO CONTROL RODS "Following completion of surveillance testing for the electrical checks of the Control Rod Drive power train, the operating crew observed that Group 7 regulating control rods unexpectedly lost power and inserted into the core. The Operators manually tripped the reactor prior to exceeding any RPS trip set point. There were no other safety system actuations and the plant is stable at normal post-trip temperature and pressure." There are seven rods in Group 7. Operators tripped the unit within 7 seconds. All rods fully inserted on the trip. The plant is removing decay heat through the main condenser and feeding generators with auxiliary feed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-08-24
45285 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-08-24 02:40 | 2009-08-24 04:06 | 2009-08-25 | TSC AIR FILTRATION SYSTEM INOPERABLE DUE TO PLANNED MAINTENANCE "Planned maintenance activities will commence today (August 24, 2009) on the Quad Cities Station Technical Support Center (TSC) ventilation air filtration system. The maintenance will be completed in approximately 36 hours, and is scheduled to be worked continuously to minimize out-of-service time. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing procedures; contingency plans are in place to expeditiously restore the TSC ventilation to an operable status. If TSC evacuation is warranted due to radiological conditions, the facility will be relocated in accordance with existing procedures. "This event is reportable per 10CFR50.72(b)(3)(xiii) since the scheduled maintenance affects an emergency response facility. "The NRC Resident Inspector has been notified." * * * UPDATE FROM KEVIN O'SHEA TO CHARLES TEAL AT 1858 ON 8/25/09 * * * The TSC air filtration system maintenance has been completed. The TSC has been returned to normal operation. Notified R3DO (Orth). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-24
45284 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2009-08-23 17:50 | 2009-08-23 21:52 | 2009-08-23 | UNPLANNED INOPERABILITY OF THE HIGH PRESSURE CORE SPRAY SYSTEM "A momentary alarm for loss of HPCS system DC control power was received in the NMP2 control room. Troubleshooting has determined that a loose connection existed at a fuse block in the DC control power circuitry. The HPCS system was declared inoperable and Technical Specification 3.5.1, Condition B, was entered at 1715. In accordance with Condition B, the Reactor Core Isolation Cooling (RCIC) system was verified to be operable. "Repairs were subsequently completed and the HPCS system has been declared operable as of 2046." The licensee has notified the NRC Resident Inspector | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-08-23
45283 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2009-08-21 16:30 | 2009-08-21 17:15 | 2009-08-21 | INDIVIDUALS UNESCORTED ACCESS REVOKED An individual who did not provide complete information had his access to the facility terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 96 | 0 | 100 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-08-21
45282 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-08-21 09:52 | 2009-08-21 15:02 | 2009-08-21 | LOGIC FOR COMMON ACCIDENT SIGNAL IS FLAWED FOR SAFE SHUTDOWN INSTRUCTION "Safe Shutdown Instruction (SSI) 0-SSI-9 for an Appendix R fire event requires for a Unit 1 Safe Shutdown success path that 4kV Shutdown Board A be supplied by Diesel Generator 3A via 4kV Shutdown Board 3EA. During a Unit 2 simulator exercise utilizing this SSI, reactor vessel water level lowered to Level 1 (-122 inches) causing a Common Accident Signal (CAS) trip of 4 Kv Shutdown Board 3EA inter-tie breaker (1844) that de-energized 4kV Shutdown Board A. This condition will not support the Unit 1 success path for alternate decay heat removal during an Appendix R fire. The 4 Kv Shutdown Board A must be re-energized by closing breaker 1844. For this SSI (0-SSI-9) the subsequent automatic start of the 2A RHR and Core Spray pumps in response to the CAS logic has not been considered in the development of the SSIs. In response to this condition, compensatory measures have been implemented to provide equivalent shutdown capability, documented on Fire Protection Impairment Permit (FPIP) 09-1920. "This event is reportable within 8 hours under 10CFR50.72 (b)(3)(v)(A) - Any event or condition that results in the condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: Shut down the reactor and maintain it in a safe shutdown condition. This event is also a reportable within 60 days under 10CFR50.73(a)(2)(v)(A) - Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: Shut down the reactor and maintain it in a safe shutdown condition. "This condition has been documented in the BFN Corrective Action program as PER# 177130. Unit 1, 2 and 3 remain at 100% power and are not affected by this event. The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2009-08-21
45281 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-08-21 06:48 | 2009-08-21 11:22 | 2009-08-21 | FEED WATER ISOLATION DUE TO HIGH STEAM GENERATOR WATER LEVEL "Turbine trip and Feed [Water] Isolation Signal generated as result of high level in 'A' Steam Generator. At approximately 0648 CDT a turbine trip and Feed Water Isolation Signal was generated when the level in the 'A' Steam Generator exceeded the initiation set point of 78%. Steam Generator level returned below the initiation setpoint at approximately 0656 CDT. "The turbine was already in the tripped condition and Feed Water Isolation Valves closed due to the plant trip that occurred at 1549 CDT on 8/19/2009 (Reference EN# 45278). "Steam Generators are being fed with the motor driven Auxiliary Feed Water Pumps. Decay heat removal is via the Steam Generator Atmospheric Relief Valves. The plant is in Mode 3 with Reactor Coolant System pressure at approximately 2235 psig and temperature at approximately 561 F. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-08-21
45280 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-08-20 16:43 | 2009-08-20 20:14 | 2009-08-25 | LOSS OF PLANT INTEGRATED COMPUTER SYSTEM RESULTING IN LOSS OF ERDS AND SPDS "At 0950 the Plant Integrated Computer System started to fail as indicated by a loss of computer link to Generation. Investigation by computer maintenance personnel was initiated. The failure mode of the computer precluded accessing screens to allow use of Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS). Computer core thermal power indication remained available to the control room operators. Redundant, normal control room indications are still available to the operators. At 1217 hours on 08/20/09, a planned loss of computer core thermal power indication occurred due to ongoing computer maintenance activities. "At 1458 hours on 08/20/09, the Plant Integrated Computer System was fully restored to service, including the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) functions. At 1643 hours on 08/20/09, the Plant Integrated Computer System started to fail again as indicated by loss of computer link to Generation. This problem with the computer again precluded accessing Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS). Core thermal power indication remained available via the plant computer system. However, anticipated troubleshooting actions will require a reduction in power by approximately 0.25-0.33% by reducing core flow. "Due to the cumulative impacts of the loss of the plant computer system, this notification is being communicated ahead of the 8 hour unavailability of the Unit 2 SPDS and ERDS computer system. This is considered a Loss of Emergency Assessment Capability and therefore reportable under 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RICHARD KLINEFELTER TO CHARLES TEAL AT 1222 EDT ON 8/25/2009 * * * As of 1200 hours, Unit 2 ERDS and SPDS (Safety Parameter Display System) were restored to normal operation. The licensee has notified the NRC Resident Inspector. Notified R1DO (White). | 0 | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-20
45279 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-08-20 08:38 | 2009-08-20 15:19 | 2009-08-20 | BOTH DIVISIONS OF VITAL SWITCHGEAR INOPERABLE BECAUSE FLOOD DOOR FOUND CLOSED "At 08:38 on 08/20/09, a plant operator identified that DOOR-18, which is a normally open fire door, had closed due to a failed fusible link. With this door closed, the pathway for a potential flood due to a high energy line break (HELB) is blocked therefore closing off a drain path for the water. This represented an unanalyzed condition where both divisions of essential switchgear could be impacted. As a result, both divisions of essential switchgear were declared inoperable and Technical Specification LCO 3.0.3 was entered. "With both switchgear divisions being inoperable, this condition is also an event that could have prevented fulfillment of a Safely Function and reportable under 50.72(b)(3)(v). At 0942 on 08/20/09, the closed fire door was restored to the open state. Both divisions of switchgear were declared Operable and LCO 3.0.3 was exited. No system actuations occurred as a part of this event." A continuous fire watch was posted as a compensatory measure while the fire door is being repaired. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2009-08-20
45278 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-08-19 15:49 | 2009-08-19 20:38 | 2009-08-25 | AUTOMATIC REACTOR TRIP CAUSED BY TURBINE TRIP "Wolf Creek experienced a reactor trip at 1549 CDT. The first out annunciator was TURBINE TRIP and P9 Reactor TRIP. At approximately the same time the unit experienced a momentary loss of offsite power. "The emergency diesel generators started [and loaded] as expected to supply power to the safety busses due to the loss of offsite power. Auxiliary Feedwater and Feedwater Isolation actuations occurred as expected. All control rods inserted into the core during the trip. All Reactor Coolant Pumps tripped due to the loss of offsite power. Decay heat was initially being removed by the Steam Generator Atmospheric Relief Valves. "Presently the plant is stable in Mode 3. The 'D' Reactor Coolant Pump has been restarted. The licensee is continuing to investigate the cause of the trip." The atmospheric relief valves lifted for approximately 10 minutes, however there was no primary to secondary leakage. Both A & B EDG's loaded for about 2 minutes. At the present time the electrical lineup is normal and the EDG's are shutdown. Plant is at Normal Operating Pressure and just below Normal Operating Temperature. Decay heat and S/G levels are being maintained with the Auxiliary Feedwater pumps. The licensee has notified the NRC Resident Inspector. The Licensee may issue a press release on this event. * * * UPDATE FROM DAVE DEES TO VINCE KLCO AT 1135 EDT ON 8/21/2009 * * * The atmospheric relief valves lifted for approximately 2 minutes, not 10 minutes as stated above. Also the A & B EDG's did not load for only 2 minutes. Actually "the B Safety Bus was paralleled to its normal off site source and the B Emergency Diesel was realigned for auto-start at 1740. The A Safety Bus was paralleled to its normal off site source and the A Emergency Diesel was realigned for auto-start at 1844." Notified the R4DO (Jones). * * * UPDATE FROM DAVE DEES TO VINCE KLCO AT 1730 EDT ON 8/25/2009 * * * "The initial report stated that there was no primary to secondary leakage. Actual primary to secondary leakage as measured on 8/14/2009 was a value of less than 0.722 gallons per day." The licensee notified the NRC Resident Inspector. Notified the R4DO (Miller) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-08-19
45277 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-08-19 15:00 | 2009-08-19 20:33 | 2009-08-19 | TIME TO ESTABLISH CHARGING FLOW EXCEEDED THERMAL HYDRAULIC ANALYSIS "Valve BNHV8812A RWST to RHR Pump A Isolation is manually closed in OFN RP-017, Control Room Evacuation, in response to a control room fire. Simulated timing assumed approximately 1 minute to close the valve. Discussions with the MOV engineer revealed that the valve takes 600 turns to close. Operations Standing Order 1 limits the number of hand wheel turns to 60 per minute. At a closure rate of 60 turns per minute, it will take a minimum of 10 minutes to close the valve, rather than the assumed 1-minute. The additional 9 minutes necessary to close the valve will delay the completion of subsequent steps. Most significantly, the time to establish charging flow increases from 20 minutes to a minimum of 29 minutes. Thermal hydraulic analysis documented in SA-08-006 assumed the charging flow will be established within 28 minutes. Therefore the time to establish charging flow exceeds that assumed in the thermal hydraulic analysis by at least 1 minute. Compensatory actions have been put in place in order to accomplish this task within the time allowed by the thermal hydraulic analysis." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-08-19
45276 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-08-19 | 2009-08-19 15:43 | 2009-08-19 | AGREEMENT STATE REPORT - FLOW GAUGE SHUTTER UNABLE TO CLOSE The following report was received from the state via e-mail: "A Colorado Specific licensee, Suncor Energy (USA) Inc. (License # 615-02), reported that a fixed nuclear gauge was having shutter problems. The shutter was unable to be returned to a closed position during a routine check. The gauge is an Ohmart Vega Model SH-F2 containing 250 mCi of Cs-137 (serial number M-7105). The licensee plans to have a Ohmart Vega Technician on site within the next few weeks to take a look at the gauge and determine whether or not the gauge can be fixed or [if] it needs to be replaced." The gauge is a flow gauge on a pipe in an oil refinery, and the shutter is normally open during facility operation. The radiological control area is normally maintained in force during operations, and remains in force. No inadvertent exposures are expected to have occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-08-25
45275 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-08-06 | 2009-08-19 15:10 | 2009-08-19 | AGREEMENT STATE REPORT - MEDICAL DOSE DIFFERENT THAN PRESCRIBED The following was received from the state via e-mail: "This incident was reported by a medical licensee (Centura Health Penrose - St. Francis Health Services License # 197-02) on 08/06/2009. "On 22 July 2009, at patient at Penrose Hospital was implanted with 70 Palladium-103 seeds, 2.5 U each on that day. The application was via a Mick applicator, using intra-operative planning with a Variseed planning system. It was noted on the C arm film taken at the completion of the implant that there was some clumping of the seeds in groups. A post implant CT scan was done on 23 July 2009. The results of the computerized dosimetry plan was evaluated on the 5 August 2009 and it was determined that the prostate gland was under dosed, receiving a dose to 90% of the prostate volume (D90) of 36.6% of the prescribed 125 Gy. The AU [Authorized User] written directive listed an expected range of D90 to be 90% to 135%. The discrepancy between actual dose and prescribed falls outside of the 20% tolerance for delivered dose according to [Colorado State Regulation] RH 7.21.1.1 (1). A full report is expected from the licensee within 30 days." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-08-25
45274 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-08-19 11:50 | 2009-08-19 16:19 | 2009-08-19 | OFFSITE NOTIFICATION FOR INADVERTANT ACTUATION OF SIRENS FOR 10 SECONDS During an exercise, sirens for the city of San Clemente (19 of 52 total sirens) were inadvertently actuated for approximately ten seconds. The licensee made off-site notifications to California FEMA, California Dept of Health, California State Parks, Camp Pendleton, and the cities of San Clemente, San Juan Capistrano, and Dana Point. The licensee has notified the NRC Resident Inspector. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-08-19
45273 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-08-18 09:20 | 2009-08-18 15:08 | 2009-08-18 | HPCI TURBINE STOP VALVE FAILS IN MIDPOSITION "At 0920 on 08/18/2009, the Unit 1 HPCI turbine stop valve (FV15612) showed dual indication following performance of the weekly functional test of the HPCI lube oil system. Subsequent investigation revealed that the valve stem was not in the full closed position. LCO 3.5.1 for the HPCI system was entered at 0920 on 08/18/2009. An investigation is in progress to determine the nature of the problem. "This incident is being reported as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident in accordance with 10CFR50.72(b)(3)(v)(D)." The HPCI pump was declared inoperable. This is a 14 day LCO. The licensee notified the NRC Resident Inspector. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-08-18
45272 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-08-06 | 2009-08-18 12:33 | 2009-08-18 | AGREEMENT STATE REPORT - NINE MISSING PO-210 AND PM-147 SEALED SOURCES "On 19 June 2009, TTM Technologies in Redmond was contacted as part of a routine check of their inventory of generally licensed devices. It was discovered at this time that the facility was closing and that the gauges and static eliminators had been sent to TTM Technologies facilities in other states. TTM Technologies has since tracked down as many of the missing devices as possible. Those facilities that have received sources have been informed of the reporting requirements and regulations surrounding those generally licensed devices. NRD, Inc. was contacted to see if any of the remaining unaccounted for sources had been returned to them. They have not been. The remaining missing sources are being reported as lost. "This report lists eight devices/sources. A ninth device/source (exactly the same as number 8 except for the serial number) is being included here instead. This device/source is serial number A2CK423. Seven of the nine devices/sources are Po-210 static eliminators and have gone through more than ten half-lives. The other two devices are sources of Pm-147 in beta backscatter gauges and have gone through approximately 8 half-lives. It is therefore concluded that the missing sources are of little threat to human health and safety. "Source of Radiation: Source Number: 1 Form of Radioactive Material: SEALED SOURCE Radionuclide: PM-147 Source Use: OTHER Activity:0.9E-3 Ci 0.0333 GBq Manufacturer: OXFORD INSTRUMENT Model Number: GM-1 Serial Number: 75125P "Source Number: 2 Form of Radioactive Material: SEALED SOURCE Radionuclide: PM-147 Source Use: OTHER Activity:0.6E-3 Ci 0.0222 GBq Manufacturer: OXFORD INSTRUMENT Model Number: GM-1 Serial Number: 65986P "Source Number: 3 Form of Radioactive Material: SEALED SOURCE Radionuclide: PO-210 Source Use: STATIC ELIMINATOR Activity:0.05513 Ci 2.03981 GBq Manufacturer: NRD, INC Model Number: P-2001 Serial Number: A2EA910 "Source Number: 4 Form of Radioactive Material: SEALED SOURCE Radionuclide: PO-210 Source Use: STATIC ELIMINATOR Activity:0.05513 Ci 2.03981 GBq Manufacturer: NRD, INC Model Number: P-2001 Serial Number: A2BM653 "Source Number: 5 Form of Radioactive Material: SEALED SOURCE Radionuclide: PO-210 Source Use: STATIC ELIMINATOR Activity:0.05513 Ci 2.03981 GBq Manufacturer: NRD, INC Model Number: P-2021 Serial Number: A2DY847 "Source Number: 6 Form of Radioactive Material: SEALED SOURCE Radionuclide: PO-210 Source Use: STATIC ELIMINATOR Activity:0.010 Ci 0.37 GBq Manufacturer: NRD, INC Model Number: P-2021 Serial Number: A2CE789 "Source Number: 7 Form of Radioactive Material: SEALED SOURCE Radionuclide: PO-210 Source Use: STATIC ELIMINATOR Activity:0.010 Ci 0.37 GBq Manufacturer: NRD, INC Model Number: P-2021 Serial Number: A2BM653 "Source Number: 8 Form of Radioactive Material: SEALED SOURCE Radionuclide: PO-210 Source Use: STATIC ELIMINATOR Activity:0.010 Ci 0.37 GBq Manufacturer: NRD, INC Model Number: P-2021 Serial Number: A2CK423 "Corrective Actions: 1 Personnel received additional training." Washington state reporting requirement WAC 246-221-240 Washington Report No: WA090061 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-08-21
45271 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2009-08-14 08:00 | 2009-08-18 10:10 | 2009-08-18 | AGREEMENT STATE REPORT - TROXLER GAUGE RUN OVER BY CONSTRUCTION EQUIPMENT The following information was received from the State via facsimile: "The Virginia Radioactive Materials Program received a telephone message on Monday, August 17, 2009 (message was left at 6:30 PM on Friday, August 14, 2009) concerning the licensee's Troxler gauge. The gauge had been run over by a roller while in operation. The Radioactive Materials Program returned the call to the licensee's RSO at 7:45 AM on Monday, August 17. The accident occurred at 8AM on Friday, August 14. The guide rod and source rod were broken off the gauge, but the instrument's case was otherwise intact. The operator of the gauge placed it into the shipping container, placed the shipping container in the locked box on the back of the pickup truck, and transported the gauge back to the shop. The licensee's RSO surveyed the gauge and took wipe samples. Two radiation safety specialists from the Radioactive Materials Program visited the licensee, arriving at 12:00 noon on Monday, August 17. The radiation safety specialists visually inspected the gauge, took survey measurements with a maximum level of 100 mR/hr at the surface and 4 mR/hr at one meter from the shipping container, and also took wipe samples. When the gauge was run over, it was operating in "backscatter" mode, so the Cs-137 source was within the case of the gauge. The accident did damage the shutter mechanism for the Cs-137 source so that it could not be closed. The gauge in its shipping container was placed in a locked storage cabinet in the shop pending disposal. The local Troxler vendor had been contacted by the licensee's RSO. The licensee was advised to give the vendor the current radiation survey of the package and to obtain the results of the wipe tests prior to allowing the vendor to transport the gauge. The radiation safety specialists also visited the site of the accident, where they surveyed the ground at the site of the accident, the roller that ran over the gauge, and the pickup truck that transported the gauge. All surveyed areas at the accident location were at background." VA Event Report ID No.: VA-2009-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2009-08-21
45270 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-08-17 12:10 | 2009-08-18 02:00 | 2009-08-18 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM AND SAFETY PARAMETER DISPLAY SYSTEM DUE TO COMPUTER PROBLEMS "At 1210 hours on 08/17/09, reactor operators noticed [the] Plant Integrated Computer System was beginning to fail. This computer system also performs the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) functions. Investigation by computer maintenance personnel was initiated. It was determined that [the] Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were not reliable. Redundant, normal control room indications are still available to the operators. "At 1955 hours on 08/17/09, the Plant Integrated Computer System was restored to service, including the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) functions. "A few hours later at 0004 hours on 08/18/09, the Plant Integrated Computer System failed, including loss of Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS). Reactor power was lowered by 0.3% from the initial authorized limit of 94.4% to 94.1% due to the loss of the core thermal power heat balance provided by the computer system. "Since the Unit 2 SPDS and ERDS computer systems were not available for greater than an 8 hour time period, this is considered a Loss of Emergency Assessment Capability and therefore reportable under 10CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1321 ON 8/17/2009 FROM JIM HUFFORD TO KARL DIEDERICH * * * "As of 1336 hours on 08/18/09, Unit 2 ERDS and SPDS were restored to normal operation. Unit 2 reactor power was returned to full power of 94.4% shortly thereafter." The licensee has notified the NRC Resident Inspector. Notified R1DO (Conte). | 0 | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-18
45269 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-08-17 09:31 | 2009-08-17 18:51 | 2009-08-17 | FITNESS FOR DUTY - SUPERVISOR TESTED POSITIVE FOR ALCOHOL A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2009-08-17
45268 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-17 | 2009-08-17 17:40 | 2009-08-17 | AGREEMENT STATE REPORT - FOUR PO-210 STATIC ELIMINATORS LOST The following information was obtained from the State of Texas via email: "In the afternoon of August 17, 2009, the licensee had concluded that four static eliminators, NRD Model P-2021-Y000 containing 500 microCi each could not be located and were presumed lost, probably discarded in the general refuse. The sources were removed from the machines they were mounted on while the area was undergoing some renovation or relocation of equipment. However, when the equipment in which the devices were housed were attempted to be placed back in service, the devices were noted as missing. Repeated attempts to locate the sources and devices have proved futile." Texas Report I-8659 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-08-20
45267 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-17 04:00 | 2009-08-17 15:55 | 2009-08-17 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECTED FROM ITS CABLE The following information was obtained from the State of Texas via email: "On the morning of August 17, 2009, a 79.1 Curie Ir-192 source in a Sentinel Model 880 exposure device (S/N D5517) could not be retracted into the fully shielded position. After several attempts to back the source out, it was surmised that the source remained at the end of the source tube and the Radiation Safety Officer (RSO) was notified. A 2 mR/hr line was established by the radiographers and the licensee's report indicated that visual surveillance was maintained at all times. The RSO then utilized additional shielding and remote handling tools to retrieve the source and place it into another camera. It was determined after the recovery that the ball shank broke from the drive cable leaving the source pigtail in the source tube. The RSO reported that all personnel were monitored with direct reading devices and no exposures exceeded regulatory limits." Source: QSA Global model 424-9, Serial #56552B Texas Incident Report I-8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-08-20
45266 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-08-10 | 2009-08-17 13:49 | 2009-08-17 | AGREEMENT STATE REPORT - IMPROPERLY PACKAGED RADIOACTIVE SHIPMENT The following was received from the State via FAX: "The Radiation Safety Officer (RSO) for the University of Massachusetts - Lowell (UMASS - Lowell) reported an improper shipment of radioactive material where the package was prepared for shipment as a regular package and should have been prepared for shipment as a Class 7 (radioactive) package. "On Friday, August 14, 2009, the RSO discovered, from information received by General Dynamics C4 Systems (GD), that GD received, on Tuesday, August 12, 2009 a regular package sent by UMASS-Lowell on Monday, August 10, 2009 that should have been prepared as Class 7. The package was reported by GD to UMASS-Lowell to have radiation levels of 2.6 mrad/hr at 2 cm above the package or contents of package as measured with a Ludlum G-M instrument. "The RSO reports that the package contained electronic components subjected to irradiation from UMASS - Lowell's research reactor and that the radioactive materials contained in the package was likely Bromine-82. The RSO reports that he does not believe that there was any contamination discovered on the outside of the package. "The RSO reports that based on calculations performed, the estimated activity of the package, for Bromine-82, was one (1) MBq and that the specific activity of bromine-82 of the samples (electronics) was likely between 42 and 170 Becquerel's/gram. The address reported for GD, the recipient of the package, is Scottsdale, AZ 85252 and any radioactive materials license number for GD was not known at time of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-08-20
45265 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2009-08-15 16:06 | 2009-08-15 20:06 | 2009-08-15 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "At 1606 CDT on August 15, 2009, LaSalle Unit 2 automatically scrammed due to a turbine trip. The turbine trip occurred during weekly turbine trip testing. Two safety relief valves actuated [and reseated] in the relief mode on the turbine trip. The reactor water cleanup system isolated during the transient (not being reported as there was no isolation in multiple systems). The plant is stable with reactor pressure control to the main condenser via the main steam isolation valves. The plant is planning to remain in hot shutdown pending [turbine] electro-hydraulic (EHC) system troubleshooting and repair." All control rods fully inserted during the scram. The site is aligning the ring bus for the normal shutdown electrical lineup. Reactor water level is being maintained using the main feedwater system and decay heat is being removed via the turbine bypass valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-08-15
45264 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-08-14 19:58 | 2009-08-15 00:51 | 2009-08-15 | HPCI INOPERABLE DUE TO AUTOMATIC CLOSURE OF INBOARD ISOLATION VALVE "On 8/14/2009 at 19:58, the Unit 1 High Pressure Coolant Injection (HPCI) System inboard isolation valves automatically isolated. Inboard isolation was caused by an inadvertent high ambient temperature signal from the HPCI steam leak detection module. Local temperatures were confirmed to be normal and no steam leak was identified. With the HPCI system steam supply isolated, the HPCI system is inoperable in accordance with Technical Specification 3.5.1. HPCI is a single-train safety function system. "The initial safety significance of this condition is considered to be minimal. The Reactor Core Isolation Cooling (RCIC) system, Automatic Depressurization System (ADS), and Low Pressure Emergency Core Cooling systems (ECCS) remain operable at this time. Actions have been taken to protect redundant safety systems. Unit 1 risk condition is currently yellow due to the concurrent inoperability of a single loop of Residual Heat Removal (RHR) Service Water for system maintenance. "The HPCI system remains isolated and inoperable pending further troubleshooting of the inboard isolation. "The NRC resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-08-15
45263 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-14 | 2009-08-14 16:41 | 2009-08-14 | AGREEMENT STATE REPORT - SR-90 SOURCE FOUND IN MAIL The following report was received via e-mail: "Customs called to report a detection at the international post office at DFW [Dallas/Ft Worth] airport. The source was contained in a package with some other materials including a couple of electronic devices, a small plastic container about the size of a contact lens holder, some dice and other articles. The package was being mailed to a private citizen living in Ft. Worth, TX. Customs provided pictures of the package and contents. The radioactive material was identified as Sr-90. Inspector surveys measured 0.3 mrem closed window, 60 mrem open window." The State of Texas notified EPA, FBI, and ICE. Texas Report #I-8656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-08-19
45262 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-08-13 15:41 | 2009-08-13 19:35 | 2009-08-13 | OFFSITE NOTIFICATION DUE TO A GRASS FIRE IN THE OWNER CONTROLLED AREA "A fire was reported to the unit-2 control room at 1541 Central time [CDT]. The fire was reported in the Owner Controlled Area. Local [Bay City] fire department was dispatched to fight the fire. The fire occupied approximately 2 acres. The fire was reported to be under control at 1635 [CDT]. No plant equipment was damaged nor was the operations of the unit affected. Region 12 of the Texas Commission of Environmental Quality was notified at 1721 [CDT] and no further actions were required by the Agency [Texas Department of Environmental Quality]." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-08-13
45261 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-12 18:00 | 2009-08-13 18:08 | 2009-08-28 | AGREEMENT STATE REPORT - POSSIBLE OVEREXPOSURE DURING TRANSPORTATION "On August 13, 2009, at 1630 the Agency [Texas Department of Health] received a call from the licensee's Radiation Safety Officer (RSO) stating that they had shipped a 2.5 curie Cesium 137 source via common carrier to Tyler, Texas from Van Buren, Arkansas. Some time after receiving the source in Tyler, Texas, the licensee discovered that the source had been shipped in a container designed to carry Americium. The licensee recreated the event and determined that the dose rate in the cab of the transport truck was 25 millirem per hour. The trip was estimated to take six hours to complete, so the dose to the driver was calculated to be 150 millirem for the trip. The licensee is attempting to identify the driver and will determine additional dose rates required for shipping during their investigation. A survey was conducted by the licensee prior to the package leaving Arkansas and the individual who performed the survey stated that he did not see any unusual dose rates from the package. The RSO stated that they will provide a copy of the survey and additional information as it is gathered. This Agency [Texas Department of Health] will perform an onsite investigation on August 14, 2009, and will provide additional information to the NRC when prudent." Texas Incident #I-8655 * * * UPDATE PROVIDED BY ART TUCKER TO JASON KOZAL ON 08/28/09 AT 1740 * * * The following was provided by the State via e-mail: "The following information was gathered during interviews conducted at Baker Hughes Oilfield Operations DBA Baker Atlas in Tyler, Texas, on August 21, 2009." "The Corporate Radiation Safety Officer (CRSO) was asked to describe the events that had occurred on July 12, 2008. He provided pictures which confirmed that the driver had left the facility in Van Buren, Arkansas, at 1545 on July 12, 2009. A picture of the truck arriving in Tyler, Texas, at 21:35 on July 12, 2009, was also provided. The CRSO stated that the driver was not in or around the truck other than for driving. He was not in the area of the source during the time it was loaded on the truck. No video or pictures were available of a survey being performed on the truck. A dose rate survey was provided, but no contamination survey information could be provided. The dose rate survey indicated a reading of 15 microsieverts/hour (uSv/hr) at the back of the truck and 5 uSv/hr and 2 uSv/hr on the sides of the truck. The dose rate inside the cab of the truck is difficult to read, but was stated to be 2 uSv/hr. The CRSO stated that the dose rates were actually in units of millirem/hour (mr/hr) and not uSv/hr as stated on the survey. The CRSO provided a survey done during the investigation that showed the dose rate at the back of the truck to be 15 mr/hr, but the dose rates on the sides of the truck, 3 feet from the container were 170 mr/hr and 140 mr/hr. The 170 mr/hr was recorded on the side of the truck were the Cesium (Cs) 137 source was located. The dose rate inside the cab was recorded as between 24 and 28 mr/hr. The CRSO stated that the vehicle used to take dose readings in the cab actually had a shorter distance from the source to the driver than the actual truck used. The CRSO used 25 mr/hr as the dose rate to assign a dose to the driver. This gave him a dose of 150 millirem for the drive. "The CRSO was asked if the individual who shipped the packages had ever performed a radioactive shipment before. He said probably not. The CRSO was asked if the Site RSO (SRSO) had reviewed the shipment before it left Arkansas. He stated the individual who had shipped the package was the SRSO. He stated that the old SRSO had left the facility a few weeks prior to this event. The CRSO stated that to his knowledge, the SRSO had not received any training on performing shipments involving radioactive material. I asked if the CRSO had talked with the new SRSO prior to this shipment. The CRSO stated that he was not aware that this individual was the SRSO until this event occurred. He stated that the source that was shipped did not fit into the first container that the SRSO tried to use. He looked around till he found a cask it would fit into and assumed it was the correct one." "The CRSO was asked why the lack of labels on the shipping container did not raise a flag for the SRSO. He stated that they where in a hurry to get the package out. I asked why the truck did not have placards. He stated that the SRSO knew that it should have been placarded, but he said that the transport company stated that they would place the placards on the truck. I asked why the shipment did not have a contamination survey. The CRSO could not provide an answer. "The source was removed from the container and placed in the storage location shortly after it arrived in Tyler, Texas. No surveys were performed on arrival in Tyler, Texas. "The CRSO stated that the error was discovered on August 12, 2009, when the source was being packaged to send to a field site. The person preparing the source for shipment could not find a holder they would normally use, so they decided to use the container that was used when it was shipped from Arkansas. The transport container now had the appropriate labels. The source was placed in the transport container in an area monitored by an area radiation monitor. The area radiation monitor continued to alarm even after the source was fully inserted into the transportation container. This was the first indication the licensee had that there was a problem with the transport container. "The CRSO was asked if anyone else was on the loading dock while the source was being prepared for shipment. He stated that there was not. "The CRSO stated that he believed the transport container used borated paraffin or poly as it was designed for a five curie Americium/Beryllium source. He stated that he would send us the transport container certification. "The CRSO stated that conversations with the driver indicated that the driver was not concerned with his radiation exposure. The driver was offered medical assistance, but refused it." Notified R4DO (Miller), and FSME EO (Suber). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-08-18
45260 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-08-13 13:04 | 2009-08-13 17:25 | 2009-08-13 | POTENTIAL MEDIA INTEREST DUE TO PLANNED MAINTENANCE OUTAGE "On August 13, 2009, at 1304 PDT, Unit 2 was shut down in accordance with established plant procedures to perform more in-depth analysis of the main electrical transformer 'A' phase 500 kV bushing. Diablo Canyon Unit 2 was taken off line in a planned maintenance outage to investigate a power-factor condition currently identified by the 500 kV bushing monitoring instrumentation. The main electrical transformer 'A' phase 500 kV bushing will be replaced if warranted by the results of testing. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-08-13
45259 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-08-11 16:30 | 2009-08-12 18:01 | 2009-08-12 | AGREEMENT STATE REPORT - STOLEN TROXLER SUBSEQUENTLY RECOVERED The following was provided by the State via e-mail: "[An] 8 mCi Cs-137 source [was] stolen from PaveTex at 16:30 CST 8/11/2009 at the O'Reilly Auto Parts on US 87 in Big Spring, TX. [The] Source was in a Troxler model 4640 thin layer density gauge, serial no. 1280. [The State was] notified [at] 15:30 CST on 8/12 that the source was located by a member of the public at the TA Truck stop on I-20 at US-87 north of town and that [the] site RSO had sent someone to pick up [the] gauge." Texas Incident # - I-8654 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-08-17
45258 | 0 | STATE OF CALIFORNIA |  |  |  |  | 2009-08-05 | 2009-08-11 16:09 | 2009-08-11 | AGREEMENT STATE - LOSS OF CONTROL OF NUCLEAR MATERIAL The following was received from the state via email: "On 08/05/09 during the evening a T.C. Inspection radiographer was performing radiography at the Chevron refinery in Richmond, CA. The job was completed around 8:30 p.m. The radiographer loaded the gear into the truck leaving the locked camera (INC, Model IR100, S/N 7019, 49 Ci activity) at the job site. Approximately 10 to 15 minutes later, Chevron maintenance noticed the exposure device and notified the Chevron fire department. The A T.C. Inspection radiographer who was at the refinery heard the call on the radio and responded to the event location, however, he did not have a survey meter to approach the camera. He noticed that the plug was in and the device appeared to be locked with no key in the lock. They barricaded the area, and kept the camera under surveillance until a survey meter was brought in. The radiographer surveyed the camera and confirmed that the source was in a shielded position and transported the camera to the storage location. The radiographer who left the camera at the job site is no longer employed by T.C. Inspections." CA Report #: 80609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | MAT | [5 empty] | 0 | 2009-08-11
45257 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-08-11 | 2009-08-11 14:50 | 2009-08-13 | AGREEMENT STATE - LOST STATIC ELIMINATORS The State of North Carolina discovered 2 missing static eliminators containing 500 microCi of Po-210 and 80 microCi of Am-241. The licensee was billed for the annual fees related to these gages and notified the State that they no longer had the gages in their possession. The State sent an inspector to investigate the situation. The inspector discovered that the manufacturing facility had been relocated to Vietnam 3 years ago. When this occurred the licensee believes it is possible that the sources were relocated with the majority of the manufacturing facility assets to the Vietnam location at that time. The State is continuing to follow-up with the licensee to determine disposition of these sources. * * * UPDATE ON 8/13/09 AT 1022 EDT FROM BARNES TO HUFFMAN * * * A representative of the State of North Carolina provided the following additional information about the lost sources: The Am-241 source was manufactured by Pyrotronics. Model number F315A. Serial Number 1000635. Date received - 1971 The Po-210 source was manufactured by Nuclear Products. Model number 2U500. Serial Number Unknown. Date received - 1989 R1DO (Cook) and FSME (McIntosh) have been notified of this update. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-08-13
45256 | 0 | ATC ASSOCIATES |  |  |  |  | 2009-08-10 08:00 | 2009-08-11 13:55 | 2009-08-11 | STOLEN MOISTURE DENSITY GAUGE An employee drove home [Crawfordville, IN] with the density gauge in the back of his car on Friday August 7, 2009. Sunday morning he locked the density gauge into the trunk of another car parked in the front of his home. He then left to attend a family event. The employee noticed the gauge was missing on Monday morning. The licensee notified Montgomery County Police and Indiana Department of Health. Seaman Nuclear Moisture Density Gauge Model: C75A SC757582 Source: Radium-226 Activity: .00616 TBq THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-08-11
45255 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-08-10 20:32 | 2009-08-10 23:55 | 2009-08-11 | INDIAN POINT UNIT 3 AUTOMATICALLY TRIPPED DURING THUNDERSTORM "Indian Point Unit 3 automatically tripped from 100% power at 2032 [EDT] on 8/10/2009 due to [a] generator trip. Indian Point Unit 3 is currently in mode 3. All control rods inserted on the trip. No safety relief valves lifted due to the trip. The motor driven aux feedwater pumps automatically started on low steam generator level and are being used to maintain steam generator level. Condenser steam dumps are maintaining reactor temperature. "After the trip , [the] 6.9kv bus 2 did not transfer to offsite power and is de-energized resulting in a loss of [the] '34' RCP [Reactor Coolant Pump]. [The] 480v bus 2A was energized by the diesel generator. "Plant operators are investigating the cause of the generator trip and loss of bus 2. "Unit 2 was unaffected and remains in mode 1 at 100% power. "The licensee has notified the NRC Resident Inspector." The licensee informed the State of New York and plans on issuing a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-08-11
45254 | 0 | STATE OF CALIFORNIA |  |  |  |  | 2009-07-10 | 2009-08-10 18:37 | 2009-08-10 | AGREEMENT STATE - LEAKING RADIOACTIVE SOURCE The following was received from the state via email: "The source housing from a 6.58 mCi Ni-63 electron capture device (ECD), (Varian Model 02-001972-00, S/N A2296) was inadvertently opened when the detector was removed from a gas chromatograph for storage. The situation was discovered by radiation safety staff, and followed up immediately. Removable contamination was detected on the open interior of the source assembly and on top of the gas chromatograph, but was less than the removable value of 0.005 microcuries. The detector foil was not damaged or accessed. All components of the source assembly were retrieved and will be disposed of as radioactive materials waste or returned to the vendor. " CA Report #: 080509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | MAT | [5 empty] | 0 | 2009-08-10
45253 | 0 | NC RADIATION PROTECTION SERVICES |  |  |  |  | 2009-08-07 | 2009-08-10 13:55 | 2009-08-10 | AGREEMENT STATE REPORT - LEAKING RADIOACTIVE SOURCE The following was received from the state via email: "On August 7, 2009, the Agency [State] was notified by the licensee RSO (Radiation Safety Officer) of a possible leaking source discovered during a routine leak test. The source is a 25 mCi Sr-90 source (as of 07/93). The RSO said he is used to seeing approximately 75 dpm on the wipe, but this time the wipe was 323 dpm. Since this level is below the report limit of .005 uCi (11,000 dpm), no report was made. An [State] Agency inspector was in the area and said he would stop in to investigate. "The inspector arrived and discovered that the source is leaking. A contact reading using a Ludlum 14C with side window GM (Geiger Muller) was off scale high. The four swipes of the source were checked with the Ludlum 14C with pancake GM probe. The swipes/Q-tips read 0.3, 0.5, 0.7, and 1.1 mr/hr on contact. The Q-tips are contained in individual plastic zip-top bags. A swipe of the source holder did not yield any removable contamination. The background in the area is <0.1 mr/hr. The sources are in the source manipulation/storage room and all sources are in storage. "The licensee is planning to terminate their license in the next few weeks and has been in contact with DOE (Department of Energy) to take possession of their sources under the orphaned source retrieval program. "The notification is being made per NC Regulations 15 A NCAC 11 .0357(b)(1)(B) an unplanned contamination event involving RAM exceeding 5 times 10 CFR 20.1001 - .2401 Appendix C values (the Appendix C value for Sr-90 is 0.1 microcuries) as well as .0357(b)(2)(A) equipment fails to function as designed when it is required to prevent releases exceeding regulatory limits. "This is a 24 hr notification event. "The investigation is ongoing and updates will be provided as information is obtained." NC-Report #: 09-35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | MAT | [5 empty] | 0 | 2009-08-10
45252 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-08-08 18:31 | 2009-08-09 12:26 | 2009-08-09 | FITNESS FOR DUTY REPORT - SUPERVISORY EMPLOYEE TESTED POSITIVE FOR ALCOHOL A non-licensed supervisory employee had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's unescorted access has been inactivated. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 1 | 2009-08-09
45251 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-08-09 04:00 | 2009-08-09 06:25 | 2009-08-09 | STATE OF NEBRASKA NOTIFIED DUE TO MINOR SEWAGE SPILL TO THE MISSOURI RIVER "[The licensee] notified the Nebraska Department of Environmental Quality that a site sewage lift station had overflowed due to blown fuses and released an estimated 20 gallons of raw sewage the Missouri River." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-08-09
45250 | 0 | VALLEY HOSPITAL |  |  |  |  | 2009-08-06 17:00 | 2009-08-07 17:32 | 2009-08-11 | POTENTIAL DOSE TO WRONG SITE A patient with radiation seed prostate implants came back to the facility to have a CAT Scan. Based on the CAT Scan results, the physician suspects the improper positioning of the radiation seed implants. Due to the patient's medical condition the hospital cannot conduct a verification CAT Scan with contrast material. The patient plans to return to the hospital at a later date. A hospital review of the patient's treatment is ongoing. * * * UPDATE FROM TKI CHAK TO JOHN KNOKE AT 1530 ON 08/11/09 * * * The licensee confirmed that the patient had improper positioning of the radiation seed implants. This was considered an under dose to the patient since the seeds went into the tissue and not the prostate. The patient was advised by the physician and will receive a follow-on treatment with a tomotheraphy procedure. Notified FSME (Andrew Mauer) and R1DO (William Cook). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2009-08-13
45249 | 0 | YALE - NEW HAVEN HOSPITAL |  |  |  |  | 2009-08-05 | 2009-08-06 12:11 | 2009-08-06 | DOSAGE TO PATIENT WAS POTENTIALLY DIFFERENT FROM PRESCRIBED DOSE DUE TO EQUIPMENT MALFUNCTION "Two patients were scheduled for treatment using a Leksell GammaKnife Model C/B-2 stereotactic radiosurgery unit on August 5, 2009. This model uses an Automatic Positioning System (APS) to automatically change patient position during the treatment. The APS reported positioning error codes to the treatment console and the operators called Elekta, the manufacturer's US representative for help. They were told to undock the patient and reinitialize the APS system and then to complete treatment. This happened again during the second patient treatment and the local Elekta service person was called to inspect the unit. "The service representative arrived after the completion of treatment to the second patient and it was noted then that while trying to drive the APS system back to it's nominal position, one of the axis indicators was off by 5 mm. It is not known if this happened during the treatment, so this is a provisional report until a thorough analysis can be performed. The console logs have to be analyzed by the manufacturer's representatives to see if the error occurred during treatment and as a result of an APS malfunction." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-08-12
45248 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2009-08-06 10:00 | 2009-08-06 10:25 | 2009-08-14 | EMERGENCY OPERATIONS FACILITY PLANNED MAINTENANCE "At approximately 1000, on Thursday, August 6, 2009, the heating, ventilation, air conditioning (HVAC), and filtration system of the Millstone Power Station (MPS) Emergency Operations Facility (EOF) will be removed from service to perform maintenance to improve the reliability and functionality of the system. "The EOF is located inside the site's boundary approximately one mile from the protected area of the plant. As a result of this maintenance, the EOF will be unavailable for approximately 12 days. If an emergency requiring the use of the EOF is declared during this maintenance period, the designated alternate EOF, which is also located on site, will be utilized. The Station Emergency Response Organization (SERO) has been informed of this condition. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). Millstone will notify the NRC upon completion of the planned maintenance activities and restoration of the EOF which is currently anticipated to occur on August 18, 2009. "The licensee has notified the NRC Sr. Resident Inspector." * * * UPDATE ON 8/14/2009 AT 1524 FROM MIKE MARTELL TO MARK ABRAMOVITZ * * * The EOF was declared operable at 1324 EDT. Notified the R1DO (Cook). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-06
45247 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-08-06 06:00 | 2009-08-05 15:34 | 2009-08-06 | PLANNED MAINTENANCE TO AFFECT TECHNICAL SUPPORT CENTER "On 8/6/09 at 0600 hours CDT the Monticello Nuclear Generating Plant's Technical Support Center uninterruptable power supply will be isolated to perform a planned maintenance activity. The maintenance activity requires implementation of compensatory measures to maintain TSC functions during the activity. The compensatory measures include having the Emergency Director report to the Control Room and co-locating the remaining TSC staff at the EOF should an event be declared requiring ERO activation. The ERO has previously successfully demonstrated the ability to implement these compensatory measures. The maintenance activity is scheduled to be completed with the TSC returned to full functionality by the end of the dayshift on 8/6/09. The Site Emergency Response Organization has been notified of the maintenance activity and instructed on the planned compensatory measures to be implemented during the activity. MNGP will notify the NRC upon completion of the activity restoring full TSC operability. This event is considered reportable per 10CFR50.72(b)(3)(iii). The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM D. BARNETT TO P. SNYDER AT 1943 ON 8/6/09 * * * "On 8/6/09 at 1700 CDT the Monticello Nuclear Generating Plant's Technical Support Center was returned to service and declared functional. The Monticello Emergency Response Organization has been notified and the compensatory measures that were in effect have been terminated. The licensee has notified the NRC Resident Inspector." Notified R3DO (Skokowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-05
45246 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2009-08-05 | 2009-08-05 14:08 | 2009-08-05 | AGREEMENT STATE REPORT - MEDICAL DOSE DIFFERENT THAN PRESCRIBED During an embolization procedure delivering Yttrium-90 spheres to the liver an interruption occurred resulting in only 35 Gy of the 52 Gy prescribed dose being delivered. The interruption was due to unexpected contamination due to a leaking septum v-vial Contamination was contained in a container and did not enter the patient. The patient and referring physician will be notified. GA report number: 2009-09i. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2009-08-11
45245 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-08-05 07:50 | 2009-08-05 12:00 | 2009-08-05 | UNUSUAL EVENT DECLARED DUE TO TOXIC GAS FROM A SWITCHGEAR FIRE IN THE TURBINE BUILDING At 0750 PDT the licensee experienced a turbine trip and reactor scram. At approximately the same time, a fire was detected in the non-safety related 6.9 kV feed bus to switchgear SH-5 and SH-6 in the turbine building. The fire and associated fault to the switchgear feed bus caused a loss of power to both reactor recirculation pumps and the automatic reactor scram. The fire produced smoke and potentially toxic gases. Due to the presence of potentially toxic gas in the power plant, an Unusual Event was declared at 0812 PDT based on EAL 9.3.U.3. At the present time, the fire is out and the smoke is being cleared from the plant. All rods fully inserted upon the reactor scram. Systems functioned as expected except for problems with the EHC system which resulted in the bypass valves remaining open which caused the reactor to depressurize to approximately 390 psi. MSIVs were manually shut to halt the reactor depressurization and cooldown. Decay heat is being removed via relief valves to the suppression pool with reactor pressure being maintained between 500 and 600 psi. Suppression pool cooling is via RHR. Makeup water to the reactor is via normal feed. Licensee is on natural circulation at the time of this report. Normal shutdown electrical alignment is established with the exception of Division II emergency switchgear which is aligned to the backup transformer. A request for assistance was made to the Hanford fire department, however, the fire was out prior to their arrival on site. The licensee has notified State, local agencies and the NRC Resident Inspector. * * * UPDATE FROM JOHN SLACK TO DONALD NORWOOD AT 1332 ON 08/05/09 * * * The Unusual Event has been terminated as of 1006 PDT. The licensee is taking the unit to cold shutdown. The licensee will notify the NRC Resident Inspector. Notified NRR EO (Ross-Lee), R4DO (Walker), DHS (Enzer), and FEMA (Eaches). * * * UPDATE FROM NICK RULLMAN TO PETE SNYDER AT 1827 ON 08/05/09 * * * "Following the reactor scram, with the turbine bypass valves failed fully open, the inboard main steam isolation valves had to be manually closed to prevent excessive cool down. The outboard main steam isolation valves automatically closed from the inability to maintain condenser vacuum. The inability to maintain condenser vacuum was due to limited equipment access in the Turbine Building from heavy smoke. This is reportable under Part 50.72(b)(3)(iv)(A) as a valid actuation of one of the systems listed in Part 50.72(b)(3)(iv)(B)(2)." The licensee notified the NRC Resident Inspector. Notified R4DO (Walker). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 4 | WA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2009-08-05
45244 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-08-04 10:53 | 2009-08-04 12:46 | 2009-08-04 | LOSS OF EMERGENCY SIRENS "On August 4, 2009, at approximately 0953 hours (CDT), a severe thunderstorm was experienced causing a loss of 12 of 44 emergency sirens (approximately 27 percent) for Clinton Power Station. At 1053 hours (CDT), since the sirens were not restored to operation within one hour, this event was determined to be a major loss of emergency assessment capability. A total of 15 sirens were out of service at 1054. At 1109 power was restored to 13 of the 15 sirens leaving 2 sirens without power. Currently, 42 of 44 sirens are operational and no estimated return to service has been provided for the remaining sirens. "DeWitt County, Illinois Emergency Management Agency, and the NRC Resident have been informed of this information." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-08-04
45243 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-08-03 17:00 | 2009-08-04 11:48 | 2009-08-04 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "On August 3 the [Illinois Emergency Management] Agency's Radiation Duty Officer was contacted after normal business hours and advised that a portable moisture density gauge had been reported stolen from a vehicle at approximately 5 PM that same day. The caller was an officer with the Chicago Police Department who was investigating the event. The vehicle had been parked on the south side of Chicago, IL in front of the field technician's house at the time of the theft. The company's [H.H. Holmes] radiation safety officer contacted the [Illinois Emergency Management] Agency the next morning to report additional details of the theft. Evidence at the crime scene showed that the door to the SUV had been jimmied open with a crowbar and the chain which was looped through the handles of the transport case in the back of the vehicle had been pried from the case such that the lid could be opened and the gauge removed. Additional tools, a cell phone, the radio and personal equipment was also stolen from the vehicle. The company was in the process of acquiring additional information and compiling crime scene photos to include with the formal report. "Pending receipt of that report and follow up action from the Chicago Police Department, the [Illinois Emergency Management] Agency is continuing its investigation and considers the matter open." The stolen gauge was manufactured by Troxler (model number 3440, serial number 34692). The gauge contained a sealed source with 0.008 Ci of CS-137 (serial number 102112) and another sealed source with 0.04 Ci of Am-Be (serial number 47-30325). Illinois report number - IL0900059 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-08-07
45242 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-08-04 06:30 | 2009-08-04 08:28 | 2009-08-08 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into a protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. * * * UPDATE FROM M. JENKINS TO P. SNYDER AT 1315 ON 8/7/09 * * * The licensee retracted this event after investigation revealed no threat or malevolent intent. Contact the Headquarters Operations Officer for additional details. Notified the R4DO (Walker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-08-04
45241 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-07-29 | 2009-08-03 20:10 | 2009-08-28 | AGREEMENT STATE REPORT - IMPROPER TREATMENT The following report was sent from the State of Pennsylvania via facsimile: "During the patient's treatment, it was determined that the wrong side of the patient's head was being treated [using a gamma knife]. The patient treatment was halted at 47.40 minutes out of the prescribed 55.63 minutes. The prescribed dose was 42.5 Gy to the 50% isodose line. Patient received 34.5 Gy to the 50% isodose. "PA DEP [The Pennsylvania Department] Bureau of Radiation Protection was notified in writing, dated July 29, 2009. Their suggestion for improvement is while all treatment team members are present during a 'time out' procedure, to have the patient state the side of his/her lesion or treatment and place an imaging marker to designate the treatment side. "The State [of Pennsylvania] will continue to keep NRC informed of the status of the investigation." Pennsylvania Report PA090027. * * * RETRACTION FROM PENNSYLVANIA (ALLARD) TO CROUCH VIA FAX @ 2116 EDT ON 8/28/09 * * * "Regarding the Lehigh Valley Hospital Medical Event (PA090027) reported to the HOO via fax on 8-3-09, please be advised of our [Pennsylvania Department of Environmental Protection] intent to retract this report. "Based on our inspection and follow-up with the licensee, it was determined that, although the initial written directive was prepared in error, all radiation treatments received by the patient were, in fact, delivered in accordance with a written directive. However, the licensee has taken corrective actions to avoid a similar event occurring in the future." Notified R1DO (White) and FSME EO (Suber). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-08-09
45240 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-07-27 | 2009-08-03 17:15 | 2009-08-03 | AGREEMENT STATE REPORT - LOST (THEN RECOVERED) I-123 CAPSULES "On July 29, 2009, The [Illinois Emergency Management] Agency received preliminary notification from the licensee's radiation safety officer that a package of radioactive material destined for a radiopharmacy in Arizona had not arrived as scheduled, but was subsequently located and forwarded after a day's delay. Subsequent conversations indicated that for a period of approximately 12 hours the package was secured in the possession of a member of the public until it was retrieved by the courier and forwarded to the licensed recipient. The package contained a total of 3 vials with 30 capsules of I-123 which are intended for medical diagnostic studies. Those capsules were 100 to 200 microCi of I-123 each for a total activity in the package of 20.5 milliCi at the time the package was prepared for shipment on July 26, 2009. The measured dose rate 3 feet from the package at the time of shipment was less than 0.1 milliR/h. Due to limited time spent handling and being near the package for the period in question, the dose to the member of the public was well below regulatory limits. When finally received by the pharmacy, the package was found to be intact, with no signs of damage, leakage or the contents having been previously opened or removed. The licensee is investigating corrective actions to take with regards to actions by the courier top prevent a recurrence. A formal report from the licensee concerning this matter is pending. Until that time, this item remains open and under investigation by the [Illinois Emergency Management] Agency." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-08-06
45239 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-07-30 | 2009-08-03 13:15 | 2009-08-03 | AGREEMENT STATE - DAMAGED GAUGE "On 11 Dec 2008 a generally-licensed fixed gauge (serial M3465, containing 80 millicuries Cs-137 as of 2nd quarter 1989; decayed to 50.4 millicuries in July 2009) was removed by the manufacturer from its installed location and placed in storage pending disposal. On 30 July 2009, a WA [Washington] Department of Health (DOH) materials inspector visited the fixed gauge licensee (also specific license WN-I090-1) to conduct a reciprocity inspection of the manufacturer's on-site activities. The manufacturer's representative was there to remove and package a total of 14 decommissioned gauges for disposal. "Several of the gauges showed varying degrees of corrosion. The fixed gauge, serial M3465, showed significant corrosion and was missing a cover plate. The manufacturer's representative reported no unusual radiation measurements prior to packaging activities on 30 July 2009. During packaging, the fixed gauge was rolled over at which time the DOH materials inspector measured the dose rate at the opening as 500 milliRoentgen per hour. Immediate action was taken to control exposure. "The manufacturer's representative adequately secured and shielded the gauge prior to shipping. Apparently the shutter and lead shielding that blocks the radiation beam was either broken or misaligned and failed to function as designed. There was no significant exposure to personnel. The WA DOH investigation continues." The State of Washington incident number is: WA-09-055. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-08-06
45238 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-07-30 21:08 | 2009-07-30 22:55 | 2009-08-02 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF OFFSITE POWER FOR GREATER THAN 15 MINUTES Unit 2 automatically tripped from 100% reactor power as a result of the over-current trip of the 2C Reactor Coolant Pump. Both station auxiliary transformers on Unit 2 subsequently tripped offline. All control rods fully inserted on the trip. Auxiliary feedwater auto-started and maintained Steam Generator water level. The unit is stable in Mode 3. The Emergency Diesel Generators auto started and loaded supplying both emergency busses with power. All systems functioned as required. There was no affect on Unit 1. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0218 ON 8/2/2009 FROM DEAN YARBROUGH TO MARK ABRAMOVITZ * * * "At 2059 on July 30, 2009, a reactor trip of Unit 2 at Braidwood occurred. A loss of offsite power occurred and an Unusual Event was declared at 2108. NRC Headquarter Operations was notified at 2155 (ENS call # 45238). "Power from System Auxiliary Transformer (SAT) (credited offsite power supply) 242-2 was restored to buses 241 and 242 (safety related buses) at 0036 on August 2, 2009. "The Unusual Event was terminated at 0036 on August 2, 2009. This call is being made due to the termination of the Unusual Event declared on July 30, 2009. "An Event Summary Report is required by Exelon procedures within 24 hours of termination of the Unusual Event and will be communicated to the Headquarter Operations later today." The initial event was the result of the actuation of the SAT sudden pressure relay. When the transformer tripped, a slow automatic bus transfer resulted. When the RCPs [Reactor Coolant Pump] and condensate pumps were reenergized, they tripped on overcurrent causing the reactor trip. The sudden pressure relay has subsequently tripped during testing and may have caused the initial event. The licensee reported no damage to the plant. The licensee notified the NRC Resident Inspector. Notified the R3DO (Daley), IRD (McDermott), NRR (Howe), DHS (An), and FEMA (Biscoe). * * * UPDATE AT 1617 ON 8/2/2009 FROM SCOTT BUTLER TO VINCE KLCO * * * The Event Summary Report was received and documented the following technical conclusions: "The Unusual Event declaration was caused by a sudden pressure relay on SAT 242-1 causing a lockout of both SATs followed by a trip of Unit 2 due to the 2C RCP tripping during the automatic bus transfer for bus 258. This led to a loss of offsite power to Unit 2. It is currently unknown why the sudden pressure relay on SAT 242-1 actuated. Troubleshooting on the sudden pressure relay is in progress." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Daley). Notified the IRD (McDermott) and NRR (Howe) via e-mail. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2009-07-30
45237 | -1 | MUNSON MEDICAL CENTER |  |  |  |  | 2009-07-30 09:00 | 2009-07-30 15:15 | 2009-12-23 | POTENTIAL MEDICAL EVENT INVOLVING NOVOSTE BETA-CATH STRONTIUM BRACHYTHERAPY SYSTEM The licensee reported that a patient was undergoing brachytherapy treatment of the heart. During the procedure, it was determined that the source was not in the proper position. The sources were retracted and the procedure reattempted. During the reattempt, it was determined that the sources were not going into the proper position. However, the licensee was not able to retract the sources into the Novoste device. The physician removed the catheter and device as an assembly and placed in a safe box. The licensee does not know the failure mode with any degree of certainty and is sending the device to the manufacturer for evaluation. The cardiologist believes it may have been a kink in the catheter. The patient was notified of the event, and the licensee discussed the issue with NRC Region 3(G. Warren). The device is a Novoste Beta-Cath, Device number: 86865, and source number: ZB551. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM DENNIS SZMANIA TO VINCE KLCO ON 12/23/2009 @ 1056 EST* * * The licensee is retracting the event because the source never entered the patient's body and the exposure to the patient was negligible. Notified the R3DO(Kunowski) and FSME (Villamar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-08-04
45236 | 0 | AREVA NP INC |  |  |  |  | 2009-02-16 | 2009-07-29 17:06 | 2009-07-29 | PART 21 REPORT - THERMO-HYDRAULIC LIMITS BASED ON INCORRECT FUEL LIFTOFF ASSUMPTIONS Measurements obtained from LaSalle spent fuel indicates that the liftoff [corrosion film and coolant system crud deposit thickness] on LaSalle fuel may be greater than assumed in thermal-hydraulic calculations for MCPR (Minimum Critical Power Ratio) and LHGR (Linear Heat Generation Rate). Thickness measurements of liftoff on ATRIUM-10 fuel at LaSalle are as high as 93 micrometers whereas the maximum value observed for other facilities is less than 60 micrometers. The greater than expected liftoff present on LaSalle fuel has been attributed to the operation with zinc levels that exceeded EPRI guidelines for reactor water chemistry. AREVA thermal-hydraulic analyses for LaSalle did not account for the higher liftoff. Following discovery of the deviation, AREVA supplied an operability assessment to Exelon that identified limitations on the operating limit MCPR and rod average exposure. Revised operating limits are being provided to Exelon based on liftoff values that are lower than used in the original operability assessments. These limits are scheduled to be provided by July 31, 2009. Actions have been identified where AREVA will obtain information from the licensees on the anticipated water chemistry environment to be implemented for the next operating cycle, in advance of AREVA core design efforts supporting that cycle. This will assure that AREVA can adequately project the impact of this chemistry environment on liftoff, and to account for it during the design activities. AREVA states that this defect affects only LaSalle Units 1 and 2. Data from other plants currently operating with fuel licensed using AREVA methods indicate that the liftoff is low and within historical levels. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-07-29
45235 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2009-07-28 17:00 | 2009-07-29 12:40 | 2009-07-29 | FITNESS FOR DUTY REPORT - POSSIBLE LOSS OF TEST RESULTS The licensee submitted test specimens to a certified laboratory for analysis. After 5 business days, the results of the test were not reported back to the licensee. The individuals affected are being retested. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 26.719 |  |  |  | 0 | 2009-07-29
45234 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-07-22 | 2009-07-29 11:40 | 2009-07-29 | AGREEMENT STATE - LOST OR STOLEN X-RAY FLUORESCENCE DEVICE The following report was sent from the State of Washington via email: "On 22 July, 2009 [the Washington State Office of Radiation Protection] received a report of a missing XRF device. On 20 July, 2009, an employee at Cole & Associates, failed to report to work and has yet to contact employer's office as to their whereabouts. The employee has not been seen nor heard from. The employee was performing inspections at the Veterans Hospital in Tacoma, Washington, the employee's home town. The employee had in their possession a Thermo Fischer Scientific Niton XL 309 X-ray Fluorescence (XRF) device, serial number U2615TRO459, with an 14 millicurie Cadmium-109 source dated 11/15/2008. "The XRF device is used exclusively for lead analysis in paint. Thermo Fisher Scientific has been notified and will alert the licensee if anyone turns in the unit in to them. A report was also filed with the Kent police." Washington Report WA-09-049. Cadmium-109 has a half life of 462 days. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-08-03
45233 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-07-27 18:00 | 2009-07-28 19:00 | 2009-07-28 | AGREEMENT STATE REPORT - LOST IODINE 125 SEEDS The following information was received from the State of California Radiologic Health Branch via email: "Pomona Valley Hospital Medical Center discovered an Iodine-125 seed shortage of 10 seeds (.449 mCi/seed) all in one cartridge on Monday July 27, 2009 at approximately 1800 hours during a permanent prostate seed implant. The physician performing the implant discovered the cartridge missing when he opened the sterilized package. These I-125 sources are used for permanent implant into the prostate for therapy. "The physicist last saw the 7 cartridges and 100 seeds in the Hot Lab, located in the basement of the hospital on Friday July 24, 2009 at approximately 1050. Of the 100 seeds in the order, he assayed the cartridge with 9 seeds plus 1 for a total of 10 seeds. Once he completed the assay he re-loaded the cartridge with all 10 seeds, and placed the cartridge back in the storage block with the other 6 cartridges (containing 15 seeds each), and returned the storage block to the lunch box (used for carrying the cartridges to surgery). He placed the lunch box behind the loading shield and secured the Hot Lab, anti-room and exterior door before leaving the area. "On Monday at approximately 1510 the lunch box was retrieved form the locked Hot Lab and taken, with the seeds inside, to the Operating Room (OR). Possession of the lunch box was transferred to an RN, who called Sterile Processing to retrieve the seeds from her desk for sterilization. A staff member from Sterile Processing retrieved the lunch box from RN's desk (located in the surgery suite area) to prepare for sterilization. The Sterile Processing staff member had to be directed on how to wrap the seeds as he had never prepared the seeds for sterilization before. The wrapped seeds were taken back up to Surgery and placed in Sterilizer #34. Once the sterilization process was complete, the seed package was delivered to OR #2 where the implant procedure was being performed. "Once the physician discovered the missing cartridge during the procedure, the Medical Physicist and RSO, was notified and immediately went to the Hot Lab in attempt to locate the missing cartridge. The RSO contacted the physicist by phone who confirmed all 100 seeds in 7 cartridges were accounted for on Friday morning when he assayed them. The RSO also interviewed the staff member who prepared the seeds for Sterile processing to ask him if he dropped the lunch box and perhaps lost a cartridge, which the staff member denied. The RSO then took the spill meter (TBM survey meter) and surveyed Sterile Processing and both elevators. The Hot Lab was taken apart and thoroughly surveyed, as well as the anti-room and packaging materials. No evidence of radioactive materials was found. "The implant procedure concluded without incident. The dosimetry plan for the patient called for 90 seeds which they had available. At the completion of the implant we had no seeds left over. All 90 seeds were implanted into the patient and the patient is doing well. In no way was the patient's care compromised by this set of missing I-125 seeds. "Bard [Brachytherapy, Inc], the manufacturer of the sources was called to verify the shipment was in fact complete, but at 2100 hours their time July 27, 2009, no one was available. The hospital was able to contact Bard, located in Carol Stream, Illinois the following day concerning a preliminary investigation of the order. According to Bard's records the assembler of the order pulled 100 seeds off the line and 7 cartridges from inventory. None of their other customers reported receiving 10 seeds not ordered. Bard will not provide a formal report of our order until it has passed their legal department. "Last night (July 27, 2009) Security was notified and started a formal investigation of the incident. The Hospital Administration, the Chief of Security, and the Manager of Sterile Processing were notified and explained the seriousness of the situation. Today (July 28, 2009) Pomona Valley Hospital Medical Center is continuing to search for the seeds and taking statements from all the involved associates. "The Lot Number for the sources is: BBTG0030." Note that this report was edited to remove reference to the names of the employees involved. California Report number 072809. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-07-31
45232 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2009-07-27 06:30 | 2009-07-28 16:28 | 2012-11-30 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The following information was received from the Arizona Radiation Regulatory Agency via email: "At approximately 9:45 am, July 28, 2009, the Agency [Arizona Radiation Regulatory Agency] was notified that a Troxler Model 3411 had fallen out of the transporting vehicle on the way to the construction site. The operator had placed the device in the pickup truck at approximately 6:30 am on July 27, 2009, became distracted and failed to secure the device or to close the tailgate. The device, serial number 10308, apparently fell off the truck on the way to the construction site at Broadway and Jessica St. A search was instituted, but the device was not located and the Tucson Police were called at approximately 8:00 am July 27. Tucson Police report number 09 07270185 was prepared. As of the time cited above, the device has not been recovered. Press interest is expected. The Agency [Arizona Radiation Regulatory Agency] continues to investigate this event. "The U.S. NRC, the State of CA, NV, UT, NM, CO and TX and Mexico are being notified of this event. " Arizona Report Number 09-003 * * * UPDATE FROM AUBREY GODWIN TO VINCE KLCO ON 11/30/12 AT 1154 EST * * * The following information was received by email: "On 11/29/2012 [at 0915 MST], the Tucson Police were called after a couple found a yellow container with radiation stickers on it outside of a City of Tucson Recyclables Dumpster located at Park and East Fair Street, Tucson, AZ. The Tucson Police department notified the Tucson Fire Hazardous Material team who then notified the Tucson Bomb Squad who then notified the FBI. X-Rays by the Bomb Squad found nothing suspicious. During this time (10:40 AM) the Agency was then called and responded to the scene. "The Agency response team surveyed the device and made wipe smears. The survey indicated a source was in the device and the smears were negative for contamination. A review of the x-ray made by the Bomb Squad indicated the sources were in the device as designed. The case was undamaged but not locked. The device is being held by the Agency pending return to licensee. "There was minor media interest in the recovery. "The USNRC, FBI, the States of Ca, NV, UT, NM, CO and TX and Mexico are being notified of this event." The recently found Troxler serial number match with the originally reported lost Troxler. Notified R4DO (Whitten), ILTAB(Langlie) and FSME via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2009-07-31
45231 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2009-07-27 10:00 | 2009-07-27 16:51 | 2009-07-27 | TECHNICAL SUPPORT CENTER (TSC) HVAC FOUND DEGRADED DUE TO WATER INTRUSION "At about 10:00, on July 27, 2009, the Technical Support Center (TSC) HVAC was found to be degraded. The fan motor was running but there was no air flow and the TSC rooms were not being maintained with a positive pressure. Upon investigation, the fan housing was found partially filled with water, submerging the motor and preventing air flow through the system. Repair of the motor will take more than one day and is being immediately pursued. This affects the ability of the TSC ventilation to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities of the TSC are unaffected by this emergent repair. Existing procedures provide direction to relocate TSC personnel in the event of a TSC habitability concern; however, the backup facility does not have standby electrical power or a filtered ventilation system. Therefore, this condition is considered a major loss of emergency assessment capability and is reportable under 10CFR50.72(b)(3)(xiii)." The TSC HVAC was last functionally tested satisfactorily on 06/29/09. The licensee believes the water found in the HVAV fan housing may be a result of a clogged drain line. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-27
45230 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-07-27 09:35 | 2009-07-27 10:39 | 2009-07-31 | TECHNICAL SUPPORT CENTER TEMPORARILY UNAVAILABLE FOR USE "On July 27, 2009, Fermi 2 is removing the Technical Support Center (TSC) from operation to facilitate maintenance activities for furniture and facility upgrade. During this work the facility will not be available for use. Fermi 2 is making this notification in accordance with 10 CFR 50.72(b)(3)(xiii). In the event TSC activation is necessary the Emergency Operations Facility (EOF) will be utilized. Activation and use of the EOF as a back up for the TSC is included in Fermi 2's Radiological Emergency Response Preparedness Plan. The Emergency Call Out System (ECOS) is designed to facilitate contacting TSC personnel to respond directly to the EOF in the event of an emergency. Fermi 2 will notify the NRC upon completion of this work which is expected to be July 31, 2009." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JEFF GROFF TO JOE O'HARA AT 1414 EDT ON 7/31/09 * * * "Update to Event #45230 regarding unavailability of the Technical Support Center (TSC) for planned furniture and facility upgrade. The work to upgrade the facility has been completed satisfactorily. The TSC has been restored as an Emergency Response facility. The facility had been removed from operation on July 27, 2009 at 0935 EDT. The TSC was restored to operation at 1330 EDT on July 31, 2009." The NRC Resident Inspector has been notified. Notified R3DO(Daley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-27
45229 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2009-07-27 07:52 | 2009-07-27 09:52 | 2009-07-30 | TECHNICAL SUPPORT CENTER REMOVED FROM SERVICE FOR UPGRADES "On Monday, July 27, 2009, at 0752, Seabrook Station is temporarily relocating its Technical Support Center (TSC) from the permanent location on the 75 foot level of the Control Building (CB) to an alternate location in the Online/Outage Control Center (OCC). This relocation is necessary to allow for installation of new equipment and upgrading of existing equipment in the TSC. "The site Emergency Response Organization (ERO) has been notified of the modifications and has been instructed on the planned compensatory measure to be implemented during the temporary relocation. "The NRC Resident Inspector has been notified of the relocation activities. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to loss of the emergency response facility. "Seabrook Station will provide updates as necessary and will advise the NRC of the restoration of the permanent TSC." The State of New Hampshire has been notified. * * * UPDATE FROM MARK HANSEN TO JOE O'HARA AT 1635 ON 7/30/09 * * * "On Thursday. July 30. 2009. Seabrook Station completed modifications of its Technical Support Center (TSC) and has restored the TSC permanent location on the 75 foot level of the Control Building (CB) to service. The permanent TSC was declared operable at 1456 on Thursday July 30, 2009. "The site Emergency Response Organization (ERO) has been notified that the modifications to the permanent TSC have been completed, that compensatory measures are no longer necessary and that TSC personnel are to report to the permanent TSC in the case of a plant emergency. "The NRC Resident Inspector has been notified that the permanent TSC has been restored to service." The State of New Hampshire and the Commonwealth of Massachusetts have been notified. Notified R1DO (A. Dimitriadis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-27
45228 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-07-26 15:06 | 2009-07-26 18:44 | 2009-07-26 | MANUAL REACTOR TRIP DUE TO A REACTOR COOLANT PUMP SEAL MALFUNCTION "At 1506 on Sunday, July 26, 2009, the Cook Nuclear Plant (CNP) Unit 2 reactor was manually tripped after the control room staff concluded that the #22 Reactor Coolant Pump (RCP) needed to be promptly secured due to a RCP seal malfunction as indicated by lowering #1 seal leakoff flows and rising #1 seal return and pump radial bearing temperature. This requires a 4-hour report under 10CFR50.72(b)(2)(iv)(B). "Both motor-driven Auxiliary Feedwater pumps automatically started due to the reactor trip and trip of both Main Feedwater Pumps. The Turbine-Driven Auxiliary Feedwater Pump (TDAFP) started automatically due to low-low water levels in at least two steam generators, which is expected for a reactor trip from approximately full power. The automatic actuation of the reactor protection system and the TDAFP require an 8-hour report under 10CFR50.72(b)(3)(iv)(A). "All systems functioned as expected after the trip, and no major components were out of service at the time except for the Moisture Separator Reheaters which were not in service since the beginning of the current power cycle. "The licensee has notified the NRC Senior Resident Inspector." All control rods fully inserted as required. Electrical system is in normal post-trip lineup. Plant cooldown is via Condenser Steam Dumps using Auxiliary Feedwater pumps. Plant cooldown will continue to Mode 5 (cold shutdown). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-07-26
45227 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-07-24 14:15 | 2009-07-24 18:50 | 2009-09-22 | HPCI INOPERABLE DUE TO OIL LEAK IN MECHANICAL TRIP HOLD VALVE "During performance of surveillance 1-SR-3.5.1.7, HPCI Main and Booster Pump Set Developed Head and Flow Rate Test at Rated Reactor Pressure, the HPCI Turbine Stop Valve Mechanical Trip Hold Valve, 1-PCV-73-18C, developed an oil leak of approximately 0.25 gpm. HPCI was INOPERABLE at the time of discovery due to performance of SR and continued to be INOPERABLE due to the oil leak that developed. "This event is reportable within 8 hours in accordance with 10CFR 50.72(b)(3)(v) as an event or condition that at the time of discovery could have prevented the fulfillment of a safety function. It also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(vii)." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 9/22/2009 AT 1700 EDT FROM RAYMOND SWAFFORD TO DONG PARK * * * "On July 24, 2009, the High Pressure Coolant Injection (HPCI) Stop Valve Mechanical Trip Hold Valve (PCV-073-0018C) developed a ruptured diaphragm resulting an approximate 0.25 to 0.5 gallon per minute oil leak during scheduled performance of Surveillance Instruction, HPCI Main and Booster Pump Set Developed Head and Flow Rate at Rated Reactor Pressure. At the time BFN [Browns Ferry Nuclear] made [event] notification 45227, there were concerns regarding the ability of HPCI to fulfill its safety function, hence, BFN made an eight hour notification in accordance with 10CFR50.72(b)(3)(v)(B) and 10CFR50.72(b)(3)(v)(D). "An evaluation performed in response to this notification concluded that the HPCI System was capable of performing its intended safety function with the oil leak. TVA Engineering evaluated the rate of oil loss considering a worse case failure of PCV-073-0018C diaphragm and determined that the turbine oil system capacity is such that the oil loss thru the failed diaphragm would not impact HPCI operation during its mission time for the Design Basis accidents and transients for which HPCI is credited. "The circumstances discussed in the notification did not result in any condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or system that are needed to remove residual heat and mitigate the consequences of an accident. Therefore, this event is not reportable under 10CFR50.72(b)(3)(v)(B) and 10CFR50.72(b)(3)(v)(D). "TVA documented the evaluation of this event notification in its corrective action program (PER 177206). "The licensee has notified the NRC Resident Inspector." Notified R2DO (Rudisail). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-07-24
45226 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-07-15 | 2009-07-24 16:35 | 2009-08-11 | AGREEMENT STATE REPORT INVOLVING THE LOSS OF A CALIFORNIUM-252 SOURCE On 07/24/09 the State of North Carolina was notified by Duke University that a Cf-252 source could not be located during a mid-July inventory of their TUNL facility. The following information is a portion of an email forwarded by the State of North Carolina: "TUNL staff today formally reported the loss of a Californium-252 source: "(1) Source description: 3.4 microcuries of Cf-252 with an active layer of 8 mm diameter on the platinum backing 15 mm in diameter, 0.2 mm thick. The source was inside an ionization chamber, which was purchased in 1995 from Physikalish-Technische Bundesanstalt, Berlin with an initial activity of 5.17 MBq (86 microcuries; T¢ = 2.645 y) "(2) Circumstances: A physical inventory of TUNL sources during mid-July determined that this source was missing. A search of the TUNL facility failed to locate this source. Although the investigation is continuing, TUNL staff have concluded that the source is lost. "(3) Disposition or probable disposition of lost source: This source was incorporated into a piece of equipment (ion chamber) composed of a metal tube with several smaller metal tubes (vacuum lines) coming off of it. TUNL staff suspect that this piece of equipment containing the source may have been left with other scrap items shipped off site for disposal as radioactive waste during the Fall of 2008. However it is quite possible that this ion chamber and the source inside are still somewhere inside the TUNL facility. TUNL staff have been instructed to report if they happen upon it. "(4) Possible radiation exposure: None under any reasonably probable scenario. "(5) Actions taken to recover the material: TUNL staff conducted a search of the TUNL facility; the investigation into this incident is ongoing. "(6) Steps taken to prevent a recurrence: TUNL staff are developing and implementing a series of measures to tighten control over TUNL radioactive sources. The development of these policies and procedures is still underway." The RSO at the TUNL facility said the lost source is a target foil used in the TUNL linear accelerator (032-247-A1), and it was stored at TUNL. The loss occurred under the Duke University broad scope academic license 032-0247-1 and not the TUNL license. No manufacturer, make, model, or serial number reported at this time (16:45 7/24/09)." North Carolina Incident ICD 09-30 * * * UPDATE PROVIDED BY JAMES ALBRIGHT TO JASON KOZAL ON 08/11/09 AT 1702 * * * The following information is a portion of an email forwarded by the State of North Carolina: "The source was found at approximately at 1:30 PM on Monday, July 27, 2009 in room K101 of the Keck Building. The source was on a table among an assortment of other research equipment. The area where the source was found is a radiation controlled area and is not accessible to the general public. Combining the circumstances of the discovery of the source with details of our search for the source and a review of our source checkout logs, we conclude that the source has likely been mixed with research equipment in the same research area where it was discovered since the summer 2008. "Findings: The loss of inventory control of this source and our failure for timely discovery was due to three contributing factors: (1) improper removal of the source from its storage location, (2) a clerical error in the quarterly source inventories and (3) our practice of using source checkout log sheets to augment physical inspection in our quarterly inventories. Our radioactive materials (RAM) inventory control is based on proper checkout of sources by completing entries on a sign-out/in sheet for each usage and quarterly RAM inventories. Normally failures to properly sign out/in sources are caught in the quarterly inventories. However, because of our practice of augmenting the physical inspection in our quarterly RAM inventory check with information on the sign-out/in log sheets, it is possible for this check to fail due to either logging errors on the sign-out/in sheets or clerical errors made in reviewing the sheets for inventory assessment. In this rare event, both occurred. During the September 2008 inventory check, the most recent entries for this source on the sign-out/in sheets were overlooked and earlier entries were used that indicated that the source was in use by a student. We have no reason to believe the source was not in use at TUNL because he was not present at the July 2008 accelerator scheduling meeting when a faculty member mentioned that the source wasn't in the storage safe, and [the professor] forgot to alert him of the potential problem with this source. Also contributing to this oversight that delayed discovery of the problem was our policy of allowing source usage without time limitations; it is not unusual for a source to be used by an individual for several quarters. "Corrective Actions: This unfortunate event has caused us to review our practices in managing the RAM inventory at TUNL. Based on our findings, the following actions will be taken to reduce risk of loss of control of any items in our RAM inventory in the future: "1. We will discontinue the use of information from the checkout log sheets to augment physical inspections in the quarterly inventories. In the future, all sources will be physically inspected. For sources that are permanently embedded in equipment, the seal on the equipment where the source is installed will be inspected and the presence of the source will be checked with particle detectors whenever practical; "2. Open ended source usage will be discontinued source usage will be limited to a duration of one week; "3. The number of people with authorization to checkout sources will be more restrictive - Only TUNL faculty members, research scientists, post docs and selected technical staff members will be allowed to check out radioactive sources (graduate students, undergraduate students and visitors will no longer be allowed to checkout radioactive sources); "4. Substantial consequences will be imposed on individuals who do not properly checkout sources - failure to sign out radioactive sources properly will put research groups at risk of losing their privilege to use radioactive sources in the TUNL inventory; "5. Security in the area around our main source storage will be increased - the main area for radioactive materials storage at TUNL will be monitored with video cameras to record removal and return of radioactive sources; and "6. The radioactive materials in the TUNL inventory will be sorted into categories according to the reporting requirements by the State: high, medium and low. We are investigating technologies for electronic inventory control on the materials in the high and medium reporting categories. Notified R1DO (Cook), FSME EO (Mauer), and ILTAB via e-mail. 252 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-07-29
45225 | 0 | SUPERIOR WELL SERVICES |  |  |  |  | 2008-09-20 14:30 | 2009-07-23 16:33 | 2009-07-23 | LOST (THEN RECOVERED) LICENSED NUCLEAR MATERIAL This is an historical report for an incident submitted in response to an on-site inspection by an NRC Inspector (Lodhi). "On September 20, 2008 at approximately 2:30pm, while returning from an open hole job north of Buckhannon, the neutron shield and the density shield separated from the radiation compartment of an open hole logging truck near Lost Creek on Interstate 79 [exit 110] southbound. The driver continued driving to the shop. Upon return, he noticed a chain hanging freely from the radiation compartment of his truck. He looked in the compartment and noticed that both transport shields and the pig holder had been separated from the unit. He immediately called his supervisor at approximately 3:00pm, who had stopped at the BP in Lost Creek for a drink on the way to the shop, and told him that the transport shield had been separated from the wireline unit. The driver mentioned hearing something after crossing the bridge on interstate 79 South at Lost Creek. The supervisor, who was ? of a mile away from the bridge, proceeded to the spot and immediately picked up the transport shields and pig holder. The supervisor loaded the transport shields and pig holder into the box of his pick-up truck and secured them with separate chains and padlocks and returned to the facility. Upon returning to the facility with the sources, the supervisor contacted his mechanic to reweld the pig holder to the floor of the open hole wireline unit. The supervisor also contacted the camp EIC [Engineer-In-Charge] to report the incident and notify him that all equipment was resecured. The supervisor then placed both sources into the downhole storage pig until the welding was completed. "According to witness statements both sources were secured with a padlock in their respective transport shields. The shields were mounted on a pig holder that was tack welded to the floor of the radiation compartment on the right rear of the truck. The radiation compartment door was secured with the T-handle closed and locked and a hasp lock on the rear of the compartment. The transport shields were chained together. "Root Cause: Failure of the tack welds on the pig holder. The failure of the tack welds that held the pig holder to the truck caused the transport shields and the pig holder to be free in the radiation compartment. "Secondary Cause # 1: Failure of the T-handle and the hasp lock on the compartment door. The failure of the T-handle and the hasp lock on the radiation compartment door allowed the compartment door to open freely and failed to contain the 150+ lbs of material that was inside of the compartment. "Secondary Cause # 2: Hitting a pothole on interstate 79 South. When the driver of the open hole wireline unit struck the pothole on interstate 79 south it caused the transport shields and the pig holder to move inside of the radiation compartment. The movement of the equipment and the failure of the door mechanisms allowed the equipment to separate from the open hole wireline unit. "Corrective Actions: Corrective actions were taken immediately to eliminate the possibility of a reoccurrence. -Complete weld along the base of the pig holder. -Chain through both transport shields that is bolted to a structural member of the truck (floor, frame, etc). -Heavy hasp lock (bolt style) on the exterior of the radiation compartment door. "Research: Research was conducted to verify that there were no overexposures included calculating the expected dose in the worst case scenario with the transportation shields removed from the wireline unit. Surface reading: 2.0 mR/hr TI: 0.4 mR/hr Time along 79: 30 minutes Expected dose if a person were sitting on the shield for ¢ hour: 1 mR "A survey meter reading was taken at nine feet from the transport shields in order to estimate the potential for exposure to members of the public who would be traveling southbound on interstate 79. 9 ft Reading: 0.02 mR/hr Average Speed: 70 miles per hour = 369,600 feet per hour Possible exposure: 0.02/369,600 = 0.00000005411255411 mR." The licensee stated that visual inspection revealed no damage to the neutron or density shield and that this was confirmed by leak test analysis. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-07-23
45223 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2009-07-22 17:33 | 2009-07-22 18:47 | 2009-07-22 | LOSS OF A LOCAL POWER RANGE MONITOR DETECTOR CONTAINING SPECIAL NUCLEAR MATERIAL "During the annual physical inventory of special nuclear material at Grand Gulf Nuclear Station (GGNS), a special nuclear material (SNM) inventory discrepancy was discovered. One unirradiated LPRM (local power range monitor) detector could not be located. "According to SNM inventory sheets, the LPRM detector should have been stored in a LPRM canister in the SNM storage area of the Auxiliary Building. During the inventory, the LPRM detector could not be located. Based on the inventory results and interviews with personnel knowledgeable of the disposal of the LPRM detector, it is believed the LPRM detector was discarded and was shipped to an authorized disposal facility for burial as radioactive waste. The LPRM detector contained a maximum total quantity of all licensed material in the device of approximately 5.84 microCuries of U-234 and U-235 combined (approximately 80wt% U-234 and 20wt% U-235). This quantity meets the criteria for reporting since quantities are greater than 10 times the quantity specified in Appendix C to 10CFR20. "This material does not represent a hazard to the public health and safety since it is believed the material has been properly handled and disposed of as radioactive waste. There is no evidence of theft or diversion. "This notification satisfies the 30-day notification requirement of 10 CFR 20.2201(a)(1)(ii). A subsequent written report will be made in accordance with 10 CFR 20.2201(b)." The licensee has notified the NRC Resident Inspector. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-07-22
45222 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2009-07-16 | 2009-07-22 16:29 | 2009-07-22 | AGREEMENT STATE REPORT - MULTIPLE EQUIPMENT ISSUES ASSOCIATED WITH HDR BRACHYTHERAPY UNIT The following is a summary of information received via fax from the State of Wisconsin. For more details contact the Headquarters Operations Officer. On July 16, 2009, DHS [Department of Health Services] performed a reciprocity inspection at Wheaton Franciscan Healthcare - All Saints for a source exchange of a 10 Ci, Ir-192 source and routine maintenance of a Nucletron Micro Selectron HDR [High Dose Rate] classic remote afterloader brachytherapy device. During the inspection, three items were identified during testing of the HDR unit: 1) HDR control panel did not operate as designed; 2) the HDR/Linac switch was not wired correctly; and 3) Radiation area monitor was operating sporadically. On July 16, 2009, DHS informed the licensee that they would not be able to use the HDR unit for patient treatments until all areas of concerns were corrected. The licensee informed DHS that the HDR unit has NOT been used for any patient treatments since the Department authorized the licensee the HDR unit on August 8, 2008. On July 21, 2009, DHS issued the licensee a Confirmatory Action Letter effective July 17, 2009, that the licensee is not allowed to use the HDR unit for patient treatments until the listed items were corrected The licensee has committed to address all equipment malfunctions prior to treating patients using the Nucleation HDR unit. DHS plans to conduct an inspection prior to patient treatment. The State does not anticipate any media attention. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2009-07-27
45221 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-07-22 | 2009-07-22 14:07 | 2009-07-24 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received via fax from the State of Colorado. "A medical licensee notified the [Colorado Department of Health] of a misadministration during a HDR [High Dose Rate Afterloader] procedure. A positioning error resulted in an estimated dose of 700 Rads to the wrong site. "No other details are available at this time. "The Department has initiated an investigation of this incident." The licensee did not provide the State with an event date and time in the initial event report. * * * UPDATE AT 1321 EDT ON 07/24/09 BY ERIC SIMPSON * * * The following information was received by the State of Colorado via fax: "The [State of Colorado Department of Health] received the following information from the medical physicist who reported the misadministration involving a therapy treatment with a High Dose rate Remote Afterloader (HDR) at Penrose St. Francis Hospital in Colorado Springs, Colorado. -The date of the misadministration was 7/21/09. -Because of the error, the dose was delivered to the entrance of the vagina, rather than intrauteral. -The patient's physician and the patient have been informed of the incident. -The applicator used in this procedure uses a collet to hold a 3 mm source tube in place. There may have been a problem with the collet, which allowed the source tube to move. -The licensee instituted corrective actions, which include additional training for all staff involved in HDR therapy treatments, and an additional check of the applicator prior to start of treatment. "A full report from the medical physicist is expected within the next 7 days. "No other details are available at this time. "The Department has initiated an investigation of this incident." Notified R4DO (Jones) and FSME EO (Villamar). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-07-28
45220 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-07-22 08:00 | 2009-07-22 07:58 | 2009-07-22 | SPDS OUT OF SERVICE FOR PLANNED MAINTENANCE "On July 22, 2009, the Safety Parameter Display System (SPDS) will be removed from service at approximately 0800 hours for Salem Unit 1 to perform planned maintenance to the system. The maintenance consists of the replacement of the uninterruptable power source (UPS) to improve the reliability of the SPDS. The removal of SPDS will also affect the transmission of Salem Unit 1 data from the emergency response data system (ERDS). Appropriate compensatory measures will be in place while SPDS is out of service. SPDS is scheduled to be out of service for approximately 29 hours." Unit 2 is unaffected by this maintenance work. The NRC Resident Inspector has been notified. * * * UPDATE FROM TOM BYYKKONEN TO HOWIE CROUCH @ 2002 EDT ON 7/22/09 * * * The Safety Parameter Display System and the Emergency Response Data System were returned to service at 1830 EDT on 7/22/09. The licensee has notified the NRC Resident Inspector and the States of Delaware and New Jersey Emergency Management Agencies. Notified R1DO (Rogge). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-22
45219 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2009-07-21 14:05 | 2009-07-21 17:15 | 2009-07-23 | LOSS OF EMERGENCY RESPONSE CAPABILITY - TSC/OSC IS UNAVAILABLE DUE TO HVAC SYSTEM TROUBLE "Unavailability of TSC/OSC Heating, Ventilation and Air Conditioning (HVAC) System. "At 1405 hours on Wednesday, July 21, 2009, the Pilgrim Nuclear Power Station (PNPS) Technical Support Center (TSC) / Operations Support Center (OSC) HVAC system was discovered to be nonfunctional. During initial troubleshooting, the breaker providing power to the supply fan mechanically tripped and will not be reset until troubleshooting certifies the breaker is acceptable for use. This event occurred during scheduled preventative maintenance (PM) of the system. "Under certain accident conditions, the TSC/OSC may become unavailable due to inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC/OSC personnel to alternate locations. "The licensee has notified the NRC Senior Resident Inspector/Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an emergency response facility." The licensee notified the Commonwealth of Massachusetts Emergency Management Agency. * * * UPDATE AT 2100 EDT ON 07/23/09 FROM KEN GOODALL TO S. SANDIN * * * "This is a follow-up courtesy notification to EN #45219. All corrective maintenance activities on the TSC/OSC HVAC system are complete and the TSC/OSC is now functional and available for use. "The NRC Resident has been notified." The licensee will inform the Commonwealth of Massachusetts Emergency Management Agency. Notified R1DO (Rogge). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-21
45218 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-07-21 09:30 | 2009-07-21 16:42 | 2009-07-21 | ABILITY TO ACTIVATE EMERGENCY SIRENS TEMPORARILY LOST "At 0930 on 7/21/09, during routine backup diesel generator surveillance testing of the Princeton Radio Tower, the automatic electrical power transfer switch failed in an intermediate position [during] restoration to its normal electrical alignment. The Turkey Point Plant Alert Notification System is located at the Princeton Tower. The failure of the automatic transfer switch in the intermediate position resulted in a temporary loss of power to the Alert Notification System repeaters. The remote telemetry monitoring at the Tower functioned as designed and provided prompt notification of the situation to FPL personnel. An FPL Radio technician was promptly dispatched to assess the condition. The Alert Notification System (redundant activating transmitters) was deemed unavailable during this time. The Princeton Radio Tower electrical power transfer switch was manually positioned to align the Alert Notification System repeaters to their normal power supply at 1035 on 7/21/09, restoring availability. The ability to manually transfer the Alert Notification System repeaters' electrical power supply was not impacted by this failure. The Alert Notification System was tested satisfactory once the system was returned to service. An investigation to determine the failure of the automatic transfer switch is ongoing. "The failure of this system is considered a major loss of offsite communications capability and is reportable under 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-21
45217 | 0 | ORDER OF ST. FRANCIS HOSPITAL |  |  |  |  | 2009-07-21 11:45 | 2009-07-21 15:41 | 2009-07-21 | EXTERNAL CONTAMINATION ON SHIPMENT OF RADIOPHARMACEUTICALS The licensee reported they received a shipment of Thallium-201 from Covidien (formerly Mallinckrodt) that had external contamination greater than regulatory limits. The package was swiped during receipt and had 25,000 dpm of contamination. The limit is 220 dpm. External radiation levels were 0.1 mR/hr at one meter which was consistent with the shipping documents. The package is currently wrapped in plastic in secure storage at the licensee facility where it will remain until decayed and then will be properly disposed of by the licensee. The shipper and shipping company was notified of the contamination event. The driver and the vehicle were surveyed and no contamination was found. No personnel at the receiving facility were reported to be contaminated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2009-07-21
45216 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-05-25 16:15 | 2009-07-21 15:27 | 2009-07-21 | OPTIONAL 60-DAY REPORT OF INVALID SPECIFIED SYSTEM ACTUATION "On May 25, 2009, at 1615, a Unit 3 control fuse failed open causing multiple containment isolation valves for the atmospheric sampling system and containment ventilation/purge systems to close on a loss of power to the logic system. No actual valid containment isolation signals were received or processed by the containment isolation logic. Since this was an invalid signal, a telephone notification to the NRC Operations Center may be provided within 60 days after discovery of the event instead of submitting a written Licensee Event Report. [10 CFR 50.73(a)(2)(iv)(A)]. "This phone notification is being made in lieu of a written 60 day LER as allowed in 10 CFR 50.73(a)(1) to report the invalid actuation of multiple containment isolation valves that occurred as described above. The fuse is associated with the inboard containment isolation logic. This is considered a partial actuation and all components operated as expected. Troubleshooting identified that a relay failed and, in turn, had caused the fuse to open. The relay and fuse were replaced and the systems restored to their normal lineup. The NRC Resident has been informed that this notification is being made. "No further notifications or reports will be issued." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-07-21
45215 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-07-21 08:03 | 2009-07-21 14:15 | 2009-07-21 | FITNESS FOR DUTY REPORT - CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed supervisory contractor employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2009-07-21
45214 | 0 | COBRA NATURAL RESOURCES |  |  |  |  | 2009-07-21 07:30 | 2009-07-21 11:30 | 2009-07-21 | COURTESY NOTIFICATION OF AN ACCIDENT AFFECTING A GAUGE CONTAINING CALIFORNIUM-252 A licensee representative of Cobra Natural Resources LLC called concerning an accident at a coal mine loading facility where a device containing radioactive sources was stored. A train derailment of five empty coal cars at the mine damaged a "loadout" building where a process gauge with radioactive sources was stored. Due to debris at the site of the incident, the licensee is unable to reach the gauge but it appears intact and undamaged. The gauge contains four Californium-252 sources with at total activity of less than 80 mCi. The licensee RSO is continuing to evaluate the situation. * * * UPDATE FROM LICENSEE (BILL EMERSON) TO HUFFMAN AT 1605 EDT ON 7/21/09 * * * The RSO for the licensee reports that its contractor, Thermo-Fisher, has been able to perform close-in area surveys of the device using a remote probe. The surveys confirmed that there is no contamination. Remote visual examination also revealed no indication of damage. The device, a Gamma-Metrics coal analyzer, is still not accessible due to personnel risk from the building debris but the licensee believes that there is no risk of damage to the device until it can be retrieved. The licensee has discussed this event with NRC Region 1 (Miller) and FSME (Villamar). R1DO (Rogge) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | WV | MAT | [5 empty] | 0 | 2009-07-21
45213 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-06-19 | 2009-07-21 08:57 | 2009-07-21 | AGREEMENT STATE REPORT - DIFFICULTY RETRIEIVING RADIOGRAPHY SOURCE The following report was received via email: "On 6/19/09 at approximately 11:30 a.m., the licensee was unable to retract an industrial radiography source. [The] cause was due to a magnetic positioning device used during operations which fell onto the guide tube, crimping the tube and preventing the source to be retracted to the fully shielded position. [The] device was a QSA Model 660, S/N B2692, with a 91 Curie Ir-192 source, QSA S/N 53932B. No over exposure to personnel or [the] public was reported. [The] source was retrieved into [the] camera by trained personnel within approximately 1/2 hour. [The] licensee revised procedures and conducted refresher training to help prevent similar accidents in the future. ODH [Ohio Department of Health] conducted [an] inspection of [the] job site on 7/1/09. [The] licensee provided [a] written report within [the] 30-day required timeframe. [The] licensee originally thought that this event required a 30-day notice. [The] licensee has been instructed as to the need for 24-hour notification for these events." Ohio report number: OH090007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-07-24
45212 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-07-20 12:54 | 2009-07-20 19:13 | 2009-07-20 | FITNESS FOR DUTY REPORT - CONFIRMED POSITIVE FOR ALCOHOL A non-licensed supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2009-07-20
45211 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2009-07-19 01:02 | 2009-07-19 01:58 | 2009-07-19 | 1-HOUR SECURITY REPORT RELATED TO A SAFEGUARDS EVENT The licensee discovered vulnerability in a safeguard system that could allow access to a controlled access area which compensatory measures had not been employed. Upon discovery, compensatory measures were immediately implemented. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-07-19
45210 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-07-17 17:42 | 2009-07-18 00:26 | 2009-07-18 | ACTUATION OF EMERGENCY DIESEL GENERATORS DUE TO LOSS OF POWER TO SAFETY RELATED BUS "At 1742 EDT on July 17, 2009, while attempting to restore normal alignment providing offsite power following repair of the 'D' Common Station Service Transformer (CSST), the transfer from the alternate to the normal power supply for the 6.9kV Shutdown Board 2B-B failed because of an apparent failure of the interlock that should have prevented closing the normal breaker until an undervoltage condition existed on the alternate feed. The emergency diesel generators received a blackout signal and all four diesel generators started. Loads transferred and shed properly, and all systems functioned as expected. "WBN [Watts Bar Nuclear] had been in LCO 3.8.1 condition A since 0032 EDT on July 16, 2009 due to the outage of the D CSST. Because loads did not transfer to the offsite power source, WBN remains in LCO 3.8.1 A which requires restoration of the offsite power supply by 0032 EDT 7/19/2009. "All systems are operating properly and the plant is stable. Troubleshooting and maintenance has begun and WBN anticipates return of the normal offsite power supply to the 2B-B Shutdown Board within the time required by technical specifications. "This event is reportable under 10 CFR 50.72(b)(3)(iv) as an event or condition that resulted in valid actuation of the emergency diesel generators. "The licensee has notified the NRC Resident Inspector" The 6.9kV Shutdown boards at Watts Bar are safety related busses. The electrical configuration prior to the event had the 1A-A and 2A-A Shutdown Boards aligned to their normal offsite power source. The 1B-B and 2B-B Shutdown Boards were aligned to an alternate offsite power source because their normal source, the 'D' CSST had been out of service for repairs. Following completion of the repairs to the 'D' CSST, the licensee attempted to restore normal offsite power to the 2B-B Shutdown Board from the 'D' CSST using a fast transfer from the alternate power supply. For unknown reasons, the normal supply breaker attempted to close onto the 2B-B bus before the alternate supply breaker had opened. This, in effect, would have paralled both the primary and alternate sources of power to the 2B-B bus. An interlock prevents paralleling these two sources and resulting in both supply breakers tripping and the bus being de-energized. This generated a blackout signal that started all four emergency diesels generators (EDGs). All the EDGs started as required, only the 2B-B loaded onto its associated shutdown bus, as expected, because of the bus had been de-energized. The other busses (1A-A, 1B-B, and 2A-A) remained energized and the associated EDGs did not load. The 1A-A, 1B-B, and 2A-A EDGs were shutdown and returned to a standby condition. The 2B-B EDG continued to power the 2B-B Shutdown Board while the licensee investigated the fast transfer problem. All systems functioned as required during this event except for the 2B-B fast bus transfer from the alternate to normal offsite power supply. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-07-18
45209 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-07-16 | 2009-07-17 17:31 | 2009-08-20 | POSSIBLE RADIOGRAPHER OVEREXPOSURE Texas Incident #8646 "On July 17, 2009, the Agency [Texas Department of Health] was notified by the licensee that they had been informed by their dosimetry processor that a radiographer had received an exposure exceeding the annual exposure limit. The licensee stated that the individual's thermoluminescent dosimeter was reading 9,000 millirem for the exposure period of June 9, 2009, through July 10, 2009. The licensee conducted a preliminary interview with the employee and was not able to determine how the exposure could have occurred. The radiographer stated that he had not received any dose rate alarms while performing his duties during the monitoring period. He also stated that his self reading pocket dosimeter had never indicated any unusual readings. The licensee's Radiation Safety Officer stated that the individual's duties during the exposure period were almost exclusively dark room operations grading film. The licensee is continuing to investigate and will provide additional information to the Agency [Texas Department of Health] as it becomes available." * * * UPDATE ON 8/13/2009 AT 1243 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "7/21/09 0830 Contacted the RSO. He stated that they had completed a review of the individuals daily exposure recorded for the previous 6 months and had not found any reason for the exposure. I asked him if they were going to seek any medical assistance for the individual involved. He stated that he was unsure of what action he should take in this area. I provided him with REACTS contact information. "7/21/09 1320 Received a call from the RSO. He stated that he had just received a call from his dosimetry processor informing him that the same individual's badge for the exposure period of May 10, 2009, and June 9, 2009, was 17,840 millirem. The RSO stated that he was making arrangements to have a medical exam for the individual done. He was also going to contact REACTS again to seek advice on how to proceed. "7/21/09 1530 The RSO for Radiographic Specialist contacted the Agency [Texas Department of Health] and stated that they had scheduled the worker for blood test and that REACTS had shipped him a study kit to analyze the workers blood to help determine if he had received the dose indicated by his badge. REACTS stated that it would take a few weeks after they received the sample to have the results. I told the RSO that the Agency [Texas Department of Health] is planning to conduct their investigation at his facility on July 29, or 30, 2009, and requested copies of the dosimetry processors reports for the individual. "7/21/09 1614 Received the dosimetry reports. The report for the June 2009 period indicates 9,470 millirem for the exposure period. The processor states that the reading appears normal and they cannot determine if the exposure is static or dynamic. No radioactive contamination was found on the film. The film for the May exposure period indicates 17,840 millirem and the reading also appears normal and they cannot determine if the exposure is static or dynamic. No radioactive contamination was found on the film. The RSO still believes that this is a badge only exposure. "Additional information "On August 6, 2009, the Licensee provided a copy of the Cytogenetic Biodosimetry report from Cytogenetic Biodosimetry Laboratories - REAC/TS performed on their employee reported as receiving the overexposure. The initial report indicated that the dose received was not significantly different from background. The Agency [Texas Department of Health] requested clarification of what REAC/TS used as a background. On August 12, 2009, the licensee provided a copy of a document from REAC/TS, which indicated that their background would be a dose of 14 rad for the study conducted. The Agency [Texas Department of Health] will perform an on-site investigation of the event on or about August 19, 2009." Notified the R4DO (Whitten) and FSME (McIntosh). * * * UPDATE ON 8/20/2009 AT1844 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On August 19, 2009, the Agency [Texas Department of Health] completed an on-site investigation with the licensee. The investigation was not able to determine how that much exposure was recorded on the individual's badge. The licensee presented the Agency [Texas Department of Health] with a copy of an email sent from the Cytogenetic Biodosimetry Coordinator at REAC/TS in which he stated that they found no evidence that an overexposure to this individual had occurred. The licensee stated that he would be requesting a dose assignment of 417 millirem for each of the two exposure periods of May and June 2009, reducing the TEDE for the year of 2009 to less than 5 rem." Notified the R4DO (Jones) and FSME (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-07-22
45208 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-07-16 17:15 | 2009-07-16 17:31 | 2009-07-16 | ALERT DECLARED DUE TO A FIRE IN AN ABANDONED COOLING TOWER An ALERT was declared at 1715 due to a fire lasting greater than 15 minutes. The fire is in an abandoned cooling tower (bldg X-633D) on the Department of Energy portion of the site. The fire is not in proximity to any safety related equipment. A request for assistance was made to Scioto and Adams counties Fire Departments. At 1917, the licensee reported that the fire was out and the firemen were removing siding and looking for residual hot spots. * * * UPDATE AT 2046 ON 7/16/2009 FROM TERRY SENSAWAY TO MARK ABRAMOVITZ * * * The fire is out and the ALERT has been terminated. Recovery operations are in progress and a fire watch will be stationed throughout the night. Notified R2DO (O'Donohue), R2 Deputy RA (McCree), NMSS (Weber), NMSS EO (Kotzalas), DHS (Kettles), FEMA (Biscoe), DOE (Parsons), HHS (Nunn), USDA (Timmons), and EPA (Threatt). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | OH | FUE |  | 76.120(a)(4) |  |  |  | 0 | 2009-07-16
45207 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-07-15 19:45 | 2009-07-15 20:18 | 2009-07-15 | LOSS OF CRITICALITY SAFETY CONTROLS FOR MATERIAL FOUND IN AN UNEXPECTED LOCATION "On July 15, 2009 at 1945 B&W Nuclear Operations Group in Lynchburg, Va. activated [its] Emergency Operations Center due to an issue in [the] Uranium Recovery facility. A Do-All Saw used for sectioning of fuel components was found to have a collection of cutting fluid with an unknown amount of HEU in an unfavorable geometry. The volume is estimated at 54 liters. All IROFS [Items Relied On For Safety] have been lost. A criticality is not considered imminent. The situation with the equipment is stable. "There were no radiological concerns with this event. There was no immediate risk or threat to the safety of workers or the public as a result of this event." The NRC Resident Inspector has been notified. * * * UPDATE AT 0043 EDT ON 7/16/09 BY BARRY COLE * * * The licensee terminated its ALERT at 0035 EDT on 7/16/09 after "mass control" was re-established for the HEU material in the saw cutting fluid. The mass control determination was based on sampling and analysis of the fluid which provided an HEU mass assay indicating that there was significantly less than a critical mass of material present. The licensee stated that the fluid will be removed in a controlled manner later today. The NRC Resident Inspector is onsite and has been notified. NRC Region 2 and HQ management informed via monitoring team. R2DO(O'Donohue), DHS(Doyle), FEMA(Kuzia), DOE(Parsons), USDA(Timmons), and HHS(Miller) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | VA | FUE |  | 70.32(i) |  |  |  | 0 | 2009-07-15
45206 | 0 | NANTICOKE COOK MEMORIAL HOSPITAL |  |  |  |  | 2009-03-15 | 2009-07-15 12:54 | 2009-07-15 | MEDICAL UNDEREXPOSURE DURING BRACHYTHERAPY "A prostate seed implant was performed on March 5th, 2009, using needles preloaded with I-125 seeds. After implanting a total of 61 seeds, 22 seeds were found and then retrieved from the bladder. The patient later returned for a pelvic CT for post implant dosimetry. This dosimetry revealed an under dosing of the prostate with a D90 dose less than 80% of the prescribed dose. The seed distribution error was caused by the position of the needles in respect to depth when the seeds were released. The patient received no ill effect, but requires further therapeutic radiation in order to complete the prescription. The patient is currently scheduled for a second seed implant to complete the therapy." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-07-21
45205 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-07-13 11:00 | 2009-07-14 22:18 | 2009-07-16 | TEMPORARY LOSS OF POWER TO TEN EMERGENCY NOTIFICATION SIRENS "On Monday July 13, 2009, at approximately 1100 PDT, Southern California Edison discovered a loss of the ability to activate 10 Community Alert Sirens (CAS) located on the Camp Pendleton Marine Corp Base. Prior to the discovery, the most recent test demonstrating operability of the sirens was performed on July 10, 2009, at approximately 1152 PDT. On July 13, 2009, at approximately 1130 PDT, SCE re-established the ability to activate the sirens. SCE is currently conducting an investigation to determine the cause of the problem, to try to ascertain the time that the loss of ability to activate the sirens occurred, and to identify the cause of the delay in reporting this event. SCE assumes the sirens were inoperable for greater than 48 hours, and therefore, is reporting this event as a loss of emergency offsite capability, in accordance with 10 CFR 50.72(b)(3)(xiii). "At the time of this report, Unit 2 and Unit 3 were operating at about 99 percent and 100 percent power, respectively." A CAS power panel was found with a tripped breaker. An investigation into the cause of the breaker trip is ongoing. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1354 EDT ON 7/16/09 FROM M. MCBREATY TO CHARLES TEAL * * * "During a follow up investigation, SCE identified information to indicate the loss of the ability to activate the 10 Community Alert Sirens located on the Camp Pendleton Marine Corp Base occurred at approximately 1800 PDT on July 10, 2009. Therefore, the sirens were inoperable for greater than 48 hours. Additionally, SCE verified that, prior to the discovery of the inoperable sirens, the most recent test demonstrating operability of the sirens was performed on July 10, 2009 at 1053 PDT (not 1152 PDT as initially reported)." The NRC Resident Inspector has been notified and will be provided with a copy of this report. Notified R4DO Vincent Gaddy. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-14
45204 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2009-07-13 03:03 | 2009-07-14 09:14 | 2009-07-14 | DEGRADED CONDITION DUE TO RCS PRESSURE BOUNDARY LEAK At 0303 EDT on July 13, 2009, while in Hot Standby Mode 3, operators at Millstone Power Station Unit 2 identified a leak in the vicinity of the "A" reactor coolant pump (RCP). The containment sump leakage trend indicated a leak rate of 0.03 gallons per minute. At 0540 EDT, chemical analysis confirmed the leakage to be from the reactor coolant system. Follow up inspections are in progress to determine the source of the pressure boundary leak. Operators have cooled the plant to Cold Shutdown Mode 5 in accordance with plant Technical Specification 3.4.6.2, Reactor Coolant Operational Leakage. The plant entered Cold Shutdown Mode 5 at 1601 EDT on July 13, 2009. The licensee stated that this report is late due to an administrative oversight. Licensee notified NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-07-14
45203 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2009-07-13 22:00 | 2009-07-14 01:46 | 2009-07-14 | LOSS OF ENS PHONE CIRCUITS AND SOME COMMERCIAL COMMUNICATION CAPABILITY "At 2200 CDT on 7/13/09 it was discovered the Emergency Notification System (ENS) phone lines in the Unit 1 and Unit 2 control rooms and the Technical Support Center were not functioning. Additionally, the Health Physics Network is not functioning. This discovery occurred during extent of condition troubleshooting when it was determined that local cellular phone and land-line phone service was unavailable in some local areas. A successful land-line phone call to the NRC Operations Center was completed following this discovery, All State and local authorities required to be contacted in the event of an Emergency Class declaration were contacted via land-lines and made aware of the situation. "Also at this time, the Dedicated Emergency Fax/Voice System (DEF/VS) is unable to fax to the Arkansas Department of Health (ADH) Little Rock Operations Center. Land-line voice communications to Little Rock have been verified. The Russellville ADH office is able to receive fax notifications from ANO and can ensure that all state and local agencies can be notified. The Russellville ADH office will remain manned until the situation is resolved. "At approximately 2345 CDT, it was determined that the NRC Operations Center was unable to directly contact either Unit 1 or Unit 2 control room. "The cause of the loss of communications is suspected to be a major fiber-optic line being cut In Morrilton, Arkansas. No estimate of time for repairs Is available at this time." The licensee has established that communication capability exists via either radio or phone with local emergency response and law enforcement organizations. The licensee can still contact the NRC via commercial circuits but cannot receive calls from the NRC. A dedicated cell phone line has been established by the licensee to facilitate communication from the NRC if necessary. State and local authorities have been informed of the problem. The NRC Senior Resident Inspector has been notified and has responded to the site. * * * UPDATE BY HUFFMAN AT 0500 EDT ON 7/14/09 * * * The ENS lines and commercial phone service have been restored to ANO and verified operable. R4DO (Gaddy) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-14
45202 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-06-18 | 2009-07-13 15:04 | 2009-07-13 | MINNESOTA AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Minnesota via email: "[On June 18, 2009, at a temporary job site,] the licensee was conducting radiography of circumferential welds. At approximately 1220 hrs, the radiographers heard a 'bang' from inside the horizontal heavy wall vessel. The licensee was using a 42 Curie Cobalt-60 source in an AEA 680 exposure device. The lead radiographer immediately attempted to retract the source but could not move the control handle. Thinking that the problem was the result of a tight radius, the radiographer attempted to withdraw the guide tube from the tank. That effort was abandoned when the guide tube began to slide out of the vessel. However, the radiographer identified a dent in the guide tube that was approximately 18 inches from the far end. The source was shielded with 3/8 inch lead plates. "The radiographer conducted a survey and calculated the exposure to hammer out the crimp in the guide tube. After consultation with the Radiation Safety Officer, a radiographer approached the guide tube, turned it 1/4 of a turn, and hit it once with a hammer. The source was then successfully retracted. "Total doses for the retrieval were 190 mrem to the lead radiographer and 20 mrem to the second radiographer. The damaged guide tube has been removed from service. "The root cause of the problem has been determined to be that the guide tube was extended to its fullest length; therefore, the tension and/or weight of the tube caused the stand to fall over and crimp the guide tube. The corrective action was to add an additional guide tube and to secure the stand with weights to prevent tipping." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2009-07-16
45201 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-05-20 13:00 | 2009-07-13 15:00 | 2009-07-13 | MINNESOTA AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Minnesota via email: "On Wednesday, May 20, 2009, at approximately 1300 hrs, a licensee was performing radiography at a temporary job site using a 41 Curie Ir-192 source when the stand holding the guide tube fell from its secured position and landed on the guide tube near the camera, crimping the guide tube. The radiographer attempted numerous times to retract the source and was unsuccessful. The radiographer performed radiation surveys to reset the boundaries and contacted the management. The Radiation Safety Officer was also contacted. "The NDT [Non-Destructive Testing] manager used steel plates for shielding in order to disconnect the guide tube from the camera. Once disconnected, the NDT manager proceeded to the collimator end of the guide tube and pulled the guide tube to allow the source to pass through the crimped portion. When the source passed through the kink, the radiographer cranked the source into its shielded position. The NDT manger received 121 mrem, the radiographer received approximately 40 mrem. Leak tests results indicate that the source was not effected. The guide tube has been discarded. "The root cause of the event was determined to be that the radiographers failed to ensure that all four legs of the magnets on the ring stand used to support the guide tube were not in contact with metal due to the curvature of the surface. The weight of the guide tube caused the stand to fall and to crimp the guide tube. " This is an update to EN #45083, dated May 25, 2009. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2009-07-16
45200 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2009-07-13 07:00 | 2009-07-13 11:37 | 2009-07-13 | PRESSURE BOUNDARY LEAKAGE IDENTIFIED "On 07/13/2009 at 00:38 EDT a planned manual reactor trip was initiated on Unit 2 based on increased, unidentified RCS leakage. The RCS leakage had increased over a four day period. The downpower was initiated at 21:32 EDT from 100% power and proceeded in a controlled manner to 25% power. The reactor was manually tripped at 00:38 EDT, as planned. Following the reactor trip, EOP-1, Standard Post Trip Actions, and EOP-2, Reactor Trip Recovery procedures were completed and the unit was stabilized in Mode 3. Decay heat was removed by the Steam Bypass Control System (SBCS) to the condenser. The Main Feedwater Pump unexpectedly tripped on low suction pressure just prior to the reactor trip, but was recovered prior to levels reaching the Auxiliary Feedwater Actuation (AFAS) setpoint. There were no further major equipment failures identified post trip. "On 7/13/2009 at 07:00 EDT a Containment walkdown confirmed the leak was caused by a J-joint weld defect on the 2B2 RCP Seal injection line. The leak is classified as reactor coolant pressure boundary leakage. "The plant is in the process of cooling down to enter Mode 5 as required by Technical Specification 3.4.6.2.a. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(A). Additional investigation is being performed to determine the cause of the leak." The initial leak rate was less than 0.2 gpm. The repair will require taking the plant to a reduced inventory. The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-07-13
45199 | 0 | US AIR FORCE |  |  |  |  | 2009-06-22 | 2009-07-13 09:43 | 2009-07-13 | LOST AMERICIUM-241 SOURCES DUE TO AIRCRAFT CRASH On June 22, 2009, an F-16 crashed in a remote area in the Great Salt Lake test range in the area of the Utah and Nevada borders near Hill AFB. The aircraft was carrying a Sniper Laser Targeting Pod with two Am-241 sources each with an activity of 4 microcuries (8 microcuries total). Following investigation of the crash site and aircraft remnants, the licensee has determined that the sources are lost. The licensee has previously notified NRC Region IV (Browder) of this occurrence. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-07-13
45198 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-07-12 07:20 | 2009-07-12 09:56 | 2009-07-12 | LAW ENFORCEMENT NOTIFIED OF DISCOVERY OF FIREARM DURING X-RAY SCREENING "At 0120 on 7/12/09, Turkey Point Nuclear Power Station Security personnel discovered a hand gun in a personal bag being processed through an x-ray search machine in the nuclear entrance building. Security personnel immediately established control of the weapon and the owner. The owner of the weapon is a permanent employee of Florida Power and Light's Turkey Point Nuclear Power Station. Miami-Dade Police (Local Law Enforcement Agency) were contacted by Security and responded to the station. Upon arrival, LLEA established control over the weapon and the owner. At this time, LLEA investigation is still in progress. Owner has been determined to hold proper permits for the weapon. No further information is available at this time. Updates will be provided as required as investigation is concluded. "NRC Senior Resident Inspector has been notified. "This notification is being conducted in accordance with 10CFR50.72(b)(2)(xi) for notification to an outside government agency." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-07-12
45197 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-07-12 01:35 | 2009-07-12 06:38 | 2009-07-12 | SAFEGUARDS EVENT - VULNERABILITY RELATED TO VEHICULAR CONTROL Licensee discovered a vulnerability in a safeguard system related to vehicular control for which compensatory measures were not employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-07-12
45196 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-07-12 01:48 | 2009-07-12 02:11 | 2009-07-13 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF OFFSITE POWER At 0135 EDT on 07/12 both Startup Transformers "SA" and "SB" were deenergized due to the loss of the 34.5kV power distribution lines (offsite power). The licensee declared an Unusual Event at 0148 EDT based on the loss of power to both transformers for greater than 15 minutes (EAL MU1). As a result of the loss of offsite power, the Unit automatically scrammed with all control rods fully inserting. Both Emergency Diesel Generators EDG #1 and EDG #2 auto started and are carrying vital loads. The Unit is stable in Hot Shutdown with decay heat removal via the Isolation Condenser. The licensee reported that the transient may be due to a possible lightning strike caused by adverse weather. The licensee informed the NJ State Police and the NRC Resident Inspector. * * * UPDATE AT 0413 EDT ON 07/12/09 FROM WILL TOLBERT TO DONALD NORWOOD * * * At 0405 EDT on 07/12 the licensee terminated the Unusual Event based on restoration of offsite power and reenergizing both Startup Transformers. The licensee informed the NJ State Police and the NRC Resident Inspector. Notified R1 (Lew), EO (Holian), IRD (Gott), FEMA (Austin) and DHS (Inzer). * * * UPDATE AT 0413 EDT ON 07/13/09 FROM CALVIN TAYLOR TO DONALD NORWOOD * * * Licensee changed one reporting requirement from 50.72(b)(3)(v)(B) to 50.72(b)(3)(iv)(A). Notified R1DO (Dentel). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | POT UNABLE TO SAFE SD | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(iv)(A) | 0 | 2009-07-12
45195 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2009-07-10 20:00 | 2009-07-12 00:08 | 2009-07-14 | UNPLANNED CONTAMINATION EVENT REQUIRING ADDITIONAL RADIOLOGICAL CONTROLS (RESPIRATORS) FOR MORE THAN 24 HOURS "An unplanned contamination event occurred on 10 July 2009. This is a reportable event in accordance with 10CFR40.60 sub paragraph (1) based on an unplanned event that resulted in additional radiological controls being required for more than 24 hours. The 24 hour period ended at 2000 CDT on 11 July 2009 (the reported event). The additional control imposed was the wearing of air purifying respirators on the fourth floor of the Feed Materials Building. The location of the event was the Feed Materials Building fourth floor. The Feed Materials Building converts milled uranium oxide material to uranium hexafluoride by using a dry process. Air samples from the fourth floor were analyzed and the airborne radioactivity averaged approximately 6.11E-11 microcuries/ml. The airborne contaminant was natural uranium ore concentrate and the physical form is a light microscopic dust. The processes in the area of elevated levels of airborne radioactivity have been secured and potential leakage paths are being investigated. "The licensee will notify NRC Region II." HOO Note: See similar Event Numbers 44857, 44871, 45058, and 45163. * * * UPDATE FROM MICHAEL GREENO TO HOWIE CROUCH @ 1628 EDT ON 7/14/09 * * * The isotope responsible for the increased controls was natural uranium in the chemical form of uranium tetraflouride (UF4); green salt. The amount of unplanned contamination that was released in the form of green salt was estimated to exceed 5 times the ALI [Annual Limit on Intake] (3 grams). The airborne activity averaged approximately 6.11E-11 microCuries/ml. (5.0E-11 microCuries/ml is 30% of 1 DAC [Derived Air Concentration]). The licensee states that bioassay sampling of any potentially exposed individuals will be performed within the routine sampling frequency, but prior to 7/30/09. The licensee has notified NRC Region II. Notified R2DO (O'Donohue) and NMSS EO (Kotzalas). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2009-07-12
45194 | 0 | ELK RUN COAL COMPANY |  |  |  |  | 2009-07-09 10:00 | 2009-07-10 20:03 | 2009-07-10 | LOSS OF CONTROL OF RADIOACTIVE DENSITY GAUGE The licensee reported that they were informed by a scrap material yard that a load of material from their facility set off a radiation detector. The scrap yard Radiation Safety Officer (RSO) discovered that a piece of pipe had a density gauge still mounted on it. The scrap yard RSO obtained the proper permits and appropriately packaged the gauge and returned it to the licensee RSO. The source did not appear to be damaged and the leak test performed by the licensee RSO indicated no leakage. Through employee and contractor interviews, the licensee does not believe there were any personnel overexposures. The Cs-137 source is a 7062 BP Kay-Ray that had an original source strength of 100 mCi. The estimated age of the source is 20 years so the current strength is in the 60-70 mCi range. The licensee has the source shielded and in secure storage awaiting shipment to the manufacturer (now Thermo-Electron) for proper disposal. The licensee has been in contact with NRC Region 1 (Miller) over this incident. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-07-10
45193 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2009-07-10 12:31 | 2009-07-10 13:40 | 2009-07-10 | ELEVATED TRITIUM LEVELS FOUND IN ON-SITE WELL "Exelon has issued a news release due to elevated levels of tritium found in an on-site exploratory well at the Peach Bottom Atomic Power Station. The elevated levels of tritium were found in an area adjacent to the Peach Bottom Unit 3 Turbine Building." Tritium levels were measured as 123,000 picoCuries per liter. The licensee notified the NRC Resident Inspector, Pennsylvania Emergency Management Agency, Maryland Emergency Management Agency, and the counties of York, Cecil, Lancaster, and Chester. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-07-10
45192 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2009-07-08 | 2009-07-10 10:46 | 2009-07-10 | AGREEMENT STATE REPORT INVOLVING UNPLANNED CONTAMINATION The following information was received from the State of Oklahoma via email: "An incident involving veterinary use of 3.7 milliCuries of Iodine 131 occurred at Oklahoma State University (OSU) on the afternoon of July 8. OSU holds a broad scope license OK-00237-03 and is located in Stillwater, OK. This was the licensee's first such treatment of a cat since an incident late last Fall where a veterinarian who was not an authorized user did a similar injection and stuck himself with the needle after the injection. An inspector from Oklahoma DEQ was present for the treatment, though not in the actual injection room because of space concerns. The University RSO directly observed the procedure and reports that the technician administering the dose appeared to follow the procedure precisely. She did not report anything unusual about the injection, though she observed that the cat (whose body was enclosed in a bag) struggled somewhat. The problem was discovered when a survey of the technician was done, and contamination was discovered on protective clothing covering the hand and the outer surface of the opposite forearm. "Licensee measurements indicate that the cat reads 0.25 mrem/hr at 30 cm from the body, while measurements in the area where the cat was injected read over 60mrem/hr without the cat present. The licensee believes that the cat did not receive the majority of the dose and that the majority of the Iodine ended up on the injection shelf and the floor of the room. Thyroid screening of the technician, the RSO, and a control person with NaI probe does not indicate any internal absorption. The technician does not have any removable contamination on her skin, and meter readings of her skin are at background. A whole body scan at a hospital is being scheduled for her. She was given 0.13 cc of SSKI mixed with 2 ounces of water shortly after the incident. "The area where the incident occurred has been closed off. The cat is being maintained in a cage in the room. The syringe assembly, its carrying case, and all protective garments worn by the technician have been preserved. The licensee is investigating, getting the advice of a team of experts. "The licensee has not reached a conclusion of the cause of the problem, theories include mechanical failure in the preloaded syringe assembly or that the struggling cat may have caused the needle to stick out through the subcutaneous injection site causing the dose to be ejected outside the cat." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2009-07-15
45191 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-07-08 22:45 | 2009-07-08 23:25 | 2009-07-08 | OFFSITE NOTIFICATION - OSHA CONTACTED DUE TO ON-SITE FATALITY "A non-contaminated individual was transported by ambulance from the Catawba Nuclear Station parking lot to a local hospital due to a personal illness. The individual was pronounced dead at the hospital. Catawba Nuclear Station is notifying [Occupation Safety Health Administration] OSHA of an on-site fatality." Licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-07-08
45190 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-07-08 10:13 | 2009-07-08 16:05 | 2009-07-08 | VALID EMERGENCY DIESEL GENERATOR ACTUATION "On July 8, 2009, at 1013 hours, during planned maintenance activities, electrical power was lost to the 4160V emergency bus E-2. The power loss to emergency bus E-2 affected both Unit 1 and 2. Emergency diesel generator #2 automatically started and re-energized the E-2 bus. "The loss of power to E2 resulted in Unit 1 Primary Containment Isolation System (PCIS) Group 2 (i.e., Drywell Equipment and Floor Drain, Residual Heat Removal (RHR) Discharge to Radwaste, and RHR Process Sample), Group 3 (i.e., Reactor Water Cleanup), Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems), and Group 10 (i.e., air isolation to the drywell) isolations. The actuations of PCIVs were completed and the affected equipment responded as designed. Per design, no Unit 2 safety system group isolations or actuations occurred. "Other Unit 1 actuations included the Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation), and the automatic start of Standby Gas Treatment (SGT) System trains A and B and the Control Room Emergency Ventilation System (CREV). Systems functioned as designed. "Safety systems functioned as designed following the de-energization of bus E-2. The safety significance of this event is minimal. Plant systems responded as designed. The cause of the event is under investigation. "Reporting requirements met by this notification: 10 CFR 50.72(b)(3)(iv)(A). The NRC Resident Inspector has been notified." Licensee was conducting maintenance on the switchgear at the time of the loss of power. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-07-08
45189 | 0 | NEXTERA ENERGY DUANE ARNOLD |  |  |  |  | 2009-05-10 | 2009-07-08 13:10 | 2009-07-08 | PART 21 - SAFETY RELATED CONTROL VALVE SPRING ACTUATOR SIZED INCORRECTLY "NextEra Energy Duane Arnold (NextEra Energy) makes the following notification under 10 CFR 21.21(d)(3)(i) of a failure to comply found during surveillance testing. The specific issue is insufficient clearance between the spring and the inside of the cylinder of the actuator for a Miller series A63B2N air cylinder actuator for a control valve (CV-1956A, Control Building Chiller Discharge to Emergency Service Water Isolation). The resulting improper clearance caused an increase in running load, which caused the valve to become stuck in the closed position. The valve failure was discovered on May 10, 2009. The control valve actuator was supplied by Flowserve US, Inc, as a basic component in April, 2008 for use at the Duane Arnold Energy Center. Flowserve has indicated that the actuator was procured as a commercial grade item and dedicated for safety related installation under their QA program. The valve and actuator were installed on April 17, 2009. "The lack of spring to actuator clearance resulted in a loss of capability of CV-1956A to perform its intended safety function of providing a safety related seismic discharge path for cooling water from the safety related Control Building Chiller, 1V-CH-1A. The Chiller was declared inoperable as a result of this failure to comply and, on July 1, 2009 was determined to have resulted in a substantial safety hazard. "The actuator for CV-1956A was rebuilt with a replacement spring having proper dimensional clearance and higher opening force capability. The actuator has been installed by a plant modification and the control building chiller has been returned to an operable status. "The air operated valve assembly supplier, Flowserve US Inc, was contacted on July 1, 2009 to discuss NextEra Energy's findings. "NextEra Energy has verified that no other safety related actuators with the incorrect valve actuator cylinder to spring clearances have been installed at the Duane Arnold Energy Center." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-07-08
45188 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-07-07 00:54 | 2009-07-07 01:57 | 2009-07-09 | 4-HOUR REPORT DUE TO NOTIFICATION OF OHIO EPA BECAUSE OF BOILER OPACITY LIMIT BEING EXCEEDED "At 2130 hours, 07/06/09, the PORTS Plant Shift Superintendent's (PSS) Office was notified of an operational upset at the X-600 Steam Plant Facility due to a loss of power on the #3 (operating) Boiler. The operational upset resulted in three separate six minute periods, where the permissible opacity limit was exceeded, while power was being restored to the boiler. The PORTS PSS Office notified the Ohio Environmental Protection Agency (OEPA) of this incident, at 0054 hours, 07/07/09. This notification to another government agency is reportable to the NRC as a 4-hour Event, per the United States Enrichment Corporation (USEC) Nuclear Regulatory Event Reporting Procedure UE2-RA-RE1030, Appendix D, Section P (Miscellaneous) which states: 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials'." The licensee notified the Paducah NRC Resident Inspector. * * * RETRACTION FROM ERIC SPAETH TO JOE O'HARA AT 1427 EDT ON 7/9/09 * * * "PORTS [Nuclear Regulatory Affairs] NRA has reviewed the basis for the above NRC event notification and recommends that event notification #45188 be retracted. The following provides the basis for this recommendation. NUREG-1022, Event Reporting Guidelines 10 CFR 50.72 and 50.73 was reviewed. In essence, the following sentence from the NUREG provides sufficient clarification of the reporting criteria to assess the applicability of the steam plant opacity exceedances: 'The purpose of this criterion is to ensure the NRC is made aware of issues that will cause heightened public or government concern related to the radiological health and safety of the public or on-site personnel or protection of the environment.' The significance of opacity exceedances as they might impact the public or on-site workers was discussed with environmental compliance personnel. It was concluded that beyond any regulatory issues, opacity exceedances of limited duration pose no significant health or environmental concerns. Based on the specifics of this event and the additional guidance provided by the NRC, more specifically that NRC is most concerned about events or situations that would cause heightened public or government concern, the opacity exceedances reported to the OEPA should not trigger a 4 hour NRC report." The licensee notified the NRC Resident Inspector. Notified R2DO(Nease) and NMSS EO(Tschiltz) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2009-07-07
45187 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-07-01 | 2009-07-06 16:55 | 2009-07-06 | LOST SHIPMENT OF YTTRIUM Y-90 The following was provided from the Commonwealth of Massachusetts via fax: "Shipment [was] made [by common carrier] from North Billerica to Stanford Medical Center, Palo Alto, CA on 6/23/09. The quantity was 10 milliCuries of Y-90. The package was reported missing as of July 1, 2009." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-07-09
45186 | 0 | VISTEON CORPORATION |  |  |  |  | 2009-07-06 | 2009-07-06 14:25 | 2009-07-06 | LOST TRITIUM EXIT SIGNS The licensee reported 108 Tritium exit signs are unaccounted for and are considered lost and unrecoverable. The signs were used at various locations where Visteon, an auto parts supplier, has outlet stores. Based upon conversations with the NRC, the licensee has spent approximately three weeks attempting to account and locate the whereabouts of the 108 Tritium exit signs without success. The licensee did account for one sign with 9.5 curies of Tritium and 4 other signs with 11.5 curies of Tritium. The licensee has spoken to NRC employees A. McIntosh and K. Lambert regarding the issue. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-07-06
45185 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-07-06 07:12 | 2009-07-06 08:09 | 2009-07-06 | UNAVAILABILITY OF TSC VENTILATION SYSTEM AND CHARCOAL FILTER FOR SCHEDULED MAINTENANCE "At 0712 on Monday, July 6, 2009, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system air conditioning and filtration systems were removed from service for scheduled preventive maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system maintenance is scheduled to complete at 1600 on Monday, July 6, 2009. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." * * * UPDATE FROM JAMES SHAW TO JOE O'HARA AT 1640 EDT ON 07/06/09 * * * "The TSC Ventilation System and Charcoal Filter have been returned to functional status at 1517 EDT on Monday, July 6, 2009. "This follow up notification is being made to provide closure from the initial notification under 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility. "The licensee has notified the NRC Senior Resident Inspector - Jay Lennartz." Notified the R3DO(Passehl). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-07-06
45184 | 0 | GAMMA KNIFE CENTER OF THE PACIFIC |  |  |  |  | 2009-07-02 14:00 | 2009-07-03 18:42 | 2009-07-17 | MEDICAL EVENT - GAMMA KNIFE MISADMINISTRATION A gamma knife treatment was prescribed for a patient being treated for multiple brain metastatic sites using an 8 mm collimator. The prescribed dose was 24 gray. The treatment was prescribed for 7 discrete sites in the brain. After the second discrete site had been treated it was found that an 18 mm collimator was being used to administer the treatment instead of the prescribed 8mm collimator. After discovery, the collimator was changed to the 8 mm collimator. Treatment to the remaining 5 discrete sites was administered with the 8 mm collimator. Both the patient and the patient's physician were notified of the use of the wrong collimator. The licensee states that there should be no clinical effects to the patient as a result of this misadministration. The previous patient had been treated using the 18 mm collimator as the prescribed collimator. Investigation into this event is continuing and a written report will follow. In an effort to prevent recurrence, the licensee will send a notice to all authorized users, neurosurgeons and medical physicists that they should each independently check collimator size before each treatment is started. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 1551 ON 7/17/2009 FROM RONALD FRICK TO MARK ABRAMOVITZ * * * "The use of the 18 mm collimator instead of the 8 mm collimator increased the treatment site dose by 3%. The larger collimator caused the volume of each of the two treatment areas to increase by 2.35 cm3 [cubic centimeters]. This additional tissue received a dose of 24 Gy. If the correct collimator had been used, this tissue would have received a dose of approximately 4.3 Gy." Both the physician and patient have been notified by the licensee. Notified the R4DO (Gaddy) and FSME (Reis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2009-07-09
45183 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2009-07-03 13:05 | 2009-07-03 14:32 | 2009-07-03 | REACTOR TRIP RESULTING FROM TURBINE TRIP A reactor trip occurred at 1305 EDT and a Connecticut "echo" event was declared at 1315 EDT. The load dispatcher reported a loss of a 115 kV line at the time of the trip which may have caused and/or contributed to the turbine trip. The turbine trip may have resulted from a loss of B12 MCC (motor control center) which carries stator cooling pumps or a momentary interruption to non-vital instrument panels VR11 and VR21. The following events occurred: "1) loss of non-vital power may have caused the turbine trip, "2) RPS [Reactor Protective System] actuation from turbine trip, "3) system operator reported brief loss of 115 kV line immediately prior to trip, "4) Primary PORV [Pilot Operated Relief Valve on the pressurizer] lifted [at its setpoint of 2397psia], "5) Steam generators reached a high level, and "6) Main feed pump manually tripped due to high steam generator level and manually started AFW pumps [Auxiliary Feedwater Pumps]. "Note: The 'C' charging pump was inoperable at the time of the event." All control rods fully inserted on the trip. The plant is in its normal shutdown electrical lineup. Decay heat is being dumped to the main condenser and steam generator level is being maintained with the AFW pumps. There was no effect on Unit-3. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-07-03
45182 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-05-13 | 2009-07-02 23:28 | 2009-07-02 | AGREEMENT STATE REPORT - FETAL EXPOSURE FROM RADIOIODINE THERAPY The following report was received via facsimile: "Patient was administered 54.1 mCi of I-131 on 3/30/2009. Patient had a false negative pregnancy test on 3/30/2009. Patient found out on May 13, 2009 that she was 9.5 weeks pregnant. Therefore, the therapy dose was given 5 days post-conception. Dose Eq to embryo/fetus = 11.9cGy. Dose Eq to fetal thyroid = 0.97cGy "PA DEP Bureau of Radiation Protection was notified in writing, dated May 22, 2009, [from] the Radiation Safety Officer. "The State has an inspection scheduled sometime in the future and will continue to keep NRC informed of the status of our investigation." PA event: PA090024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-07-08
45181 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-07-02 14:15 | 2009-07-02 18:40 | 2009-07-02 | HPCS INOPERABLE DUE TO LOGIC CARD FAILURE "On July 2, 2009, at 0100 hours (CDT), the Main Control Room received an alarm associated with a failure of the Nuclear System Protection System (NSPS) Self Test System (STS). The indicated failure was on a High Pressure Core Spray (HPCS) system logic card. The card was removed and testing of the card, completed at 1415 hours, determined that the failure was on a circuit that would have prevented the automatic initiation capability of HPCS. Since HPCS is an emergency core cooling system and is a single train safety system, this is reportable under 50.72 (b)(3)(v)(D). It is unknown at this time what caused the failure and plans are in progress to repair or replace the card." The logic card is being sent out for repairs. The HPCS system will remain inoperable until the card is repaired and replaced. There is no estimate at this time as to when the card will be replaced. The licensee will notify the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-07-02
45180 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2009-05-19 16:09 | 2009-07-01 16:19 | 2009-07-01 | INVALID FEEDWATER SYSTEM ACTUATION WHILE SHUTDOWN "On 5-19-09 ONS [Oconee Nuclear Station] Unit 3 was in Mode 3 during startup from a refueling outage. At 1609 EDT the 3A Motor Driven Emergency Feedwater Pump (MDEFWP) unexpectedly started when the control switch was placed in the AUTO2 position as part of system alignment prior to unit startup. Investigation found that the impulse line for the hydraulic oil pressure switch on the operating 3A Main Feedwater Pump was clogged, causing sensed pressure to read below setpoint. Repositioning the control switch enabled the 3A MDEFWP auto start circuitry, which immediately actuated due to the pre-existing false low pressure indication. Several other redundant indications validated that the pressure signal to the pressure switch was false and that actual hydraulic oil pressure remained above the pressure switch setpoint. Although the pressure switch did see low pressure in the impulse line, the actuation is considered invalid since the signal was based on a false reading that did not represent actual plant conditions. "Therefore this report is being made under 10 CFR 50.73(a)(1) and 50.73 (a)(2)(iv)(A). "Per NUREG-1022, Rev. 2 the following information is requested: A) The specific train(s) and system(s) that were actuated. 3A Motor Driven Emergency Feedwater Pump (MDEFWP) which feeds the 3A Steam Generator (SG). B) Whether each train actuation was complete or partial. The train actuation was considered complete. The pump started per the signal and operated as required/expected in response to the signal. This pump is the only component in the train which receives a specific signal as part of the actuation circuitry. C) Whether or not the system started and functioned successfully. The 3A MDEFWP started and the system functioned successfully. The EFW control valve (3FDW-315) is set to control at 30 inches (SG startup level) versus 25 inches for Main Feedwater control. Therefore the SG level increased and the train then controlled at approximately 30 inches while an investigation determined the reason for the actuation (as explained above). The 3A MDEFWP was stopped at 2050 EDT and returned to normal status. "Initial Safety Significance: Due to low feedwater demand at the time, there was little impact on the unit. Since the SG level was maintained above the normal control system setpoint, Main Feedwater flow was automatically reduced to compensate for the EFW flow. The 3A MDEFWP and associated pressure switch/actuation circuit were declared inoperable during pump shutdown and restoration to normal. "Corrective Action(s): After troubleshooting identified the clogged impulse line, it was isolated and cleared. The 3A MD EFWP and the associated pressure instruments were returned to service." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-07-01
45179 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-06-30 16:00 | 2009-07-01 13:12 | 2009-07-01 | SAFETY EQUIPMENT FAILURE OF THE CRITICALITY ALARM SYSTEM "The public address system (criticality accident alarm) was impaired for a portion of the Building 310 warehouse and a subcontractor trailer. The cause of the impairment was determined to be the result of a contractor drilling into a public address system speaker wire while installing fire protection components in the Building 310 warehouse. This created an electrical short which rendered the speakers inoperable for a portion of the Building 310 warehouse and a subcontractor trailer. The speaker wire was obscured from view by a structural beam. The system was repaired, tested, and placed back into service by 1721 hours (EDT) on 6/30/2009." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2009-07-01
45178 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-06-30 15:13 | 2009-06-30 21:49 | 2009-06-30 | POTENTIAL MEDIA INTEREST DUE TO FORCED OUTAGE "On June 30, 2009, at 1513 PDT, Unit 2 commenced a ramp[-down] in accordance with the annunciator response guidance to enter Operating Procedure (OP) Abnormal Procedure AP-25 due to loss of forced cooling to main transformer bank (MTB) C-Phase transformer. At 1538, Unit 2 was separated from the grid in accordance with plant OP AP-25 initiation of a main generator unit trip. At 1554 PDT, the Reactor Trip Breakers (RTBs) were manually opened per OP AP-25 Step 24.j. [Reactor] power was being held in Mode 2 at about 3% reactor power per the procedure when the RTBs were opened. "The investigation into the cause is continuing. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi), Offsite Notification, as Pacific Gas and Electric plans to make a news release regarding the event that may raise media interest." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-30
45177 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-06-30 | 2009-06-30 17:52 | 2009-06-30 | AGREEMENT STATE REPORT - SAFETY FUNCTION FAILURE The following information was received via facsimile: "The electronics are not working on a [thickness] gauge on the Z-34 press. The equipment is out of use. The [Integrated Industrial Systems] gauge [is a Model #SS-3A] with a serial number [of] #9834LX; 1000 milliCurie Am-241. A potential cause is the source moved." The licensed contractor RSI (Radiometric Services and Instruments) was contacted to fix the thickness gauge. A Commonwealth of Massachusetts investigation is pending. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-07-03
45176 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-06-30 11:30 | 2009-06-30 17:27 | 2009-09-17 | AGREEMENT STATE REPORT - POTENTIAL WORKER OVEREXPOSURE The following information was received via facsimile: "A worker was working in a hot cell when a F-18 [radio-isotope] was mistakenly delivered to the hot cell. [The] initial estimated worker dose [was] 100 Rad extremity dose and 20 Rad to the whole body (upper arm). The dosimeter has been sent to Landauer for immediate processing. [The] worker has been taken off Rad work and is being monitored" A Commonwealth of Massachusetts investigation is pending. * * * UPDATE ON 8/13/2009 AT 1130 FROM TONY CARPENITO TO MARK ABRAMOVITZ The following report was received via e-mail: "On 6/30/09, 1.6 Curies of Fluorine-18 was mistakenly delivered to a shielded vial within the cyclotron facility hot cell while a worker was performing routine maintenance within the hot cell. Delivery was intended for a different hot cell. The total worker exposure time was less than 3 minutes. The worker was removed from radiation work and dosimeters were sent out for immediate processing. Same day notification was made from the licensee to the Agency [Massachusetts Radiation Control Program]. The licensee submitted an independent consultant written report, dated 7/8/09, to the Agency [Massachusetts Radiation Control Program] on 7/27/09. The worker's effective dose equivalent was conservatively determined to be not more than 0.170 Rem, the maximum extremity not more than 26.9 Rem, and the eye dose equivalent not more than 1.2 Rem. These dose values were assigned to the worker. The worker was returned to radiation work with cumulative dose closely monitored. "Licensee's formal descriptions of cause, contributing and precipitating factors, and corrective actions are pending. "The Agency [Massachusetts Radiation Control Program] considers this situation to still be OPEN." Notified the R1DO (Cook) and FSME (McIntosh). * * * UPDATE ON 9/17/2009 AT 0949 FROM CARPENITO TO HUFFMAN * * * The following update was received via e-mail: "9/16/09 Update: A subsequent on-site Agency inspection was performed. On 8/27/09, the licensee submitted report of cause, contributing and precipitating factors, and corrective actions. "Cause: Pre-event re-configuration of transport tubing during an earlier calibration effort was not returned to original configuration and operators were not aware of the routing change. "Precipitating and Contributing Factors: Licensee procedures related to use of personnel dosimeters, functioning survey instruments, and hot cell door closure, were not followed. "Corrective Actions: Licensee to implement procedural changes and retraining of staff. "The Agency considers this situation to be closed." Notified the R1DO (Jackson) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-07-03
45175 | 0 | LANGAN ENG. AND ENVIR. SERVICES INC |  |  |  |  | 2009-06-29 02:15 | 2009-06-30 12:24 | 2009-06-30 | DAMAGED TROXLER MOISTURE DENSITY GAUGE "Based on discussion between field personnel (authorized nuclear gauge user) and [the licensee], the rubber-tire wheels of a piece of construction equipment ran over [a Troxler] gauge. [The licensee] personnel, with assistance from the contractor, immediately cordoned off the area so that the appropriate steps could be taken to access the situation. "Based on the pictures that were sent to [the licensee] and conversations with the field personnel, [the licensee] does not believe that the gauge was damaged severely enough to cause a radiation leak from the gauge. "The source rod was inside the inner protective housing (i.e. shield) when it was damaged. It appears that only the outer plastic casing was cracked and the index rod was snapped. The inner protective housing (i.e. shield) protecting the CS-137 source and the Americium 241 source protective cover appear to still be intact. The source rod was not bent. The sliding block at the bottom of the gauge is fully closed. "Since the index rod locks the source rod in place, [the licensee] instructed field personnel how to temporarily restrain the index rod and therefore keep the source rod inside the protective shield. After properly securing the source rod, [the licensee] had field personnel place the damaged gauge inside the yellow DOT transport box. The transport box / gauge was then properly secured inside a large steel container (dedicated to [the licensee]) at the construction site. Only [licensee] personnel have access to the steel container. "[The licensee] sent down a radiation meter to field personnel via FedEx overnight. The radiation meter only showed that the radiation level immediately next to the gauge was 4 mrem. The measured radiation level several feet away from the gauge was about 0.12 mrem. No radiation was measured outside of the steel container. "[The licensee has] scheduled for the gauge to be picked up on Thursday by [licensee's] repair service firm. The repair service will perform their own leak test in the field prior to transporting the gauge back to their shop. "Gauge Make/Model: Troxler 3440 Gauge Serial Number: 28929 Langan Gauge No.: #22 Nuclide (Serial No.): AM-241:BE (47-25121), CS-137 (750-3218)" Typical Troxler gauges of this series contain a 8 mCi Cs-137 source and a 40 mCi Am/Be source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-06-30
45174 | 0 | KARMANOS CANCER INSTITUTE |  |  |  |  | 2008-02-18 12:00 | 2009-06-30 10:33 | 2009-06-30 | MEDICAL EVENT INVOLVING A DOSE THAT IS DIFFERENT THAN PRESCRIBED "On February 18, 2008, an administrative error medical event occurred at our Leksell Gamma Knife facility which resulted in the total dose delivered differing from the written directive by more than 20%, but which agreed with the therapy that was intended and planned by the radiation oncologist authorized user (AU) and the neurosurgeon. This was discovered during the 2008 annual quality management review that was completed on June 24, 2009. "On February 18, 2008, a stereotactic radiosurgery treatment plan was developed by the neurosurgeon, AU and authorized medical physicist (AMP) that satisfied the therapy intentions of the AU and neurosurgeon. Two of the three metastatic lesions that were discussed in advance at the neurosurgery tumor board meeting on February 13, 2008 by the neurosurgeon and AU were treated, the third being geometrically out of range of the gamma knife system. Specifically, the lesion locations selected at the tumor board meeting were right cerebellum, right occipital lobe and left temporal/parietal. The left temporal/parietal was out of range. The correct intended dose of 20 Gy to 50% isodose was planned and delivered on February 18. The AU and AMP specified both lesions on the Gamma Knife planning QA form which was signed by the AU, Neurosurgeon and AMP. The AU signed the plan and initialed every page including screenshots of the isodoses superimposed on the MRI images for both lesions. The plan included all of the information required in 10 CFR 35.40 (b)(3). Finally, the time out form was completed by the AU, neurosurgeon and AMP. "The administrative error medical event is the result of the AU not writing a directive for treatment of the right occipital lesion. "[The event occurred due to] lack of attention to administrative tasks. "[The individual who received the administration had] no detrimental effect. Treatment was delivered as planned according to doctor's orders. "The gamma knife quality management review will be done on the day of treatment prior to delivery by a second physicist using the form/checklist attached. This process is already in effect." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-07-03
45173 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-06-06 22:46 | 2009-06-29 20:45 | 2009-06-29 | INVALID CONTAINMENT VENTILATION ISOLATION SYSTEM ACTUATION "This telephone notification is provided in accordance with 10CFR50.73(a)(1), to report an invalid actuation reportable per 10CFR50.73(a)(2)(iv)(A), 'Any event or condition that resulted in manual or automatic actuation of any system in paragraph (a)(2)(iv)(B) ' General containment isolation signals affecting containment isolation valves in more than one system is identified in paragraph (a)(2)(iv)(B). Although the Containment Ventilation Isolation signal affects multiple containment isolation valves in several systems, at the time of the invalid actuation, only containment isolation valves associated with the containment area radiation monitor were open. Therefore, this notification is being conservatively made. NUREG 1022 Revision 2 identifies the information that needs to be reported as discussed below. "(A) The specific train(s) and system(s) that were actuated. "On June 6, 2009 at 2246 hours, with Unit 1 in Mode 1, a containment area radiation monitor failed high, resulting in an invalid A and B train automatic Containment Ventilation Isolation (CVI). Four containment isolation valves, associated with a containment radiation air monitor, that was in-service at the time of the actuation, closed. Additionally, valves (non-containment isolation valves) in the Auxiliary building closed in response to the actuation. "(B) Whether each train actuation was complete or partial. "The actuation was considered complete. The CVI signal automatically isolated all valves that were open at the time of the actuation. "(c) Whether or not the system started and functioned successfully. "The Containment Ventilation Isolation signal automatically actuated and functioned successfully. The CVI signal was not in response to actual plant conditions and is therefore considered invalid. "In reviewing this CVI actuation it was also discovered that on July 6, 2007 a similar CVI had occurred on Unit 1 when a circuit board associated with the containment vent radiation monitor failed. The failure resulted in an actuation of CVI train A and Train B. The actuation was considered complete since all valves that were open at the time of the actuation isolated as required. The CVI was not in response to actual plant conditions and was therefore considered invalid." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-06-29
45172 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-06-29 11:34 | 2009-06-29 12:53 | 2009-07-23 | OFFSITE NOTIFICATION DUE TO POSSIBLE RELEASE OF FUEL OIL TO THE ENVIRONMENT "A notification to the Tennessee Department of Environment and Conservation (Chattanooga Field Office) was made at 1134 [EDT], 29 June 2009, pursuant to a failed pressure test on an underground section of diesel generator fuel oil transfer piping. This section of piping is not required for operability of the emergency diesel generators. The section of piping has been isolated. Efforts are in progress to determine if fuel oil was released to the environment." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1642 EDT ON 07/23/09 FROM CALVIN FIELDS TO S. SANDIN * * * During work to remediate the above concern, an offsite notification was required as described below: "A notification to Hamilton County Air Pollution Control Bureau was made on July 23, 2009 at 1505 in accordance with the Site's Annual Asbestos Removal Notification . Work was being performed on buried piping when the pipe wrapping was determined to contain asbestos. Work was stopped and the work area controlled by site work documents." The licensee informed the NRC Resident Inspector. Notified R2DO (Vias). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-29
45171 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-06-26 11:30 | 2009-06-29 11:02 | 2009-06-29 | AGREEMENT STATE REPORT - DIFFICULTY RETRIEVING RADIOGRAPHY SOURCE The following report was received via facsimile: "Licensee contacted Ohio Department of Health at approx. 3:45 PM on 6/26/09 to report an incident which occurred earlier that day involving the inability to retrieve a radiography source at a job site near Dayton, Ohio. The incident involved a QSA Global Model 880D camera with a 85 Ci Ir-192 source. "At approximately 11:30 AM and after several unsuccessful attempts to retrieve the source, the radiography crew secured the area around the source and contacted a trained source recovery individual at their Cincinnati office for assistance. This person arrived at the job site at approx. 12:20 PM and assessed the situation. "The recovery person determined that a flange had fallen on the guide tube during the previous shot, which crushed the guide tube and prevented source retrieval. The shot involved a 90-degree bend on a six-inch pipe and the flange was a scrap piece of material found on site that the crew had used to hold the guide tube in place during the shot. It was further determined that the set-up used by the crew for the shot was not very stable, which contributed to the falling of the flange onto the tube. The recovery person was able to retract the source into the camera at approximately 12:45 PM. "The licensee determined that there was no exposure to the public or radiography crew as a result of this incident. The radiography crew was reminded to ensure the stability of future shot setups before exposing the source. The guide tube was replaced and work continued." Ohio report number: OH090006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-07-02
45170 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-06-27 13:20 | 2009-06-27 17:58 | 2009-06-27 | AUXILIARY BUILDING GAS TREATMENT SYSTEM RENDERED INOPERABLE "On June 27, 2009, Plant Operations was starting up the U2 [Unit 2] Auxiliary Building General Ventilation System upon completion of U2 damper maintenance. During startup of the U2 Auxiliary Building Ventilation System, the operator started the U2 General Exhaust fan followed by the startup of the U2 General Supply fan. During the time span of less than 1 minute, when the U2 General Exhaust fan was running but before the U2 General Supply fan was running, the differential pressure condition across a set of Auxiliary Building Secondary Containment Enclosure (ABSCE) doors caused the doors to come off of the tracks and therefore created an ABSCE breach. A breach of this magnitude renders both trains of Auxiliary Building Gas Treatment System (ABGTS) inoperable. "Upon identification of the failed doors at 1320 EDT on June 27, 2009 the plant entered TS Condition 3.7.12.B for 2 trains of ABGTS being inoperable. Repairs to re-establish the integrity of the ABSCE were immediately initiated and TS Condition 3.7.12.B was exited at 1649 EDT, approximately 3 and 1/2 hours later. "This event is reportable under 10 CFR 50.72(b)(3)(v)(C) and (D) as a condition that could have prevented the safety function of structures or systems that are needed to : (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-06-27
45169 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-06-26 20:05 | 2009-06-26 23:45 | 2009-06-27 | UNUSUAL EVENT DECLARED BASED ON FIRE LASTING GREATER THAN 15 MINUTES At 1949 PDT, a small fire was observed between the #1 and #2 bearings on the main turbine involving some lube oil leakage and lagging. The fire brigade was dispatched and at 1953 PDT, the reactor was manually scrammed. At 2005 PDT, the licensee declared an Unusual Event (EAL 9.2.U.1) based on a fire lasting greater than 15 minutes. At 2006 PDT, the fire was reported out. The manual scram was uncomplicated and all systems functioned as required. The reactor is being cooled by normal feedwater and discharging decay heat to the condenser. The licensee is cooling down the reactor to Mode 4. Currently reactor pressure is 495 psi. The licensee has stationed a re-flash watch at the fire location and is assessing any damage that may have occurred. The only damage currently reported involves lagging at the fire location. The NRC Resident Inspector, State and local authorities have been notified. * * * UPDATE FROM BILL HART TO HOWIE CROUCH @ 0128 EDT ON 6/27/09 * * * The licensee terminated the NOUE at 2159 PDT. The termination criteria was the fire is out, a re-flash watch stationed and the plant is stable and transitioning to Mode 4. The licensee has made State and local notifications and has notified the NRC Resident Inspector. Notified R4DO (Powers), IRD (Grant), NRR ET (Lubinski), FEMA (Casto) and DHS (Vestal). | 0 | 0 | 0 | 73 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 4 | WA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2009-06-27
45168 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-06-26 | 2009-06-26 19:25 | 2009-06-26 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "The licensee reported a M/D [moisture density] gauge was stolen from the residence of a Krazan and Associates employee. The gauge was a Troxler 3430 portable moisture density gauge, serial number 35729 containing approximately 8 mCi of Cesium 137 and 40 mCi of Americium 241. The gauge was stolen sometime between 5pm on Thursday, June 25 and 6:00 am on Friday, June 26, 2009. The gauge was stolen from the back of an open pickup bed at the employee's residence in Bakersfield, CA. According to the RSO, the gauge was stored in the locked gauge case that was chained to the vehicle frame. The licensee has reported the incident to the Kern County Police and the Kern County Sheriffs Office. The licensee will also be offering a reward in the local newspaper and on Craigslist." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-07-01
45167 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-06-26 | 2009-06-26 15:30 | 2009-06-26 | AGREEMENT STATE REPORT INVOLVING A MISSING TRITIUM SOURCE The following information was provided by the State of North Carolina via email: "NC Radioactive Materials [Agency] was contacted this afternoon regarding a lost portable gas chromatograph. "Notification: June 26, 2009 at 15:00 "Device: Sentex Sensing Technology - Sentex Model Sentor Gas Chromatograph. "No serial number available. "SS&D: NY-1210-D-101-B "Source: Hydrogen-3 "Safety light corp source 58508-3 "No serial number available "Activity: 150 millicuries "Manufacturer: Infacon, Inc. "Manufacturer Address: 2 Technology Way, East Syracuse, NY 10357 "Summary: Licensee's RSO contacted Agency at 15:00 on 6/26/09. Conducted a physical inventory of sources at licensee's address, and could not locate the 150mCi Sentex Gas Chromatograph. Inquired whereabouts of device, and primary Authorized User speculated that the source/device could have been lost as a result of the renovations at the University in 2007-2008." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-07-01
45166 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2009-06-26 13:00 | 2009-06-26 13:36 | 2009-06-26 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY "At approximately 1015 [EDT] a Dominion employee was transported via ambulance to Lawrence Memorial hospital where he was later pronounced dead from an apparent cardiac arrest. The death was not occupationally related and occurred outside the Protected Area. The individual was treated by the onsite first responders who administered CPR and AED (automatic external defibrillator). State [of Connecticut] and local notifications were made. "OSHA is being notified of the event under the requirements of 29 CFR 1904. "The licensee notified the NRC Senior Resident Inspector." | 0 | 100 | 100 |  | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-26
45165 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2009-06-25 | 2009-06-26 12:11 | 2009-06-26 | AGREEMENT STATE REPORT INVOLVING MEDICAL EVENT The following information was provided by the State of Wisconsin via email: "On June 26, 2009, the Radiation Safety Officer (RSO) notified DHS of a probable medical event that occurred on June 25, 2009 involving an HDR treatment to the esophagus. The authorized user intended to insert the applicator 2 cm past the distal part of the esophageal tumor. A GI specialist verified the location prior to treatment using a scope. Post treatment location of the applicator was reviewed using an AP lateral film. It was then realized that the applicator went 10 cm too far. The prescribed dose was 500 cGy. Therefore, a dose was given to a organ or tissue other than the intended treatment site that exceeds 0.5 Sv (50 rem) to an organ or tissue, and was 50% or more of the dose expected from the administration defined in the written directive (DHS 157.72(1)(a)(3.). DHS inspectors will investigate June 29, 2009." Wisconsin Incident Number: WI090005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2009-07-02
45164 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-09-01 | 2009-06-26 11:57 | 2009-06-26 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILED TO CLOSE The following information was received from the State via e-mail: "On June 25, 2009, at 1630 the Agency was notified by the licensee that while looking for information requested by the State for a previous gauge failure ( EN 44981), the licensee discovered an additional event. This event occurred in early September, 2008, and had not been reported as required. The event involved an Ohmart/VEGA Model SH-F2 level gauge containing a 300 millicurie ( 228 mCi calculated current activity) Cesium (Cs) - 137 source. The gauge shutter would not close due to a sheared shutter rotor. The manufacturer was notified, and a technician arrived at the facility [located in Odessa, TX] on September 30, 2009. The technician replaced the rotor, cleaned and lubricated the gauge, and the gauge operated normally. The technician found that a great deal of material had collected in the source holder causing the failure. The licensee has removed all of their nuclear gauges and is in the process of terminating their license." Texas Incident Report # I-8642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-07-01
45163 | -1 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2009-06-24 10:45 | 2009-06-25 13:06 | 2009-07-01 | ACCESS RESTRICTION DUE TO UNPLANNED CONTAMINATION "An unplanned airborne contamination event occurred beginning June 24, 2009 at 1045 at the Honeywell Metropolis, IL facilities' pond mud calciner area. Access was restricted to the area by requiring respiratory protection to be worn. "Average airborne concentrations during the following 24 hour period were 7.19 E -11 microcuries per cubic centimeter which exceeds the administrative limit of 5 E -12 microcuries per cubic centimeter. Natural uranium dust was the isotope involved. "There was no known effect to employees. This event is being entered into the facilities corrective action program." * * * UPDATE AT 1020 EDT ON 07/01/09 FROM BOB STOKES TO S. SANDIN * * * The licensee is retracting this report based on the following: "[The licensee is] withdraw[ing] the event reported June 25th, 2009 Event Number 45163. Following a review of the circumstances associated with the report [the licensee] determined that the event did not meet the criteria as described in 10CFR40.60(b). The event review determined that the contamination event was expected. And the area DID have a respiratory protection requirement in place at the time of the elevated air activity." The licensee informed NRC Region 2 (John Pelchat). Notified R2DO (Musser) and NMSS (Easton). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2009-06-25
45162 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2009-06-25 00:49 | 2009-06-25 11:44 | 2009-06-25 | DISCOVERY OF AN AFTER-THE-FACT ALERT DUE TO CATASTROPHIC FAILURE OF CCPD "A transitory ALERT [condition was determined to have existed] based on Emergency Action Level 7.D.2 - 'Onsite Explosion Affecting Plant Operation'. At time 0049 on 06/25/09 a catastrophic failure-explosion of the Constant Current Potential Device (CCPD) on 'J' Bus near Air Circuit Breaker (ACB) 34563 resulted in a loss of switchyard 345 KV Bus 'J'. This event de-energized Startup Transformer 01 which is a tie from offsite sources to the Unit 13.8 KV Busses. The unit entered [Technical Specification] LCO 3.8.1, Condition A [due to the loss of one offsite power source]. The Unit remains stable and in operation at 100% RTP [reactor thermal power]. A problem solving decision making team is working on [the] troubleshooting/repair/restoration activities. This event did not impact any plant safety systems or result in any release of radioactive material." Failure of the CCPD caused automatic opening of the breakers on both sides of the 'J' bus which was configured as part of a switchyard ring bus at the time of the event. This resulted in the loss of one of the offsite power ties. However, startup Transformer 02 is still energized from offsite power and remains available for plant operations. Other than the de-energized startup transformer, onsite electrical configurations are normal including availability of emergency diesel generators. The licensee is in a 72 hour LCO per Tech Spec 3.8.1, Condition A, to restore the lost offsite power source. The licensee is inspecting the switchyard for collateral damage to other equipment from the failure of the CCPD. The licensee believes the CCPD failure is likely a result of equipment failure and not the result of any equipment tampering. The licensee stated that initially, the severity of the CCPD failure was not recognized because of the night time conditions and minimal lighting in the area. After daylight examination of the location of the event, it was determined that the failure of the CCPD should have been classified as an explosion affecting plant operation under EAL 7.D.2. Consequently, the licensee made the after-the-fact declaration. Licensee has notified the NRC Resident Inspector, and will be notifying State and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-06-25
45161 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-06-24 16:39 | 2009-06-24 19:02 | 2009-06-24 | ILLINOIS DEPARTMENT OF NATURAL RESOURCES NOTIFIED OF A FISH KILL "At 1639 CDT on 6/24/09, it was discovered that a fish kill took place in the Braidwood Station's cooling lake due to increased temperature. As summer air temperature increased, the cooling lake temperature increased above 93 degrees F, the threshold at which species susceptible to increased temperature begin to perish. It was communicated to the Illinois Department of Natural Resources (IDNR) that a fish kill has occurred. This notification is being made in accordance with the Exelon Reportability Manual section SAF 1.9, Braidwood Station Facility Operating License Appendix B Section 4.1,'Unusual or Important Environmental Events', and 10CFR50.72(b)(2)(xi)." See also EN #45151 for similar event. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-24
45160 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-03-20 | 2009-06-24 14:57 | 2009-06-24 | AGREEMENT STATE REPORT INVOLVING A POTENTIAL OVEREXPOSURE DURING GAMMA KNIFE TREATMENT The following information was received from the State of California via email: "The licensee reported a patient undergoing a gamma knife stereotactic radiosurgery (Elekta Instruments AB, Gamma Knife Perfexion, serial number 6021) on March 20, 2009 received a significant dose to an untargeted area due to an error in the imaging process used for treatment planning. The fiducial marker box (coordinate markers) used to register the CT images was misaligned (the CT locator box had not been firmly seated on the targeting frame as it should have been) which resulted in a target shift of approximately 2.0 mm. Due to the small size of the target (7mm x 4mm x 3mm) and the small size of the radiation shots (4 mm collimators), this shift of the 2.0 mm resulted in only about 52% of the target receiving the prescribed dose of 11 Gy. Therefore, a significant portion of this dose (48%) was shifted to normal tissue (temporal bone) outside of the intended treatment volume. This was a single fraction treatment. The patient is not expected to have any adverse consequences from this event. The physician did not feel additional treatment was advisable. The physician counseled the patient regarding this misadministration. Corrective actions taken by the licensee include: 1) additional training for the CT technologists on the correct placement of the fiducial box; 2) for all ongoing similar treatments, the medical physicist will double check the box placement; and 3) the policies and procedures were updated. "On June 22, 2009, RHB-Brea RAM received a written report from Hoag Hospital that was dated April 1, 2009, and was faxed to RHB-Sacto on April 3, 2009 at 4 PM. The report was mailed from RHB-Sacto on June 12, 2009 to the RHB-Brea X-ray office and date stamped by that office on June 15, 2009 at 12:45 PM. The report stated they were reporting a misadministration which occurred on March 20, 2009 and that this event was previously reported on the evening of March 20, 2009 by telephone. Per the licensee, they had left a voice message on the answer phone at RHB-Sacto on the night of the incident instead of reporting the incident to the 24/7 radiological emergency assistance center." CA 5010 Number: 032009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-06-30
45159 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-06-22 | 2009-06-24 13:30 | 2009-06-29 | AGREEMENT STATE REPORT INVOLVING A POTENTIAL PERSONNEL OVEREXPOSURE DUE TO EQUIPMENT MALFUNCTION The State of California provided the following information via email: "During a teletherapy treatment of a cat on 6/22/09, an apparent malfunction of the MDS-Nordion Model C-146 teletherapy device resulted in the radiation beam not terminating at the end of the treatment. Two entries into the treatment room were apparently made with the radiation beam on, one by a technologist (who wore dosimetry), and one by a veterinarian (who did not wear dosimetry). The veterinarian was exposed to the beam when he removed the cat from the treatment table. The technologist reportedly did not enter the beam. The technologist's dosimetry was submitted to the dosimetry vendor for emergency evaluation. "The veterinarian indicated that he was aware of the location and size of the radiation treatment beam when he removed the cat, and only his lower arms entered the beam. The beam was approximately 70 R/minute at the treatment site. The veterinarian estimated his time in the beam at one and one-half to two minutes. A re-enactment will be conducted as soon as the veterinarian returns to the office from a trip he is on the rest of the week. "A state inspector arrived at the licensee facility at 0630 on 6/24/09 to investigate this event. The licensee has suspended use of the teletherapy device pending the results of the onsite investigation." California 5010 Number: 052309 * * * UPDATE FROM ROBERT GREGER TO VINCE KLCO (VIA EMAIL) ON 6/29/09 @ 1919 * * * "The current best estimate for the dose to the veterinarian has changed to less than one rem (both whole body and extremity). This is based on an on-site re-enactment of the event today that confirmed a significantly lower exposure time and dose rate for the event than was originally believed to have existed. " Notified FSME (Foster) and R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-06-29
45158 | 0 | US ARMY TACOM LCMC ROCK ISLAND |  |  |  |  | 2009-04-16 | 2009-06-24 12:29 | 2009-06-24 | SOURCES LOST DURING SHIPMENT Two Improved Chemical Agent Monitors (ICAMs) were lost during a shipment from ORNG [Oregon National Guard] to Guam National Guard. Each ICAM contains a sealed source containing 10 mCi of Ni-63. (SSDR NR-1129-D-103-S). The ICAMs were packaged by ORNG personnel in May, 2007. The missing ICAMs were reported missing to the licensee on 9 Feb 09. In the weeks following the notification, the licensee conducted an investigation to determine if the ICAMs were actually lost or misplaced within military control. The licensee believes the two ICAMs were lost during the transport between Andersen AFB and Guam National Guard between 15-17 Aug 2007. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-06-24
45157 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2009-06-24 | 2009-06-24 11:48 | 2009-06-24 | LOSS OF TONE ALERT RADIOS "At 0945 on June 24, 2009, with the Nine Mile Point (NMP) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified NMP that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 0845. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the NMP and James A. Fitzpatrick Nuclear Power Plants. This failure meets NRC 8-hour reporting criterion 10CFR.50.72(b)(3)(xiii). "The National Weather Service is currently working to determine the cause of the failure and time frame for system restoration. "The County alert sirens which also function as part of the public prompt notification system remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the prompt notification system be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program and the NRC Resident Inspector has been briefed and the State PSC will also be notified." See Event Notice # 45156 James A. Fitzpatrick Nuclear Power Plant report. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-24
45156 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2009-06-24 | 2009-06-24 11:19 | 2009-06-24 | LOSS OF TONE ALERT RADIOS "At 0945 on June 24, 2009, with the James A. Fitzpatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 0845. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8-hour reporting criterion 10CFR.50.72(b)(3)(xiii). "The National Weather Service is currently working to determine the cause of the failure and time frame for system restoration. "The County alert sirens which also function as part of the public prompt notification system remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the prompt notification system be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program and the NRC Resident Inspector has been briefed and the State PSC will also be notified." See Event Notice #45157 for Nine Mile Point report. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-24
45155 | 0 | MATTINGLY TECH SERVICES |  |  |  |  | 2009-06-22 | 2009-06-24 10:37 | 2009-06-24 | RADIOGRAPHY CAMERA TEMPORARILY LOST On June 22, 2009, the licensee placed an INC IR-100 radiography camera on the tailgate of his work truck. The radiography camera contained a 54 curie Ir-192 source. The camera was not secured on the truck and the tailgate remained in the open position. When he arrived at the job site 25 minutes later he realized the camera had fallen off the truck. In order to look for the camera, the licensee proceeded back along the same route he had taken to the work site. The licensee noticed a police vehicle travelling on the same remote rural road. He stopped the police vehicle for assistance and discovered that the police officer had coincidentally just recovered the camera from a passerby. A passerby had found the camera on the road and contacted the police. The camera was not damaged. There was no personal exposure as a result of this event. The camera was out of the licensee's possession for approximately one hour. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-06-24
45154 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2009-06-23 17:04 | 2009-06-23 23:37 | 2009-06-24 | AUTO START OF EMERGENCY DIESEL GENERATORS DUE TO OFFSITE VOLTAGE TRANSIENT "This report is being made under 10CFR50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(A) of this section' due to the auto start of the 'A' and 'B' Standby Diesel Generators. "The auto start of the 'A' and 'B' Standby Diesel Generators occurred on a valid bus undervoltage condition caused by a transient on the 161 kV Fairfax line while there were severe thunderstorms in the DAEC area. The Standby Diesel Generator supply breakers did not close onto their respective essential buses. The essential buses were not required to load onto either diesel as they remained powered from their normal power supply, 1X003 Start-up Transformer, during and after the event. Offsite power remained fully operable during and following the event. The Standby Diesel Generators have been returned to the standby/readiness condition. "As designed, both Emergency Service Water systems auto started when the SBDGs started. The Emergency Service Water systems have been returned to the standby/readiness condition. "All ECCS systems were available before the event and have remained available following the event. "The NRC Resident Inspector has been informed of the automatic SBDG start." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-06-24
45153 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-06-23 20:30 | 2009-06-23 22:40 | 2009-06-24 | PARTIAL LOSS OF THE EMERGENCY RESPONSE DATA SYSTEM (ERDS) "A partial loss of the ability to send ERDS data to the NRC for greater than 60 minutes occurred. The loss affects transmission of Standby Liquid Control Tank levels, Main Condenser Vacuum levels, and data for North and South Ventilation Stacks and Drywall Post LOCA radiation monitors. "The [Safety Parameter Display System] SPDS, [Health Physics Network] HPN and [Emergency Notification System] ENS systems are not affected. "Troubleshooting to identify and correct the data loss to ERDS is in progress." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0029 EDT ON 6/24/09 FROM SHULTZ TO HUFFMAN * * * "Data for North and South Ventilation Stacks and Drywell Post LOCA radiation monitors was restored to ERDS at 2345 hours on 6/23/09" The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1310 EDT ON 06/24/09 FROM MARK CHRISTOPHER TO S. SANDIN * * * "Data gathered from Standby Liquid Control and Main Condenser Vacuum is not plant data that is transmitted to ERDS. ERDS was fully restored with the required input data at 2345 hours on 6/23/2009." The licensee informed the NRC Resident Inspector. Notified R1DO (Henderson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-23
45152 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2009-06-23 18:23 | 2009-06-23 20:35 | 2009-06-23 | POTENTIALLY DEGRADED INVENTORY CONTROL DURING SHUTDOWN "[At 1823 EDT, the] 23 charging pump, the in-service pump, exhibited degraded capacity resulting in slowly lowering pressurizer level. The 21 charging pump was placed in service and the 23 charging pump was secured. The 23 charging pump is required for fulfillment of the [Reactor Coolant System] RCS inventory control safety function needed to shut down the reactor and maintain it in a safe shutdown condition. Troubleshooting is in progress to determine cause of degraded capacity." In accordance with Technical Specification 3.3.4, the out of service 23 charging pump places the Indian Point Unit 2 into a 30 day shutdown action statement. The licensee notified the NRC Resident Inspector and the New York Public Service Commission (PSC) of the event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2009-06-23
45151 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2009-06-23 12:49 | 2009-06-23 15:16 | 2009-06-23 | OFFSITE NOTIFICATION DUE TO FISH KILL "At 1249 CDT on 06/23/09, it was discovered that a fish kill took place in LaSalle County Nuclear Station's cooling lake, due to increased temperature. As summer air temperatures increased, the cooling lake temperature increased above 93?F, the threshold at which species susceptible to increased temperature begin to perish. It was communicated to the Illinois Department of Natural Resources (IDNR), that a fish kill has occurred. Efforts are under way to contact the IDNR district fish biologist to quantify the mortality. "This notification is made in accordance with Exelon Reportability manual SAF 1.9, ENV 3.26, LaSalle County Station Facility Operating License Appendix B Section 4.1 'Unusual or Important Environmental Events', and 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-23
45150 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-06-15 | 2009-06-23 11:06 | 2009-06-23 | AGREEMENT STATE REPORT - DAMAGED GAUGE "On 15 Jun 2009 a fixed gauge fell off a digester blow line, about 4 feet onto a grating platform. Licensee staff working in the area noticed the gauge and alerted their supervisor and radiation safety officer. After ensuring the shutter was closed and the source [CS-137; .4092 Ci] was still present, the device (containing its source) was moved to a secure location. Licensee performed wipe surveys to check for leaking / contamination. Meter surveys confirmed the presence of the source, and also the absence of elevated dose rates. There is concern that the welds failed that attached the device to the mounting on the pipe. The manufacturer [Ohmart Vega] has been notified and will assist in arranging return of device (containing its source) and further assessment of cause of failure. The manufacturer uses same model [SR-1A] and serial [#6339] for both source and device." The Washington State incident number is WA-09-034. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-06-26
45149 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2009-05-07 | 2009-06-23 11:15 | 2009-06-23 | AGREEMENT STATE REPORT - MEDICAL UNDER DOSAGE The licensee notified the State of Oregon of a misadministration of "Sirspheres" during the treatment for liver cancer. The dosage of radioisotope Y-90 administered was 34.2% less than that prescribed. The patient was informed of the under dosage. The patient may be rescheduled to receive an additional treatment. The State is investigating. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2009-06-29
45148 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-06-23 03:51 | 2009-06-23 05:08 | 2009-06-23 | AUTOMATIC REACTOR SCRAM DUE TO HIGH REACTOR WATER LEVEL "[The reactor automatically scrammed] on a Main Turbine Trip >27.6% rated thermal power. The main turbine trip was due to reactor high level. Post scram, reactor level decreased to approximately -26 inches. Reactor water level was restored with the condensate system. "Both reactor recirc pumps tripped as required on EOC RPT Logic when the main turbine tripped. Both pumps have been restarted. "A Group 2 isolation was received at +3 inches reactor water level with all valves closing as required. "Investigation as to the cause of the transient is underway." All rods inserted during the scram. No relief valves actuated during the transient. Decay heat is being removed via turbine bypass valves to the main condenser. The plant is within normal shutdown temperature and pressure limits. The electrical grid is stable and the plant is in a normal shutdown electrical lineup. The Group 2 has been reset. There was no effect on Unit 1. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 61 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-06-23
45147 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-06-21 17:50 | 2009-06-21 20:58 | 2009-06-21 | AUTOMATIC REACTOR SCRAM RELATED TO A MAIN TURBINE TRIP "On June 21, 2009, at approximately 1750 hours, an automatic Reactor Protection System (RPS) actuation occurred at the Perry Nuclear Power Plant, Unit 1. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the core and the plant is currently stable, in Mode 3 (Hot Shutdown) with reactor pressure at approximately 930 psig. No Emergency Core Cooling Systems were required or utilized to respond to the event and there were no other reportable actuations. Reactor coolant level is being maintained in its normal band by the feedwater system and decay heat is being removed by the condenser. The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available if needed. "The cause of the reactor scram is currently under investigation. Preliminary indications are that the cause of the RPS actuation is related to a main turbine trip. The NRC Resident Inspector has been notified." No safety relief valves lifted during the event and a reactor cooldown is in progress. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-06-21
45146 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2009-06-21 03:08 | 2009-06-21 07:42 | 2009-06-21 | LOSS OF UNIT 2 EMERGENCY RESPONSE DATA SYSTEM (ERDS) DUE TO A PLANT PROCESS COMPUTER ISSUE "On June 21, 2009, it was identified that Unit 2 ERDS was unavailable for approximately 3 hours and 1 minute (0208-0509 hours CDT). This was due to the loss of the Unit 2 Plant Process Computer (PPC) interface with ERDS. Unit 2 ERDS was restored when the Unit 2 PPC interface with ERDS was restored. The cause of the Unit 2 PPC interface interruption is under investigation. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a major loss of communications capability. "The Duty NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-21
45145 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-06-20 14:17 | 2009-06-20 15:47 | 2009-06-20 | AUTOMATIC REACTOR SCRAM FROM HIGH REACTOR PRESSURE SCRAM SIGNAL "Plant Hatch Unit 2 experienced a full reactor scram from the main generator protection circuitry (generator runback circuit). Preliminary indications are that a main generator high temperature signal was received, initiating the generator protection (runback) circuitry and a high reactor pressure scram signal was received during the turbine/generator runback. Investigations into the cause of the generator high temperature signal are ongoing. "Reactor water level was recovered using the reactor feed system, and reactor pressure was controlled using main turbine bypass valves. All control rods inserted, as expected, during the scram. Other than the cause of the main generator high temperature signal, all systems functioned as expected." Unit is currently at 837 psig; 540 degrees F in Mode 3. Electrical system is in a normal lineup. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-06-20
45144 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-06-10 02:35 | 2009-06-19 10:02 | 2009-06-19 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was obtained from the State of Texas via email: "On June 10, 2009, at approximately 2:35 a.m. while performing radiographic operations at GE Oil & Gas, two radiographers found they were unable to retract the radioactive material into the shielded position. "They had made approximately 13 radiographic exposures prior to the malfunction. One of the radiographers contacted an approved Source Retrieval Supervisor, who was at the jobsite grading film. The Source Retrieval Supervisor immediately went to the area where the radiographic operation was located, assessed the situation and ensured the barricaded area was at less than 2 mR/hour. He determined the source was located within the collimator, but would not retract by normal means. The source tube was positioned with a fairly sharp bend which he felt may have put the drive cable in a bind, so he ran to the exposure device and repositioned it to reduce the source tube's bend. This action had no effect. "The Source Retrieval Supervisor contacted the Site Radiation Safety Officer (RSO) by phone and reported the situation. They agreed that the Source Retrieval Supervisor should attempt to return the source to the exposure device by hand pulling the drive cable. After obtaining tools, the Source Retrieval Supervisor and one of the radiographers approached the crankout assembly, disassembled the crankout, and pulled the drive cable to return the source to the shielded position. After ensuring the source was in the exposure device, the crankout was further disassembled so that it could be disconnected from the source pigtail, the exposure device was locked and the source tube removed. The Source Retrieval Supervisor then called the RSO at approximately 3:00 a.m. to report the successful source retrieval. There were no members of the public in the immediate area. "Pocket dosimeter reading for Source Retrieval Supervisor: 10 mR at start of retrieval operation, 15 mR at finish. "Pocket dosimeter reading for Radiographer Aiding in Source Retrieval: 15 mR at start of retrieval operation, 15 mR at finish. "Pocket dosimeter reading for Other Radiographer: 0 "Equipment involved: Exposure device: Spec-150, s/n 0181 Source: QSA Global, 969, s/n 52911B, 35.8 curies Source tube: NDT Repair & Supply, 7', serial number B13-2 Crankout: SPEC, 35', s/n 0603" Texas Incident No. I-8641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-06-24
45143 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-06-18 21:39 | 2009-06-18 22:04 | 2009-06-19 | EMERGENCY DECLARED DUE TO INDICATED FIRE IN EMERGENCY RESPONSE FACILITY SUBSTATION At 2139, the licensee declared a Notification of Unusual Event in response to a fire alarm and CO2 activation in the emergency response facility (ERF) substation. The licensee entered emergency action level (EAL) 4.1. The fire brigade responded to assess for damage. No damage was found. The incident was attributed to a spurious activation of the CO2 system. The licensee terminated the unusual event at 2236. The licensee notified the NRC Resident Inspector. The NRC did not change agency response mode for this event. * * * UPDATE FROM JAMES DAUGHTERY TO HOWIE CROUCH @ 0135 EDT ON 6/19/08 * * * The CO2 discharge was isolated to the Emergency Response Facility Substation Building, and the building has been ventilated. Investigation into the cause of the spurious CO2 actuation is ongoing. Notified the R1DO (Burritt) via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-06-18
45142 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-06-18 11:15 | 2009-06-18 19:26 | 2009-06-19 | INCOMPLETE TESTING OF RADIOACTIVE WASTE SHIPMENT CONTAINERS "On June 17, 2009, Catawba prepared a radioactive waste shipment cask for transportation to the Barnwell low level waste disposal facility. The shipment consisted of miscellaneous spent filters and the shipment was made on the same day. On June 18, 2009, Catawba discovered that all of the required conditions of approval in the Certificate of Compliance for the shipping container were not observed in making the shipment. Specifically, Catawba failed to conduct all of the required leak rate tests for the container prior to shipment. According to procedure, leak rate tests of the container's primary lid, secondary lid, and vent line are required to be performed. Contrary to this requirement, leak rate tests of the secondary lid and vent line were not performed. This event will require a written report to the NRC within 60 days pursuant to 10 CFR 71.95(c). "Catawba is making this ENS notification as a courtesy notification. There is no requirement for Catawba to notify any government agency of this event. However, the State of South Carolina Department of Health and Environmental Control (SC DHEC) will ultimately be made aware of this event by Energy Solutions at Barnwell. There is no evidence that the affected shipping container has actually leaked or is leaking. The secondary lid and vent line were successfully leak rate tested at Barnwell following notification and a request by Catawba management on June 18, 2009. "Catawba has notified the NRC Senior Resident Inspector of this event." * * * UPDATE FROM WAYNE JARMAN TO JOE O'HARA AT 1442 ON 6/19/09 * * * The licensee intends to notify the state warning point as well as York, Gaston, and Mecklenburg Counties. Notified the R2DO(Bartley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2009-06-18
45141 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-06-18 09:40 | 2009-06-18 15:22 | 2009-06-18 | SECURITY WEAPON LEFT UNATTENDED A site security weapon was left unattended for less than one hour. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-06-18
45140 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-06-18 | 2009-06-18 15:02 | 2009-06-18 | AGREEMENT STATE REPORT - FIVE INDUSTRIAL SMOKE DETECTORS CONTAINING RADIUM 226 DISCOVERED INSIDE DUMPSTER The following information was received via fax: "On June 16,2009, Allied Waste - Howard Transfer Station located at 68 Norfolk Ave. Roxbury, Massachusetts responded to a radiation alarm at its facility and notified the Commonwealth of Massachusetts, Radiation Control Program. Radiation levels of about four (4) times background, measured at 18.8 microrem per hour, were reported coming from a roll off container dumpster attached to a truck operated by Casella Waste Systems, Inc. and a DOTÀE 11406 exemption was issued to Casella for proper transport of the unknown radioactive materials to its Peabody, Massachusetts facility located at 295 Forest Street. The roll off container originated from Massachusetts Institute of Technology (M.I.T) at 400 Main Street, Cambridge, Massachusetts and M.I.T. responded to this incident and recovered the radioactive materials. "On June 17, 2009, M.I.T reported the radioactive material was five (5) industrial smoke detectors, each containing 40 micrograms of radium-226. M.I.T. reported that the detectors are now in their possession and will be disposed of as low level radioactive waste. "The Commonwealth of Massachusetts continues to investigate this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-06-23
45139 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-05-22 | 2009-06-18 09:20 | 2009-06-18 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL DISCOVERED IN SCRAP METAL The following information was obtained from the Commonwealth of Massachusetts via facsimile: "On 5/22/2009, a tractor trailer with scrap metal [originating from Second Street Iron & Metal Co., Inc.] set off the radiation alarm monitors at Prolerized New England Company, LLC. "The tractor trailer was returned to [the] originator (under DOT Special Permit MA-09-001) where a gauge with Ra-226 luminescent paint was found and isolated. The contact exposure rate was 1.65 mR/hr and the estimated activity was 1 microcurie. "On 6/15/2009, the gauge was picked up for disposal by a Radioactive Waste broker." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-06-23
45138 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-06-17 08:56 | 2009-06-17 17:10 | 2009-06-17 | FITNESS FOR DUTY INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 99 | 100 |  | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2009-06-17
45137 | -1 | RAPID CITY REGIONAL HOSPITAL |  |  |  |  | 2009-04-24 14:00 | 2009-06-17 11:48 | 2009-06-18 | REPORT INVOLVING THERAPEUTIC ADMINISTRATION OF I-131 TO PATIENT IN EARLY PREGNANCY On 4/24/09 at approximately 1400 hours, a female patient undergoing treatment for hyperthyroidism received a 12.1 millicuries dose of I-131. She had completed both a questionnaire and lab test indicating that she was not pregnant prior to receiving treatment. Subsequent to the administration, she learned she had conceived approximately 2-3 days prior to treatment. This information was provided to hospital staff on 6/16 at which time an evaluation for potential adverse consequences was initiated. The licensee discussed this issue with NRC Region IV staff (Leonardi). * * * RETRACTION FROM LOWELL HUSMAN TO JOE O'HARA AT 1242 EDT ON 6/18/09 * * * The licensee is retracting the event report because they believe the dose to the embryo is less than the limit specified in 10CFR35.3047(a). Notified R4DO(Cain) and FSME(McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 4 | SD | HOS |  | 35.3047(a) |  |  |  | 0 | 2009-06-17
45136 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-06-17 08:25 | 2009-06-17 11:46 | 2009-06-17 | OFFSITE NOTIFICATION TO FISH AND WILDLIFE AGENT "On 06/17/2009 at 0825 CDT, Kewaunee Power Station notified US Fish and Wildlife Agent that a Peregrine Falcon died onsite. Kewaunee Power Station (KPS) had a breeding pair of Peregrine Falcons nesting on top of the Containment structure with four fledglings. On 6/16/09, one of the fledglings landed on the ground under the nest. "The fledgling was found dead from natural causes when checked the morning of 6/17/09. The local US Fish and Wildlife Agent was notified by phone message and e-mail at 0825 hrs on 6/17/09. The carcass will be stored frozen at KPS until it is delivered to the local USFWS Agent per USFWS request. "This is being conservatively reported under 10 CFR 50.72(b)(2)(xi),'Offsite Notification'. The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-17
45135 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-06-16 | 2009-06-16 17:09 | 2009-06-16 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO DOUBLE ADMINISTRATION OF DIAGNOSTIC DOSE The following information was received from the State of Florida Bureau of Radiation Control via facsimile: "Patient received two doses of Thalium-201 (Liquid form - 7.2 milliCurie) for a diagnostic Cardiovascular Procedure in the Nuclear Medicine Department. Two nuclear medicine technologists were working in the same room. Second technologist misunderstood that the first tech had already delivered the first dose. Jacksonville area office will investigate." Estimated maximum internal organ dose received by patient is 9.36 Rem. Florida Report FL09-052 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-06-22
45134 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-06-10 | 2009-06-16 15:10 | 2009-06-16 | AGREEMENT STATE - LEAKING LIQUID SCINTILLATION COUNTER SOURCE The following information was received from the State of California Radiologic Health Branch via e-mail: "On June 10, 2009, the RSO for Beckman Coulter Instruments reported that a 21.5 year old Cs-137 source removed during decommissioning from a Beckman Coulter LSC (Liquid Scintillation Counter): model LS 5801 counter (s/n 7015110) was found to have 0.013 microcuries removable contamination. The reportable limit is 0.005 microcuries. It was removed from the LS counter by a Beckman Field Service Technician and returned to the Beckman Coulter facility in Fullerton for disposal, where the leak test was performed. No other contamination was found inside the LS device. The source part number is 598860, lot # ST1022018 - reference date was 12/18/87. The most probable cause of the leakage was the source holder was cracked due to age. Beckman Coulter has determined that the useful life is 8 years for these sources. The company is replacing all sources older than 8 years as corrective action." The State provided additional information indicating that the original source activity was 30 microcuries. CA Report Number 5010-061009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-06-19
45133 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-06-16 00:31 | 2009-06-16 05:51 | 2009-06-22 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT OF SERVICE DUE TO COMPUTER PROBLEMS "[The licensee experienced] a loss of the ability to send ERDS data to the NRC for greater than 60 minutes due to a computer problem. The HPN and ENS communications systems were not affected and remained available through a commercial communication line. SPDS also remained in service and remained available during this period. The ERDS system was restored to service after 109 minutes." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1240 EDT ON 06/22/09 FROM MARK ARNOSKY TO VINCE KLCO * * * "06-22-2009 Update to clarify the above statement: The HPN and ENS communications systems were affected by the computer problem, however, they remained available for use through an alternate and unaffected commercial communication line." Notified R1DO (Burritt). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-16
45132 | 0 | ACUREN INSPECTIONS |  |  |  |  | 2009-06-13 09:15 | 2009-06-15 08:53 | 2009-06-15 | STUCK SOURCE IN RADIOGRAPHY CAMERA Two radiographers were examining welds on a tank when the magnetic stand that was attached to the side of the tank fell. The Amersham radiography camera (model 660B) was secured to the tank by a shackle and swung freely. This mishap damaged the guide tube extension and crimped the guide tube at the source connect. When the radiographers realized the source (65.2 Ci Ir-192) was stuck they followed O&E (Radiographic Operating & Emergency) procedures and notified the FRSO (Facility Radiation Safety Officer). At that same time the radiographers reassessed the area and established appropriate boundaries. The tank being examined was in an area away from the general public, therefore the public was not exposed. The FRSO, in retrieving the stuck source, was not over exposed. Both individuals on the job-site, as well as the FRSO are carded radiographers. FRSO is also trained in source retrieval. Corrective actions planned by the licensee to prevent recurrence of this incident is to use two lifts instead of one, which should prevent the stand from falling to its farthest point. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-06-15
45131 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-06-13 11:30 | 2009-06-13 19:20 | 2009-06-19 | DEGRADED CONDITION DUE TO REACTOR COOLANT PRESSURE BOUNDARY LEAK "This notification is made pursuant to 10CFR50.72(b)(3)(ii) to report degradation of a principal safety barrier. During ASME Section XI (Table 2500-1 Code Category B-P, Item Number B15.10) refuel outage system leak testing of the reactor vessel and reactor coolant pressure boundary, leakage of approximately 1 drop per minute was detected from the bonnet vent leak-off connection on the reactor recirculation pump inlet isolation valve (RRC-V-23A) in the reactor coolant recirculation loop A. This condition is consistent with example (A)(2) provided in NUREG-1022, rev. 2 'Event Reporting Guidelines 10CFR50.72 and 50.73.' This example indicates that reporting under the above criteria is required for 'Welding or material defects in the primary coolant system which cannot be found acceptable under ASME Section XI, Table IWB-3410-1, 'Acceptance Standards.' "A cause evaluation will be performed and a 60-day follow-up report provided pursuant to the corresponding 10CFR50.73 reporting requirement." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM FRED SCHILL TO VINCE KLCO AT 1955 EDT ON 6/19/09 * * * "Subsequent evaluation of the point where leakage was observed reveals that the 1 drop per minute leakage from RRC-V-23A was actually emanating from the packing chamber leak-off connection and not from the bonnet vent leak-off connection as reported. The packing chamber leak-off connection provides a means to monitor leakage from the packing. It does not provide a pressure containing function at its location on the valve and, therefore, is not part of the Reactor Coolant Pressure Boundary (RCPB) as defined in Part 50.2. "Since the packing chamber leak-off connection is not a pressure-retaining structure it is not part of the RCPB, therefore the condition reported in event report #45131 is not a degradation of a principle safety barrier and is not reportable pursuant to Part 50.72(b)(3)(ii)(A). For this reason, the subject event report is hereby retracted." The licensee notified the NRC Resident Inspector. R4DO (Cain) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-06-13
45130 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-06-13 14:15 | 2009-06-13 18:10 | 2009-06-13 | SUSPECTED TAMPERING INVOLVING THE MAIN TRANSFORMER Discovery of suspected tampering during maintenance activities. Immediate compensatory actions taken upon discovery. The licensee informed LLEA and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-06-13
45129 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-06-13 13:53 | 2009-06-13 16:36 | 2009-06-13 | OFFSITE NOTIFICATION DUE TO EMERGENCY SIREN ACTUATION "At approximately 1353 (CDT), [the licensee] received notification of a single siren actuation in the Early Warning Siren System. This call came from a Pierce County 911 dispatcher after they received a call from a local resident. The siren system vendor reports the siren actuated at approximately 1310 and was inactivated by Pierce County Deputies at 1345 using the local emergency key. The siren (P14) remains out of service and is the only siren in Pierce County currently out of service. The licensee's procedural requirement to maintain at least 70% of sirens within the 10 mile EPZ is still met. Neither Pierce County nor the licensee intend on making a press release." The licensee notified the Pierce County Emergency Government Manager. The licensee notified the NRC Resident Inspector | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-13
45128 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-06-13 09:45 | 2009-06-13 09:19 | 2009-06-19 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE "Planned maintenance activities are being performed today (June 13, 2009) on the Vogtle Nuclear Plant's Technical Support Center (TSC) power sources. This work activity is planned to be performed and completed expeditiously within approximately 3 days (78 hours). This maintenance activity is to perform a transformer replacement, perform preventative maintenance on several circuit breakers, perform preventative maintenance on the TSC HVAC unit, repair a leak on the Back-Up D/G [diesel generator] which provides a back-up power supply to the TSC HVAC, and other minor maintenance activities. "If an emergency condition occurs that requires activation of the Technical Support Center during this work activity, contingency plans are in place to restore the TSC to fully functional status, with the time to restoration dependent on the stage of the work activity at the time the emergency occurs. Plans are to utilize the Shift Manager's Office in the Control Room as the Backup TSC for any declared emergency during the time the work activity is being performed. Procedure 91201-C, Activation and Operation of the Technical Support Center, provides instructions to direct TSC management to the Control Room to continue TSC activities if it is necessary to relocate from the primary TSC. At the beginning of the TSC outage, the ENN [Emergency Notification Network] and ERDS [Emergency Response Data System] will not be available until temporary power is being provided. This outage for the communications equipment will last from 2-4 hours, at which time they will be available. "This event is reportable per 10 CFR 50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the evolution. "The licensee has notified the NRC Resident Inspector." The licensee provided notification of this issue prior to initiation of the maintenance per the licensee's 10 CFR 50.54(q) evaluation for the activity. The licensee intends to update this report when the temporary modification is completed such that the ERDS system is returned to service. * * * UPDATE FROM MIKE HENRY TO HOWIE CROUCH @ 0735 EDT ON 6/15/09 * * * The licensee has returned the ERDS system to service using temporary power. Preventive maintenance still continues on the TSC. The licensee has notified the NRC Resident Inspector. Notified R2DO (McCoy). * * * UPDATE ON 6/19/2009 AT 1153 FROM RICHARD COTTY TO MARK ABRAMOVITZ * * * The ventilation system has been returned to its normal power supply at 1121 on 6/19/2009. The licensee will notify the NRC Resident Inspector. Notified the R2DO (Bartley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-13
45127 | 0 | ELI LILLY & COMPANY |  |  |  |  | 2009-05-22 | 2009-06-12 13:53 | 2009-06-12 | REPORT INVOLVING DISPOSAL OF GENERAL LICENSED TRITIUM EXIT SIGNS The Corporate RSO for Eli Lilly & Co. located at 639 South Delaware St, Indianapolis, IN 46225 called in response to the NRC request for info on tritium exit signs, dated 1/16/09. He reported that they have 26 intact tubes (received on 5/22/09) which had been removed from the exit signs for reasons unknown (manufacturer/serial number/activity unknown). They have a specific license to possess tritium and the expertise to dispose of the material in an acceptable manner. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN |  |  |  |  | 0 | 2009-06-12
45126 | 0 | LOUISIANA DEQ |  |  |  |  | 2009-05-29 | 2009-06-12 11:04 | 2009-06-12 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via facsimile: "On May 29, 2009, H & S Construction reported that a Troxler moisture density gauge was accidently backed into. The gauge was a Troxler model 3440, serial number 28470, with a 9 mCi source of Cs-137 and a 44 mCi source of Am:Be. The source was in the locked and shielded position when it was hit. The plastic cover on the gauge was broken on one side. An investigation was performed by DEQ [Department of Environmental Quality]. A radiation survey was performed with readings of 7 mR/hr on the damaged side and 3 mR/hr on the undamaged side. The gauge was taken to Gamma-Tron Services so a leak test could be performed. The leak test (less than 0.005 uCi of removable contamination) confirmed that neither the Cs-137 source nor the Am:Be source were damaged or compromised during this incident. Louisiana Report: LA090013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-06-17
45125 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-03-26 | 2009-06-11 21:00 | 2009-06-11 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING AN UNDERDOSE DUE TO TECHNICIAN ERROR The following information was received via fax: "Event Report ID No: PA090015 "License No: PA-0082 "Licensee: Mercy Fitzgerald Hospital "Event date and time: March 26, 2009/time unknown "Event location: Mercy Fitzgerald Hospital Lansdowne & Baily Rds., Darby, PA "Event type: Medical Event "Notifications: A letter dated April 9, 2009 was sent to DEP "Event description: Under dose for a Sr-90 eye applicator "City, State: Darby, PA "Description: PA DEP Bureau of Radiation Protection was notified in writing, dated April 9, 2009, by the Radiation Safety Officer for Mercy Fitzgerald Hospital. An ADCL calibrated Sr-90 ophthalmic applicator was used on a patient for an external eye application for the treatment of pterygium. The guard ring needed to be removed before treatment and was not, hence only delivered 5% of the prescribed dose to the patient. "The State has an inspection scheduled and will continue to keep NRC informed of the status of our investigation." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-06-17
45124 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-06-11 15:55 | 2009-06-11 18:24 | 2009-06-15 | UNIT 2 INITIATED A TECH SPEC REQUIRED SHUTDOWN DUE TO A RISE IN UNIDENTIFIED DRYWELL LEAKAGE "At noon on 06/11/2009 Browns Ferry Unit 2 experienced a rise in drywell leakage during reactor startup. The 4 hour unidentified leak rate from 0800 to 1200 on 6/10/2009 was 0 GPM, while the 4 hour unidentified leak rate from 0800 to 1200 on 6/11/2009 was 3.88 GPM. This increase in leak rate exceeded the allowable limit of a 2 GPM increase in unidentified leakage in a 24 hour period per Technical Specification 3.4.4. At 1555 [CDT] on 06/11/2009, Unit 2 inserted a manual reactor SCRAM to comply with Technical Specification 3.4.4 Condition C to be in Mode 3 in 12 hours and Mode 4 within 36 hours. "All systems responded as required except that when reset of the SCRAM was attempted after all control rods had inserted, a portion of the 'B' RPS channel (B2/B3) failed to reset. The 'A' RPS channel was then actuated by a spike on the Intermediate Range Monitors while they were being driven into the core resulting in a full RPS SCRAM actuation. "The licensee notified the NRC Resident Inspector." Unit 2 is currently removing decay heat using normal feedwater with bypass steam to the main condenser. The electrical system is in a normal shutdown configuration. The licensee has not identified the source of the unidentified leakage and anticipates taking Unit 2 to Cold Shutdown (Mode 4). * * * UPDATE AT 1730 EDT ON 6/15/09 FROM HUNTER TO SANDIN * * * "Plant personnel entered the drywell after the reactor was shutdown. The resulting investigation revealed two sources of increased drywell leakage. One source of leakage was from 2-CKV-10-511 and 2-CKV-10-526, SRV Tailpipe Vacuum Breakers, which were apparently damaged by leakage past the pilot valve for 2-PCV-001-0023, Main Steam Safety Relief Valve. The combination of damaged vacuum breakers and a leaking pilot valve resulted in steam leakage into the drywell atmosphere. The other source of leakage was noted through the packing for 2-DRV-10-505, RPV Drain to RWCU. The vacuum breakers, pilot valve, and drain valve have been repaired. "The 'B' RPS contactors were repaired and the scram reset. "The NRC Resident Inspector has been notified." R2DO (McCoy) notified. | 0 | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-06-11
45123 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-06-11 | 2009-06-11 14:45 | 2009-06-11 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received via E-mail: "As we [the Texas Department of Health] understand it, a gauge, Ronan Eng. Co., Model SA-1 with 3Ci of Cs-137, has a broken handle and the shutter will not close. The serial number (S/N) is M7844 and I see that the source model could be 3M or QSA (AEA) so that will [be] determined later. It said that the external exposure rate is a nominal 1.5mR/hr and the gauge is 40' high on a vessel which is in process so no vessel entry is anticipated. They hope to keep operating until their next scheduled outage on July 15." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-06-16
45122 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2009-06-10 09:20 | 2009-06-10 18:00 | 2009-06-15 | UNANALYZED CONDITION - UNKNOWN CABLE WITH COMBUSTIBLE COATING FOUND IN DIVISION I / DIVISION II CABLE TRAY "At 0920 on June 10, 2009, technicians [performing] a Halon detection functional surveillance found a No. 10 AWG Tefzel coated conductor that ran in the Division 1, Division 2, and non-divisional cable trough in the Main Control Room subfloor panels. The conductor is terminated at a ring lug to a bus bar on one end, and the termination point on the other end is unknown. The Tefzel coating is combustible. "This is reportable as an 8 hour report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as 'any condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "Clinton is required to have divisional separation in the event of a fire, and if the cable caught fire both Division 1 and Division 2 could be impacted. "The station is working on determining the design function of the conductor and what the conductor is connected to." The licensee will notify the on-site state IEMA Resident Inspector. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1655 EDT ON 6/15/09 FROM REANDEAU TO HUFFMAN * * * The licensee is retracting this event based on the following: "Further inspection of the duct run in the subfloor section reveals that the #10 AWG Tefzel coated conductor is actually 2 separate conductors, not just one. Each is a ground for the flex conduits in the divisional ducts (as described in USAR section 8.3.1.4.5.5), installed to ensure that hot shorts in the wiring inside the flex conduit will melt the upstream fuses. In addition, between the division 1 and division 2 duct sections, there is a metal barrier in the duct, providing the separation barrier between redundant Class 1E equipment (Division 1 and Division 2 cables) as described in IEEE 384. "Also, further review shows that Tefzel is flame retardant and non-propagating, passes the IEEE 383 and UL vertical tray flame test, and is rated 'non-burning' under ASTM D635. "There is no divisional separation issue and no condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety." The licensee has notified the on-site state IEMA Resident Inspector and NRC Resident Inspector. R3DO (Lipa) notified. | 96 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-06-10
45121 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2009-06-06 | 2009-06-10 11:31 | 2009-06-10 | STOLEN MOISTURE DENSITY GAUGE The following was received from the State of Kansas via facsimile: "Case number: KS090005. "Kansas Division of Emergency Management reported that the duty officer received a call at 5:29 on 6/9/09 from licensee that a moisture density gauge had been stolen from a job site in Roeland Park, KS, Johnson County, on 6/6/09. The Roeland Park police were notified at 5:12 pm on 6/9/09. [The responding officer] stated he observed the vehicle and chains used to secure the gauge. The chains were rusty and did not appear to have been tampered with (no scrape marks or areas where the rust had been disturbed). The licensee employee stated the gauge transport case was secured by the chains through the handles. KDHE [Kansas Department of Health and Environment] was notified 0905 6/10/09." The gauge was a Humboldt Scientific model number 5001, with sealed sources of 50 mCi Am-241:BE and 11 mCi Cs-137. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2009-06-15
45120 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-06-09 | 2009-06-10 09:54 | 2009-06-10 | AGREEMENT STATE - LOST SOURCE The following information was received via facsimile: "The device is a product fill level gauge that was on a line that was being disassembled and cleared out. [Proctor & Gamble] P&G had told the contractor to leave the part of the line with the gauge until Industrial Dynamics (their consultant for radioactive materials) had a chance to remove the device from the package line. However, the device was not removed and the line was sent off for disposal. "The device was physically removed from the site on or about May 28, 2009. The Licensee discovered the [device to be missing] on June 9, 2009. The disposed-of material was sent to DH Griffin [a scrap yard] in Greensboro, NC. DH Griffin has been contacted and they are in the process of sorting and searching for the device. They say there is a good chance that the device is still at the scrap yard as the material received from P&G should be in one of two piles still at the yard. "[The State of North Carolina] asked P&G if they needed any assistance and [P&G] said no, at this time." The device is an Industrial Dynamics FT-50 Filtec device used to measure the fill level of liquid products. The source is an Am-241, 100 mCi source. Gauge S/N: 110585, Source S/N: 3770. The source was leak tested in Sept. 2006 and it was not leaking at that time. The North Carolina Incident number is NC-09-25. * * * UPDATE FROM HENRY BARNES TO DONALD NORWOOD ON 06/10/2009 AT 1307 EDT * * * "D.H. Griffin contacted P&G [at] 10:15 am. They informed P&G that they had located the Filtec unit on site. [An employee of P&G] drove to the D.H. Griffin site [and] verified that it was their Filtec unit. The unit is now isolated on a pallet and secured in a warehouse at D.H. Griffin. P&G is in contact with their Industrial Dynamics regional resource to arrange to have the source removed. They will keep [the State] informed as to the progress on the removal of the unit." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-06-15
45119 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2009-06-09 18:52 | 2009-06-10 01:02 | 2009-06-29 | DOOR FOR SECONDARY CONTAINMENT BOUNDARY LEFT OPEN "This notification is being made pursuant to NRC regulation 10 CFR 50.72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "At 1852 [CDT] on June 9, 2009, River Bend Station personnel discovered that a normally closed auxiliary building door was open. This door serves as part of the secondary containment boundary. At discovery, immediate action was taken to close the door. This action restored the secondary containment to the design configuration. Investigation determined that the door was last accessed at 1242 on June 9 and was most probably left open at that time. Further action is being taken to investigate the cause of the event. "Secondary containment leak tightness is required to ensure that the release of radioactive materials from the primary containment is restricted to those leakage paths and associated leakage rates assumed in the accident analysis, and that fission products entrapped within the secondary containment structures will be treated by the Standby Gas Treatment System prior to discharge to the environment. With the subject door being open, the function of secondary containment would be impacted. A second door is located in the same exterior passage way as the secondary containment door found open. This door was closed during the period of time the secondary containment door was open. This second door serves a security function. However, it potentially could serve to perform the secondary containment function. An evaluation is being performed to determine the actual impact of the condition on the secondary containment function. However, based on the identified condition, this report is being made as a condition that could have prevented fulfillment of a safety function." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM D. WILLIAMSON TO D.PARK AT 1325 ON 6/29/09 * * * "(This event was reported by River Bend Station on 6/10/09 at 0102 [EDT]. This update is being provided for the purpose of retracting that notification.) "Subsequent investigation determined that the secondary containment door was left open for unknown reasons some time after 0800 on the morning of June 9. At the 1242 observation by the persons exiting the building, the door was open and it was left in that condition. However, a separate exterior door in that same passageway serves the security function, and it has been confirmed that, other than for routine access, the security door remained closed and locked during the time that the interior pressure boundary door was open. "An engineering analysis has determined that the as-found condition did not defeat the function of secondary containment. While the security door is not air-tight, the maximum potential leakage past it under postulated accident conditions has been evaluated. "An existing engineering calculation provides a means to determine the maximum size of a breach in the auxiliary building boundary such that the draw-down requirement prescribed by Technical Specifications is maintained. That calculation uses the additional flow area of an identified breach, in addition to the most recent test results of the standby gas treatment system (that system establishes and maintains a negative pressure in the building as part of the its design). "Measurements taken on the door found that the potential flow area around it totaled 35 square inches. The current test results indicate that the standby gas treatment system can support the safety function of the auxiliary building with an analytical breach size of 230 square inches. As there is significant margin between the measured gap around the security door and the analytical value, this event was well bounded by the assumptions of the design basis of the building. As such, this event did not constitute a loss of the safety function of secondary containment." The licensee notified the NRC Resident Inspector. Notified the R4DO (D.Powers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-06-10
45118 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-06-09 12:00 | 2009-06-09 16:27 | 2009-06-09 | REMAINS DISCOVERED OUTSIDE OCA "On June 9, 2009 at approximately 1200 CDT, remains not yet identified as human or animal were found by Prairie Island Nuclear Generating Plant (PINGP) employees. The remains were discovered on Xcel Energy property just outside the PINGP owner controlled area along the transmission line path, near the railroad tracks. "The Red Wing City Police Department and the Prairie Island Indian Community Police Department have both been notified and are on the scene. Notifications are being made to appropriate agencies and officials. No press release is planned." The licensee has notified the NRC Resident Inspector. The licensee is treating this as a media sensitive event. * * * UPDATE FROM L. PASCHKE TO HOWIE CROUCH @ 2026 EDT ON 6/9/09 * * * The licensee reported that the Prairie Island Police, Red Wing City Police and the Minnesota Bureau of Criminal Apprehension have cleared the scene after they determined that the remains were that of a large bird. There has been no intense media interest at this time. Notified R3DO (Pelke), HQPAO (Brenner) and ILTAB (Allston). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-09
45117 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-06-05 15:30 | 2009-06-08 12:17 | 2009-06-08 | ILLINOIS AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "On Friday June 5, the licensee's Radiation Safety Officer, called the Agency [Illinois Emergency Management Agency] to report a traffic accident involving their portable moisture density gauge that afternoon around 15:30. Apparently, a drunk driver entered the north bound construction zone on IL Rt. 49 at a speed in excess of 70 miles per hour and struck the gauge. The gauge was drug [approximately] 350 to 500 feet from the site of the impact. The car backed up to dislodge the gauge from under the vehicle and sped off. The license plate and identity of the vehicle was noted by a member of the road crew. The driver later crashed his vehicle and was apprehended by local law enforcement. "The gauge source rod was in a shallow test position at the time of impact which separated the handle with indexing rod and source rod from the base of the gauge. The licensee attempted to recover all the pieces but some fragments of the source rod appeared to be missing. Radiation measurements taken at the scene by the RSO using a hand held instrument suggested both the Cs-137 and Am-241 sources were present. Digital pictures forwarded from the site to the Agency seemed to corroborate that finding however, after the gauge was returned to the storage location approximately one hour later, readings from the source rod definitely showed the source was no longer attached to the bottom of the rod. "The Agency immediately dispatched an individual to investigate the matter. "[The investigator, using] direct measurements and observation confirmed that although the Am-241:Be source was intact and in the shielded base of the destroyed gauge, the Cs-137 was no longer present with the other remaining pieces of the gauge and that the source rod tip had been cleanly severed from the source rod. Arrangements were made with the RSO and QA/QC Manager for the licensee to acquire additional safety equipment and begin a search of the section of pavement where the accident occurred. The nighttime scanning of the 1 mile section of roadway from the point of impact with a rate meter and scintillation probe produced elevated readings along the roadside off of the shoulder of the new asphalt. The readings were used to pinpoint the area where the source was located. Additional lighting eventually lead to the discovery of the source capsule within a grassy area of the shoulder some 5 feet from the road bed. The source was subsequently collected by the Agency investigator and placed into a shielded transport container. Gross monitoring of wipe tests collected at the scene showed no signs of contamination from the source or any equipment used to handle the source. The source was subsequently secured and isolated at the licensee's storage facility pending transfer to the manufacturer. Interviews with staff and assessment of radiation readings from the source indicated that no individual received a notable exposure from the actual event nor did any one handle a piece of the gauge that would result in an extremity exposure. Pocket dosimeter readings from those involved in the recovery showed no measured exposures. "This item remains open pending transfer of the source and submission of the required report from the licensee." The gauge contained a 8 mCi Cs-137 source and a 40 mCi Am/Be-241 source. Illinois Event No. IL0900046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-06-11
45116 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2009-06-06 15:22 | 2009-06-06 17:19 | 2009-06-06 | OFFSITE NOTIFICATION MADE DUE TO ELEVATED LEVELS OF TRITIUM "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the fact that Exelon Nuclear has informed the Illinois Emergency Management Agency and Illinois Environmental Protection Agency of recent groundwater monitoring results at Dresden Station. This notification was made at 15:22 hours CDT on June 6, 2009. "As part of the Station's continuing environmental monitoring and sampling program, sample results from some of the monitoring wells have indicated elevated levels of tritium requiring notification of the State of Illinois. Based on sampling data obtained to date, the tritium in the groundwater is confined to Exelon property and poses no threat to public health or safety. "The IEPA/ IEMA regulation requires notification when a release to soil, groundwater, or surface water goes off-site at greater than 200 pCi/L or remains on-site greater than 0.002 Curies. Based upon the monitoring well results and the volume and concentration of groundwater infiltration into the nearby storm sewer, it is likely that the 0.002 Curie on-site threshold has been exceeded. "The Station continues to track this issue by monitoring the existing wells and initiation of mitigative actions to contain any release and ensure it remains on-site. At this time, the source of the tritium has not been identified. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-06
45115 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-06-06 09:00 | 2009-06-06 08:16 | 2009-06-06 | VOLUNTARY NOTIFICATION - MOVING IRRADIATED STEAM DRYER IN A SHIELDED CONTAINER The NRC Operations Center was pre-notified of the following activity: "The following was determined to be an Event of Potential Public Interest (EPPI) and required reporting to the Pennsylvania Emergency Management Agency (PEMA). "On Saturday, 06/06/09 and Sunday, 06/07/09, Susquehanna will be moving an irradiated steam dryer from the reactor building to an onsite storage area. The dryer will be in a shielded container to minimize personnel dose during the move. In addition, access to the owner controlled areas near the site will be restricted. The presence of these controls may result in public inquiries about this planned activity. "If onsite emergency response is required during the move, offsite agencies that support Susquehanna will not be impacted. Susquehanna will maintain the ability of Fire and Emergency Medical personnel to access the site." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2009-06-06
45114 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-06-05 09:30 | 2009-06-05 11:23 | 2009-06-05 | TECHNCIAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE "Planned maintenance activities are being performed today (June 5, 2009) on the Hatch Nuclear Plant's Technical Support Center (TSC). This work activity is planned to be performed and completed expeditiously within one work shift (less than 12 hours). This maintenance activity is to repair or replace solenoid for valve 1X75F003 on the TSC HVAC System which is not always reliably opening. During this work the TSC HVAC will be rendered non-functional during the performance of the work activity. "If an emergency condition occurs that requires activation of the Technical Support Center during this work activity, it will take no more than two hours to return the equipment back to functional status, dependent on the stage of the work activity at the time the emergency occurs. Plans are to utilize the TSC for any declared emergency during the time the work activity is being performed, as long as radiological conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the evolution." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM B. COLEMAN TO J. KOZAL AT 1406 EDT ON 6/5/09 * * * The planned maintenance activities are complete and the TSC ventilation system has been returned to service. The licensee has notified the NRC Resident Inspector. Notified R2DO (Lesser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-05
45113 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-06-01 15:45 | 2009-06-03 13:03 | 2009-06-22 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was obtained from the State of Arkansas via email: "On June 1, 2009 at 1600, the licensee notified the Department [Arkansas Department of Health] that while retracting the source after a shot, the source stopped and could not be retracted into the camera and could not be moved into the collimator. This occurred at 1545. The radiography is conducted inside an open top and open ended cell at the facility. The radiography crew evacuated the cell area, adjacent work areas and established a 2 mR/hr boundary around the cell. Observing from the far end of the cell, the radiography crew established that the piece of pipe being radiographed fell from the work table onto the guide tube. The radiography crew notified the State of Arkansas and also QSA Global in Baton Rouge, LA. "The State of Arkansas sent two Health Physicists to the facility. [They arrived] at 2320 and remained on site throughout the source retrieval. "QSA Global responded to the site at 0030 on the morning of June 2, 2009. Using portable shielding and standard radiation safety practices, QSA Global personnel were able to move the source into the collimator, cut out the crimped guide tube, and return the source to the camera at 0230 on the morning of June 2. "The Camera involved: Industrial Nuclear Company, Inc., Model IR-100, Serial Number 4150. "The Source involved: QSA Global, Model 87703, Serial 49390B, manufactured on April 8, 2009 and contained 64 Curies at the time of the incident. "The Camera has been taken out of service for repair and inspection. "The State of Arkansas is awaiting a report from QSA Global and the licensee." * * * UPDATE FROM STEVE MACK TO HOWIE CROUCH (VIA EMAIL) ON 6/22/09 @ 1005 EDT * * * "The State has received written reports from the licensee with corrective actions and from QSA Global regarding the response and source retrieval. "Doses to the source retrieval team were 18 mR and 11 mR as noted on the electronic dosimeters. "After retrieval of the source, DU [Depleted Uranium] contamination was noted in the guide tube. The licensee is currently working to evaluate and replace cameras due to probable 'S' tube wear. "The Department considers this event to be closed." Notified FSME (McIntosh) and R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-06-08
45112 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-06-02 01:22 | 2009-06-02 04:50 | 2009-06-02 | UNUSUAL EVENT - SMOKE ALARM IN PROTECTED AREA LASTING GREATER THAN 15 MINUTES Licensee declared an Unusual Event due to a possible fire in the protected area inside containment. The smoke alarm could not be verified before 15 minutes, therefore licensee entered into EAL HU 2.1. Seventeen smoke detectors located inside the containment feed into this alarm, and it is unknown if more than one smoke detector initiated the alarm. The local fire department was not requested to respond to the site. Licensee is sending personnel inside containment to investigate whether or not this alarm was spurious. There is no indication of smoke or an increase in temperature in or around the containment. There was no radiological release to the environment. * * * UPDATE FROM JAMES DILLIS TO JOHN KNOKE AT 0618 EDT ON 06/02/09 * * * Licensee completed their investigation inside containment and determined there was no fire. Licensee terminated the Unusual Event at 0618 EDT. Licensee has notified the NRC Resident Inspector. Notified R4DO (Ryan Lantz), IRD MOC (Jeff Grant), NRREO (M. Evans), DHS (Inzer), FEMA (D. Barden) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-06-02
45111 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-06-01 16:50 | 2009-06-02 00:54 | 2009-06-15 | LOSS OF TSC AIR CONDITIONING UNIT COMPRESSOR "On 5/20/09, the Technical Support Center (TSC) air conditioning unit compressor failed to restart following refueling outage electrical bus maintenance. On 5/31/09, the compressor was discovered to be shorted to ground. The short renders the air conditioning unit nonfunctional and at 1650 on 6/1/09 the nonfunctional air conditioner was determined to adversely affect TSC habitability based on meteorological conditions. TSC filtration capabilities are not affected by this problem. The nonfunctional air conditioner leaves the TSC in a degraded state; however, the TSC is currently habitable and available for service. Should the TSC need to be activated, habitability of the TSC will be monitored per existing plant procedures. Relocation of the TSC to an alternate location would be performed in accordance with station procedures as necessary to ensure continued TSC functionality. The control room and all other emergency response facilities are unaffected by the TSC chiller outage. Work instructions to repair the chiller are in review and work is expected to commence on June 2nd and proceed with high priority. A follow-up notification will be made when the TSC chiller has been restored. This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC resident has been notified." * * * UPDATE AT 1503 EDT ON 6/15/09 FROM RULLMAN TO HUFFMAN * * * "Repairs to the TSC air conditioning unit have been completed and it has been placed in service. There is no longer any challenge to TSC habitability." The NRC Resident Inspector has been notified. R4DO (Cain) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-06-02
45110 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-05-27 19:05 | 2009-06-01 18:06 | 2009-06-01 | BOTH TRAINS OF AUXILIARY BUILDING GAS TREATMENT SYSTEM RENDERED INOPERABLE "On May 27, 2009, Plant Operations was shutting down the Auxiliary Building General Ventilation system [ABGTS] as a compensatory measure in response to an historical deficiency that was identified in the surveillance procedure for conducting TS SR 3.7.12.4. The building's general ventilation was being shut down to place the plant in a known tested configuration to ensure continued safe operation while plans were being developed to properly perform SR 3.7.12.4. While shutting down the building's ventilation system, the operator shut down the building's supply fans followed by the shut down of building's exhaust fans. This sequence resulted in an unacceptable differential pressure condition across a set of Auxiliary Building Secondary Containment Enclosure (ABSCE) doors. Upon identification of the failed doors at 1905 EDT on May 27, the plant entered TS Condition 3.7.12.B for 2 trains of ABGTS being inoperable. Repairs to re-establish the integrity of the ABSCE were immediately initiated and TS Condition 3.7.12.B was exited at 2239 EDT, approximately 3 and 1/2 hours later. "The reportability of this condition was not recognized at the time of this event. Based upon a review subsequent to the event on June 1, 2009, this event was determined to be reportable under 10 CFR 50.72(b)(3)(v)(C) and (D) as a condition that could have prevented the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-06-01
45109 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2009-05-30 | 2009-06-01 11:10 | 2009-06-03 | AGREEMENT STATE REPORT - LOST SHIPMENT OF I-125 BRACHYTHERAPY SEEDS "On Saturday May 30, 2009 the Virginia Radioactive Materials Program received notification from Best Medical International, Inc. that a shipment of I-125 Brachytherapy seeds had been lost in transit by Fed-Ex. A follow-up telephone conversation on June 1, 2009 revealed the following: "On Friday May 22, 2009, a shipment of 70 I-125 seeds was prepared for shipment to the University of New Mexico - Albuquerque for patient implant on Friday May 29, 2009. The source strength was 30.3 mCi at the time of shipment. On May 26, 2009, Best Medical noticed that the shipment had not been received by the University and contacted Fed-Ex. Fed-Ex initiated a search for the material. Best Medical contacted Fed-Ex on May 27th and was told that Fed-Ex could not find the shipment. The patient's treatment has been postponed." * * * UPDATE FROM MIKE WELLING TO BILL HUFFMAN AT 1234 EDT ON 6/3/09 * * * The State of Virginia has clarified the original report it made to the NRC to note that the shipment was inadvertently directed to Windsor Locks, CT instead of Memphis TN. Specifically, the State reports the following update: "Further conversations on Wednesday, June 3 revealed the following: "On Tuesday, June 2, 2009 Fed-Ex found the I-125 package in Windsor Locks, CT. The package was shipped back to Best Medical and received on June 3, 2009. According to Fed-Ex, the I-125 package was not placed in the shipping container for Memphis, TN. The package had an incorrect URSA (routing) label [and] the package was then sent from Springfield, VA to Windsor Locks, CT [instead]." The R1DO (Perry) and FSME EO (McIntosh) have been notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2009-06-04
45108 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-06-01 09:25 | 2009-06-01 10:07 | 2009-06-01 | OFFSITE NOTIFICATION TO STATE AGENCY "On 04/22/09 Whole Effluent Toxicity test for Outfall 002 failed. South Carolina Department of Health and Environmental Control has been notified. Follow-up testing was completed and passed by the licensee." No media release is expected from this event. The licensee has notified the NRC Resident Inspector, and will be notifying the States of North Carolina and South Carolina. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-06-01
45107 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-05-31 13:30 | 2009-05-31 17:39 | 2009-06-02 | DEGRADED CONDITION DUE TO DISCOVERY OF PRESSURE BOUNDARY LEAKAGE "During the performance of 2-SI-3.3.1.A ASME Section XI System Leakage Test of the Reactor Pressure Vessel and Associated Piping (ASME Section III, Class 1 and 2), a pressure boundary leak was identified on the RHR Shutdown Cooling Root Valve (2-SHV-074-0049) at a weld between the valve body and a 3/4 inch schedule 160 pipe nipple. The pipe nipple is a 6 inch long capped valve leak off line. This valve and line are ASME Code Class 1 equivalent components located between the A recirculation piping and the inboard Shutdown Cooling isolation valve (2-FCV-074-0048). This condition caused entry into Technical Requirements Manual (TRM) 3.4.3 - Structural Integrity - Condition A - in which the applicability is at all times and the required action is to immediately restore the structural integrity of the affected component to within its limit or maintain the reactor in MODE 4 or 5 or the reactor coolant system less than 50?F above the minimum temperature required by NDT considerations, until each indication of a defect has been investigated and evaluated. The plant is currently in MODE 4 with Shutdown Cooling in service. "This event is reportable within 8 hours under 10CFR50.72 (b)(3)(ii)(A), 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' This event is also a reportable within 60 days under 10CFR50.73(a)(2)(ii)(A), 'Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' The NRC Resident Inspector has been notified. This condition has been documented in the BFN [Browns Ferry Nuclear] Corrective Action program as PER# 172551. "Unit 1 and 3 remain at 100% power and are not affected by this event." * * * UPDATE FROM W. BAKER TO P. SNYDER AT 1839 ON 6/2/09 * * * "Additional review of available data and inspection results revealed that the original identification of a 6 inch long ¥ inch diameter schedule 160 pipe nipple was part of the original design of the 2-SHV-074-0049. This connection to the valve body was subsequently modified by a design change documented in DCN S17640C and installed in 1992 by Work Order 92-49415-00 as a 2.55 inch long plug with a 0.800 inch tapered end, fabricated from bar stock to fit the existing valve socket weld cavity. All other details described in the original (REV 0) event notification remain as stated. The BFN Corrective Action PER# 172551 will be amended to include this additional information. "The NRC [Resident Inspector] has been notified of this event notification revision." Notified R2DO (Lesser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-05-31
45106 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-05-30 06:53 | 2009-05-30 07:39 | 2009-06-04 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA. Attempted introduction of contraband into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM JASON WEATHERSBY TO JOHN KNOKE AT 1040 EDT ON 06/04/09 * * * Licensee is retracting this event because there was no malevolent intent. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (Mark Lesser) and emailed ILTAB. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-05-30
45105 | 0 | ASCO VALVE INCORPORATED |  |  |  |  | 2009-04-29 | 2009-05-29 11:54 | 2009-05-29 | PART 21 FOR MISSING PARTS ON ASCO SOLENOID VALVES The following information was obtained from ASCO Valve QA Engineering via facsimile: On 4/24/09 ASCO Engineering was made aware of a non-conformance in the valve assembly area. During the assembly of a solenoid valve, part number NPEFKX8300141EG 10688 125/DC, the valve assembler noticed that the valve was missing an insulating barrier and a wiring label used with screw terminal coils. Neither item was included on the valve Bill of Materials. Purchase orders were reviewed and it was determined that North Anna Nuclear Power Station had purchased two of the subject valves. ASCO notified North Anna on April 27, 2009. ASCO has taken measures to prevent future occurrences. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0 | 2009-05-29
45104 | -1 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-05-28 21:40 | 2009-05-29 04:49 | 2009-06-08 | LOSS OF CONTROL POWER TO ECCS VALVES "At 2140 on 5/28/09 Braidwood Station identified a loss of control power for a Safety Related MCC (Motor Control Center) which provided power to SVAG (Single Valve Actuation Group) valves associated with both trains of the ECCS system. The MCC is normally de-energized to maintain the valve power removed in accordance with Tech Specs for ECCS. Loss of the control power for the associated MCC would prevent operation of these valves, which would prevent realignment of components required for transfer to cold leg recirculation and hot leg recirculation for long term core cooling. "Entry was made into LCO 3.5.2, ECCS Operating, and LCO 3.0.3 due to inoperability of both trains of ECCS based on the inability to realign portions of both trains of the ECCS system from injection to cold leg recirculation and subsequent hot leg recirculation. At 2230 on 5/28/09 preparations had been completed for ramp off line per LCO 3.0.3. "Troubleshooting was performed and a blown control power fuse was identified and replaced at 2319 on 5/28/09. No Unit ramp was initiated. "The NRC Resident Inspector was notified." * * * RETRACTION ON 6/8/09 AT 12:27 EDT FROM KELLER TO HUFFMAN * * * "The purpose of this report is to retract the ENS report made on May 29, 2009 at 04:49 EDT (ENS #45104) under 10CFR50.72(b)(3)(v)(B), a condition that could have prevented fulfillment of a safety function. "The initial report was made based on identification of a loss of control power for a Safety Related MCC (Motor Control Center), which provided power to SVAG (Single Valve Actuation Group) valves associated with both trains of the ECCS system. The MCC is normally de-energized to maintain the valve power removed in accordance with Technical Specifications. The loss of the control power for the associated MCC would prevent operation of these valves. It was initially concluded that this condition would prevent realignment of components required for transfer to cold leg recirculation and hot leg recirculation for long term core cooling. Therefore, the referenced ENS report was made for a loss of safety function. "Subsequent review of UFSAR information and previously developed analytical data determined that the safety function for ECCS was not lost due to the event. The failure of the MCC to energize would have NOT affected the ability of the 1B ECCS train to perform its design function of cold and hot leg recirculation. "A blown control power fuse, the cause of the event, was identified and replaced on May 28, 2009 at 23:19 hours. "The NRC Senior Resident Inspector has been notified of this retraction." R3DO(Pelke) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2009-05-29
45103 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2009-05-28 22:06 | 2009-05-29 03:37 | 2009-06-11 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM EXCESSIVE LEAKAGE "On 28 May 2009 the Control Room Emergency Filtration System (CREFS) was declared inoperable due to a degraded Control Room Envelope (CRE). Two CRE boundary doors were found with excessive leakage. Based on the identified leakage, reasonable assurance that CREFS would fulfill its safety function could not be established. "The CRE boundary doors support CREFS at CNS. CREFS is a single train system and per 10CFR50.72(b)(3)(v)(D) an 8 hour report is required due to the fact that at the time of discovery this condition could have prevented the fulfillment of the safety function of an SSC [system, structure or component] that is required to mitigate the consequences of an accident. "Actions to implement mitigating actions have been initiated in accordance with plant Technical Specifications. "The NRC Senior Resident Inspector has been notified of the condition." * * * UPDATE FROM KIRKPATRICK TO PARK AT 16:50 EDT ON 06/11/09 * * * The licensee is retracting this report based on the following: "This notification is being made to retract Event Notification EN# 45103 which reported a loss of safety function due to the unplanned inoperability of the Control Room Emergency Filtration (CREF) system. The CREF system was declared inoperable on May 28, 2009, due to a degraded Control Room Envelope (CRE). Two CRE boundary doors were found with excessive leakage and reasonable assurance that the CREF system would fulfill its safety function could not be established at that time. Cooper Nuclear Station (CNS) has subsequently determined through further testing that while the CREF system was procedurally required to be declared inoperable, the ability of the CREF system to perform its safety function was not lost. CREF system safety function is to maintain the habitability of the CRE following a loss of coolant accident or fuel handling accident involving handling lately irradiated fuel. "CNS performed testing on June 5, 2009. CRE adjacent building pressures were raised to create harsh conditions and one CRE door was cracked open to simulate a boundary leaking at about four times the CRE leakage of May 28, 2009. Testing results showed the CRE remained considerably more positive, in comparison to previous tracer gas testing performed in July 2004, and it is not credible the CRE unfiltered in-leakage exceeded maximum allowable limits. Thus, CNS determined the CREF system was still capable of performing its safety function during the timeframe when the two CRE boundary doors were identified leaking excessively. "The NRC Resident Inspector was notified of this retraction." Notified R4DO (Geoffrey Miller) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-05-29
45102 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-05-28 | 2009-05-28 18:55 | 2009-05-28 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN TRITIUM EXIT SIGN The following information was obtained from the licensee via email: "[The licensee] notified the [California Radiation Health Bureau] that a tritium exit sign had been stolen from a Roseville property they manage. The sign was an SRB Technologies Model 171-10-wh-s-gn." SRB Technologies Tritium exit signs typically contain 10-20 Ci of tritium. California Incident number: 5010-052809 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-06-02
45101 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-05-26 11:30 | 2009-05-28 18:10 | 2009-06-18 | AGREEMENT STATE REPORT - DAMAGED X-RAY FLOURESCENCE DEVICE The following information was obtained from the State of Nebraska via facsimile: "The Douglas County Health Department, a Nebraska licensee (license no. 01-45-01), reported that a Radiation Monitoring Devices, Inc. (RMD) Model LPA-1 portable x-ray fluorescence [XRF] device had been damaged on May 27, 2009. The XRF contained 12 millicuries of Cobalt-57. An authorized user left the XRF on a window sill and the XRF fell approximately eight feet to the floor. The XRF case was cracked in several pieces, but the integrity of the sealed source shield was not damaged. Radiation dose readings of the damaged XRF were within the expected range [for this device]. No individuals of the public or occupational workers were exposed as a result of this event. The licensee was able to return the XRF to its shipping container [which was placed in the] licensee's secured storage facility. The licensee was instructed to contact the manufacturer, perform a leak test and contact [the State of Nebraska] prior to shipping the XRF back to the manufacturer." Nebraska Event Report ID: NE-09-0011 * * * UPDATE FROM TRUDY HILL (VIA EMAIL) TO HOWIE CROUCH @ 0924 EDT ON 6/18/09 * * * "The licensee contacted RMD. RMD was satisfied with the reported low radiation dose readings, and the licensee was instructed to ship the XRF back in its storage container. The Nebraska Office of Radiological Health received written confirmation that RMD received the RMD LPA-1 XRF for decommissioning." Notified R4DO (Cain) and FSME EO (McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-06-02
45100 | 0 | WESTINGHOUSE ELECTRIC |  |  |  |  | 2009-05-28 | 2009-05-28 10:15 | 2009-05-28 | PART 21 REPORT - AIR CIRCUIT BREAKER DEFICIENCY The following information was received from Westinghouse via facsimile: Westinghouse provided information pursuant to the requirements to 10 CFR 21 to report an issue concerning the failure of a Westinghouse DB-100 circuit breaker to close after a new manufacturing cotter pin was installed during refurbishment. Westinghouse has supplied the air circuit breaker at nuclear generating stations. When a DB-100 air circuit breaker failed to close on demand, the air circuit breaker was returned to Westinghouse to investigate the cause of this failure. The air circuit breaker was successfully cycled several times at Westinghouse before the failure to close was repeated. Upon discovery of the DB-100 circuit breaker failing to close, Westinghouse identified plants that have purchased safety related DB-75 and DB-100 circuit breakers and reviewed the configuration of available breakers and drawings. Westinghouse has notified the affected plants which are: R. E. Ginna, Indian Point Unit 2, Point Beach and H. B. Robinson. Westinghouse will be issuing a Nuclear Safety Advisory Letter (NSAL) documenting this issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-05-28
45099 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-05-06 13:52 | 2009-05-28 08:59 | 2009-05-28 | AUTOMATIC ACTUATION OF RPS, ECCS AND EDG GENERATED BY AN INVALID ACTUATION SIGNAL "On May 6, 2009, Beaver Valley Power Station Unit 1 was in Mode 5 during a refueling outage. At 1352, a Low Steam Line Pressure Reactor Trip and Safety Injection (SI) signal was unexpectedly received on Train A. The Train A Emergency Diesel Generator started upon the SI signal, as designed, but did not load since there was no actual emergency bus low voltage condition. The Train A Charging pump (Emergency Core Cooling Pump) was in service and operating before the generation of the SI signal, and continued to operate following the SI signal. Other plant components not isolated for plant outage conditions properly actuated in response to the generated SI signal. "A SI Block must be inserted whenever the Solid State Protection System (SSPS) is operating in Mode 5 to prevent a SI signal from being generated on low steam line pressure since steam line pressure will be below the low steam line pressure setpoint. Since the plant was in Mode 5 (temperature less than 200F), there can be no steam in the steam lines. Thus, the receipt of a Low Steam Line Pressure Safety Injection signal while the plant was in Mode 5 was invalid. "It was determined that the SI Block was removed due to a degraded Steam Line Pressure SI Block/Reset switch on the control room benchboard. Further troubleshooting detected a similar erratic type degradation on the Train A Pressurizer SI Block switch. Both switches were replaced. "This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since it involved an actuation of the Reactor Protection System (RPS) per 10 CFR 50.73(a)(2)(iv)(B)(1), an Emergency Core Cooling System (ECCS) pump per 10 CFR 50.73(a)(2)(iv)(B)(3), and an Emergency Diesel Generator (EDG) per 10 CFR 50.73(a)(2)(iv)(B)(8). However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification, instead of submitting a written Licensee Event Report, since the automatic actuation of the RPS, ECCS Pump and EDG was not generated by a valid actuation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-05-28
45098 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-05-28 06:25 | 2009-05-28 07:12 | 2009-05-28 | AUTOMATIC REACTOR TRIP RESULTING FROM A HIGH STEAM GENERATOR LEVEL TURBINE TRIP "At 0530 EDT a power reduction commenced due to elevated vibrations on 32 MBFP [Main Boiler Feedwater Pump]. When reactor power reached 60% the team was attempting to stabilize reactor power when a level excursion occurred in 32 steam generator. When level reached its high level turbine trip set point an automatic reactor trip occurred and all systems responded as expected. Auxiliary feedwater actuated as expected. The Unit is currently in mode 3 and stable with auxiliary feed water in service and reactor temperature maintained with the steam dumps to the main condenser. Investigation into the cause of the steam generator level excursion is in progress. Offsite power is available and supplying safeguard busses. Unit 2 was unaffected and remains at 100% power. The [NRC] Resident Inspector has been notified." No safety or relief valves lifted during this event. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-05-28
45097 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-05-27 19:04 | 2009-05-27 22:12 | 2009-05-27 | REACTOR TRIP FROM POWER RANGE HIGH NEUTRON FLUX RATE "At approximately 1904 on 05/27/09, Sequoyah Unit 2 received an Automatic Reactor trip on Power Range High Neutron Rate Reactor Trip. The automatic trip occurred during severe weather and lightning onsite. ESF functions initiated as designed including Aux Feed Water auto-start and automatic Feedwater isolation. All control rods fully inserted. The plant is currently being maintained in Mode 3 at approximately 547 degrees F 2235 PSIG. Decay heat is being removed by the Auxiliary Feedwater system and Steam Dump valves. "The cause of the Power Range Neutron Flux High Rate Reactor Trip is not known at this time and investigation is ongoing. "Unit 1 remains at 100% power". No relief or safety valves lifted. The electrical lineup is normal and the 2B Diesel Generator is tagged out for maintenance. The licensee has contacted the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-05-27
45096 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-05-26 | 2009-05-26 17:17 | 2009-05-26 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK OPEN The following was received from the State of Massachusetts via fax: "A gauge on the Z-24 press is sometimes stuck open. The equipment is out of use. A licensed contractor was contacted to fix the gauge. Gauge s/n Z3239, model number SS-3a. Radionuclide is 1000 mCi of Am-241." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-05-29
45095 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-06-06 | 2009-05-26 14:59 | 2009-05-26 | AGREEMENT STATE REPORT - DROPPED RADIOGRAPHY DEVICE The following was received from the State of Washington via e-mail regarding a previously unreported event: "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "A radiography crew was attempting to hoist a Co-60 radiography device to an elevated platform to perform work at an oil refinery. During the process of hoisting the device it slipped out of its rigging and fell an estimated 23 feet to the pavement below. No associated equipment was connected to the device and the plugs were still inserted. The metal flange on the device was dented but there was no other obvious damage. The device is an AEA model 741B, serial number B100. It contained a 5.5 Curie Co-60 Model 424-18 AEA source, serial number 2418. "A radiation survey was performed by the radiography companies' crew and later by the RSO. The readings were normal for that device. A control cable was attached to the source inside the device and the source was rotated. It was determined to move freely and not bound in the shielded position within the device. Operations with this device were terminated and the device was sent back to its licensed storage location in Burlington, Washington. The radiography company sent the device back to QSA Global for evaluation and maintenance. "The licensee's RSO stated that repairs were made to a bracket and the handle was replaced. The maintenance was performed. The device was resourced and relabeled and returned to the licensee. "This incident, given [Washington state] report number WA-06-043 is closed. There was no release of activity. Personnel exposure was kept low so that no exposure limits were exceeded." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-05-29
45094 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2009-05-26 | 2009-05-26 14:51 | 2009-05-26 | SAFEGUARDS EVENT - VULNERABILITY IN VITAL AREA Discovered vulnerability in a safeguards system that could have allowed access to a controlled access area for which compensatory measures have not been employed. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-05-26
45093 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-05-26 12:28 | 2009-05-26 13:56 | 2009-05-26 | OFFSITE NOTIFICATION DUE TO FAILED NPDES EFFLUENT SAMPLE "The quarterly National Pollutant Discharge Elimination System whole effluent toxicity testing for Outfall #001 failed for the 2nd quarter of 2009. This required notification to the South Carolina Environmental Agency. "The system is the Low Pressure Service Water (RL) discharge. The licensee will be contacting the NRC Resident Inspector. "A toxicity evaluation is being performed by an outside lab." In addition to South Carolina, the licensee notified the State of North Carolina and York, Gaston, and Mecklenburg counties. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-05-26
45092 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2009-05-25 16:50 | 2009-05-25 21:32 | 2009-05-25 | INOPERABLE RCIC PRIMARY CONTAINMENT ISOLATION VALVES "The Reactor Core Isolation Cooling (RCIC) system tripped on high turbine exhaust discharge pressure during surveillance testing on May 24, 2009. Following the surveillance it was identified that the containment (torus) inboard stop check valve in the RCIC turbine exhaust line could not be closed, necessitating the shutdown of Unit 1 to perform repairs on this inboard isolation valve. At 1650 hours on May 25, 2009, with the unit shutdown, inspections revealed that the inboard isolation valve could not close due to [the presence of] valve material originating from the containment (torus) outboard swing check isolation valve in the turbine exhaust line. Given the inspection findings it has been concluded that neither the inboard stop check valve or the outboard swing check valve in the RCIC turbine exhaust line would have performed their primary containment isolation function while the unit was at power, [thus] impacting containment integrity. As a result, this event is being reported in accordance with 10 CFR 50.72 (b)(3)(ii) for a degraded or unanalyzed condition. The inboard and outboard containment isolation valves in the RCIC turbine exhaust line will be repaired prior to unit startup. The NRC Resident Inspector has been notified of this condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-05-25
45091 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-05-20 | 2009-05-22 13:30 | 2009-05-22 | AGREEMENT STATE REPORT - SHUTTER ON GAUGE INOPERATIVE "On March 21, 2009, at 1050 AM, the Agency [Texas Department of Health] received a report from the licensee that while performing the biannual test on a Ronan Engineering nuclear gauge, model # SA-1, containing an original activity of 100 millicuries (calculated current activity of 75 millicuries) of Cesium (Cs) - 137, the shutter failed to close. The gauge is installed on the side of a vessel approximately 50 feet above ground and is used for level detection. A dose rate measurement taken at the gauge indicated 0.03 millirem per hour, and poses no risk of radiation exposure to their workers. The manufacturer has been contacted to provide corrective maintenance on the shutter." Texas Incident # I-8635I | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-05-27
45090 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2009-05-20 15:00 | 2009-05-22 12:42 | 2009-09-16 | LICENSE CONDITION REPORT INVOLVING SNM ACCOUNTABILITY "Facility: Westinghouse Electric Company LLC (WEC), Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt.% U-235) fuel fabricator for commercial light water reactors. License: SNM-1107. "Time and Date of Event: May 20, 2009, approximately 1500. "Reason for Notification & Sequence of Events: "Notification made based on Materials License Number SNM-1107, Safeguards Conditions Section 1.0 Material Control and Accounting, SG-1.1 which states in part; 'The licensee shall follow Chapters 1.0 through 9.0 of its 'Fundamental Nuclear Material Control Plan for the Columbia Fuel Fabrication Facility.' The Fundamental Nuclear Material Control Plan, Section 2.2.2 contains specific requirements for notification for issues related to resolving item and/or material control anomalies. "The Environment, Health and Safety (EH&S) Department was informed that a small scrap fuel pellet container containing uranium, which is Special Nuclear Material (SNM), could not be readily located. The anomaly was identified by operations personnel conducting a routine weekly audit of SNM-bearing items. Initial investigation and search efforts did not locate the SNM, which was in a small container (approximately 8 inches in diameter x 8 inches tall) used for routine processing, commonly called a 'polypak.' "Personnel independent of the affected area conducted a Material Balance Inventory, which concluded that the SNM did not leave the area. The Material Balance results and findings were reviewed by an independent contractor, a Material Control and Accounting expert who agreed with the conclusion and methodology used. Based on this material balance and other investigative actions conducted by WEC, there is no indication that the material left the affected area, and the SNM was processed through the normal scrap process flow. "Safety Basis: There are no actual or potential health or safety consequences to the workers, the public or the environment. "As Found Condition: See Reason for Notification. "Summary of Activity - Operations in the affected manufacturing area were halted and the area was extensively and systematically searched by Operations, Management and EH&S personnel. - The empty container was located within the affected manufacturing area. - Retraining on item control requirements for production personnel was completed prior to restart of production activities. - Enhanced accountability and control measures for item control of scrap containers was completed prior to restart of production activities. - An investigative review team was assembled and interviewed personnel in the affected manufacturing areas to determine the cause of the item control discrepancy. - The event was entered into the WEC Corrective Action Process and a formal Root Cause Analysis was completed. - Interim corrective actions have been completed and longer term corrective actions have been initiated to reduce the likelihood of a repeat occurrence based on the results and recommendations of the Root Cause Analysis." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2009-09-17
45089 | -1 | ST. JOHNS MERCY MEDICAL CENTER |  |  |  |  | 2009-05-21 15:30 | 2009-05-22 09:51 | 2009-05-22 | MEDICAL EVENT INVOLVING A DOSE THAT IS DIFFERENT THAN PRESCRIBED The patient was undergoing brachytherapy treatment of the prostate. After 6 seeds were implanted, the procedure was aborted because of concerns in placing additional needles into the patient. The prescribed dose was 145 Gy. However, only 6 of 88 prescribed seeds were implanted. Each seed total activity is 0.288 mCi of I-125. Family members were notified of the aborted procedure. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM ROBERT TURCO TO JOHN KNOKE AT 1643 EDT ON 5/22/09 * * * This event is being retracted because the physician made a choice to terminate the brachytherapy treatment of the prostate to the patient. The physician then rewrote the procedure to the patient to limit the prescribed number of seeds to 6. Having 6 seeds implanted into the patient the prescribed dose was now met under the new directive. Notified R3DO (Richard Skokowski) , FSME(Lydia Chang) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-05-28
45088 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2009-05-21 20:15 | 2009-05-21 23:09 | 2009-05-21 | RPS ACTUATION (REACTOR TRIP) DUE TO GENERATOR PHASE DIFFERENTIAL LOCKOUT "Event: Oconee Unit 3 Reactor Protection System (RPS) actuation due to Anticipatory Trip. "At 2015 hrs on 5-21-2009, Oconee Nuclear Station Unit 3 experienced a RPS actuation due to an anticipatory trip caused by a generator phase differential lockout. At the time of the RPS actuation, Unit 3 was exiting a planned refueling outage and power was at 42%. Immediately after the trip, Operators entered the appropriate emergency operating procedure and post-trip response was determined to be normal. Operators transitioned to the normal shutdown procedure at 2056 hours. Unit 3 is currently in Mode 3 and stable. "This event is being reported as a 4-Hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). "Initial Safety Significance: No Emergency Action Limits (EALs) were met and there was no safety significance as a result of the Unit 3 trip. Units 1 and 2 remain at 100% power (Mode 1) and were unaffected by the Unit 3 trip. "Corrective Actions(s): Planned corrective actions are to maintain Unit 3 in Mode 3 (Hot Standby) until completion of the post-trip evaluation. The NRC Resident Inspector has been notified." All control rods fully inserted. The reactor is currently subcritical and shutdown margin within Technical Specification limits. RCS Inventory Control is via normal makeup. PORV and Pressurizer Code Safeties are closed. SG inventory control is being maintained via Main Feedwater. Heat is being removed from the Steam Generators to the Main Condenser via Turbine Bypass Valves. | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-05-21
45087 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2009-05-21 16:35 | 2009-05-21 20:46 | 2009-05-21 | RPS ACTUATION (SCRAM) DUE TO A MAIN POWER TRANSFORMER FAULT "At 1635 CDT on May 21, 2009, LaSalle Unit 1 automatically scrammed due to a main power transformer fault. The transformer fault appears to have been caused by a failed bushing or lightning arrestor. The main power transformers deluged and other than the initial flash, there was no fire. Two safety relief valves actuated in the relief mode on the turbine trip. There were spurious non-valid isolation signals due to electrical power perturbations that were received on the reactor building ventilation system and reactor water cleanup. The plant is stable with reactor pressure control to the main condenser via the turbine bypass valves. The plant [will] remain in hot shutdown pending transformer inspection and repair." All control rods fully inserted following the scram signal. Water level is being controlled via the motor driven reactor feedwater pump. Current reactor pressure is 927 psig and current reactor temperature is 532 degrees F. The plant is in a normal post-trip electrical lineup. No diesel generators started as a result of this event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-05-21
45086 | -1 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2009-05-21 11:10 | 2009-05-21 11:58 | 2009-06-30 | SAFEGUARDS REPORT - INOPERATIVE FIRING PIN Site security determined that a contingency weapon had an inoperative firing pin. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM DAVE LANY TO JOHN KNOKE AT 1221 EDT ON 5/22/09 * * * Site security completed inspections with no other discrepancies noted. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (Robert Haag) and 73.71 group. * * * RETRACTION ON 6/30/09 AT 1100 EDT FROM HESSLING TO PARK * * * "Based on the results of the investigation, FPL is retracting the one hour NRC notification as the issue no longer meets requirements for reporting under 10 CFR 73.71." The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. R2DO (McCoy) and 73.71 group notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-05-21
45085 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-04-09 01:15 | 2009-05-21 10:13 | 2009-05-21 | OPTIONAL 60-DAY TELEPHONE REPORT OF AN INVALID START OF ALL FOUR EMERGENCY DIESEL GENERATORS "This report is being made under 50.73(a)(2)(iv)(A). "At the time of the event, Unit 1 was Defueled/No Mode and Unit 2 was 100% Power/Mode 1. "On 04/9/09 @ 0115 an invalid start of the four emergency diesel generators occurred. The actuation was caused by inadvertent actuation of the K609 relay. The K609 relay causes an emergency start of the diesel generators on a SI [Safety Injection] signal. The actuation of the K609 relay was caused by technicians inadvertently depressing the K609 relay latch pushbutton while working on a nearby K604 relay. The K609 relay is located just below the K604 relay in the same SSPS [Solid State Protection System] panel. "The train actuated was both Train A and Train B for both Units 1 and 2. The system actuated was the emergency diesel generators. Complete train actuation occurred. The emergency diesel generators started successfully." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-05-21
45084 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-05-18 | 2009-05-20 16:23 | 2009-07-09 | AGREEMENT STATE REPORT - STUCK SHUTTER The State provided the following information regarding a previously unreported event received via e-mail: "On May 19, 2009, the Department was notified by the licensee of a stuck shutter. The gauge is a Kay-Ray Model 7063S, Serial S97D2115, containing 100 millicuries of Cesium-137. The gauge was originally installed in 1997. The stuck shutter was discovered during routine shutter checks on May 18, 2009. The licensee tried to release the shutter, but was unable to do so and is currently working to schedule a service provider for repair. The licensee is maintaining control of the area where the gauge is installed." * * * UPDATE FROM ROBERT PEMBERTON TO JOE O'HARA AT 1538 ON 7/9/09 * * * The State provided the following information via e-mail: "The following are the findings of the Arkansas Department of Health, Radioactive Materials Program, concerning event Number 45084 at Albemarle Corporation in Magnolia, AR. From information provided by Albemarle Corporation and ThermoFisher Scientific, the Department has determined that this event was caused by the use of an improper lubricant that deposited a residue, over time, and interfered with the rotation of the shutter. The technician noted, at the time, that the gauge housing had been installed upside down, and that this may have contributed to the shutter sticking. Both ThermoFisher's report, dated June 11, 2009, and Albemarle Corporation's report, dated June 15, 2009, concur with the Department's observations; that the technician was able to close the shutter and then reinstalled the gauge in its proper orientation. No personnel exposures occurred during this incident. The Department has concluded that the root cause of this incident is improper maintenance. The Department considers this incident to be closed. " Notified R4DO(Hay) and FSME EO(Vontill). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-05-25
45083 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-05-20 15:30 | 2009-05-20 17:26 | 2009-05-20 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The State sent this event via fax: "Radiography was being performed by American Engineering and Testing at Midwest Tank in Big Lake, Minnesota when after performing an exposure, the 41.4 curie, Ir-192 source would not retract back into the camera. The radiographer attempted numerous times to retract the source and was unsuccessful. The radiographer and radiography's assistant performed surveys and reset the boundaries. The RSO for the Minnesota license was called at 1300. The RSO had performed the source retrieval and it was secured back in the camera at 1420. MDH received a call at 1530 providing notification of the incident. Preliminary cause was a kink in the guide tube. Minnesota RSO who performed the retrieval will be notified tomorrow for additional information. A written report will be required within 30 days of notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2009-05-25
45082 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-05-19 08:30 | 2009-05-20 15:14 | 2009-05-20 | AGREEMENT STATE REPORT - UNACCOUNTED FOR SEALED SOURCES The Commonwealth of Massachusetts provided the following information via facsimile: The Commonwealth dispatched an inspector to a general licensee facility to conduct an inspection of their thickness gauges. Upon arrival, the inspector discovered that the licensee had undergone bankruptcy in 2007 and the facility was being demolished by a national liquidation company. The building that the gauges were supposed to be stored in had already been demolished. The 12 thickness gauges were NDC Systems Model #103 and each contained 150 mCi of Am-241. The Commonwealth of Massachusetts has notified local scrap yards and material recyclers and will be continuing their investigation. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Less than Cat 3" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-05-25
45081 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2009-05-19 15:00 | 2009-05-19 16:13 | 2009-05-19 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) COMPUTER HARDDRIVE OUT OF SERVICE "The Emergency Response Data System (ERDS) Computer hard drive has failed. It is expected to be returned to service by the end of the week." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-19
45080 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-05-19 09:00 | 2009-05-19 15:11 | 2009-05-19 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) DUE TO NETWORK SERVICE NOT FUNCTIONING "On May 19, 2009, it was identified that ERDS was unavailable for approximately 65 minutes (0900 - 1005 hours CDT). It was determined that a network service responsible for broadcasting ERDS data was not functioning. ERDS was restored when the network service was restarted. The cause of the service interruption is under investigation. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a major loss of communications capability. "The NRC Resident Inspector has been notified." The State of Illinois will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-19
45079 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-05-18 08:45 | 2009-05-19 12:34 | 2009-05-21 | RADIOGRAPHY SOURCE STUCK IN THE UNSHIELDED POSITION The state reported that two radiographers from Team Industrial Incorporated, were performing radiography on some bend joints at the Dakota Gasification Plant (DGP). Following a number of radiography shots, the radiographers attempted to fully retract the source and were unsuccessful. The radiographers expected to retract the source in approximately 4 cranks. However, they were only able to retract approximately 3.5 cranks. The corporate RSO at the site was notified. Barriers were erected and lead shielding has been deployed around the source. Each worker received approximately 30mR. The licensee contacted QSA Global, who has arrived on site and is going to retrieve the source. The device is identified as a SPEC150, S/N 0129 with a 90 curie Ir-192 source. * * * UPDATE FROM LOUIS ROEHRICH TO HOWIE CROUCH @ 0020 ON 5/20/09 * * * The State of North Dakota reported that the licensee and technicians from QSA were not able to retrieve the source. Currently, the source is shielded and boundaries have been established. Personnel have been assigned to monitor the boundaries throughout the night. The QSA representatives are expecting delivery of a drum tool and source change tool in the morning to retract/retrieve the source. Notified R4DO (Jones) and FSME EO (Chang). * * * UPDATE FROM LOUISE ROEHRICH TO DAN LIVERMORE @ 0903 ON 05/20/09 * * * The State of North Dakota reported that the drum tool and source change tool will arrive via FedEx on 05/21/09. The area remains controlled with barriers erected. Notified R4DO (Jones) and FSME EO (McIntosh). * * * UPDATE FROM LOUISE ROEHRICH TO DONALD NORWOOD @ 1953 ON 05/21/09 * * * The State of North Dakota reported by telephone that the source had been fully retracted back into the camera. The camera will be taken to Minnesota tomorrow by Team Industrial personnel. After arrival in Minnesota the camera will be shipped to QSA for evaluation and repair. This incident did not result in any injuries or any excess exposures. Notified R4DO (Jones) and FSME EO (Chang) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2009-05-22
45078 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-05-18 14:00 | 2009-05-19 10:31 | 2009-06-03 | FALSE POSITIVE ERROR ON A BLIND SAMPLE The licensee received notification of a false positive error on a blind sample. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 6/03/09 AT 1407 EDT FROM GRASSANO TO HUFFMAN * * * After further investigation into this event, the licensee has determined that the blind sample test was an invalid test and not a false positive error as originally reported. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. R2DO (Lesser), NMSS EO (Silva), and a copy sent to the Fuels OUO group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2009-05-20
45077 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2009-05-18 13:05 | 2009-05-18 14:41 | 2009-05-18 | TURBINE TRIP/REACTOR TRIP DUE TO CONDENSER VACUUM "Prairie Island Unit 1 experienced an automatic turbine and reactor trip following a lockout trip of [the] 12 Circulating Water Pump. Lockout of the circulating water pump resulted in a condenser A/B differential pressure trip of the main turbine which in turn caused an automatic reactor trip. Auxiliary Feedwater Pumps automatically started on low steam generator level. All control rods fully inserted. Decay heat removal is via auxiliary feedwater and condenser steam dump. Offsite power was maintained to safeguards and non-safeguards AC buses. Operations are in progress per Reactor Trip Response emergency procedures to stabilize plant conditions, restore main feedwater flow to the steam generators, and then shut down auxiliary feedwater pumps. The plant will then be maintained per normal shutdown procedures until the cause of the trip is corrected." No safety or relief valves lifted during the transient. There was no impact on Unit 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-05-18
45076 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2009-05-18 04:50 | 2009-05-18 05:06 | 2009-05-20 | TSC HVAC RENDERED NON-FUNCTIONAL DUE TO PLANNED MAINTENANCE "At 0450 on Monday, May 18, 2009, power was removed to the Peach Bottom Atomic Power Station (PBAPS) Technical Support Center (TSC) ventilation system for planned preventative maintenance activities on the Unit 1 480VAC Load Center 10B014. During the 10B014 bus outage work activities, temporary power will be supplied to maintain all TSC facility equipment functional with the exception of TSC Normal and Emergency Ventilation. The TSC Supply, Exhaust and HEPA Filter fans will be de-energized, rendering the TSC HVAC non-functional while planned maintenance activities are in progress. This maintenance is scheduled to be worked continuously until completion to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 48 hours, including a total of 5 hours to establish and remove the clearances. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing EP procedures and checklists. It will take no more than 4 hours to return the Ventilation system back to an operable status, dependent on the stage of the work at the time the emergency occurs. If radiological conditions require TSC facility evacuation during ventilation system restoration, the Station Emergency Director will evacuate and relocate the TSC staff in accordance with, EP-AA-112-200-F-01. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BRAD KIRKMON TO HOWIE CROUCH @ 0400 EDT ON 5/20/09 * * * "This is a follow-up courtesy notification to EN# 45076. All scheduled work to the Unit 1 480VAC Load Center 10B014 is complete, with [the] exception of relay trip testing. Bus restoration has been delayed due to differences between the newly installed transformer and the old transformer, which required changes to the clearance. TSC facility restoration to normal power, including Normal and Emergency Ventilation system operation, is scheduled to occur on 5/20/09 day shift. "The [NRC] Resident Inspector has been notified." Notified R1DO (Jackson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-18
45075 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-05-17 09:21 | 2009-05-17 14:29 | 2009-05-19 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE LOSS OF EMERGENCY DIESEL GENERATOR "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Required Action B.2. The Functionality of the Technical Support Center (TSC) has been lost due to failure of the Backup Diesel Generator (which provides backup power to TSC related equipment) to pass a required surveillance. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. The NRC Resident Inspector Tim Chandler has been notified." * * * UPDATE ON 5/19/09 AT 1615 FROM ROBERT ROWLAND TO VINCE KLCO * * * At 1559 the Backup Diesel Generator was declared operable. The licensee will notify the NRC Resident Inspector. Notified the R2DO (Henson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-17
45074 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-05-17 03:35 | 2009-05-17 05:24 | 2009-05-29 | MANUAL REACTOR SCRAM DUE TO LOSS OF SCRAM AIR HEADER "At 0335, Hope Creek was manually scrammed due to indications of multiple control rods drifting. All rods indicate fully inserted. Reactor level is being controlled in the normal band with Start-up level control in automatic. Reactor pressure is being controlled by bypass valves to the main condenser. Recirc pumps are in service and no ECCS system actuations were reached. The failure is a solder joint on the air supply to HCU 22-15. A manual scram was reinserted at 0445 to mitigate the air leak." The licensee reset the scram to re-pressurize the scram air header. Once the leak was located, a second manual scram signal was initiated to secure the leak. No safety relief valves lifted during the transient. The electrical grid is stable and the plant is in a normal shutdown electrical lineup. The licensee will be notifying the Lower Alloways Creek Township and has notified the NRC Resident Inspector. * * * UPDATE ON 5/17/2009 AT 0552 FROM MICHAEL REED TO MARK ABRAMOVITZ * * * The failure was on HCU 22-11 not 22-15. The licensee notified the NRC Resident Inspector. Notified the R1DO (Holody) via e-mail. * * * UPDATE ON 5/29/2009 AT 1133 FROM JIM PRIEST TO VINCE KLCO * * * "On 5/17/09, at 0335, Hope Creek automatically scrammed due to low Reactor Pressure Vessel water level approximately two seconds prior to locking the Reactor Mode Switch in Shutdown due to indications of multiple control rods drifting. All rods indicate fully inserted. Reactor level is being controlled in the normal band with Start-up level control in automatic. Reactor pressure is being controlled by bypass valves to the main condenser. Recirc. Pumps are in service and no ECCS system actuations were reached. The failure is a solder joint on the air supply to HCU 22-11. A manual scram was reinserted at 0445 to mitigate the air leak." The licensee notified the NRC Resident Inspector. Notified the R1DO(Dentel). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-05-17
45073 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-05-16 18:01 | 2009-05-16 20:04 | 2009-07-16 | FAILURE OF HIGH PRESSURE COOLANT INJECTION STEAM SUPPLY VALVE TO CLOSE DURING TEST "At 1801 on 5/16/2009, the HPCI turbine steam supply valve (HV255F001) failed to close during shutdown of the system following performance of its quarterly flow surveillance. The auxiliary oil pump was de-energized to prevent an inadvertent start of HPCI and the HPCI system was declared inoperable. "LCO 3.5.1 for the HPCI system being inoperable was entered at 1720 on 5/16/2009 at the start of the HPCI surveillance. "An investigation is in progress to determine the nature of the problem. "This is being reported as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident in accordance with 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 7/16/09 AT 1543 FROM TODD CREASEY TO CHARLES TEAL * * * "On May 16, 2009, the HPCI system was declared inoperable at 1720 hours and LCO 3.5.1 was entered to support the planned quarterly HPCI flow surveillance test. During the surveillance test, at 1801 hours, the HPCI turbine steam supply valve (HV255F001) failed to close during shutdown of the system. It was also identified that neither the open nor closed indication lamp in the control room were lit. Troubleshooting was performed by cycling the valve's breaker in an attempt to restore power to the HPCI steam supply valve. No movement of the valve was observed. Because the position of the HPCI steam supply valve was unknown, Operations secured HPCI by opening the auxiliary oil pump breaker for the purpose of conducting additional troubleshooting (maintenance) of the failure of the HV255F001 valve to close. On 5/16/09 at 2004 hours EDT, Susquehanna made an 8-hour ENS notification (45703) to the NRC, due to HPCI being declared inoperable when HV255F001 failed to close during performance of the quarterly surveillance. "Subsequent investigation concluded that the HPCI turbine steam supply valve (HV255F001) did close as expected, but did not indicate closed due to a loss of position indication. It was determined that the closed indicating lamp had burned out. Upon replacement of the lamp, the valve was successfully stroked open and closed and HPCI was declared operable at 0800 EDT 5/17/2009. "Because a condition did not exist at the time of discovery that could have prevented the fulfillment of a safety function in accordance with 10 CFR 50.72(b)(3)(v)(D), EN #45073 is hereby being retracted. "It should be noted that the subsequent action to disable HPCI by opening the auxiliary oil pump break does not preclude retraction of the ENS notification. This action did not create a new reportable condition since HPCI was already inoperable for planned surveillance testing. This action was taken as part of troubleshooting activities (maintenance) on the HV255F001 valve and to prevent an inadvertent start of HPCI. The NRC Resident has been notified. Notified R1DO (Gray) | 0 | 13 | 0 | 0 | 13 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-05-16
45072 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2009-05-15 19:42 | 2009-05-15 21:37 | 2009-05-15 | 21 OF 44 SIRENS OUT OF SERVICE DUE TO SEVERE WEATHER "On May 15, 2009 CPS was notified by the maintenance vendor that 21 EPZ sirens are out of service. This is 48% of the EPZ sirens out of service for greater than 1 hour as of 1942 CDT, due to severe weather and power outages. " The licensee notified the Illinois Emergency Management Agency and the NRC Resident Inspector. * * * UPDATE FROM RICHARD KISS TO PETE SNYDER ON 5/15/09 AT 2304 * * * "As of 2130 CST only 2 sirens remain out of service which is below the 25% out of service requirement of 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. Notified R3DO (Kunowski). | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-15
45071 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-05-15 05:19 | 2009-05-15 10:13 | 2009-05-15 | GROUP 1 ISOLATION OF ALL MAIN STEAM VALVES WHILE PERFORMING A SPECIAL PROCEDURE "At 0519 on 5/15/09, a Group 1 isolation signal was received which resulted in all eight Main Steam Isolation Valves closing. The signal was received based upon a valid main condenser low vacuum signal coincident with reactor mode switch placed in RUN position. The isolation was an unanticipated result of a special purpose procedure which was being performed as a functional test for maintenance work that had been performed on intermediate range nuclear instrumentation. The procedure had installed jumpers to bypass the Group 1 isolation for Mode Switch in Run, but did not account for low condenser vacuum isolation. The low condenser vacuum switches were in the bypass position, but this logic does not prevent Group 1 isolation in the Run mode. The Group 1 isolation was completed successfully with all MSIVs and small bore valves closing as designed. MSIV closure with Mode Switch in Run position also caused a RPS actuation / full scram. The reactor was subcritical and all control rods were already fully inserted as the reactor was being maintained in Cold Shutdown." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-05-15
45070 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  |  | 2009-05-12 | 2009-05-15 09:38 | 2009-05-15 | EXTERNAL CONTAMINATION FOUND ON MODIFIED SEALED SOURCE The following information was obtained from the licensee via facsimile: "One of the research projects at NIST involves research and testing of different types of bomb detection instruments. One of the experiments required that the source be removed from one of the instruments. Prior to January 2008, Researcher 1 spoke to the RSO for Smiths Detection in Canada. They discussed the possibility of removing the 15 mCi Ni-63 source from their instrument, an lonScan 400b, sealed source device number ND-0163-D-1014-G. The Smiths RSO approved this and sent schematics to assist with the project. Researcher 1 then started planning the project with NIST Health Physics review. It was decided that Health Physics would monitor this project to confirm that there was no unanticipated exposure or contamination resulting from the operation. On January 31, 2008, Researcher 1 began the process for source removal. Work was performed in a hood, in a controlled laboratory space, with a health physicist monitoring the operation. The process of source removal was based on the manufacturer schematics. These schematics were general and not a specific instruction for source removal. No information was available at the time that clearly defined the source encapsulation barrier. After a ceramic cap was removed, the side of the source holder was wiped and contamination was detected. It is believed that the wipe may have touched some of the nickel foil. Upon observing the way the source was placed in the ceramic in addition to the contamination detected, it was decided that it was not possible to safely modify the device in the intended manner. The ceramic head was reattached and reinserted into the box. External swipes were verified to be clean. It was decided to leave the source this way while it was determined if there was anything more they could do to meet the intended research results. It is believed that the sealed source containment was breached in the experiment thereby negating the manufacturer's sealed source certificate. In doing this, it became an unsealed source. The reassembly restored containment. The device was placed into secured storage. "On May 12, 2009 wipes were taken of the external portion of the ceramic head and confirmed contamination of 72 nCi. A wipe was taken at the manufacturers recommended typical sealed source leak check location and was clean. The source box was collected for disposal. The hood, all items in the hood, and the floor were checked for potential contamination. They were verified to be clean. "It is unclear whether this constitutes a reportable sealed source leakage situation with respect to 10CFR31.5c, since this occurred during an intended and controlled effort to modify the source configuration. The levels of unsealed source activity are within the limits prescribed in our license, SNM-362." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | MD | MAT | [5 empty] | 0 | 2009-05-15
45069 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-05-15 01:53 | 2009-05-15 03:58 | 2009-05-15 | MANUAL REACTOR TRIP DUE TO FAILURE OF THE MAIN FEEDWATER REGULATING VALVE "On May 15, 2009 Indian Point Unit 3 initiated a manual Reactor Trip at 0153 in response to a failure of 33 Main Feed Regulating Valve. 33 Main Feed Regulating Valve failed open causing 33 Steam Generator Level to rise. A manual Reactor Trip signal was inserted when it was determined that the level rise in 33 Steam Generator could not be corrected. As a result of the reactor trip, the Auxiliary Feedwater System automatically actuated per plant design. Unit 3 is currently in Mode 3. "This results in a condition that resulted in an actuation of the Reactor Protection System which is reportable under 10 CFR 50.72(b)(2)(iv)(B). "The valid actuation of the Auxiliary Feedwater System is reportable under 10 CFR 50.72(b)(3)(iv)(A)." All rods inserted during the trip. There were no relief or safety valves that lifted during the transient. The electrical grid is stable and is in the normal shutdown electrical lineup. The plant is being maintained at normal operating temperature and pressure using steam dumps to condenser to remove decay heat. Unit 2 was not affected by the trip. The licensee notified the New York Public Service Commission and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-05-15
45068 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-05-14 14:15 | 2009-05-14 18:16 | 2009-05-14 | MISSING MOVEABLE INCORE DETECTORS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "During an extent of condition assessment of Special Nuclear Material (SNM) control and accounting, seven moveable incore detectors (MID) were identified not to be controlled under the Material Control and Accounting (MC&A) program as required by 10 CFR 74. Four of the MIDs have been located in the Dry Active Waste Processing and Storage (DAWPS) facility. Three MIDs each containing approximately 2 milligrams of Uranium 235 (U235) have not been located, however, efforts continue to locate these detectors. One MID was removed from the MC&A program in 1986 and the other two were removed from the MC&A program in 1995 when they were removed from the units. "The NRC Resident Inspector has been notified of the loss and the event notification. "The information contained within this ENS is considered to be Security Sensitive and should be handled accordingly." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 74.11(a) |  |  |  | 1 | 2009-05-14
45067 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-05-14 09:53 | 2009-05-14 16:58 | 2009-05-14 | FITNESS FOR DUTY INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive test for alcohol during a For-Cause fitness-for-duty test. The employee's access to the plant has been temporarily suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2009-05-14
45066 | 0 | BELLEFONTE | 1 | 2 |  | [1] B&W-R-LP (205),[2] B&W-R-LP (205) | 2009-05-14 10:45 | 2009-05-14 11:45 | 2009-05-14 | CONFIGURATION CONTROL LAPSE "DESCRIPTION OF DEFICIENCY "Configuration control was not maintained and physical equipment issues were not documented under a Quality Assurance Plan for the period of time from in which Construction Permits CPPR-122 and CPPR-123 were withdrawn until they were reinstated. "SAFETY IMPLICATIONS "There are no safety implications because controls are in place under TVA's corrective action program that will prohibit current plant structures, systems or components, including those affected in the course of resource recovery activities, from being placed into service without being further evaluated and having been fully restored or replaced. "This deficiency has been entered into TVA's Corrective Action Program as Problem Evaluation Report 170988." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY | [9 empty] | NON EMERGENCY | 2 | AL | POW |  | 50.55(e) |  |  |  | 0 | 2009-05-14
45065 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-05-13 11:37 | 2009-05-13 20:03 | 2009-05-13 | FITNESS FOR DUTY REPORT A contractor supervisor had a confirmed urine sample substitution. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2009-05-13
45064 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-05-13 15:05 | 2009-05-13 18:14 | 2009-05-13 | TRACK HOE SLID INTO INTAKE FOREBAY "At approximately 1505 a Track Hoe clearing brush and foliage on the SQN Site berms slid into the SQN Intake Forebay. This is outside the Protected Area and does not affect Safety Related or other plant equipment. A small oil sheen was noted at the Track Hoe requiring notification of Federal and State Agencies in accordance with the Site Spill Prevention, Control and Countermeasure Plan. The containment of the oil sheen is in progress. An extraction plan is being developed by on-site personnel." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-05-13
45063 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-05-13 10:09 | 2009-05-13 16:55 | 2009-05-13 | VIOLATION OF ACCESS AUTHORIZATION PROGRAM REQUIREMENTS Actual entry of an unauthorized person into the protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-05-13
45062 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2009-05-13 16:00 | 2009-05-13 16:45 | 2009-05-13 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The licensee reported to the State that a vehicle transporting a Troxler gauge (Model 3430, s/n 38185) was involved in a traffic accident in Perry, GA along Highway 341, Mile Marker 3. The licensee's RSO is enroute to the site. The licensee indicated there was no harm to personnel. The gauge contained both a 40 mCi Am-241/Be source and a 8 mCi Cs-137 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2009-05-18
45061 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-05-13 | 2009-05-13 09:58 | 2009-05-14 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING AN UNDERDOSAGE TO THE PROSTATE "Ohio Department of Health (ODH) Bureau of Radiation Protection (BRP) was notified of a medical event that occurred at The Urology Center, LLC located at 4700 Smith Road, Suite M, Cincinnati, OH. 45212, Ohio license # 02200310002 at 12:30 PM 05/12/2009. The patient received a permanent implant of 64 I-125 seeds on 5-11-09. The total activity implanted was 28.422 mCi. (.444mCi/seed). The prescribed dose to the prostate was 144.0 Gy. The post-plan CT was evaluated 5-12-09 and determined that the prostate volume receiving the prescribed dose was 47% (i.e. V100%=47%) resulting in a 53 percent under dose of the prescribed dose. The patient and physician have been notified. ODH BRP will continue to evaluate this event. The licensee has initiated an internal evaluation." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-05-19
45060 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-05-12 21:30 | 2009-05-13 02:36 | 2009-05-13 | INSTRUMENT VALVE MALFUNCTION POTENTIALLY AFFECTING THE ISOLATION CAPABILITY OF ONE OF THE MAIN STEAM LINES "The equalizing valve for one of the four Main Steam Line (MSL) Flow - High differential pressure switches on the 'B' MSL was leaking through. The leak effectively reduced the differential pressure across all four MSL Flow - High valves on the 'B' MSL. This reduction in differential pressure thus potentially would not allow the switches to isolate the 'B' MSL at the required setpoint. This switch was for group 1 isolation. This loss of safety function was restored by isolating the faulty valve block for DPIS-2-117A. All other switches are now reading normally. The repairs for the faulty valve are in progress." The licensee will notify NRC Resident Inspector, State, and local authorities. | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-05-13
45059 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-05-12 | 2009-05-12 13:05 | 2009-05-12 | AGREEMENT STATE REPORT - FOUR TROXLER GAUGES FOUND MISSING The State of Florida provided the following via fax: "[The licensee RSO] found 4 Troxler gauges missing from [a] storage facility [located in Winter Park, FL] on 12 May 2009. [The] gauge handles were locked, also a second lock to [the] structure and door was locked to storage room [when last checked by the licensee]. [The] owner is contacting local police department and will offer an award. [The Florida Bureau of Radiation Protection] Orlando Inspection Office will investigate." The four Troxler gauges each contained 8 mCi Cs-137 and 40 mCi Am-241/Be sources. Three of the Troxler gauges were Model 3430 (S/N: 29922, 35106, and 35474), and the fourth Troxler gauge was a Model 3440 (S/N: 23037). Florida Incident Number FL09-042. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-05-15
45058 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2009-05-11 11:30 | 2009-05-12 12:18 | 2009-05-12 | MULTIPLE FAILURES TO MEET 24 HOUR REPORTING CRITERIA "On May 11, 2009, at approximately 1130 CST, licensee initial evaluation concluded that events meeting the 24 hour reporting criteria of 10CFR40.60 (b)(1) had not been reported during the period 10/17/08 through 03/29/09 (37 events total). Each event involved leakage from processing equipment located in the Feeds Material Building, (FMB). The material involved in each case was either natural uranium, or UF4 (green salt), in the form of a dry powder or dust. It is believed in each case the quantity of material exceeded 5 times the lowest ALI as specified in 10CFR40.60(b)(1)(ii), which for this material is less than 3 grams. "In each case appropriate protective measures were applied when contamination was discovered. Protective measures included turning on precautionary lights, and requiring the wearing of respirators for personnel entering affected areas. Cleanup of affected areas was also conducted. "A more conservative interpretation of which events are considered unplanned versus planned has been incorporated. The previous interpretation historically applied, considered the event planned, if at the first indication of leakage, mitigating actions were initiated. The more conservative interpretation will incorporate considering the event unplanned, if mitigating measures were not already in place for a planned activity at the time of discovery. This more conservative interpretation has been discussed with NRC Region II, has been adopted as the facility's practice, and communicated to licensee management. "Review of personnel bioassay data indicates no resulting increase in personnel dose measurements. Review of liquid and gaseous effluent data, and sampling data from the restricted area boundary all indicate no significant increases in effluent measurements, and all analytical results are well within regulatory limits. There is no impact to plant workers or members of the public as a result of this event. Routine contamination surveys are being conducted in accordance with Health Physics program procedures, and results are reviewed with the plant ALARA committee. "This event will be addressed by corrective actions in accordance with the plant Corrective Action Program." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2009-05-12
45057 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-05-12 02:44 | 2009-05-12 11:40 | 2009-05-12 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "Communication problems between the plant process computer and radiation monitoring system occurred at 0244 CDT. The failure disabled 17% of the plant data information inputs to the NRC Emergency Response Data System (ERDS). ERDS was not restored within one hour, which necessitates this ENS notification per 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM SHANE HARVEY TO JOHN KNOKE AT 1605 ON 05/12/09 * * * Licensee stated that ERDS has been restored and Emergency Assessment capability is fully operable. The licensee notified the NRC Resident Inspector. Notified R3 (Michael Kunowski). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-12
45056 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-05-12 07:16 | 2009-05-12 08:40 | 2009-05-12 | OFFSITE NOTIFICATION DUE TO ELEVATED TRITIUM LEVELS IN GROUND WATER SAMPLE "[The licensee was] notified by Southern Nuclear Company (SNC) Chemistry that, while performing [the procedure for monitoring] the tritium activity results for ground water sample well number T3, elevated tritium levels were detected. "On May 5, 2009, [a] data report from Georgia Power Central (GPC) Lab containing tritium activity results for ground water sample well T3 was received and reviewed for input into [the] Chemistry database. [The] activity for well T3 was observed to be elevated (36,500 pCi/L). This concentration had increased from [the] last sample activity (5400 pCi/L) on March 16, 2009. Chemistry personnel were directed to resample for verification [of the elevated activity levels]. A sample was collected on May 6, 2009 and shipped to GPC Lab. Sample results for the verification sample were received May 11, 2009. These results were confirmed to be elevated (34,300 pCi/L) compared to previous levels. Chemistry Management has notified the resident NRC inspector as well as SNC environmental affairs. SNC Corporate is performing the necessary notifications to the Georgia State Environmental Protection Division (EPD)." The licensee is developing a plan to ascertain the cause of this event. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-05-12
45055 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-05-11 16:00 | 2009-05-11 17:11 | 2009-05-11 | OFFSITE NOTIFICATION TO NATIONAL RESPONSE CENTER "[The licensee was] Notified by chemistry, that while performing [the procedure for monitoring] the annual releases via unplanned routes for gamma sampling for groundwater well P17B, which is located near the southeast corner of the Diesel Generator (DG) building, a strong diesel / fuel oil odor in the groundwater being collected was detected by the sampling technician. In addition to the strong petroleum odor, the groundwater from the well had a reddish tint. This color is indicative of the red dye used to identify off-road diesel. "The P17B is normally sampled annually for tritium and gamma. The last sample from this well was taken in January 2009 for the tritium sample surveillance. "Southern Nuclear Company (SNC) Corporate Environmental Affairs was contacted to make the appropriate communications. Environmental Affairs has contacted the National Response Center. "[The licensee's] Plans are to excavate in the area of well P17B to determine potential source of fuel oil to [the] ground water well." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-05-11
45054 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-05-07 | 2009-05-11 15:31 | 2009-05-11 | AGREEMENT STATE REPORT - RADIUM SOURCE FOUND The State of Colorado sent this report in by fax. "On 5/7/09, the Department received a request for assistance from a private citizen regarding the disposition of a load of scrap metal that he sent to a scrap metal recycling facility. The load was rejected after it tripped the gate radiation monitor. "On 5/8/09, representatives from the Department went to the owner's site to investigate. After sifting through the pile of scrap, a radium source was found. The source, which was approximately 2 inches [in] diameter and 0.25 thick, had a glass face and appeared to be some type of light source. The back of the source was stamped with the following, 'USRC, UNDARK, 22MTTR58, Poison Inside.' The source was reading approximately 35 millirem per hour on contact and 0.3 millirem per hour at one foot. No removable contamination was detected by wipe test. The owner, who was cleaning out an old building on the property, did not know where the source came from. "The source is currently being stored inside a locked, empty building on the property pending disposition. No other details are available at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-05-14
45053 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-05-11 08:30 | 2009-05-11 12:28 | 2009-05-11 | CONCURRENT REPORT - VIRGINIA DEPARTMENT OF ENVIRONMENTAL QUALITY NOTIFIED OF WASTE TREATMENT RELEASE "On May 10, 2009 at about 0215, Waste Treatment operations began pumping sanitary sludge from the sanitary sludge holding tank to the Low Level Radioactivity (LLR) press. This is accomplished by activating an air-actuated diaphragm pump which suctions from the holding tank and discharges to the LLR press. Observations by area operators both at the press and the Programmable Logic Controller (PLC) display showed no abnormal conditions. "Near or around 0345, area security officers notified the area operators that liquid was accumulating on the ground under the sanitary sludge holding tank. The operator attending to the reported release observed a leak on the discharge side of the diaphragm pump. The pump was halted and the isolation valve at the bottom of the holding tank was closed to halt the release. "Plant supervision was promptly notified and efforts were initiated to contain the release using absorbent pads and dikes. Most of the liquid was contained and pumped back into the sanitary system, and approximately 10-20 gallons drained to the system Final Effluent Pond (FEP 601). No liquid was observed to have been released to the James River. "On May 11, 2009 at approximately 8:30 am, the Virginia Department of Environmental Quality (DEQ) was notified of the release both verbally and by email. This notification was performed to satisfy the notification requirements contained in the current site Virginia Pollutant Discharge Eliminations System (VPDES) permit for unanticipated bypasses of treatment systems. Notification is required verbally (within 24 hours) and in writing (within 5 days) upon discovery of the circumstances surrounding the bypass. "There were no radiological concerns with this event." The licensee will contact the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2009-05-15
45052 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-05-10 10:41 | 2009-05-10 12:52 | 2009-05-10 | INTERMEDIATE RANGE REACTOR SCRAM DURING TRANSITION TO RUN "During Startup of HNP-1, after reaching greater than or equal to 7% RTP [rated thermal power], the crew placed the Reactor MODE switch to 'RUN,' in accordance with the Startup Procedure 34GO-OPS-001-1. Upon placing the MODE switch to 'RUN,' a full RPS actuation occurred due to upscale trip signals on the Intermediate Range Nuclear Instrumentation (IRM) 1C51K601A, 1C51K601D and 1C51K601H. Placing the Reactor MODE switch to 'RUN' bypasses the IRM inputs to the RPS system, so actuation of the RPS from the IRMS was not expected. All withdrawn control rods inserted properly upon receipt of the full SCRAM signal. All equipment functioned as expected, with the exception of the unexpected upscale trips of IRMs 1C51K601A, 1C51K601D and 1C51K601H and the subsequent RPS actuation from the IRMs. "No reactivity changes were in progress at the time to cause the upscale trip signals. At this time, investigation is in progress, but the investigation and corrective action have not yet been completed. "The shift crew is progressing to Cold Shutdown, MODE 4 at this time." The decay heat is being removed by main turbine sealing steam with makeup provided via the control rod drive system. Offsite power is provided by the normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-05-10
45051 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-05-08 10:45 | 2009-05-08 17:41 | 2009-05-08 | MANUAL REACTOR SCRAM AFTER LOSS OF GENERATOR SEAL OIL "At 1045 hours, a manual scram was inserted due to a loss of main generator seal oil pressure and subsequent loss of hydrogen pressure in the Main Generator. Initial investigation revealed that a filter in the seal oil system became clogged during a system test. Even though the test was stopped and the system lineup restored, seal oil system pressure did not return to normal until the main turbine generator was secured. No indications of turbine or generator damage exist. "All rods fully inserted, MSIVs remained open, no SRVs opened, and all other safety systems operated as designed. Reactor Water Level was restored and maintained with the Reactor Feedwater and Condensate systems during the post scram transient within normal operating bands. Reactor Pressure was controlled using the Main Turbine Bypass Valves in automatic control. Normal cool down to the Main Condenser is in progress. Offsite power is available. EDG-2 was inoperable but available due to surveillance testing, restoration is in progress. All other EDGs are operable and in standby status. "This shutdown occurred 13 hours before a planned shutdown for the refueling outage, so the plant will not be restarted until after the outage." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-05-08
45050 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-05-06 | 2009-05-08 17:37 | 2009-05-08 | AGREEMENT STATE REPORT- MISSING SEALED SOURCES "UCLA was unable to locate 2 sealed sources which were listed in their inventory database. The first source was 50 micro Ci Co 60 as of 5/1/2000. Current activity is 15.28 micro Ci which exceeds the 1 microCi 24 hour reporting requirement. The second source was listed in their database as 1.83 micro Ci of Cm 244 as of 10/12/1988. "UCLA believes the original activity for the Cm 244 source to be 1.83 nano Ci, and was listed incorrectly in their database. They contacted the Manufacturer, Isotope Products Laboratory, who informed them that they did not manufacture micro Curie quantities, but only nano Curie quantities of Cm 244. The current activity of the Cm 244 source (decayed to date of notification) is either 832 nano Curies or 0.832 nano Curies. The former exceeds the 1 nano Ci 24 hour reportable quantity requirements. "UCLA believes the Cm 244 Source was installed in an instrument, but they were unable to locate the instrument at the time of notification. UCLA is continuing to search for the missing sources." The UCLA RSO (Radiation Safety Officer) believes the sources are still on the campus. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-05-13
45049 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2009-05-08 15:15 | 2009-05-08 17:29 | 2009-05-08 | INADVERTANT MAIN STEAM ISOLATION WHILE PERFORMING MAINTENANCE "At 1515 on 5/8/09, a Group 1 isolation signal was received which resulted in all eight Main Steam Isolation Valves closing. The signal was received based upon a valid main condenser low vacuum signal coincident with a main turbine reset signal which opened the turbine stop valves. The reset of the turbine was an unanticipated result of ongoing Mark VI turbine control system processor repair work. The reactor was maintaining hot shutdown while conducting nuclear instrumentation repair. The Group 1 isolation was completed successfully with all MSlVs and small bore valves closing as designed. The condition causing the turbine reset has been cleared and the turbine tripped with all valves closed. The Group 1 isolation signal has been reset and the MSIVs have been re-opened. "The cause of the turbine reset signal is being investigated by Station Engineering and the on-site GE representative." The reactor is being taken to cold shutdown for intermediate range nuclear instrument maintenance. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-05-08
45048 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-05-08 08:17 | 2009-05-08 15:26 | 2009-05-08 | PRIMARY CONTAINMENT ISOLATION VALVES DISCOVERED OPEN "At 0817, 4 of the 5 ball valves associated with the Traversing Incore Probe (TIP) system were discovered to be open. In conjunction with explosive shear valves located on each line, these ball valves function to isolate the primary containment upon the receipt of a containment isolation signal. Further investigation revealed that the associated TIP detectors were in the drywell at the indexer. With the TIP detectors in the drywell the detector cable is passing through the ball valves and this condition renders the valves inoperable. This condition had existed for approximately 48hrs and was due to improper shutdown of the system on May 5, 2009. "This is a violation of technical specification 3.6.3 and resulted in a condition which would have prevented the automatic safety function of the TIP system to control the release of radioactive material during an accident. The explosive shear valves are manually actuated per Operations abnormal procedures should a ball valve not close during accident conditions and remained operable throughout the time the ball valves were impaired. "At 0937 the TIP detectors were withdrawn to their chamber shields, the ball valves closed and declared operable. "This event was limited to the TIP system and its associated containment penetrations. Plant operation was not affected. Investigation is in progress and will be entered into the station's corrective action program. There was nothing unusual or not understood. All safety related equipment and systems are operable." The licensee notified the NRC Resident Inspector. Notified the R1DO(Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2009-05-08
45047 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-05-08 10:00 | 2009-05-08 08:02 | 2009-05-08 | SAFETY PARAMETER DISPLAY SYSTEM OUT OF SERVICE FOR MAINTENANCE "On May 8, 2009, the Safety Parameter Display System (SPDS) will be removed from service at approximately 1000 hours for Salem Unit 1 to perform planned maintenance to the system. The maintenance consists of the replacement of the uninterruptable power source (UPS) to improve the reliability of the SPDS. The removal of SPDS will also affect the transmission of Salem Unit 1 data from the emergency response data system (ERDS). Appropriate compensatory measures will be in place while SPDS is out of service. SPDS capability is scheduled to be restored using a temporary power feed later today." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/8/2009 AT 1541 FROM JACK OSBORNE TO MARK ABRAMOVITZ * * * "The Salem Unit 1 Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were returned to service at 1530 hours." The licensee will notify the NRC Resident Inspector. Notified the R1DO (Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-08
45046 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-04-13 16:46 | 2009-05-07 13:09 | 2009-05-07 | HUMAN PERFORMANCE ERROR WHILE TROUBLESHOOTING A POWER SUPPLY "This telephone notification, instead of a written LER is provided in accordance with 10CFR50.73(a)(1), to report an invalid actuation reportable under 10CFR50.73(a)(2)(iv)(A). "On 4/13/2009, during troubleshooting activities for a control room annunciator power supply problem, a 'D' channel LOCA Level 1 Isolation Logic relay trip occurred when the relay power supply was de-energized and then re-energized. De-energization of the relays caused the 'D' Emergency Diesel Generator (EDG) to auto start, the 'B' Control Room Emergency Filtration System to auto start and the 'D' Safety Auxiliaries Cooling System pump to auto start. The other components of this logic system were properly removed from service and did not actuate. "This is classified as an 'invalid' actuation reportable under 50.73(a)(2)(iv)(A). The logic system actuation was due to a human performance error and not the plant conditions. At the time, the plant was in Operational Condition 5 with the reactor cavity flooded and 'A' RHR system in shutdown cooling. In accordance with the existing plant conditions, all actions that should have occurred for this actuation did occur; no other initiations or actuations were noted. "This event was entered into the HCGS [Hope Creek Generating Station] corrective action program. "There was no radiological release associated with this event. "The NRC Senior Resident Inspector has been notified of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-05-07
45045 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-05-06 22:56 | 2009-05-07 00:29 | 2009-05-07 | MANUAL REACTOR TRIP DUE TO FEED REGULATING VALVE FAILURE "On 5/6/09 at 2256 Sequoyah Unit-1 was manually tripped from 100% reactor power. The manual trip was in response to the failure of Loop 1 Feed Water Regulating Valve (FRV). Manual control was attempted to control level in Loop 1 Steam Generator however Loop 1 FRV failed to respond. A manual reactor trip was initiated as a result of this failure. In addition, Auxiliary Feedwater (AFW) initiated as required due to a Feedwater Isolation signal. The Loop 1 FRV did not isolate from the Feedwater Isolation signal, however the Loop 1 Feedwater Isolation Valve closed as designed. "The Plant is currently being maintained in Mode 3 at NOT/NOP, approximately 547 [degrees] F and 2235 psig, with Auxiliary Feedwater supplying the steam generators and Steam Dumps to Main Condenser removing decay heat. "Maintenance activities have been initiated to repair the Loop 1 FRV." All rods inserted on the trip. No safety or relief valves lifted as a result of the transient. The plant is in its normal shutdown electrical lineup. No grid instabilities exist and there was no effect on Unit 2. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-05-07
45044 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2009-05-05 23:27 | 2009-05-06 06:22 | 2009-05-06 | VALID AUTO-START AND LOADING OF EMERGENCY DIESEL GENERATOR TO SAFETY BUS DUE TO UNDERVOLTAGE CONDITION "A valid Engineering Safety Feature (ESF) actuation for emergency A/C power for the 15AA bus occurred at 2327 on 5/5/09 due to degraded voltage on ESF Transformer 12. ESF Transformer 12 was supplying power to the 15M bus due to Service Transformer 21 being out of service for maintenance. A fault occurred on the site power loop at switch 389-2901S causing breaker J3872 and breaker 5X01 to open de-energizing the site power loop and degrading the offsite power circuit 115kv voltage to the point that Division 1 Load Shedding and Sequencing (LSS) sensed a degraded voltage condition and performed a Load Shedding and Sequencing on the 15AA bus and started Division 1 Emergency Diesel Generator to power the 15AA bus. Division 1 Diesel Generator is now supplying power to the 15M bus. Operators implemented appropriate off normal event procedures to mitigate the transient. All systems responded as designed. "The exact cause of the fault to switch 2109S is not known at this time." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-05-06
45043 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2009-05-05 03:30 | 2009-05-05 05:41 | 2009-05-05 | 3C MAIN STEAM ISOLATION VALVE PROBLEMS "While preparing to perform main turbine testing prior to returning Unit 3 to service, a possible weld defect was identified by plant personnel during a main steam system walk down. This defect appears to be on a small bore section of pipe upstream of a steam trap on a socket weld. This resulted in a small steam leak on the upstream side of the 'C' main steam isolation valve. The repair must be completed with the steam line depressurized and, as such, the plant is in the process of reducing temperature to less than 200 degrees F. Based on previous interpretations of TS 3.4.10 and the applicability to ASME Class 2 piping, TS 3.0.3 has been entered based on current plant conditions. "At 0348 on 5/5/09, while bringing the Unit 3 to Mode 3 to comply with TSAS [Technical Specification Action Statement] 3.0.3, the 3C MSIV failed to close when demanded. The 3C MSIV was declared inoperable and Unit 3 entered TSAS 3.7.1.5 due to the inability to fulfill its safety function. The unit is required to be in Mode 3 in 6 hours and Mode 4 within the following 6 hours. "At 0437, the 3C MSIV was closed. This is in compliance with TSAS 3.7.1.5. An investigation is in progress as to the cause of the failure of the 3C MSIV to close when demanded. "Plant shutdown continues to comply with TSAS 3.0.3." All other safety systems are operable and there is no impact on Unit 4. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2009-05-05
45042 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-05-04 05:07 | 2009-05-04 16:29 | 2009-05-04 | 24 HOUR 91-01 BULLETIN REPORT ON LOSS OF ONE OF TWO CRITICALITY CONTROL CONTINGENCIES "At 0507 CDT, on 05/04/09 the Plant Shift Superintendent was notified that a fissile sample buggy in C-331 Process Building was in violation of the 2-foot spacing requirement from a fissile HEPA vacuum. The buggy was pushed up against the HEPA vacuum spacing pan which resulted in approximately 21-inches of separation between the fissile material items. The situation has been remediated according to Nuclear Criticality Safety guidelines. "Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01 Supplement 1. "SAFETY SIGNIFICANCE OF EVENTS: There were approximately 21-inches of separation between fissile material items, therefore, although the minimum 24-inch (2-feet) spacing was violated, there was significant spacing provided. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: Even if the items had been configured with no spacing, an additional upset would be necessary in order for a criticality to be possible. "CONTROLLED PARAMETERS: Geometry, interaction. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: The assay of any material is less than or equal to 5.5 wt. % U235. "NUCLEAR CRITICALITY SAFETY CONTROL AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on maintaining a minimum of 2 feet edge to edge between the HEPA vacuum and other fissile material; this control was violated. The second leg of double contingency, which was not violated, relies on the geometry of the HEPA vacuum cleaner and demonstrates that a single spacing violation is subcritical. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Control access to the area. Move the sample buggy in a direction away from the HEPA vacuum such that the spacing is always increasing until the minimum 2-feet edge to edge spacing has been re-established. Double contingency was re-established by 1300 hours on 5/4/09. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2009-05-04
45041 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-04-29 | 2009-05-04 13:53 | 2009-05-04 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The Nebraska Office of Radiological Health provided the following report via e-mail: "The [Kellogg USA] facility was not able to locate four H-3 exit signs (SRB Model BXU20WS containing 17.51 Curies [each] of H-3, for serial #'s 217897, 217965, & SRB Model B100BX20 containing 17.51 Curies [each] of H-3 for serial #'s 220063 and 220071) while completing their annual inventory. They have made a number of searches and can not locate the four missing signs. The company is planning on the removal and proper disposal of all H-3 exit signs in the facility by 8/31/2009. The facility has 230 plus exit signs." Nebraska Report NE090010 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-05-07
45040 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-04-15 | 2009-05-04 13:40 | 2009-05-04 | AGREEMENT STATE REPORT - PROCESS LEVEL GAUGE SHUTTER STUCK OPEN The following report was received from the Texas Department of State Health Services via e-mail: "The licensee reported that during the performance of a routine six month inspection, the shutter on an Ohmart/VEGA level gauge model SH-F2, containing a 200 mCi Cesium (Cs) - 137 source, serial # 7548GK, would not properly close. The gauge is used as a level monitor on a vent stack. The source was left in its normal operating position and does not pose an exposure risk to individuals. Radiation levels in the area were measured and found to be normal. As a corrective action, the licensee lubricated the operating mechanism on the gauge. They again tried to operate the mechanism, but could not. They continued to lubricate the mechanism periodically in an effort to free the mechanism. The licensee contacted a service provider and arrangements were made for assistance in closing the shutter if needed. On 4/29/09, the licensee was able to close the mechanism and operate the shutter normally. There was no apparent damage to the shutter operating mechanism." Texas Report Number I-8633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-05-07
45039 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-05-03 03:10 | 2009-05-03 18:29 | 2009-05-07 | 24-HOUR NRC BULLETIN 80-24 REPORT DUE TO POSSIBLE SERVICE WATER SYSTEM LEAKAGE INTO CONTAINMENT "V.C. Summer Nuclear Station is notifying the NRC in accordance with NRC Bulletin 80-24, regarding Service Water System leakage into containment. "At approximately 0310 on 05/03/09, Reactor Building sump sample analyses, in response to increasing sump level, indicated a probable leak from the Industrial Cooling Water System at 0.38 gpm. "In accordance with Bulletin 80-24, a 14 day written report will be submitted." The licensee is continuing to monitor at this time. A corrective action plan to definitively identify where the leak is coming from will be developed. The licensee notified the NRC Resident Inspector. The licensee plans on notifying State of South Carolina and the counties of Fairfield, Richland, Lexington, and Newberry EP representatives. * * * RETRACTION ON 5/7/2009 AT 1705 FROM JASON WEATHERSBY TO MARK ABRAMOVITZ * * * "On 05/06/2009, a reactor building entry was made, and the previously reported leak was determined to be from the Industrial Cooling Water system. The location of the leak was from a mechanical seal of a non-safety rod position indication equipment cabinet cooling pump. No degradation of a containment boundary exists. EN # 45039 is being retracted, and a 14 day report will not be submitted." The licensee notified the NRC Resident Inspector. Notified the R2DO (Guthrie). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | RESPONSE-BULLETIN |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2009-05-03
45038 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2009-05-03 07:45 | 2009-05-03 14:32 | 2009-05-03 | LOSS OF EOF COMMUNICATION CAPABILITY DUE TO EQUIPMENT FAILURE "At approximately 0745 [CDT] it was determined that the ANO telephone system communications for outgoing and incoming calls had been lost. An ENS phone check was performed satisfactory with the NRC. Two alternate dedicated outside lines located in the Control Rooms and five alternate NRC lines in the TSC were operating satisfactory. "However, when E-plan personnel evaluated the EOF located in the nearby training center, there was only one outside line that was functioning and in addition to a lack of external phone lines, there was no internal phone communications available between the EOF and the plant. The impairment to the EOF due to the lack of communications was considered a major loss of emergency assessment capability per 50.72(b)(3)(xiii). "Phone service to the site was returned at 1031 [CDT]. Phone service to the EOF was verified at 1145 [CDT]." This event was the result of an offsite power outage on 05/02/09. Following the loss of power, the onsite telephone equipment transferred automatically to battery supplied backup power. When the affected offsite power was restored, the telephone equipment power supply failed to automatically realign (auto transfer). No alarms were available to operators to detect the power supply misalignment. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-03
45037 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2009-05-03 09:02 | 2009-05-03 10:50 | 2009-05-03 | SECURITY PRECAUTIONS TAKEN DUE TO SEVERE WEATHER Specific security measures have been suspended or modified due to severe/hazardous weather on site. Alternate security measures have been initiated when and where possible based on weather limitations and personnel safety concerns. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JULIA THOMPSON TO JOE O'HARA ON 5/3/09 AT 1156 EDT * * * Security measures have been restored to normal after severe weather hazards exited the area. The licensee will notify the NRC Resident Inspector. Notified R4DO (Walker). Notified Part 73.71 Safeguards Report Group via E-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-05-03
45036 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2009-05-02 00:02 | 2009-05-02 08:18 | 2009-05-02 | EMERGENCY OPERATIONS FACILITY POWER INTERRUPTION "The Emergency Operations Facility lost power due to a fault on the site power loop. The licensee has not been able to restore power to the facility. The emergency generator also failed to operate. "This call is required due to not being able to promptly restore the facility in the event of an accident as noted in NUREG 1022 Section 3.2.13. Maintenance is ongoing. "The backup EOF is available and the EOF team will be notified." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-05-02
45035 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2009-04-30 10:39 | 2009-04-30 17:39 | 2009-05-01 | HPCI DECLARED INOPERABLE DUE TO FAILURE OF TEST LINE PRESSURE CONTROL VALVE DURING SURVEILLANCE TEST "During plant startup on 4/29/09 at 2239 [EDT], the startup had progressed to the point where plant conditions were adequate to allow performance of SR 3.5.1.9, High Pressure Coolant Injection (HPCI) System flow testing against system head corresponding to reactor pressure. A Note to SR 3.5.1.9 allows 12 hours to perform this test after adequate reactor steam dome pressure and flow have been established for test performance. "During the test performance, the test line pressure control valve did not properly operate to establish the required system head. The HPCI system was shutdown and returned to Standby. Earlier, on 4/29/09, SR 3.5.1.10, low pressure HPCI flow testing was successfully completed. Troubleshooting of the test line pressure control valve was begun. "At 1039 [EDT] on 4/30/09, the 12 hour allowance of the Note to SR 4.5.1.9 expired and the HPCI system was declared inoperable for failure to complete the required surveillance. The HPCI system remains in Standby and is configured to perform its safety function. "However, this event represents a potential loss of a single train safety system pending repair of the test line pressure control valve and completion of flow testing." With HPCI inoperable, the Unit is in the 14-day Tech. Spec. Action Statement 3.5.1. The licensee is revising their surveillance procedure to allow for manual operation of the failed control valve and estimates that the required testing will be completed within 4 hours. The Unit will remain in Mode 2 pending completion of this test. The licensee informed the NRC Resident Inspector. * * * RETRACTION PROVIDED BY D. DUNCAN TO JASON KOZAL 05/01/09 AT 1128 * * * "High Pressure Coolant Injection (HPCI) Surveillance Requirement 3.5.1.9, HPCI system flow testing against system head corresponding to reactor pressure, was satisfactorily completed and HPCI declared OPERABLE May 1, 2009 at 0221 hours. There was no loss of HPCl safety function. Therefore this event is retracted." Notified R3DO (Hills). | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-04-30
45034 | 0 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2009-04-29 13:30 | 2009-04-30 14:51 | 2009-04-30 | MEDICAL EVENT INVOLVING AN UNDERDOSAGE DURING TREATMENT FOR LIVER CANCER "At approximately 1:30 pm, on April 29, 2009 a medical event occurred at Indiana University Medical Center, NRC License No. 13-02752-03. This medical event involved the treatment of a patient with Y-90 microspheres (Nordion TheraSpheres). A dosage of 61.3 mCi was prescribed by the Authorized User. TheraSpheres are provided as a unit dosage and said dosage was assayed at 12:15 pm (4/29/09) to contain 60.1 mCi. Based upon a radiation monitoring device affixed to the TheraSphere delivery system, the pre-treatment reading was 7 milliroentgens per hour (mR/hr). Following the administration of the microspheres and four subsequent flushings of the delivery system, the radiation monitor exhibited a reading of 2 mR/hr, indicating that approximately 28.6% (17.2 mCi) of the dosage remained in the delivery system. When the subsequent flushing failed to reduce the remaining activity in the system, an independent measurement of the residual activity was performed to confirm that the entire dosage had not been delivered as prescribed. "The vendor (Nordion) was notified of this event earlier today (4/29/09). Based upon discussions with their technical representatives, it is their opinion that the residual microspheres may be attached to the septum of the dose vial. For future treatments, the vendor representative suggested that the dose vial be given a good shake during the check-in and assay procedure to help dislodge any microspheres that may have adhered to the vial septum during shipment. They also suggested that during the administration process if the residual dosage appears to be present in the dose vial, tilting and tapping the dose vial and/or the acrylic box containing the dose vial may dislodge any microspheres that may adhere to the vial septum. These suggestions are being incorporated into the written procedures for TheraSphere treatments. "The Radiation Safety Office attempted to perform some radiation measurements of the delivery system to determine the location of the residual activity. Due to the relatively high exposure rates from the residual radioactivity in the delivery system, it was not possible to definitively determine the distribution of the residual activity in the system at this time, mainly due to the potential for contamination and elevated radiation levels to RSO staff. More thorough evaluations may be possible once the radioactivity in the system diminishes due to radioactive decay. "Notification of the referring physician of the occurrence of this medical event was made at 10:25 am today (4/30/09). The patient's wife was notified of the occurrence of the medical event at 10:30 am today." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-05-06
45033 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-04-30 13:06 | 2009-04-30 13:06 | 2009-04-30 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) UNAVAILABLE FOR GREATER THAN 1 HOUR "Oyster Creek's ERDS is expected to be unavailable at 1315 EDT today, 4/30/09, and remain unavailable until scheduled maintenance on the Plant Process Computer is returned to service at approximately 1600 EDT today, 4/30/09." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM THOMAS DUNN TO DONALD NORWOOD ON 4/30/09 AT 1633 EDT * * * ERDS was returned to normal as of 1550 EDT today. The licensee will inform the NRC Resident Inspector. Notified R1DO (Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-30
45032 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2009-04-30 08:55 | 2009-04-30 12:50 | 2009-04-30 | OFFSITE NOTIFICATIONS MADE DUE TO INADVERTANT ACTIVATION OF SIX EPZ SIRENS "At 0855 six sirens had been activated by the Ottawa County dispatch console for 3 minutes. "At 0905 Ottawa County Sheriff Dispatch Center notified [the licensee] that sirens in Ottawa County had been inadvertently activated. It appears this was caused by the county radio service vendor resetting the dispatch center consoles during trouble shooting of the sheriff's radio system. "Immediate actions taken: RA-EP-00420, Response to Prompt Notification System Malfunction, was implemented. The siren system was polled and the data from the Emergency Operations Facility (EOF) siren computer was reviewed. The computer data indicated at 08:55:55 the six sirens located in Bay Township had been activated by the Ottawa County Dispatch Console for 3-minutes. Fleet siren maintenance was contacted and requested to come to Ottawa County to meet with the radio service vendor to determine the cause of the inadvertent activation. "In addition, NOP-LP-5001, Communicating Events of Public Interest, was implemented and associated notifications were made." These notifications included the State of Ohio, Ottawa County, and Lucas County. The NRC Resident Inspector was notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-30
45031 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2009-04-29 19:38 | 2009-04-30 00:48 | 2009-04-30 | TONE ALERT RADIOS OUT OF SERVICE "At 2230 on April 29, 2009, with Nine Mile Point Unit 1 and Unit 2 operating at 100% reactor power, Oswego County Emergency Management notified the Unit 1 and Unit 2 Control Rooms that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 1938 [on 4/29/09]. At 0015 on April 30, Oswego County Emergency Management notified the Control Rooms that the Tone Alert Radios had been restored to service as of 0012, April 30, 2009. "This impacted the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF [James A. FitzPatrick see EN# 45030] Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens which also function as part of the Public Prompt Notification System remained operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency offsite communications capability. Compensatory measures were verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program, and the [NRC] Resident Inspector has been briefed, and the state PSC will also be notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-30
45030 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2009-04-29 19:38 | 2009-04-30 00:13 | 2009-04-30 | TONE ALERT RADIOS OUT OF SERVICE "At 2230 on April 29, 2009, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 1938 [on 4/29/09]. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The National Weather Service is currently working to determine the cause of the failure and time frame for system restoration. "The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program, and the [NRC] Resident Inspector has been briefed, and the state PSC will also be notified. "UPDATE: Notified by Oswego County that the Tone Alert Radios were restored 00:12 on 04/30/2009." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-30
45029 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-04-28 21:59 | 2009-04-28 23:50 | 2009-04-29 | MANUAL REACTOR TRIP INITIATED AS A RESULT OF A LOSS OF CONDENSATE FLOW "At 2159 Sequoyah Unit 1 was manually tripped from 18% reactor power. The manual trip was in response to automatic isolation of all intermediate pressure feedwater heater strings resulting in a loss of all condensate flow. The feedwater heater strings isolated following a manual trip of the main turbine. The main turbine was manually tripped in response to a failed open moisture separator reheater relief valve. At the time of the event Sequoyah Unit 1 was raising power following a refueling outage. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary feedwater automatically actuated as expected on loss of the operating main feedwater pump. "The plant is currently being maintained in Mode 3 at NOT/NOP, approximately 547 F and 2235 psig, with auxiliary feedwater supplying the steam generators and steam dumps to main condenser removing decay heat. "Maintenance activities have been initiated to repair the MSR relief valve." Electrical lineup is normal with all safety related equipment operable. Licensee is investigating the cause for the relief valve failure. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-04-29
45028 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2009-04-28 18:34 | 2009-04-28 19:34 | 2009-05-18 | PROCESS COMPUTER REPLACEMENT IMPACTING ERDS AND SPDS "During the current Unit 1 refueling outage, the plant process computer system will be taken out of service for approximately three weeks to support a planned modification which will install a new (upgraded) plant process computer system. During this timeframe, ERDS [Emergency Response Data System] and SPDS [Safety Parameter Display System] will be unavailable on Unit 1 which will remain in a shutdown condition. The computer outage will also render ERDS and SPDS unavailable on Unit 2 for approximately eight hours. Should the need arise, plant status information will be communicated to the NRC, [State, and local responders] using other available communication systems. The computer outage is expected to commence at 2200 CDT on 4/28/2009, and the process computer will be restored prior to Unit 1 startup currently scheduled for 05/21/2009. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a Major Loss of Assessment Capability." The licensee will update this report when ERDS and SPDS is restored to Unit 2. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM C. STEFFES TO JOE O'HARA AT 0558 ON 4/29/09 * * * "Follow-up notification - U2 ERDS and SPDS is restored as of 0315 CDT 4/29/09." The licensee notified the NRC Resident Inspector. Notified R3DO(Hills) * * * UPDATE FROM BRIAN MAGNUSON TO JOE O'HARA AT 1509 EDT ON 5/18/09 * * * "Follow-up notification - U1 ERDS and SPDS have been restored. Acceptance testing was completed on 5/15/09." The licensee notified the NRC Resident Inspector. Notified R3DO(Skokowski) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-28
45027 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2009-04-28 15:27 | 2009-04-28 17:41 | 2009-04-28 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR LEVEL DUE TO FEEDWATER VALVE FAILURE "Wolf Creek experienced a reactor trip at 1527 CDT. The RX trip resulted from low level in 'B' S/G. [The] 'B' Main Feedwater Regulating Valve [FRV] AE FCV-520 closed causing a loss of feedwater to the 'B' S/G. Initial investigation indicates that the FRV controllers lost power due to blown primary and backup fuses associated with its card rack. "One intermediate range instrument (SE NI-36) stuck at 10E-10 amps requiring manual energization of source range instruments. "Aux Feedwater and Feedwater Isolation actuations occurred as expected." All control rods inserted into the core during the trip. There were no relief or safety valves actuated during the transient. The electrical plant is in the normal shutdown alignment with offsite power supply emergency busses. Decay heat is being removed via the steam dumps to condenser. The licensee is investigating the cause of the blown fuses. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-04-28
45026 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-04-28 09:53 | 2009-04-28 12:00 | 2009-04-28 | EMERGENCY DIESEL AUTO-START DUE TO LOSS OF THE "B" RESERVE STATION SERVICE TRANSFORMER "At 0953 hours on April 28, 2009, a loss of the 'B' Reserve Station Service Transformer resulted in a Degraded Voltage / Under Voltage automatic start of the Unit 2 'H' Emergency Diesel Generator. The Unit 2 'H' Emergency Diesel Generator is operating and supplying electrical power to the Unit 2 'H' 4160 Volt Bus. The Unit 2 'B' Charging Pump (2-CH-P-1B) and the Unit 2 'B' Component Cooling Water Pump (2-CC-P-1B) also auto started in response to the loss of power. [Procedure] 0-AP-10, 'Loss of Electrical Power', was entered to address the loss of the normal power source for the Unit 2 'H' Emergency Bus. "Unit 2 is operating at 100% power and an investigation has been initiated to determine the cause of the event and appropriate corrective actions. "The NRC Resident Inspector has been notified." There was no impact on Unit 1 operation. There was no loss of significant safety equipment as a result of the transformer loss. The licensee will continue to supply the 'H' 4160V bus with the 'H' Emergency Diesel Generator until compensatory measures are put in place. The loss of the 'H' bus places Unit 2 in a 72-hr shutdown action statement. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-04-28
45025 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-04-27 17:30 | 2009-04-28 00:55 | 2010-03-10 | RESIDUAL HEAT REMOVAL (RHR) PUMP TRIPPED WHILE IN OPERATION FOR SHUTDOWN COOLING "On April 27, 2009, at approximately 1730 hours, with the plant in Mode 5 during refueling outage (RFO) 12, RHR 'A' pump tripped while operating in shutdown cooling. RHR 'A' was the primary decay heat removal shutdown cooling system. RHR 'B' was the backup decay heat removal shutdown cooling system. Preliminary investigation shows that jumper installation activities associated with plant testing resulted in a blown fuse and closure of the RHR shutdown cooling outboard common suction isolation valve (1E12F008). Closure of the 1E12F008 valve tripped the RHR 'A' pump and prevented the RHR 'B' pump from being used to initiate shutdown cooling from the control room. Operators were preparing to manually open 1E12F008 in parallel with activities to restore control from the control room. "The plant entered Technical Specification 3.9.9, 'RHR - Low Water Level', Conditions A and C due to 1E12F008 isolating causing the loss of shutdown cooling. Action A.1 calls for verification of an alternate method of decay heat removal available for each inoperable RHR shutdown cooling subsystem in 1 hour and once per 24 hours thereafter. This was completed with the fuel pool cooling and cleanup system's two pumps and two heat exchangers cooled by NCC [Nuclear Closed Cooling System] (available due to the ability to reflood the upper pools with a hotwell pump through normal cavity reflood path) being one alternate system. A second alternate system was the utilization of the low pressure core spray to flood the vessel, returning to the suppression pool through safety relief valves, and a loop of RHR in suppression pool cooling. Actions for Condition C, to verify reactor coolant circulation by an alternate method and to monitor reactor coolant temperature were not met due to no reactor coolant flow past a valid temperature monitoring point. Approximate reactor coolant temperature was being trended using the reactor water cleanup system. "The blown fuse was identified and replaced at approximately 1816 hours. The RHR 'B' pump was started at approximately 1834 hours. From the time that the RHR 'A' pump tripped (approximately 1730), until the RHR 'B' pump was started, the reactor temperature increased from 94 degrees F to 97 degrees F. Pre-determined time to boil had been calculated to be 9 hours. At approximately 1835 hours, TS 3.9.9 Condition C was exited due to the RHR 'B' shutdown cooling loop being placed in operation. "This event is being reported as an event or condition that at the time of discovery could have prevented fulfillment of a safely function of structures or systems that are needed to remove residual heat under 10 CFR 50.72 (b)(3)(v)(B). "The NRC Resident Inspector has been notified." * * * RETRACTION FROM C. ELBERFELD TO P. SNYDER AT 1727 ON 6/25/09 * * * "The purpose of this call is to retract Event Number 45025. On April 28, 2009, at 0055 hours, notification was made to the NRC Operations Center by the Perry Nuclear Power Plant (PNPP) reporting a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to remove residual heat [10 CFR 50.72(b)(3)(v)(B)]. Jumper installation activities associated with plant testing resulted in a blown fuse and closure of the Residual Heat Removal (RHR) shutdown cooling outboard common suction isolation valve. Closure of the valve resulted in the RHR A pump tripping, as designed. The blown fuse was replaced and the valve reopened. The RHR B subsystem was then started as the primary decay heat removal shutdown cooling system. Additionally, it was initially questioned whether Technical Specification Limiting Condition for Operation 3.9.9 Required Actions were met to verify reactor coolant circulation by an alternate method and to monitor reactor coolant temperature. "Based on further evaluation, it was determined that there was not a reasonable expectation of the loss of safety function of a system needed to remove residual heat (i.e., the RHR System). The redundant RHR B subsystem was manually aligned and operated in a timely manner to continue to meet the system requirements to fulfill the safety function. Since the condition reported in Event Number 45025 would not have prevented the fulfillment of the safety function of a system that is needed to remove residual heat, the condition is not reportable, and this notification is retracted. Additionally, it was determined that verification of reactor coolant circulation by an alternate method (i.e., Reactor Water Cleanup System) was performed and that monitoring of reactor coolant temperature was appropriate. Therefore, based on not meeting any 10 CFR 50.73 reporting criteria, no Licensee Event Report is required. The evaluations (i.e., Reportability Reviews) for this condition are documented in Condition Report 09-58110 and Condition Report 09-58123." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOHN PELCIC TO CHUCK TEAL AT 1515 EST ON 3/10/10 * * * "The Residual Heat Removal (RHR) system common suction isolation valve 1E12-F008 received an invalid isolation signal resulting in the operating RHR A pump tripping while the system was in the shutdown cooling mode of operation. The event was reported to the NRC Operations Center on April 28, 2009 in accordance with 10 CFR 50.72(b)(3)(v)(B). The event notification was subsequently retracted on June 25, 2009. This event was reevaluated for reportability via Condition Report 10-71293 using additional guidance and enforcement history related to safety system functional failure reporting. Based on results of this evaluation, the April 27, 2009, loss of shutdown cooling event is reportable as a Licensee Event Report (LER) under 10 CFR 50.73(a)(2)(v)(B), 'Any event or condition that could have prevented the fulfillment of the safety function of structures, or systems that are needed to remove residual heat.' "Perry LER 2010-001 will be submitted to report this event. The NRC Resident Inspectors have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2009-04-28
45024 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-04-27 15:00 | 2009-04-27 17:34 | 2009-04-27 | FITNESS FOR DUTY INVOLVING A NON-LICENSED CONTRACT SUPERVISOR A non-licensed contract supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2009-04-27
45023 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-04-26 15:45 | 2009-04-26 21:31 | 2009-04-29 | ERDS AND PLANT COMPUTER UNAVAILABLE DURING MAINTENANCE ON COMPUTER ROOM COOLING "At 1545 on 04/26/2009, the Emergency Response Data System (ERDS) at the Beaver Valley Power Station (BVPS) Unit 1 was removed from service. The ERDS is a direct near real-time electronic data link between the licensee's onsite computer system and the NRC Operations Center that provides for the automated transmission of a limited data set of selected parameters. The ERDS supplements the existing voice transmission over the Emergency Notification System (ENS) by providing the NRC Operations Center with timely and accurate updates of a limited set of parameters from the licensee's installed onsite computer system in the event of an emergency. "The BVPS Unit 1 plant computer and ERDS was removed from service due to planned maintenance on the River Water cooling to the air conditioning for the computer room. The maintenance is scheduled to be completed in approximately 48 hours. This is being reported pursuant to 10 CFR 50.72(b)(3)(xiii). "Until the ERDS communication is restored, BVPS Unit 1 would utilize its pre-planned backup information flow path in event of an emergency as provided in Procedure 1/2-EPP-IP-1.4, Attachment G when the ERDS system is not operational. "The BVPS Unit 2 ERDS is not affected and remains operational. "The NRC Resident has been notified." * * * UPDATE FROM RONALD T. GREEN TO DONALD NORWOOD ON 4/29/09 AT 1355 EDT * * * "As of 1320 on 04/29/2009, the BVPS Unit 1 plant computer and the data communication link to the Emergency Response Data System (ERDS) were returned to service. "The site NRC Resident Inspector has been notified." Notified R1DO (Krohn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-26
45022 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-04-26 10:00 | 2009-04-26 13:46 | 2009-04-26 | NDT REVEALS CIRCUMFERENTIAL INDICATIONS ON RCS HOT LEG DRAIN PIPING "On April 26, 2009 at approximately 1000 hours during the Beaver Valley Power Station Unit No. 1 (BVPS-1) refueling outage, ultrasonic (UT) examinations were performed on pipe base material per the Materials Reliability Project (MRP) MRP-146 recommendations. The MRP recommendations were to address industry operating experience for similar indications identified by other utilities. Two circumferential UT indications approximately 3/8 inches in length were recorded in the base material adjacent to a socket weld on the horizontal portion of line BV-1 RC-41 which is a two (2) inch drain line that connects to the 'A' Reactor Coolant System (RCS) Hot Leg. The function of this piping is to drain the applicable loop during maintenance periods. The indications are not through wall and there was no evidence of leakage. Similar 2 inch drain lines on the other loops have been inspected satisfactorily. "The plant is currently shutdown and in Mode 6. The affected RCS loop is not required to be Operable and is currently isolated and drained. Repairs are currently being planned and will be completed prior to startup. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-04-26
45021 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-04-25 18:05 | 2009-04-25 20:50 | 2009-04-25 | MANUAL SCRAM FOLLOWING LOSS OF COOLING TO MAIN TRANSFORMER "Oyster Creek inserted a manual reactor scram due to a loss of cooling to one of its main transformers. All systems responded normally during the reactor scram. The NRC Resident Inspector has been notified. " The manual scram was described as uncomplicated. All control rods fully inserted. No safeties or PORVs lifted during the transient. There were no electrical power issues besides the problem associated with the main transformer cooling. Normal feedwater cooling was maintained to the reactor and decay heat removal is to the main condenser. There were no ESF actions during the transient. The loss of cooling was to one of Oyster Creeks' two main transformers. Power to the transformer cooling system components (oil cooling pumps and cooling fans) was lost when the control power transformer to the cooling system components failed. The licensee manually scrammed because sustained operation at power would not be possible with loss of cooling to the main transformer and operation with one of the main transformers de-energized is also not possible. The licensee will continue to cold shutdown to perform other maintenance activities while shutdown. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-04-25
45020 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-04-25 10:48 | 2009-04-25 16:02 | 2009-04-25 | ERDS UNAVAILABILITY DUE TO PLANT PROCESS COMPUTER FAILURE "The Unit One Plant Process Computer failed at 1048 CDT. The failure disabled plant data information inputs to the NRC Emergency Response Data System (ERDS). ERDS unavailability was validated by the NRC. ERDS was not restored within one hour, which necessitates this ENS notification per 50.72(b)(3)(xiii). The Plant Process Computer was restored at 1342, which restored ERDS." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-25
45019 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2009-04-24 11:20 | 2009-04-24 16:33 | 2009-04-24 | AGREEMENT STATE REPORT - TWO MISSING GENERAL LICENSED DEVICES The following information was received via facsimile from the Alabama Office of Radiation Control: "On the morning of April 24, 2009 at approximately 1120 am CDT, the Alabama Office of Radiation Control received a phone call from representatives of BF Goodrich in Tuscaloosa, Alabama advising the [State] Agency of the discovery of two missing general licensed devices containing radioactive material. The representatives of BF Goodrich indicated that on April 23, 2009, two NDC model 103 profile gauges containing 150 millicuries each of Am-241 were discovered to be missing. The gauges were installed at the facility but had not been in use for an extended period of time. The shutter for each of the devices were reported as closed. The serial numbers reported were 13311 and 13312. The gauges were possessed and used under a general license registration. Representatives of BF Goodrich continue to investigate the incident and will provide a written report within 30 days." Alabama Incident 09-15 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2009-04-29
45018 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2009-04-24 | 2009-04-24 15:32 | 2009-04-24 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR "On April, 23, 2009, the Virginia Department of Health (VDH) was notified by Virginia Commonwealth University (VCU) that a Nuclear Radiation Developments, Inc. 'Ionotron' containing an Am-241 source has been lost. The source is a model number A-001 with an activity of 20 microcuries on 12/75. "The source was last inventoried on February 27, 2009. Since then, VCU began to clean up this storage location and placing unwanted material in a barrel for disposal through RSO, Inc. The barrel was picked up on April 1, 2009. "VCU found the source missing when they went to take a picture for its disposal through the SCATR program. It is believed that the source was placed into the barrel and has been disposed of by RSO, Inc. "VCU will submit the 30 day written report to VDH." This report is VA number: VA-09-01. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2009-04-29
45017 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-04-24 11:41 | 2009-04-24 15:15 | 2009-04-24 | AUTOMATIC REACTOR TRIP DURING INSTRUMENT CALIBRATION "At 1141 CT, Braidwood Unit 2 experienced an automatic Reactor Trip. The Reactor Trip red first out annunciator was Over Temperature Delta Temperature (OTDT). At the time of the Reactor Trip the Instrument Maintenance Department was performing a scheduled calibration of a Pressurizer Pressure channel (2PT-456) which is in the B loop of reactor protection. During the calibration a spike occurred on the D loop of reactor protection. Specifically, the RCS [Reactor Coolant System] temperature for the D loop. This caused a Reactor Trip on a 2 of 4 coincidence. "After the reactor trip occurred, all four steam generators reached their low-2 Reactor Trip setpoints and pressurizer pressure reached its low pressure Reactor Trip setpoint all of which is an expected response on a trip from full power. Steam Generator levels and Pressurizer pressure have been restored. Both the 2A and 2B Auxiliary Feedwater pumps auto started on the low-2 steam generator levels as expected. All control rods fully inserted into the core. "No secondary relief valves lifted and no secondary steam released as a result of the Reactor Trip. Steam Generators are now being filled by the 2A Main Feedwater pump and the Auxiliary Feedwater pumps have been placed in standby. The main steam dumps are in service to the main condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. "This report is being made per 10 CFR 50.72(b)(2)(iv)(B) for RPS actuation, 4 hour notification, and per 10 CFR 50.72(b)(3)(iv)(A) for automatic actuation of the Auxiliary Feedwater System, 8 hour notification. "The electrical line up transferred to the normal shutdown configuration with the standby diesel generators and safety systems available. There is no Unit 1 impact. "The licensee plans on issuing a press release and has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-04-24
45016 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-04-23 09:10 | 2009-04-23 16:23 | 2009-05-07 | ACTUATION OF AUTO LOAD SEQUENCER DURING FAST BUS TRANSFER TESTING "At 0910 during planned testing of the 10A401 vital bus, an unplanned momentary loss of power was experienced when testing the fast transfer function. A delay of approximately 1 second was experienced when forcing a fast transfer (simulating a transformer lockout via the 86 device) from the alternate to the normal 4KV bus infeeds. This condition resulted in an initiation of the 'A' channel LOP sequencer (ELS) as a direct result of bus under voltage and is considered valid ESF actuation. All other equipment operated as expected that was available for service. "The bus de-energized for <1 second and restored power automatically from the bus normal infeed. No major loads were lost. The channel is currently inoperable for planned maintenance and is not required per tech specs. "Prior to the transient, the reactor was shut down, in operational condition 5, with all control rods fully inserted, and the reactor cavity flooded and communicating with the spent fuel pool. All other 'A' and 'C' channel equipment, including the 'A' and 'C' emergency diesel generators are inoperable for maintenance. Decay heat is being removed by the 'B' loop of residual heat removal operating in the shutdown cooling mode. "No personnel were injured. The licensee is conducting an investigation to understand the response and cause." The licensee has notified the NRC Resident Inspector and will notify the township. * * * RETRACTION ON 5/7/2009 AT 1309 FROM TOM FOWLER TO MARK ABRAMOVITZ * * * "During a subsequent review of the event, it has been determined that this was not a valid actuation of one of the systems listed in 10CFR50.72(b)(3)(iv)(B). The original report was made based on the event being an actuation of (8) Emergency AC electrical power systems, including: emergency diesel generators (EDGs); hydroelectric facilities used in lieu of EDGs at the Oconee Station; and BWR dedicated Division 3 EDGs'. "The Hope Creek (HC) Updated Final Safety Analysis Report (UFSAR) º8.3.1.1.2 states that there are three potential power sources for the Class 1E AC power system: (a) normal power source, (b) alternate power source and (c) dedicated standby diesel generator (SDG). The HC UFSAR º8.3.1.1.3 lists the components of the 'Standby Power System' (Emergency AC Power System). The ELS is not one of the components listed. Additionally, the sequence of events did not complete the required logic to actuate a start of the EDG. "Since no EDG actuation signal was generated, this was neither a valid nor invalid actuation of a system listed in 10CFR50.72(b)(3)(iv)(B) and is not reportable." The licensee notified the NRC Resident Inspector. Notified the R1DO (Caruso). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-04-23
45015 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-04-23 10:15 | 2009-04-23 15:26 | 2009-04-23 | DAMAGED AREA IN CONTAINMENT LINER "On April 21, 2009 during the Beaver Valley Power Station Unit No.1 (BVPS-1) refueling outage, an ASME XI Section IWE General Visual examination was performed on the interior containment liner. A suspect area was identified at the 738 foot elevation level of containment. This area was approximately 3 inches in diameter and exhibited blistered paint and a protruding rust product. At approximately 1015 hours on April 23, 2009 after cleaning the area and removal of the corrosion products, a rectangular area approximately 1 inch (horizontal) by 3/8 inch (vertical) was discovered that penetrated through the containment steel liner plate (nominal .375 inch thickness). The BVPS-1 containment design consists of an internal steel liner that is surrounded by reinforced concrete. "With the plant currently shutdown and in Mode 6, the containment as specified in Technical Specification 3.6.1 is not required to be operable. The cause of this discrepancy is currently being evaluated. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) as a condition of the principal safety barrier (i.e., containment) being seriously degraded." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2009-04-23
45014 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-04-16 | 2009-04-23 14:49 | 2009-04-23 | COMMINGLED WASTE The following was received from the commonwealth via fax: "On April 16, 2009, the Covanta Haverhill trash-to-energy plant requested a routine DOT-E 11406 for the rejection of a shipment of commingled commercial and industrial trash. The shipment was returned to the point of origin in Peabody, which was the Casella Waste Systems facility at 295 Forest Street. The load was secured at 295 Forest Street in Peabody until their competent consultant could survey and process the load on April 21, 2009. The consultant separated out over 150 industrial smoke detectors from the front end loader. These devices were industrial smoke detectors. Most models contained Am-241 80 micro curies each; but many others contained 40 micro curies each of Radium-226. The consultant faxed a preliminary report to the [MA state] Agency on April 22, 2009 and pledged to follow-up with an accurate breakdown of the exact RAM and total activities involved as the information is developed. Complete information was not available as of the time of this report. This same consultant is also arranging for the legal disposition of the smoke detectors and assisting the Casella Waste Systems management in tracking down the source of the RAM." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-04-28
45013 | -1 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-04-22 05:00 | 2009-04-23 14:47 | 2009-07-09 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - ALERT - DUE TO FIRE DAMAGE TO SAFETY-RELATED BREAKER "At 1410 hours on April 23, 2009, it was identified that an ALERT classification had not been declared on April 22, 2009 as required by EPIP-1.01. North Anna Emergency Plan, Emergency Action Level H2.1 requires the declaration of an ALERT for a fire or explosion in any safe shutdown area and either plant personnel report visible damage to any safety-related structure, system or component within the area or affected system parameter indications show degraded performance. A description of the event is provided below. "On April 22, 2009, at approximately 0500 hours, Operations personnel identified a strong odor in the North Anna Unit 1 Cable Vault area. Subsequent investigation identified that the odor was coming from circuit breaker 01-EE-BKR-1J1-2S-J1 associated with the "D" Control Rod Drive Mechanism (CRDM) Fan (1-HV-F-37D). Operations personnel locally opened the circuit breaker to place it in a safe condition. 1-HV-F-37D had tripped approximately 30 minutes prior to the event. 1-HV-F-37D is not safety-related and not required for safe shutdown however; the supply breaker is safety-related since it is located on an emergency bus. Operation personnel then opened the circuit breaker cabinet and a small (6-inch) flame was observed. Operations personnel used a CO2 extinguisher on the internals of the circuit breaker to quickly extinguish the small fire. Appropriate levels of management were informed. The breaker has been quarantined. The cause of the circuit breaker failure has not been identified. A Root Cause Evaluation is in progress. There were no injuries. The plant continues to operate at full power. As a result of identifying that the criterion for the EAL was exceeded and no longer exists, a notification is being made to the NRC Operations Center in accordance with 10CFR50.72(a)(1)(i). "The NRC Resident Inspector has been notified and the State and local governments will be notified." * * * RETRACTION FROM KEMP TO SANDIN AT 1105 ON 07/09/09 * * * "On April 22, 2009, at approximately 0500 hours, operations personnel identified a strong odor in the North Anna Unit 1 Cable Vault area. Subsequent investigation identified that the odor was coming from circuit breaker 01-EE-BKR-1J1-2S-J1 associated with the 'D' Control Rod Drive Mechanism (CRDM) Fan (1-HV-F-37D). Operations personnel locally opened the circuit breaker to place it in a safe condition. 1-HV-F-37D had tripped approximately 30 minutes prior to the event. 1-HV-F-37D is not safety-related and not required for safe shutdown however; the supply breaker is safety-related since it is located on an emergency bus. Operation personnel then opened the circuit breaker cabinet and a small (6-inch) flame was observed. Operations personnel used a C02 extinguisher on the internals of the circuit breaker to quickly extinguish the small fire. A root cause evaluation is in progress. "At 1447 hours on April 23, 2009, a one hour notification was made to the NRC Operations Center in accordance with 10CFR50.72(a)(1)(i), which identified that the criterion for a ALERT EAL was exceeded due to the small fire in the circuit breaker and subsequent damage to the breaker internals. The notification also stated that the condition no longer exists. "Subsequent reviews have determined that the 'Initiating Condition' for the Emergency Action Level was not met and the event was not required to be classified as an ALERT. The initiating condition states -Fire or explosion affecting the operability of plant safety-related structures, systems or components required to establish or maintain safe shutdown. The 'D' Control Rod Drive Mechanism is not required to establish or maintain safe shutdown and the emergency bus remained operable during the event. The notification made to the NRC on April 23, 2009 is being retracted. "The NRC Resident Inspector has been notified." Notified the R2DO (Nease). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2009-04-23
45012 | 0 | ALASKA DEPT OF TRANSPORTATION |  |  |  |  | 2009-04-22 14:00 | 2009-04-23 13:26 | 2009-04-23 | DAMAGED TROXLER MOISTURE DENSITY GAUGE Troxler Moisture Density Gauge model 3440, serial number 25403, was run over by a truck at the Auke Bay ferry terminal in Juno, Alaska on 4/22/09 at 1400. This gauge has Am-241 40 mCi and Cs-137 8 mCi sources. The gauge was in the retracted and shielded position when it was damaged. The cover was damaged. Surface contamination surveys following the event were negative. The licensee intends to ship the device to the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-04-23
45011 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2009-04-22 09:00 | 2009-04-23 11:46 | 2009-04-23 | AGREEMENT STATE - MEDICAL MISADMINISTRATION The following was received from the agreement state with a state control number of KY0901: "At 1400 on 4/22/2009, the RSO of a medical licensee reported the misadministration of a radiopharmaceutical to a seven-month-old infant. The infant was scheduled for a renal scan and was ordered to receive a 2 mCi dose tagged with Tc-99m. The patient was inadvertently administered a 35 mCi dose of Sestamibi/Tc-99M. "Event date: 4/22/2009. Discovery date: 4/22/2009. Report date: 4/22/2009. "Licensee Reporting Party Information: University of Kentucky, Lexington KY 40506, License number: 202-049-22. "Site of event: Lexington, KY. "Event type: MD2 - Medical event. "Event cause: Human error." The patient was informed on 4/22/2009. The intended diagnostic study was renal-glomerular filtration with dimercaptosuccinic acid (DMSA) radiopharmaceutical, with a 2 mCi (74 MBq) Tc-99m radionuclide. The given diagnostic study was cardiac perfusion with sestamibi/cardiolite radiopharmaceutical, with a 34.9 mCi (1291.3 MBq) Tc-99m radionuclide. The dose exceeded the prescribed dose by 1650%. It is estimated that the heart received a dose of 2.84 rem, and the whole body does was 6.84 rem. The effect on the patient is unknown at this time. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2009-04-29
45010 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2009-04-22 19:45 | 2009-04-23 02:33 | 2009-06-18 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE "On 4/22/2009 during an inspection of the HPCI (High Pressure Coolant Injection) Suppression Pool Suction piping it was identified that the suction piping was in contact with a piping support clamp. Per the design of the support, the clamp ring to pipe clearance should be 1/2 inch. With the identified contact, the integrity of the pipe support cannot be assured during a seismic event. At the time of discovery, the HPCI suction was aligned to the Suppression Pool. Subsequently, the suction has been realigned to the Condensate Storage Tank with both Suppression Pool suction valves deenergized in the closed position. HPCI remains available with suction aligned to the Condensate Storage Tank. "Due to this, HPCI was declared INOPERABLE on 4/22/2009 at 7:45 PM (local time). This event is reportable per 10 CFR 50.72(b)(3)(v)(D) for a single train safely system potentially unable to perform its safely function of accident mitigation. The licensee entered a 14 day LCO (Limiting Condition of Operation) associated with the inoperable HPCI system. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM BOB MURRELL TO JOE O'HARA AT 1417 ON 6/18/09 * * * "The purpose of this notification is to retract a previous report made on 4/23/09 at 0233 (ET) (EN 45010). Notification of the event to the NRC was initially made as a result of declaring High Pressure Coolant Injection (HPCI) system inoperable when the Suppression Pool Suction piping was identified as being in contact with a piping support clamp. Per the design of the support, the clamp ring to pipe clearance should have been 1/2 inch. With the identified contact, the integrity of the pipe support could not be assured during a seismic event. "Since the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the HPCI system was capable of performing its safety function. "NextEra concluded that the identified configuration, while not meeting design requirements, would not prevent HPCI from performing its intended safety function. This conclusion was based on analysis that demonstrated that the piping would remain intact during a design basis accident. "This event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73." The licensee notified the NRC Resident Inspector. Notified R3DO(Lipa) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-04-23
45009 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2009-03-24 13:26 | 2009-04-22 13:37 | 2009-04-22 | PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) GROUP 3 INVALID ACTUATION "This sixty day notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) to provide the NRC with information pertaining to an unplanned invalid actuation of specific systems, specifically, a Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment isolation valves in more than one system. "On March 24, 2009, at approximately 1326 hours, Vermont Yankee Nuclear Power Station (VYNPS) experienced an invalid PCIS Group 3 isolation associated with personnel error during quarterly calibration of the Refuel Floor Zone Radiation Monitors. VYNPS had removed the East Refuel Floor Zone Radiation Monitor from service for calibration. The technician, in the field, had completed a phone communication with the control room and was dispatched to the East Refuel Floor Zone Radiation Monitor to perform the calibration activity. However, the technician incorrectly went to the inservice West Refuel Floor Zone Radiation Monitor and removed the detector from service. This incorrect action caused a momentary invalid high radiation signal containment isolation signal and the Subsequent PCIS Group 3 isolation. The following actuations resulted: "Both trains of the Standby Gas Treatment System started as designed. "The PCIS functioned properly providing a complete Group 3 isolation valves in the following system actuated as a result of the PCIS Group 3 isolation: "Drywell Air Purge and Vent, "Drywell and Suppression Chamber Main Exhaust, "Suppression Chamber Purge and Vent, "Containment Air Compressor Suction, "Exhaust to Standby Gas Treatment, "Containment Purge Supply and Makeup, "Containment Air Sampling, "Air Dilution Subsystem, [and] "Containment Air Dilution Vent System. "This event has been entered into VYNPS's corrective action program." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-04-22
45008 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2009-04-22 11:21 | 2009-04-22 13:03 | 2009-04-22 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE "On 4/22/09 at approximately 1121, during surveillance testing on the High Pressure Coolant Injection (HPCI) System, the associated Primary Containment Isolation valves closed. This isolation rendered the HPCI system incapable of performing its safety function and is, therefore, reportable under 10 CFR 50.72(b)(3)(v). Technical Specification LCO 3.5.1 Condition C had been entered at 0837 to support testing. The cause of the isolation is unknown at this time. Troubleshooting is in progress. LCO 3.5.1 Condition C provides 14 days for restoration of the HPCI System, the plant will remain in the LCO until the cause is determined and any associated repairs have been completed. "A follow-up Licensee Event Report will be filed within 60 days. "The NRC Resident Inspector has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-04-22
45007 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-04-14 | 2009-04-21 14:39 | 2009-07-01 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL MISADMINISTRATION The following information was obtained from the State of Washington via email: "On 15 April 2009, the licensee notified Washington Office of Radiation Protection by phone of a possible HDR (high dose-rate Remote after-loader Brachytherapy device) malfunction during a patient prostate treatment on 14 April 2009. The licensee discovered the event immediately upon termination of the treatment. "The aluminum connector to needle 13 detached from the plastic guide tube. It is possible that the source wire or the dummy wire, during retraction, snagged on the seam between the aluminum connector and the plastic guide tube. The HDR is connected to the plastic guide tube, the plastic guide tube is attached (glued) to the aluminum connector, and the aluminum connector screws into the needles that are implanted in the patient. "It is unknown whether the source wire successfully entered needle 13 as planned; or the source wire failed to enter needle 13 and therefore hung about 6 inches past the disconnected guide tube in open air, for the 32 second dwell time assigned to that particular needle. The event occurred with needle 13 of the 17 treatment needles. The source wire did retract normally after the event. The event did not interfere with the remaining treatment needles. Isotope and Activity involved: Iridium-192, 185.2 GBq (5.0 curies). Source serial number: 02-01-0080-001-0121. Overexposures: The dose possibly differed by approximately 180 rads to a small volume of the prostate in vicinity of needle 13. If so, then the total dose would be less than 5% under-dose for the total treatment. The dwell time for needle 13 could have resulted in as much as 12.5 Gy (1250 Rem) to a small area of skin on the inner thigh. Several subsequent inspections of the patient have found no skin reaction. After discussion with the attending physician and examination of the patient's skin, the licensee does not believe there was any clinically significant effect to the patient. Washington Incident Number: WA-09-015 * * * UPDATE PROVIDED VIA EMAIL FROM KETTER TO PARK AT 0823 EDT ON 7/1/09 * * * "Updated, corrected event narrative: On 15 April 2009, the licensee notified Washington Office of Radiation Protection by phone of a possible HDR (high dose-rate Remote after-loader Brachytherapy device) malfunction during a patient prostate treatment on 14 April 2009. The licensee discovered the event immediately upon termination of the treatment. "The aluminum connector to needle 13 detached from the extension adaptor. The HDR is connected to the plastic guide tube, the plastic guide tube is attached to the extension adaptor (which includes the attached (glued) aluminum connector, and the aluminum connector screws into the needles that are implanted in the patient. "The root causes of the failure of the adhesive that attached the aluminum connector to the plastic extension adaptor are: sterilization of the extension adaptor (manufacturer's written product information cautions that sterilization may cause adhesive failure), and reuse of extension adaptors (manufacturer's written product information recommends for single use only). "It is unknown whether the source wire successfully entered needle 13 as planned; or the source wire failed to enter needle 13 and therefore hung about 6 inches past the disconnected guide tube in open air, for the 32 second dwell time assigned to that particular needle. The event occurred with needle 13 of the 17 treatment needles. The source wire did retract normally after the event. The event did not interfere with the remaining treatment needles. "The dose possibly differed by approximately 180 rads to a small volume of the prostate in vicinity of needle 13. If so, then the total dose would be less than 5% under-dose for the total treatment. The dwell time for needle 13 could have resulted in as much as 12.5 Gy (1250 Rem) to a small area of skin on the inner thigh. Several subsequent inspections of the patient have found no skin reaction. After discussion with the attending physician and examination of the patient's skin, the licensee does not believe there was any clinically significant effect to the patient." Notified the R4DO (Pick) and FSME EO (Burgess). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-04-27
45006 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-02-23 04:06 | 2009-04-21 14:23 | 2009-04-21 | INADVERTENT ACTUATION OF TURBINE AUXILIARY FEEDWATER PUMP "On February 23, 2009 at 0406, with Unit 1 at 100% power level, McGuire Nuclear Station experienced an inadvertent actuation of the Unit 1 Turbine Driven Auxiliary/Emergency Feedwater (TDAFW) Pump. This event occurred when power was removed to the steam admittance solenoid valves for the Unit 1 TDAFW Pump prior to isolating the steam supply to the pump. Removing power to the steam admittance valves caused them to fail open, starting the pump and injecting water into all four Unit 1 Steam Generators (S/Gs). Flow to the S/Gs was isolated by manually closing the Unit 1 TDAFW discharge isolation valve to each S/G. During recovery from the event, power was restored to the steam admittance solenoid valves for the running Unit 1 TDAFW Pump. Restoration of power generated a pump auto start signal which resulted in inadvertent automatic closure of both trains of blowdown containment isolation valves and both trains of sample containment isolation valves for each Unit 1 S/G. "Subsequent evaluation of the event concluded that the actuation of the Unit 1 TDAFW Pump, S/G blowdown containment isolation valves, and S/G sample containment isolation valves was not the result of a valid signal initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function provided by the respective component. In addition, the actuation of these components was not the result of an intentional manual initiation. Therefore, actuation of the Unit 1 TDAFW Pump, S/G blowdown containment isolation valves, and S/G sample containment isolation valves represented invalid actuations which are not reportable per the requirements of 10 CFR 50.72(b)(3)(iv)(A). Although the actuation of these components represented invalid actuations, they were not pre-planned, the systems were not removed from service, and the safety function provided by the components had not already been completed. Therefore, McGuire is reporting actuation of the Unit 1 TDAFW Pump, S/G blowdown containment isolation valves, and S/G sample containment isolation valves in accordance with the requirements of 10 CFR 50.73(a)(2)(iv)(A). Note that closing the Unit 1 TDAFW Pump discharge isolation valve to each S/G to isolate flow rendered the Unit 1 TDAFW inoperable. However, these valves were opened and the Unit 1 TDAFW Pump was restored to an operable status within the required completion time specified in the Auxiliary Feedwater System Technical Specification. "As indicated in 10 CFR 50.73(a)(1), in the case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv)(A) other than actuation of the Reactor Protection System when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC within 60 days after discovery of the event instead of submitting a written LER. In these cases the telephone report is not considered an LER. McGuire is exercising this option by providing this telephone notification. The following additional information is being provided as part of the telephone notification of this event: "The Unit 1 TDAFW Pump injected water into all four Unit 1 S/Gs for approximately 3 and 1/2, minutes before flow was isolated by manually closing the Unit 1 TDAFW discharge isolation valve to each S/G. Subsequent evaluation determined that Unit 1 reactor power did not exceed 100% during the event. The actuation of the Unit 1 TDAFW Pump was complete and successful. "This event actuated both trains of blowdown containment isolation valves and both trains of sample containment isolation valves for each Unit 1 S/G. Each train's actuation was complete and successful. "The licensee has notified the NRC Resident Inspector." The TDAFW pump was being removed from service, and the steam admittance solenoid valves should have been isolated prior to removing power to them. | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-04-21
45005 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-12-22 | 2009-04-21 10:26 | 2009-04-21 | MIS-ADMINISTRATION OF I-125 SUBCUTANEOUSLY VICE INTRAVENOUSLY The following abnormal occurrence information was received via e-mail: "PA NMED PA090013. "Date and Place: 12-22-2008; Hahnemann University Hospital, Philadelphia, PA. "Procedure/Dose (Actual vs. Intended), Nature, and Probable Consequences: Patient prescribed 50 mCi of Iodine-125 monoclonal antibody to be administered intravenously. On December 22, 2008 the injection was made subcutaneously when patient's port was not located properly during the injection. Estimated skin dose is 360-710 rads. "Notification: Patient was notified at the time of the event that the injection was subcutaneous rather than intravenous. "Health Effect: Doctor is confident that the therapeutic effects of this dosage have still been received by the patient. There have been no noted skin effects reported to date. "Cause or Causes: The nurse did not have the port completely visualized and admitted to not palpating the site as well as possible "Actions Taken to Prevent Recurrence: Staff was retrained in December 2008 that patients with ports are to disrobe completely and be palpated to ensure that the injection is occurring within the port. "State Agency: Just received notification of medical event, follow-up inspection to be performed by the State. "This event is closed for the purpose of this report." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-04-27
45004 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-04-21 03:00 | 2009-04-21 07:53 | 2009-04-21 | INADVERTENT ACTIVATION OF ONE EMERGENCY SIREN "At 0300 on 4/21/09, Emergency Siren K-008, which had a population coverage of 1%, inadvertently actuated and required Emergency Planning Personnel to deactivate [it]. Currently Siren K-008 is non-functional and required population coverage of KPS [Kewaunee Power Station] emergency sirens is acceptable. Due to Siren Activation, local offsite agencies have been notified of the failure as follows: "Kewaunee Sheriff Department and Kewaunee EOC are aware of the local activation and disconnect so compensatory measures can be initiated if required. "Point Beach has been notified. "Manitowoc EOC has been notified." The licensee has notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-21
45003 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2009-04-20 12:08 | 2009-04-20 17:02 | 2009-04-20 | INJURED PERSON TRANSPORTED OFF SITE WITH CLOTHING CONTAMINATION "At 1208 on 4/20/2009, the control room was notified of an injured person inside the Unit 3 Containment. It was immediately reported that this person fell about 4 feet off of the Reactor Head (while the Reactor Head was on the head stand) and potentially had head/back trauma. At 1210, Miami Metro Dade Fire and Rescue (911) was called. At 1218, Medical and Safety personnel arrived in containment and began preparation to transport the individual outside of containment. At 1225, Metro Dade Fire and Rescue arrived on site. At 1240, the individual was transported outside of containment via the equipment hatch. At 1253, FPL Radiation Protection reported to the control room that due to the individual's injuries and the difficulty in completing a full frisk, the individual would be transported offsite as a potentially contaminated-injured person. At 1255, security contacted the control room and stated that Metro Dade Fire and Rescue received the individual and began transport offsite to Baptist Hospital, Miami, Florida. At 1408,an FPL Radiation Protection representative that traveled to Baptist Hospital reported that the individual's clothing (protected clothing and modesty garments) was contaminated at 200 corrected cps > background. No skin contamination was found. An FPL Radiation Protection representative at Baptist Hospital took physical control of all material brought to the hospital from the site and are transporting all material back to site." The ambulance, other equipment, people, and structures with whom the contaminated individual and his clothing made contact between the containment control point and the hospital were surveyed, showed no contamination, and released. The individual was an FPL employee, and was staging equipment at a work site. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2009-04-20
45002 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-04-20 12:50 | 2009-04-20 15:43 | 2009-04-20 | INADVERTENT ACTUATION OF ONE AUTOMATIC NOTIFICATION SYSTEM SIREN "At approximately 1242 on April 20, 2009, three New Jersey Emergency Planning Zone (EPZ) Alert Notification System sirens went into AC power failure. This caused an automatic swap of the power supply from an AC source to a back up DC battery source. When this auto swap occurred, the Salem County 9-1-1 Center received an alarm which the dispatcher acknowledged. Sirens 127 and 114 were successfully acknowledged but when the dispatcher went to acknowledge Siren 128 he inadvertently selected 'alert with report' at 12:50:34 which when selected, initiated the siren. An ANS Services technician immediately received notification of the siren system actuation and called the Salem County 9-1-1 Center to provide direction to cancel the actuation. The siren actuation was cancelled at 12:52:21. Salem County officials notified the Lower Alloways Creek (LAC) Public Safety director and the New Jersey State Police (NJSP). The NJSP was notifying the NJ Regional Operation Intelligence Center (ROIC), LAC Police, and making a courtesy call to the LAC elementary school which is located in the vicinity of the siren. This event is being reported to NRC in accordance with the requirements of 10CFR50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-20
45001 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-04-20 01:53 | 2009-04-20 05:09 | 2009-05-13 | UNEXPECTED START OF THE STEAM DRIVEN AUXILIARY FEEDWATER PUMP DURING PLANT COOLDOWN "On 4/20/09 at 0153 hours, while in Mode 3 performing a plant cooldown for a refueling outage, a control room operator noted that the 'B' train steam supply (TV-1MS-105B) to the steam driven auxiliary feedwater pump, FW-P-2, was open. This caused the steam driven auxiliary feedwater pump to start and inject auxiliary feedwater into the steam generators. This was an unexpected condition. The start of the FW-P-2 auxiliary turbine driven feedwater pump is reportable under 10CFR50.72(b)(3)(iv)(A). "At 0209, TV-1MS-105B was closed. The steam driven auxiliary feedwater pump was declared inoperable and Technical Specification action statements were entered. Technical Specification 3.7.5 Condition B requires the pump to be restored to operable status within 72 hours or be in Mode 4 within the following 18 hours. "Mode 4 was entered on 4/20/09 at 0347 hours. The steam drive auxiliary feedwater pump is not required to be operable in Mode 4. Technical Specification 3.7.5 Condition B was exited on 4/20/09 at 0347. "Investigation is in progress to determine the cause of TV-1MS-105B opening. "The licensee notified the NRC Resident Inspector." * * * UPDATE ON 5/13/09 AT 1021 EDT TO RETRACT ORIGINAL EVENT AND REPORT AS INVALID ACTUATION FROM MATTY TO HUFFMAN * * * "This notification retracts 10 CFR 50.72 Event Notification No. 45001 since the actuation that was reported has subsequently been determined to be invalid. "On April 20, 2009, Beaver Valley Power Station Unit 1 (BVPS-1) was in Mode 3 and being shutdown in preparation for a refueling outage. At 0153 hours, one steam supply isolation valve (TV-1 MS-105B) to the steam-driven Auxiliary Feedwater System Pump (FW-P-2) unexpectedly opened at BVPS-1, causing this pump to commence feeding all three steam generators. FW-P-2 functioned as designed with steam being supplied to the pump's steam-driven turbine. This actuation was reported in NRC Event Notification No. 45001. "This start of the steam-driven Auxiliary Feedwater Pump was not valid. There was no adverse Steam Generator water levels, no Safety Injection signal, and no Reactor Coolant Pump undervoltage condition which could have caused an Auxiliary Feedwater Pump start. No maintenance or tests were ongoing with the Auxiliary Feedwater System at the time. After observing that there was no demand for this Auxiliary Feedwater System pump to be operating, the control room crew closed the steam supply isolation valve from the control room at 0209 hours, terminating operation of this auxiliary feedwater pump. "A follow-up problem solving team investigation did not identify any deficiencies within the solid state protection system. The most likely cause involved a degraded control room benchboard switch for TV-1 MS-105B. The physical degradation of the control switch would have allowed for the unplanned opening of the steam supply to the Auxiliary Feedwater Pump. This benchboard switch has been replaced and satisfactorily tested. "This event is being retracted since the Auxiliary Feedwater Pump actuation was not valid and therefore not reportable pursuant to 10 CFR 50.72(b)(3)(iv)(A) as previously reported. "This event is, however, reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since it involved an actuation of a PWR Auxiliary Feedwater system train as listed per 10 CFR 50.73(a)(2)(iv)(B)(6). However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification, instead of submitting a written Licensee Event Report, since the automatic actuation of the Auxiliary Feedwater System pump was not generated by a valid actuation." The licensee has notified the NRC Resident Inspector. R1DO (Holody) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-04-20
45000 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-04-20 01:15 | 2009-04-20 05:09 | 2009-04-20 | AUXILIARY FEEDWATER ACTUATION ON VALID STEAM GENERATOR HI-HI SIGNAL DURING SHUTDOWN "On April 20,2009 at 0115 during Beaver Valley Power Station Unit 1 shutdown and cooldown in support of the 19th refueling outage, Unit 1 experienced an Engineered Safety Feature (ESF) actuation P-14 due to Steam Generator (SG) HI-HI water level in the 'B' Steam Generator. This ESF actuation initiated automatic actions resulting in full feedwater isolation, trip of the only operating 'B' main feed and the start of two Auxiliary Feedwater System pumps. The unplanned automatic initiation of the Auxiliary Feedwater system [was] due to the Main Feedwater pump trip. The P-14 automatic ESF features properly closed the main and bypass feedwater regulating valves and [caused the] closure of the Feedwater Containment Isolation valves. A turbine trip signal was generated but the turbine was not on-line. The automatic start of the MDAFW pumps from this valid signal is reportable under 10CFR50.72(b)(3)(iv)(A). "The cause of the steam generator high level transient is the failure of the FCV-1FW-489, 'B' steam generator feed water bypass level control to automatically maintain level. Attempts to control the level manually were not successful. Additional investigation is in progress. "P-14 ESF actuation reset actions are being performed. Unit one cooldown continues using the MDAFW pumps and controls. AFW continues to be injected into the steam generators. "The licensee notified the NRC resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-04-20
44999 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-04-19 23:15 | 2009-04-19 23:38 | 2009-04-20 | SAFETY PARAMETER DISPLAY SYSTEM AND EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE FOR PLANNED MAINTENANCE "On 4/19/09 at 2315 EDT, Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service to support activities for a planned maintenance outage on the UPS vital bus power supply. The duration of work is expected to be approximately 24 hours. During this time, the majority of the Control Room indications remain available to the plant staff, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems, if needed. The plant is currently in Mode 5, and will remain in Mode 5, for the duration of the SPDS and ERDS unavailability. Since the unavailability will last greater than 8 hours, this is considered a Loss of Emergency Assessment Capability, and reportable under 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." * * * UPDATE FROM MIKE HIMEBAUCH TO HOWIE CROUCH ON 4/20/09 @ 2301 EDT * * * "Update to Event #44999 regarding SPDS and ERDS being removed from service to support planned maintenance on the UPS vital bus power supply. Maintenance is complete, and SPDS and ERDS were returned to service on 4/20/09 at 2230 EDT. The NRC Resident Inspector has been notified." Notified R3DO (Cameron). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-19
44998 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2009-04-18 01:20 | 2009-04-18 08:38 | 2009-04-18 | COURTESY NOTIFICATION MADE TO STATE OF MASSACHUSETTS INVOLVING AN EMPLOYEE FATALITY "On April 18, 2009 an informational notification was made to the US NRC. "At approximately 0120 EDT on April 18, 2009, the Pilgrim main control room received an emergency medical call stating that a Pilgrim employee had been found unconscious inside the radiologically controlled area of the plant. The individual was treated by the on-site first responders who administered CPR and AED treatment. Off site medical assistance was requested and the individual was transported to the local hospital. "At approximately 0230 EDT, Pilgrim was notified that the individual had died of an apparent heart attack. "A courtesy notification was made to the Massachusetts Emergency Management Agency. "The NRC Resident Inspector has been notified. "The event had no adverse effect to the health and safety of the public." The licensee confirmed that the employee transported offsite was not radiologically contaminated. No press release is planned. * * * UPDATE FROM BRUCE CHENARD TO HOWIE CROUCH ON 4/18/09 @ 1300 EDT * * * "While Pilgrim does not plan to issue a news release regarding this event, it is anticipated that media coverage of the event will ensue based upon the off-site response to the medical emergency. This 10 CFR 50.72(b)(3)(xi) notification is conservatively being made in advance of any media attention." Notified R1DO (Powell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-18
44997 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2009-04-16 16:00 | 2009-04-17 18:44 | 2009-04-17 | UNANALYZED CONDITION DUE TO POSSIBLE UNFAVORABLE GEOMETRY "During a routine NRC inspection, the inspector questioned the adequacy of a 5-gallon limit on liquids allowed in certain process areas to prevent accidental nuclear criticality if the other controls in place are missing. "While further investigation is underway, this event is being reported per 10CFR70 Appendix (b)(1) on a conservative basis. "SAFETY SIGNIFICANCE: The safety significance is low "POTENTIAL CRITICALITY PATHWAYS: Liquid from 5-gallon container would have to spill and all enter normally closed equipment, or uranium dioxide powder spilled from the equipment. "CONTROLLED PARAMETERS: Controlled parameters are moderation "CORRECTIVE ACTIONS: A prohibition of spillable liquids exceeding 3-gallons was established in the affected areas." The licensee will be notifying the NRC Region 2 Senior Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2009-04-17
44996 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2009-04-17 11:00 | 2009-04-17 18:07 | 2009-04-17 | FITNESS FOR DUTY INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2009-04-17
44995 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-04-17 02:07 | 2009-04-17 09:22 | 2009-04-17 | PLANNED MAINTENANCE ON SPDS AND ERDS "At 0207 hours on 04/17/2009, the SPDS [Safety Parameter Display System] and ERDS [Emergency Response Data System] was removed from service to support activities for a planned maintenance outage on the UPS power supply. The duration of work is expected to be approximately 48 hours. During this time, Control Room indications and alternate methods will be available. Since the SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). "The plant is in Op. Con. 5 [Refueling], Reactor Coolant Temperature is 87 [degrees] F and 'A' RHR is in shutdown cooling. "The licensee will notify the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-17
44994 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-04-16 18:28 | 2009-04-16 22:33 | 2009-04-16 | REACTOR SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "At 1828 [CDT] on 4/16/09, it was discovered that the procedure for calibrating Low Steam Line Pressure Safety Injection Lead/Lag units may not ensure that the Tech Spec setpoint requirements were met. Calibration methodology used a ratio of lead over lag time constants to determine acceptance criteria. KPS [Kewaunee Power Station] Tech Specs Table 3.5-1 item 4 requires that the lead and lag time constants have individual ESF initiation instrument setting limits. When the error was discovered, data was reviewed from the most recent calibrations of the pressure channels. While the ratios met acceptance criteria per the calibration procedure, the individual lag time constants did not meet acceptance criteria per Tech Specs. Per TS Table 3.5-3 item 1c, all channels of the Low Steam Pressure/Line Safety Injection signal were declared inoperable. Per KPS Tech Spec 3.5.c., the plant must be placed in Hot Shutdown, as soon as practicable. "Negative reactivity insertion began at 2004 [CDT] on 4/16/09. Therefore, this is reportable under 10 CFR 50.72(b)(2)(i) 'Initiation of a shutdown required by Tech Specs.' Since both trains of Steam Line Low Pressure SI channels are affected this is also reportable under 10 CFR 50.72(b)(3)(ii)(B) 'any event or condition that results in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety' and 10 CFR 50.72(b)(3)(v)(D) 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.'" At 2140 CDT, the reactor was at 56% power and hot shutdown is expected to be achieved at 2330 CDT. The licensee notified the NRC Resident Inspector. | 56 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2009-04-16
44993 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-04-15 16:44 | 2009-04-15 20:19 | 2009-04-15 | OFFSITE NOTIFICATION DUE TO POTENTIAL RELEASE OF TRITIUM "Oyster Creek notified the New Jersey Department of Environmental Protection of a potential release due to the discovery of detectable levels of Tritium in a cable vault that was found while replacing the cable to an [Emergency Service Water] ESW pump. No release is known to be occurring and no release is known to have occurred. The source of the Tritium water is not currently known. A prompt investigation is in progress." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-15
44992 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-04-15 04:15 | 2009-04-15 07:31 | 2009-04-15 | UNAVAILABILITY OF TSC VENTILATION SYSTEM AND CHARCOAL FILTER DURING SCHEDULED MAINTENANCE "At 0415 on Wednesday, April 15, 2009, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system and charcoal filter was removed from service for scheduled preventive maintenance. The charcoal bed filtration system is also out of service in support of the maintenance on the TSC ventilation system. "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system maintenance is scheduled to complete at 1600 on Wednesday, April 15, 2009. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." * * * UPDATE FROM DEAN BRUCK TO JOHN KNOKE AT 1352 ON 4/15/09 * * * "At 1255 on Wednesday, April 15, 2009 the planned maintenance and testing was completed. The TSC ventilation system and charcoal filter have been returned to service restoring full availability to the TSC. "The licensee has notified the NRC Senior Resident Inspector." Notified R3DO (Laura Kozak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Refueling |  | Cold Shutdown | Refueling |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-15
44991 | 0 | NORTH CAROLINA STATE UNIVERSITY |  |  |  | 1000 KW PULSTAR POOL TYPE | 2009-04-10 09:30 | 2009-04-14 16:00 | 2009-04-14 | VIOLATION OF LIMITING CONDITIONS IN TECHNICAL SPECIFICATION 3.5B "On Monday, 13 Apr 2009 at approximately 9 AM, the stack sample pump was observed to be off. On Friday, 10 Apr 2009, the reactor operated from approximately 11 AM to 4 PM. "Upon investigating this situation it was learned that at approximately 9:30 AM on 10 Apr 2009 the stack sample pump apparently lost power. The stack pump remained off until being re-started on 13 Apr 2009. "Technical Specification (TS) 3.5b requires the stack particulate and stack gas radiation monitoring channels to be operable during reactor operation. With the stack sample pump off, neither of these two channels were operable during reactor operation on 10 Apr 2009. The Auxiliary GM may serve as a substitute for one of the two required channels. As a result, the reactor was operated on 10 Apr 2009 in violation of TS 3.5b. "This event is a reportable event as defined in TS (1.2.24d and 6.6.2) under TS 6.7.1 since both channels were not operable as required by the Limiting Conditions for Operation TS 3.5b. The US Nuclear Regulatory Commission (NRC) was notified by telephone on 14 Apr 2009 at approximately 4 PM. The event will be investigated further with a detailed explanation of the event and actions taken and planned to prevent recurrence. The NRC will be given a written report on or before 24 Apr 2009. "Consequences of this event were not significant. Other radiation monitors were in service to monitor airborne radioactive effluent and reactor bay airborne activity. All of those monitors indicated typical radiation levels during reactor operation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 2 | NC | NPR | [5 empty] | 0 | 2009-04-14
44990 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2009-03-31 16:45 | 2009-04-14 15:40 | 2009-04-14 | AGREEMENT STATE REPORT - LEAKING TANK TRAILER WITH TOTAL ACTIVITY OF VARIOUS RADIONUCLIDES OF 20 MILLICURIES The State submitted the following report via fax: "This event involved a leaking Tank Trailer containing a total activity of radionuclides of 742.88 MBq (20 mCi), primarily of H-3 (738 MBq) and Tc-99 (3.88 MBq). Small contribution from U-233, U234, U235, U236 and U238. The licensee filled the tank trailer and classed the material as an RQ, of UN 1992, Waste, Flammable Liquids, toxic, nos., (n-butyl alcohol, penol), 3 (6.1), PGIII, Marine Pollutant, (PCB's benzene). "Tank Trailer number E-112178, total gross weight of 46,765 pounds of flammable liquids, toxic, nos, with radioactive condensate. "This incident is still under investigation, a written report is pending." Event Report ID No: UT 090003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2009-04-17
44989 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-04-14 07:43 | 2009-04-14 14:18 | 2009-04-14 | SAFETY PARAMETER DISPLAY SYSTEM AND ERDS OUT OF SERVICE "On April 14, 2009, at approximately 0743 hours, electrical power was lost to 480 volt busses V-1-F and V-2-F. These busses supply electrical power to the Emergency Response Data System (ERDS). The electrical power loss caused the ERDS, the Safety Parameter Display System (SPDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) to be disabled. Preliminary investigation indicates that a failed inverter caused the power loss. "Contingency plans have been established to transmit plant parameter data and perform the dose assessment function in the event of an emergency while ERDS is unavailable. The ERDS, SPDS and CADAP were restored at 1110 hours. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-14
44988 | 0 | PORTSMOUTH AMERICAN CENTRIFUGE |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-04-14 | 2009-04-14 13:40 | 2009-04-15 | DIESEL FUEL OIL SPILL REQUIRING OFFSITE NOTIFICATIONS "On 04/14/09 at approximately 0918 hours, the Plant Shift Superintendent was notified of an oil spill that occurred on the plant site. A diesel generator sitting near a construction area was leaking fuel. Primary and secondary containment was initiated to contain the spill. At 1130 hours environmental response personnel determined that the quantity of oil spilled exceeded the Reportable Quantity (RQ). "At 1144 hours, 04/14/2009, the Plant Shift Superintendent notified the National Response Center and the Ohio EPA that a Reportable Quantity (RQ) of oil (diesel fuel) was released to the environment. "Ohio EPA assigned incident #: 0904-66-1084. "National Response Center assigned incident #: 902636 "ACD2-RG-044, Appendix N, section 1 requires an NRC event notification when other government agencies are notified." The amount of fuel oil spilled was 25 to 40 gallons. Licensee will be issuing a press release about this spill. * * * UPDATE AT 2241 ON 4/14/2009 FROM SPAETH TO ABRAMOVITZ * * * The licensee is issuing a press release and has revised the estimated spill to 300 gallons. Notified the R2DO (Widman), NMSS (Kokajko), and PAO (Hayden) via e-mail. * * * UPDATE ON 4/15/2009 AT 1400 FROM SPAETH TO ABRAMOVITZ * * * This event occurred at the American Centrifuge Plant (Docket 70-7004, license SNM-2011) and not the gaseous diffusion plant. Notified the R2DO (Widman) and NMSS (Kokajko) via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2009-04-15
44987 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-04-13 | 2009-04-14 12:20 | 2009-04-24 | AGREEMENT STATE REPORT - THEFT OF A TROXLER NUCLEAR GAUGE State submitted this report via email: "The owner of Global Laboratories, called the Louisiana Department of Environmental Quality on April 14, 2009 to report the theft of a work truck that had a Troxler Nuclear Gauge chained in the back of the truck. The Troxler Gauge 3440 (s/n 27805) contained 40 mCi of Am-241 (s/n 47-24434) and 8 mCi of Cs-137 (s/n 750-1721). According to Mr. Kent, the gauge was locked in the case and the case was doubled chained in the bed of the truck. Mr. Kent reported the theft to the West Monroe Police Department on April 13. 2009 at approximately 3:30PM and also contacted the Ouachita Sheriffs Office. Mr. Kent is offering a $500.00 reward for the return of the Troxler Nuclear Gauge. An investigation is ongoing and any further information will be forwarded to the NRC." Transport vehicle description: White 2000 GMC Z71 license plate number B412958 Event Report ID No. LA090012 * * * UPDATE FROM SCOTT BLACKWELL TO HOWIE CROUCH ON 4/17/09 @ 1512 EDT * * * The State of Louisiana reports that the stolen work truck has been recovered but the gauge is still missing. Law enforcement agencies continue to investigate. Notified R4DO (Whitten), FSME (Einberg) and ILTAB via email. * * * UPDATE FROM SCOTT BLACKWELL TO KARL DIEDERICH ON 4/24/09 @ 1537 EDT * * * The State of Louisiana reports that the stolen gauge has been found and the licensee has taken possession of it. It was found in a sheriff's evidence room, and appears undamaged. Complete surveys will be performed Monday 4/27/09. Notified R4DO (Gaddy), FSME (White), and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-04-17
44986 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-02-03 | 2009-04-13 12:21 | 2009-07-01 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO THE LUNGS The following report was received from the state of Washington via e-mail: "On February 9 2009, a worker was sent for a lung count at the Battelle (Pacific Northwest National Laboratory) lung counter for a bioassay measurement. The lung count was ordered due to the worker working in an area where airborne contamination levels could cause more then 2.5 DAC-hrs (with respiratory protection factors applied), and greater then 520 DAC-hrs assuming no respiratory protection was worn in one day. The reason for requiring this count was to ensure that measures used to protect the workers were functioning properly. The workers first lung count detected approximately 0.2 nCi of Am-241. Assuming the exposure was from 10 days prior, the intake was approximately 1.9 nCi Am-241. The annual limit of intake for Am-241 is 6 nCi (1micron AMAD particle size). The estimated dose was about 1/3 of the annual limit, or 16 REM CDE (Annual limit 50 REM). The worker had previous whole body exposure, but this added amount did not cause a limit to be exceeded. "On March 25, 2009 the licensee informed the Washington State Department of Health [DOH] that further testing by Battelle caused a revision to the original calculated dose and the new calculated dose would exceed the 50 REM CDE limit. The date of exposure (February 3, 2009) was assumed by the licensee, based on air sample data and the use of respiratory protection that may not have provided adequate coverage (use of filtering respirator instead of supplied air). On February 3, the worker was in a containment in which air sample results were about 1e-8 microCi/ml gross alpha activity concentration for several hours and was wearing a Powered Air Purifying Respirator (PAPR, protection factor of 1000). Bioassay results (fecal) from one other worker who was also in the containment showed a small amount of activity, and a dose was assigned to this second worker that did not exceed the legal limit. The second workers lung count was less than detection limits. "The cause is still unknown. "Contributing factors: High airborne activity, loss of respiratory protection. "DOH is conducting an investigation of this incident. "Corrective action : Curtailment of work in containment, training on removal of anti contamination clothing and respirator, investigation of respiratory protection failure. "There was no media coverage of this incident. "Activity and isotope(s) involved: Am-241, Pu-240/241 Overexposures: (number of workers/members of public; dose estimate; body part receiving dose; consequence): There was one potential overexposed worker, no members of the public were exposed, estimated dose to the worker is about 100 REM CDE and 5 REM CEDE. This value will change following further measurements, investigation and calculations. "Worker was removed from the restricted area, work in the area where the intake was assumed to occur was stopped, pending the outcome of further investigation." Washington State Incident Number: WA-09-013 * * * UPDATE PROVIDED VIA EMAIL FROM KETTER TO PARK AT 0823 EDT ON 7/1/09 * * * "On June 22, 2009 the licensee informed the Washington State Department of Health that the Committed Effective Dose Equivalent (CEDE) for the worker was 6.8 cSv (6.8 REM) and the Committed Dose Equivalent (CDE) was 120 cSv (120 REM) to the bone surface. The workers Deep Dose Equivalent (DDE) from his dosimetry for the first quarter 2009 was 0.3mSv (30 mRem). The dose calculation was completed by a consultant for the licensee. Intake was calculated using methodology of ICRP 30, modified for clearance function. Intake for Am-241 was calculated from lung deposition and calculated clearance rates. Intake of Plutonium (Pu) was inferred from excreta bioassay results and assumed ratios of Am-241 to Pu. Dose was calculated using CINDY code version 1.2. The particle size was considered, and a 1micron Activity Median Aerodynamic Diameter (AMAD) was chosen as the best fit. The total calculated intakes are: Am-241 153 Bq (4.14 nCi), Pu239/240 89.9 Bq (2.43 nCi),Pu 238 16.8 Bq (0.455 nCi). "The exact cause of the incident is unknown. The assumed cause is a failure of the respiratory protection system. The licensees corrective actions to prevent reoccurrence are to test each worker with a challenge gas prior to high risk work, increased engineering controls to mitigate airborne contaminants, specific training using phosphorescent powder and black lights for workers, more frequent bioassay samples, inclusion of nasal smears for immediate detection of intakes, use of supplied air respirators over air filtering respirators for high risk work, and training for workers, managers and health physics staff. Note that work was resumed in the area, and no further exposures have occurred. "Worker was removed from the restricted area, work in the area where the intake was assumed to occur was stopped, changes to operations and training methods, changes to engineering controls, changes to testing of respirators prior to use. "Contributing factors [are] high airborne activity, [and] loss of respiratory protection. "DOH has completed an investigation of this incident. "There was no media coverage of this incident. "There was one overexposed worker. No members of the public were exposed. Estimated dose to the worker was 120 REM CDE and 6.8 REM CEDE." Notified the R4DO (Pick) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-04-16
44985 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-04-12 04:30 | 2009-04-12 13:47 | 2009-04-12 | OFFSITE NOTIFICATION DUE TO SULFURIC ACID SPILL INTO BURM "On Sunday, April 12, 2009 at about 0430 PDT, Southern California Edison (SCE) discovered that approximately 300 gallons of sulfuric acid had overflowed from the Unit 3 Sulfuric Acid Day Tank. The acid was contained within a berm around the tank, and there was no release to the environment. SONGS (San Onofre Nuclear Generating Station) Hazardous Materials personnel are in the process of responding to this event. Once onsite they will remove the acid from the berm for disposal at a hazardous waste facility. The overflow was caused by leakage from the Bulk Acid Tank to the Acid Day Tank. "At about 1004 PDT, SCE notified the San Diego County Department of Environmental Health, and at about 0940 PDT, SCE notified the California Office of Emergency Services. "SCE is making this notification in accordance with 10CFR50.72(b)(2)(xi). "At the time of the report, SONGS Unit 2 is in Mode 1 at approximately 99% power and Unit 3 is in Mode 1 at approximately 100% power. The NRC Senior Resident Inspector has been notified of this occurrence and will be provided with a copy of this report." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-12
44984 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-04-11 12:10 | 2009-04-11 14:27 | 2009-05-01 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY - TECHNICAL SUPPORT CENTER VENTILATION UNAVAILABLE "Notified by Engineering that Technical Support Center (TSC) emergency charcoal sample failed acceptance criteria. Declared TSC ventilation unavailable at 12:10 PM EDT, 4/11/09. TSC ventilation supports RERP radiological habitability function and as such represents a major loss of emergency assessment capability, offsite response capability, or offsite communications capability in accordance with 10CFR50.72(b)(3)(xiii). Notified all Shift Managers if an emergency event is declared (Alert or higher), Shift Managers will need to modify emergency call out service so that TSC staffing report to Emergency Operating Facility (EOF). The use of the EOF as a backup facility for the TSC is included in Fermi's RERP Plan. Fermi will notify the NRC upon completion of corrective maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ROBERT MATUSZAK TO DONALD NORWOOD ON 5/1/09 AT 1621 EDT * * * "Regarding Technical Support Center (TSC) ventilation unavailability: Corrective maintenance to restore HVAC system has been completed satisfactorily. TSC has been restored as an Emergency Response facility." The TSC was declared operable at 1457 EDT. Corrective maintenance included replacing the out-of-spec charcoal filters and satisfactory follow-up tests. The licensee notified the NRC Resident Inspector. Notified R3DO (Hills). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-11
44983 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-04-10 09:00 | 2009-04-10 18:21 | 2009-04-10 | OFFSITE NOTIFICATION DUE TO SULFURIC ACID OVERFLOW "On Friday April 10, 2009, at about 0900 PDT, Southern California Edison (SCE) discovered that approximately 1,000 gallons of sulfuric acid had overflowed from the Unit 3 Sulfuric Acid Day Tank. The acid was contained within a berm around the tank, and there was no release to the environment. SONGS (San Onofre Nuclear Generating Station) Hazardous Materials personnel responded to the event, and are in the process of removing the acid from the berm for disposal at a hazardous waste facility. The overflow was caused by leakage from the Bulk Acid Tank to the Acid Day Tank. "At about 1340 PDT, SCE notified the San Diego County Department of Environmental Health, and at about 1353 PDT, SCE notified the California Office of Emergency Services. "SCE is making this notification in accordance with 10CFR50.72(b)(2)(xi). "At the time of this report, SONGS Unit 2 is in Mode 1 at approximately 99% power and Unit 3 is in Mode 1 at approximately 100% power. The NRC Senior Resident Inspector has been notified of this occurrence and will be provided with a copy of this report." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-10
44982 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2009-04-10 05:38 | 2009-04-10 12:43 | 2009-04-10 | HIGH PRESSURE COOLANT INJECTION AUTOMATIC INITIATION DUE TO TURBINE TRIP "At 0538 on Friday, April 10, 2009, Nine Mile Point Unit One manually tripped the turbine at approximately 28% rated power in response to rising turbine bearing vibrations. Following the manual turbine trip, the High Pressure Coolant Injection (HPCI) system automatically initiated on the turbine trip signal. The HPCI system initiation signal was reset immediately following the turbine trip. Reactor water level was maintained in the normal operating range throughout the transient. At Nine Mile Point Unit One the HPCI system is a mode of operation of the feedwater and condensate system. It is not an Emergency Core Cooling System (ECCS). A HPCI system actuation signal on a turbine trip is an expected response of the HPCI system. Nine Mile Point Unit 1 remains at power since the turbine was tripped at a power level that is within the capacity of the turbine bypass valves. "10 CFR 50.72(b)(3)(iv)(A) requires reporting within 8 hours when a valid actuation of the feedwaler coolant injection system occurs. "The event has been entered into the corrective action program. "There are no other adverse impacts to the station based on this event." The NRC Resident Inspector was notified. | 23 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-04-10
44981 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-04-09 19:21 | 2009-04-10 08:30 | 2009-04-10 | AGREEMENT STATE REPORT - LEVEL GAUGE CESIUM-137 SOURCE WOULD NOT RETRACT The following information was provided via email: "On April 9, 2009, at 19:21 the Agency [state] received a phone call from the Radiation Safety Officer (RSO) at Flint Hills Resources in Odessa Texas. The RSO reported that a 300 millicurie (120 mCi calculated) Cesium (Cs) -137 source used in an Ohmart\VEGA model # SHLM level gauge would not fully retract into the source holder. The gauge is installed on the side of a [chemical] reactor vessel. The source will retract to the sleeve between the vessel and the gauge housing, but will not go into the gauge. The source is currently fully inserted into the vessel. Dose rates in the area are normal. No additional exposure was received by individuals at the facility. Management will meet on April 10, 2009, to determine how to address the source retrieval. The gauge was to be removed from the vessel for disposal by the manufacturer. The licensee will provide additional information next week. A similar event occurred at this facility in October, 2008 (EN44543)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-15
44980 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-12-09 | 2009-04-09 17:07 | 2009-04-09 | AGREEMENT STATE REPORT - LEAKING CS-137 SCINTILLATION COUNTER CHECK SOURCE Received the following information via fax: "On April 2, 2009, [deleted] Radiation Safety and Control Services, a New Hampshire Health Physics company [located in Stratham, NH] reported that a Beckman scintillation counter (model 3801, # 7014048) owned by them is believed to have a leaking Cs-137 check source. The instrument was not operating properly. In December 2008, a technical support person was called, who determined the source was not reaching the sample. During an inspection of the source mechanism, a smear of the exposed spring that push[e]s the source revealed 500 cpm of removable contamination by direct frisk of the Q-tip. More smears were taken and two near the spring indicated 4,285 and 5,586 dpm beta when counted on a LSC on December 10, 2008. This LSC contains a 40 microCi cesium 137 check source, part number 598860, # 60219005-A originally dated August 18, 1986. The device was taken out of service immediately and labeled as internally contaminated. Follow-up with Beckman Instruments will take place regarding replacement of the source and decontamination efforts." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-04-14
44979 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-04-08 11:45 | 2009-04-09 13:48 | 2009-04-09 | AGREEMENT STATE REPORT - MISADMINISTRATION INVOLVING Y-90 MICROSPHERES The following was received via facsimile: "N.C. Radiation Protection Section was notified of a misadministration involving Y-90 microspheres. The licensee reports that the administered dosage was 24 percent less than the prescribed dosage. "Licensee reports no equipment malfunction and no leakage of radioactive material from the delivery device. Licensee has notified patient and there are no plans to perform a second administration. "Licensee is contacting vendor to assist in investigation. "N.C. Radiation Protection has not received any media attention as of this report. No press release has been issued." The North Carolina Event Report ID Number for this event is NC-09-22. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-04-15
44978 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2009-04-08 14:55 | 2009-04-08 17:22 | 2009-04-08 | OFFSITE NOTIFICATION TO THE STATE OF CONNECTICUT DUE TO ONSITE FATALITY "The purpose of this report is to notify the NRC of an untimely death involving a Dominion worker at the Millstone station. Specifically, at 1406 EDT the Unit 3 Control Room was notified that an individual located outside the Protected Area had lost consciousness. The site emergency medical team responded and an ambulance was requested at 1410. At 1455 the Unit 3 Control Room was notified via Lawrence Memorial Hospital that the individual passed away. The untimely death was not occupationally related." State and local offsite notifications were made. The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-08
44977 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-04-06 13:20 | 2009-04-08 14:45 | 2009-04-08 | CONTAMINATED SEALED SOURCES RECEIVED IN TWO SHIPMENTS The following information was provided by the state via fax: "On 4/6/09, the Agency [MA Radiation Control Program] received written notification from Thermo NITON Analyzers that they had received 2 shipments of Isotope Products Laboratory Model XFB-3 Cd-109 sources, both of which contained a few contaminated sealed sources. On 9/9/08, NITON received a shipment of 45 sealed sources containing 40 mCi of Cd-109 each and 3 of the sources were found to be contaminated. On 10/13/08, NITON received a shipment of 30 sealed sources containing 10 mCi of Cd-109 each and 3 of the sources were contaminated. The licensee, NITON, returned the sources to IPL for evaluation. IPL's evaluation concluded the sources were contaminated and not leaking. The licensee stated that a notification was drafted in October 2008, however, an oversight occurred and inadvertently the notification was not submitted." Massachusetts Docket No.: 04-8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-04-13
44976 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2009-04-07 23:45 | 2009-04-08 04:47 | 2009-04-08 | LOSS OF ERDS DUE TO EQUIPMENT FAILURE "During a routine check of the ERDS link, it was discovered that the computer housing the modem was frozen and not updating; therefore, the modem would not be transmitting information to the NRCOC. This condition only affected Unit 3; Unit 4 communication link is still operating. This is an 8-hr reportable event per 10CFR 50.72(b)(3)(viii)." The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-08
44975 | 0 | HALLIBURTON ENERGY SERVICES INC. |  |  |  |  | 2008-08-20 | 2009-04-07 14:43 | 2009-07-14 | POSSIBLE OVEREXPOSURE DURING THE SECOND QUARTER OF 2008 Landauer, a dosimeter processing vendor, notified Halliburton Energy Services of a possible overexposure in their quarterly dosimetry report on 8/20/2008. Around that same time Halliburton had just terminated the previous RSO and was in the process of hiring a new RSO. The current RSO became aware of this possible overexposure when she received an annual exposure report from Landauer. One well logging engineer, who had been performing work for Halliburton at the Prudhoe Bay, Alaska site, reportedly received an exposure of 9141 millirem from 4/1/2008 to 6/30/2008. The report from Landauer contains a note to the effect that the dosimeter had been read twice with the second reading in agreement with the first; however, there was an irregularity. The RSO is investigating the occurrence. * * * UPDATE AT 1807 ON 7/14/2009 FROM ELIZABETH FOLTZ TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "Halliburton conducted an investigation to determine the validity and potential cause of the 9141 millirem exposure. To assist with the investigation, Halliburton engaged the services of a recognized expert in the field of radiation dosimetry. The investigation was comprehensive and included employee interviews and a review of their work involving sources of radiation, review and analysis of exposure monitoring data for all personnel working in Alaska, review of job records involving radioactive sources, and actual recreations of multiple exposure scenarios. Landauer technical experts were also engaged during the investigation process. Upon conclusion of the investigation, it was determined that the employee involved did not receive a 9141 millirem dose or any dose in excess of that allowed by the regulations. Halliburton has requested a modification of the employee's dose record by Landauer. On May 7, 2009, Halliburton submitted a written notification of this event to the NRC Region IV Deputy Director, including a detailed report of the investigation and findings." Notified the R4DO (Gaddy) and FSME (Reis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2009-04-07
44974 | 0 | DOW CHEMICAL |  |  |  |  | 2009-04-06 08:30 | 2009-04-06 16:50 | 2009-04-06 | LEVEL GAUGE SHUTTER FAILURE The shutter for an Ohmart SHRM-B strip source containing 12 millicuries of CS-137 failed in the open position. The source is used as a level instrument with the shutter normally open for this application. For the past two weeks the licensee attempted to close the shutter without success. On April 6, 2009 at 0830 the shutter pin broke while employees were attempting to once again close the shutter. There were no personnel radiation exposures during this event. The licensee is devising a method to shield the source and remove it for shipment to a repair facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-04-06
44973 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-12-15 | 2009-04-06 13:00 | 2009-04-06 | INCIDENT INVOLVING CO-60 GAMMA KNIFE DURING PATIENT TREATMENT The following information was provided by the state via e-mail: "During an inspection on March 17 through 19, 2009, the ODH [Ohio Department of Health] inspector identified through the licensee's radiation safety committee meeting minutes an incident involving the Co-60 Gamma Knife that occurred on December 15, 2008, at approximately 2:15 pm. During a patient treatment, the couch moved out of treatment position. The emergency stop button was activated and the system did not respond. The licensee's staff had to manually pull out the couch from the Gamma Knife and manually close the doors to the Gamma Knife to shield the source. "According to the licensee, radiation exposure to all individuals involved with the incident was minimal. The incident DID NOT result in a medical event for the patient. The manufacturer (Elekta) was immediately contacted and the Gamma Knife was repaired. Patient treatment was resumed and completed without incident. According to Elekta, the Gamma Knife system experienced an illegal couch sensor error due to a known software bug problem. "The licensee failed to notify the Ohio Department of Health, Bureau of Radiation Protection of this device failure and therefore this is determined to be non-compliant with the provisions of rule 3701:1-40-20 (B)(2)(a,b,c) of the Ohio Administrative Code." Ohio State Reference Number: OH 2009-008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-04-09
44972 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-04-06 12:30 | 2009-04-06 14:18 | 2009-04-06 | TRUCK ENGINE FIRE WITH CONTAMINATED MATERIAL IN TRAILER "At ~ 1230 EDT on 04/06/09, the Virginia DOT was notified that a truck shipment from North Anna to Surry Power Station containing radioactive contaminated equipment had caught on fire. "The fire was contained to the truck tractor engine compartment, and was put out with no radioactive release having occurred. The trailer is on state route 522, approximately 1 mile from route 33 in Louisa County, Virginia, within 10 miles of North Anna. "The truck is not drivable at this time. North Anna management and Health Physics personnel are at the site. The station NRC residents are also at the site. Media personnel are present. "The shipment type is described by the state DOT as: 'Radioactive Material Surface Contaminated Objects, SCO-II, 7, UN 2913 Fissile Excepted'. Activity: 7.82 millicuries total in 2 containers, or 2.89 E2 MBq. The materials were GSI-191 support equipment and tools, grating covers, and herculite wrapped Styrofoam." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-06
44971 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-04-02 | 2009-04-06 13:44 | 2009-04-06 | LOST AMMONIA ANALYZER Cormetech Inc. was unable to locate an ammonia analyzer containing 10mCi of Ni-63 during a routine inspection on April 2, 2009. The manufacturer of the instrument is Environmental Technologies Group. The instrument is a FP-IMS/CEM Ammonia Analyzer Model 221. The licensee is taking action to locate the item but it is believed that the item is lost. NC Incident: 09-21 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-04-09
44970 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2009-04-03 23:54 | 2009-04-04 08:54 | 2009-05-22 | MANUAL REACTOR SCRAM DUE TO HIGH VIBRATIONS IN THE TURBINE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On April 3, 2009, at approximately 2345 Mountain Standard Time (MST), Palo Verde Unit 3 operators manually tripped the reactor from approximately 29% rated thermal power in response to increasing vibration on the main turbine. The unit was being shutdown from 100% power for a refueling outage at the time of the trip. "Following the manual reactor trip, all CEAs fully inserted into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event." No relief or safety valves lifted during the event. Decay heat is being removed via the steam dump to condenser valves. The licensee will continue to cool the plant down to support their planned refueling outage. There was no effect on Unit 1 or Unit 2. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DANIEL HAUTALA TO JOHN KNOKE AT 1429 EDT ON 05/22/09 * * * "This notification is being made to retract Event Notification (EN 44970) made by Arizona Public Service Company (APS) on April 4, 2009, that reported a reactor protection system actuation in Unit 3 during a planned shutdown for a refueling outage. Further review of the reporting guidance in NUREG 1022 (revision 2) has concluded that since the manual trip was not initiated to mitigate an event and the decision to trip the reactor was at the discretion of the licensed operators the reporting threshold was not met. The procedure for a normal reactor shutdown directs that a manual reactor trip be initiated at approximately 20% rated thermal power. Due to prior issues with vibration of the main turbine monoblock rotor during power reductions related to plant shutdown, just-in-time training was provided to the plant operators which included action to trip the reactor if main turbine bearing vibration increased. Without the pre-determined discretion provided through the just-in-time training, the main turbine alone could have been tripped, followed by lowering reactor power to 20%, and then tripping the reactor. The plant design does not include an automatic reactor trip when the main turbine is tripped. "Event Summary: On April 3, 2009, at approximately 23:45 Mountain Standard Time (MST) Palo Verde Unit 3 operators manually tripped the reactor from approximately 29% rated thermal power in response to increasing vibration on the main turbine. The unit was being shutdown from 100% power for a refueling outage at the time of the trip. "Following the manual reactor trip all CEAs fully inserted into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event." NRC Resident Inspector has been notified. Notified R4DO (William Jones) | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-04-04
44969 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-04-03 16:00 | 2009-04-03 21:23 | 2009-04-07 | MEDIA RELEASE DUE TO ACID SPILL "At approximately 4:00 p.m. on April 3, an acid leak occurred [on top of Building 5A] at the B&W Mount Athos facility in Campbell County, Va. As a result of the incident, employees were evacuated from the immediate area in accordance with the company's operating procedure. "The B&W Emergency Team was immediately dispatched and secured the area and the leak. Two company employees were exposed to the acid and treated on the scene. "There was no release of radioactive material during this incident. No danger was posed to the public, and there was no release of the acid into the environment. B&W is investigating the incident." The acid was nitric acid, 69% concentration. The affected employees washed off the acid with water and required no further medical treatment. NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2009-04-08
44968 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-04-03 16:30 | 2009-04-03 17:07 | 2009-04-09 | PLANNED MAINTENANCE ON SPDS AND ERDS "At 1630 hours on 04/03/2009, the SPDS and ERDS system was removed from service to support activities for a planned maintenance outage on the UPS vital bus power supply. The duration of work is expected to be approximately 24 hours. During this time, Control Room indications and alternate methods will be available. Since the SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY J. GROFF TO J. KOZAL ON 04/09/09 AT 1257 * * * "Update to event #44968 regarding SPDS and ERDS system removed from service to support planned outage on the UPS vital power supply. Planned work which resulted in the removal from service of the SPDS and ERDS has been completed." The licensee will notify the NRC Resident Inspector. Notified R3DO (Daley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-04-03
44967 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2009-04-03 11:36 | 2009-04-03 13:40 | 2009-04-03 | MANUAL REACTOR TRIP DUE TO LOSS OF 21 MBFP "At 1136 hours on April 3, 2009 with the plant in mode 1, Indian Point Energy Center Unit 2 experienced a 21 Main Boiler Feed Pump (MBFP) trip. Following the MBFP trip the turbine runback circuit did not actuate as expected. The plant operators attempted to perform a manual main turbine runback and inserted a manual reactor trip based on the impending trip signal of Steam Generator low level. Auxiliary feedwater automatically started as expected. Troubleshooting of the cause of the transient is in progress. Unit 2 is stable in mode 3 with AFW in service. Heat removal is to the main condenser via the steam dumps. Offsite power is available and supplying all safeguards busses. Unit 3 is not affected and remains in mode 6 for 3R15. "The [NRC] Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-04-03
44966 | 0 | GAF MATERIALS CORPORATION |  |  |  |  | 2009-04-03 | 2009-04-03 09:55 | 2009-04-03 | LOST NI-63 SOURCE The licensee was performing their annual registration inventory when they discovered that a gas chromatograph detector was missing. A search of the premises was conducted and they were unable to locate the device thus it is considered lost. The detector contained a Ni-63 source with an original source strength of 15 mCi (on 11/15/87). Its original use was in a Hewlett-Packard model 19233B Gas Chromatograph, serial number L-3031. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-04-03
44965 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2009-04-03 00:28 | 2009-04-03 03:27 | 2009-04-03 | MANUAL REACTOR SCRAM DUE TO INCREASING REACTOR WATER LEVEL DURING CALIBRATION "This report is being made under [10 CFR] 50.72(b)(2)(iv)(B) for inserting a manual reactor scram due to indicated reactor water level of 205 inches and rising. The exact cause of the reactor water level increase is not known at this time. However, STP [Surveillance Test Procedure] 3.3.3.2-09, 'Reactor Water Level and Pressure Instruments Calibration' was in progress at the time and is likely the cause of the level transient. "In addition, this report is being made under [10 CFR] 50.72(b)(3)(iv)(A) due to PCIS [Primary Containment Isolation System] groups 2, 3 and 4 being received when reactor water level dropped below 170 inches following the reactor scram. All isolations went to completion. This level response is considered normal following a reactor scram from power and reactor water level is currently being controlled in the normal band. All PCIS group isolations were reset." All rods fully inserted during the scram. The plant is in a normal shutdown electrical lineup with offsite sources powering the safety busses. No safety or relief valves lifted during the transient. Decay heat is being removed via the steam bypass to condenser valves. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-04-03
44964 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-03-19 | 2009-04-02 17:45 | 2009-04-08 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following information was received from the State of Texas via Email: "On February 19, 2008, an industrial radiography trainee working with two trainers at a chemical plant in La Porte, TX observed that his survey meter remained off-scale despite his attempt to crank the source into the shielded position. The device was a QSA Model 880, serial number D3759 containing a 76.7 curie Ir-192 sealed source QSA model A424-9. At that time the radiographers established a 360 degree barricade at the 2mR/hr level and notified the Radiation Safety Officer (RSO) who was out of town. The RSO called a specific licensee authorized by the State of Texas to perform source retrievals. Visual watch over the area was maintained by four employees as some radiation fields extended outside a fenced area. The retrieval was performed in an uneventful manner and although the camera was returned to a fully operational state, the company decided to take the camera out of service and have it fully inspected by the manufacturer. This event is closed. "This event was reported within 24 hours of the event using the NMED reporting system and not to the HOO [NRC Headquarters Operations Officer]. Failure to properly report this event was determined after a review was conducted of all radiography related events reported in the State of Texas from September 1, 2006 to March 31, 2009. This review was initiated in response to the State of Texas Incident Investigation Program (IIP) determining that they had failed to correctly interpret the requirements for reporting this type of event. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. In an effort to prevent a reoccurrence of this, each member of IIP was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Number: I - 8495 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44963 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-01-05 | 2009-04-02 18:54 | 2009-04-08 | AGREEMENT STATE REPORT- RADIOGRAPHY CAMERA MALFUNCTION The following information was received from the State of Texas via Email: "On February 5, 2008, the Agency was notified by the licensee that one of their crews had contacted their office and informed them that the guide tube on their camera had detached from the camera housing and a 91.4 curie Iridium (Ir) 192 source could not be retracted into the camera. The crew was instructed to maintain surveillance of the area until the source recovery team got to their location. Once there, the source recovery team determined that the source drive cable was no longer in the gear housing. They then cut the drive cable housing about one foot from the gear housing. The drive cable was located, and they manually pulled the cable and returned the source to the shielded position. The cause of the failure was determined to be a build up of material in the threads of the camera where the guide tube connected to it. This prevented the guide tube from adequately threading into the camera and allowing the guide tube to separate from the camera during use. The camera was inspected and cleaned. All cameras of similar design were also inspected. No other cameras were found to have the same problem. This event is closed. "This event was reported within 24 hours of the event using the NMED reporting system and not to the HOO [NRC Headquarters Operations Officer]. Failure to properly report this event was determined after a review was conducted of all radiography related events reported in the State of Texas from September 1, 2006 to March 31, 2009. This review was initiated in response to the State of Texas Incident Investigation Program (IIP) determining that they had failed to correctly interpret the requirements for reporting this type of event. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. "In an effort to prevent a reoccurrence of this, each member of IIP was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Report: I- 8480 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44962 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-11-25 | 2009-04-02 17:47 | 2009-04-08 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following information was received from the State of Texas via Email: "On November 25, 2008, the Agency was notified by the licensee that a source disconnect had occurred while using an INC IR - 100 radiography camera containing an 80 curie Iridium -192 source. While the licensee was collecting information on this event, they received a phone call informing them that the source involved with the event had failed the latest leak test performed on it. A source recovery team was sent to the location and returned the source to the radiography camera. A second leak test was taken on November 26, 2008. The company performing the analysis of the leak test informed the licensee that both the first and the second test were both within acceptable limits. The first test had been misinterpreted. The disconnect was determined to have caused by a worn connection in the pigtail. The pigtail was sent to the manufacturer for repair. All exposures to individuals involved in this event were well below applicable limits. This file is closed. "This event was reported within 24 hours of the event using the NMED reporting system and not to the HOO [NRC Headquarters Operations Officer]. Failure to properly report this event was determined after a review was conducted of all radiography related events reported in the State of Texas from September 1, 2006 to March 31, 2009. This review was initiated in response to the State of Texas Incident Investigation Program (IIP) determining that they had failed to correctly interpret the requirements for reporting this type of event. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. In an effort to prevent a reoccurrence of this, each member of IIP was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Number: I - 8583 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44961 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-10-18 | 2009-04-02 18:37 | 2009-04-08 | AGREEMENT STATE REPORT - INABILITY TO RETRACT RADIOGRAPHY SOURCE The following information was received from the State of Texas via Email: "On November 9 2007, the agency was notified by the licensee of an event that occurred while they were performing radiography operations at a remote location. The licensee reported that the guide tube on a radiography camera containing a 75 curie Iridium (Ir) - 192 source was damaged, preventing them from being able to retrieve the radiation source back into the camera. The radiographer contacted the licensee's main office and was instructed to monitor the area and restrict access until the source retrieval supervisor arrived at the location. The supervisor was able to remove the crimp in the guide tube, allowing them to sufficiently retract the source into the camera. No exposures were received that exceeded regulatory limits. The licensee is redesigning their holder to prevent this from occurring in the future and provided additional training to their personnel. This event is closed. "This event was reported within 24 hours of the event using the NMED reporting system and not to the HOO [NRC Headquarters Operations Officer]. Failure to properly report this event was determined after a review was conducted of all radiography related events reported in the State of Texas from September 1, 2006 to March 31, 2009. This review was initiated in response to the State of Texas Incident Investigation Program (IIP) determining that they had failed to correctly interpret the requirements for reporting this type of event. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. "In an effort to prevent a reoccurrence of this, each member of IIP was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Report: I-8454 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44960 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-05-20 | 2009-04-02 18:19 | 2009-04-08 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE UNABLE TO RETURN TO THE FULLY SHIELDED POSITION The following information was received from the State of Texas via Email: "On June 4, 2007, the Agency was notified by the licensee personnel that while performing industrial radiography using a QSA Global Model 660 exposure device serial number B- 2515, with a 61 Ci, IR-192 source, serial number 34471B, one of the radiography crews had an exposure device fall, causing a severe crimp in the source guide tube. As a result of the crimp, the source was not able to be returned to the fully shielded position. Licensee personnel expanded the radiation boundary and shielded the source until authorized personnel could retrieve the source. The source was retrieved and the source guide was returned to the manufacturer for repair. This event is closed. "Failure to report this event was determined after a review was conducted of all radiography related events reported in the State of Texas. This review was initiated in response to the State of Texas Incident Investigation Program (IIP) determining that they had failed to correctly interpret the requirements for reporting this type of event. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. "In an effort to prevent a reoccurrence of this, each member of IIP was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Report: I-8419 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44959 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-01-28 | 2009-04-02 17:50 | 2009-04-08 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNTION The following information was received from the State of Texas via Email: "On January 28, 2008, the Agency was notified by the licensee that a radiographer was doing work in one of their shooting bays when a 35.7 curie Iridium -192 source would not retract into the radiography camera. The radiographer used an installed video camera to look into the room and saw that the component he was working on had fallen and crimped the guide tube attached to the camera. The source was cranked to the end of the guide tube, and two attempts to straighten the guide tube and retract the source failed. A source retrieval supervisor then entered the room and placed lead bags over the end of the source guide tube and placed a lead sheet over the lead bags. The supervisor attempted to reshape the section of the guide tube that had been damaged using a hammer. This also did not work. Finally, the supervisor cut the damaged section of the guide tube out and the source was then retracted to the camera. The reported exposure for this event was 15 millirem. The radiographer received additional instruction on proper set up and operation of a radiography camera. This file is closed. "This event was reported within 24 hours of the event using the NMED reporting system and not to the HOO [NRC Headquarters Operations Officer]. Failure to properly report this event was determined after a review was conducted of all radiography related events reported in the State of Texas from September 1, 2006 to March 31, 2009. This review was initiated in response to the State of Texas Incident Investigation Program (IIP) determining that they had failed to correctly interpret the requirements for reporting this type of event. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. In an effort to prevent a reoccurrence of this, each member of IIP was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Report: I - 8604 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44958 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-10-18 | 2009-04-02 17:39 | 2009-04-08 | AGREEMENT STATE REPORT- INABILITY TO RETRACT RADIOGRAPHY SOURCE The following information was received from the State of Texas via Email: "On October 19, 2006, the agency received a call from the licensee reporting a problem on a radiography camera at a temporary job site. The Radiation Safety Officer (RSO) stated that he had received a call from his radiography trainer stating that the technician had set a radiography camera on a 2" pipe about 2 feet off the ground in preparation to take an exposure. With the source cranked out, the camera fell over and bent the source tube. The trainer tried to crank the source in to the camera and was not successful. The trainer then tried to crank it out, but was still unsuccessful. The trainer then put 14"x17" lead cassettes and two lead shot bags around the source to shield it. The RSO surveyed the area upon his arrival and verified that the barricade boundary was below 2 millirem per hour. Next, he surveyed the camera area, with results of 10 millirem per hour. The RSO noted that the camera was in an area that was surrounded by several pumps and cement blocks, so additional on-site inherent shielding was provided to protect members of the public. The RSO straightened out the source tube with a pair of pliers and retracted the source back into the camera. He estimated that the retrieval process took him approximately five minutes. The trainer and trainee were suspended from any additional radiography operation until their TLDs are read. Both the trainer and trainee received disciplinary reports in their personnel files and all employees were informed of the event. This file is closed. "This event was reported using the NMED reporting system and not to the HOO [NRC Headquarters Operations Officer]. Failure to properly report this event was determined after a review was conducted of all radiography related events reported in the State of Texas from September 1, 2006 to March 31, 2009. The state used 10 CFR 34.101 to report these events, and not 10 CFR 30.50(b)(2), due to conflicting interpretations of NRC rules requiring reporting. "In an effort to prevent a reoccurrence of this, each member of IIP [State of Texas Incident Investigation Program] was required to read Information Notice 2001-03, Incident Reporting Requirements for Radiography Licenses, dated April 6, 2001. In addition, the IIP database has been changed to clarify the reporting requirement and bring it in line with the NRC requirements." Texas Incident Report: I-8369 * * * UPDATE PROVIDED TO KOZAL FROM TUCKER AT 1735 ON 04/08/09 * * * Upon request of the State the reference to 10 CFR 30.50(b)(a) was changed to 10 CFR 30.50(b)(2). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44957 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-04-02 05:43 | 2009-04-02 13:30 | 2009-05-28 | RESIDUAL HEAT REMOVAL INOPERABLE "At 0543 [CDT] on April 2, 2009 at the Monticello Nuclear Generating Plant (MNGP) an Operator made the following discovery during performance of his rounds. The flowrate and pressure of the #14 Residual Heat Removal Service Water (RHRSW) pump motor cooling appeared to be low. Investigation found the flow to be approximately 1 gpm. The cooling water supply flow to the pump motor cooler comes from either RHRSW or Service Water. Based on these indications, Operators declared the RHR Shutdown Cooling inoperable and entered actions for Technical Specifications 3.9.7. Actions have been completed to provide an alternate water supply to the RHRSW pump motor oil cooler. Based on the inoperability of the RHR Shutdown Cooling, this event is reportable under 10 CFR 50.72(b)(3)(v), 'An Event or Condition that could have Prevented the Fulfillment of a Safety Function-Capability to Remove Residual Heat.' The station is performing further investigation into the event and will develop corrective actions based on the results of the investigation." The Licensee notified the NRC Resident Inspector. * * * RETRACTION FROM RANDY SAND TO JOE O'HARA AT 1149 EDT ON 5/28/09 * * * "Monticello is retracting the event reported based on further evaluation. An investigation of the event found test data that demonstrates the RHRSW pump would not have lost its ability to provide cooling water to the shutdown cooling system and therefore no loss of safety function occurred. The test data provides documentation that the thrust bearing oil bath temperature of the RHRSW pump motor would not have exceeded the 200 deg F limit imposed by the motor supplier (GE) at the flow rate found by the operator. The test data indicated with the cooling water at a flow rate of less than 0.9 GPM, at 65 deg F the service water temperature and flow would be sufficient to maintain the motor oil bath temperature below 200 deg F. During the event, the actual event parameters (cooling water flow rate >1 gpm and temperatures< 65 deg F) were less severe than the test parameters and therefore are bounded by the test. "Since there was no impact on the RHRSW system's ability to provide cooling water to the RHR system, the RHR system maintained the ability to provide shutdown cooling and residual heat removal. Therefore the event can be retracted since the condition that was reported in the initial event notification report would not have resulted in the prevention of the fulfillment of a safety function (residual heat removal)." The licensee notified the NRC Resident Inspector and will notify the State of Minnesota. Notified R3DO(Lara) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2009-04-02
44956 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2009-03-23 | 2009-04-02 11:25 | 2009-04-02 | AGREEMENT STATE REPORT - SOURCE RETRACTION CHALLENGES The following information was received from the State of Mississippi via Email: "On 03-23-2009, Licensee's radiographic crew were unable to return the source [Source Model 424-9; SN 51178B; IR-192; 51.3 Ci] to the shielded and safe position while performing NDT radiography (RT) profile inspection at the Chevron Refinery [located in Pascagoula, MS] using a Sentinal Delta 880 radiography camera (D-2549), QSA cranks, and a QSA source tube. The radiography crew increased their barrier, notified the RSO and field operator of the situation. The two technicians maintained the security of their barrier while awaiting arrival of the RSO. "Acuren's RSO notified the site manager, supervisor, assistant RSO, Chevron's RSO, and a Chevron company representative. Once a meeting was held to devise a plan for source retraction the source was retracted within one (1) hour. Dose received [by the RSO and the associate RSO] during the retraction of the source was 90 mR and 25 mR, respectively. The [two technician] radiography crew received a dose of 45 mR and 65 mR, respectively. There were not any non-occupational or over-exposures received. "Licensee concluded that during the course of the source retraction and investigation, it was determined that the source tube had a crimp in it. The positioning of the source tube during radiographic operations could have been the cause of the hang up, but all equipment was shipped to QSA-Global Inspection to determine if equipment failure contributed to the incident. "Licensee stated inspection report from QSA-Global Inspection will be reviewed and sent to DRH [Mississippi Division of Radiological Health]. Licensee has implemented safety meetings and additional training before the crew involved can resume radiographic operations, to cover proper equipment use, inspection, safety notification processes, proper inspection techniques, and equipment limitations. "DRH received written report from licensee on 04-01-2009. DRH called licensee on 04-01-2009 to verify source activity and ask about licensee's investigation. DRH also requested 24 hr telephone notification from the licensee in the future." MS report number - MS 09004. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44955 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-03-16 | 2009-04-02 12:57 | 2009-04-02 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was received from the State of Nebraska via email: "H-3 exits signs were shipped to the ethanol facility in December of 2006. Fagan was the contractor for the ethanol plant. The new Plant Manager did an inventory of the facility in March of 2009 and discovered two missing exit signs. SRB Technologies Model BX-20-BK, Serial # C061306 and C061307, containing 17.51 Ci of H-3. The Manager was not sure if a physical inventory had been done before. He contacted Fagan to see if they had any information concerning the signs. They did not. Nebraska has reported missing H-3 exit signs that Fagan ordered for other ethanol plants in Nebraska. No one is sure if the signs were ever installed in the plant." NE Report Number NE090008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44954 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-03-03 | 2009-04-02 12:44 | 2009-04-02 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received from the State of Nebraska via email: "The owner of the building requested that the exit signs be removed when the store closed. The store had all of the exit signs removed. One sign was not located. They do not know where the sign is or if they ever had the sign. Records indicate that the sign had been shipped 5-6-1998 from SRB Technologies but it is unknown whether it was ever installed at this location. It contained 9.21 Ci of H-3 and Model number was BXU1-GS and serial number 205249" NE Report # 090007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-04-07
44953 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-04-02 | 2009-04-02 11:05 | 2009-04-02 | AGREEMENT STATE REPORT - TWO PATIENTS GIVEN IODINE-123 TREATMENTS ABOVE PRESCRIBED AMOUNT. The following information was received from the State of Florida via facsimile: "During inspection it was found that two patients were given I-123 treatments greater than 20% of prescribed amount. The amount prescribed was 200 microcuries. The amounts given were 318 microcuries [for patient #1] and 314 microcuries [for patient #2]. [The State of Florida] Licensing and Materials Office is investigating this incident." Florida Incident FL09-032. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-04-08
44952 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2009-04-01 18:05 | 2009-04-01 20:51 | 2009-04-01 | UNPLANNED MANUAL REACTOR TRIP "At 1805, due to lowering Condenser Vacuum caused by ingress of algae and seaweed, Unit 2 was manually tripped. Power had been reduced to 94% for the securing of one Circulating Water Pump (2A1). It was then identified that 2A2 Circulating Water Debris filter differential pressure was above administrative limits of 200 inches water. While the station was making preparations to reduce Circulating water flow on the 2A2 Circulating Water Pump, the unit began losing condenser vacuum. Plant was manually tripped at 92% power. All CEA's fully inserted on the trip. Auxiliary Feedwater automatically initiated on Low Steam Generator Level. No PZR PORVS opened. RCS Heat removal is now being maintained with Main Feedwater and Steam Bypass control system. All systems functioned normally, and plant is stabilized at normal operating Temperature and Pressure. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual RPS actuation and 10 CFR 50.72(b)(3)(iv)(B) due to PWR auxiliary feedwater system actuation." There was no impact on Unit 1. The licensee informed the Resident Inspector. | 0 | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-04-01
44951 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2009-04-01 14:30 | 2009-04-01 14:49 | 2009-04-01 | OFFSITE NOTIFICATION TO STATE/LOCAL AGENCIES REGARDING TRITIUM RELEASE ONSITE "On April 1, 2009, the results of an ongoing hydrology study being conducted by Harris Nuclear Plant as part of the voluntary Industry Groundwater Protection Initiative revealed that a pipe leak in the buried Cooling Tower Blowdown line was releasing water containing tritium into surrounding soil. The maximum tritium activity level discovered was 2,120 pCi/L, well below maximum levels allowed by regulation. While the leak rate has not been determined, it appears to be small. The Cooling Tower Blowdown line is used for liquid effluent dilution as part of permitted, routine releases. The permitted liquid effluent release point is the discharge from the Cooling Tower Blowdown line into Harris Lake. This line is leaking upstream of the permitted release point. All leaking water is contained within the site boundary, and based on studies performed by an independent hydrologist, offsite migration is not anticipated. "Immediate corrective actions include voluntary notifications, installation of additional monitoring wells at various locations to determine groundwater flow and to check for the presence of tritium. The water containing low levels of tritium is in a localized area immediately surrounding the Cooling Tower Blowdown line. "The health and safety of the public are not affected by this event, as the activity levels discovered are significantly below maximum levels allowed by regulation. Harris Nuclear Plant is following the guidance contained in NEI 07-07 and has initiated this Event Notification as a result of our voluntary communication to State agencies in accordance with the Groundwater Protection Initiative." The licensee informed the State of North Carolina (Division of Radiation Protection and Department of Water Quality) and the NRC Resident Inspector. The licensee will also inform local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-04-01
44950 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2009-03-16 | 2009-04-01 13:55 | 2009-04-01 | LOSS OF 30 MILLICURIES OF TECHNICIUM-99m "A loss of permitted material by VA Tennessee Valley Healthcare System at Nashville, Tennessee, occurred on March 16, 2009. The loss involved a unit dosage of 30 millicuries of Technicium-99m, in the form of a liquid radiopharmaceutical used for cardiac stress tests. Efforts were undertaken to find the lost dosage but were unsuccessful. "As corrective action, the permittee (VA Tennessee Valley Healthcare System) has performed an in-service on the security of radioactive materials with its nuclear medicine technologists. The in-service emphasized that radioactive materials must be controlled through direct supervision/attention or be locked in a secure area at all times." VA Tennessee Valley Healthcare System Permit No. 41-00104-04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | AR | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-04-01
44949 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-03-31 | 2009-04-01 08:48 | 2009-04-01 | AGREEMENT STATE REPORT - LOST I-125 SEED The following information was received from the State of Florida via fax: "Cardinal Health working under Mayo Clinic license lost one I-125 seed. Sterilization room and adjoining spaces and personnel were surveyed. It is speculated that the source entered the internal plumbing of the sterilizer. The pipes are of sufficient thickness to prevent external detection. It is surmised by Mayo RSO that Cardinal Health personnel did not follow procedure. RSO estimates that remaining activity as of 31 Mar 2009 is 150 micro Ci's [original activity 300 micro Ci's], with no increased exposure to Cardinal Health staff. Mayo Clinic will work with Cardinal Health staff to modify procedure to ensure source cannot escape vial or tray during sterilization. In addition, retraining will be conducted with all Cardinal health staff involved. Any further investigation is referred to Materials and Licensing. This office will take no further action on this incident." The Florida Incident Number for this event is FL09-030. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-04-06
44948 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-03-31 18:50 | 2009-04-01 00:10 | 2009-04-01 | VALID DIESEL START SIGNAL RECEIVED DURING MAINTENANCE TESTING OF DIESEL "A valid actuation of the D23 Emergency Diesel Generator bus undervoltage minimum actuation logic occurred following manual operator action to mitigate a bus overvoltage condition during emergency diesel generator post maintenance testing . Due to the output breaker being opened, the D23 EDG experienced a undervoltage start signal. EDG undervoltage actuation instrumentation actuated, however, the EDG was in PTL (Pull-to-Lock) EDG shutdown. The event was caused by a failure of the emergency diesel generator voltage regulator most likely due to an intermittent failure of the #1 rectifier bank." The licensee stated that the D23 EDG was powering an isolated safety related bus for a post-maintenance test when the overvoltage condition occurred. The operator opened the EDG output breaker and placed the EDG in PTL. With the bus de-energized, a valid start signal was sent to EDG D23. However, EDG D23 did not actually start because it was in PTL. No safety related equipment was lost when the bus was de-energized because the bus had been unloaded prior to the test. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-04-01
44947 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-03-31 12:00 | 2009-03-31 16:43 | 2009-03-31 | EMERGENCY SIREN ACTIVATED FOR REASONS UNKNOWN "On 3/31/2009 at 1323 CDT Prairie Island Nuclear Generating Plant was notified by the site's siren contractor (NELCOM) that Pierce County siren P-20 had falsely activated at around 1200 CDT. Pierce County notified NELCOM of the siren activation after receiving several calls from the public. No press release is planned for this event. "Siren P-20 (1 of 52 sirens) has been removed from service and backup route alerting will be used in the event siren activation is required. The cause of the false activation is being investigated and will be repaired. "The NRC Resident Inspector has been notified." At 1544 CDT siren P-20 was repaired and returned to service. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-31
44946 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-03-31 08:30 | 2009-03-31 14:41 | 2009-03-31 | AGREEMENT STATE REPORT - CONTAMINATION FOUND ON NUCLEAR MEDICINE PACKAGING The following was received from the state via e-mail: "N.C. Radiation Protection Section was notified on March 31, 2009 by the hospital about a nuclear medicine package received from a nuclear pharmacy in excess of the loose contamination limits. "The swipes performed on the package read 2890 dpm vs the limit of 2200 dpm. The package was placed in hot storage and will be stored for decay. "Licensee notified the carrier and the pharmacy." NC Event Report ID Number is NC-09-20. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-04-03
44945 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-03-30 18:43 | 2009-03-30 23:04 | 2009-03-31 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT OF SERVICE "On March 30, 2009, at approximately 1843 hours EDT, the control room reported a loss of power to non-safety 480 volt busses F1C and F1D. Initial investigation revealed an instantaneous ground over-current (50G) relay had actuated. This relay actuation resulted in the supply breaker tripping and all associated loads being de-energized. This resulted in a loss of 120 VAC non-essential electrical power to a portion of the Emergency Response Data System (ERDS). "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the status Board Ring Down circuit with back-up by the Private Branch Exchange, Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The ability to open and maintain an open line using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii) as a condition that results in a major loss of emergency offsite communications capability. A follow-up notification will be made when the equipment is restored. "The NRC Resident Inspector has been notified." The unit is currently defueled. * * * UPDATE FROM TOM STEC TO JOE O'HARA AT 1600 EDT ON 3/31/09 * * * Last evening, power was restored to ERDS following maintenance. ERDS is capable of performing its intended function. Notified R3DO(Orth) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-03-30
44944 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-03-30 02:55 | 2009-03-30 09:35 | 2009-03-30 | NOTIFICATION TO OTHER GOVERNMENT AGENCY OF ON-SITE FATAL HEART ATTACK A licensee employee, working in the Outage Command Center (office environment), which is located inside the Protected Area, had symptoms of a heart attack. On-site emergency personnel responded and the individual was transported off-site to Piedmont Medical Center. Piedmont Medical Center notified the licensee at 0445 hours that the heart attack was fatal. The licensee notified OSHA. The licensee does not plan to make a media or press release. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1453 EDT ON 03/30/09 FROM STEVE CHRISTOPHER TO S. SANDIN * * * "This notification is being made to supplement today's 0935 [EDT] notification. The offsite notification to OSHA occurred at 0847 [EDT], placing the 0935 [EDT] notification to the NRC within the 4 hours required by 10 CFR 50.72 (b)(2)." The licensee informed state/local agencies and the NRC Resident Inspector. Notified R2DO (Vias). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-30
44943 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-03-29 18:25 | 2009-03-29 20:18 | 2009-03-29 | POTENTIALLY CONTAMINATED PERSON SENT OFFSITE FOR HOSPITAL EVALUATION "A worker performing U2 outage activities was exhibiting signs of heat stress and dizziness when exiting the U2 drywell access control point. Offsite medical assistance was requested and the worker was transported to the Pottstown Memorial Medical Facility as a potentially contaminated person. The ambulance left the site at 1825 hours 3-29-09. At 1845 hours while at the Pottstown Memorial Medical Facility it was determined that the worker was NOT contaminated. This report being submitted via the requirements of 10CFR50.72 (b)(3)(xii)." The individual was performing routine valve operations and was a plant employee. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2009-03-29
44942 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-03-28 01:46 | 2009-03-28 03:45 | 2009-03-28 | REACTOR SCRAM DUE TO MODE SWITCH BEING PLACED IN SHUTDOWN FOLLOWING HIGH VIBRATION ON MAIN TURBINE #1 BEARING "At 0146 EDT 3/28/09, the reactor mode switch was taken to shutdown in response to high vibration levels on the Main Turbine #1 bearing. Reactor power was at its reduced level in preparation for entry into Refueling Outage #13 which was scheduled to begin at 0300 EDT. All control rods fully inserted into the core. The lowest reactor vessel water level reached was 162 inches. HPCI & RCIC did not initiate. No safety relief valves (SRV) actuated. Reactor water level is being controlled in the normal band using the Control Rod Drive (CRD) system. All isolations and actuations for reactor vessel water level 3 occurred. "The cause of the high main turbine vibrations is currently under investigation. There was no maintenance or testing in progress that would explain the high turbine vibration levels. At the time of the scram all ECCS systems and Emergency Diesel Generators were operable. This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B), any event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-03-28
44941 | 0 | MEDICAL PHYSICS CONSULTANTS |  |  |  |  | 2009-03-27 | 2009-03-27 12:30 | 2009-03-27 | MISSED CONFIRMATIONS LED TO PATIENT RECEIVING A HIGHER DOSE A patient was prescribed a 12 millicurie dose of I-131 for treatment. When the hospital requested the dose from the pharmacy, a 15 millicurie dose was mistakenly requested. The dose requested was not confirmed against the prescribed dose. When the patient came in for treatment, the technologist preparing the dose measured a 15.5 millicurie dose but did not realize or confirm that this dose differed from the 12 millicurie prescribed dose. The 15.5 millicurie dose was administered instead of a 12 millicurie dose resulting in a dose to the patient of more than a 20% difference from the prescribed dose. The licensee will inform the patient of the higher dose. To prevent this same type of incident from happening in the future the hospital plans on changing current practice to confirm two different times that the prescribed dose and the requested dose from the pharmacy are the same. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-03-31
44940 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2009-03-02 11:55 | 2009-03-27 08:40 | 2009-03-27 | INVALID PRIMARY CONTAINMENT ISOLATION SIGNAL DUE TO MAINTENANCE ERROR "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Unit 3 Primary Containment Isolation System (PCIS). On 3/2/09, at approximately 1155 hours, Unit 3 experienced an invalid PCIS partial isolation. Associated with the momentary shorting of a terminal lead during maintenance, a fuse was blown and power was lost to nine Primary Containment Isolation Valves (PCIVs). This resulted in two of the PCIVs re-positioning to the closed position. The re-positioned PCIVs were the AO-3-07B-3509 (Inner Drywell Exhaust Valve) and the AO-3-16-5235 (Instrument Nitrogen System Suction Valve). Closure of these valves affected the Containment Atmospheric Control (CAC), Containment Atmospheric Dilution (CAD) and Containment Instrument Nitrogen systems. Closure of these valves was the expected response for loss of power to this portion of the PCIS control circuitry. The fuse was replaced and the valves were restored to an operable condition by 1235 hours on 3/2/09. "The invalid PCIS isolation was a result of the momentary shorting of an energized terminal lead associated with preventive maintenance to replace a pressure switch associated with PCIV AO-3-07B-3519 (Nitrogen Supply Purge Valve). "This issue has been entered into the site Corrective Action Program (CR 887441) for evaluation and implementation of further corrective actions. The NRC resident has been informed of this notification." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-03-27
44939 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2009-03-24 13:30 | 2009-03-26 21:16 | 2009-03-26 | BUILDING CONTAMINATED DURING MAINTENANCE The licensee was troubleshooting a green salt filter leg when approximately 100 pounds of green salt was released from a secondary dust collector drop leg pipe. Four personnel were in the area wearing respiratory protection and anti-contamination clothing. The personnel left the area and access was restricted until 1030 on 3/26/2009. The green salt contaminated four floors of the building and the four personnel. Personnel contamination was removed with removal of the anti contamination clothing and subsequent showers. Most of the floor contamination was cleaned within four hours and the remainder was completed on 3/26/2009. No contamination was released outside the building. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2009-03-26
44938 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-03-26 12:26 | 2009-03-26 19:43 | 2009-09-09 | NON-FUNCTIONAL STEAM EXCLUSION BARRIER This event was additionally reported under 10 CFR 50.72(b)(3)(v)(D), 'Mitigate the Consequences of an Accident.' "On 03/26/2009 at 1226 CDT, an engineering analysis determined that a steam exclusion door would not provide adequate steam exclusion protection. A metal plate, that had been installed over the door's glass window, would fail under the steam overpressure postulated during a high energy line break. The metal plate was replaced with one of a stronger design. Permanent repairs were completed on the door at 1549 on 03/26/2009. While the original plate was installed, the barrier was non-functional. In accordance with TRM 3.0.9, Section A.1 all equipment supported by that steam exclusion barrier was immediately declared inoperable. This zone includes both trains of ECCS and support equipment (i.e., SI, RHR, ICS, CCW, etc.). TS 3.0.c was entered and exited during the time the door issue was identified and repaired. "All 3 trains of Auxiliary Feedwater were declared inoperable due to AFW low suction pressure trip channels were declared inoperable per TS 3.4.b.5. Power was reduced to less than 1673 MWt per TS 3.4.b.3. All mode changes were suspended per TS 3.4.b.2. "Therefore, this is reportable under 10 CFR 50.72 (b)(3)(v), 'Any event or condition that at the time of discovery could have prevented the fulfillment of a safety function,' and under 10 CFR 50.72(b)(3)(ii)(B) 'any event or condition that results in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety.'" Containment Fan Coil Unit A was not operational during this event. "The licensee notified the NRC Resident Inspector." * * * RETRACTION FROM JACK GADZALA TO PETE SNYDER ON 9/9/09 AT 1718 * * * "On March 26, 2009 EN # 44938 provided notification that both trains of ESF equipment (e.g. SI, RHR, ICS, CCW, etc.) were inoperable based on an engineering analysis, which determined that a steam exclusion door in the auxiliary building would not provide adequate steam exclusion protection. "Subsequent physical pressure testing of equivalent doors and engineering evaluation of the test results determined that the door remained capable of fulfilling its steam exclusion function. A series of pressure tests demonstrated that the door (including a metal plate that had been installed over the door's glass window) would withstand the steam overpressure postulated during a high energy line break. "Therefore, the door remained functional and the supported ESF equipment in the auxiliary building remain operable. Consequently, this condition did not meet the reportability criteria in 10 CFR 50.72. "As a result, the notification made on 3/26/09 is hereby retracted. "This condition was also reported in Licensee Event Report (LER) 2009-005-00 on May 21, 2009." The licensee is planning on retracting this LER. | 94 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2009-03-26
44937 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2009-03-27 | 2009-03-26 18:52 | 2009-04-08 | TROUBLESHOOTING EMERGENCY OFFSITE FACILITY COMMUNICATIONS "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) as an event that will result in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g. significant portion of control room indication, Emergency Notification System or offsite notification system.) "At approximately 0000 on 3/27/09, all five of the T-1 data lines to the Emergency Offsite Facility (EOF) will be taken out of service to troubleshoot and repair malfunctioning phone company equipment. Multiple short duration outages will occur until the malfunction can be located and repaired. This outage will cause a loss of Plant Management Information System printer capability, Safety Parameter Display System (SPDS) capability, FTS 2001 system, Alternate Intercom system, Low Band base radio (the primary Downwind Survey team radio), State Notification Telephone System, Dose Assessment and some external phone lines at the EOF. This loss of capability affects only the off-site EOF. All other emergency communications from the site to the NRC are not affected. "Compensatory measures being put into effect include SPDS information relayed via telephone from the Technical Support Center, dose assessment and offsite notifications and reports via alternate means, or relocate the on-call Emergency Director to the Control Room and make notifications to offsite agencies via the Control Room Communicator. CNS is in contact with communications personnel to restore the T-1 lines as quickly as possible in the event of a declared emergency. "Region IV and the NRC Resident Inspector were notified of the planned loss of the T-1 lines. CNS will notify the NRC when all EOF equipment affected by the T-1 lines have been satisfactorily tested and verified to be operational." * * * UPDATE ON 3/27/09 AT 1405 FROM STEVE WHEELER TO MARK ABRAMOVITZ * * * "This notification is an update to EN#44937 regarding the planned troubleshooting of Emergency Off Site Facility (EOF) communications equipment. Discussion with the NPPD telecommunications vendor have identified that the planned troubleshooting and repair of Cooper's EOF communications equipment was completed non-intrusively. There was no actual interruption of the EOF communications equipment. Testing by the vendor, NPPD Telecommunications Department personnel and NPPD Emergency Preparedness Department personnel has been completed and all EOF communications equipment has been verified to be fully functional. The NRC Senior Resident Inspector and the State and Local Agencies will be notified that the CNS EOF communications equipment is fully functional." Notified the R4DO (O'Keefe). * * * UPDATE AT 1739 EDT ON 3/30/09 FROM ED MCCUTCHEN TO JOE O'HARA * * * "This notification is a second follow up to Event Notification EN# 44937 of 3/26/09 at 1852 EDT which reported the planned troubleshooting of Emergency Off Site Facility (EOF) communications equipment. The first follow up reported that the planned troubleshooting was completed non-intrusively and that no actual interruption of EOF capability occurred. "Subsequently the telecommunication provider has advised that further troubleshooting is required. Therefore, at approximately 2300 on 3/30/09, all five T-1 data lines to the EOF will be taken out of service to troubleshoot and repair malfunctioning phone company equipment. Multiple short duration outages will occur until the malfunction can be located and repaired. This outage will cause a loss of Plant Management Information System printer capability, Safety Parameter Display System (SPDS) capability, FTS 2001 system, Alternate Intercom system, Low Band base radio (the primary Downwind Survey team radio), State Notification Telephone System, Dose Assessment and some external phone lines at the EOF. This loss of capability affects only the off-site EOF. All other emergency communications from the site to the NRC are not affected. "Compensatory measures being put into effect include SPDS information relayed via telephone from the Technical Support Center, dose assessment and offsite notifications and reports via alternate means, or relocate the on-call Emergency Director to the Control Room and make notifications to offsite agencies via the Control Room Communicator. CNS is in contact with communications personnel to restore the T-1 lines as quickly as possible in the event of a declared emergency. "Region IV and the NRC Resident Inspector were notified of the planned loss of the T-1 lines. CNS will notify the NRC when all EOF equipment affected by the T-1 lines have been satisfactorily tested and verified to be operational." Notified R4DO(Deese). * * * UPDATE AT 0840 EDT ON 3/31/09 FROM ROY GILES TO DONALD NORWOOD * * * "Third follow-up of event notification EN #44937. "Discussions with the NPPD telecommunications vendor have identified that troubleshooting and repairs to the EOF communications equipment are complete [as of 0639 CDT]. Post-work testing by Telecommunications Department personnel and NPPD Emergency Preparedness Department personnel has been completed and all EOF communications equipment has been verified to be fully functional. The NRC Senior Resident Inspector will be informed." Notified R4DO (Deese). * * * UPDATE FROM ED MCCUTCHEN TO JOE O'HARA AT 1425 EDT ON 4/7/09 * * * "This notification is a fourth follow up to Event Notification EN# 44937 of 3/26/09 at 1852 EDT which reported the planned troubleshooting of Emergency Off Site Facility (EOF) communications equipment. The third follow up reported that subsequent repairs were completed and that EOF full communication capability had been restored. "Since then, the telecommunication provider has advised that more troubleshooting is required. Therefore, at approximately 2300 on 4/7/09, all five T-1 data lines to the EOF will again be taken out of service to troubleshoot and repair malfunctioning phone company equipment. Multiple short duration outages will occur for approximately 7 hours until the malfunction can be located and repaired. This outage will cause a loss of Plant Management Information System printer capability, Safety Parameter Display System (SPDS) capability, FTS 2001 system, Alternate Intercom system, Low Band base radio (the primary Downwind Survey team radio), State Notification Telephone System, Dose Assessment and some external phone lines at the EOF. This loss of capability affects only the off-site EOF. All other emergency communications from the site to the NRC are not affected. "Compensatory measures being put into effect include SPDS information relayed via telephone from the Technical Support Center, dose Assessment and offsite notifications and reports via alternate means, or relocate the on-call Emergency Director to the Control Room and make notifications to offsite agencies via the Control Room Communicator. CNS is in contact with communications personnel to restore the T-1 lines as quickly as possible in the event of a declared emergency. "Region IV and the NRC Resident Inspector were notified of the planned loss of the T-1 lines. CNS will notify the NRC when all EOF equipment affected by the T-1 lines have been satisfactorily tested and verified to be operational." Notified R4DO(Spitzberg). * * * UPDATE FROM CLYDE EDGINGTON TO JOE O'HARA AT 1443 EDT ON 4/8/09 * * * "Discussions with the NPPD telecommunications vendor have identified that troubleshooting and repairs to the EOF communications equipment were not necessary and no work was performed. Post-work testing by Telecommunications Department personnel and NPPD Emergency Preparedness Department personnel has been completed and all EOF communications equipment has been verified to be fully functional. The NRC Senior Resident Inspector has been informed. Notified R4DO(B. Spitzberg) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-03-26
44936 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-03-26 | 2009-03-26 14:58 | 2009-03-26 | TROXLER MOISTURE DENSITY GAUGE DAMAGED AT CONSTRUCTION SITE The following information was received from the State of Louisiana by Fax: "On March 21, 2009, a soil moisture/density gauge operated by the licensee under radioactive material (RAM) reciprocity was struck by the axle of a moving pick-up truck while the source was fully extended into the soil and while soil measurements were being performed. During an initial phone interview with the gauge operator, he stated that the gauge plunger handle had been damaged. The operator stated that the source rod might have been bent during this incident. "The gauge operator was able to retract the source into the shielded position. Radiation readings were taken through the entire process. The gauge operator stated that he succeeded in padlocking the source rod plunger handle with the source rod in the fully upright position even though the plunger handle had been partially damaged. The operator then secured the gauge in its transportation case and performed a survey of the transportation case. "The operator stated that he got a highest reading of 1 mR/hr at the case surface on the side next to the base of the gauge. The gauge case was resurveyed before placing the gauge back into storage in the licensee's source vault. A leak test was performed but the results are not available at this time. "The gauge is a Troxler Model 3440, serial #31096, containing 8 mCi of Cs-137, serial # 750-5735 and a 40 mCi source of AmBe241,serial #47À3180. "Additional information will be forwarded once it is received. An inspector was sent to the temporary jobsite on March 25, 2009 to verify this information." Louisiana Event Report ID: LA090010. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-03-31
44935 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-03-26 04:52 | 2009-03-26 08:29 | 2009-03-26 | AUTOMATIC REACTOR TRIP AND AUX FEED WATER START DUE TO LOSS OF AN OFF SITE POWER SOURCE "At approximately 0452 on 03/26/09, Sequoyah Unit 2 received an Automatic Reactor trip on Reactor Coolant Pump Busses Undervoltage. A loss of Common Service Station Transformer C caused a loss of power to the 2B and 2D Unit Boards. The 2B and 2D unit boards are the 6.9Kv electrical feeds to the 2-2 and 2-4 RCPs, respectively. RCPs 2-1 and 2-3 are running. "ESF functions initiated as designed including Aux Feed Water auto-start, automatic Feedwater isolation, and auto-start of all four EDGs. The 2A Shutdown Board is being powered from the 2A EDG. "The plant is currently being maintained in Mode 3 at approximately 547 degrees F /2235 PSIG. Decay heat is being removed by the auxiliary feedwater system and Steam Generator Atmospheric Relief valves. "The cause of the loss of Common Service Station Transformer C is not known at this time and investigation is ongoing." All rods inserted as expected. No safety related equipment is out of service. Unit 2 has no known Steam Generator Tube leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-03-26
44934 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-03-26 04:52 | 2009-03-26 08:29 | 2009-03-26 | AUTOMATIC REACTOR TRIP AND AUX FEED WATER START DUE TO LOSS OF AN OFF SITE POWER SOURCE "At approximately 0452 on 03/26/09, Sequoyah Unit 1 received an Automatic Reactor trip on Reactor Coolant Pump Busses Undervoltage. A loss of Common Service Station Transformer C caused a loss of power to the 1B and 1D Unit Boards. The 1B and 1D unit boards are the 6.9Kv electrical feeds to the 1-2 and 1-4 RCPs, respectively. RCPs 1-1 and 1-3 are running. "ESF functions initiated as designed including Aux Feed Water auto-start, automatic Feedwater isolation, and auto-start of all four EDGs. The 1A Shutdown Board is being powered from the 1A EDG. "The plant is currently being maintained in Mode 3 at approximately 547 degrees F /2235 PSIG. Decay heat is being removed by the auxiliary feedwater system and Steam Generator Atmospheric Relief valves. "The cause of the loss of Common Service Station Transformer C is not known at this time and investigation is ongoing." All rods inserted as expected. No safety related equipment is out of service. Unit 1 has no known Steam Generator Tube leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-03-26
44933 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-03-25 09:40 | 2009-03-25 12:05 | 2009-04-21 | AGREEMENT STATE REPORT - POSSIBLE OVEREXPOSURE OF EMPLOYEE "On March 25, 2009, at 0940, the State of Texas was notified by a licensee that they had received a report from their dosimetry processor indicating that one of their employees had received greater than 1000 rad exposure for the month of February, 2009. The exposure record provided did not indicate whether the exposure was static or dynamic. The Radiation Safety Officer (RSO), who started this position in the first part of March, 2009, contacted the radiographer. The radiographer stated that she had not performed any operations with a radiography camera because she had hurt her knee. The radiographer stated that she had worked nine jobs, and all her work was done in the dark room. The RSO has made arrangements for the radiographer to have blood work done today, 3/25/09. The RSO stated that she had two other individuals who had received higher than normal readings but had not exceeded any limits. These individuals were reassigned to duties that will limit their exposure. "An Agency (state) investigator contacted the radiographer and asked her when in the month of February she had started wearing her badge. She stated that she began wearing the badge in the middle of February. She stated that she picked it up from a mail box at the company's office. She stated that she carried the badge with her in [her] lunch box when she was not wearing it and that no one else would have had access to the badge from this point on. "She stated that no source disconnects had occurred at any of the work sites she was at in the month of February. She stated that she does not know how her badge could have received that much exposure, but she is sure she had not received that much exposure. She stated that she felt fine. Additional information will follow as it is received." Texas Incident Number: I-8622 * * * UPDATE FROM ART TUCKER TO PETE SNYDER AT 1218 ON 3/27/09 * * * "The state received a fax which contained a copy of the blood work done on 3/26/09 for the individual involved from the licensee. Also included in the fax was a copy of blood work that was done on the individual on 2/25/09 prior to a medical procedure. Both samples returned very similar results and were considered normal by her physician." Notified R4DO (O'Keefe) and FSME (McIntosh). * * * UPDATE FROM ART TUCKER VIA E-MAIL TO KARL DIEDERICH AT 1239 ON 4/21/09 * * * "The licensee has removed the exposure recorded on the individual's dosimeter and assigned a dose of 416 millirem for the exposure period. The licensee provided a copy of the dosimetry processor's report indicating the change in exposure." Notified R4DO (Gaddy) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-03-30
44932 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-09-15 18:35 | 2009-03-24 13:13 | 2009-04-15 | ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA An outage worker who should have been denied plant access was granted access into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM GENE DORMAN TO JOHN KNOKE AT 1732 EDT ON 04/01/09 * * * An additional case similar to the first case was found by licensee. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R1DO (Mel Gray), and 73.71 GROUP. * * * UPDATE FROM JOSEPH PECHACEK TO JOHN KNOKE AT 1551 EDT ON 04/15/09 * * * Licensee is retracting the case identified in the 4/1/09 update to this Event Notification, because it has been determined that the background check was adequate, the individual was appropriately authorized access, and no update of the original notification was required. Licensee has notified the NRC Resident Inspector. Notified R1DO (Art Burritt) and 73.71 GROUP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-03-24
44931 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2009-03-23 17:00 | 2009-03-23 23:10 | 2009-03-23 | UNANALYZED CONDITION FOR POSTULATED MISSILE HAZARD THAT COULD DISABLE BOTH TRAINS OF COMPONENT COOLING "At 1700 on 3/23/09 Prairie Island staff declared both trains of Unit 1 Component Cooling (CC) system inoperable due to discovery that a postulated missile hazard in the Fuel Handling Area could fail a CC line to 122 Spent Fuel Pool Heat Exchanger (SFP HX), affecting both trains of CC. This condition represented an unanalyzed condition reportable under 10 CFR 50.72(b)(3)(ii)(B) since the event might represent a significant degradation of plant safety. The inoperability of Unit 1 CC caused entry into Technical Specification LCO 3.0.3. The CC line in question does not have automatic closure and the resulting loss of CC inventory would eventually affect both trains of CC. This condition represents a loss of safety function for safe shutdown capability and is reportable per 10 CFR 50.72 (b)(3)(v)(A). "122 SFP HX was last modified by design change 99SF02 to allow for full redundant capacity of the 121 SFP HX. While seismic was addressed in the design change, tornado protection was not. "The CC line to the 122 SFP HX was isolated at 1759 on 3/23/09 returning Unit 1 CC to operable status. Unit 1 remained at 100% power. "121 SFP HX is currently in service and is in a location that meets the missile protection requirements. "The condition was discovered during a tornado protection vulnerability walk-down. A similar line on Unit 2 was already isolated. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2009-03-23
44930 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-03-22 | 2009-03-23 16:28 | 2009-06-18 | AGREEMENT STATE REPORT - ABNORMAL EXCESS LOSS OF WATER INTO DRAIN SYSTEM FROM DE-IONIZATION SYSTEM The following information was provided from the State of Nebraska via e-mail: "The Nebraska DHHS [Department of Health and Human Services] was notified on March 23, 2009 at 0825 by the Radiation Safety Officer (RSO) for Becton Dickinson in Broken Bow, Nebraska. On March 22, 2009 in the evening, the RSO received a call from one of the pool irradiator operators. During the operator's weekly sterilizer checks, he noticed that the pool water make-up meter indicated the pool had used 1,103 gal for the week. Normal usage is about 120 gal/week. Investigation on the next morning revealed a bleed valve on the D.I. [de-ionizing] water system was cracked open, allowing D.I. water to flow to drain. This was not readily apparent because the hose goes down into the drain. The RSO closed the valve, recorded the current meter reading, noting the meter had used about 100 gal overnight. The RSO intends to check the reading Tuesday morning to see if closing the valve solved the problem. This water leaking does not affect the level of the pool water. "Nebraska DHHS has notified Randy Erickson, NRC, Region IV "Event report ID No. NMED NE090006" * * * UPDATED FROM TRUDY HILL (VIA EMAIL) TO HOWIE CROUCH @ 0924 EDT ON 6/18/09 * * * "The next [meter] reading on 3/29 was also elevated at 336 gallons. The next readings were 201 gallons on 4/5, 244 gallons on 4/12 and 231 gallons on 4/19. Levels had dropped, but were still slightly higher than expected. The licensee's maintenance technicians discovered that the oil pressure safety switch in the compressor unit of the water chiller system was tripping off and shutting down the unit. The safety switch was replaced on May 1. "In addition, the licensee installed a beacon and an audible alarm to alert an operator when the chiller oil pressure safety switch tripped out. This prevents the chiller from being down for any length of time without anyone's knowledge. The safety switch continued to trip out occasionally but was reset immediately so the water use returned to normal readings of 110 gallons on 5/3, 60 gallons on 5/10 and 63 gallons on 5/17. The licensee continued the investigation and parts were obtained to repair the compressor unit. On 5/18, the licensee replaced the oil pump, pressure sensor and changed the oil in the compressor. The unit ran for the next 24 hours without any further issues. The licensee said they would continue to monitor the situation closely, but they believe the issue has been resolved." Notified R4DO (Cain) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-03-26
44929 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-03-23 07:31 | 2009-03-23 10:56 | 2009-05-18 | NON-FUNCTIONAL STEAM EXCLUSION BARRIER "On 3/23/09 at 0731 an I&C Supervisor transiting though a steam exclusion double door found the door sweep misaligned causing one side to catch and stick open. This prevented the door from closing automatically until the sweep was readjusted back to its original position. The door was then closed and monitored while permanent repairs took place. While the door was open and could not close automatically, the barrier was Non-Functional for Steam Exclusion. In accordance with TRM 3.0.9 Section A.1 all equipment supported by that steam exclusion barrier was immediately declared inoperable. This zone includes both trains of ECCS and support equipment (i.e., SI, RFIR, ICS, CCW, etc ). TS 3.0.c was entered and exited during the time the door could have stuck open (6 minutes) with both trains of ECCS inoperable. Permanent repairs were completed on the door at 0809 on 3/23/09. "Therefore, this is reportable under 10 CFR 50.72 (b)(3)(v), 'Any event or condition that at the time of discovery could have prevented the fulfillment of a safety function, and under 10 CFR 50.72(b)(3)(ii)(B) 'any event or condition that results in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety.' The licensee is also reporting this event under 10 CFR 50.72 (b)(3)(v)(D), Accident Mitigation. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM STEVE TAYLOR TO JOE O'HARA AT 1443 ON 05/18/09 * * * "05/18/2009 - Retraction of EN # 44929. NonÀFunctional Steam Exclusion Barrier. "EN # 44929 provided notification that both trains of ESF equipment (e.g. SI, RHR, CCW, etc ) were inoperable due to degradation of a steam exclusion boundary door in the auxiliary building on March 23, 2009. "Subsequent engineering evaluation determined that the degraded door remained capable of fulfilling its steam exclusion function during the brief (eight minute) period when it was degraded. The door had become degraded while being used for routine transit when the lower door sweep became misaligned, thereby preventing the door from completely closing. However, an engineering evaluation determined that the resulting gap was sufficiently small such that the total allowed leak path criteria were not exceeded. Additionally, the door swing was in the direction of postulated steam flow, such that the door would have been held in the closed direction by any steam overpressure postulated under accident conditions. "Therefore, the door remained functional and the supported ESF equipment in the auxiliary building remained operable. Consequently, this condition did not meet the reportability criteria in 10 CFR 50.72. "As a result, the notification made on 03/23/2009 is hereby retracted." The licensee notified the NRC Resident Inspector. Notified the R3DO(R. Skokowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2009-03-23
44928 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2009-03-23 07:30 | 2009-03-23 10:51 | 2009-03-23 | DEGRADED ITEM REQUIRED FOR SAFETY IN THE PELLETING AREA "Reason for Notification "Notification is being made based on following criteria: '10 CFR 70 Appendix A (b)(2) Loss or degradation of IROFS [Items Relied On For Safety] that result in failure to meet the performance requirements of 10CFR70.61' "WEC CFFF [Westinghouse Electric Company, Commercial Fuel Fabrication Facility) has identified a degraded IROFS condition exists in the Pelleting Area. Safety Bulletin No: M-01-09-01, issued by GE FANUC has been evaluated by CFFF Engineering and this evaluation has identified a degraded IROFS condition exists in the Pelleting Area. GE PLC of the type discussed in the Safety Bulletin (IC695CPU310) is used in Pelleting Area Furnaces 1B, 2B, and 4C. This common mode failure is applicable to IROFS PELSINT-903, PELSINT-904, & PELSINT-905. "These IROFS are preventive controls for a Hydrogen Deflagration Event in the sintering furnaces. While several potential initiating sequences can lead to this event, the only scenario where the performance requirements are not met due to this degraded condition is if the furnace is above the auto ignition temperature for hydrogen and the PLC CPU fails as the furnace is cooling, then the hydrogen shut-off valve could remain open with a potential to result in an explosive atmosphere in the furnace. This event is evaluated in the CFFF ISA-08 Summary for the Pelleting Area. "See Reason for Notification. Impacted Pelleting Area Furnaces are 1B, 2B and 4C. Furnace 1B is currently at normal operating temperature (above auto ignition temperature) and in operation with approximately 550 kg's of Uranium. The other two Furnaces, 2B and 4C are currently at normal temperature (above auto ignition temperature) with no uranium present in either furnace." The licensee will contact NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2009-03-23
44927 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-03-22 13:34 | 2009-03-22 20:02 | 2009-03-22 | UNIT 1 STEAM GENERATOR FOUND IN AN UNANALYZED CONDITION RELATED TO GAPS ON SEISMIC WASHER PLATES "At 1334 on March 22, 2009, while Unit 1 was in Mode 3, replacement steam generator (RSG) 1-3 was conservatively determined to be in an unanalyzed condition in that seismic washer plates were found to have nonconforming gaps on two of the four steam generator support columns. A plant walk down discovered that the two washer plates were not seated in the column adapter due to an interfering weld on the interior recess of the column adapter. Because of this condition, Technical Specification 3.0.3 was entered for Unit 1. "At 1536 on March 22, 2009, a shim was installed between the washer plate and the column adapter at each of the two non-conforming locations on RSG 1-3 of sufficient thickness to clear the weld metal interfering with washers. This action brought the support columns for RSG 1-3, support foot joints into compliance with the full design capacity. Technical Specification 3.0.3 was exited for Unit 1 at that time. "This issue was discussed with US NRC DCPP Senior Resident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-03-22
44926 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2009-03-21 12:07 | 2009-03-21 18:15 | 2009-05-06 | HPCI DECLARED INOPERABLE FOLLOWING FAILURE OF VALVE TO FULLY OPEN DURING SURVEILLANCE TEST "The Peach Bottom Atomic Power Station Unit 3 High Pressure Coolant Injection System (HPCI) was declared inoperable at 12:07 on March 21. 2009 when HPCI Outboard Suppression Pool Suction Valve, MO-3-23-057, failed to fully open during testing. At this time the cause of the failure of MO-3-23-057 to stroke fully open is unknown. Investigation is in progress." This places Unit 3 in two (2) Tech Spec LCO Action Statements; 3.5.1 (14 day restoration with HPCI inop) and 3.6.1.3, Condition A (4 hour immediate action with verification every 31 days of Primary Containment Isolation Valves). Actions required by both have been completed. The failure occurred during performance of the quarterly surveillance test. The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM DAVE FOSS TO HOWIE CROUCH @ 0824 ON 5/6/09 * * * "The purpose of this notification is to retract a previous report made on 3/21/09 at 1815 hours (EN# 44926). Notification of the event to the NRC was initially made as a result of declaring the Unit 3 High Pressure Coolant Injection (HPCI) system inoperable when unexpected conditions were found during performance of routine surveillance testing of HPCI. Specifically, it was noted that a motor-operated Suppression Pool suction valve for HPCI (MO-57) did not complete its stroke in the open direction during testing. The HPCI system was not operating at the time of the discovery. "Since the initial report, Engineering has determined that HPCI was capable of performing its safety function. The evaluation determined that the MO-57 valve was capable of opening to a position sufficient to ensure that the HPCI safety function was met for design basis conditions. Additionally, since the torque switch is bypassed during actual design events, full motor torque would have been available which was sufficient to allow the valve to reach its full open position. It has also been determined that the valve was capable of closing on a signal to close automatically. "During resolution of the HPCI MO-57 concern, the suction source from the Suppression Pool was isolated in accordance with Technical Specifications since MO-57 is listed as a Primary Containment Isolation Valve. This action was performed in accordance with station procedures and is considered planned maintenance. "The NRC resident has been informed of the retraction." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-03-21
44925 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-03-21 04:06 | 2009-03-21 11:50 | 2009-03-21 | UNEXPECTED LOGIC LOCKOUT OF DIVISION I RHR DURING SURVEILLANCE TESTING "Operations was performing 1-SR-3.3.5.1.6(BI), Functional Testing of RHR Loop I Pump and Minimum Flow Valve Logic, which rendered Division I of RHR INOPERABLE. While placing a jumper in accordance with procedural direction. Unit 1 received RHR Pump Initiate Lockout amber lights 1-IL-74-28 and 1-IL-74-39 for 1B and 1D RHR pumps (Division II). This was immediately recognized as being unexpected and action was taken to restore the 1B and 1D RHR pump auto start capability. The 1B and 1D RHR pumps were prevented from auto starting for approximately 1 minute. The Logic functioned as designed; however, this condition was caused by a procedure error. Entered TS LCO 3.0.3 based on TS LCO 3.5.1 Condition H - Two or more Low pressure ECCS injection/spray subsystems inoperable for reasons other than Condition A. TS 3.0.3 was exited after approximately one minute when the auto start capability of 1B and 1D RHR pumps was restored. 1B and 1D RHR pumps were available for manual initiation and remained OPERABLE for Containment Cooling and Shut Down Cooling Functions. "This event is reportable within 8 hours per 10CFR 50.72(b)(3)(v)(D) 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "The NRC resident inspector has been notified. "At 0407, the condition requiring this report was removed and safety function capability was restored." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-03-21
44924 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2009-03-21 09:00 | 2009-03-21 11:53 | 2009-03-21 | VARIOUS CONTROL ROOM ANNUNCIATORS AND ALARMS OUT OF SERVICE DUE TO MAINTENANCE ON POWER SUPPLY "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 21, 2009, from approximately 09:00 Mountain Standard Time (MST) until 14:00 MST, Palo Verde maintenance personnel will be performing scheduled maintenance to repair one of two redundant 120 VAC power supplies in Unit 2 that provides power to various alarms in the main control room. This work will require both power supplies to be de-energized resulting in approximately 50 percent of the Unit 2 plant annunciators being unavailable. "The following compensatory measures will be in place for the duration of the scheduled work: Other assessment indications will remain available: Plant Monitoring System Qualified Safety Parameter Display System Emergency Response Facility Data Acquisition System No changes in plant power or operating mode are planned. A third licensed operator will be in the control room. "The NRC Resident Inspector has been notified of the scheduled outage and this ENS call." * * * UPDATE FROM JAMES BLAZEK TO DONALD NORWOOD AT 1821 EDT ON MARCH 21, 2009 * * * The power supply was successfully repaired and all annunciators were restored to normal as of 1515 MST. The Licensee will notify the NRC Resident Inspector. Notified R4DO (Hay) and NRR EO (Holian). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-03-21
44923 | -1 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2009-03-21 01:21 | 2009-03-21 07:54 | 2009-05-15 | HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION FOLLOWING PLANNED MANUAL SCRAM "At 0121 on Saturday, March 21, 2009, Nine Mile Point Unit One was manually scrammed from approximately 18% rated power in preparation for Refueling Outage 20. The plant scram was a planned evolution. Following the manual scram insertion at 0121, the High Pressure Coolant Injection (HPCI) System automatically initiated on low Reactor Pressure Vessel (RPV) level. At 0123, RPV level was restored above the HPCI System low level actuation setpoint, and the HPCI System initiation signal was reset. At Nine Mile Point Unit One the HPCI system is a mode of operation of the feedwater and condensate system. It is not an Emergency Core Cooling System (ECCS). A HPCI System actuation signal on low RPV level is normally received following a reactor scram, due to level shrink. "10 CFR 50.72(b)(3)(iv)(A) requires reporting within 8 hours when a valid actuation of the feedwater coolant injection system occurs. The event has been entered into the corrective action program. There are no other adverse impacts to the station based on this event." All control rods fully inserted. Electrical lineup is normal and there are no safety equipment out of service. The licensee has notified the NRC Resident Inspector * * * UPDATE FROM BRIAN FINCH TO JOE O'HARA AT 1611 ON 5/15/09 * * * "Event notification 44923 is being retracted after further evaluation because it has been determined that the High Pressure Coolant Injection (HPCI) system initiation was part of a pre-planned sequence. "10 CFR 50.72(b)(3) requires that any event or condition that results in valid actuation of any of the systems listed in this section, including a feedwater injection system, must be reported within 8 hours. Except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "The HPCI actuation that occurred after the manual scram from 18% Rated Thermal Power (RTP) was part of a pre-planned sequence in accordance with an operating procedure on plant shutdown. The HPCI initiation was also discussed during Just-in-Time training for the operating crew prior to performance of the soft shutdown. "At Nine Mile Point Unit 1, the HPCI system is a mode of operation of the feedwater and condensate systems. The HPCI system is not an Emergency Core Cooling System (ECCS). A HPCI system actuation signal on low reactor water level is normally received following a reactor scram, due to reactor water level shrink." The licensee will notify the NRC Resident Inspector. Notified R1DO (Holody). | 0 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-03-21
44922 | 0 | PALISADES | 1 |  |  | [1] CE | 2009-03-20 20:30 | 2009-03-20 22:56 | 2009-03-20 | STATE OF MICHIGAN NOTIFIED OF ONSITE SEWAGE SPILL "At 2030 hours on March 20, 2009 it was determined that sewage from the onsite sewage system had exited the system through a manhole on the 590 foot elevation of the site. This discharge, a clear odorless water, then flowed along the asphalt roadway to a storm drain which ultimately discharges to the beach of Lake Michigan (no fluid reached Lake Michigan waters). The State of Michigan, via the Pollution Emergency Alert System (PEAS), was notified as required by the Site Spill Plan by the Site Environmental Coordinator at 2207 hours. The local government (Van Buren County) was notified at 2220 hours via 911." The licensee informed both state/local agencies and the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-20
44921 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2009-02-18 08:00 | 2009-03-20 14:13 | 2009-03-25 | MISSING NICKEL-63 LICENSED RADIOACTIVE MATERIAL "On February 18, 2009, during a scheduled radioactive material inventory activity, a personnel explosive detection device containing 15 mCi of Nickel-63 was discovered missing. A search of the facility has not located the licensed material at this time. "This is being reported under 10 CFR 20.2201 (a)(ii), Loss of licensed material greater than 10 times the quantity specified in Appendix C to 20.1001 - 20.2401 {20.2201(a)}." The personnel explosive detection model information is: Smiths Detection; Ionscan Sentinel II; Instrument Serial Number - 213028; Sealed Source Serial Number (from the manufacturer) - MY 636. The Licensee suspects that this material was disposed as trash. The NRC Resident Inspector has been notified. * * UPDATE FROM FRED POLLAK TO JOHN KNOKE AT 0949 EDT ON 03/25/09 * * Licensee is adding a sentence to the first paragraph "The location of the source remains indeterminate at this time." The licensee is deleting the sentence in the fourth paragraph "The licensee suspects that this material was disposed as trash." The licensee has notified the NRC Resident Inspector. Notified R2DO (Steven Vias). Notified NRR EO (Ross-Lee) and FSME EO (McIntosh) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-03-20
44920 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2009-03-19 15:32 | 2009-03-19 21:39 | 2009-03-20 | UNPLANNED START OF A COOLING WATER PUMP DURING TESTING "In preparation for planned maintenance of 12 Diesel Driven Cooling Water Pump (Train A), 121 Cooling Water Pump was aligned as a safeguards replacement pump per plant procedures. Maintenance steps were then completed to a point allowing testing and 12 DDCLP was restored. The Operations procedure steps to enter the Cooling Water LCO 3.7.8 Condition A and realign 121 CL Pump away from being a safeguards replacement were missed and permission was granted to perform testing. 12 DDCLP was locally started per the PM and then tripped as directed from rated speed at 1513. The pump trip resulted in a cooling water pressure transient that automatically started 121 CLP and is reportable under 10CFR 50.72(b)(3) as an unplanned safety related system actuation. 121 CLP operated normally and there were no adverse plant effects from the transient. "During the investigation of the automatic start, it was recognized that with 121 CLP still aligned as a safeguards replacement and 12 DDCLP running locally, a Safety Injection signal and start of 22 Diesel Driven Cooling Water Pump (Train B) would result in 121 CLP trip. LCO 3.7.8 Condition A was entered for one safeguards pump OOS and 121 CLP was returned to OPERABLE status at 1613. 121 Cooling Water Pump was shut down and returned to standby at 1936. "Maintenance activities and testing for 12 DDCLP have been suspended pending investigation and corrective actions. 121 CLP remains aligned as a safeguards replacement and both cooling water headers have operable safeguards pumps." The licensee notified the NRC Resident Inspector. * * * * UPDATE AT 1700 EDT ON 03/20/09 FROM TYLER GREENFIELD TO S. SANDIN * * * "The licensee has completed its initial investigation and corrective actions. Maintenance and testing activities for 12 Diesel Driven Cooling Water Pump has resumed. "There was an error in the text of the initial notification, the time of the autostart of 121 Motor Driven Cooing Water Pump was 1532 not 1513." The licensee informed the NRC Resident Inspector. Notified R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-03-19
44919 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-03-04 | 2009-03-19 19:32 | 2009-03-19 | AGREEMENT STATE REPORT INVOLVING A MISSING GENERAL LICENSED SOURCE The following information was received from the Commonwealth of Pennsylvania via fax: "PA DEP Bureau of Radiation Protection [BRP] was notified in writing, dated March 9, 2009, by the Purchasing / Customer representative of Say Plastics. The device has not been found but they will continue to search for it. To prevent future incidents, they have created a sign out sheet that is to be signed when a worker checks the device out and returns the device. "The State has an inspection scheduled for March 19, 2009 and will continue to keep NRC informed of the status of our investigation. "Event description: Lost a model P2021 Nuclecel Static Eliminator "City, State: McSherrystown, PA "Description: (Serial Number A2GB696) (Manufacturer NRD, LLC) Device was discovered missing on March 4, 2009. "Eliminator containing Po-210 (originally 10 mCi; decayed to approximately 1.4 mCi) "PA Event Report ID No: PA090012" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-03-24
44918 | 0 | VIRTUA HEALTH SYSTEM |  |  |  |  | 2009-03-19 14:15 | 2009-03-19 17:01 | 2009-03-20 | MEDICAL BRACHYTHERAPY TO UNINTENDED SITE "At approx. 1415 hrs. [3/19/09] the physicist was performing a post operative dosimetry analysis of the Iodine-125 prostate seed brachytherapy implant for [the patient] when it was discovered that none of the implanted seeds made it to their intended destination, and were, in fact, implanted outside the target organ. The seeds retained their planned pattern grouping, with the superior end of the seed cloud being about 2 cm from the apex of the prostate gland. A dosimetric analysis of the CT image revealed all 93 seeds accounted for, and a calculated dose to 90% of the target organ (prescription line) being 2.24 Gy. The prescribed dose in the Written Directive was 145 Gy. "As the seeds appear distal to the target organ, the dose appears to be maximally confined to soft tissue including muscle and subcutaneous fat. A complete analysis was requested of the Radiation Oncologist who was immediately informed. A preliminary dose report was printed for review. "Actions Taken: The attending Radiation Oncologist was immediately notified. It was also noted by the physicist/RSO that this event was reportable as a Medical Event under 10CFR35. [The] License Administrator, was notified at approximately 3:00 PM as was the Nuclear Medicine Manager. The preliminary dosimetry report was printed at 1632 hrs and the NRC Operations Center was notified at 1701 hrs by telephone. A follow-up notice will be emailed to the Ops Center within 1 hr. "The involved individuals were notified of the NRC contact and a request was made for an investigation. Marlton Risk Management will also be informed." Incident Number: 2009-03-19 A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-03-21
44917 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2009-03-19 | 2009-03-19 12:57 | 2009-03-20 | AGREEMENT STATE REPORT INVOLVING IMPROPERLY PACKAGED MATERIAL The following information was received from the State of Wisconsin via fax: "On March 19, 2009 the department received a telephone notification that UW-Madison had received a Yellow II package that exceeded the limits of the external radiation levels permitted for this type of package. The RSO stated that the contents are two sealed sources of Cs-137 with a combined activity of 52 millicuries. The package was not delivered to the Radiation Safety Officer, but was shipped directly to the University calibration lab on March 18, 2009 and received about 3:30 pm. Alarms went off at the loading dock and the calibration lab when the package was delivered. The [transportation index] TI on the package stated 0.2, however, the radiation levels at one meter were 20 mR/hr. The highest reading on contact was 0.9 R/hr. The licensee wipe tested the package and found no removable contamination. The package has been placed in a secured area and has not been opened. "The RSO has contacted the shipper's contact person at LAC + USC and the courier. The package is approximately 10 inches x 10 inches x 10 inches in size. The State of Wisconsin will continue to monitor the situation, provide assistance as needed to address any jurisdictional issues, and perform independent dose assessments as the public dose limit may have been exceeded." Wisconsin Event Report ID No.: WI09004 * * * UPDATE AT 1646 EDT ON 03/20/09 FROM CHERYL K. ROGERS TO S. SANDIN * * * The following information was provided as an update via fax: "On March 19, 2009 the department received a telephone notification that UW-Madison had received a Yellow II package that exceeded the limits of the external radiation levels permitted for this type of package. The RSO stated that the contents are two sealed sources of Cs-137 with a combined activity of 52 millicuries. The package was not delivered to the Radiation Safety Office as required, but was shipped directly to the University Calibration Lab on March 18, 2009. It was received and signed for at the Wisconsin Institute for Medical Research (WIMR) loading dock at around 9:00 am and delivered to the calibration lab at 9:52 am. An area monitor in the lab shipping/receiving room alarmed when the package was delivered. A student worker immediately notified the Technical Director of the UW Calibration Lab. "The Director used a meter to identity the package and noted that the exposure rate on one package exceeded 50 mR/hr on contact. The package was placed on a cart and transported to a secure location. The TI on the package stated 0.2, however, the radiation levels at one meter were 20 mR/hr. The highest reading on contact was 0.9 R/hr. The package was approximately 10 inches x 10 inches x 10 inches in size. The licensee conducted a thorough wipe test and confirmed that there was no removable contamination on the outside of the package. He then left a message for UW Safety. "The call was returned about noon and the Safety Office staff arrived around 2 pm. The RSO and Assistant RSO concluded that the two sealed sources were outside of the lead shielded container due to the high radiation readings on contact with the package. The RSO called the shipper's contact person named on the shipping papers at LA County, University of Southern California and the courier. The individual who had prepared the package stated that the package must have been opened either in transport or by the Calibration Lab. The UW-Madison RSO emphatically stated that the package had not been opened. "The State of Wisconsin was notified on the morning of March 19, 2009 and made an immediate notification to the NRC Operations Center. Contact was established with the California jurisdiction for the shipper/licensee in order to facilitate contact with the licensee's radiation safety office. The State of Wisconsin inspector made arrangements to be present on the morning of March 20, 2009 to monitor and video the package opening. "On March 20, 2009, the Director of the UW Radiation Calibration Laboratory carefully opened the package and conducted multiple wipe tests to assure there was no contamination inside the package. The package contained an open lead pig. The sources were loose in the box. One source was located under the bottom of the styrofoam tray and one source was stuck in the styrofoam tray. There were multiple problems with the packaging, markings and shipping paperwork. The main problems were that the lead pig was not adequately taped shut and the inner packaging was not sufficient to hold the pig in place, thus, the pig moved about in the package. It does not appear that this was an approved shipping container. The sealed sources were wipe tested and were not leaking, however, the Director would like to take a closer look at the sources to assure that they were not damaged. "The State of Wisconsin will continue to monitor the situation, provide assistance as needed to address any jurisdictional issues, and perform independent dose assessments as the public close limit may have been exceeded." Notified R3DO (Ring) and FSME (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2009-03-24
44916 | 0 | BILLINGS CLINIC |  |  |  |  | 2009-03-13 | 2009-03-19 10:49 | 2009-03-19 | LOST THREE VIALS OF XENON - 133 The RSO for the licensee reported the hospital inadvertently disposed of 78 millicuries of Xenon-133 through the solid waste system. The hospital believes that a housekeeper may have thrown it away as solid waste. Couriers delivered the material without the knowledge of the hospital on 3/13/09. Later that same day, the licensee believes that the housekeeper picked up the boxes that the material was located inside of and mistakenly threw them away as waste. A search of the facility was conducted without success. The licensee is not taking any action to recover the material from the dump. All trash is compacted on site into a common container. The trash has already been taken to the landfill and buried. The licensee is not taking any action to recover the material from the dump. The licensee has taken corrective actions with the couriers and designated a new storage area for the material in a restricted area. Housekeeping will no longer be handling the boxes. This licensee does not consider the loss be a threat to the health and safety of the community. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | MT | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-03-19
44915 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2009-01-07 | 2009-03-19 09:14 | 2009-03-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Oklahoma was notified by a Walmart corporate representative located in Bentonville, AR, indicating that Walmart was unable to account for 276 tritium exit signs (which are general licensed materials) that were used at one time in Walmart stores throughout the State of Oklahoma. The Walmart representative informed the state office that Walmart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The State of Oklahoma was provided a listing from corporate Walmart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2009-03-24
44914 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-03-18 16:15 | 2009-03-18 17:08 | 2009-03-18 | SAFEGUARDS REPORT The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-03-18
44913 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-03-18 10:55 | 2009-03-18 14:37 | 2009-03-18 | MASSACHUSETTS AGREEMENT STATE REPORT - HIGH RADIATION ON OUTSIDE OF A RADIOPHARMACEUTICAL PACK The following information was obtained from the Commonwealth of Massachusetts via facsimile: "Lantheus Medical Imaging was receiving a delivery from Cardinal Health Nuclear Pharmacy [MA License# 41-0366] of F-18 and found the dose rate on the outside of package to be 1.7 R/hr. Lantheus immediately contacted Cardinal Health and notified them of the dose rate. Cardinal Health believed the shielding somehow moved in route. Lantheus accepted the delivery and placed the package in a restricted room to check out later in the day." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-03-23
44912 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-03-17 | 2009-03-18 09:44 | 2009-05-05 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER HANDLE BROKE "On the afternoon of 3/17/09, while closing the shutter of a Ohmart/Vega SH-F1 level detection gauge, the handle separated from the shutter closure device. The gauge contains a 10 milliCurie Cesium (Cs) - 137 source serial # 5747 GK. The license can not confirm the exact position of the shutter, but they are sure that it is not closed yet. Lubricants have been used on the shutter mechanism to aid in its operation. The licensee will continue their attempts to close the shutter on 3/18/09. If unable to close, they will request assistance from the manufacturer. Additional information will be provided as it is received." Texas Event: I-8620 * * * UPDATE FROM ART TUCKER TO HOWIE CROUCH VIA EMAIL @1745 ON 3/18/09 * * * "The Radiation Safety Officer notified the [State of Texas] that the gauge had not been fully closed yet, but area dose rates were normal therefore the gauge does not create additional risk of exposure to their workers." Notified R4DO (Hay) and FSME EO (Camper). * * * UPDATE FROM ART TUCKER TO JOE O'HARA VIA EMAIL AT 1021 ON 5/5/09 * * * "The licensee reported [to the State of Texas] that on April 28, 2009, a technician from the manufacturer installed a shield over the source and removed the gauge from the vessel. The gauge has been placed in a radioactive material storage area until it can be packaged and returned to the manufacturer." Notified R4DO (Pick) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-03-23
44911 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-03-17 | 2009-03-17 09:05 | 2009-03-17 | PENNSYLVANIA AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received from the State of Pennsylvania via email: "A female patient was to receive HDR twice a day for a total of 10 treatments with an expected dose of 34Gy via mammosite treatment. A dummy wire was inserted into the balloon to check and measure the tube length for dosage calculations. A CT scan was performed daily to verify the position of the treatment site. Treatment calculations were done, reviewed, approved, and treatment began Monday, February 23, 2009. "[On] Friday, February 27, 2009, a different therapy physicist was checking the patients charts and thought that there may have been an error. "[On] Monday, March 2, 2009, the original physicist checked the findings of the different therapy physicist and discovered that there had been an error in the placement of the source during the treatment. The source was not fully inserted into the balloon, but was 3cm from where it should have been, thereby resulting not only in a large difference in the tumor dose received (approx. 30% of intended) but also in a severe dosage to non-intended areas of the patient. "The physicist, RSO and two licensee's radiation oncologist reviewed the situation once it was discovered. The patient is being followed for any sequelae (pathological conditions) to the event. It was reported that erythema (dilated capillaries) is developing consequential to the event. Follow ups are expected to occur weekly. The oncologist has discussed the event with the patient." PA Case # PA090011 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-03-20
44910 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-03-16 12:25 | 2009-03-16 20:17 | 2009-04-30 | SHORT TERM LOSS OF SUPPLEMENTAL SPENT FUEL COOLING "On 3/16/2009 at 1225, Unit 2 was in Mode 5 (Refueling), during natural circulation mode to support maintenance on the common suction line to both loops of Residual Heat Removal (RHR) Systems, both Secondary Side Supplemental Spent Fuel Pool Cooling pumps tripped. Earlier on the same day at 0550, the unit had been placed into natural recirculation mode when the RHR Loop 'A' was secured from the Shutdown Cooling mode of operation. In this mode the 'A' loop of Supplemental Spent Fuel Pool Cooling coupled with the 'A' loop of the Fuel Pool Cooling system was designated as the primary decay heat removal system and the 'B' loop of both systems were designated as the backup decay heat removal system. At the time of the secondary pump trips, the RHR Common loop suction was being placed under clearance. "The trip of the Secondary Side pumps caused a loss of the entire ('A' and 'B' loops) Supplemental Spent Fuel Pool Cooling System and resulted in a partial loss of the decay heat removal system. Both 'A' and 'B' loops of the Fuel Pool Cooling System remained in service. In addition, Unit 2 remained in an Active LCO for Technical Specification 3.9.7 due to securing all loops of Shutdown Cooling at 0550. The Supplemental Spent Fuel Pool Cooling system was restored to operation at 1245, and actions to restore RHR to the Shutdown Cooling Mode of operation were in progress. "RHR 'A' Loop was restored to on available status at 1259, and placed in the Shutdown Cooling mode of operation at 1447. "Based on the combination of systems out of service, and no supporting calculation to ensure Spent Fuel Pool Temperature remains below 150 degrees Fahrenheit (as described In the UFSAR), this could have prevented the fulfillment of the safety function for Decay Heat Removal. "The safety significance of the loss of primary decay heat removal was minimal. During the loss of the Supplemental Spent Fuel Pool Cooling system, reactor vessel temperature rose by approximately 0.5 degrees Fahrenheit. Total heatup of the Spent Fuel Pool was less than 2 degree Fahrenheit. Allowed Technical Specification Heatup rate is limited to 100 degrees Fahrenheit per hour which the was not approached, or exceeded, at any time. Calculated time to boil (with no cooling supplied) was greater than 24 hours; transient was brief in duration and did not challenge time to boil. At all times, the Fuel Pool Cooling System remained in service. There were no challenges to the reactor pressure vessel, or the fuel, due to the loss of decay heat removal. "The Supplemental Spent Fuel Pool Cooling System was restored to operation at 1245. RHR was restored to service in the shutdown cooling made of operation at 1447." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1342 EDT ON 04/30/09 FROM MARK TURKAL TO S. SANDIN * * * The licensee is retracting this report based on the following: "On March 16, 2009, at 2017 hours, the Control Room Supervisor made a notification (Event Number 44910) to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(v)(B) (i.e., any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat). The notification was made as a result of a loss of the secondary side Supplemental Spent Fuel Pool Cooling (SSFPC) system pumps. At the time of the loss, both loops of Residual Heat Removal (RHR) shutdown cooling were out of service to support maintenance. In this mode, the 'A' loop of the SSFPC system coupled with the 'A' loop of the Fuel Pool Cooling (FPC) system was designated as the primary decay heat removal system and the 'B' loop of both systems were designated as the backup decay heat removal system. Loss of the secondary side SSFPC system pumps impaired the ability to remove decay heat; both the 'A' and 'B' loops of the FPC system remained in service. "Basis for Retraction "Event Notification 44910 was conservatively made because, although the FPC system remained capable of removing decay heat, there was no documented calculation which demonstrated that the FPC system could maintain the fuel pool and reactor cavity temperature at or below 150 degrees F, as described in the Updated Final Safety Analysis Report. An Engineering Calculation (i.e., 0041-0021. 'Fuel Pool Cooling Heat Removal Capability') demonstrating that the FPC system was capable of maintaining temperature below 150 degrees F, at that point in the outage, has been completed. As such, the March 16, 2009, loss of the secondary side SSFPC system pumps does not represent a condition that could have prevented the fulfillment of a safety function and this event is not reportable under 10 CFR 50.72(b)(3)(v)(B). "Investigation of this condition is documented in the corrective action program in Nuclear Condition Report (NCR) 325496. "The NRC Resident was notified of this retraction." Notified R2DO (Ernstes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2009-03-16
44909 | 0 | ARMED FORCES RADIOBIOLOGY RSCH INST |  |  |  | 1100 KW TRIGA MARK-F | 2009-03-16 11:23 | 2009-03-16 13:54 | 2009-03-16 | MANUAL TRIP DUE TO FAILURE OF TECHNICAL SPECIFICATION REQUIRED FUEL THERMOCOUPLE The licensee provided an informational call to inform the NRC Operations Center that it had manually tripped the research reactor from approximately 75% power (750 KW) due to the failure of a core fuel thermocouple that provides a reactor trip function. The technical specifications for the reactor require that two fuel centerline temperature thermocouples that provide a reactor trip function be available while the reactor is operating. The two fuel centerline thermocouples were confirmed to be functioning properly during a pre-startup surveillance earlier this morning. While at power the operators noticed fluctuations in one of the two thermocouple readouts. After about 4 minutes, it was concluded that one of the thermocouples was not functioning properly and the reactor was manually tripped to be in compliance with the technical specification action statement. The licensee was within technical specifications as soon as the reactor was tripped. The reactor did not trip automatically with the failure of the thermocouple because the failed thermocouple was providing a low temperature input into the reactor protection logic. There were no other issues with the research reactor and the licensee noted that it was not required to make an immediate notification to the NRC Operations Center per its license. The licensee had also notified the NRC inspector for this facility (Pat Isaac) of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | MD | NPR | [5 empty] | 0 | 2009-03-16
44908 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-03-16 10:45 | 2009-03-16 13:02 | 2009-03-16 | OFFSITE NOTIFICATION DUE TO 1 GALLON OIL SPILL AT FOSSIL UNITS "On 3/16/09 at 1045, Miami-Dade County was notified of a 1 gallon fuel oil spill from the Turkey Point Fossil Plants. This fuel oil went into a storm drain which drains into the cooling canals used for all four units. The fuel oil spill originated from a leak in a fuel oil heater. This leak has subsequently been isolated. "At 1141, the Florida State Warning Point was also notified of the oil spill. "Notification to the Environmental Protection Agency is not required. "This four hour notification to the NRCOC is required per 10CFR50.72(b)(2)(xi) due to the notification to offsite government agencies." The licensee will be notifying the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-16
44907 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-03-16 09:00 | 2009-03-16 12:34 | 2009-03-16 | OFFSITE NOTIFICATION DUE TO FISH KILL DURING ROUTINE SHUTDOWN The licensee notified state and local authorities of a fish kill that occurred during a routine plant shutdown for refueling. The fish kill, in the Mississippi River, was monitored for a two day period. Notifications were made to the State of Minnesota Emergency Management Agency, Wright County Sheriff's Office, and Sherburne County Sheriff's Office. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-16
44906 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2009-03-13 21:51 | 2009-03-14 02:03 | 2009-03-14 | FEEDWATER REGULATING VALVE FAILURE LEADS TO MANUAL REACTOR TRIP "At 2151 CDT on 3/13/2009 with plant power at 84% following securing of the 2P-1A Main Feedwater Pump at 1934 due to bearing degradation, Unit 2 experienced a failure of the 'B' Main Feedwater Regulating Valve 2CV-0740 which caused 2E-24B Steam Generator level to lower. At 2151, with 2E-24B Steam Generator level at approximately 25% control room staff manually tripped the reactor anticipating an automatic trip at 22% steam generator level. Emergency Feedwater Actuation System automatically actuated at 22% steam generator level and responded to restore level to the normal post-trip levels. All Control Element Assemblies (rods) Inserted on the reactor trip." No safeties or relief valves opened after the trip. The plant is in its normal shutdown electrical line-up. Steam generator level is being maintained with emergency feedwater and decay heat is being dumped to the main condenser. The licensee notified the State of Arkansas and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  | 0 | 2009-03-14
44905 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-03-13 00:25 | 2009-03-13 00:42 | 2009-03-17 | PARTIAL LOSS OF PLANT COMPUTER FOR SCHEDULED MAINTENANCE TAKING ERDS OOS "The Perry Nuclear Power Plant has taken a portion of the Plant Computer out of service for scheduled maintenance. This has resulted in a portion of ERDS being out of service. From 0025 hours EDT on March 13, 2009 for approximately 36 hours, personnel will be performing maintenance activities which result in a partial loss of the Plant Computer. During this planned maintenance, portions of the Safety Parameter Display System (SPDS) and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Private Branch Exchange, Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10CFR50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communication capability. A follow-up notification will be made when the maintenance activities are completed and the equipment is restored." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1132 ON 3/14/2009 FROM TONY JARDINE TO MARK ABRAMOVITZ * * * The plant has extended the expected plant computer outage time by 60 hours (ending 3/16/2009 at 2400). Notified the R3DO (Lara). * * * UPDATE AT 1907 EDT ON 3/16/2009 FROM TOM STEC TO BILL HUFFMAN * * * The licensee has extended the expected outage time for the plant computer maintenance by an additional 24 hours. Repairs are now expected to be completed by 2400 EDT on 3/17/09. The licensee will notify the NRC Resident Inspector. R3DO(Ring) notified. * * * UPDATE AT 1723 EDT ON 3/17/2009 FROM ANTHONY JARDINE TO BILL HUFFMAN * * * The licensee states that that the plant computer and all associated functions (SPDS, CADAP, and ERDS) were returned to service at 1313 EDT on 3/17/09. The licensee has notified the NRC Resident Inspector. R3DO(Ring) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-03-13
44904 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2009-03-12 16:20 | 2009-03-12 23:24 | 2009-05-06 | HPCI DECLARED INOPERABLE "This non-emergency 8-hour report is pursuant to 10CFR50.72(b)(3). On 03/12/09 at 1620, Operations performed [Standard Operating Procedure] S.O. 23.7.B-2 to swap the CST and Torus suctions in conjunction with scheduled I&C testing. While opening the HPCI Torus Inboard Suction valve MO-2-23-58, its travel stopped at approximately the 50% full open position. The HPCI system was declared inoperable per Technical Specification (T.S.) 3.5.1. The HPCI system remains available and the HPCI Torus Outboard Suction valve MO-2-23-57, was closed and de-energized for PCIV isolation as required by T.S. 3.6.1.3. "Both MO-2-23-058 and the Unit 2 HPCl system are inoperable. The valve has been quarantined in accordance with station procedures and required Technical Specification actions have been taken. Reactor operation is unaffected and Unit 2 remains at 100% power. The inoperability of the HPCI system places the plant in a 14 day shutdown Tech Spec action statement. Further investigation of the cause of the valve failure is currently in progress." RCIC has been verified operable. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DAVE FOSS TO HOWIE CROUCH @ 0824 ON 5/6/09 * * * "The purpose of this notification is to retract a previous report made on 3/12/09 at 2324 hours (EN# 44904). Notification of the event to the NRC was initially made as a result of declaring the Unit 2 High Pressure Coolant Injection (HPCI) system inoperable when unexpected conditions were found during performance of routine surveillance testing of HPCI. Specifically, it was noted that a motor-operated Suppression Pool suction valve for HPCI (MO-58) did not complete its stroke in the open direction during testing. The HPCI system was not operating at the time of the discovery. "Since the initial report, Engineering has determined that HPCI was capable of performing its safety function. The evaluation determined that the MO-58 valve was capable of opening to a position sufficient to ensure that the HPCI safety function was met for design basis conditions. Additionally, since the torque switch is bypassed during actual design events, full motor torque would have been available which was sufficient to allow the valve to reach its full open position. It has also been determined that the valve was capable of closing on a signal to close automatically. "During resolution of the HPCI MO-58 concern, the suction source from the Suppression Pool was isolated in accordance with Technical Specifications since MO-58 is considered as a Primary Containment Isolation Valve. This action was performed in accordance with station procedures and is considered planned maintenance. "The NRC resident has been informed of the retraction." Notified R1DO (Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-03-12
44903 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-03-12 16:45 | 2009-03-12 21:05 | 2009-03-12 | OFFSITE NOTIFICATION FOR LOW INTAKE WATER LEVEL DUE TO AN ICE JAM "On March 12, 2009 at 1249 CDT, Fort Calhoun Station entered AOP-01, 'Acts of Nature' Section IV, 'Low River Water Level' due to lowering river level resulting from an ice jam upstream from the station. At that time, Missouri River level had lowered to 983 feet and posed a potential challenge to continued operation of the circulating water pumps. AOP-01 requires offsite notification of the U.S. Army Corps of Engineers to determine current river conditions, expected river levels for Fort Calhoun Station, and planned actions to alleviate the lowering levels. "Current river level at 1900 CDT was 982' 6" with the U.S. Army Corps of Engineers predicting the minimum river level to be 981' 6" feet. At this time, there has been no degradation in the circulating water pump or plant performance and compensatory measures are in place to monitor river level hourly. Barring degradation in circulator performance, additional actions will not be required if river level stays above the predicted minimum levels." The minimum level for operating the circulating water pumps is 978'. A break in the ice jam is not expected to adversely affect the plant. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-12
44902 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-03-05 16:45 | 2009-03-12 15:15 | 2009-06-05 | SOURCE DISCONNECT FROM RADIOGRAPHY CAMERA DRIVE CABLE The Agency (State) was notified (at 1645 CDT) by the licensees RSO that they had a source disconnect and that the source was later retracted. The event involved an INC IR-100 camera containing a 94 curie Ir-192 source. The source was in use for about one week, about 6 jobs. A local Texas inspector went to the site to investigate the event. The licensee later notified the Agency (State) that in this case, the connector crimped fitted on the source pig tail had separated from the source drive cable. The two individuals who returned the source to the camera housing received 425 millirem by self reading dosimeter for one worker, and between 750 and 800 millirem calculated for the other worker. The RSO stated that neither worker exceeded the annual DDE limit. TLD's for the workers involved have been sent to their processor and the results should be back on 3/9/09. The State of California has been informed of the event. On March 13, 2009, the RSO notified the Agency (State) that the radiography camera had been packaged and will be returned to the manufacturer today. Texas Incident # I-8614 UPDATE FROM ART TUCKER VIA EMAIL TO JOHN KNOKE AT 1237 0N 04/14/09 "[The State] received exposure reports for two workers involved in the source retrieval. The support individual received 299 millirem DDE, and the individual who actually retrieved the source received 502 millirem DDE, and 425 millirem calculated to the hand." Notified FSME (Angela McIntosh) and R4DO (Jack Whitten) * * * UPDATE ON 06/05/2009 AT 1015 FROM ART TUCKER TO VINCE KLCO * * * Report received via e-mail: "The [State of Texas] received the following information from the manufacturer of the source device: "[The] license, Industrial Nuclear Company [INC], was notified by Desert Industrial X-ray that there had been a source disconnect of 97 curies, source S/N-N597 on March 5, 2009. Source and connector was received at Industrial Nuclear Co, Inc on March 13, 2009. "Upon inspection of source connector [on] S/N- N597 that was received from Desert Industrial X-ray, INC found no evidence [of] physical damage. The cable appeared to have some stretching but not any more than would be expected after the pull test. "Dimensions were performed on all previous inspected source assembly components and found to be within design limits. "All INC source connector assemblies in inventory (from the same manufacturing date) were re-load tested and all passed. INC has to date never had a Source Connector come off in pre-inspection or after it was put in use. INC has not been able to discover just how this might have happened. In the report the licensee stated the connector crimp failed. INC has tried to recreate this event but [has] had no success in doing so. The licensee said the source had been in use for one week [and] if the source connector crimp was bad it should had failed on the first day. "The licensee has not reported any additional problems associated with their exposure devices." Notified R4DO (Lantz) and FSME EO (McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-03-17
44901 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-03-12 04:20 | 2009-03-12 12:31 | 2009-03-12 | PROCESS COMPUTER AND ERDS UNAVAILABLE FOR GREATER THAN 60 MINUTES "Byron Unit 1 Process Computer was unavailable for use from 0420 to 0814 EDT on 3/12/09. This resulted in a loss of Unit 1's ability to send Emergency Response Data System (ERDS) to the NRC for greater than 60 minutes. The Unit 1 Process Computer and ERDS was restored at 0814 on 3/12/09. Byron's reportabllity procedure defines a loss of ERDS for greater than 60 minutes as being a major loss of emergency preparedness capability." NRC Resident Inspector was notified by licensee. Notified R3DO (Julio Lara) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-03-12
44900 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-03-06 | 2009-03-12 15:04 | 2009-03-18 | AGREEMENT STATE REPORT - TWO SOURCES DISPOSED AS SCRAP "On February 20, 2009 during an internal audit/inspection, it was discovered that two Filtec Model FT 50 level detection devices each with 100 mCi of Am-241 were missing [and] apparently moved off the facility as scrap metal. Notification to state offices were through inappropriate channels and thus Incident Investigation staff were not informed of [the event] until March 12, 2009. A preliminary investigation has determined that the metal scrap along with these devices was subsequently shipped to a mill in India and [has] probably been melted. Specific details of the shipping, route and mode of transport, vendors as well actual location in India are being gathered. The serial numbers are 112733/5393 and 116813/2555." Texas Incident # I-8618 * * * UPDATE ON 03/13/2009 AT 1400 FROM RAY JISHA TO DAN LIVERMORE * * * Report received via e-mail: "The gauges were accidentally removed from the plant and placed into a metal scrap dumpster and picked up from our property by MC3 International Scrap Salvage on December 8, 2008. "MC3 International Scrap Salvage delivered the mixed shear cut metal to Lone Star Fox Export Metals on December 8, 2008. Lone Star Fox Export shipped the mixed cut metal to India before or around December 13, 2008. The licensee provided a list of 10 containers. "The mixed metal was sent to Nhava Sheva, India. The licensee does not have any information on the mill in India. They do not have any information on products that may have been produced from the scrap. "The state is in the process of contacting the scrap metal dealers. Additional information will follow as it is obtained." Notified R4DO (Farnholtz), FSME EO (McIntosh), OIP (Ramsey), and ILTAB (via email). * * * UPDATE ON 03/18/2009 AT 1253 FROM RAY JISHA TO VINCE KLCO * * * Report received via e-mail: "On Monday, March 16, 2009 [State of Texas] staff proceeded to Dr. Pepper Bottling Company (DP) in Irving, TX, General License Acknowledgement (GLA) G01697. This was in response to a report that two gauges were removed from the facility, potentially sheared at a local area scrap yard, and then shipped to India as feed for a steel mill. Upon arrival [state personnel] interviewed the Manager of Environmental Health and Safety and the Maintenance Manager in order to investigate the details of the two missing fixed fill level gauges (Industrial Dynamics, FT-50 containing 100 mCi, Am-241 each). The current contact person listed on the permit, was out of town at the time of this investigation. "This gauge is a stainless steel box with overall head dimensions of 17 inches high, 4 ¢ inches wide and 19 ¢ inches long. These particular models have a manual shutter that was assumed to have been closed when the device was taken off-line. The Industrial Dynamics Source model 06110 is a matrix Americium 241 oxide and ceramic powder fired into a cavity 2 inches wide, 2 inches high and 1 3/8 inches deep. There is a 0.005 inch thick radiation window and when the shutter is closed, the radioactive material is covered on all sides by at least 0.5 inch of stainless steel. "Apparently, the gauges were taken out of service some years back and stored in a used or discarded equipment area. Then on Monday December 8, 2008, the gauges, along with other scrap metal, were removed by a single contractor. "Those materials were taken to Lone Star Fox Export Metals for processing and packaging and it was assumed that the gauges would have been shipped in one of ten containers. "The mixed shear cut metal was reportedly sent to Nhava Sheva, India as feed for a steel mill on or about Saturday, December 13, 2008 via Port of Entry (POE) Los Angeles/Long Beach. Research from US Customs and Boarder Protection (CBP) found evidence that seven of the ten containers were reportedly shipped from this POE on December 27, 2008 and arrived in India on February 12, 2009. "As confidence is high that the gauges were taken to Lone Star Metals and bulk material is sheared at the yard, arrangements were made to survey the property of 2019 Ruder Lane, Dallas, TX. Staff utilized an E-600 meter with probe optimized for Am-241 (PG-2), a Thermo Interceptor and Ludlum 14C with a 44-3 probe. All instruments should be capable of detecting the single 100mCi, Am-241 source at three feet even when housed in the device. Specific surfaces surveyed in the yard included where material is off loaded, likely places where the gauges may have been sheared, tracks on large equipment, where scrap was pushed into a pile and the container loading areas. Then a random [based] walk through of the area was conducted but all surveys did not detect any radiation above background. [It was noted] that the entire yard was covered in one or more inches of mud from recent rains and dust reduction measures. "Additional information is being acquired from several sources and the [State of Texas] is considering the utility of other methods and means of surveying." Notified R4DO (Hay), FSME EO (Camper), OIP (Ramsey), and ILTAB (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-03-17
44899 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-01-20 10:10 | 2009-03-12 11:21 | 2009-03-12 | INVALID ACTUATION OF SECONDARY CONTAINMENT "Monticello Nuclear Generating Plant is making a telephone Report in Accordance with 10 CFR 50.73(a)(2)(iv)(A) Invalid Actuation of the Standby Gas Treatment and Secondary Containment Isolation Systems due to high resistance resulting from inadequate contact wipe of a relay. This report is being made in lieu of a written Licensee Event Report. "SPECIFIC TRAINS AND SYSTEMS THAT WERE ACTUATED "The 'A' Standby Gas Treatment system actuated and Secondary Containment isolated. "DESCRIPTION OF WHETHER EACH TRAIN ACTUATION WAS COMPLETE OR PARTIAL "On January 20, 2009, during performance of Step 29 of Procedure 0003, Drywell High Pressure Scram and Groups 2, 3, & Secondary Containment Isolation Test and Calibration, the Standby Gas System automatically initiated and Secondary Containment isolated due to high contact resistance on a Drywell High Pressure HFA relay. This resulted in increased steam chase temperatures, entry into Action Statement TS 3.3.6.2.A for Secondary Containment Isolation Instrumentation, entry into Action Statement TS 3.6.4.1.A for Secondary Containment, entry into Action Statement TS 3.6.4.3.A for Standby Gas Treatment, and 10CFR50.73 reportability. "DESCRIPTION OF WHETHER OR NOT THE SYSTEM STARTED AND FUNCTIONED SUCCESSFULLY "All systems started and functioned successfully. "The cause of the initiation of SBGT and isolation of Secondary Containment during performance of Step 29 of Procedure 0003 was the presence of high resistance at relay 16A-K60A, contacts 5-6. The cause of high resistance at relay 16A-K60A, contacts 5-6, was inadequate contact wipe. The cause of the inadequate contact wipe was inadequate contact wipe adjustment after replacement of HFA coils with the new Century series coil. "The NRC Resident Inspector was notified of this event report." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-03-12
44898 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2009-03-06 | 2009-03-12 08:55 | 2009-03-12 | MISSING STATIC ELIMINATOR CONTAINING POLONIUM-210 "This report is in reference to a lost 13 [inch] Nuclestat ionizer bar that contains Polonium-210. The model number is P-2001-012, and the serial number is A2FS026. [The licensee] entered into a lease agreement for 13 ionizer bars, 2 Nuclecel in-line ionizers, and 1 Nuclecel ion air blower with NRD, LLC to minimize the amount of static present in our operation. "On Friday, March 6, 2009, it was reported by [the licensee's] Maintenance Department that an ionizer bar was missing from Winder #23. They were in the process of removing all of the ionizer bars from the winders to return them to NRD, LLC. The security cable was found attached to the winder, but it appeared someone had unscrewed the ionizer bar. All bars were attached to the end of the plastic winders with a steel cable and two screws. Upon investigation, [a licensee representative] found [that] the operators [remembered] the ionizer bar [being] present the week of February 23 - 27th on Winder #23, but they [did] not remember seeing the ionizer bar when [they] returned from a two day shutdown on Wednesday, March 4, 2009. After learning [that] the ionizer bar was missing on March 6th, the Plastic Winding Department was shutdown in the afternoon to search for it. About 15 employees searched the entire building including the trash and the building next door that contains old equipment. On Monday, March 9, 2009, the trash from the trash compactor was dumped in the parking lot, and the department searched through it for the missing ionizer bar. Once it was determined the ionizer bar was still missing, [a licensee representative] reported the lost device to [a State of Maryland representative] on March 9th. "The remaining in-line ionizer bars, Nuclecel in-line ionizers and Nuclecel ion air blower will be returned to NRD, LLC to terminate our lease agreement. We will replace them with carbon bars and electronic air ionizers to reduce static in our operation." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2009-03-17
44897 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2009-03-11 11:55 | 2009-03-11 19:49 | 2009-03-11 | CONTRACT EMPLOYEE FOUND USING ILLEGAL DRUGS IN PROTECTED AREA A non-supervisory contract employee was found using illegal drugs in the Protected Area. A for-cause fitness for duty test resulted in a confirmed positive drug test. The contract employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2009-03-11
44896 | 0 | ABB INC. |  |  |  |  | 2009-03-11 | 2009-03-11 15:52 | 2009-03-16 | PART 21 NOTIFICATION - DEFECTIVE HK AND K-LINE CIRCUIT BREAKER TENSION SPRINGS The identification of the subject component is as follows: ABB P/N 716359A00 Tension Spring. These springs are used in both HK (Medium Voltage) and K-Line (Low voltage) circuit breakers. In the HK breaker, the spring is used on the racking mechanism to position the racking mechanism interlocking latch. In the K-Line circuit breaker, the spring resets the prop latch mechanism following a circuit breaker trip. Circuit breakers and spare parts procured from ABB between 04/23/2008 and 02/27/2009 may have suspect springs installed. Nature of the deviation: Micro-cracks in the base of the hooked end of the springs may result in failure of the springs after repetitive cycles. A broken spring could potentially affect the ability of a K-Line or HK breaker to reset and close after an opening operation. Initial report of the nonconformance was generated on 02/11/2009 (NCR #68999JL), reporting that springs failed during mechanical life testing being performed on a K-Line breaker. These springs failed after approximately 2,800 cycles each. Given the large number of applications for the affected circuit breakers, ABB (Medium Voltage Service) cannot determine if the potential for a substantial safety hazard exists at any licensee's facility if a similar failure of the tension spring occurs. Licensees are requested to evaluate the history of inspections, maintenance practices, and circuit breaker operating cycles for K-Line breakers, and racking cycles for HK breakers to determine if the circuit breaker spring should be replaced immediately or at the next convenient maintenance opportunity. ABB recommends that any suspect spring with greater than 1,400 operating cycles be replaced as soon as possible. Currently ABB is determining the affected licensees and will notify them on or about March 30, 2009. * * * UPDATE FROM K. WELBORN TO P. SNYDER AT 0759 ON 3/16/2009 * * * ABB updated the original report by providing a list of affected customers. Notified R1DO (DeFrancisco), R2DO (Nease), R3DO (Lara), and R4DO (Hay). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2009-03-11
44895 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2009-03-09 | 2009-03-11 14:00 | 2009-03-11 | AGREEMENT STATE REPORT - PROSTATE BRACHYTHERAPY OVERDOSE "The Wisconsin Radiation Protection Section (RPS) was notified on 3/10/09 of a possible medical event that occurred on 3/9/09. The medical event occurred at Lombardi Cancer Center, which is affiliated with Aurora Health Center in Sheboygan (RML #117-1022-01). "The treatment was a permanent prostate brachytherapy implant using I-125 seeds. The intended total dose was 107 Gy and the patient was administered a total dose of 144 Gy. The overdose was discovered on 3/9/09, following review by the dosimetrist. "The patient was notified on 3/10/09. The referring urologist and the patient's primary care provider were also notified. "RPS has had telephone communications with the RSO and the Authorized User (AU) and has requested additional documents. The RSO will be unavailable (out-of-town). A team of RPS staff will be conducting a site visit at the facility when the AU returns." Wisconsin Radiation Protection Section Event Report ID Number: WI090003. An on-site investigation is planned by Wisconsin Radiation Protection Section beginning 3/12/09. A follow-up report will be issued after the investigation is completed. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2009-03-17
44894 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-03-06 14:40 | 2009-03-06 17:06 | 2009-03-06 | OFFSITE NOTIFICATION DUE TO GASOLINE SPILL "At 1440 a gasoline spill occurred while filling a company vehicle from a mobile gasoline truck. The auto-fill valve failed to shut off immediately when the gas tank was full and sprayed / spilled a small quantity (< 1 gallon) of gasoline on the ground. The spill was immediately terminated. This gasoline travelled to the nearest storm drain via water from melting snow. The Operations department was notified at 1445. Initial investigation revealed that the next storm drain in line to the river from the affected storm drain had significant water flow through it from the melting snow and no sheen was observed. There was also no oil sheen visible in the Delaware River. Based on the available indications, a 15 minute report to the State of New Jersey was completed at 1458 in accordance with the Hope Creek Event Classification Guide. The National Response Center was also notified at 1600. "Spill recovery actions are in progress and expected to complete before the end of the day. The NRC Resident Inspector has been informed. Plant operation was unaffected, no safety systems were impacted." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-06
44893 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-03-05 12:00 | 2009-03-06 10:47 | 2009-03-23 | UNDERDOSE TO PATIENT DIFFERS >20% OF INTENDED DOSE The following was provided by the state via e-mail: "Incident is a Medical Event per 15A NCAC 11.0364(a)(1)(A) where the EDE [effective dose equivalent] exceeds 5 Rem, and the total dose delivered differs from the prescribed dose by 20% or more. "[This incident] occurred during the use of Y-90 TheraSpheres. It appears that the TheraSpheres became stuck in the source vial, and the entire dose could not be administered to the patient. This resulted in a 26.4% underdose to the patient. The licensee is investigating why the Medical Event occurred. The Agency [NCDENR] has requested that the licensee submit the source vial lot or batch number in the report to assist in the determination if it may have been a manufacturing error." * * * UPDATE FROM JAMES ALBRIGHT TO JOE O'HARA VIA E-MAIL ON 3/20/09 AT 1715 * * * "We were unable to obtain complete administration of the Y-90 TheraSphere dosage even after repeated flushes of thee dosage vial. The unadministered dosage appeared to remain in the dosage vial. Proper administration protocol was followed, and included four flushes of the vial. Two attempts were made to agitate and remove the remaining material by inverting the vial. The inversions were not completely successful at removing the remaining dosage. "The decision was made to stop the administration after four flushes since the previous inversion and flush did not lower the dosimeter readings (a dosimeter is mounted on the delivery device which serves as an indicator of relative activity remaining in the dosage vial). "The prescribed dosage was 44,7 mCi. It was estimated that [about] 32.9 mCi of the prescribed dosage was administered (73.6%). The intended dose to the right lobe of the liver was 120 Gy. The actual delivered dose to the right lobe was [about] 88.3 Gy. Although the other lobe of the liver (left) will be treated, there are no plans at this time to treat the right lobe again. "MDS Nordion is conducting an investigation of this event. If deemed necessary upon completion of their investigation, supplemental procedures or recommendations will be provided to prevent further events of this type. Manufacturer representatives will be on-site on March 19, 2009 for further evaluation and follow-up. The TheraSphere dosage lot number was 9990019." Notified R1DO (J. Dwyer) and FSME EO (L. Camper) A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-03-10
44892 | 0 | EDLOW INTERNATIONAL |  |  |  |  | 2009-03-05 13:00 | 2009-03-05 13:44 | 2009-03-09 | INDUSTRIAL SHIPPING INCIDENT CONTAINING UF6 (URANIUM HEXAFLUORIDE) NRC Operations Center was notified by the Vice President for Operations at Edlow International of a marine incident at Dundalk Marine Terminal in Baltimore, MD. While offloading a flat rack containing UX30 protective overpacks with type 30B cylinders containing uranium hexafluoride from the MV Atlantic Conveyor, the rigging gear failed and the rack dropped onto the pier on top of another flat rack containing UX30 type 30B cylinders. There is no indication of a leak or release at this time. There were no injuries. Surveyor is at the scene. * * * UPDATE FROM FRANCHONE OSHINOWO TO JOE O'HARA AT 1640 EST ON 03/05/09 * * * Edlow confirms no material spill or damage to the packages. Damage was confined to the flat rack itself. Contrary to what was reported earlier, the mishap occurred onboard the vessel and NOT on the pier. Preliminary indications are that the spreader used to lift the flat rack was not engaged on all four lifting points prior to the lift commencing. Notified R1DO (Hansell), R2DO(D. Rich), NMSS EO(M. Tschiltz), and FSME EO (McConnell). * * * UPDATE FROM FRANCHONE OSHINOWO TO PETE SNYDER AT 1055 EST ON 03/06/09 * * * Upon inspection of the shipping containers on land, Edlow personnel have verified that only cosmetic damage was caused to one flat rack by the mishap. The highest radiation readings on contact with the containers were 0.5 millirem/hour which were within expected levels. Notified R1DO (Hansell), R2DO (Rich), NMSS EO (Tschiltz), and FSME EO (McIntosh). * * * UPDATE FROM FRANCHIONE OSHINOWO TO PETE SNYDER AT 1139 EDT ON 03/09/09 * * * Edlow stated that the information put into the last update above was incorrect. The previous update should have read that there was only cosmetic damage to one overpack however one flatrack was rendered unusable. Notified R1DO (Dimitriadis), R2DO (Rich), NMSS EO (Tshiltz), and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | MD | TRA | [5 empty] | 0 | 2009-03-06
44891 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2009-03-04 14:40 | 2009-03-04 15:53 | 2009-03-04 | RELIEF VALVE FAILURE RESULTS IN TRITIUM AND CESIUM SPILL "At 1100 on March 3rd, 2009 the Main Control Room received a report from the Health Physics Shift Supervisor that 1-BR-RV-114B ( 'B' PG tank heater relief valve) was relieving to the RCA yard near the Primary Grade (PG) tanks. At 1115 an operator confirmed the initial report, stating the relief valve appeared to be full open and relieving at approximately 20 gallons per minute. 0-AP-35.01 (Radioactive Liquid Release Control) was then entered and executed. At 1120 the PG line was then isolated by closing isolation valves, thereby stopping the release. "The release amount was then determined per 0-AP-35.01. Using the tank level initial indication of 87.5% taken on operator rounds at 1050 and a final level indication of 87.25%, approximately 450 gallons of water was released. This volume of water coincides with the initial report of an approximate 20 gpm release rate over the 20 minute duration of the event. "A sample of the water released was evaluated for tritium and cesium as part of the Nuclear Energy Institute (NEI) Ground Water Protection Initiative. Sample analysis results showed that tritium concentration was 4,810 picoCuries per liter and cesium concentration was 25.1 picoCuries per liter. These concentrations of tritium and cesium pose no threat to employees or the public. Even though the concentrations are well below reportable limits for groundwater, a spill or leak to soil greater than 100 gallons containing licensed material requires that notification be made per VPAP-2103S (Offsite Dose Calculation Manual) as part of our commitment to the NEI Ground Water Protection Initiative. "This leak has been contained and relief valve will remain isolated until repaired. "This notification is being transmitted due to Notification of Other Government Agencies under 10CFR50.72(b)(2)(xi). The Surry County Administrator was notified. The Senior NRC Resident, Virginia Department of Health, Virginia Department of Emergency Management and Virginia Department of Environmental Quality has or will be notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-04
44890 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-03-04 14:40 | 2009-03-04 15:19 | 2009-04-30 | GLOVEBOX OVERFLOW DRAINS MAY BE INADEQUATE TO PERFORM THEIR SAFETY FUNCTION "Many gloveboxes in the processing areas are equipped with overflow drains to prevent solution from exceeding an unsafe depth. These overflow drains are sized to accommodate the credible flow rates into the associated gloveboxes. During the generation of set-point analyses for overflow drains in a new process area, questions arose regarding how the drain discharge flow rates are calculated. To resolve these questions, NFS performed field tests using a glovebox on 2/26/2009 and 2/27/2009. Initial results of these tests indicated that the discharge flow rates are sensitive to drain weir height and glovebox floor flatness. This caused NFS to question the ability of the drains to perform their intended function. NFS, therefore, generated a plant-wide list of all potentially affected gloveboxes and suspended operations in them on 2/27/2009. Uranium-bearing materials were removed from the gloveboxes and all of the affected gloveboxes were tagged out of service. Engineering evaluations of the affected gloveboxes were performed and proceeded through 3/4/2009. As a result of Engineering evaluations, it was determined that in some instances a single drain alone was not capable of maintaining a solution depth to within design parameters in some localized areas within the glovebox. Modifications are being made to the drains to restore their functionality. "There were no actual or potential safety consequences to the public or the environment. The potential criticality consequences to the workers were low due to the conservatisms included in the analyses." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1350 EDT ON 04/30/09 FROM RANDY SHACKLEFORD TO S. SANDIN * * * The licensee will issue a press release to summarize the results of NRC Special Inspection Report No. 2009-007. The licensee will inform the NRC Resident Inspector. Notified R2DO (Ernstes), NMSS (Bjorkman) and Fuels Grp via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | OFFSITE NOTIFICATION/NEWS REL | [8 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.74 APP. A | PART 70 APP A (c) |  |  | 0 | 2009-03-10
44889 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2009-02-19 | 2009-03-04 11:35 | 2009-03-04 | IMPROPERLY PACKAGED RADIOACTIVE MATERIAL The following was provided by the state via email: "A single Cs-131 Brachytherapy seed was put back into the 'mick' cartridge by Banner Baywood Medical Center in Mesa, AZ, - the medical customer and end-user - and then returned to the manufacturer, IsoRay, a Washington State seed manufacturing licensee. When the shipping container, holding the mick container, arrived at IsoRay, contamination was found on the inside of the shipping container but not on the outside. There was no damage to the shipping container. "While unpacking the seed, a technician noticed there was visible damage to the seed. The tech monitored the packing material and found contamination. The RSO determined that a few microcuries of radioactive material leaked onto the packing material. The remaining millirem of material was in the damaged source and the pig. No material was missing. IsoRay called Washington State, Office of Radiation Protection, and reported the event that day. "There was no contamination found at the customer's site. IsoRay's Radiation Safety Officer reported that the seed had been visibly damaged, as if sheared. This may have happened when it was returned to the mick container or when the mick cartridge was re-inserted into the pig. Since all the contamination was inside the shipping container, it is doubtful that any personnel exposure was received. "The cartridge was a Mick Radio-Nuclear Instruments, Inc catalog number 0216-DS. The SS&D registration for the seed is WA-1220-S-101-S." Incident Number: WA-09-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2009-03-09
44888 | -1 | KAKIVIK ASSET MANAGEMENT, LLC |  |  |  |  | 2009-03-03 13:06 | 2009-03-03 19:47 | 2009-03-04 | FAILURE TO FULLY RETRACT SOURCE OF RADIOGRAPHY CAMERA Radiography technicians were performing pipeline corrosion shots on piping in the North Slope of Alaska when they inadvertently locked the source outside of the shielded position in the camera while retracting the source. The technicians were using an Industrial Nuclear Corporation (INC) IR-100 camera which contains a nominal 120 Curie (original strength) Ir-192 source. When the technicians realized what had occurred, they immediately cordoned off the area and requested help. A trained camera technician arrived and, after shielding the source, was able to manipulate the key lock and retract the source into the safe (shielded) position. The highest radiation reading observed behind the camera was 40 mR/hr. Exposures to all personnel involved in the recovery of the source was less than 20 mR. Since the radiography was being performed in a remote location, there was no chance of exposure to any members of the general public. Currently, the camera has been removed from service and is being sent to INC for inspection and maintenance. * * * RETRACTION FROM KEENAN REMELE TO JOE O'HARA VIA E-MAIL ON 3/4/09 AT 1443 * * * "After receiving all the reports by the parties concerned it was not a malfunction of the exposure device that caused this event. The event occurred due to snow and ice build up in the locking mechanism and the radiographer turning the key inadvertently. "This report will be forwarded to Region IV." Notified R4DO (Proulx) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-03-03
44887 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-03-03 | 2009-03-03 15:32 | 2009-03-03 | DEGRADATION OF ITEM RELIED ON FOR SAFETY (IROFS) "Area F is part of the solvent extraction uranium recovery process. The solvent extraction process removes usable uranium and strips out impurities from the solution. An organic solvent and nitric acid are used as part of this process. Column-0F13 is a strip column which has organic solvent flowing into the bottom and usable uranium/nitric acid entering from the top. After passing down through the solvent, the nitric acid exits Column-0F13 from the bottom, into feed Column-0G04. Column-0G04 then feeds into evaporator Column-0G05. If solvent were to enter Column-0G05 and begin reacting with the heated nitric acid while the system was closed (i.e., no vent relief) then a potential overpressurization or 'red oil' accident could occur. The scenario assumes that the reaction continues (self-heating) even though the heaters are shut off. "IROFS FAF-19 consists of flow switch FS-0F13, located in Column-0F13, which is interlocked to PUMPMT-0F19. This IROFS is in place to prevent a red oil accident by isolating organic solvent in-flow to evaporator Column 0G05 (via feed Column 0G04) upon loss of solvent-nitric acid interface in strip Column 0F13. If flow switch FS-0F13 senses loss of Column 0F13 interface, PUMPMT-0F19 shuts off which stops flow into Column 0G04 and thus into Column-0G05. "The equipment associated with IROFS FAF-19 is designated as Safety Related Equipment (SRE) and is functionally tested monthly. The regularly scheduled SRE Test was performed on March 3, 2009, and the purpose of the test is to demonstrate that the flow switch will fall when interface is lost and thus will shut off PUMPMT-0F13. The test failed because the flow switch did not fall, so the pump did not stop (PIRCS Problem #17584). Though there are defense in depth factors such as procedural requirements for operators to verify that no solvent is present in feed Column-0G04 prior to operation of evaporator Column-0G05, it was determined that IROFS FAF-19 was degraded and that the performance criteria of 10CFR70.61 were not met. "IROFS FAG-12 is an open vent that is credited as an additional control that is in place to prevent overpressurization due to self-heating. However IROFS FAF-19 is also required to be available in order to the performance criteria. "Previous SRE testing of the flow switch in January 2009 identified a potential problem with the flow switch sticking. As follow-up to that occurrence, the area process engineer reduced the SRE testing frequency from semi-annual to its current frequency of monthly in order to provide better indication if a problem was developing. Area F is currently in a safe condition and is operating under approved compensatory measures." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2009-03-05
44886 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2009-03-02 11:35 | 2009-03-02 13:02 | 2009-03-07 | WEATHER RELATED LOSS OF AUTOMATIC NOTIFICATION SYSTEM SIRENS "Sixteen of seventy three ANS [Automatic Notification System] sirens are inoperable for failure to pass the weekly growl test. The following sirens that are OOS are located in Calvert County (9 of 50 sirens), St. Mary's County (5 of 17 sirens) and Dorchester County (2 of 6 sirens)." The failures were most likely due to the weather conditions. The licensee has notified the local governments. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0750 EST ON 03/07/09 FROM BRUCE SHICK TO S. SANDIN * * * The licensee is updating this report to show that all sirens were restored to service as of 1000 EST on 3/6/09. The licensee informed the NRC Resident Inspector. Notified R1DO (Hansell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2009-03-02
44885 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-03-02 09:15 | 2009-03-02 12:57 | 2009-03-02 | ONSITE FATALITY "A contract employee associated with the Unit 2 refueling outage died this morning from an apparent heart attack. The death was not the result of any industrial safety issue and did not occur in a contaminated area. The individual was treated by the onsite first responders who administered CPR and AED (automatic external defibrillator). He was transported via ambulance to Dosher Memorial hospital where he was pronounced dead at 0915." "OSHA is being notified of the event under the requirements of 29 CFR 1904." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-03-02
44884 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-02-27 | 2009-02-28 13:56 | 2009-02-28 | PERSONNEL CONTAMINATION FROM PACKAGE CONTAINING DOSIMETERS The following was received form the state via facsimile: "RHB [California Radiologic Health Branch] was informed on 2/27/09 that contamination was detected on 3 packages delivered on the 26th of February at Radiation Detection Company [RDC]. One RDC employee was contaminated with an unknown isotope who received the packages and placed them into the lab for scanning. It is not known if all 3 packages were contaminated or if only 1 was and it cross contaminated the other 2 at Radiation Detection Company. The contamination levels were low, around 100 cpm above background (Ludlum with a pancake). An approximate 10% efficiency is likely reasonably valid, yielding contamination of 1000 dpm per probe area. The resulting contamination level likely exceeded DOT's 2200 dpm/100 cm^2 acceptance criteria for shipments. "The contamination of the person who handled the packages was low (60 cpm) on her arm and clothes. REAC/TS [Radiation Emergency Assistance Center/Training Site] was contacted by the licensee and the contaminated person was decontaminated and her clothes were placed in a drum with the package material and decon supplies and liquids that were used for other decontamination efforts for later inspection if necessary. Nasal smears were negative with regards to contamination. The minor contamination on this person was significantly below levels that would cause negative health effects. "Two carriers were involved in the 3 packages. One carrier's package originated in San Diego, CA and in Vermont, and another carrier's package originated from Honduras. It is possible that one package was contaminated at the shipper's facility, and cross contaminated the others at Radiation Detection Company. It is also possible that 1 or 2 of the packages was cross contaminated in the shipment stream, and the other 1 or 2 were subsequently cross contaminated at Radiation Detection Company. The 3 facilities that shipped the dosimetry badges will be contacted to check their respective facilities. "Radiation surveys using alpha, beta, and gamma, and some gross wipes were conducted during the evening of 2/27/09 on the driver and the carrier's truck used to deliver 2 packages to RDC yesterday. The surveys were negative. All readings were at background. Consequently, the carrier's vehicle that delivered one international package from Honduras is suspect regarding the contamination. [The State of CA] has not been able to get the information from that carrier regarding the truck or driver who made the delivery. [DELETED] is also the RSO for one of the carrier's and he is also working on getting the carrier's info to set up some surveys. "Radiation Detection Company appears to have discarded the contaminated packaging, so it may be difficult to ascertain which of the above scenarios occurred based on the contamination levels (or nuclides) on the packaging." CA (5010) Number: 022709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-03-04
44883 | -1 | UNION HOSPITAL INC |  |  |  |  | 2009-02-26 | 2009-02-27 15:32 | 2009-03-26 | POTENTIAL LEAKING I-125 PROSTATE CANCER THERAPY SEED A patient was being treated for prostate cancer. After a treatment of (15) I-125 seeds, the magazine used to inject the seeds into the patient was surveyed and the survey indicated that the magazine was contaminated. Initially, the staff believed that a seed may have been stuck inside the magazine. However, upon disassembly the staff determined that the magazine was empty. The prostate cancer therapy treatment continued without incident. The patient was x-rayed, and all seeds were accounted for. A survey of the room, instruments, and packaging material revealed no loose surface contamination. The contamination is confined to the inside of the magazine. The staff believes there are two potential scenarios to explain the contamination inside the magazine: (1) the seeds had external contamination when placed inside the magazine, or (2) during the autoclave a weak weld failed and the seed began to leak. If a seed is leaking iodine into the patient, then if left untreated, the patient could potentially receive a dose of 50 Rem to the thyroid gland. A physician has prescribed a treatment to block uptake to the thyroid, and the blood and urine samples thus far are inconclusive in determining if iodine is leaking into the patient. I-125 seed activity is .302 millicuries per seed. The patient is aware of the issue. Thyroid scans and urine assays will continue for the next four weeks to determine if radioactive iodine is present in sufficient quantities to indicate a leaking seed. * * * RETRACTION PROVIDED BY DEAN TAYLOR TO JASON KOZAL 0N 03/26/09 AT 1125 * * * The licensee's theory is that the seed in question had a bad weld that was not realized until the seed was exposed to the heat sterilization process. This is due to the fact that there was no contamination present prior to the sterilization process. The licensee completed multiple thyroid scans and blood work on the patient with negative results. Additionally, the licensee performed multiple urine assays with negative results. The patient will continue with potassium iodine treatment for the next 2 years to minimize thyroid uptake. Based on this information the licensee is retracting this event. Notified the R3DO (Peterson) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2009-03-05
44882 | 0 | USAF |  |  |  |  | 2009-02-04 | 2009-02-27 12:52 | 2009-02-27 | LOST NICKEL-63 SOURCE "Description of the material involved, including kind, quantity, and chemical and physical form: GE Vapor Tracer 2 detection system (SN 07024933861). Approx. 8 mCi Nickel-63 (#09-3896). "Description of the circumstances under which the loss occurred: On 29 Jan 09, during a routine semi-annual audit, the Andrews Air Force Base (AAFB) Radiation Safety Officer (RSO) identified the missing device used by the Aerial Port Squadron (APS). The device was used to screen luggage for explosives/narcotics. A review of records indicated the device was sent to the Defense Reutilization and Marketing Service (DRMS) through base supply by the user on 1 Jul 08. On 4 Feb 09, the RSO contacted the USAF Radioisotope Committee (RIC) to report the event. NOTE: The RSO is a member of the Bioenvironmental Engineering (BE) office. "An investigation shows the APS (user) contacted the BE office on 24 Jan 08 and received instructions for disposing of the device via the DRMS. A technician from the BE office certified the device did not contain any hazardous material and would be suitable for turn-in to the DRMS. On 25 Jan 08, an officer from the BE office (not the RSO) sent a letter to the user affirming the technician's assessment. The technician and officer had no knowledge the device contained radioactive material (RAM). No RAM warning labels were visible on the exterior surface of the device. "During the investigation of the loss of material, the RSO found the RAM warning label was located under the battery pack and not visible. Being unfamiliar with the device, the technician evaluated it for chemical hazards (and found none) but didn't consider radiological aspects. "After review of all transfer/receipt and inventory documents over a span of three years, the RSO found no evidence that another event of this type had occurred at AAFB. This is an isolated event. Air Force Instruction 40-201, Managing Radioactive Material in the U.S. Air Force, expressly prohibits GLDs from being sent to the DRMS. "A statement of disposition, or probable disposition, of the material involved: The investigation by the RSO revealed the device left AAFB and traveled to DRMS at FT Meade, MD and then to the DRMS at Mechanicsburg, PA. It was sold to a de-manufacturing contractor, Global Investment Recovery, where it was shredded for scrap. The scrap was sold through the DRMS scrap sales partner, Government Liquidation, LLC. It could not be tracked further. "Exposures of individuals to radiation, circumstances under which the exposures occurred, and the possible total effective dose equivalent to persons in unrestricted areas: Nickel-63 is a pure beta emitter with a 100 year half life. The ingestion annual limit on intake (ALI) is 9 millicuries (mCi). Ingestion of the source would not exceed the ALI and the committed effective dose equivalent (CEDE) would be less than 5 rem. The (Class D) inhalation ALI is 2 mCi. Using the EPA's inhalation dose conversion factor of 3.1 millirem/microCuries, the CEDE for 8 mCi of Ni-63 (Class D) is 25 rem. The size of the source is approximately that of a pencil eraser. It is unlikely an industrial shredder could have pulverized it to such an extent so as to present an inhalation hazard. The possible total effective dose equivalent to persons in unrestricted areas is presumed to be less than 1% of the ALI. "Actions that have been taken, or will be taken, to recover the material: The RSO tracked the device from AAFB (1 Jul 08) to the DRMS at Fort Meade, MD and to the DRMS at Mechanicsburg, PA (7 Aug 08). It was shredded by Global Investment Recovery, the DRMS de-manufacturing contractor and sold as scrap through the DRMS scrap sales partner, Government Liquidation, LLC. It could not be tracked further. "Procedures or measures that have been, or will be, adopted to ensure against a recurrence of the loss of material: The RSO has determined the root cause of the event to be inadequate training. The users of the device and the BE office did not, collectively, possess information about GL material. The RSO had not shared his knowledge about the material with the BE office. "The following corrective measures have been taken: Photographs of GLDs will be taken and provided to the BE staff, the users, base supply and DRMS. If warning labels are considered to be inadequate, new labels will be affixed to GLDs to alert individuals that RAM is present. The RSO, working with BE staff, has initiated awareness training for users of GLDs. Such will be conducted annually. Users will be required to possess binders in which to maintain information about their devices (e.g., safety data sheets, owner's manuals, policy, pictures, inventory, leak test results, contact numbers, etc.). "The RSO has informed management of the event. Lessons learned will be passed down to targeted audiences. Andrews AFB instructions will be evaluated for gaps in policy and strengthened as necessary. The means for purchasing and transferring GLDs back to the manufacturer will be addressed in detail. "The RIC Secretariat has contacted the GE Radiation Safety Officer regarding the placement of the radiation warning label. The RIC Secretariat informed Ms. Rachel Browder, NRC Region-IV, about the loss of a GLD on 10 Feb 09." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-02-27
44881 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-02-27 05:00 | 2009-02-27 04:37 | 2009-02-27 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT OF SERVICE "The Perry Nuclear Power Plant will be taking the Plant Computer out of service for scheduled maintenance which will take ERDS out of service. From 0500 hours EST on February 27, 2009 for approximately 15 hours, personnel will be performing inspection and cleaning activities on the Plant Computer power center panel. During the planned maintenance, the Safety Parameter Display System (SPDS) and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Private Branch Exchange, the Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. A follow-up notification will be made when the maintenance activities are completed and the equipment is restored. "The NRC Resident Inspector has been notified." * * * UPDATE FROM TOM MORSE TO JOE O'HARA AT 1910 EST ON 2/27/09 * * * The Perry Plant computer and the ERDS have been restored to service as of 1845 EST this evening. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-27
44880 | 0 | STATE OF CONNECTICUT |  |  |  |  | 2009-02-26 11:45 | 2009-02-26 16:33 | 2009-02-26 | ABANDONED DENSITY GAUGE DISCOVERED "Fabric Trends International, 55 Lathrop Rd, Plainfield, Ct. 06374. "On Thursday the 26th of Feb. at 1145 hours, [I was] notified of an abandoned density gauge at the above facility. [Another] DEP Inspector discovered the device while arriving for an inspection. He did not know the facility was closed. While there with the Owner of the building he discovered the device. He turned over information to [another inspector] who notified Supervision. I called the Owner, after getting information on the registration and the Owners cell phone number. "At 1300 hours, I met [the Owner] and he led me to the device that was stored in a large plywood box. [The Owner] told me he used to own the business but sold all the equipment to another party. He will send that info to [DEP] on Friday morning. [The Owner] was very familiar with the instrument and stated that it was part of the material he sold from the facility. "I surveyed the device using a Mod. 3 with 44-38 gamma probe and nothing above background was noted (0.02 mR/hr). I frisked the outside surfaces of the device with the 44-9 probe and did not note any counts above background. I took 3 swipes and counted them and found nothing above background on them. The window on the detector head was broken and this area was part of the head swipe. "There were no markings found that indicated that the device contained RAM [Radioactive Material]. The only indication was on a DYNO Tape found on the front of the device's meter housing. It stated Beta Gauge. The device info is as follows: "Mahlo Gravimat FM-1-7a, Type FM1R/7AK, JAHR 1.84/110 volt, Funkentstorgrad G, FABR.NR. 6271/12/709, 1.6 amp, 50/60 hz. "Detector Head, Ser. No. 6270/710, Stamped on case 3.627050/4. "[The Owner] stated his lawyers are trying to contact the party that bought out the equipment to get them to take possession of the equipment. I contacted [my supervision] and discussed my findings. The current registration listed four beta devices with Kr 85 and two Gamma devices with Am 241. This device was not on the registration. "I briefed [the Owner] that as the owner of the property, he was responsible for the device. I suggested that he seal the box with wood screws and that he insure that the device was not moved or handled. I stated that he was responsible to insure the device was not stolen or lost." The state plans a follow-up inspection at the site tomorrow. The State of Connecticut Incident Number for this event is 09-026. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-02-26
44879 | 0 | IDAHO DEPT OF ENVIRONMENTAL QUAL |  |  |  |  | 2009-02-24 08:30 | 2009-02-25 17:28 | 2009-02-25 | FOUND ORPHAN SOURCE - SUSPECTED WELL LOGGING SOURCE On 2/24/09 around 0830 MST, an orphaned source was found at Pacific Recycling, 3575 Highway 30 West, Pocatello ID 83204, in Bannock county. The source was observed from a distance on a dirt pile on the back part of the facility, and was not approached by Pacific Recycling personnel. Expected exposure to Pacific Recycling personnel is zero. Pacific Recycling does not hold an NRC license. Idaho Department of Environmental Quality responded. The senior health physicist determined by spectral analysis that the source was Cs-137. No plates or identifying markings remain on the source, but it is suspected to be a well logging source. It has an on-off shutter. Radiation levels for the source are 2 mrem on contact except for the plate believed to be the source access cover, which is 22 mrem on contact. There was no removable contamination. The source was quarantined on the site. Disposition will be determined. The senior health physicist has consulted with regional personnel, and a regional inspector will respond to the site. The curie content of the source is unknown. However well logging Cs-137 sources typically contain less than 2.7 Curies which is a "Less than Cat 3" level. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-02-25
44878 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2009-02-25 | 2009-02-25 16:51 | 2009-03-06 | LICENSED EMPLOYEE TESTS POSITIVE FOR ALCOHOL A licensed employee had a confirmed positive test for alcohol during a for-cause fitness-for-duty test. The employees access to the plant has been suspended. Contact the Headquarters Operations Officer for details. The licensee will inform state/local agencies and has informed the NRC Resident Inspector. * * * UPDATE PROVIDED BY JASON WEATHERSBY TO JASON KOZAL ON 03/06/09 AT 1511 * * * The licensed employee's for-cause fitness-for-duty test also confirmed positive for marijuana. The employee's access to the plant has been revoked. Notified the R2DO (Rich). The licensee will inform state/local agencies and has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2009-02-25
44877 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-02-25 | 2009-02-25 12:33 | 2009-03-26 | FAILURE TO REPORT CRIMINAL CHARGES A non-licensed non-supervisor contractor had non-reported criminal charges. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * RETRACTED ON 3/26/09 AT 1719 FROM M. MCNEELY TO P. SNYDER * * * This one hour event report is retracted per the guidance contained in Regulatory Guide 5.62. This event has been determined to be a 'logged only' report. The employee concerned is now eligible for nuclear access. Notified R2DO (Vias) and 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-02-25
44876 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-02-25 | 2009-02-25 11:18 | 2009-03-04 | POSSIBLE OVER EXPOSURE DURING RADIOGRAPHY "Employee's TLD recorded an overexposure of 6.381 rem whole body deep dose; shallow was 6.061 rem. Date [exposure occurred] was between 10 Jan 2009 to 9 Feb 2009. [The] affected employee claims he left his shirt with TLD in area where radiography was being performed. Pocket dosimeter reading was no more than 20 mr. Other employees who worked with him during [the] same time period 10 Jan 2009 to 9 Feb 2009 have no excessive exposures. RSO calculates dose should be approximately 205 mr during month as per records. RSO believes [this is] not an occupational overexposure. Employee's TLD report received today 25 Feb 2009." Isotope(s): Ir-192 from two (2) separate radiography cameras with activities of 24 Ci and 77 Ci. State radiation personnel plan to investigate the event. Florida incident number FL09-020. * * * UPDATE AT 0730 EST ON 03/04/09 FROM STEVE FURNACE TO S. SANDIN * * * The State of Florida is updating this report to provide the results of their onsite investigation: "[The] Tampa office investigator performed an onsite interview, and concurred with [the] RSO findings. [The] Owner's corrective actions consists of training employees in personnel monitoring, and procured a belt pouch for holding [the] TLD and dosimetrv. No further action to be taken on this incident." Notified R1DO (Hansell) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-03-02
44875 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2009-02-10 | 2009-02-25 09:50 | 2009-02-25 | UNPLANNED TRITIUM RELEASE DURING INCINERATION "This report is made under 10 CFR 20.2201(a)(1)(ii). A loss of permitted material by Edward Hines Jr. VA Hospital in Hines, Illinois, became known on February 10, 2009. Approximately 54.6 millicuries of hydrogen-3 were released in animal research wastes handled as non-radioactive over a period of 15 years (1994-2008). The maximum amount released in any one year was 12.8 millicuries. These wastes were processed by incineration at off-site facilities. The activities that generated the affected wastes ended in March 2008. Hospital staff will review disposal practices for compliance before allowing similar activities. "A written report for this event will be submitted to NRC Region III within 30 days of making this telephone notification. We have discussed with event with our NRC Project Manager (Cassandra Frazier, NRC Region III). "Additional information: "Department of Veterans Affairs holds NRC License No. 03-23853-01VA, a master materials license. Permits are issued under the license to Veterans Health Administration facilities. The permit number for the facility involved in these medical events is VHA Permit No. 12-01087-07. National Health Physics Program makes required notifications to NRC." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-02-25
44874 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2009-02-25 08:35 | 2009-02-25 09:33 | 2009-02-25 | FITNESS FOR DUTY - CONTROLLED SUBSTANCE FOUND IN PROTECTED AREA Actual introduction of contraband into a vital area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | MD | POW |  | 26.719 |  |  |  | 0 | 2009-02-25
44873 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-02-23 | 2009-02-24 20:58 | 2009-02-24 | AGREEMENT STATE REPORT - PARTIALLY LOST AM-241 SOURCE The following was provided by the state via email: The licensee discovered a damaged Am-241 alpha source during a routine sealed source inventory and leak test on Monday February 23, 2009. A pinhole leak was discovered through the source active area. After further assessment on February 24, 2009, it was determined that more than half of the source activity cannot be located. The Am-241 source was manufactured by North American Scientific (model # CAL2702, source #67250) with an activity of 845.8 nCi (nanocuries) as of October 1, 2005. Currently there is 160 nCi remaining on the Am-241 source and 160 nCi of contamination on the sponge insert in the source container. 521 nCi of the activity cannot be accounted for. The licensee has performed preliminary contamination surveys of the source storage area, source use area, and the common lab area. The survey were performed using GM survey meters with pancake detectors and wipes counted with a liquid scintillation counter. No significant contamination was found. The licensee will perform additional surveys and continue to investigate the cause of this incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-02-27
44872 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-10-06 12:00 | 2009-02-24 16:23 | 2009-03-26 | FAILURE TO SELF REPORT CRIMINAL CHARGE A non-licensed non-supervisor contractor had a non-reported criminal charge. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATED ON 2/25/09 AT 1508 EST FROM MARK McNEELY TO KARL DIEDERICH * * * The event is updated to be reported under 73.71 rather than 26.719. Informed R2DO (Randy Musser) and 73.71 Group via e-mail. * * * RETRACTED ON 3/26/09 AT 1719 FROM M. MCNEELY TO P. SNYDER * * * This one hour event report is retracted per the guidance contained in Regulatory Guide 5.62. This event has been determined to be a 'logged only' report. Notified R2DO (Vias) and 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-02-24
44871 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2009-02-23 10:30 | 2009-02-23 18:13 | 2009-02-23 | AIRBORNE CONTAMINATION OVER THE LIMIT IN THE FEED MATERIALS BUILDING "An unplanned contamination event occurred on February 22, 2009. This is a reportable event in accordance with 10 CFR 40.60 paragraph (b)(1) based on an unplanned event that results in additional radiological control being required for more than 24 hours. The 24 hour period ended at 10:30 on February 23, 2009. The additional control imposed was wearing a half face respirator in the 6th floor of the Feed Materials Building. The Feed Materials Building converts uranium ore concentrates into uranium hexafluoride. Air samples from the 6th floor were analyzed and the airborne radioactivity average was approximately 6.73 e-11 microCi/ml. The airborne radioactivity exceeded the MTW [Honeywell Metropolis Facility] action level of 30% of a DAC (5.00 e-11 microCi/ml). One DAC is 1.7e-10 microCi/ml. Uranium tetrafluoride (green salt) was the material that was airborne on the 6th floor. A release point could not be determined. The air samples indicate that the air emission occurred on the northwest side of the building likely to be from a release of material from the green salt elevator and conveyor system." See similar event number 44857 on 2/17/09. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2009-02-23
44870 | 0 | BAYER CROPSCIENCE |  |  |  |  | 2009-02-10 12:00 | 2009-02-23 14:56 | 2009-02-23 | PROBABLE LOSS OF 3.3 mCi C-14 IN TRANSIT A package of 3.3 mCi of solid form C-14 was picked up at the Kansas City, MO facility by courier Towne Air on February 6, 2009, for shipment to Held & Associates, in Chicago, IL, for further shipping to Bayer Cropscience's research site in Wuppertal, Germany. It has not been received by Held & Associates. On February 10, the licensee inquired with Town Air regarding tracking information. Recent response indicates that recovery of the shipment and its material is considered unlikely. This quantity is more than five orders of magnitude less than the IAEA D value. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-02-23
44869 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-02-23 04:06 | 2009-02-23 05:46 | 2009-02-26 | INADVERTENT ACTUATION OF THE TURBINE DRIVEN AUXILIARY FEEDWATER PUMP "The Turbine Driven Auxiliary/Emergency Feedwater pump auto started when power was lost to the steam admittance solenoid valves. Additional feedwater to the steam generators caused an increase in power; in response, turbine load was manually decreased. At no time were any power limits exceeded. Power level is currently at 87% and stable." Maximum power, as determined by core delta temperatures, did not exceed 100%. The licensee has notified the NRC Resident Inspector. * * * UPDATED AT 1048 EST ON 02/26/09 FROM JOEL HOWARD TO S. SANDIN * * * "Event Report 44869 Retraction: "On February 23, 2009, McGuire Nuclear Station notified the NRC of an inadvertent actuation of the Unit 1 Turbine Driven Auxiliary/Emergency Feedwater (TDAFW) Pump (reference Event Report 44869). This event occurred when power was removed to the steam admittance solenoid valves for the Unit 1 TDAFW Pump prior to isolating the steam supply to the pump. Removing power to the steam admittance valves caused them to fail open, starting the pump. As per the requirements of 10 CFR 50.72(b)(3)(iv)(A), this event was reported as a valid actuation of the Unit 1 TDAFW Pump. "Further evaluation of the event concluded that the actuation of the Unit 1 TDAFW Pump was not the result of a valid signal initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function provided by the pump. In addition, the actuation of the Unit 1 TDAFW Pump was not the result of an intentional manual initiation. Therefore, actuation of the Unit 1 TDAFW Pump represented an invalid actuation which is not reportable per the requirements of 10 CFR 50.72(b)(3)(iv)(A). Therefore, McGuire is retracting Event Report 44869. Note that McGuire will report this event in accordance with the requirements of 10 CFR 50.73. "The licensee has notified the Resident Inspector." Notified R2DO (Musser). | 87 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-02-23
44868 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-02-20 | 2009-02-20 16:53 | 2009-02-20 | AGREEMENT STATE REPORT - ABANDONED PET SCANNER AND ASSOCIATED SOURCES The following information was received via fax: "Licensee has gone bankrupt, is out of business and has abandoned a PET scanner and associated sealed sources. Sources will be in a pig in the hot lab. Items are in a locked building not accessible to anyone except the landlord. Orlando Inspection office will retrieve sources on Monday. "There are 3 Ge/Ga sources (10.65 mCi) and 2 Cs-137 sources (1 x 250 microCi and 1 x Unknown activity) ." FL Incident Report # FL09-019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-02-25
44867 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-02-20 11:55 | 2009-02-20 14:55 | 2009-02-20 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE The following information was received via fax: "The licensee was conducting an operational test of their thickness gauge at their office facility. Upon turning the gauge on the operational check revealed the thickness gauge shutter would not open. The manufacturer's service contractor has been notified and a service technician has been requested to visit and repair the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-02-25
44866 | 0 | EDAX, INC |  |  |  |  | 2009-02-18 | 2009-02-20 14:25 | 2009-03-12 | LOST CALIBRATION SEALED SOURCE OF FE-55 A 2 milliCurie sealed source of Iron-55, used for calibration, was misplaced and believed to be lost. The source (Mfg # C1-375) was stored in a pig in a locked cabinet in a secure lab. Inventory is taken daily, and the last time it was seen was 2/17/09. Licensee believes that a lab technician was working with the source and it accidently rolled off the desk into a trash container. Licensee has searched every possible area where it may have gone. The sealed source was in a plastic tube, and therefore the exposure to personnel is just above background. * * * UPDATE AT 1627 ON 3/12/2009 FROM BOB WESTERDALE TO MARK ABRAMOVITZ * * * The strength of the Fe-55 source was calculated to be 660 microCuries on 3/10/2009. Notified the R1DO (Dimitriatis), FSME (Mauer) and ILTAB (Whitney via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-02-20
44865 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-02-19 11:20 | 2009-02-19 18:40 | 2009-02-19 | INJURED WORKER TRANSPORTED TO OFFSITE MEDICAL FACILITY "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 19, 2009, at approximately 11:20 Mountain Standard Time (MST), an employee of Arizona Public Service (APS) was injured while working at the Palo Verde Independent Spent Fuel Storage Installation (ISFSI) which is considered to be a radiologically controlled area (RCA). The ISFSI is located within the owner controlled area but outside the plant's protected area. The ISFSI has been evaluated as having a very low probability for contamination, so administrative controls are used to allow workers access into the ISFSI and return to the appropriate Unit RCA egress point located in the protected area where personnel monitoring for contamination is performed prior to leaving the site. Upon exiting the ISFSI area, the individual was initially transported to the Palo Verde Medical Clinic to attend to the injury. Subsequently, the individual was transported to an offsite medical facility for further evaluation. The individual was not monitored for contamination prior to being transported offsite. The individual and the transporting vehicle were frisked offsite and found to be free of contamination. There were no exposures from licensed material and no consequence to the public or environment." Injured person was an employee of licensee. Employee was transported to the hospital via private owned vehicle. The NRC Resident Inspector was notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2009-02-19
44864 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2009-02-19 10:21 | 2009-02-19 11:52 | 2009-02-19 | UNUSUAL EVENT DECLARED DUE TO MAIN GENERATOR HYDROGEN GAS LEAK "An Unusual Event was declared at 1021 CST due to toxic, corrosive, flammable gasses in amounts that have or could adversely affect normal plant operations. Licensee estimated that a plume of hydrogen gas 20 feet high was leaking in the Turbine Building at the North Generator Bearing. Licensee entered EAL HU3.1. There was no release above normal operating limits (0.1 Mr/hr at EAB). No offsite response required. Gas is being dissipated via emergency degassing of Main Generator. Presently, the Main Generator degas has been completed and no flammable environments remain. The Unusual Event will stay in effect until the area is accessible to personnel, as evaluated by chemistry." There was no fire or personnel injury related to this event. The Plant was already in Mode 3 due to an earlier event requiring a Technical Specification Action 3.3.2.Q shutdown. The licensee has notified the NRC Resident Inspector, and local, state and other government agencies. No media press release was anticipated. * * * UPDATE FROM DAVID HURT TO JOHN KNOKE AT 1255 EST ON 02/19/09 * * * "The hazard was eliminated by 1055 on 2/19/2008. The Unusual Event was closed out at 1115. The state and counties (Callaway, Gasconade, Montgomery, and Osage) were notified of the event closeout at 1126. A news release will be made by Ameren Corporate Communications." The licensee has notified the NRC Resident Inspector. Notified R4DO (Powers), DHS ( Cassandra McKentry) and FEMA (Mike Eaches). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 4 | MO | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-02-19
44863 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2009-02-19 05:30 | 2009-02-19 10:07 | 2009-02-19 | POWER SUPPLY FAILURE RESULTING IN A TECH SPEC REQUIRED SHUTDOWN "The plant was operating in MODE 1 at 100% power. At 0228 on 2/19/09, a power supply to cabinet SA036D, Channel 1 of the Engineered Safety Features Actuation System (ESFAS) failed. As a result of the failure, both trains of control room ventilation isolation signal (CRVIS), containment purge isolation signal (CPIS), and fuel building isolation signal (FBIS) inadvertently actuated. The cause of the failure of SA036D is under investigation. Technical Specification (TS) Action 3.3.2.Q was entered which requires the plant to be in MODE 3 in 6 hours and MODE 4 in 12 hours. Load reduction began at 0530. MODE 2 was entered at 0750. MODE 3 was entered at 0817. "All systems functioned properly. "The NRC Resident Inspector has been notified." The licensee is replacing the entire power supply and will investigate the cause. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2009-02-19
44862 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2009-02-18 17:15 | 2009-02-18 18:06 | 2009-02-18 | 1-HOUR SECURITY REPORT RELATED TO POTENTIAL SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to the inadvertent release of Safeguard Information (SGI). Compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for details. The licensee will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-02-18
44861 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2009-02-18 13:45 | 2009-02-18 16:45 | 2009-02-18 | AGREEMENT STATE REPORT INVOLVING A STOLEN MOISTURE DENSITY GAUGE The following report was received from the State of Alabama via fax: "At 1:45 PM CST the Alabama Office of Radiation Control received a call from Qore, Inc. in Birmingham, Alabama (Alabama license No. 708). They reported that a CPN Model MC1DR (S/N MD30406940) had been stolen from the back of one of their trucks. The licensee indicated that the device case had been secured with 2 separate locked chains, but that they had been cut. The device had been stolen sometime during the morning or early afternoon while the truck was parked at an employees residence in Center Point, Alabama. The licensee is filing a report with local law enforcement. They are also sending an information flyer to area pawn shops, and will issue a message to the media regarding the device, and offer a reward for information leading to the recovery of the device. "This information is accurate as of 3:20 PM CST. Further information, including methods to prevent a recurrence, is forthcoming from the licensee." Alabama Incident # 09-08 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2009-02-23
44860 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-02-18 03:51 | 2009-02-18 08:03 | 2009-02-21 | TURBINE TRIP DUE TO POWER LOAD UNBALANCE SIGNAL ON MAIN GENERATOR RESULTING IN REACTOR SCRAM "At 0351 on 2/18/09, the Unit 1 reactor automatically scrammed due to actuation of the Reactor Protection System from a turbine trip due to a power load unbalance signal on the main generator. The cause of the power load unbalance signal was due to a generator neutral over voltage condition of which the cause is unknown and the investigation is continuing. All systems responded as expected to the turbine trip. One Safety Relief Valve (SRV) opened due to the reactor pressure transient, and then reactor pressure was automatically controlled by the Main Turbine Bypass valves. No Emergency Core Cooling System (ECCS), or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached, all expected containment isolation and initiation signals were received, and reactor water level is being automatically controlled by the feedwater system. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) for any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." All control rods fully inserted. The plant electrical system is in normal shut down alignment. No Diesel Generators started as a result of this event. There was no ECCS injection to the reactor vessel. * * * * UPDATE FROM RICKY GIVENS TO JOHN KNOKE AT 1828 0N 02/21/09 * * * * "Review of available data indicates that no Main Steam safety/relief valves (MSRVs) opened in response to the Unit 1 reactor scram on 02/18/2009. There were no indications of an open MSRV on any discharge tailpipe thermocouple or acoustic monitor. Initial indications of the discharge tailpipe thermocouples for MSRV (1-PCV-1-30) did indicate a slight increase in temperature (approximately 36 degrees F) as reactor pressure decreased, which resulted in the initial assumption of an SRV opening. However, this behavior is a classical indication of slight main seat leakage and system engineering believes this seat leakage is what the post scram data indicates. Utilizing multiple reactor pressure instrumentation responses, the peak reactor pressure was determined to be approximately 1130 psig which is 15 psi below MSRV 1-PCV-1-30 setpoint. Additionally, the rise in tailpipe temperature did not coincide with the peak pressure but was after pressure had lowered. Based upon a thorough review of this data and a better understanding of the timing of the temperature rise, it is now believed that the MSRVs performed as designed during the reactor pressure transient event. The initial determination that concluded an MSRV opened will be further investigated within the corrective action program; reference PER 164114." The licensee has notified the NRC Resident Inspector. Notified R2 DO (Charlie Payne) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-02-18
44859 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-02-17 11:00 | 2009-02-17 18:28 | 2009-02-17 | BOTH EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE AFTER REVIEW OF WORK BOUNDARY ISOLATION "At 1100 on 2/17/2009 with D5 Diesel Generator (A-Train EDG) out of service for planned maintenance, it was discovered that an isolation had been hung that inadvertently disabled the D5 Fuel Oil Storage Tanks Transfer Pumps. These transfer pumps provide the primary fuel oil supply to D5 EDG Day Tank and the secondary supply to D6 (B Train EDG) Day Tank. With D5 Fuel Oil Storage Tanks Transfer Pumps not functional, their ability to transfer fuel oil to the D6 Diesel Generator (B-Train EDG) Fuel Oil Storage Tanks was disabled. Although D6 had both of its primary fuel oil transfer pumps available with approximately 50,000 gallons of diesel fuel, this left PINGP Unit Two with less than the Tech Spec required 65,000 gallons available to maintain Unit Two EDG operability. Therefore, at 1100 on 2/17/2009 D6 EDG was declared inoperable. Thus, both trains of Unit 2 EDGs were inoperable (safety function was lost) for ~34 hours. 65,000 gallons fuel oil inventory is to ensure the EDGs have enough inventory to mitigate the probable maximum flood which would result in being unable to get new fuel oil on site for ~14 days. There is no flooding predicted per the National Weather Service Advanced Hydrologic Prediction Service. The observed level at Lock & Dam #3 is more than 12 feet below flood stage with river level decreasing the last four days. This isolation had been in place since 0129 on 2/16/2009. "At 1145 on 2/17/2009 the 21 and 23 D5 Fuel Oil Transfer Pumps were returned to service and D6 Diesel Generator was declared Operable." This did not affect Unit 1. The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-02-17
44858 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2009-01-28 | 2009-02-17 16:33 | 2009-02-17 | NOTIFICATION TO SC-DHEC CONCERNING EXCEEDANCE OF BIOLOGICAL OXYGEN DEMAND (BOD5) LIMIT "On January 28, 2009, the composite sample from our waste treatment facility analyzed by our NPDES certified vendor laboratory indicated that wastewater discharged from the Westinghouse Columbia plant (to Congaree River) during the 24 hour period contained 60.8 pounds of BOD5 (56 mg/l BOD5) which exceeded the Daily Maximum Permit Limit of 60 # of BOD5 per day. The daily average for BOD5 discharges during January was approximately 23.6 pounds per day and is within permit limitations (30 #/D). Other BOD5 results for the month were less than 12 # BOD5/day. "Following recognition of the problem on 2/3/09, Westinghouse immediately responded to evaluate the waste treatment facility including the sanitary package plant, the sanitary lagoon, process lagoons, and final discharge tanks. All systems were operating properly and producing clear effluent with no unusual odors or solids present. Waste treatment operations logs were inspected and no unusual problems were noted. All dissolved oxygen results for the month of January were greater than 10.0 mg/l indicating satisfactory performance of the wastewater treatment facility. Visual analysis of the entire waste treatment facility on 2/3/09 indicated that all processes were operating normally and no problems were being experienced. "Investigation samples for BOD5 were collected on 2/3/09 from process source locations prior to the final discharge. All precursor investigation BOD5 samples were analyzed to contain less than 11.0 mg/l BOD5. "Based on our information and discussions with [South Carolina - Department of Health and Environmental Control (SC-DHEC)], we are reporting the exceedance data, but believe the sample was anomalous (or contaminated) due to the lack of any elevated source of BOD5 (based on investigation samples) or process upsets noted in the entire waste treatment facility. "Westinghouse remains deeply committed to continuous compliance with all NPDES requirements." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2009-02-17
44857 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2009-02-16 10:30 | 2009-02-17 13:52 | 2009-02-17 | 24-HOUR REPORT INVOLVING AN UNPLANNED CONTAMINATION EVENT "An unplanned contamination event occurred on February 16th, 2009. This is a reportable event in accordance with 10CFR40.60 paragraph (1) based on an unplanned event that results in additional radiological controls being required for more than 24 hours. The 24 hour period ended at 1030 on February 17th, 2009. The additional controls imposed was wearing a half-face respirator in the basement of the Feed Materials Building. The Feed Materials Building converts uranium ore concentrates into uranium hexafluoride. Air samples from the basement were analyzed and the airborne radioactivity average was approximately 8.27 e-11 microCi/ml. The airborne radioactivity exceeded the MTW action level of 30% of a DAC (5.0 e-11 microCi/ml). One DAC is 1.7e-10. Uranium Tetrafluoride (green salt) was the material that was airborne in the basement. An elevator that is used to transport green salt to different levels of the Feed Materials Building was leaking around an inspection cover which caused the airborne radioactive material." The licensee attributes the contamination to a failed gasket. The airborne contamination was discovered during routine air sampling which is performed daily. There is no plan to perform personnel testing for uptake or ingestion at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2009-02-17
44856 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2009-02-17 10:00 | 2009-02-17 11:16 | 2009-02-17 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM DUE TO PLANNED MAINTENANCE "At 04:05 hours EST, on February 17, 2009, the Plant Process Computer System was removed from service to perform a planned maintenance on the inverter power supply. The plant computer provides monitoring capability for the Safety Parameter Display System (SPDS). The expected duration of plant computer inoperability is approximately 16 hours. The loss of the plant computer requires alternate methods, as described in plant procedures, to be used. Therefore, appropriate assessment of plant conditions, notifications and communications can still be made, if required, during the time that the plant computer is inoperable. "This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii) which is any event that results in a major loss of emergency assessment capability, offsite response capability or offsite communications capability. As previously stated, alternate means remain available to assess plant conditions, make notifications and accomplish required communications, as necessary. An additional notification will be provided when plant computer operability is restored. "The NRC Senior Resident Inspector has been notified." * * * UPDATE AT 1600 EST ON 02/17/09 FROM KENT MILLS TO S. SANDIN * * * The SPDS was restored at 1545 EST. The licensee informed the NRC Resident Inspector. Notified R1DO (Jackson). | 0 | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-17
44855 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2009-02-16 16:55 | 2009-02-16 22:09 | 2009-02-16 | INADVERTENT RELAY ACTUATION RESULTS IN AUTO START OF 1C EMERGENCY DIESEL GENERATOR "No release of radiation has occurred as a result of this event." "At 1655 CST, the Unit One 'H' 4160V bus phase two differential relay actuated when the relay panel was inadvertently bumped. This resulted in the de-energization and lockout of the 1H 4160V bus and the auto start of the 1C Emergency Diesel Generator [EDG]. Recovery actions have been successful in restoring power to the affected switchgear. All equipment functioned as expected. Normal equipment lineup has been restored. Unit One remained at full power during this event." The 1C EDG never picked up any loads because of the lockout on the 1H bus. Some loads were lost including an air compressor and some oil pumps but this equipment was either re-started or backups were started within about two hours. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-02-16
44854 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-02-16 05:13 | 2009-02-16 09:45 | 2009-02-16 | MANUAL REACTOR SCRAM DUE TO LOSS OF STATOR COOLING WATER "At 0513 on 2/16/09, the Unit 2 reactor was manually scrammed in accordance with alarm response procedure 2-ARP-9-8A 'TURBINE TRIP TIMER INITIATED'. Other associated alarms and indications both locally and in the Main Control Room indicated a failure of the stator cooling water system. The exact cause of the failure is still being investigated. "All systems responded as expected to the insertion of the manual scram. No ECCS injection was initiated or required, and all expected containment isolation and initiation signals were received. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation'. It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A)." All rods inserted fully into the reactor. The electrical power system is in a normal shut down configuration. Decay heat removal is through the main condenser via the turbine bypass valves. There is no impact on Units 1 and 3. The NRC resident inspector has been notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-02-16
44853 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2009-02-12 | 2009-02-13 21:09 | 2009-02-13 | BRACHYTHERAPY SEEDS MISPLACED IN PATIENT "A medical event was discovered on February 12, 2009, for a patient treated at the VA Greater Los Angeles Healthcare System, Los Angeles, California. "The medical event involved a patient who had undergone permanent implant prostate seed brachytherapy on February 12, 2009, using iodine-125 seeds. Approximately five seeds were mistakenly placed more than one centimeter from the prostate toward the perineum. This treatment result is interpreted to meet the definition of a medical event under 10 CFR 35.3045(a)(3). "The causes and clinical effects are under review. At this time, it is not believed that the misplaced seeds will cause any adverse deterministic effects to the patient. "The permittee is aware of the requirements in 10 CFR 35.3045 regarding notification of the patient and referring physician. A 15-day written report for the medical event will be submitted to NRC Region III. National Health Physics Program will notify the NRC Project Manager, NRC Region III, of the medical event. "The permit number for the facility involved in this medical event is VHA Permit No. 04-00181-04." A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | CA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-02-19
44852 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2009-02-13 12:02 | 2009-02-13 18:26 | 2009-02-13 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for illegal drugs during a follow-up fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2009-02-13
44851 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-02-13 15:26 | 2009-02-13 17:00 | 2009-04-01 | UNUSUAL EVENT - ENGINEERING ANALYSIS REQUIRES TECHNICAL SPECIFICATION SHUTDOWN "On February 13, 2009 at 1526 CST, Fort Calhoun Station declared a Notification of Unusual Event [NOUE] based upon EAL 4.2 - Both Diesel Generators NOT Operable. The station has entered Technical Specification 2.0.1(1) requiring the Unit to be placed in at least HOT SHUTDOWN within 6 hours. "The cause of the NOUE is a potential common mode failure of the diesel generators. Design Engineering has identified an unanalyzed condition in which a High Energy Line Break in Room 81, Main Steam Lines Containment Penetration Room, or an auxiliary steam leak in Room 82, Turbine Building Ventilation Room, can potentially result in water entering both diesel generator rooms through the floor of Room 82 located directly above the diesel rooms, Rooms 63 and 64. This condition presents a potential common mode failure of the diesel generators due to loss of diesel generator auxiliaries from a single failure. The possibility of water leaking into Rooms 63, 64 and the Switchgear rooms prompted this declaration." Compensatory measures to exit the NOUE will be to remove auxiliary steam from room 82 and blockading shut the door between rooms 81 and 82. These actions are expected to be completed within one to three hours. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1928 ON 2/13/2009 FROM SCOTT EIDEM TO MARK ABRAMOVITZ * * * At 1828 CST, Fort Calhoun Station exited the Notification of Unusual Event. Both Diesel Generators were declared operable based upon establishing compensatory measures. Diesel 2 was confirmed operable by running in accordance with approved procedures. Diesel 1 was successfully run on February 11, 2009 per a monthly surveillance tests. No additional water intrusion had occurred into the diesel 1 room since completion of the surveillance test. Compensatory measures to prevent water intrusion into Room 82 include isolating auxiliary steam to room 82 to eliminate a source of water to room 82, installing a temporary barrier at the door between rooms 81 and 82 to prevent water from flowing from room 81 to room 82, should an HELB occur in room 81, and to open the door between room 81 and the turbine building to allow water to flow out of room 81 so as not to flow into room 82. Technical Specification 2.0.1 has been exited as of time 1828 CST." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Miller), IRD (McDermott, McMurtray), DHS (Doyle), and FEMA (Via). * * * UPDATE AT 1539 EDT ON 4/1/2009 FROM ERICK MATZKE TO DONG PARK * * * "This is a retraction [of the report made under 10 CFR 50.72(b)(3)(ii)(B) - Unanalyzed Condition] "Fort Calhoun has performed a detailed evaluation of water intrusion through cracks in the floor of room 82 above the emergency diesel generators, as identified in part in the notification of 2/13/2009. This evaluation determined that no common mode failure mechanism existed and that the diesel generators were capable of performing their design safety functions." The licensee informed the Resident Inspector. Notified R4DO (Rick Deese). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) |  |  | 0 | 2009-02-13
44850 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-02-12 15:00 | 2009-02-12 19:22 | 2009-02-12 | US COAST GUARD AND NEW JERSEY ENVIRONMENTAL HOTLINE NOTIFIED DUE TO CAPSIZED BOAT "This notification is based on 10 CFR 50.72(b)(2)(xi) HCGS RAL 11.8.2.a Unusual Conditions Warranting a News Release or Notification of Government Agencies. The US Coast Guard and New Jersey State Environmental Hotline were contacted and provided the following communication. "Between 14:00 and 15:00 hours today, an unmanned 25' boat owned by Atlantic Subsea (a PSEG Nuclear contractor) that was tied in the Hope Creek Generating Station barge slip, which is on the Delaware River, at Hope Creek Generating Station overturned and became partially submerged. There were no passengers onboard at the time. Atlantic Subsea reports that the boat contains approximately 40 gallons of gas in a sealed fuel system and 5 gallons of oil in a sealed oil system. Atlantic Subsea does not believe the sealed fuel or oil systems will leak, and there is NO indication of gas or oil leaking into the Delaware River. The gas tank does have a vent, but this vent is fitted with a mechanical vacuum breaker that is not expected to leak. "Because of the wind and high seas, PSEG and Atlantic Subsea are unable to safely remove the boat or its contents from the water at this time. It is expected that the boat will be removed from the water tomorrow when the weather improves. PSEG is presently deploying absorbents into the entrance of the barge slip to contain any oil or gas that does leak. In addition, inspections of the water in and around the barge slip will be performed hourly. A notification will be made in the event that a discharge occurs. "Atlantic Subsea has informed the Coast Guard. "This is a courtesy notification only from PSEG Nuclear LLC's Hope Creek Generating Station. There is no evidence of a leak of petroleum products into the Delaware River." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-02-12
44849 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-02-12 12:30 | 2009-02-12 16:56 | 2009-03-20 | HIGH PRESSURE COOLANT INJECTION SUCTION SOURCE INSTRUMENT MALFUNCTION "Unit 2 HPCI (High Pressure Coolant Injection) system is being considered inoperable due to the following information: (Condition Report 2009101257) The instrumentation associated with the automatic suction swap for Unit 2 HPCI was reviewed as a result of CR 2009100480 to confirm the set points that determine the condensate storage tank (CST) level at which the suction swap would occur. During the course of this review, the corporate design engineer contacted the level switch vendor to review the configuration of the level switches and to confirm the expected operation of the switches (2E41-N002 & 2E41-N003) given their configuration. Based on the configuration of the instrument lines and physical location of the level switches, the vendor reported that either liquid or gas would most likely be entrapped in the external cage of the Magnetrol level switches. This would prevent the instruments from performing their automatic swap function. Based on this information the 'as found' condition of the switches indicate that this condition has been present since the installation of the switches when implementing the DCP in 1991 which affects the operability of this instrumentation. "Even though the suction swap instrumentation on low CST level is considered inoperable, there is no apparent actual adverse impact on nuclear safety. However, the instrumentation is included in the Technical Specifications and its inoperability would make HPCI inoperable if it is aligned to the CST rather than being aligned to the suppression pool. The normal system alignment is with its suction source to the CST, therefore HPCI is being considered as inoperable. "Until the configuration of the level switches has been addressed, these Magnetrol level switches must be considered inoperable, the appropriate Technical Specification RAS [Required Action Statement] will be entered and the suction source for HPCI should be aligned to the suppression pool when HPCI is required to be operable. This condition only applies to Unit 2." The licensee has notified the NRC Resident Inspector. * * * UPDATED AT 1648 EDT ON 03/20/2009 FROM EDWEN URQUHART TO V. KLCO * * * Event Report 44849 Retraction: "On February 12, 2009, a condition was discovered where the physical location of level switches relied upon for automatically transferring the suction of the Unit 2 high pressure coolant injection (HPCI) system from the condensate storage tank (CST) to the suppression pool on low CST level did not meet the setpoints given in the Technical Specifications. Based on the information available at that time HPCI would have to be considered inoperable based on the fact that the affected instrumentation was inoperable and with HPCI aligned to the CST. Since the unit was shutdown HPCI was not required to be operable. "After further review the determination has been made that at the time of discovery the 'as found' plant configuration associated with the suction swap setpoint for the Unit 2 high pressure coolant injection (HPCI) system could NOT have prevented the fulfillment of the safety function since the unit was in Cold Shutdown, and HPCI was not required to be operable. Based on this information this condition did not require an NRC notification in accordance with I0CFR50.72 and as such is being retracted through this update response. The condition will be reported in accordance with I0CFR50.73(a)(2)(v)," The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-02-12
44848 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-02-12 12:15 | 2009-02-12 16:30 | 2009-02-12 | CONTAMINATED WORKER SENT TO OFFSITE HOSPITAL FOR TREATMENT "Operator was changing a filter in a glove box when he noticed liquid on his sleeve. Safety Department was notified and operator was found to be contaminated above limits. Decontamination attempts were unsuccessful due to nitric acid burn on forearm. Several small holes/cuts in rubber glovebox glove were identified. Operator was sent to medical facility for further evaluation. Operator was treated for second degree burns at medical facility and released. "There were no exposures from licensed material. There were no actual consequences to the public or environment. "Personal protective equipment was used by the worker. Emergency safety shower was available and utilized. Locker room shower was also available and utilized." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2009-02-18
44847 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-01-20 | 2009-02-12 11:41 | 2009-04-17 | AGREEMENT STATE REPORT - SOURCE SHUTTER STUCK OPEN The following report was received from the state via e-mail: "Nucor Steel Company informed the [Arkansas] Department [of Health] that they had a stuck shutter on one of their caster sources. The licensee utilized a lifting mechanism that allowed the technicians to lift and move the source without being near the source. The source and source holder were placed in an appropriate container and surveys were performed. The highest reading on the storage container with the shutter open at contact was 120 MicroR/hour. "The storage container was relocated to a remote area on the casting deck and surveys were performed. A source service provider was contacted and arrived on site the next day to evaluate the problem. "Source: Berthold Model LB 300 MLT, Serial number 730-4-97, 36 mCi of Co-60 used for mold level control. "On 02/12/2009, at 10:01 AM the licensee provided the Department with a more detailed description of the steps taken by the technicians during the event, storage of the source, exposure reading at the source, and security of the source at this time. The licensee is currently awaiting feedback from the gauge service provider. "The Department will leave this report open pending receipt of a final written report from the licensee, due in 30 days." Arkansas Report: 09-02-01 * * * UPDATE FROM ROBERT PEMBERTON (VIA EMAIL) TO HOWIE CROUCH ON 4/17/09 @ 1119 EDT * * * "The following are the findings of Arkansas Department of Health [ADH], Radioactive Materials Program, concerning event Number 44847 at NUCOR Steel in Armorel, AR. From information provided by NUCOR Steel and JENDCO Corporation, the Department [ADH] has determined this event was caused by a small metal chip that interfered with the rotation of the shutter. The Department has concluded that the root cause of this incident is mechanical failure. The Department considers this incident to be closed." Notified FSME (Flannery) and R4DO (Whitten). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-02-17
44846 | -1 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2009-02-11 13:18 | 2009-02-11 19:31 | 2009-02-12 | POSSIBLY INADEQUATE BACKUP NITROGEN SUPPLY FOR ATMOSPHERIC DUMP OPERATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS of under the reporting requirements of 10 CFR 50.73. "Palo Verde Nuclear Station declared all three Unit's atmospheric dump valves (ADV) inoperable at 1318 MST. The reason for the inoperability is the discovery by engineering personnel that the ADV backup nitrogen capacity, required to operate the valves to mitigate certain accident scenarios, was not adequate. "There are 4 ADVs (one on each steam line with two steam lines per steam generator) for each of the three units. Engineering review of a loss of offsite power event determined that the current nitrogen supply of 13.3 hours will not be adequate to get the plant to shutdown cooling entry conditions during a natural circulation asymmetric cooldown (i.e. Feedwater Line Break, Main Steam Line Break, and Steam Generator Tube Rupture). "Actions are in progress to restore the operability of the ADVs. If unsuccessful, all three units will be required by the Technical Specifications to be in Mode 3, Hot Shutdown, by 1918 MST on February 12, 2009." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM RAY BUZARD TO PETE SNYDER AT 1840 ON 2/12/09 * * * "This is a retraction of the condition reported in EN # 44846 on February 11, 2009 at 19:31 EST. Upon further review of the condition, engineering personnel have determined that the ADV nitrogen supply was adequate to mitigate the consequences of the postulated events and the ADVs were declared operable at 04:30 MST on February 12, 2009. Therefore, no reportable condition existed." The licensee notified the NRC Resident Inspector. Notified R4DO (Miller). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-02-11
44845 | 0 | WAYNE STATE UNIVERSITY |  |  |  |  | 2009-02-10 19:00 | 2009-02-11 15:40 | 2009-02-11 | MISSING VIAL CONTAINING 5 MILLICURIES OF CHROMIUM - 51 The RSO for the Wayne State University's School of Pharmacy reported a missing vial containing 5 millicuries of Chromium-51 in a saline solution. The vial was received at the licensee's laboratory on February 6 along with two cartons of tritium. The tritium was removed from its shipping cartons and placed in a lab storage refrigerator. The Chromium was left on a desk in the carton to be leak tested prior to being placed in the refrigerator. Apparently, the lab student did not perform the leak test on the Chromium before leaving the lab. The carton with the Chromium vial was left on the desk near the trash can with the empty tritium containers. The facility custodian came in later that day and put the empty tritium containers in the trash as well as the Chromium container (not realizing it still had the radioactive material inside). On February 10 around 1900 EST it was discovered that the Chromium vial was missing. The licensee performed a search of the facility including radiological surveys and has concluded that the vial was likely thrown out in the trash. The trash dumpster had already been emptied by the waste management firm used by the university. The waste management firm has been notified. It should be noted that the amount of Chromium-51 in the vial is only 5 times the 10 CFR Part 20, Appendix C limit. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MI | MAT | [5 empty] | 0 | 2009-02-11
44844 | 0 | PARKVIEW HEALTH |  |  |  |  | 2009-02-02 | 2009-02-10 14:45 | 2009-02-10 | LOST IODINE-125 SEED The RSO for the licensee reported that a 0.337 milliCurie Iodine -125 seed has been lost from the Parkview Health facility. The seed that is missing was used as a calibration seed for a prostrate procedure on 1/28/09. The seed was not to be part of the seeds implanted and was to be returned to a storage vial. During an inventory on 2/2/09, it was discovered that the seed was not in the vial. It was confirmed that the seed was not implanted in the patient. All areas where the seed might have been dropped or placed within the facility were checked including vacuum cleaners and trash. The licensee has exhausted its search and considers the seed lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2009-02-10
44843 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2009-02-10 08:10 | 2009-02-10 09:45 | 2009-02-10 | PLANT COMPUTER OOS FOR SCHEDULED MAINTENANCE TAKING ERDS OOS "The Perry Nuclear Power Plant took the Plant Computer out of service for scheduled maintenance which took ERDS out of service. From 0810 hours EST on February 10, 2009 for approximately 6 hours, personnel will be performing maintenance activities on the Plant Computer. During this planned maintenance, the Safety Parameter Display System (SPDS) and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Private Branch Exchange, Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10CFR50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communication capability. A follow-up notification will be made when the maintenance activities are completed and the equipment is restored. The [NRC] Resident Inspector has been notified." * * * UPDATE AT 1250 EST ON 2/10/09 FROM STANLEY TO HUFFMAN * * * At 1240 EST the licensee returned the plant computer to service. ERDS, CADAP, and SPDS have been restored to operable status. The licensee has notified the NRC Resident Inspector. R3DO (Burgess) has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-10
44842 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2009-02-09 16:00 | 2009-02-09 17:50 | 2009-02-09 | REMOVABLE SURFACE CONTAMINATION ABOVE LIMITS "Two packages containing radioactive material were received with removable surface contamination on the outside of the packages greater than the limit cited in 10 CFR 71.87(i). "The two packages were received at approximately 4:00 p.m. EDT, February 9, 2009, by the VA Medical Center in West Palm Beach, FL. The two packages contained Germanium-68 PET/CT calibration sources. "Wipe tests performed on the two packages indicated the following removable contamination levels: 802 dpm/cm2 on one package and 400 dpm/cm2 on the other, as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. Spectral measurements (gamma energy) of the wipes were consistent with the radionuclide contained in the package. "The final delivery carrier was notified of the contaminated packages at approximately 5:00 p.m. EDT on February 9, 2009, by the VA Medical Center's Radiation Safety Officer. The shipper [Eckert Ziegler Isotope Products] was also notified (by recorded voice message) of the contaminated packages. "Licensee will notify our NRC Project Manager (Cassandra Frazier, NRC Region III) of this event. "Additional information: Permits are issued under the license to Veterans Health Administration facilities. The permit number for the facility involved in these medical events is VHA Permit No. 09-25328-01." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | FL | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2009-02-09
44841 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-02-09 04:15 | 2009-02-09 04:31 | 2009-02-09 | TSC OOS DUE TO PLANNED HVAC MAINTENANCE "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance being performed on the TSC HVAC. Alternate facilities are available to provide emergency functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. A 10CFR50.54(q) evaluation has been performed for this planned maintenance activity and has determined that this work may be performed without prior NRC approval. "The NRC Resident Inspector has been notified." The licensee stated that the planned maintenance on the TSC HVAC and return to service of the TSC should be completed within 12 hours. * * * UPDATE PROVIDED AT 1446 EST ON 02/09/09 FROM HANS BISHOP TO JEFF ROTTON * * * TSC HVAC maintenance is complete and the TSC was restored to service at 1441 EST. The licensee will notify the NRC Resident Inspector. Notified R2DO (Rudisail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-09
44840 | -1 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2009-02-08 16:02 | 2009-02-08 20:18 | 2009-02-11 | TEST REACTOR EXCEEDED LICENSED POWER LIMIT DURING CALIBRATION "Performing routine thermal power calibration of nuclear instruments at indicated power of 230 kW per SOP-33. Calculation indicated actual power of 263 kW after collecting data. Licensed power limit is 250 kW. "No apparent cause for the calibration error. [The previous] calibration was successfully done on January 16, 2009." The reactor was shutdown. All systems functioned as required. The licensee noted that the pool temperature was about 7 degrees Celsius cooler than the historical pool temperature. The licensee will notify the NRR Project Manager and the State of Oregon. * * * RETRACTION AT 1850 EST ON 2/11/09 FROM FRANTZ TO HUFFMAN * * * The licensee re-performed the thermal calibration per SOP-33 to check results obtained on 2-08-09. The difference this time is the licensee extended the calibration for a much longer period (approximately 7 hours). The licensee has determined that data obtained during the first 30 to 60 minutes of calibration indicated erratic information. "[The licensee has] concluded that when [the reactor was] operating on 2-08-09 at an indicated power of 230 KW, actual power was 245 KW. [This power] is less than [the reactor's] licensed limit of 250 KW. Thus Reed did not violate its licensed power limit on 2-08-09 as previously reported. SOP-33 will be revised to avoid this error in the future." Notified the NRR PM (Hughes via e-mail) and NRR EO (Lee). R4DO (Miller) was notified for information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2009-02-08
44839 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2009-02-08 11:25 | 2009-02-08 18:08 | 2009-02-08 | AUTOMATIC REACTOR SCRAM DUE TO A GOVERNOR VALVE FAST CLOSURE SIGNAL "Following a downpower to 75% for replacement of DEH-SV-TRIP/B (solenoid for quadvoter valve) a reactor SCRAM occurred during the performance of the DEH [Digital Electric Hydraulic] quadvoter valve testing. The cause of the reactor SCRAM was Governor Valve Fast Closure signal due to DEH trip header pressure fluctuation. The cause of the DEH trip header pressure fluctuation is unknown and being investigated. All rods fully inserted. MSIVs remained open. No SRVs opened. RPV level is being controlled in the normal band using the feedwater and condensate systems. RPV pressure is being controlled in the normal band using the Bypass valves and Main Steam Line drains. All other safety systems operated as designed. Off-site power is available. All three emergency diesel generators are operable and available." The licensee will be making a press release. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-02-08
44838 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-02-06 06:00 | 2009-02-07 17:14 | 2009-02-09 | AGREEMENT STATE - STOLEN TROXLER GAUGE On 2/6/09, between the hours of 0200 and 0600 PST, a 3400 series Troxler gauge was stolen from a residence. The gauge was in a camper on the premises of the residence located in Martinez, California. The licensee (Stevens, Ferrone & Bailey Engineering Co.) reported the stolen gauge to the State of California on 2/7/09 at 1300. The density gauge contains approximately 8 mCi of Cesium 137 and 40 mCi of Americium 241. The Sheriff was notified and the licensee plans to offer a reward. This notification is preliminary and will be updated by the state of California as more information is available. * * * UPDATE AT 1629 EST ON 2/9/09 FROM PRENDERGAST TO HUFFMAN VIA E-MAIL * * * "[The licensee RSO reported] on 2/7/09 that [a] portable gauge had been stolen early in the morning on 2/7/09. Apparently, one of [the licensee's] employees had transported a Troxler model 3440 portable gauge to his residence [deleted] in Martinez, CA. 94553, after work on 2/6/09. According to [the RSO], the Troxler model 3440 series moisture density gauge (serial number T344-33708 containing 9 mCi of cesium 137 and 44 mCi of Am-241) gauge was stolen from the back of a locked camper shell between 12:00 a.m. and 6:45 a.m. on 2/7/09. [The RSO] stated that the gauge was stored inside a locked camper shell that was backed up to the garage at the employee's residence. The camper shell was broken into, the chains were cut and the gauge was removed from the vehicle. According to [the RSO], the gauge had been covered inside the camper shell to prevent detection. The Martinez Police were also notified and filled out Martinez Police report # 09-513. "The [California Radiologic Health Branch] was notified by [the RSO] that a trucker had called [the RSO] at 10:00 a.m. on 2/9/08 to inquire on the reward. The trucker, who did not give his name, indicated that he had found the gauge and case on the side of the road. The anonymous trucker was concerned and stated that he had to notify his management before he turned over the gauge." CA Report #020909 R4DO(Miller), FSME EO (Shaffer), and ILTAB (via e-mail) were notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-02-11
44837 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2009-02-07 10:59 | 2009-02-07 12:18 | 2009-02-10 | UNUSUAL EVENT DECLARED DUE TO A FIRE ONSITE Arkansas Nuclear One Unit 1 declared an Unusual Event per EAL 7.5 at 1059 CST based on a fire onsite. The fire occurred on the 354 foot elevation iso-phase bus deck of the turbine building. The fire was attributed to a failed bonnet on a manual valve which had unthreaded during operation releasing hydrogen in the vicinity of the hydrogen add station. The licensee extinguished the fire using water and posted a reflash watch. There were no reported personnel injuries. Offsite assistance was requested from the London Fire Department which arrived onsite after the fire had been extinguished. The reactor was manually tripped with all control rods fully inserting. The plant is currently stable with decay heat removal via the steam dumps to the main condenser. The licensee informed state/local agencies and the NRC Resident Inspector. * * * UPDATE AT 1338 EST ON 2/7/09 FROM JACKSON TO SANDIN * * * The Unusual Event was terminated at 1338 CST after confirmation that the fire was extinguished and a review of the exit criteria as defined in plant procedures. The licensee is performing a damage assessment at this time. The licensee was in the process of informing state/local agencies and will inform the NRC Resident Inspector. Notified R4DO (Clark), NRR(Hiland), IRD (Grant), DHS (Banner) and FEMA (Canupp). * * * UPDATE AT 1508 EST ON 2/10/09 FROM SCHEIDE TO HUFFMAN * * * "The subject event notification erroneously reported that all control rods fully inserted following the manual reactor trip initiated in response to a fire on site. In actuality, the rod bottom light for Rod 6 in Rod Group 7 on the CRD Position Indication Panel did not illuminate following the reactor trip and it was verified by plant computer to have inserted to 2.3 percent withdrawn. "The control board operator identified this condition quickly and reported it to the Control Room Supervisor in his immediate action response. This condition did not necessitate any additional operator actions and shutdown margin requirements were maintained." The licensee has informed the NRC Resident Inspector. R4DO (Miller) notified. | 0 | 100 | 0 | 90 | 100 | 0 | -1 | -1 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | Power Operation | Power Operation |  | Hot Standby | Power Operation |  | UNUSUAL EVENT | 4 | AR | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2009-02-07
44836 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2009-02-06 | 2009-02-06 15:54 | 2009-02-06 | PART 21 REPORT - DEFECTIVE ASME SA-193, GRADE 6 CAP SCREW MATERIAL The following information was obtained from Fisher Controls International via facsimile: Fisher Information Notice (FIN 2009-01, dated February 2, 2009) was issued to notify customers of an issue reported to Fisher by Duke Energy. "[Fisher has] informed [their] customers of record of this circumstance in accordance with 21.21 (b) of 10CFR21 because Fisher Controls International LLC, is not aware of each and every application or system design and cannot determine whether an anomaly could cause a defect or "failure to comply," relating to a substantial safety hazard. In particular, this Information Notice deals with customer orders that used improperly heat treated cap screws provided by Texas Bolt Company (Texas Bolt Order 204653, Certified by Texas Bolt Company, April 20, 1987). Receipt of this notice does not necessarily mean that the recipient has been shipped any of the subject equipment. It is expected that the recipients of this notice will review the information for applicability to their facilities, and if required, take the appropriate action as described in the section at the end of this notice. "This notice applies only to customer orders processed by Posi-Seal International that used the 100 quantity lot of hex head cap screws identified by Texas Bolt Company Material Certification Report Number 001.87-1758, certified by Texas Bolt Company, April 20, 1987. "Fisher was informed by Duke Energy that there have been failures of ASME SA-193 Grade B6 hex head cap screws at the Catawba Nuclear Station. These bolts are used on various size Posi-Seal butterfly valves to maintain a pressure seal on the outboard side of the valve body. Failure of these bolts will impair the pressure retaining capability of the valve body. "Based on the experiences at Duke Energy, it is possible that a defective batch of cap screws were used by Posi-Seal around 1987. Fisher Controls International has attempted to determine a complete list of valve serial numbers that may have used bolts from this particular lot. Unfortunately, Fisher Controls International's review of available Posi-Seal records cannot provide validation of its completeness. "It is recommended that customers verify if the QA documentation package, provided with the valve, contains a copy of the cap screw material certification attached to this information notice. If so, Fisher Controls International recommends that the subject cap screws be replaced. "Fisher Controls requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR21. "If there are any technical questions or concerns, contact: Michael Wedemeyer Manager, Quality Fisher Controls International LLC 205 South Center Street Marshalltown, IA 50158 Fax: (641) 754-2854 Phone: (641) 754-2066 Michael.Wedemeyer@.Emerson.com" Possible domestic constructions with defective cap screw material (Posi-Seal part number 131550, drawing number 5200-001) include McGuire, Catawba and Indian Point. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-02-06
44835 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2009-02-03 14:30 | 2009-02-06 15:33 | 2009-02-06 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of Mississippi Division of Radiological Health (DRH) via email: "Location of Incident: Petal, Mississippi (temporary jobsite off Hwy. 42) "Description of Incident: Approximately 2:30 pm on 2-3-09, an employee who uses the nuclear gauge with Dunn Roadbuilders notified the Radiation Safety Officer that a Troxler 3440 moisture/density gauge, SN# 23209, had been run over by a company pick-up and dragged about 5 feet. The operator told the RSO that the plastic case of the gauge was broken and a battery was outside the device. The area was blocked off with a 15 foot radius around the damaged gauge until the RSO arrived. When the RSO arrived, he surveyed the gauge with a TroxlerAlert survey meter, SN# 2163, and observed readings of 16 mR/hr at gauge surface. He observed that the sources were still shielded and the source rod was not bent or broken. The gauge was put in the transport box and taken back to the company facility. A leak test was performed on the sources and sent to Troxler for analysis. DRH was notified of the incident at 4:30 pm on 2-3-09. "Pictures of the gauge were taken by the RSO and emailed to the Division of Radiological Health. "Upon further review of the incident, the authorized user for the moisture/density gauge was trained and certificates are on file with the Division of Radiological Health. The gauge was also last leak tested on 10/08. "Isotope(s) and Activity: Cesium-137 (8 mCi) and Americium-241:Be (40 mCi) "Describe clean-up actions taken by DRH: DRH did not respond to incident after RSO confirmed normal survey readings observed and pictures showed only gauge plastic cover damaged." Incident No.: MS 09002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2009-02-11
44834 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-02-04 18:00 | 2009-02-06 13:26 | 2009-02-06 | AGREEMENT STATE REPORT INVOLVING A DOSE DELIVERED TO THE WRONG TREATMENT SITE The following information was received from the State of California via email: "On February 5, 2009, [the Radiation Safety Officer (RSO) for the] City of Hope/Beckman Research Institute, contacted LA County Radiation Management regarding a misadministration that occurred at approximately 6:00 pm on February 4, 2009. The incident involved HDR treatment of the wrong site. "Using HDR, a patient was scheduled for groin sarcoma therapy treatment. The treatment planning comprised of administration of approximately 4000 cGy to the tumor. The dose is to be administered in 10 fractions of 400 cGy/fraction; 2 fractions per day for 5 days. Six catheters to be administered/fraction. Per [the RSO], an error was made in the interpretation of the CT data, and therefore, the wrong distance was calculated. On February 4, 2009, the first day of the treatment, the catheters administered went to the body, past the tumor site, then to the outside of the thigh. [The RSO] stated that there was no dose administered to the tumor. All the dose was administered to the skin of the thigh. The patient had two treatments, and received approximately 800 cGy to the skin of the thigh. "A written report will be submitted by the licensee within 15 days. "Based on the current report of 800 rad to the wrong treatment site (skin), this medical event does not meet the criteria for an Abnormal Occurrence (see SA-300, Appendix section 6.3.IV)." CA 5010 Number: 020509 A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-02-12
44833 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2009-02-05 18:28 | 2009-02-05 22:25 | 2009-02-05 | OFFSITE NOTIFICATION TO LOCAL FIRE DEPARTMENTS FOR ASSISTANCE "At 1828 CST, a fire alarm in the Administration Building was reported to the Fort Calhoun Station Control Room. The Administration Building is located outside of the Protected Area on Owner Controlled Property. An Equipment Operator was dispatched to investigate the cause of the alarm. The Control Room entered AOP-06 Fire Emergency at 1830 CST. "At 1832 CST, a report was received from a building occupant that smoke was emanating from a Mechanical Equipment Room located on the first floor of the building. At that time, personnel in the building attempted to extinguish the fire using a portable fire extinguisher but were unsuccessful. Local Fire Departments in the City of Blair and Fort Calhoun were dispatched. "At 1840 CST, the Operator arrived at the scene, found light smoke coming from the Mechanical Equipment Room and proceeded to de-energize the ventilation equipment. At 1844 CST, the fire was then extinguished using portable fire extinguishers. It was at that time that Blair and Fort Calhoun Fire Companies arrived on site to assist. "At 1911 CST, AOP-06 was exited. Preliminary investigation shows that filter media had become dislodged and contacted duct heaters in the ventilation system. The fire ignited secondary material in the area. The Protected Area of Fort Calhoun Station was not affected at any time during this incident. "This event may cause heightened public or government concern related to the health and safety of on-site personnel. Therefore, this report is being made in reference to 10 CFR 50.72(b)(2)(xi)." The licensee informed the NRC Resident Inspector and plans to issue a press release. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-02-05
44832 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-02-05 15:39 | 2009-02-05 21:36 | 2009-03-26 | STEAM EXCLUSION DOOR GAP "At 1539 on 02/05/2009 it was identified that a Steam Exclusion door seal was not flush with the door. The door seal gap was noted during a Fire Zone Inspection. It was determined that the door exceeded the allowed limit. This could have allowed steam from the Turbine Drive Auxiliary Feed Pump room into the emergency safeguards bus area. This could have resulted in both trains of ESF Equipment failing to perform their required functions. Upon discovery Specification 3.0.c was entered at 1539. Work was completed on the door to return it to functional status at 1601, and Technical Specification 3.0.c was exited at that time. "The NRC Resident inspector has been notified." * * * RETRACTION PROVIDED BY JACK GADZALA TO JASON KOZAL ON 3/26/09 AT 1102 * * * "Retraction of EN 44832, both trains of Engineered Safeguards Features (ESF) equipment inoperable due to a degraded steam exclusion boundary door. "EN 44832 provided notification that both trains of ESF equipment were inoperable due to degradation of a steam exclusion boundary door in the turbine driven auxiliary feedwater pump room on February 5, 2009. "Subsequent engineering evaluation determined that the degraded door remained capable of fulfilling its steam exclusion function during the period when it was degraded. A degraded door seal had resulted in a slight gap to exist between the door and the sill. This gap could have allowed steam from the turbine driven auxiliary feedwater pump room into the emergency safeguards bus area. However, the force that would be exerted on the door by steam overpressure postulated under accident conditions, would compress the door seal sufficiently to reduce the gap such that the total allowed leak path criteria would not be exceeded. "Therefore, the door remained functional and the supported ESF equipment in the emergency safeguards bus area remained operable. "Consequently, this condition did not meet the reportabllity criteria in 10 CFR 50.72. As a result, the notification made on 02/05/2009 (EN 44832) is hereby retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (Peterson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2009-02-05
44831 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2009-02-05 15:24 | 2009-02-05 19:20 | 2009-02-05 | UNIT 1 MANUALLY TRIPPED DUE TO CONTROL ROD DRIVE MOTOR HIGH TEMPERATURES "Arkansas Nuclear One Unit 1 was manually tripped from 61% power due to Control Rod Drive motor (CRD) high temperatures due to a loss of cooling water flow from Non-Nuclear Intermediate Cooling Water (ICW). No significant equipment issues were observed. No primary safeties lifted. Secondary safeties lifted for ~18 seconds. Emergency feedwater did not actuate and was not needed. Post trip response was normal and the plant is stable in mode 3. Post transient review is in progress." All control rods fully inserted into the core. There is no known primary-secondary steam generator tube leakage. The offsite electrical grid is stable. The loss of ICW flow is attributed to the mechanical failure of service air compressor C-3A. Decay heat removal is via main feedwater to the steam generator and steam to the main condenser. The licensee informed state, other government agencies and the NRC Resident Inspector and will inform local government agencies. No press release is planned. | 0 | 0 | 0 | 61 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-02-05
44830 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2009-02-05 14:13 | 2009-02-05 14:34 | 2009-02-06 | UNUSUAL EVENT DECLARED DUE TO LOSS OF CONTROL ROOM ANNUNCIATORS At 1413 EST Ginna Station declared an Unusual Event due to the Loss of Main Control Board Annunciators E, F, G and H. There was ongoing maintenance at the time, however, no specific cause for the loss has been identified. The licensee confirmed that they have redundant indication available to monitor plant parameters. The unit is currently stable and operating at 100% power. The licensee informed state and local agencies and the NRC Resident Inspector. * * * UPDATE FROM DOUG GOMEZ TO DONALD NORWOOD AT 0458 ON 2/6/09 * * * Based on testing, troubleshooting, and restoration of power to the Main Control Board Annunciators, Ginna Station exited the Unusual Event at 0435 hours on 2/6/09. The licensee notified the NRC Resident Inspector. Notified RDO (Gray), NRR EO (Hiland), IRD MOC (Grant), DHS (Kettles), and FEMA(LaForty). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-02-05
44829 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-02-01 | 2009-02-05 09:26 | 2009-02-05 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED GAUGE DEVICE The following report was received from the State via E-mail: "Licensee reported a stuck shutter on a fixed gauge, which was discovered during the leak test and shutter check maintenance activity. Licensee stated that shutter had been difficult to move on past checks, but had neglected to have unit serviced. Licensee has contacted service provider to repair shutter mechanism. Device normally operates in continuous mode, so no additional actions are required at this time. "Ohio will leave this report open pending receipt of final written report from licensee, due in 30 days. "Note: Licensee stated that they were making this report as a result of awareness of requirements found in Ohio Information Notice 2008-02 regarding fixed gauge stuck shutters and reporting requirements." This was an Ohmart Corporation model number SH-1 fixed gauge device. There is 0.005 Ci Cs-137 in this device. The Ohio State reference number for this report is OH 2009-003. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2009-02-10
44828 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-02-04 13:20 | 2009-02-04 14:20 | 2009-02-04 | SIRENS OUT OF SERVICE DUE TO PLANNED MAINTENANCE "The Prairie Island Nuclear Generating Plant is making an ENS notification in accordance with 10 CFR 50.72(b)(3)(xiii) due to planned maintenance on the Goodhue County radio repeaters. This maintenance will result in unavailability of 51 of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) for approximately 3 hours. The maintenance is scheduled to occur on the afternoon of 02/04/2009. "The Goodhue County Sheriff's Office has been notified to implement the established process of back-up route alerting if required. "Upon completion of the maintenance a cancel test will be performed to verify availability of the Goodhue County sirens and an update to this notification will be provided. "The NRC Resident Inspector has been notified." * * * UPDATE FROM R. FORTIER TO HOWIE CROUCH @ 1735 EST ON 02/04/09 * * * The cancel test was performed by the Goodhue County Sheriff's Office to all Goodhue County sirens successfully. All sirens have been returned to service. The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Ring). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-04
44827 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2009-02-03 13:37 | 2009-02-03 14:55 | 2009-02-04 | SAFETY PARAMETER DISPLAY SYSTEM INOPERABLE "This 8-hour non-emergency report is being made based upon requirements of 10CFR50.72(b)(3)(xiii) which states, 'The licensee shall notify the NRC as soon as practical and in all cases within eight hours of the occurrence of any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)'. "At 0539 EST on Tuesday, February 3, 2009, the Control Room discovered that the plant process computer was not updating and subsequently observed the Safety Parameter Display System (SPDS) Computer Display was not updating data. This was discovered during periodic Control Room monitoring. The last data update on the SPDS display was at 0537 EST. "Information Technology Department personnel are investigating the cause of the loss of SPDS capability. The Information Technology Department personnel have been unsuccessful in recovering within the 8 hour restriction. "No other Control Room emergency assessment capabilities have been adversely affected. All Control Room panel indicators and annunciators are responding properly." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM HICKS TO KLCO @ 2215 EST ON 02/04/09 "On Wednesday, February 04, 2009 at 1319 EST, the Plant Process Computer (PPC) was successfully restarted. The performance of the PPC and SPDS was monitored for approximately eight hours. SPDS was declared operable at 2130, restoring full emergency assessment capability." The licensee will notify the NRC Resident Inspector. Notified R1DO (White). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-03
44826 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2009-01-28 15:45 | 2009-02-03 10:45 | 2009-02-03 | AGREEMENT STATE REPORT - PATIENT LEAVES RADIATION THERAPY TREATMENT WITHOUT RECEIVING REQUIRED INSTRUCTIONS Received from the state by facsimile: The patient left the hospital without receiving the required radiation therapy instruction. "The patient and her husband were adamant about leaving without waiting any longer. This was an unreasonable patient's husband driving this situation and we [Swedish Hospital] see no need to change our release criteria or procedures because of aberrant behavior of a family member. The patient had this procedure twice before [September 2005 and April 2006]. The implant in 2005 delivered 0.99 GBq. At the time the exposure reading at one meter was 0.25 mR/hr. This most recent procedure delivered less activity, and I would anticipate an even smaller exposure risk at one meter." Source: Y-90 SIR Spheres at approximately 0.9 GBq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2009-02-09
44825 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2009-02-02 15:45 | 2009-02-02 18:48 | 2009-02-02 | OFFSITE NOTIFICATION TO THE ENVIRONMENTAL PROTECTION AGENCY "On 02/02/2009, at 1545, the Environmental Protection Agency (EPA), Atlanta, Georgia, was notified of a loss of approximately 85 pounds of refrigerant R-22 (Chlorodifluoromethane) from a crack in a sensing line on the Unit 1 Control Room Air Conditioner, ACC-3B. The 85 pounds of refrigerant represents the entire charge in the air conditioner and exceeds the limit specified in 40 CFR 82.156. The EPA was notified as required by the station's Environmental Reporting procedures. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification made to the EPA." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-02-02
44824 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2009-02-02 14:00 | 2009-02-02 16:21 | 2009-02-04 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL "On February 2, 2009, at 1400, the Technical Support Center (TSC) heating, ventilation, and air conditioning system was discovered to be nonfunctional. Initial investigation revealed an electrical fault in the supply fan motor. Fermi is making this notification in accordance with 10CFR 50.72(b)(3)(xiii). In the event that TSC activation is necessary, the Emergency Offsite Facility (EOF) will be used. Activation and use of the EOF as a backup facility for the TSC is included in Fermi's Radiological Emergency Response Preparedness Plan, and drills have been held performing both the TSC and EOF functions from the EOF. Fermi will notify the NRC upon completion of corrective maintenance." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM KONRAD TO CROUCH @1609 EST ON 02/04/09 * * * "Corrective maintenance activities on the TSC HVAC system are complete and the TSC is now available for use." The licensee has notified the NRC Resident Inspector. Notified R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-02-02
44823 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-01-27 | 2009-02-02 12:25 | 2009-02-06 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was obtained from the State of North Carolina via facsimile: "On January 27, 2009, a Therasphere (Y-90 microsphere) procedure was scheduled for a patient in Room 4, Special Procedures. The treatment was planned to deliver 110 Gy to the left lobe of the liver. The delivery apparatus was assembled according to manufacturer instructions, without incident. The treatment was initiated. During the first infusion, the Authorized User noticed fluid leakage at the outlet flow line and needle insertion at the source vial. The RSO was contacted. An attempt was made to continue the infusion. The liquid continued to leak at the outlet flow line and needle junction. No additional radioactivity was delivered to the patient. The procedure was terminated. "Post procedure survey readings of the source vial indicated that approximately 65% of the intended radioactivity was delivered to the patient. This resulted in a dose of 70 Gy delivered to the left lobe of the liver. "The Authorized User indicated that no adverse clinical symptoms are expected. This was the second treatment for this patient. "The manufacturer (MDS Nordion) was notified of the device problem on 01/28/09. "All liquid and contamination was contained by Radiation Safety personnel." A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 1425 ON 2/06/09 FROM ALBRIGHT TO KLCO* * * Notified that the event is documented by the North Carolina Radioactive Materials Branch as incident NC-09-11. Notified the R1DO (Gray) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-02-05
44822 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2009-02-01 21:56 | 2009-02-01 23:05 | 2009-02-02 | UNUSUAL EVENT AND REACTOR SCRAM DUE TO MAIN TRANSFORMER FIRE At 2156 EST, a fire occurred on Main Transformer M1A. The loss of the main transformer resulted in a reactor scram from full power without complications. The transformer deluge system activated. The fire brigade responded and offsite assistance from the fire department was obtained to help extinguish the fire. The fire department has since departed the site. An Unusual Event was declared at 2211 EST based on the transformer fire lasting longer than 15 minutes. The fire was extinguished at 2227 EST. A fire reflash watch was established. There was no damage to any other equipment besides the main transformer. During the reactor scram transient, the isolation condenser actuated as expected and was subsequently secured. Four electro-magnetic relief valves actuated and reseated normally. The plant is currently in hot standby with reactor pressure at 927 psi and water level at 150 inches with all conditions stable and a normal electrical configuration. The licensee is assessing the criteria for exiting the UE at this time. The licensee has notified State and local government agencies and the NRC Resident Inspector. * * * UPDATE FROM ZUCHOWSKI TO HUFFMAN AT 0001 EST ON 2/02/09 * * * The licensee terminated the UE at 2337 EST due to stable plant conditions with all entry criteria for the UE exited and no concern of reflash. The licensee did note that there is an oil sheen on the water around the transformer and indication of a small amount of oil dripping from the transformer. The licensee is taking efforts to contain the spill with spill kits and barriers. The NRC Resident has been notified. Notified R1DO (Schmidt), R1 (Bellamy), NRR EO (Blount), and IRD (McMurtray). Informed DHS (Banner) and FEMA (Barden). * * * UPDATE FROM FLESHER TO HUFFMAN AT 1907 EST ON 2/02/09 * * * Upon review of the electromagnetic relief valve performance during the reactor scram at 2156 EST on 2/1/09, two electromagnetic relief valves opened - not four (as originally reported). Due to subsequent seat leakage of one electromagnetic relief valve, the valve was cycled and was able to be reseated. At 0444 EST on 2/2/09 downstream relief temperatures confirmed that the valve had reseated. The licensee has notified the NRC Resident Inspector. R1DO (Schmidt) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2009-02-01
44821 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2009-02-01 18:00 | 2009-02-01 21:28 | 2009-02-01 | MANUAL REACTOR SCRAM DUE TO LOSS OF CONDENSER COOLING "[The licensee manually inserted a reactor scram] due to imminent loss of heat sink (condenser). Circulating water to the condenser suffered an unisolable break resulting in loss of suction source to pumps with cavitation. [The] plant was stabilized per emergency operating procedures. Containment isolations signals operated per design with Groups 2, 3, and 4 received. "Plant response [was] complicated with [an] unexpected loss of one 161 KV bus in the switchyard. This was caused by a breaker failure lockout of the bus caused by signal from the output breaker. This output breaker did open. Cause of the breaker failure being investigated. "[The] power loss [of the 161 KV bus] had minor plant effect. One power supply to essential service offsite transformer 1X3 [was] lost due to the bus lockout. [The] transformer and offsite circuit remained available. [The] plant did sustain a temporary loss of spent fuel pool cooling system. Cooling has been restored with no level or temperature complications. "Essential power [remained] available with both onsite SBDG's (Standby Diesel Generators) and offsite circuits (current source). All ECCS available. All safety related equipment operat[ed] as designed, except Reactor Core Isolation Cooling (RCIC) turbine which had difficulty in automatic control. Manual control [of RCIC] was effective. This is not unexpected during the conditions it was operating (low flow)." The licensee was shutting down to enter a refueling outage as the time of the event. Circulating water to one cooling tower had been isolated when a riser on the second cooling tower ruptured and resulted in loss of supply to the circwater pumps. All systems functioned as required except for the lockout of the 161KV bus and RCIC automatic control. Rods fully inserted. The plant is in a normal electrical configuration except for the loss of the 161 KV bus which does not supply any safety related busses. No safety relief valves lifted during the transient. Cooling is currently via HPCI and RCIC to the torus with torus cooling via essential service water. The plant is currently stable at 600 psi and being cooled-down to cold shutdown. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 53 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2009-02-01
44820 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-01-31 01:50 | 2009-01-31 13:22 | 2009-01-31 | LOSS OF POWER TO CRITICALITY ACCIDENT ALARM SYSTEM HORN "At 0150 CST, on 01-31-09 the Plant Shift Superintendent (PSS) was notified that a Criticality Accident Alarm System (CAAS) trouble alarm had actuated for the C-409 (Stabilization Building). The PSS dispatched personnel to investigate and discovered that a circuit breaker had tripped causing a loss of power to the CAAS horn uninterruptible power supply (UPS). Further investigation revealed that the output of the UPS was off. This caused loss of CAAS audibility for C-409 and TSR LCO 2.6.4.1b was immediately entered. There were no fissile material operations in progress and all personnel in the affected area had a radio in constant communication with the Central Communications Facility satisfying the required actions of TSR 2.6.4.1 b. The circuit breaker that tripped was closed, the UPS was turned back on, and TSR 2.6.4.1b was exited at 0317 hours. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." PGDP Assessment and Tracking Report No. ATR-09-0203; PGDP Event Report No. PAD-2009-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2009-01-31
44819 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-01-30 12:17 | 2009-01-30 19:33 | 2009-01-30 | 24 HOUR REPORT OF PROCESS GAS LEAK DETECTION SYSTEM INOPERABILITY "At 1217 CST, on 01-30-09 the Plant Shift Superintendent (PSS) was notified that C-310 (product withdrawal facility) had lost power due to an electrical fault. As a result of the power loss, the C-310 High Voltage Process Gas Leak Detection (PGLD) System was rendered inoperable. This PGLD System contains detectors that cover the C-310 UF6 condensers, accumulators, and piping heated housing. At the time of this loss of power, these areas were operating above atmospheric pressure. TSR 2.3.4.4 requires that all of detector heads in this system be operable during operations above atmospheric pressure. Power was restored to this PGLD System at 1240 hours, which is within the one hour required by TSR LCO 2.3.4.4.A.1 to enter a continuous smoke watch. This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. Once the source of the fault was identified, power was restored to the C-310 the High Voltage PGLD System and the system was tested. "Power was restored at 1240 hours and the system was tested at 1258 hours. The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2009-01-30
44818 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-01-28 | 2009-01-30 15:31 | 2009-02-26 | AGREEMENT STATE REPORT - TWO MISSING STATIC ELIMINATORS The following report was received from the State via facsimile: "Precix [the licensee] called the Agency [the State] on 1/28/09 to report 2 missing static eliminator devices. A follow-up letter dated 1/29/09 was received on 1/30/09. The letter indicates the missing devices are 'NRD' model P-2021 devices having serial numbers A2DR562 and A2EZ592. The licensee reports that at the end of their one year useful life, the units were removed from the system along with others and set aside in preparation for returning them to NRD for disposal. The licensee states they have conducted several searches for the missing devices and have not had any success finding them. The licensee thinks the 2 units inadvertently got separated from the other units being held for return to NRD and were disposed off in the non-hazardous waste stream." This model static eliminator typically contains approximately 10 millicuries of Po-210. * * * UPDATE ON 2/26/09 AT 1453 FROM JOHN SUMARES TO KARL DIEDERICH * * * The following report was received from the State via facsimile: "In a follow up telephone conversation with Precix, the Agency [the State] determined that the static eliminators became missing a few years prior to [the] Precix report of missing GL [Generally Licensed] devices to the Agency [the State]. Precix stated that corrective action as described above has been in place for a few years. "The Agency [the State] considers this event closed." Informed R1DO (Cahill), FSME EO (Bubar), and ITLAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-02-04
44817 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-01-30 12:49 | 2009-01-30 15:29 | 2009-01-30 | OFFSITE NOTIFICATION TO LAW ENFORCEMENT A package with non-standard labeling and appearance was discovered at the Monticello Nuclear Generating Station site mailroom. The mailroom is outside the protected area. The package was moved to a remote location on the owner controlled area and local law enforcement responded to site to investigate the package. No plant systems were affected and the plant continues to operate a full power. The licensee made this report based on notification to offsite local law enforcement as well as other State and local government agencies. * * * UPDATE AT 1915 EST ON 1/30/09 FROM LICENSEE (BARNETT) TO HUFFMAN * * * Subsequent investigation proved the package to be a legitimate parcel. The NRC Resident Inspector has been notified. R3DO (Pelke) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2009-01-30
44816 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-01-29 | 2009-01-30 12:13 | 2009-01-30 | AGREEMENT STATE REPORT - PERSONNEL CONTAMINATION FROM I-131 SPILL IN HOT LAB "The radiation safety officer [RSO] for Northwestern Memorial Hospital called the Agency [State] to advise that a technician had spilled a significant quantity of I-131 in their hot lab. The technician was preparing a radioiodine therapy dose of 100 milliCi for ingestion by a patient when the spill of the liquid occurred. The technician had been removing the vial from the fume hood to perform a dose calibration when the material slipped from his hands and broke on the floor of the hot lab. The technician was contaminated on his hands, torso and legs. The material, although small in volume, was concentrated, such that even small drops of the liquid exhibit high dose rates. Initial decontamination efforts managed to reduce the contamination on the individual such that the contamination only remained on their hands. The initial measured dose rate was approximately 7 milliR/h. "The spill victim was excluded from the cleanup process to reduce the possibility of a significant uptake to their thyroid. All individuals involved in the clean up as well as the technician took prophylactic KI. According to the RSO, decontamination will continue until only fixed contamination remains. He estimated that as much as 80% of the contamination had been contained/removed by the time of his call a few hours after the event. Dose rates in the area were initially over 50 milliR/h. Additional shielding was moved into the area so that medically necessary nuclear medicine procedures could be completed while the decontamination was finished. Dose rates behind the shielding indicated less than 1 milliR/h. Bioassays will be conducted during subsequent days to determine the extent of any uptake that has occurred for those involved. "Arrangements were made for the radiopharmacy to be shut down and operations relocated to another temporary facility within the hospital. Waste generated from the initial decontamination effort was secured within the pharmacy hot lab in the fume hood. Access will be restricted to only those granted leave by the RSO to reenter the lab. Arrangements have been made for an Agency [State] inspector to go to the site to ascertain and verify the dose rates in the area, the extent of contamination and ensure that bioassays are being conducted properly. Depending on the results of those assessments, the Agency [State] may take additional action." Incident number: IL0900010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-02-04
44815 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-01-29 08:50 | 2009-01-29 09:40 | 2009-01-29 | UNUSUAL EVENT - TOXIC GAS DISCHARGE IN WASTE GAS TREATMENT BUILDING An unisolable pipe break on an in-service waste gas treatment building chiller has resulted in a toxic release of asphyxiant freon gas. All personnel were evacuated and no injuries occurred. An entry by operations personnel with self contained breathing apparatus verified that all site personnel have evacuated the building. There was no impact to offgas processing equipment in the area and actual gas concentration was not known at the time of declaration so the assumption of toxic gas concentration is conservative. The Licensee notified the NRC Resident Inspector, Georgia Emergency Management Agency, Appling County, Jeff Davis County, Tattnall County, and Toombs County. * * * UPDATE FROM TONY SPRING TO PETE SNYDER AT 0957 ON 1/29/09 * * * Air samples in the area indicated no detectable freon. Licensee terminated the event at 0946. Notified R2DO(McCoy), NRR EO(Ross-Lee), DHS(Inzer), and FEMA(LaForte) | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2009-01-29
44814 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-01-28 14:25 | 2009-01-28 18:00 | 2009-01-28 | UNANALYZED CONDITION RELATED TO A POSTULATED APPENDIX R FIRE SCENARIO "A postulated Appendix R fire scenario has been identified which could result in the plant being in an unanalyzed condition that may degrade plant safety. The unanalyzed condition involves a potential loss of power to the credited train of fire safe shutdown equipment for postulated fires in two areas of the Auxiliary Building. "Safety-related loads on the 6.9KV Shutdown Boards (Centrifugal Charging Pumps, Safety Injection Pumps, Containment Spray Pumps, Motor-Driven Auxiliary Feedwater Pumps, and Residual Heat Removal Pumps) are equipped with local control switches to allow starting or stopping the pumps from the Auxiliary Building. The DC control circuit wiring for these local switches is routed in the same area as the power cables for pump motors. If the fire damages the control circuit cables, the control circuit fuses may fail, resulting in loss of trip capability for the associated 6.9KV breaker. If the breaker is already closed (due to a spurious signal or a previous valid start signal), then the breaker could be disabled in the closed position. If the fire damages the power cables resulting in a phase-to-phase fault with the load breaker trip capability disabled, then the Shutdown Board feeder breaker is designed to trip open on overcurrent to provide backup protection. This could result in the shutdown board being de-energized. "In two areas in the Auxiliary Building (elevation 669 and 690 common areas), the above scenario could result in a condition which is outside the fire safe shutdown analysis due to loss of power to the credited train of fire safe shutdown equipment (e.g. Centrifugal Charging Pump, Essential Raw Cooling Water Pump, and motor-operated valves). "As a result of this condition, Sequoyah has entered the Fire Protection Report Limiting Condition for Operation 3.7.12 for inoperable fire barriers. In accordance with this LCO action, the operability of fire detectors in the affected areas has been verified and an hourly fire watch has been established in the affected areas. "This issue has been entered into the corrective action program. A permanent resolution is being evaluated." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-01-28
44813 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2009-01-27 | 2009-01-28 15:48 | 2009-01-28 | MEDICAL EVENT - ACTUAL DOSE LESS THAN PRESCRIBED DOSE "Two medical events were discovered on January 27, 2009, for patients treated during 2005 at VA Greater Los Angeles Healthcare System, Los Angeles, California. "These two medical events involved patients who had undergone permanent implant prostate seed brachytherapy using iodine-125 seeds. The resulting seed distributions in the patients were associated with a D90 dose to the treatment site that was less than 80% of the prescribed dose. "These patient circumstances are interpreted to meet the definition of a medical event under 10 CFR 35.3045(a)(1)(i). "A 15-day written report for the medical events will be submitted to NRC Region III. "We have notified our NRC Project Manager (Cassandra Frazier, NRC Region III) of the medical events." A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | CA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-02-03
44812 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2009-01-28 12:24 | 2009-01-28 13:24 | 2009-01-28 | STEAM EXCLUSION DOOR INAPPROPRIATELY HELD OPEN BY A DOOR CHOCK "At 0834 on 01/28/2009 it was identified that a Steam Exclusion door was held open by a door chock installed on the door for less than 15 minutes. The door was open to ventilate the room during venting of carbon dioxide piping for routine maintenance. A Maintenance Mechanic was stationed at the door as per procedure. This door would have allowed steam into the emergency safeguards bus area from the Carbon Dioxide Tank room. This could have resulted in both Trains of ESF Equipment failing to perform their required functions. Upon discovery the door chock was disengaged to allow the door to self-close if required." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2009-01-28
44811 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2009-01-28 07:30 | 2009-01-28 12:16 | 2009-03-11 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "On January 28, 2009 at 0730 the Division 2 Emergency Equipment Cooling Water System (EECW) was declared inoperable due to a blown control power fuse in the bucket for the P4400F604 - Div 2 EECW Supply to Control Rod Drive (CRD) pumps. This is a normally open valve and is required to close upon EECW initiation to remove non-essential loads. The blown control power fuse would have prevented this action from occurring. The ECCW System cools various safety related components including the High Pressure Coolant Injection (HPCI) System Area Cooler. An unplanned HPCI inoperability occurred due to the Division 2 EECW inoperability based on a loss of the HPCI System Area Cooler. A 14 day Limiting Condition for Operation (LCO) was entered for HPCI per LCO 3.5.1. The control power fuse was replaced, EECW and HPCI were declared operable, and LCO 3.5.1 exited on January 28, 2009 at 1025. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on loss of a single train safety system. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM JIM KONRAD TO DONALD NORWOOD AT 1449 ON 3/11/09 * * * "The As-Found condition of the Division 2 Emergency Equipment Cooling Water (EECW) Control Rod Drive (CRD) Pump Supply Valve and High Pressure Coolant Injection (HPCI) System Room Cooler were evaluated. "The HPCI System Room Cooler was operable with P4400-F604, Division 2 EECW to the CRD supply valve open. Based on an Engineering evaluation of EECW flow during a Loss of Coolant Accident (LOCA) and Non-LOCA conditions with the valve open, there is adequate flow margin in the EECW system. "The HPCI Room Cooler had adequate cooling flow to perform its design function. The HPCI room temperature would have been maintained below the HPCI equipment room high temperature isolation setpoint. Additionally, plant procedures provide directions for bypassing the HPCI equipment room high temperature trip. Consequently, there was no loss of HPCI safety function. Declaring HPCI inoperable was conservative and based on initial considerations. Therefore, event notification 44811 is retracted." The Licensee notified the NRC Resident Inspector. Notified R3DO (Lara). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-01-28
44810 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2009-01-27 20:07 | 2009-01-28 03:12 | 2009-01-28 | UNIT 2 HPCI SYSTEM INOPERABLE FOR TWO HOURS DUE TO CONDENSATE IN EXHAUST LINE "On January 27, 2009 at approximately 2007, the Unit 2 High Pressure Coolant Injection (HPCI) System was declared inoperable due to a sustained high level in the HPCI Exhaust Line Drain Pot. This sustained high level was caused by a failure of the HPCI Barometric Condenser Condensate Pump, which prevented the removal of the accumulated condensate. An alternate drain path was established and the exhaust line drain pot high level condition was cleared at 2202. However, due to this condition existing for approximately two hours, it cannot be assured that HPCI would have been able to perform its designed function under all conditions. The potential of HPCI system component damage or isolation from an exhaust line failure due to water hammer during a system initiation could not be positively eliminated. "Initial safety significance: Minimal. The Reactor Core Isolation Cooling (RCIC) System, Automatic Depressurization (ADS) System, and Low Pressure Emergency Core Cooling Systems (ECCS) - two Loops of Core Spray and two Loops of Low Pressure Coolant Injection (LPCI) - remain operable. "Manual actions have been taken to drain the HPCI Exhaust Line Drain pot and have been successful. Determination of the cause of the failure of the HPCI Barometric Condenser Condensate Pump and restoration to service are in progress." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-01-28
44809 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2009-01-27 | 2009-01-27 17:11 | 2009-01-27 | PART 21 REPORT - PART NOT EVALUATED FOR ALL CRITICAL CHARACTERISTICS The following information was obtained from Fisher Controls International via facsimile: The equipment supplied included a 20 inch Fisher valve coupled to a Bettis actuator. "The purpose of this Fisher Information Notice (FIN 2009-03) is to alert Alabama Power that as of January 16, 2009, Fisher Controls International LLC became aware of the possibility of a situation which may affect the performance of the applicable equipment. "This notice applies only to the subject equipment supplied by Fisher Controls International LLC, identified above, that was provided to Alabama Power - Farley. "Fisher Controls has determined that the subject items were provided with parts that were not properly processed per active valve requirements specified by the Alabama Power Order. "Specifically, Fisher provided a coupler between the actuator drive lever and valve shaft that was not evaluated for all the critical characteristics deemed necessary for a commercial grade dedicated item per EPRI 5652 and Fisher Manufacturing Procedure FMP 2K27, 'Control of Commercial Grade Items to be Dedicated for Use in Nuclear Safety-Related Systems,' (Fisher Processing Level C). "We [Fisher Controls] are reviewing the situation and will pursue a corrective action investigation to prevent problems like this in the future. "Arrangements have been made with Alabama Power to retrofit a correctly processed part on the subject serial number. "This is a formal notification; Alabama Power was notified of this situation on January 16, 2008." The coupling provided to Alabama Power did not meet the hardness requirements specified in the order. The coupler provided was annealed versus quench-hardened. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-01-27
44808 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2009-01-27 | 2009-01-27 17:11 | 2009-01-27 | PART 21 REPORT - WATER QUALITY DEFICIENCY The following information was obtained from Fisher Controls International via facsimile: Fisher Controls International issued a Fisher Information Notice: FIN 2009-02, that notified customers of an issue discovered during an internal audit of manufacturing procedures followed by Fisher Controls International LLC. Specifically, on orders processed by Fisher Controls that invoked demineralized water cleaning requirements, Fisher Controls erroneously certified that all orders met demineralized water requirements when all requirements could not be proven to be met. To meet the certification requirements, demineralized water must meet the quality requirements of NQA-1. Fisher Controls uses FMP [Fisher Manufacturing Procedure] 12B3 to verify that demineralized water used to clean parts meets NQA-1. Fisher determined that water quality testing using FMP 12B3 performed from January 1, 2001 to May 1, 2008 did not meet the test protocols. "Twenty two orders have been identified, from 500+ orders reviewed, which require either the use of demineralized water and/or NQA-1 high quality water for which Fisher cannot prove full compliance. It is important to note that this review was limited to nuclear assembly orders only. Safety-related parts orders were not included because final cleaning was done either with alcohol or acetone." The affected plants are: Indian Point 2 Seabrook Millstone (two valves) D.C. Cook North Anna (two valves) Catawba (seven valves) Oconee (five valves) McGuire (three valves) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2009-01-27
44807 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2009-01-27 10:17 | 2009-01-27 12:41 | 2009-01-27 | MANUAL REACTOR TRIP DUE TO LOSS OF 4160V BUS "Calibrations of the 'A' Unit 4160V Switchgear metering were in progress when the 'A' Unit 4160V Bus tripped. This resulted in the loss of the 'A' Feedwater Booster Pump (FWBP) and 'A' Condensate Pump (CDP). The Operating crew identified the loss of the 'A' FWBP with increasing RCS pressure and manually tripped the reactor. There were no other safety system actuations and the plant is stable at normal post-trip temperature and pressure." All rods inserted during the trip. Decay heat is being removed via steam dumps to the condenser. The electrical grid is stable with plant loads being supplied by offsite power via the startup transformer. Both vital busses are being powered from offsite. During the transient, main steam relief valves did lift but have been reseated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-01-27
44806 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-01-25 | 2009-01-26 17:29 | 2009-01-27 | AGREEMENT STATE REPORT - STOLEN PORTABLE NUCLEAR GAUGE The following information was obtained from the State of Texas via email: "[On January 25, 2009], a Thermo NITON Analyzer X-Ray Fluorescence Device Model XL3p 800 was stolen from Allied Alloys [located in] Houston, TX. The device contains a 30 mCi Am-241 source with either a QSA Global AMCL or IPL XFB-4 model source. The external radiation levels on the shipping case and instrument of <0.01 mRem/hr and the useful beam measurements are 0.3, 3, and 45 mrem/hr at 100, 30, and 5 centimeters respectively according to the SSDR sheet, MA-1159-D-102-B dated August 30, 2007. The company is considering a reward as the device is valued at $30K and a police report has been filed with [Houston Police Department]. There is some suspicion of the device being stolen by a former employee as there were other articles of value in the direct vicinity of the analyzer and this was the newest model out of six in the possession of the company. "The pertinent identification numbers of the Niton hand held analyzer are as follows: Model No. XL3p 800 Serial No. 31000 Americium 241 source SN: 07-232 Detector SN: 55276" Texas Incident No.: I-8602 * * * UPDATE FROM JISHA TO SNYDER ON 1/27/09 AT 0732 * * * The State of Texas provided the following information via e-mail: "[The licensee is] not considering an award at this time. More cameras are being installed and all Nitons will be locked up in the main building [of the licensee's facility] where anyone going near the Niton storage area will pass through at least 4 cameras or more. The was the first noticeable break-in [that the licensee has] had in 5 years at this location." Notified R4DO (Cain) and FSME EO (Burgess). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-01-29
44805 | 0 | AMETEK |  |  |  |  | 2009-01-26 | 2009-01-26 11:32 | 2009-01-26 | AMETEK PART 21 REPORT ON TYCO/POTTER & BRUMFIELD RELAYS The following information was received from AMETEK via facsimile: "COMPONENT DESCRIPTION: Electro-mechanical 14 pin relays, with AC voltages of 120 and 240, and DC voltages of 12, 24, 48 and 110. The Tyco/[Potter & Brumfield] relays were removed from the Approved Supplier Listing in 2006. The relays can be installed in Ametek Solidstate Controls equipment, or provided as a spare part. "PROBLEM YOU COULD SEE: Nuisance alarming or erratic operation of the equipment. "CAUSE: The problem appears to be an age related degradation of unknown cause. A failure analysis performed by First Energy Laboratory Services identified a potential cause as a crinkled appearance on the surface of the moving contact pads resulting in uneven contact with the opposing stationary contact pad. Over time, a layer of oxidation forms on the pads inhibiting electrical contact and increasing resistance. "EFFECT ON SYSTEM PERFORMANCE: Potential unstable output voltage caused by intermittent high relay resistance. The relays are generally used for alarm functions but can be used in control circuitry as well. "ACTION REQUIRED: Replace all Tyco/Potter & Brumfield relays listed below remaining in service with the approved Ametek Solidstate Controls equivalent. "Component: Tyco/Potter & Brumfield Relays SCI PIN 07-740001 - P&B PIN KHAU-17A18-120 SCI PIN 07-740002 - P&B PIN KHAU-17A18-240 SCI PIN 07-740005 - P&B PIN KHAU-17D18-12 SCI PIN 07-740006 - P&B PIN KHAU-17D18-24 SCI PIN 07-740007 - P&B PIN KHAU-17D18-48 SCI PIN 07-740008 - P&B PIN KHAU-17D18-110" The faulty relays are a subcomponent of AMETEK battery chargers, inverters, and uninterruptible power supplies. These types of AMETEK equipment are installed at various reactor licensees. There was no information on which licensees are affected. The manufacturer received notification of the faulty relays from Beaver Valley Power Station. The problem was revealed through a malfunction of a battery charger on 12/11/2008. The manufacturer does not believe that there is an immediate safety concern. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2009-01-26
44804 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2009-01-16 | 2009-01-23 17:53 | 2009-01-23 | AGREEMENT STATE REPORT - LOST RADIOACTIVE MATERIAL The following information was received from the Commonwealth of Massachusetts via facsimile: "A package containing 250 ÁCi P-32 was lost at Dana Farber. The package was delivered and the RP (Radiopharmaceutical) department performed a receipt survey. The package was then carried to laboratory 714. The deliverer claimed he gave it to someone in the lab. Laboratory personnel claimed not to have received it. The RP department has conducted an unsuccessful search to locate the package." Massachusetts No. MA-09 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-01-28
44803 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-01-21 11:30 | 2009-01-23 13:42 | 2009-01-23 | AGREEMENT STATE REPORT - LEAKING I-125 BRACHYTHERAPY SEEDS The following information was obtained from the State of North Carolina by fax: "[The] Licensee stores unused I-125 Brachytherapy seeds in bulk with other unused I-125 sources. A routine leak test of the bulked I-125 seeds in October yielded no removable contamination. A routine leak test of the bulked I-125 seeds in January 2009 showed removable contamination: 2.3-2.8 microCuries. "The licensee has 223 total iodine brachytherapy seeds stored in the storage container and cannot determine which seeds are leaking. 164 seeds were added to the storage container since the October leak test. "[The] Licensee has contacted [the] manufacturer (Core Oncology) to return seeds and perform assay on seeds to determine which seeds are indeed leaking. "The licensee cannot ascertain if the I-125 seeds were damaged at patient loading (by licensee physicians) or at the manufacturer." It is unknown if any patients have been contaminated. All patients are being contacted for bioassays. Total activity for all the seeds to be returned is 78.71mCi (@0.3 mCi per seed). NC Incident No. 09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-01-28
44802 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-01-13 15:00 | 2009-01-23 13:03 | 2009-01-23 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE "Licensee performing a routine radiography source exchange. New source (100 Ci) would not come out of source exchanger. Licensee Asst RSO attempted to withdraw old source (22 Ci), and old source came out of source exchanger and had to be recovered. "WB [Whole Body] Dosimetry From Landauer (confirmed) "317 [mR] WB for Asst RSO "366 [mR] WB for Radiographer who retrieved source "Dose Estimates to Extremity "7.5 Rem to left hand for Asst RSO "1.73 Rem to right hand for Radiographer who retrieved source "REACTS has received blood tube for testing for Asst RSO." The licensee is shipping both sources back to the manufacturer. Location of the event: 1721 William Road, Monroe, NC 28110 NC Incident: 09-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-01-28
44801 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-01-07 | 2009-01-22 17:29 | 2009-01-22 | AGREEMENT STATE REPORT - LOST, THEN FOUND, MOISTURE DENSITY GAUGE The following information was received from the State of Pennsylvania via email: An Applied Testing & Geosciences employee had possession of a vehicle containing a moisture density gauge. After an evening on the town, the employee had a taxi return him to his hotel as he had forgotten where he left the vehicle. The next day, the employee called in sick and then reported the vehicle stolen to local law enforcement. Later in the day, the vehicle was recovered with the gauge intact. The licensee took possession of the gauge. PA Reference Number: PA090005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-01-27
44800 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-12-04 | 2009-01-22 17:04 | 2009-01-23 | AGREEMENT STATE REPORT - DOSE ADMINISTERED TO PATIENT WAS LESS THAN 50% OF PRESCRIBED DOSE The following information was obtained from the Commonwealth of Pennsylvania via email: "Dose administered to patient was only 44% of the prescribed amount of Y90. "Cause: the treatment catheter became occluded and prevented further delivery of the Y-90 microspheres to the patient. It is not known what caused the occlusion. A later radiation survey of the catheter indicated a relative increased amount of radioactivity within the last 2cm from the tip. The catheter will be sent to the manufacturer for further analysis. "Effect to the Patient: None "Notifications : The referring physician was verbally notified of the medical event by the Authorized User. The referring physician verbally notified the patient. "Corrective Action: Equipment returned to manufacturer for repair or disposal." Dose given was 5.3 mCi of Y-90. Dose intended was 12.1 mCi. PA Reference Number: PA080033 A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2009-01-26
44799 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-01-19 17:15 | 2009-01-22 16:06 | 2009-01-22 | AGREEMENT STATE REPORT - LOST, THEN FOUND, MOISTURE DENSITY GAUGE The following information was received from the State of North Carolina via email: "N.C. Radiation Protection Section was notified on 19 Jan 2009 by the State EOC of the loss of a Troxler Model 3430 portable moisture density gauge (Serial No. 20385) possessed by ECS Carolinas under a specific license. The gauge contained two sealed sources: (1) Cesium-137, 8 mCi, source serial no. 75-1733 and (2) Americium-241:Beryllium, 40 mCi, source serial no. 47-15863. "The device was lost while being transported between job sites. While in transit, the device was on the tailgate of the transport vehicle; the device was not secured in its transport box nor was it blocked and braced. The Greensboro Police and Fire Departments were notified by the company's RSO at 17:35 [hrs.] and arrived at the scene. Efforts to find the device were not successful. NC Emergency Management was notified by the company's RSO. Instrotek [a local vendor] notified the RSO that a citizen passer-by had observed the device being struck by an SUV on Merritt Drive in Greensboro, NC. The citizen stopped and placed the device in the bed of his pickup truck and transported it to his home in Burlington, NC. The citizen notified Instrotek (telephone number on calibration label on device) of his discovery. A Health Physicist from the NC Radiation Protection Section was dispatched to the citizen's residence and arrived at 19:45 [hrs.]. The device was located on the back, screened porch of the residence, well away from any occupants of the residence. The plastic housing of device was broken, but was otherwise in good condition. Radiation surveys indicated that the sources were in the shielded position, the source rod was in good condition and in the fully retracted position. The source handle/ rod assembly was not locked. The citizen reported that no one had extended the source rod while the device was in his possession. The RSO and an Authorized User from ECS Carolinas, LLP arrived at the residence, packaged the device in an appropriate transport box, blocked and braced the box in a company pickup truck, and transported the device to the authorized storage site at their home office in Greensboro, NC. There were no exposures to radiation from these sources during this event. The Health Physicist was notified on 20 January 2008 by Troxler Electronics that it took possession of the device for damage assessment and repair. "The investigation of this event by the NC Radiation Protection Section is ongoing." NC Event Report ID No.: NC-09-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-01-27
44798 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-01-22 09:35 | 2009-01-22 18:10 | 2009-01-22 | POSITIVE FITNESS FOR DUTY TEST A non-licensed contract supervisor had a confirmed positive for alcohol during "for-cause" fitness-for-duty test. The contractor's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2009-01-22
44797 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-01-22 09:30 | 2009-01-22 17:08 | 2009-01-22 | LOSS OF PHONE COMMUNICATIONS "At approximately 0930 CST on 01/22/2009, the Monticello Nuclear Generating Plant became aware of a loss of ENS, HPN, and ERDS lines as well as a partial loss of in-coming commercial lines. Cell phone communications were not affected. The NRC Operations Center was contacted, and a back-up means of communication was established. The back-up communication methods to off-site State and Local agencies remained available. The ENS communications were conducted via commercial phone lines or a cell phone line to the NRC Operations Center. "The NRC Resident Inspector, NRC Region III, NRC Operations Center, State and local government agencies were notified. "At 1300, all communications were re-established. At 1455 communication capabilities in the Control Room, Shift Managers Office, TSC, and EOF were verified to be operating properly. Communications were lost due to a problem at the local telephone company office, and not due to any on-site equipment issues. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-01-22
44796 | 0 | CONSTRUCTION TESTING AND ENGINEERIN |  |  |  |  | 2009-01-22 10:57 | 2009-01-22 16:50 | 2009-01-22 | DAMAGED MOISTURE DENSITY GAUGE A moisture density gauge was run over by construction equipment and badly damaged. The source is not within the gauge. The RSO did not know the sources however the police on the scene identified the source as Cs-137 and that the dose rate was approximately 5 REM on contact and background at 20 feet. Location: 4424 Old Columbia Pike, Annandale, VA The state EOC was contacted and verified that a contractor was hired to clean up the source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2009-01-22
44795 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2009-01-22 | 2009-01-22 13:25 | 2009-01-22 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGNS The State of New Hampshire was notified by a Walmart corporate representative located in Bentonville, AR, of a total of three (3) tritium exit signs (TES) (which are general licensed materials) that were damaged at Walmart stores throughout the State of New Hampshire. All three signs have been properly packaged and shipped to a specific licensee authorized to receive damaged TES. There were no overexposures to Walmart personnel. All contamination has been cleaned and all areas were free released. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2009-01-29
44794 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2009-01-22 | 2009-01-22 13:25 | 2009-01-22 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The State of New Hampshire was notified by a Walmart corporate representative located in Bentonville, AR, indicating that Walmart was unable to account for 35 tritium exit signs (which are general licensed materials) that were used at one time in Walmart stores throughout the State of New Hampshire. The Walmart representative informed the State office that Walmart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state of New Hampshire was provided a listing from corporate Walmart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2009-01-29
44793 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-01-21 13:00 | 2009-01-21 16:00 | 2009-01-21 | LOSS OF CONTROL ROOM AIR CONDITIONING AND EMERGENCY VENTILATION SYSTEM "At approximately 1300 hours on January 21, 2009, a loss of control air to the Control Room ventilation system occurred. As a result, the three Control Room Air Conditioning subsystems required by Technical Specification (TS) 3.7.4, 'Control Room Air Conditioning (AC) System,' and the two Control Room Emergency Ventilation subsystems required by TS 3.7.3, 'Control Room Emergency Ventilation (CREV) System,' became inoperable. As a result, this condition could have prevented the fulfillment of the safety function for these systems. Because Brunswick has a shared control room, Unit 1 and Unit 2 entered TS 3.7.3 Required Action B.1, for two CREV subsystems inoperable (i.e. be in Mode 3 within 12 hours) and TS 3.7.4, Required Action E.1, for three Control Room AC subsystems inoperable (i.e. enter LCO 3.0.3 immediately). Operability of the Control Room AC subsystems and CREV subsystems was restored and related LCO's including TS 3.0.3 were exited at 1429 hours following the restoration of control air to the Control Room ventilation systems. "No power reduction took place as a result of the LCO 3.0.3 entry. This report applies to both Units 1 and 2 and is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The condition existed for approximately 1 hour and 29 minutes. Plant staff took immediate action to return the equipment to service. For the brief time the Control Room AC and CREV systems were inoperable, performance of plant personnel and equipment in the Control Room was not adversely affected. "The control air to the Control Room ventilation systems has been restored to service. This allowed restarting the Control Room air conditioning units. Both CREV trains and the three Control Room air conditioning units have been restored to operable. TS 3.7.3 and TS 3.7.4 Actions have been exited." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-01-21
44792 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-01-21 12:00 | 2009-01-21 12:40 | 2009-01-21 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was received from the State of Florida via fax: "Troxler gauge run over by dump truck at job site. Sources allegedly in shielded position. State inspector sent to investigate. Upper control rod bent, some damage to outer container. Sources in shielded position, radiation readings nominal. Gauge being transported to Troxler representative in Orlando for repair. No further action will be taken by this office." Sources: 40 mCi Am:Be, 8 mCi Cs-137 Florida Report: FL 09-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-01-26
44791 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-11-27 10:16 | 2009-01-20 15:01 | 2009-01-20 | INVALID ACTUATION OF CONTAINMENT ISOLATION FUNCTION "On November 27, 2008 at 10:16 Central Standard Time, while operating at 100 percent power, Grand Gulf Nuclear Station experienced an invalid actuation resulting in isolation of containment isolation valves for two different systems. A failed temperature monitoring relay resulted in the invalid actuation of the isolation logic for the Reactor Core Isolation Cooling (RCIC) and Residual Heat Removal (RHR) 'A' systems. The RCIC system was declared inoperable. RHR 'A' system operability was not affected. Appropriate procedures and Technical Specification Limiting Condition for Operations (LCOs) were entered and implemented. There were no abnormal temperatures found during the initial investigations by plant operators for the affected rooms and systems, therefore the actuation was considered invalid. The actuation was considered a complete actuation of Division 1, Group 3 and Group 4 isolation valves. Corrective actions were taken to replace the failed temperature relay. This report is made under 10CFR50.73(a)(2)(iv)(A)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.73(a)(1) |  |  |  | 0 | 2009-01-20
44790 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2009-01-20 08:07 | 2009-01-20 14:33 | 2009-01-20 | VARIAN HDR SOURCE STUCK OUT IN AN UNSHIELDED POSITION The Varian equipment representative (R. Piccolo) provided notification of the following event that occurred at the McLaren Regional Medical Center (License #21-04171 04) in Flint, Michigan. A technician was warming up a GammaMedPlus, HDR Unit, Model GM325 in preparation for a patient treatment when the Ir-192 source became stuck in the unshielded position. The Ir-192 source has an activity level of 8.3 Curies. After consulting with Varian Medical Systems, the technician unsuccessfully attempted to retract the source with the hand crank. The area is secured, and Varian Medical Systems is on-site troubleshooting the problem. The licensee will forward dosimetry for evaluation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-01-20
44789 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2009-01-07 | 2009-01-20 14:29 | 2009-01-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The state of Louisiana was notified by a Walmart corporate representative located in Bentonville, AR, indicating that Walmart was unable to account for 281 tritium exit signs (which are general licensed materials) that were used at one time in Walmart stores throughout the state of Louisiana. The Walmart representative informed the state office that Walmart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state of Louisiana was provided a listing from corporate Walmart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. Louisiana Event Report Number: LA090008. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-01-23
44788 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-12-23 | 2009-01-20 14:11 | 2009-01-20 | AGREEMENT STATE - MEDICAL MISADMINISTRATION The following was provided by the state via facsimile: Description and Analysis of event: "A medical event was discovered at 11:00 AM on January 2, 2009 involving a patient who was undergoing high dose rate brachytherapy (HDR) for papillary serous adenocarcinoma of the uterus. The patient completed 4600cGy of external beam radiation therapy on 9/11/08 and was currently undergoing 3 high dose rate brachytherapy fractions, approximately 3 cm in length, at 500 cGy per fraction. During the patient's second HDR treatment, a review of the first HDR plan showed that the tandem was not fully inserted into the cylinder. The visualization on the CT scan of the placement of the tandem being partially inserted was not recognized by the planner or reviewer of the plan. The dwell positions were therefore placed in the airspace where the tandem should have been inserted versus at the retracted location. The first fraction (12/23/08) was therefore treated approximately 6 cm distal to what was represented by the isodoses on the plan printout. The x-ray (port film) at the time of treatment also showed the tandem not fully inserted into the cylinder. "A plan was run with the isodoses placed 6 cm distal to the tip of the tandem channel. The isodoses show that the patient received dose (3 cm of active dwell positions as planned) to the distal vagina versus the proximal vagina as prescribed. "The radiation oncologist was immediately notified of the tandem placement after discovery. The prescribing physician (radiation oncologist) notified the patient and the referring physician about the variance that had occurred in the patient's treatment as well as the possible complications. "Patient Management: "The radiation oncologist explained to the patient that there was no clinically significant increase in possible complications as a result of the HDR treatment to the distal vagina for 1 fraction (12/23/08). After careful review, the radiation oncologist decided he will continue as planned with the third HDR fraction at 500 cGy. He does not expect any increase in bladder or rectal toxicity and expects to see a decrease in normal tissue toxicity. "Prevention of Future Occurrence: "1. When the nurse assembles the cylinder applicator, the nurse will measure the tandem length outside the cylinder to ensure the tandem has been inserted to the maximum extent. "2. The dosimetry and physics staff will receive an in-service on the difference in CT image based plans with an emphasis on how the tandem channel looks in the cylinder with the tandem fully inserted versus a partial insertion. "3. The physicists will begin looking at the pre-treatment port film along with the radiation oncologist prior to initiating treatment." Louisiana event number - LA090007 A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2009-01-23
44787 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2009-01-08 | 2009-01-20 13:11 | 2009-01-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Oregon was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 230 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2009-01-23
44786 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2008-05-21 | 2009-01-20 13:11 | 2009-01-21 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGNS The State of Oregon provided the following information on damaged tritium exit signs (TES) contained in 7 separate reports from Wal-Mart. 1. Serial # 256279, Activity: 11.5 Curies, Date of Damage: unknown: Store Location: 3025 Lancaster Drive, NE Salem, Oregon 2. Serial # 275536, Activity 20 Curies, Damage Date: unknown: Store Location: 3002 Stacy Allison Way, Woodburn, OR 3. Serial # 283177, Activity 20 Curies, Damage Date: unknown: Store Location: 3002 Stacy Allison Way, Woodburn, OR 4. Serial # 271065, Activity 20 Curies, Damage Date: unknown: Store Location: 2051 Newmark Ave., Coos Bay, OR 5. Serial # 286545, Activity 11.5 Curies, Damage Date: unknown: Store Location: 3600 Washburn Way, Klamath Falls, OR 6. Serial # 292245, Activity 20 Curies, Damage Date: unknown: Store Location: 135 N.E. Terry Lane, Grants Pass, OR 7. Serial # 292236, Activity 20 Curies, Damage Date: unknown: Store Location: 135 N.E. Terry Lane, Grants Pass, OR "Wal-Mart retained Shaw, an environmental services contractor with extensive experience with management of radioactive material, for its company wide program to inventory TES." Shaw has remediated the areas, if necessary, and has either returned the signs to the manufacturer for repair or proper disposal. "Wal-Mart has implemented and communicated protocols to its stores for the proper handling of TES to ensure public health and safety and protection of its employees." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2009-01-23
44785 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2008-08-27 | 2009-01-20 09:45 | 2009-01-20 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGNS The State of Utah reported that it had received information from Corporate Wal-Mart of the discovery of damaged tritium exits signs. A summary is as follows: On August 27, 2008, a report of one damaged sign was received concerning a Wal-Mart store at 10 East 1300 South, Richfield, UT; the activity of the sign was 20 Curies; the sign serial number was 306796. On September 3, 2008, a report of two damaged signs was received concerning a Wal-Mart store at 4848 S. 900 West St. Riverdale, UT; the activity of the signs was 20 Curies each; the serial numbers were 265518 and 265533. On October 30, 2008, a report of two damaged signs was received concerning a Wal-Mart store at 1052 South Turf Farm Road, Payson, UT; the activity of the signs was 20 Curies each; the serial numbers were 300305 and 300977. An environmental services contractor was retained and remediated the areas, as necessary. The signs were returned to the manufacturer for disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2009-01-23
44784 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2009-01-17 04:32 | 2009-01-17 07:25 | 2009-01-17 | MANUAL SCRAM DUE TO LOSS OF TACS "Hope Creek was manually scrammed due to a complete and sustained loss of TACS (Turbine Auxiliary Cooling System). Turbine Auxiliary cooling supplies cooling water to the main generator. A loss of cooling to the main generator resulted in a turbine and reactor recirculation pump runback. The unit was removed from service in accordance with station procedures. TACS was subsequently restored post scram. "The cause of TACS loss is under investigation. All control rods are inserted and the reactor is shutdown. All safety systems responded as required. Plant is currently stable with pressure control 800 - 1000 psi (automatic pressure control set at 880 psi) on turbine bypass valves. Level band 12.5" - 54" (level 3 - level 8) (automatic level control set at 25") feeding with 'A' RFPT in startup level control. Decay Heat removal is being maintained by the main condenser through the turbine bypass valves. No personnel injuries occurred. The plant will be maintained in the current condition while troubleshooting the cause of the loss of TACS." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2009-01-17
44783 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2009-01-16 13:28 | 2009-01-16 20:43 | 2009-01-16 | EXTREME COLD WEATHER IMPACT ON SIRENS "Based on discussions with another utility, the station reviewed the impact of the recent extreme cold temperatures for the 106 sirens in the Monticello 10-mile Emergency Planning Zone (EPZ). On several occasions during the early morning hours for January 15 and 16, 2009 the outside temperature readings in the Emergency Planning Zone (EPZ) as recorded by the station's meteorological tower temperature instruments fell below a negative twenty-two degrees Fahrenheit. A review of the siren manufacturer and the FEMA approved siren design report information determined that the sirens are considered functional between the temperature readings of -22 degrees Fahrenheit and +140 degrees Fahrenheit. "A discussion with the manufacturer's technical representative confirmed that the sirens are operational and no special testing is required when the temperature goes below and then returns within the operating temperature limits. The station is coordinating with the local county authorities to perform confirmatory testing with in 24 hours to validate the manufacturer's information. The Prairie Island Nuclear Generating plant has the same sirens as Monticello, and a test performed today confirmed the functionality of the sirens. "The current temperature at the station is within the operational limits and the local temperatures are forecasted to remain within the stated temperature range during the next week. Therefore the 106 sirens are considered functional at this time. "Sherburne and Wright Counties, and Minnesota Department of Homeland Security and Emergency Management were notified that if the temperature falls below negative twenty-two degrees Fahrenheit again, the established process of back-up route alerts is available for implementation to notify the public in the event of a nuclear emergency where the sirens are activated, but fail to respond. No press release is planned by Xcel Energy. "The NRC resident inspector was notified [by the licensee]. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-01-16
44782 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-01-16 | 2009-01-16 20:47 | 2009-01-16 | EXTREME COLD WEATHER IMPACT ON SIRENS "Based on discussions with another utility, the station reviewed the impact of the recent extreme cold temperatures for the 117 sirens in the Prairie Island 10-mile Emergency Planning Zone (EPZ). On several occasions during the early morning hours for January 15 and 16, 2009, the outside temperature readings in the Emergency Planning Zone (EPZ) as recorded by the station's meteorological tower temperature instruments fell below a negative twenty-two degrees Fahrenheit. A review of the siren manufacturer and the FEMA approved siren design report information determined that the sirens are considered functional between the temperature readings of -22 degrees Fahrenheit and +140 degrees Fahrenheit. "A discussion with the manufacturer's technical representative confirmed that the sirens are operational and no special testing is required when the temperature goes below and then returns within the operating temperature limits. The station coordinated with the local county authorities and successfully performed confirmatory testing to validate the manufacturer's information. "The current temperature at the station is within the operational limits and the local temperatures are forecasted to remain within the stated temperature range during the next week. Therefore, the 117 sirens are considered functional at this time. "Goodhue, Pierce, and Dakota Counties, the Prairie Island Indian Community, Wisconsin Emergency Management and Minnesota Department of Homeland Security and Emergency Management were notified that if the temperature falls below negative twenty-two degrees Fahrenheit again, the established process of back-up route alerts is available for implementation to notify the public in the event of a nuclear emergency where the sirens are activated, but fail to respond. No press release is planned by Xcel Energy. "The NRC Resident Inspector was notified [by the licensee]. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii)." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-01-16
44781 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2009-01-16 | 2009-01-16 17:08 | 2009-01-21 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Illinois was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 469 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state of Illinois. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state of Illinois was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. Illinois report number: IL0900003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2009-01-23
44780 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2009-01-15 | 2009-01-16 13:16 | 2009-03-06 | AGREEMENT STATE - FIRE INVOLVING RADIOGRAPHY CAMERA The following was provided by the State via e-mail: "On 1-15-09, DRH was notified by the Forrest County ERC that JANX Integrity Group had an accident with one of their darkroom trucks off Hwy 59 N., in Hattiesburg, MS. The driver for JANX struck a tree off the side of the interstate causing the vehicle to catch fire. The driver then left the scene of the accident. The radiography camera, SPEC-150, SN 150 (Ir-192, 65 Ci), was not discovered until the fire department saw a 'Caution Radiation Area' sign in the bed of the darkroom truck after extinguishing the fire. Surveys were conducted by firefighter personnel for their safety and to pinpoint the location of the radioactive device in the darkroom truck. The Forrest County ERC contacted an industrial radiography company and MS licensee located in Hattiesburg to take possession of the camera and secure it in their storage vault. The radiography camera was retrieved off the darkroom truck and out of its locked storage box by the MS licensee. The radiography camera was surveyed by the MS licensee before being transported to their storage facility. On 1-15-09, JANX retrieved the radiography camera out of storage for transport back to the manufacturer to assess the damage. "DRH took surveys of the darkroom truck and the radiography camera. Radiation measurements were as follows: 24 mR/hr at the surface of the camera; 4 mR/hr at 6 inches from the camera; levels were background at the vehicle. DRH coordinated the receipt of radiography camera between JANX and a MS licensee for delivery back to the manufacturer." MS report number - MS 09001 * * * UPDATE FROM JAYSON MOAK TO HOWIE CROUCH AT 1739 ON 1/23/09 * * * The following was provided by the State via e-mail: "On 1-15-09, swipes were taken on the camera and revealed no removable contamination. Leak test results for the source and DU shielding were received from SPEC on 1-23-09 and also revealed no removable contamination." Notified FSME EO (Chang) and R4DO (Farnholtz). * * * UPDATE FROM JAYSON MOAK (VIA EMAIL) TO JASON KOZAL AT 1232 ON 1/28/09 * * * The following was provided by the State via e-mail: "On 1-28-09, DRH received the SPEC - 150, Exposure Device S/N 150 Final Inspection Certificate from SPEC. The camera met the requirements contained in 10 CFR 34.20, ANSI N432 1980, USA/9263/B(U)-96 and SPEC's QA Program approval number 102." Notified FSME EO (White) and R4DO (Cain). * * * UPDATE FROM JAYSON MOAK (VIA EMAIL) TO JOHN KNOKE AT 1718 ON 02/20/09 * * * The following information was provided by the state via e-mail: "Source was Ir-192, 65 Ci, S/N PJ1606, Source Model G-60." Notified FSME EO (Vontill) and R4DO (Powers). * * * UPDATE FROM JAYSON MOAK TO JOE O'HARA VIA EMAIL AT 1704 ON 02/23/09 * * * The following information was provided by the state via e-mail: The State of Mississippi has taken enforcement action and cited their licensee with four violations. Notified R4DO (Gaddy) and FSME EO (Vontill). * * * UPDATE FROM JAYSON MOAK TO PETE SNYDER VIA EMAIL AT 1003 ON 03/06/09 * * * The following information was provided by the state via e-mail: "On 3/5/09 [the State of Mississippi] received a written report from JANX Integrity Group." This incident has been closed on 3/5/09. Notified R4DO (Proulx), and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2009-01-21
44779 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2009-01-15 | 2009-01-15 14:10 | 2009-01-15 | TREATMENT SITE DOSE LESS THAN PRESCRIBED "A medical event was discovered on January 15, 2009, for a patient treated at the VA Medical Center, Durham, North Carolina. "This medical event involved a patient who had undergone permanent implant prostate seed brachytherapy using iodine-125 seeds. The resulting seed distribution in the patient was associated with a D90 dose to the treatment site that was less than 80% of the prescribed dose. The circumstances are interpreted to meet the definition of a medical event under 10 CFR 35.3045(a)(1)(i). "A 15-day written report on this medical event will be submitted to NRC Region III. [The licensee] notified [the] NRC Project Manager, Cassandra Frazier (NRC Region III), of this medical event. "Department of Veterans Affairs has a Master Materials License (MML) from the NRC: License No. 03-23853-01VA. Permits are issued under the MML to VA facilities. The VA submits reports to the NRC through the VHA's National Health Physics Program office located in North Little Rock, AR. Address of permittee involved in this event: VA Medical Center, 508 Fulton Street, Durham, North Carolina 27705. VHA permit number of permittee involved in event: Permit No. 32-01134-01." A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NC | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2009-01-20
44778 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2009-01-07 | 2009-01-15 13:59 | 2009-01-15 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The State of Kansas was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 126 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. Kansas case number- KS090001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2009-01-20
44777 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-01-13 18:00 | 2009-01-14 23:00 | 2009-01-14 | AGREEMENT STATE - POTENTIAL EXTREMITY OVEREXPOSURE "Via relay by the N.C. Division of Emergency Management Operations Center, N.C. Radiation Protection Section was notified on 14 Jan 2009 by the Corporate RSO for MISTRAS Holding Group, doing business as Conam Inspection and Engineering Services, Inc/ Quality Services Laboratories, Inc. of a possible extremity over exposure. The possible over exposure occurred during a routine radiography source transfer between a QSA 660 camera containing 22 Curies of Iridium 192 (the old source) and an Ir-50 source exchanger containing 100 Curies of Iridium 192 (the new source). Difficulties in completing the exchange resulted in manual attempts to complete the transfer. The licensee is reporting at the end of the event all radioactive material was confirmed as being appropriately stored and secured. Dosimetry for the licensee staff involved in the event were overnighted to the dosimetry vendor for evaluation, results are pending. Details of the event and status confirmation are to be determined during an onsite investigation by the N.C. Radiation Protection Section on 15 Jan 2009." NC event report #: NC-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-01-19
44776 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2009-01-14 20:39 | 2009-01-14 22:53 | 2009-01-15 | ONGOING RECIRCULATING COOLING WATER LEAK AT C337A FACILITY The site staffed their Emergency Operations Center to troubleshoot an ongoing recirculating cooling water leak under the concrete floor of the C337A autoclave facility. The process in that facility automatically shutdown and is in a stable condition. Overall impact to the plant is minimal and processes continue to operate in the cascade facility. Offsite assistance has been requested. DOE, Massac County, Illinois and McCracken and Ballard Counties in Kentucky have been notified. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0220 ON 1/15/2009 FROM MIKE BOREN TO MARK ABRAMOVITZ * * * The event was terminated at 0220. The leak is not isolated but has been localized. Notified the R2DO (Rudisail) and NMSS (Davis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2009-01-14
44775 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2009-01-14 14:30 | 2009-01-14 16:46 | 2009-01-14 | CONTROLLED SHUTDOWN FOR FEEDWATER HEATER REPAIRS "Unit 2 performed a controlled shutdown from 60% power to make repairs to a low pressure feedwater heater. The unit was taken off line at 1148 today. The unit is stable in Mode 3, Hot Standby. A press release was made at 1430 today." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW | [5 empty] | 0 | 2009-01-14
44774 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2009-01-14 | 2009-01-14 16:38 | 2009-01-15 | PART 21 REPORT DUE POTENTIAL ISSUE OF AFTERLOADER SOURCE STICKING "The active source may have movement difficulties and become stuck during source extension or retraction. The problem may occur with the source outside of the HDR unit's tungsten shield. "This type of event was first seen in December 2008. "This event has occurred three times: "a) Southwest Regional Cancer Center, Austin TX - December 2, 2008 [see EN #44697] "b) Hershey Medical Center, Hershey PA - December 11, 2008 "c) Stanford University Medical Center, Stanford, CA - December 30, 2008 "In each case the problem occurred during a routine source exchange and patients were not involved. The emergency retract handle was used in each occurrence to retract the source and park it safely in the HDR unit's tungsten shield. The relationship between the source exchange and the problem is unknown." "The affected sites in the United States are as follows:" St. Joseph's - Mercy Hospital of Macomb - Clinton Twp., MI Cancer Healthcare Associates Cedars Med Ctr - Miami, FL Providence Hospital - Anchorage, AK Coborn Cancer Center - St. Cloud, MN Stanford University Medical Center - Palo Alto, CA Barnes Jewish #2 - Washington University - St. Louis, MO Mayo Clinic - Rochester, MN DeKalb Medical Center - Decatur, GA Cy-Fair Cancer Center - Houston, TX Billings Clinic - Billings, MT Palm Beach Cancer Institute - West Palm Beach, FL St. Lukes - Bethlehem, PA University of Nebraska Medical Center - Omaha, NE Geisinger Health System - Wilkes-Barre, PA Southwest Regional Cancer Center - Austin, TX Hershey Medical Center - Hershey, PA Carolinas Medical Center - Charlotte, NC Cheyenne Regional Medical Center - Cheyenne, WY Mary Washington Hospital - Fredericksburg, VA Treasure Coast Radiation Oncology - Stuart, FL Mayhill Denton Cancer Center - Denton, TX Hamilton Medical Center - Dalton, GA Providence Hospital - Everett, WA Good Samaritan Hospital - Downers Grove, IL Seattle Cancer Care Alliance - Seattle, WA * * * UPDATE FROM RICHARD PICCOLO TO JASON KOZAL AT 1240 ON 01/15/09 * * * After conferring with Region 1 (Gabriel) and NRC HQ (Flannery) the licensee is also reporting this under 10 CFR 30.50(b)(2). Notified R1DO (Burritt) and FSME (Flannery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNSPECIFIED PARAGRAPH | SAFETY EQUIPMENT FAILURE | [8 empty] | NON EMERGENCY | 1 | VA | HOS |  | 21.21 | 30.50(b)(2) |  |  | 0 | 2009-01-14
44773 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2009-01-14 11:30 | 2009-01-14 15:17 | 2009-01-14 | MANUAL ACTIONS FOR FIRE NOT IN COMPLIANCE "During review of the 10 CFR 50 Appendix R safe shutdown compliance assessment, it was discovered that a fire in either fire area 31 or 32, the Aux Feedwater Pump and Instrument Air Compressor Room, could cause the loss of the instrument air system which is credited to supply compressed air for the control room chillers. The effect of the loss of compressed air supply to the control room chillers was not fully analyzed in the Appendix R compliance assessment. "The chillers have compressed air cylinders to provide at least an 8 hour backup supply of compressed air and operators routinely validate that there is at least a 12 hour supply of compressed air and have a procedure to replace the compressed air cylinders if needed. The control room chillers are required to cool the control room to achieve and maintain hot shutdown and per the guidance in RIS 2006-10, 'Regulatory Expectations with Appendix R Paragraph III.G.2 Operator Manual Actions,' operator manual actions to replace compressed air cylinders for the loss of the instrument air compressors are not in compliance with 10 CFR 50 Appendix R. "The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). An hourly fire patrol has already been in place for fire area 31 and 32 as a compensatory measure for other issues identified in these fire areas. "The 60-day licensee event report, submitted to the Commission in accordance with 10 CFR 50.73(a)(2)(ii), will provide the results of the manual action compliance review and follow-up corrective actions." The licensee has informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2009-01-14
44772 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2009-01-13 13:45 | 2009-01-13 16:40 | 2009-01-13 | STOLEN AND RECOVERED MOISTURE DENSITY GAUGE The following information was received by from the State of Alabama via facsimile: "At 1:45 PM CST the Alabama Office of Radiation Control received a call from Gallet and Associates. They reported that one of their trucks, carrying a licensed moisture/density gauge [Humboldt Model 5001, Serial No. 707] had been stolen that morning. The truck and the gauge had been recovered; however, the truck had been set on fire when it had been abandoned." The gauge was recovered and found to be intact and undamaged. A wipe test was performed on the gauge and surrounding area and had been sent for evaluation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44771 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2009-01-07 | 2009-01-13 19:49 | 2009-01-22 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Nebraska was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 4 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. * * * UPDATE FROM THE STATE OF NEBRASKA VIA EMAIL ON 1/22/09 @ 1438 EST * * * Wal-Mart updated their report to the State of Nebraska to include an additional missing tritium exit sign. This brings the total lost signs in the state of Nebraska to five. Notified R4DO (Farnholtz), FSME EO (Chang) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2009-01-22
44770 | 0 | CONSOL ENERGY |  |  |  |  | 2009-01-12 | 2009-01-13 13:36 | 2009-01-13 | PROCESS GAUGE SHUTTER STUCK OPEN On 1/12/09 Consol Energy noted that the shutter stuck open on a pipe mounted process gage used in their facility in Bickmore, West Virginia. Consol had their RSO and Thermo-Fisher Scientific respond to the site to survey the area to ensure that the material was properly contained and that access to the area was restricted such that no one could inadvertently receive unmonitored exposure. The gauge is an Ohmart Model SR-A with a 100 millicurie Cs-137 source. The gauge is generally licensed material. Consol is currently planning remedial actions to either replace or properly dispose of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2009-01-13
44769 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2009-01-06 | 2009-01-13 11:50 | 2009-01-13 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Wisconsin was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 191 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. Wisconsin Event Report ID: WI090001. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many week | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44768 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2008-07-01 | 2009-01-13 13:58 | 2009-01-13 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGNS The State of Maine provided the following information via facsimilie on damaged tritium exit signs (TES) contained in 3 separate reports from Wal-Mart: On June 27, 2008 two reports of damaged signs were received. The following signs at the following store locations were damaged: 1. Serial #: 284986, Activity: 11.5 Ci, Damage Date: between 5/2007 and 1/2008, Store Location: 80 Waterville Commons Dr., Waterville, ME; 2. Serial #: 259008, Activity: 11.5 Ci, Damage Date: 5/2008, Store Location: 440 Payne Rd., Scarborough, ME. On August 7, 2008 a report of damage to two signs at the Wal-Mart Store at 15 Tibbets Drive, Brunswick, ME was received: 1. Serial #: 297006, Activity: 11.5 Ci, Damage Date: Unknown; 2. Serial #: 297031, Activity: 11.5 Ci, Damage Date: Unknown. "Wal-Mart retained Shaw, an environmental services contractor with extensive experience with management of radioactive material, for its company wide program to inventory TES." Shaw has remediated the areas, if necessary, and has either returned the signs to the manufacturer for repair or proper disposal. "Wal-Mart has implemented and communicated protocols to its stores for the proper handling of TES to ensure public health and safety and protection of its employees." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44767 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2009-01-09 | 2009-01-13 12:36 | 2009-01-13 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Maine was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 87 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44766 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-01-13 | 2009-01-13 11:42 | 2009-01-13 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Texas was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 1558 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. Texas Report Number I-8596 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44765 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-01-13 09:07 | 2009-01-13 09:21 | 2009-01-13 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO SCHEDULED HVAC MAINTENANCE "At 0907 on Tuesday, January 13, 2009, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems were removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "Ventilation system maintenance is scheduled to complete at 1500 on Tuesday, January 13, 2009. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM SCOTT SCHNEIDER TO PETE SNYDER AT 1534 ON 1/13/09 * * * "The TSC ventilation system air conditioning was returned to functional status at 1532 on Tuesday, January 13, 2009. This follow up notification is being made to provide closure from the initial notification under 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility. "The licensee notified the NRC Resident Inspector." Notified R3DO (Passehl). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-01-13
44764 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-01-13 02:19 | 2009-01-13 07:00 | 2009-01-13 | LOSS OF COMMUNICATIONS CAPABILITY DUE TO A FIBER OPTIC CABLE CUT At 0219 CST on 01/13/09 communications via commercial telephone and FTS system was lost due to a fiber optic cable cut in the Glen Rose, TX area. This loss of communications does not affect emergency response capability. The licensee has confirmed that communications at the EOF were unaffected. Repairs are underway with restoration anticipated within 1 hour. The licensee has verified communications capability with the NRC Operations Center using a telephone which is routed through the Dallas-Fort Worth exchange. The licensee has informed the NRC Resident Inspector. * * * UPDATE FROM TIM BENNETT TO HOWIE CROUCH AT 0733 EST ON 1/13/09 * * * Phone lines to the site have been restored. The licensee will be notifying the NRC Resident Inspector. Notified R4DO (Lantz) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-01-13
44763 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-12-10 14:54 | 2009-01-12 17:40 | 2009-01-12 | CONTRABAND INTRODUCED INTO THE PROTECTED AREA Contraband was introduced into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2009-01-12
44762 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2009-01-07 | 2009-01-12 16:05 | 2009-01-12 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The state of North Carolina was notified by a Walmart corporate representative located in Bentonville, AR, indicating that Walmart was unable to account for 266 tritium exit signs (which are general licensed materials) that were used at one time in Walmart stores throughout the state of North Carolina. The Walmart representative informed the state office that Walmart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state of North Carolina was provided a listing from corporate Walmart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44761 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2009-01-09 13:30 | 2009-01-09 17:26 | 2009-01-14 | DURING TESTING, A SPECIALTY FUELS FACILITY FURNANCE FAILED TO SHUTDOWN WHEN REQUIRED "A furnace in the Specialty Fuels Facility (SFF) was being tested in order to return it to operation. As part of the test, the airflow for the ventilation was checked to ensure that if the airflow decreased to a level below what was required per the Integrated Safety Analysis (ISA), then the appropriate furnace systems would automatically shutdown. During the test with hydrogen gas flowing into the furnace and therefore the ventilation system, the shutdown sequence shutdown the hydrogen flow when the flow was at 100%, but it did not shutdown the hydrogen flow when the flow was at 8%. There was no immediate risk or threat to the safety of workers or the public as a result of this event. "An evaluation is currently being performed. "BWXT is making this 24 hour report in accordance with 10 CFR 70.61, Appendix A (b)(1) - 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61.' "The furnace is shutdown pending further investigation." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM CHERYL GOFF TO JOE O'HARA AT 1505 ON 01/14/09 * * * "On January 9, 2009 BWXT made event notification #44761 regarding a furnace in the Specialty Fuels Facility (SFF) which failed to perform the shutdown sequence for a given hydrogen flow level required per the Integrated Safety Analysis (ISA). The furnace was shutdown pending further investigation. As a result of the ongoing investigation supplemental information to this notification is being provided. "In reviewing the programming code for the furnace a note was detected related to the flow of Carbon Monoxide (CO). Specifically, the note allowed for the continuation of the flow of CO if the temperature in the furnace was above 1000 C. Simulation testing of the validity of this note was performed and the test proved that the gas would continue to flow until the temperature of the furnace reached a level below 1000 C. "An evaluation is currently being performed. The furnace continues to be shutdown pending further investigation." The licensee informed the NRC Resident Inspector. Notified R2DO(Rudisail), NMSS EO(Davis), and Fuels Group via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2009-01-13
44760 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2009-01-09 | 2009-01-09 16:19 | 2009-01-09 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The State of Alabama was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 320 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the State of Alabama. The Wal-Mart representative informed the State Office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. Additionally, Wal-mart's report also relayed information regarding 21 damaged tritium exit signs that were used at several stores in the State of Alabama. The State of Alabama was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44759 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-01-08 | 2009-01-08 17:15 | 2009-01-08 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The State of North Dakota was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 151 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the State of North Dakota. The Wal-Mart representative informed the State Office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The State of North Dakota was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44758 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2009-01-08 | 2009-01-08 14:52 | 2009-01-08 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The State of Utah was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 71 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the State of Utah. The Wal-Mart representative informed the State Office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The State of Utah was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44757 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2009-01-07 | 2009-01-07 17:54 | 2009-01-07 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The State of New Mexico was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 206 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the State of New Mexico. The Wal-Mart representative informed the State Office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The State of New Mexico was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44756 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2009-01-07 | 2009-01-07 14:16 | 2009-01-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Minnesota was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 319 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the State of Minnesota. The Wal-Mart representative informed the State Office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The State of Minnesota was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content where known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44755 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2009-01-05 | 2009-01-06 16:59 | 2009-01-06 | AGREEMENT STATE - RECEIPT OF AN UNLABELED RADIOACTIVE MATERIAL PACKAGE The following information was provided by the State via e-mail: "On 01/05/2009, an unlabeled, unmarked package containing 278 mCi of Rubidium-82 for cardiac PET studies was received at [the University of California at San Francisco] UCSF Receiving Department. The package was surveyed with radiation levels of 17 mR/hr at the surface and 0.5 mR/hr at 1 meter. A wipe of the package was negative. The container was not the usual one that UCSF has received for incoming shipments of Rubidium-82. The Receiving Department failed to contact the RSO's office, and instead contacted Nuclear Medicine to take custody of the package. Nuclear Medicine took custody of the package and exchanged the new Rubidium-82 generator for the old one. Nuclear Medicine alerted the RSO on 01/06/09, to the matter. The package insert indicated that the package was distributed by Bracco Diagnostics in Princeton, New Jersey." The UCSF Assistant RSO contacted personnel at Bracco Diagnostics and was subsequently referred to GE Healthcare in South Plainfield, NJ. Personnel at the GE Healthcare facility are investigating the matter and will report back to the assigned State of California inspector. State of California Report No. 1725-5010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2009-01-09
44754 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-11-03 | 2009-01-06 13:28 | 2009-01-06 | AGREEMENT STATE - 5 MICRO CURIES OF RADIUM-226 FOUND IN TRASH The following information was provided by the State via e-mail: "An exclusive load of trash from a residential clean out from a dwelling resulted in a rejection at the transfer station [Allied Waste] when the radiation alarms sounded. The hauler provided the name of a person who had assisted a clean out of a deceased relative's residence in Amesbury, Massachusetts. Upon notification, they were required to hire the services of a competent consultant [Radiac Environmental Services out of Brooklyn, NY] to separate and identify the radioactive constituents. The competent consultant discovered a small knob, affixed to a machine screw assembly, located within a voluminous collection of household refuse. The consultant subsequently determined that the [knob] assembly contained 5 micro-curies of radium-226. The consultant also arranged for the proper packaging and shipment of this gadget for the relative of the deceased owner. "The package was shipped from Newbury, Massachusetts to Brooklyn, New York on November 13, 2008. The shipment arrived in New York on November 17, 2008. This matter is considered closed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2009-01-09
44753 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2009-01-05 15:00 | 2009-01-05 16:20 | 2009-01-07 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE The licensee called the State of Florida at 1500 to report a lost Troxler gauge. "The gauge fell out of the truck somewhere between the intersection of Pines Blvd. and US 27 to Florida turnpike while traveling on US 27 in Broward County. The owner has filed a police report and will offer a reward." The lost gauge was a Troxler model: 3411B, serial number: 6672 containing 40mCi AmBe and 8.7 mCi Cs-137. Florida Incident Number: FL09-002. * * * UPDATE FROM STEVE FURNACE TO JOHN KNOKE AT 1327 EST ON 01/7/09 * * * The Troxler density gauge was located and a visual examination indicated it was not damaged. Licensee is having an authorized vendor conduct a leak test on the gauge, calibrate it, and then return it to the licensee for service. Notified R1DO (Gray), FSME (D. White), ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2009-01-08
44752 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-01-05 | 2009-01-05 14:23 | 2009-01-05 | FITNESS FOR DUTY INVOLVING UNIT 2 CONSTRUCTION EMPLOYEE A non-licensed contract employee was discovered to be in possession of an illegal substance inside the Unit 2 side of the common protected area following a for cause investigation. The contract employee was working in the construction of Unit 2. The contract employee's badge and access to the plant has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee has notified both the Unit 1 and Unit 2 NRC Resident Inspectors. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2009-01-05
44751 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2009-01-03 11:55 | 2009-01-03 13:53 | 2009-01-03 | OFFSITE NOTIFICATION TO STATE AGENCY DUE TO MINOR DIESEL FUEL OIL SPILL "This 4-hour Non-Emergency notification to the NRC is being made based on a notification to another government agency per 10 CFR 50.72(b)(2)(xi). "On January 3, 2009 at 1220 the Control Room was informed by Turkey Point Fossil Environmental personnel that they contacted the Florida Department of Environmental Management and Florida State Warning Point due to a spill of fuel oil at Turkey Point Fossil Units 1 and 2. The spill was approximately 2 gallons of fuel oil leaking through a drain valve and into a storm drain leading to the cooling canal system. The state agency notifications were completed at 1235 on January 3, 2009. "The NRC Senior Resident has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2009-01-03
44750 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-12-18 | 2009-01-02 16:05 | 2009-04-27 | AGREEMENT STATE REPORT - POTENTIALLY LEAKING SOURCE The following information was provided by the state via e-mail: "On December 18, 2008, the Arkansas Department of Health, Radioactive Materials Program received a written report of a potentially leaking source at Georgia Pacific Corporation in Crossett, Arkansas, General License Number GL-0074. "The Source is a Generally Licensed Device, Honeywell, Model 4201 Series Thickness Gauge, Serial Number OV522. "On November 8, 2008 a Field Services Specialist noted abnormal readings from the device and a hole in the kapton window. "Although it appears that upon arrival at the Honeywell facility in Duluth, Georgia the source is potentially leaking it is unknown exactly when the source began to leak. According to Honeywell, no contamination was found at the licensee's facility in Crossett, Arkansas. "There is possible personnel contamination (Field Services Specialist) and the Department is continuing to investigate this event and will provide a follow up when more information is confirmed." A subsequent conversation with the State of Arkansas revealed that the source is Promethium (Pm-147) with an activity level of approximately 18.5 GBq (500 milliCuries) and the State of Georgia was notified by Honeywell of the potentially leaking source. * * * UPDATE FROM STEVE MACK TO DONALD NORWOOD VIA E-MAIL ON APRIL 27, 2009 AT 1552 HOURS * * * "The kapton window was found to be torn. The Field Services Specialist appears to have damaged the source capsule window when attempting to remove a piece of kapton window, using an unapproved procedure. "The root cause of this event appears to be a failure to follow procedures. The Field Services Specialist exceeded his procedures and appears to have damaged the source capsule. Corrective actions included re-training the Field Services Specialist and a Safety Alert was sent to all personnel. "The analysis of the potentially leaking sealed source appeared to be less than 0.005 microcuries (185 Bq). It is believed that there was no personnel contamination. The initial reports of contamination were believed to have been caused by misinterpretation of survey results. "The department considers this event closed." Notified R1DO (Miller), R4DO (Walker), and FSME EO (White). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-01-07
44749 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2009-01-02 10:09 | 2009-01-02 11:53 | 2009-01-02 | UNEXPECTED AUTOSTART OF EMERGENCY DIESEL GENERATOR DURING SURVEILLANCE TESTING "During performance of 3-PT-M62C (Rev 7) 480V Undervoltage/Degraded Grid Protection System Bus 6A Functional Test, Bus 6A was inadvertently de-energized. [Number] '32' Emergency Diesel Generator (EDG) autostarted and is supplying Bus 6A. Additionally, '32' and '33' Auxiliary Feed Pumps started due to ESF actuation based on loss of Bus 6A. "All equipment operated as required. Investigation is in progress as to the cause of loss of power to Bus 6A. Bus 6A remains energized by '32' EDG." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2009-01-02
44748 | -1 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2009-01-01 14:30 | 2009-01-01 21:06 | 2009-03-02 | TWO EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE DUE TO COMPONENT FAILURE "EVENT DESCRIPTION: During return to service testing for Emergency Diesel Generator (EDG) #3, it was noted that the fuel rack limiting cylinder was not returning to its non-limiting position. The fuel rack limiting cylinder is designed to limit the stroke distance of the fuel rack assembly during the initial EDG start sequence. Once the EDG is at rated speed, ~10 seconds, the fuel rack limiting cylinder should return to its non-limiting position. Failure of this component to operate as expected may have prevented EDG #3 from fulfilling its safety function during the postulated Loss of Off Site Power and/or Loss of Coolant Accident conditions. As a result, EDG #3 remains inoperable. "During performance of subsequent surveillance testing on the remaining EDG's (#1, #2, and #4), in accordance with Technical Specifications, a similar condition as described above existed on EDG #4. EDG's #1 and #2 did not exhibit the same behavior and therefore, these EDG's remained operable during this sequence of events. Consequently, EDG #4 was declared inoperable at 1430 on 1/01/09. Failure of this component to operate as expected may have prevented EDG #4 from fulfilling its safety function during the postulated Loss of Off Site Power and/or Loss of Coolant Accident conditions. The concurrent failure of this component on EDG #3 and EDG #4 may have prevented on-site emergency power to Emergency busses 3 & 4 and thus the fulfillment of a safety function needed to mitigate the consequences of an accident. "INITIAL SAFETY SIGNIFICANCE EVALUATION: Plant operation is being maintained within the limiting conditions of the license expected. However, transient analyses relating to accident mitigation could have been impacted due to the inability to ensure emergency on-site power supply to Emergency busses 3 & 4. Off-site power and the grid have been stable during the time period both EDG's were inoperable. "CORRECTIVE ACTIONS: The fuel rack limiting cylinder for EDG #4 was repaired and EDG #4 was restored to Operable on January 1, 2009 at 1755 EST. Actions required per technical specifications for 2 EDG's were exited within the required time frame. Repair efforts are in progress for EDG #3." The licensee informed the NRC Resident Inspector. * * * RETRACTION PROVIDED BY LEE GRZECK TO JASON KOZAL AT 1530 ON 3/2/09 * * * "On January 1, 2009, at 2106 hours, the Control Room Shift Manager made a notification (i .e. Event Number 44748) to the NRC Operations Center in accordance with 10 CFR 50.72 (b) (3) (v) (D) (i.e., any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident). The notification was made due to two Emergency Diesel Generators (EDGs) being declared inoperable. During return to service testing for BSEP's EDG 3, it was noted that the fuel rack limit cylinder was not returning to its non-limiting position in a timeframe consistent with prior observations. The fuel rack limit cylinder is designed to limit the stroke of the fuel rack during the initial EDG start sequence, preventing too much fuel from being provided to the engine cylinders on initial start. Once the EDG is at half-rated speed (i.e., in approximately 5 to 8 seconds), the fuel rack limit cylinder should be released to return to its non-limiting position. Failure of this component to operate as expected may have prevented the EDG from fulfilling its safety function during the postulated Loss of Off-site Power (LOOP) and/or Loss of Coolant Accident (LOCA) conditions. As a result, EDG 3 was conservatively declared inoperable due to the potential for the unexpected response of the fuel rack limit cylinder to impact Design Basis Accident (DBA) transient loading criteria. "During performance of subsequent surveillance testing on the remaining EDG's, (i.e.,1,2, and 4), in accordance with Technical Specifications, a similar condition was identified on EDG 4. EDGs 1 and 2 did not exhibit the same behavior and therefore, these EDGs remained operable during this sequence of events. Consequently, EDG 4 was also conservatively declared inoperable at 1430 on January 1, 2009. The concurrent failure of this component on EDG 3 and EDG 4 may have prevented the onsite emergency power from fulfilling its intended safety function needed to mitigate the consequences of an accident. "Basis for Retraction "Further investigation has demonstrated that both EDG 3 and EDG 4 were fully operable. The EDG 3 evaluation concluded that the fuel rack limit would remain in effect for approximately seven (7) seconds after the diesel output breaker closed during a LOOP loading event or a design basis LOOP/LOCA loading event. After that, the fuel limit cylinder would not have limited the governor response in any way. The generator capacity during the first seven seconds of load acceptance at the fuel rack limited position would be sufficient to ensure proper acceleration of the 480-volt design basis loads and the Nuclear Service Water pump. These are the only loads expected to start during the first seven seconds of the EDG loading. The generator frequency response during the acceleration of these loads would be well within the EDG design limits. The Residual Heat Removal and Core Spray pumps are sequenced onto the EDG at 10 seconds and 15 seconds, respectively, following the closure of its output breaker and are not affected by the fuel limiter impairment. The EDG 4 evaluation is bounded by the above analysis. "Therefore, the fuel rack limiter impairment would not have prevented either EDG 3 or EDG 4 from fulfilling their intended safety function. On this basis, this event is not reportable under 10 CFR 50.72(b) (3) (v) (D). "Investigation of this condition is documented in the corrective action program in Nuclear Condition Report (NCR) 312876. "The NRC resident was notified of this retraction." R2DO (Musser) has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-01-01
44747 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2009-01-01 00:42 | 2009-01-01 10:55 | 2009-01-01 | SAFETY PARAMETER DISPLAY SYSTEM INOPERABLE "This 8-hour non-emergency report is being made based upon requirements of 10CFR50.72(b)(3)(xiii) which states, 'The licensee shall notify the NRC as soon as practical and in all cases within eight hours of the occurrence of any event that results in a major loss of emergency assessment capability, off site response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or off site notification system)'. "At 0430 ET on Thursday, January 01, 2009, Operators discovered that the Plant Process Computer (PPC) typer display output was not updating. In addition all keyboard control was lost. The Safety Parameter Display System (SPDS) Computer Display was updating, but the operators were not able to change the display to alternate views rendering the SPDS system degraded to the point of not being able to perform its monitoring function. This condition initially began at 0042 on 01 January 2009. "All Control Room panel indicators and annunciators continued to respond properly providing operators with non-computer based emergency assessment capability. The PPC was secured for troubleshooting at 0746 on 01 January 2009." "An update to this notification will be made after repairs are completed and the SPDS is returned to service." The NRC Resident Inspector has been notified. * * * UPDATE AT 1431 EST ON 01/01/09 FROM ERIC KELSEY TO S. SANDIN * * * "On Thursday, January 01, 2009 at 1140 ET, the Plant Process Computer (PPC) was successfully restarted. The performance of the PPC and SPDS was monitored for approximately one hour. SPDS was declared operable at 1300, restoring full emergency assessment capability." The licensee will inform the NRC Resident Inspector. Notified R1DO (Dentel). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2009-01-01
44746 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-12-30 11:13 | 2008-12-30 16:36 | 2008-12-30 | NON-FUNCTIONAL STEAM EXCLUSION / CONTROL ROOM EXCLUSION ZONE (CREZ) BARRIER "On 12/30/08 at 1113 an Operator transiting though a steam exclusion / CREZ door found the door sweep separated from the door. This prevented the door from performing its Steam Exclusion and CREZ boundary functions as the opening, due to the missing sweep, exceeded the allowable opening size for the respective functions. "Repairs were completed on the door at 1157 on 12/30/08. While the door sweep was not intact, the barrier was non-functional. In accordance with TRM 3.0.9 Section A.1 all equipment supported by that steam exclusion barrier was immediately declared inoperable. This zone includes both trains of Control Room Post Accident Recirculation and the Control Room itself. TS 3.0.c was entered when the sweep was identified degraded and exited following repairs. "Therefore, this is reportable under 10CFR50.72(b)(3)(v), 'Any event or condition that at the time of discovery could have prevented the fulfillment of a safety function', and under 10CFR50.72(b)(3)(ii)(B), 'any event or condition that results in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety'. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2008-12-30
44745 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-12-29 06:15 | 2008-12-29 11:19 | 2008-12-29 | LOSS OF ENS AND COMMERCIAL PHONE SERVICE At approximately 0615 on December 29, 2008, it was determined that the Emergency Notification System (ENS) and commercial telecommunications capability were out of service. The condition impacts both the Control Room and the Technical Support Center. The problem has been determined to be an offsite issue with the telecommunications provider. Immediately after discovery of the condition, communications capability via satellite phone was tested and established between the Palisades Control Room and the NRC Operations Center. In addition, if needed, the satellite phone will be used to initiate call-out of the emergency response organization and to contact the regional load dispatcher. This condition did not affect the ENS or commercial capabilities at the offsite Emergency Operations Facility. The telecommunications provider has not provided an estimated repair time. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2104 EST ON 12/29/08 FROM MULFORD TO HUFFMAN * * * "The telecommunications provider restored full ENS and commercial telecommunications capability to the Palisades Nuclear Plant at approximately 2100 EST. The condition was caused by an offsite fiber-optic cable that had been accidentally severed." The licensee notified the NRC Resident Inspector. Notified the R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-12-29
44744 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-12-28 04:45 | 2008-12-28 13:59 | 2009-02-06 | 24 HOUR REPORT - ACTUATION OF LEAK DETECTION SYSTEM DUE TO MINOR PROCESS GAS LEAK "On 12/28/2008 at 0445 the C-337 unit 5 cell 3 PGLD (process gas leak detection) head located on stage 8 actuated. Operators responded to the alarm and performed sampling in the area. The sample result indicated 3 ppm of HF at the stage 8 compressor. To stop the release the cell was taken off-stream and the pressure was reduced to below atmosphere. Investigation indicated that a UF6 release had occurred. The amount of material released has not been determined. "The actuated PGLD head is Q safety system component. At the time of the incident the cell was operating in a mode which required the system to be operable. This is being reported based on SAR 6.9 Table 1, J.2 as an Unplanned Actuation of a Q Safety System. "The NRC Senior Resident Inspector has been notified of this event." The licensee states that a compressor seal appears to have failed. The amount of material released is characterized as on the order of a few grams. Material release was only in the vicinity of the compressor. There was nothing unusual or not understood and all systems functioned as required. There was no offsite release or personnel contamination resulted from this event. * * * RETRACTION PROVIDED ON 02/06/09 AT 1427 FROM BEASLEY TO KLCO * * * "A subsequent review by USEC Regulatory Affairs concluded that the UF6 Release Detection System detectors installed 'above the `B' seals on the axial flow compressors' (SAR 3.3.5.9.5), and the detectors for the instrument cubicles do not 'prevent or mitigate the consequences of postulated accidents that could result in a member of the general public located offsite being exposed to EG (Evaluation Guidelines)-1 or EG-2 guideline values' (SAR 4.2.2). Therefore, they do not meet the criteria to be classified as 'Q' (SAR 4.2.2). "The safety equipment actuation reporting criteria (SAR 6.9-1 J.2) requires NRC to be notified of actuations of "Q" systems resulting from events that have the potential for significant impact on the health and safety of personnel, which are defined in the criteria as those events where actual plant conditions existed that the system was designed to protect against. Since the referenced UF6 Release Detection System detectors do not meet the criteria to be classified as "Q" and do not protect against a postulated accident that could result in a member of the general public being exposed to EG-1 or EG-2 guideline values, the actuations would not be reportable under this criteria. "Summary: - the B-end seal PGLD [Process Head Leak Detector] head is not required to be 'Q' - the postulated release from the B-end seal cavity does not have significant impact on personnel. - A release from the B-end seal cavity is not a condition that the PGLD system is designed to protect against. "The NRC Senior Resident Inspector has been notified of this event retraction." Notified R2DO (Rudisail) and NMSS (Kotzalas). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-12-28
44743 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-12-27 14:18 | 2008-12-27 18:36 | 2008-12-27 | AUTOMATIC REACTOR TRIP AS A RESULT OF A GENERATOR TRIP "At 1418 on 12-27-08 Braidwood Unit 2 experienced an automatic Reactor Trip. The Reactor Trip red first out annunciator was Turb[ine] Trip above P8 Rx Trip. At the time of the trip the Unit Aux Transformer [UAT] 241-1 sudden pressure relay actuated causing a main generator trip which resulted in a main turbine trip which resulted in a Reactor Trip. Also at the same time as the Reactor Trip, the 2C Heater Drain Pump tripped on phase A over current. Damage was subsequently noted on the pump motor terminal box. No fire or smoke was observed at UAT 241-1 or the 2C Heater Drain Pump. "After the Reactor Trip occurred, all four steam generators reached their low-2 Reactor Trip setpoints and the pressurizer reached its low pressure Reactor Trip setpoint all of which is an expected response on a trip from full power. Steam generator levels and pressurizer pressure have been restored. Both the 2A and the 2B Auxiliary Feedwater Pumps auto started on the low-2 steam generator levels as expected. All control rods fully inserted into the core. "No secondary relief valves lifted and no secondary steam was released as a result of the Reactor Trip. Steam generators are now being filled by the Startup Feedwater Pump and the Auxiliary Feedwater Pumps have been placed in standby. The main steam dumps are in service to the main condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. "This report is being made per 10CFR 50.72(b)(2)(iv)(B) for RPS actuation, 4 hr [notification], and per 10CFR 50.72(b)(3)(iv)(A) for automatic actuation of the Auxiliary Feedwater System, 8 hr [notification]." The electrical line up transferred to the normal shutdown configuration with standby diesel generators and safety systems available. There was no impact on Unit 1. The licensee plans on issuing a press release and has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-12-27
44742 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-12-26 20:43 | 2008-12-27 14:19 | 2008-12-31 | PROCESS GAS LEAK DETECTION SYSTEM INOPERABLE "At 2043 CST, on 12-26-08 the Plant Shift Superintendent (PSS) was notified that C-337 Unit 6 Cell 9 was above atmospheric pressure and the UF6 Release Detection (PGLD) System was inoperable. The cell had been running below atmosphere earlier in the day but a new gradient was put in and load movement caused pressure to go above atmosphere. The PGLD System for Unit 6 Cell 9 had been inoperable for an extended period of time due to wiring problems. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell are operable during steady state operations above atmospheric pressure. Even though the increase in cell pressure was due to load movement which is transient in nature, it was determined that the pressure had been above atmosphere for about four and a half hours, which is longer than the typical transient. With the Unit 6 Cell 9 PGLD system inoperable, none of the required cell heads were operable. TSR LCO 2.4.4.1.B.1 was entered and a continuous smoke watch was put in place within one hour. This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." * * * RETRACTION ON 12/31/2008 AT 1716 FROM TONY HUDSON TO MARK ABRAMOVITZ * * * "A subsequent review of the cell pressure proved that the cell pressures were below atmosphere at all times with the exception of one pressure spike of approximately 20 minutes. Since the cell was not operated above atmosphere and the TSR does not require PGLD systems to be operable during short term pressure transients, reporting under 10CFR76.120 is not required." Notified the R2DO (Lesser) and NMSS (Lorson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-12-27
44741 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2008-12-22 15:00 | 2008-12-23 14:30 | 2009-01-21 | UTAH AGREEMENT STATE REPORT The State of Utah reported that one of their licensees, Chevron USA, Inc., reported a source disconnect on a custom made Ronan level density gauge at their refinery. The gauge was located in a dry storage tank with two pressure vessels inside. The source was inside the storage tank and was retrieved by a health physics contractor. The source is currently stored at the licensee's facility in a locked storage shed, surrounded by lead bricks. The licensee is awaiting the arrival of the Ronan representative on-site. There were no excessive exposures to either workers or the public. The source was 100 mCi of Cs-137 and is a Model SA-4. * * * UPDATE AT 1416 ON 1/21/09 FROM DAVID HOGGE TO MARK ABRAMOVITZ * * * The following information was submitted by the state by fax: "Approximately 3:00 PM on December 22, 2008, Chris Crossman RSO from Chevron called to report that a Ronan Model SA-4 source holder containing a Cesium-137 source with approximately 100 mCi (s/n: 2231 CM) became unattached from a belt that the source holder was clamped to and fell to the ground and landed inside the storage silo it was mounted to. "Upon discovery, the RSO was notified and the area was immediately cordoned off, and perimeter access was maintained. A service licensee was called to the facility to perform surveys of the area and retrieve the source. The source was sequestered and placed into a lead brick cave in a secured storage shed on the licensee's premises. Ronan Engineering, who built this custom device for Chevron, has been contacted and they indicated that they will be out sometime after the first of the year to re-install the source. "On January 13, 2009, a reciprocity inspection and investigation by the Utah DRC was performed at the Chevron Refinery with a Ronan representative, [DELETED], and [DELETED] the Chevron instrument technician who initially reported the incident. "The source holder is comprised of an 18 inch stainless steel rod with a clamp at one end. This clamp, the 'tape grabber,' clamps to the end of a guide belt. Over the clamp is a stainless steel threaded sleeve, held in place with a small tension screw. At the opposite end of the source rod is the Cs-137 source mounted inside the stainless steel rod. Over the source is a cylindrical collimator which can open to fine tune the exposure field. The source rod is mounted inside a dry 'guide tube' that is raised and lowered inside the tank, via an electronic pulley mechanism. The pulley also controls in tandem, at the same level as the source, a detector mounted on the outside of the tank, also in a dry guide tube. "By using a dummy source holder for comparison, the source holder and clamp were briefly examined while inside the lead cave. The source holder was found intact and a previously done leak test indicated no leakage from the source. Closer scrutiny of the clamp end (the Tape Grabber) revealed that the set screw that holds the tape grabber together had partially loosened. Furthermore, small tension screw that holds the outer sleeve in place had worked itself loose and somehow sheared off. With the inner screw loose and the outer screw the weight of the source holder is all that was needed to pull the guide belt out of the clamp. "Root Cause: Failure of equipment to perform as designed. Poor design and testing of design contributed to the failure of this device. "Corrective Actions: The licensee called Rocky Mountain Health Physics [RMHP] who came out and relocated the source and source holder to a secure storage shed on the licensee's premises. The area where the source had fallen was roped off and all personnel in the immediate area were escorted away. RMHP wipe tested the source holder and there was no evidence of a leaking source. The licensee then called Ronan Engineering to report the failure of the device and Ronan indicated they would send a representative to the refinery in January 2009." Utah Incident Number: UT 08-0006 Notified the R4DO (Farnholtz) and FSME (Chang). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2008-12-26
44740 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-12-23 07:49 | 2008-12-23 10:36 | 2008-12-23 | DEGRADED SAFETY EQUIPMENT "Area 600 uses a flammable gas as part of its operation. IROFS [Items Relied On For Safety] FIRE6-6 is a control that prevents the flammable gas from exiting the main process equipment and being released into an attached glovebox. FIRE6-6 makes use of a dual door system in which only one (1) door is allowed to be open at a time and the chamber between the doors is purged when both doors are closed. The accident scenario of concern is release of the flammable gas into the glovebox where it could mix with oxygen, creating a potential for an explosion inside Building 302. Additionally, IROFS FIRE6-8, 6-1 and 6-9 ensure an inert gas purge occurs prior to opening the main process equipment to the glovebox and are also credited as IROFS. "The equipment associated with FIRE6-6 is designated as Safety Related Equipment (SRE) and is functionally tested annually. The regularly scheduled SRE Test was performed on December 23, 2008, and the purpose of the test is to demonstrate that each door remains closed while the other door is opened. The test failed because when the first door was opened, the second door also opened slightly (approximately one (1) inch). Though there are mitigating factors such as potential dilution of the flammable gas through the glovebox ventilation system, it was determined that IROFS FIRE6-6 was degraded and that the performance criteria of 10CFR70.61 were not met. "A similar event was reported to the NRC (#44584) on October 21, 2008 for similar equipment in Bldg 302. However, the cause of the previous IROFS failure was due to a blocked speed controller which failed to bleed off air. The blocked speed controlled is unrelated to the current IROFS failure. "POTENTIAL CONSEQUENCES: Potential explosion in a glovebox and release of radiological material and exposure to the worker. No actual explosion or radiological exposure occurred. "SEQUENCE OF OCCURRENCES: The event occurred due a degraded IROFS that was discovered during a periodic functional test. Initial investigation indicates an airline solenoid valve is leaking by. "ACTIONS TAKEN: Operations has closed the flammable gas supply for Area 600 Bldg 303 until the equipment associated with FIRE6-6 is fixed and the SRE test passes." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-12-28
44739 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-11-26 | 2008-12-22 17:37 | 2008-12-22 | TEXAS AGREEMENT STATE REPORT The following information was received from the State of Texas via email: "While removing gauges from the vessels they were attached to, in response to an investigation into a source disconnect on a different gauge [see EN #44609], the licensee found that a second source had separated from its operating rod and was located inside the insertion well. The source will remain in the well until its removal can be scheduled. The area has been isolated. Since the source separated inside the insertion well near its normal operating position, there was no additional exposures to members of the public. Two similar gauges were closed, removed from their mountings, and placed in storage. Four other devices containing radioactive sources have been closed and the shutters locked. Surveys have been completed to verify the sources are inside these gauges. "The gauge involved is a Thermo Measure Tech Model 5191 level measurement gauge serial number B45, containing a 253.4 milliCuries (decay corrected) Cesium (Cs) - 137 source serial number B45. "The licensee stated that they had informed the State of the event on 11/26/08." Texas Report No. I-8594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-12-25
44738 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2008-12-21 08:22 | 2008-12-21 11:42 | 2008-12-21 | WEATHER RELATED LOSS OF EMERGENCY SIRENS "This telephone notification is provided in accordance with 10 CFR 50.72(b)(3)(xiii) to report complications from an ice storm, including a loss of power, which has disabled seventeen (17) of the fifty EP sirens (34%). The sirens were lost at 07:22 CST and have not been restored. "This meets the threshold of Reportability based on the loss of a public notification system. "Restoration efforts are underway and are expected to occur as soon as reasonably possible with the current winter weather conditions. "At the time of the event, Unit 1 is at 80% power for scheduled surveillances and Unit 2 is at 98% power due to end of cycle conditions, and neither Unit power level is related to this event. "Unit 1 will return to full power as scheduled and Unit 2 will remain at 98% power and both units are unaffected by the loss of power." Twelve of the lost sirens were due to a loss of power. Five were lost due to a loss of communications with the data center. The licensee notified the NRC Resident Inspector. | 80 | 98 | 0 | 80 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-12-21
44737 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-12-20 10:45 | 2008-12-20 17:07 | 2008-12-20 | MOMENTARY LOSS OF 345KV OFFSITE POWER "At approximately 1045 hours on Saturday, December 20, 2008, while in a Hot Shutdown condition, Pilgrim Station experienced a momentary loss of all 345kV off-site power to the Startup Transformer (SUT). As a result, the following safety system actuations occurred: automatic Reactor Protection System (RPS) actuation (all control rods were previously inserted), automatic start of both Emergency Diesel Generators (EDG) and loading of their respective emergency buses, automatic actuation of Primary Containment Isolation Systems (PCIS) Groups I, II, VI and Reactor Building Ventilation, manual initiation of the High Pressure Coolant Injection (HPCI) system for reactor pressure control, and manual initiation of the Reactor Core Isolation Cooling (RCIC) system for reactor level control. All systems functioned as designed and expected. "Because power from an off-site source remained available from the 23kV Shutdown Transformer, the criteria for declaration of an Unusual Event were not met (Pilgrim EAL 6.3.2.1). "345kV power was automatically restored to the Startup Transformer via breaker reclose logic. Restoration of normal on-site power to all 4kV buses is complete and efforts to return systems to normal shutdown alignments are in progress. "Current plans are in place to maneuver the plant to a Cold Shutdown condition as necessary to support recovery actions. "The NRC Resident was on-site at the time of the event and has been notified. "There was no threat to the health or safety of the public as a result of this event." The loss of power was caused by a breaker icing in the onsite switchyard. The switchyard breakers were inspected for icing. The licensee notified the State of Massachusetts. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-12-20
44736 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2008-12-20 12:12 | 2008-12-20 14:23 | 2008-12-20 | MANUAL REACTOR TRIP WHEN CONTROL ROD BANK INSERTED WITHOUT OPERATOR ACTION "Arkansas Nuclear one Unit 1 manually tripped from 100% power due to control rod mechanism group 7 unexpectedly dropping from 90% to 70%. No Primary safeties lifted. Secondary safeties lifted for approximately 1 minute. Emergency feedwater did not actuate and was not needed. Post trip response was normal and the plant is stable in mode 3. Post transient review is in progress." All control rods fully inserted on the trip. The plant is in its normal shutdown electrical lineup. Steam generator level is being maintained using aux feed and steam is being dumped to the main condenser through the turbine bypass valves. There is no primary to secondary leakage. The licensee notified the NRC Resident Inspector, the State of Arkansas, and the Arkansas Department of Health. See similar event number 44716. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-12-20
44735 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-12-19 18:31 | 2008-12-19 21:52 | 2008-12-19 | AUTOMATIC REACTOR SCRAM DUE TO LOAD REJECT "On December 19, 2008, at 1831 hours with the reactor at 100% core thermal power (CTP) an automatic reactor scram occurred. It appears the scram occurred as a result of a load reject experienced during a severe winter storm. Three of the four safety relief valves opened in response to the event. Primary Containment Isolation System (PCIS) Group 2 (sample valves) and Group 6 (reactor water cleanup system) and the reactor building isolation system (RBIS-secondary containment) isolated as designed (all have since been restored) on the reactor water level +12 inches setpoint due to normal vessel shrink. Initial review indicates all safety-related systems responded as designed. Off-site power has been maintained; however the two 4kv safety related buses (A5&A6) were conservatively placed on the station emergency diesel generators due to potential grid stability concern. Currently, the reactor mode select switch (RMSS) is in the Shutdown position; the reactor scram has been reset; the reactor is being maintained at approximately 940 psig, with pressure being maintained by the main turbine by-pass valves; and reactor water level is being maintained at normal levels of 29 inches with the main condensate and feedwater system. Station maintenance personnel are assessing the status of the station switchyard. Once this activity is complete the duration of the forced outage and recovery plans will be determined." All control rods fully inserted on the scram. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-12-19
44734 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2008-12-18 | 2008-12-19 10:23 | 2008-12-19 | MISSING NRD STATIC ELIMINATOR "The Agency [Iowa Department of Public Health] was notified by the General License Registrant of a missing NRD Static Eliminator, model P-2021-8201, serial number A2FY911. The discovery was made during the annual renewal of the registration. The RSO for the company stated that the device was used to eliminate static on a part they were molding. The operators had the device hanging over a barrel and apparently the device became unscrewed from the gun and was disposed of in the trash. The registrant has developed a sleeve to assist in holding the device on the guns. In addition, the RSO instructed the shift foremen to check the devices to ensure they are properly secured to the guns. The Agency [Iowa Department of Public Health] called NRD. Inc. to verify that the device was not returned to the manufacturer. NRD Inc. stated they did not receive the device. "Corrective Action: (1) Sleeve used to help hold the device on the gun, and (2) Additional oversight to ensure devices are properly secured to guns." The Po-210 source activity is 10 milliCuries. The state considers the material to be lost not recoverable, and the event is closed. Iowa Report: IA080003. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2008-12-24
44733 | -1 | TRINITAS HOSPITAL |  |  |  |  | 2008-12-17 14:00 | 2008-12-18 17:41 | 2008-12-31 | MEDICAL DOSE LESS THAN 50 PERCENT OF PRESCRIBED DOSE "Suspected movement of catheter during endobronchial high dose rate remote afterloading treatment procedure may have resulted in a single fraction of a multifraction treatment to differ from the prescribed dose by more than 50%. [35.3045(a)(1)(iii)]. "The intended dose was 500cGy to the Rt Bronchus (lung). "Both the patient and the referring physician were notified by the authorized user of the possibility the intended treatment site did not receive full dose. "1. Patient had endobronchial catheter placed in Rt Bronchus in the endoscopy department. Catheter was taped in place and position was marked. "2. Patient was scanned in CT simulation room by therapist to determine catheter location and treatment dwell positions. "3. Patient treatment plan was created by physicist and approved by the authorized user. Second calculation check was performed. "4. Patient was monitored by nursing during the treatment planning process. "5. Patient was brought into HDR treatment room by therapist. "6. Authorized physicist and authorized user connected the treatment applicator to the HDR unit. "7. Technologist monitored patient on the camera system. "8. Treatment was administered as planned. "9. Patient was disconnected from the HDR unit. "10. Technologist removed catheter post treatment, noted the catheter she pulled out was relatively short compared to the planning scan. "11. Technologist notified the authorized user and authorized physicist. "12. Both individuals notified the RSO. "13. RSO investigated and interviewed individuals involved. "14. AU not sure at what point the catheter moved. "Patient may have dislodged catheter when coughing or wiping mouth secretions. "Actions to prevent re-occurrence: "1. Authorized user will remove all endobronchial catheters post treatment in the future to prevent any ambiguity with regard to length of catheter in patient. "2. Check marked position of the catheter at CT and both pre and post treatment prior to catheter removal. "3. Measure catheter length outside the naries prior to planning CT, prior to treatment, and post treatment as a second check to the marked position. "The Pulmonologist and Authorized user will perform a bronchoscopy in about 2 weeks [to determine if misadministration occurred]. Treatment reactions outside the planned treatment site will be evaluated and determination of treatment in an unintended area will be determined." A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 12/31/2008 AT 1507 FROM LINDA VELDKAMP TO MARK ABRAMOVITZ * * * "Basis for initial report: Basis for the initial report was the possibility that a medical event may have occurred. It was uncertain whether the endobronchial catheter moved before, during, or after the treatment. The patient's clinical response suggests that the catheter was correctly positioned during the treatment. "Evidence supporting appropriate treatment administered: Authorized user (AU) continued to follow the patient closely since administration of treatment on 12/17/08. AU reported on 12/18/08 and 12/24/08 in patient follow-up no clinical evidence exists that would support a mistreatment. The AU reported, the patient was initially admitted with hemoptysis which resolved post treatment. In addition, the AU reported the patient has 'no treatment related toxicity, no pain, no discomfort and is feeling very well.' The AU stated she does not believe there was a medical event and based on the clinical evidence and follow-up there was 'no indication of a misadministration.' Based upon the aforementioned, the AU requests the medical event be retracted. "Change in follow-up plan: Patient was discharged to another facility for treatment of an unrelated condition. AU reported based on patient improvement no additional treatment or bronchoscopy was required at this time. Subsequent treatment planned after discharge from other facility in several weeks. "Process improvement steps identified and already implemented: 1. All endobronchial catheters will be removed by the AU post treatment. 2. Current procedures will be modified as follows: At the time of insertion the catheter will be securely taped in place. A physical measurement of the catheter length extended beyond the nares/securing tape in reference to an indexing mark on the catheter will be immediately conducted after catheter insertion by the AU and/or AMP, verified by the non-measuring party and recorded in the patient record. In accordance with standard operating procedure the catheter will continue to be marked with a permanent marker for visual check and recorded. These measurements will be rechecked and recorded prior to CT imaging for planning, just prior to treatment and post treatment. Significant deviations in measurement will be reported to the AU and will require re-imaging to verify catheter placement pre-treatment." Notified the R1DO (Dentel) and FSME (Bubar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-12-24
44732 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-12-18 | 2008-12-18 15:54 | 2008-12-22 | DEFECTIVE OPTICAL ISOLATORS "Duke Energy Carolinas, LLC (Duke) herein makes the following notification under 10CFR21.21(d)(3)(i) of defective digital optical isolators. The isolators are Commercial Grade Items dedicated by Duke. Failure analysis conducted by the manufacturer determined that a manufacturing defect with the isolator capacitor will cause the output voltage to drop when the isolator is not energized and there is a very light load on the output. The subject digital optical isolators are Model 175C180, manufactured by E-max Instruments (also known as Electro-Max) 13 Inverness Way, South Englewood, CO 80112. These digital optical isolators could be utilized in a variety of applications at Duke's McGuire and Catawba nuclear stations. There are no known applications for these digital optical isolators at Oconee. "Initial Safety Significance: None. Defective digital optical isolators were never installed. Duke protocols require the conduct of a pre-installation bench test and a post installation test to assure these isolators perform satisfactorily in service. E-max Instruments has issued a Model 175C180 recall for all uninstalled isolators. Duke has returned all uninstalled digital optical isolators to the supplier. Duke is the only known nuclear utility purchasing E-max Instruments Model 175C180 digital optical isolators. "The McGuire and Catawba Senior NRC Resident Inspectors were notified of this Part 21 notification on Dec 18, 2008." * * * UPDATE FROM JIM EFFINGER TO PETE SNYDER AT 0810 0N 12/22/08 * * * McGuire Nuclear Station clarified that one of the defective digital optical isolators mentioned in the second paragraph above was scrapped, one was sent to Westinghouse Electric of Pittsburgh for a compatibility test program and the rest of the defective digital optical isolators were returned to the supplier. Even if Westinghouse returns the digital optical isolator given to them, it will not be installed. The licensee will notify the NRC Resident Inspector. Notified R2DO (Henson), NRR EO (Mike Cheok), and Part 21 Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 21.21 |  |  |  | 0 | 2008-12-18
44731 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-12-18 13:25 | 2008-12-18 14:41 | 2008-12-18 | AGREEMENT STATE REPORT - NON-NUCLEAR WORKERS RECEIVE RADIATION OVEREXPOSURE The following report was received via e-mail: "On December 18, 2008, the licensee confirmed that four of their workers, who are not considered to be radiation workers, exceeded the annual exposure limit for members of the general public of 100 millirem due to the detachment of the source from the operating rod. The dose to these individuals are: employee 1 - 280 mrem, employee 2 - 2962 mrem, employee 3 - 960 mrem, employee 4 - 78 mrem, employee 5 - 166 mrem. "The licensee will send supporting information to the Agency [Texas Department of Health] within the next few days." Texas Incident # I-8576 Texas Event Report 44609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-12-23
44730 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-01 | 2008-12-18 15:46 | 2008-12-18 | AGREEMENT STATE REPORT - MISSING NUCLEAR GAUGE "The gauge was discovered missing after Agency [Texas Department of Health] attempts to collect fees. Gauge registrant had provided self evaluation reports indicating they possessed the gauge and, after being contacted, admitted it was missing. The company had 2 gauges. The second was returned to Thermo Scientific. The missing gauge is reported to contain 1 curie of Cs-137. However, the manufacturer's information indicates it held 2 curies. A site investigation will be performed 12/09/08. A site investigation will be performed 12/09/08. "The licensee continues to dispute inappropriate disposition of the gauge/source but cannot produce documentation to support the statement. The gauge is most likely fixed on a dredge in Florida but until definitive documentation is produced to support or show the whereabouts of the source, the Agency must formerly declare the source missing. A draft Notice of Violation is being developed to call the company in for enforcement. "The source information follows: "Manufacturer: Thermo "MeasureTech (Now Thermo Fisher Scientific), Model: 5203, "Serial Number: B996, Isotope: Cs-137, Activity: 2 Ci, "Source serial number: GK3804" Texas Incident Report # I-8587 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-12-23
44729 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2008-10-29 18:04 | 2008-12-18 14:11 | 2008-12-18 | 60 DAY REPORT - INVALID SYSTEM ACTUATION "This report is being made under 10 CFR 50.73(a)(2)(iv)(A) and is not considered a Licensee Event Report. "With Unit 1 at Intermediate Shutdown (226?F and 300 psig), an invalid actuation of the Unit 1 'B' train of the Safety Injection (SI) system occurred at 1804 [EDT] during repair of a broken light socket located on the SI relay cabinet door. Plant systems and components responding to the 'B' train SI signal started and functioned successfully as designed (with the exception of those procedurally rendered inoperable due to the RCS being below 350?F and 450 psig). SI train 'B' was reset and the affected systems were restored to their pre-event configuration. "Specific trains and systems that actuated for train 'B' of SI are described below: "- With the unit at intermediate shutdown, one high head pump was currently running (the two redundant pump controls were in the Pull to Lock position in compliance with Technical Specifications). The 'B' train High Head Safety Injection motor operated valves re-aligned such that the running high head pump provided flow to the RCS Cold Legs from the RWST. During this time a bubble was present in the Pressurizer and the level remained on scale (increased 8%). "- One train of the Control Room Bottled Air System actuated on the Control Room Isolation. The ventilation alignment was restored to normal thereby isolating the Bottled Air System. The system was re-pressurized and restored to an operable condition. "- Auxiliary Feedwater (AFW) Pump motor operated valves opened but no flow was delivered to the Steam Generators since the AFW pumps were in Pull to Lock. "- The 'B' train containment isolation valves closed, isolating the 'B' RHR heat exchanger. However, shutdown cooling was previously being provided by the 'A' RHR train and was therefore uninterrupted. Containment isolation valves were later restored to a normal alignment. "- One train of Auxiliary Ventilation actuated and was restored to normal after the Safety Injection signal was reset. "- Emergency Diesel Generator (EDG) No. 3 started but did not load since its associated Emergency Bus remained energized by offsite power. The EDG was stopped and returned to automatic. "- Reactor Coolant Pumps (RCPs) were stopped due to the closure of the seal water return containment isolation valve. "A root cause evaluation is determining the cause." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-12-18
44728 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2008-12-18 08:45 | 2008-12-18 11:23 | 2008-12-18 | TONE ALERT RADIO INPUT OUT OF SERVICE "Loss of Ames Hill NOAA transmitter. Loss of the Ames Hill input from Albany, NY. Unable to establish backup input to Ames Hill transmitter from WTSA radio station, Brattleboro, VT. This results in a loss of output signal to area tone alert radios. Coordinating trouble shooting and repair with vendor. This action was successful in restoring service at 11:00, 12/18/08." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-12-18
44727 | 0 | CJW MEDICAL CENTER |  |  |  |  | 2008-12-16 15:00 | 2008-12-17 16:07 | 2008-12-17 | MEDICAL EVENT - MISADMINISTRATION A patient was prescribed a gammaknife procedure to treat trigeminal neuralgia on the right side of the face and the left was treated in error. The prescribed dose was 40 Gray (Gy) to 50% isodose. The patient was notified of the misadministration. There are no expected adverse effects to the patient. The licensee is continuing to investigate this incident to determine the cause of the misadministration and the total dose to the patient. A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2008-12-20
44726 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-12-17 09:42 | 2008-12-17 13:59 | 2008-12-17 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2008-12-17
44725 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-12-17 07:35 | 2008-12-17 10:51 | 2008-12-17 | STOLEN TROXLER GAUGE "On Wednesday, December 17, 2008 a Troxler moisture density gauge, Model 3430 (S/N 37875 with 8mCi of Cs-137 S/N 77-5152; and 40mCi of AmBe-241 S/N 78-2656) was stolen from the bed of a company pick-up truck along with some other field equipment. The transport case was chained as required by company procedures, but the entire case with gauge was noted missing when the technician briefly left the truck unattended. The chain had been cut and the theft was immediately reported to the Dallas Police Department. The area will be canvassed and dumpsters checked to see if the device had been inadvertently discarded. A reward will be posted through a notice that will be distributed to local authorities." TX Case Number I-8591. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-12-22
44724 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2008-12-16 06:00 | 2008-12-16 16:23 | 2008-12-16 | CRITICALITY WARNING SYSTEM DISABLED "At approximately 0600 on 12/16/2008, the horns of the inside Criticality Warning System (CWS) covering the Fuel Manufacturing Operation (FMO) were discovered to be in manual mode. On 12/12/08 at approximately 0700, the horns had been taken out of automatic mode and placed in manual mode as part of system maintenance activities at 0700 and inadvertently remained in this condition until this morning at 0600. According to a preliminary investigation, it appears that following maintenance on 12/12/08, incomplete system restoration left the automatic horn function disabled but the detection system remained operational. "Once identified, the system was immediately restored to the automatic mode and the inside FMO CWS system was returned to normal operation. Follow-up tests have confirmed that the warning system horns are fully operational. "The event is being reported within 24-hours pursuant to 10CFR70.50(b)(2) as an event in which safety equipment was disabled." During the time that the warning system was disabled, there were no conditions that would have resulted in warning system activation. Corrective actions have been taken to prevent re-occurrence. The licensee will be notifying NRC Region 2 as well as State and local governments. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-12-16
44723 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-12-15 16:16 | 2008-12-15 22:47 | 2009-02-06 | UNANALYZED CONDITION DUE TO STEAM CHASE TEMPERATURE GREATER THAN 165F "At 1616 on 12/15/08, a plant heating boiler trip resulted in a loss of a reactor building ventilation. The loss of reactor building ventilation resulted in maximum average main steam chase temperatures greater than or equal to 165F. High energy line break (HELB) analysis of piping in the steam chase assumes an initial average temperature prior to the break of 165F. Temperature greater than or equal to 165F in the steam chase challenges EQ qualification of the piping analysis. Abnormal procedures for loss heating boiler and ventilation system failure were entered. C.3 (Shutdown) and C.5-1300 (secondary containment control) were also entered. The plant heating boiler was restarted and ventilation restored prior to power reduction. All systems have been returned to normal." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED FROM DAVID BARNETT TO JOE O'HARA AT 1158 ON 2/6/09 * * * The licensee is retracting this report based on the following: "Monticello is retracting the event reported based on further evaluation, which found that the issue was not an unanalyzed condition that seriously degraded plant safety. The investigation of the event found the peak temperature achieved was 167.2 degrees F and the condition lasted for approximately 11 minutes. Engineering review of Safety System Components found no impact on the equipment for the temperature reached, Additionally, revised High Energy Line Break (HELB) calculations performed with an initial average Steam Chase Room temperature of 180 degrees F before a HELB determined that Safety System components could perform their safety functions. The station has identified the cause for the event and corrective actions will be tracked in the station's corrective action program. "Since there was no impact on the equipment in either Environmental Qualification (EQ) or safety function, the temperature of the event was less than the revised calculation temperature, and the unanalyzed condition that existed in the initial event notification report no longer exists and did not result in a condition that seriously degraded plant safety, this event can be retracted." The licensee informed the NRC Resident Inspector. Notified R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-12-15
44722 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-12-01 | 2008-12-15 17:44 | 2008-12-15 | AGREEMENT STATE - SAFETY EQUIPMENT MALFUNCTION "A General Licensee, a customer of Bruker AXS Handheld (Bruker) that is a device manufacturer located in Richland, Washington, returned one of Bruker's Map 4 XRF analyzers. The device had not been operating properly. When Bruker received the shipment they noticed that the package exhibited radiation levels on contact with the package of 4.9 mR/hr as measured with a GM survey instrument. This reading was unusual because it was significantly above the 0.5 mR/hr limit allowed for excepted radioactive instruments and articles transportation packaging. These packages are identified as NOS UN 2910 on the bill of lading. Bruker's receiving staff took the device to a shielded work area and when disassembled they discovered that the device's trigger mechanism was not operating properly. The mechanism did not allow the source to be fully shielded after it was released. A Bruker instrument technician discovered that one of the screws was partially backed out preventing the source block from fully closing. This screw had initially been installed per manufacturing procedure using lock-tite. This part has had no history of coming loose. The screw was replaced per the manufacturing procedure again using lock-tite on the threads as required. Bruker reported that this was the only problem like this they had experienced. The generally licensed device contained a Co-57 source, model F3-038, with a current activity of 318 megabecquerel (8.6 mCi). "The source was removed and checked for contamination. None was found. The device was repaired, calibrated and sent back to the customer. Bruker has established new guidelines for their technicians when they receive a call about a device problem / malfunction. The Bruker RSO will be notified and will work directly with the customer to assess the problem prior to the device being shipped to Bruker for repair." Washington Report # - WA-08-093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-12-18
44721 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-12-15 13:33 | 2008-12-15 15:40 | 2008-12-15 | FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2008-12-15
44720 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-12-06 | 2008-12-15 11:09 | 2008-12-15 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN "Wal-Mart employed the Shaw Group Inc. as a contractor to replace the H3 exit signs in their stores nation-wide. Shaw Group conducted an inventory of the store on March 11, 2008. They returned to the store on May 26, 2008 to replace the H3 sign with a non-tritium exit sign but found it missing. They had no information on the sign being transferred. The Shaw Group conducted interviews with store personnel and reviewed shipment and inventory records, but were not able to locate any additional information about the location or condition of the lost sign. "1. Site: Wal-Mart #5361; Source Material: Sealed source luminous; Manufacturer: SRB Technologies Inc.; Model Number: BX-20-GY; Serial Number: 310248; Activity 17.51 Ci. NE report number - NE080010. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-12-18
44719 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-12-14 17:14 | 2008-12-14 20:38 | 2008-12-14 | MANUAL REACTOR TRIP DUE TO ELECTRICAL FAULT ON AN OPERATING CONDENSATE PUMP "Callaway Plant was at 98% power with two condensate pumps in service. At 1714 on 12-14-08, the reactor was manually tripped due to a motor ground fault on the 'B' condensate pump. The 'C' condensate pump was not available for service [See EN #44714]. This left only one condensate pump available so the reactor was manually tripped. The plant is in mode 3 and stable. Reactor trip procedures have been implemented and exited and normal operating procedures are in progress at this time. All safety systems actuated as designed. All control rods inserted during the trip. Offsite power is available and powering safety loads. There is no primary to secondary leakage. Decay heat is being removed via steam dumps to the condenser with makeup provided by Auxiliary Feedwater to the steam generators. The standby diesel generators and safety systems are available. The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-12-14
44718 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-12-13 14:20 | 2008-12-13 17:30 | 2009-01-22 | STEAM EXCLUSION BOUNDARY DOOR LATCH FAILURE "At 1420 on 12/13/08 a plant electrician identified that a steam exclusion door would not close when he was transiting through the door. This door would not have closed and maintained the Steam Exclusion Boundary and could have led to steam through out the Auxiliary Building which could have resulted in both Trains of ESF Equipment failing to perform their required functions, i.e., SI, RHR, CC etc. A Unit Supervisor who was in the Auxiliary Building at the time immediately went up to the door and found the latch was broke and the broken piece was removed which then enabled the door to close and latch. At 1425 on 12/13/08 the Steam Exclusion Boundary was restored to functional and both Trains of ESF Equipment restored to operable." The licensee informed the NRC Resident Inspector. * * * RETRACTION AT 1420 ON 1/22/2009 FROM JACK GADZALA TO MARK ABRAMOVITZ * * * "01/22/2009 - Retraction of EN 44718, both trains of Engineered Safeguards Features (ESF) equipment inoperable due to a degraded steam exclusion boundary door. "EN 44718 provided notification that both trains of ESF equipment (e.g. SI, RHR, CCW, etc.) were inoperable due to degradation of a steam exclusion boundary door in the auxiliary building on December 13, 2008. "Subsequent engineering evaluation determined that the degraded door remained capable of fulfilling its steam exclusion function during the brief (five minute) period when it was degraded. A degraded latch mechanism prevented the door from latching closed. However, the door was closed against its door jam, which resulted in a sufficiently small gap such that total allowed leak path criteria were not exceeded. Additionally, the door swing was in the direction of postulated steam flow, such that the door would have been held in the closed position by any steam overpressure postulated under accident conditions. "Therefore, the door remained functional and the supported ESF equipment in the auxiliary building remained operable. Consequently, this condition did not meet the reportabllity Criteria in 10 CFR 50.72. "As a result, the notification made on 12/13/2008 (EN 44718) is hereby retracted." The licensee will notify the NRC Resident Inspector. Notified the R3DO (O'Brien). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2008-12-13
44717 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-12-12 10:42 | 2008-12-12 14:36 | 2008-12-12 | INADVERTENT VALID REACTOR TRIP AND FEEDWATER ISOLATION SIGNALS DUE TO MAINTENANCE "Valid Reactor Trip and Manual Initiation of Auxiliary Feedwater While in MODE 3" "At 1042 on 12/12/2008, while in Mode 3, a valid reactor trip signal was generated during I&C maintenance activities on intermediate range nuclear instrument SENI0036. This resulted in a feedwater isolation signal. Reactor Operators manually started both motor driven auxiliary feedwater pumps to maintain steam generator levels. These pumps were started prior to receiving an Auxiliary Feedwater Actuation. Plant is stable in Mode 3. Normal feedwater supply has been restored. The cause of the reactor trip is understood. "All systems functioned normally in response to plant conditions. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-12-12
44716 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2008-12-12 08:55 | 2008-12-12 11:48 | 2008-12-12 | UNIT 1 WAS MANUALLY TRIPPED FROM 32% POWER DUE TO AN ABNORMAL ROD PATTERN "Following startup from refueling outage 1R21, Arkansas Nuclear One Unit 1 was holding stable at 32% reactor power in order to perform Nuclear Instrumentation (NI) calibration. Control Rod Drive Mechanism (CRDM) control was in automatic with the controlling group (Group 7) at approximately 75% withdrawn. Control room operators received an asymmetric rod alarm and noted abnormal rod pattern on Group 7 with reactor power lowering. At this point, operations manually scrammed the reactor. Post trip response was normal and the plant is stable in Mode 3. Reactor Coolant System pressure is approximately 2155 psig and temperature is approximately 550 degree F. Post Transient Review is in progress." Unit 1 is in a normal post trip electrical lineup. No primary or secondary reliefs lifted during the transient. Auxiliary feedwater was placed in service to supply the Steam Generators for decay heat removal via the Main Condenser. The licensee informed both the State and NRC Resident Inspector. | 0 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-12-12
44715 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2008-10-24 13:18 | 2008-12-12 08:25 | 2008-12-12 | INADVERTENT ACTUATION OF ENGINEERED SAFEGUARDS SYSTEM FROM RELAY SENSING CIRCUIT "This event is being reported via a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. In this case, the telephone report is not considered an LER. This report is being made under 10CFR 50.73 (a)(2)(iv)(A). "During Engineered Safeguards Actuation System (ESAS) logic testing on October 24, 2008, an invalid actuation of the following heat removal systems occurred: 'B' train of the Decay Heat River Water System (DR), 'B' train of the Decay Heat Closed Cooling Water System (DCCW), and the 'B' train of the Nuclear Services River Water System (NR). There was no injection into the Reactor Coolant System. The invalid actuation occurred when the channel under test was taken to its tripped position. Since ESAS utilizes a 2 out of 3 logic for actuation, another actuation signal was present on one of the two channels not being tested, satisfying the actuation logic for the affected systems. The invalid actuation of these heat removal systems during testing on October 24, 2008 was due to oxidation on a silver-plated contact in one of the other two channels that was not being tested. This contact oxidation caused a higher input resistance to the timer relay, which resulted in an inadvertent actuation of the relay and its associated systems. The contact oxidation was caused as a result of using silver plated contacts in a low voltage application (approximately 12 VDC). During this invalid actuation, the heat removal systems were fully actuated. These heat removal systems functioned successfully and the operation of these systems did not have any adverse impact on plant operation. "All of the silver-plated contacts in the affected circuits will be replaced with gold-plated contacts. The contacts are scheduled to be replaced by December 18, 2008. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-12-12
44714 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-12-11 23:01 | 2008-12-12 01:12 | 2008-12-12 | AUTOMATIC REACTOR TRIP DUE TO A FEEDWATER TRANSIENT "The 'C' condensate pump tripped due to an electrical problem which caused a feedwater transient. The unit [automatically] tripped on high steam generator level at approximately 2301 CST. The unit is in mode 3 and stable. The reactor trip procedures are in progress at this time." All control rods fully inserted into the core during the reactor trip. Offsite power is available and powering safety loads. The steam generator atmospheric steam dumps lifted momentarily during the transient and reseated. There is no known primary to secondary leakage. Decay heat is being removed via steam dumps to the condenser with makeup provided by auxiliary feedwater to the steam generator. The standby diesel generators and safety systems are available. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-12-12
44713 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-12-11 16:45 | 2008-12-11 17:32 | 2008-12-11 | SITE VENDOR EMPLOYEE INAPPROPRIATELY ISSUED UNESCORTED PLANT ACCESS An employee of a site vendor was inappropriately issued unescorted plant access. Compensatory actions were taken. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-12-11
44712 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-12-10 14:00 | 2008-12-11 08:34 | 2008-12-11 | DETECTABLE CESIUM CONTAMINATION FOUND IN SOURCE SAFE DRAWER A contractor removed cesium sources from a source safe located in a storage area. The sources were removed, packaged, shipped without incident. Surveys were conducted in the safe, and the survey in the lower safe drawer revealed contamination levels greater than 5000 dpm per 100 square centimeters. The lower drawer of the safe has not been used during this recent storage and transfer of sources. The licensee reported to the state that they believed it was "legacy" contamination. Individuals involved in the source transfer were surveyed. No contamination was found. The storage area and passageway to and from the storage area were surveyed. No contamination was found. The licensee has secured the safe and the contaminated area. The area is secured and posted with "no access" signs. The state will follow up with their licensee once a decontamination service completes the decontamination of the affected areas and is ready to release the area for general use. The state notified Region 3 (Jim Lynch). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2008-12-16
44711 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-12-09 16:30 | 2008-12-10 15:57 | 2008-12-23 | AS-BUILT DEPTH OF LOW LEVEL DISSOLVER SYSTEM DISSOLVER TRAYS EXCEEDED MAXIMUM DESIGN DEPTH "Event Description: Planned upgrades to the Low Level Dissolver System in the BWXT's Uranium Recovery Facility were undergoing a safety review as part of the change management process. One of the upgrades involved replacement of the dissolver trays to utilize trays of the same length, width, and depth throughout the dissolution process. During the evaluation process a Recovery process engineer questioned differences between the tray heights in the current safety basis and the change review documentation. The ISA summary listed the tray geometry as an Item Relied on For Safety (IROFS). This limit was the same as that discussed in the text of the change management documentation. "Once it was determined that the discrepancy in the documentation also represented an as-built condition in the field, the Low Level Dissolution process was immediately shutdown pending further evaluation of the safety concern. The IROFS tray geometry was degraded. "Evaluation of the Event: A review of related safety release documentation indicated the original trays installed in 1999 met the NCS requirements. The requirements limited the tray or allowed modification of the tray (drilling holes, cutting slots) to limit the solution height. Due to the corrosive nature of the process, the trays degrade over time and are replaced when a minimum wall thickness is achieved. The replacement trays were intended to be of like kind. The current fabrication drawing attached to the change management documentation shows no additional features to limit the solution height. "The initial review of the accident scenario for a geometry upset indicated that although an IROFS was degraded, other IROFS (operator control of mass, operator control of moderator, and poisoning by the tray materials of construction) remained available to assure double contingency. This is a qualitative evaluation that does not analyze the magnitude of the upset condition. The original NCS analysis of the Low Level Dissolver trays conducted in 1999 evaluated tray height; the impact of a range of tray heights was not considered. "The as-found condition in the field, including tray height, was subsequently modeled using BWXT's validated NCS codes and approved methodology. The normal operating condition was determined to be within the k-effective limit of 0.92 in BWXT's NRC License SNM-42 for a high enriched uranium (HEU) system. When a fully flooded moderation upset condition was analyzed, although the resulting k-effective was shown to be subcritical, it exceeded the safety limit of 0.95 in BWXT's license for a HEU system. This determination was reached at 4:30 pm on December 9, 2008. "There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. A fully flooded condition in the Low Level Dissolver is extremely unlikely. The equipment is located on a mezzanine, well above the main process area. "There are no water sources (e.g., sprinklers) in the area, and the dissolvers are not contained in water tight enclosures. However, with the degradation of the IROFS of tray height, and demonstration that the as-found condition exceeded the license limit for a single upset condition, double contingency could no longer be assured. "Notification Requirements: BWXT is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(2) loss or degradation of items relied on for safety that results in failure to meet the performance requirement of 70.61. "Status of Corrective Actions: An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation." The Low Level Dissolution process remains shutdown. The licensee documented this event in their condition report CR#1027010. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BARRY COLE TO KARL DIEDERICH ON 12/11/2008 AT 1013 EST * * * The analysis of a fully flooded moderation upset condition showed the resulting k-effective exceeded the safety limit of 0.95 in BWXT's license for a HEU system showed a k-effective of 0.96. Notified R2DO (Ernstes), NMSS (Habighorst), and Fuels Group (via e-mail). * * * RETRACTION @ 1234 EST ON 12/23/08 FROM BARRY COLE TO RYAN ALEXANDER * * * "This report was made based on the assumption that the tray dimensions on the drawing were representative of as-built tray dimensions in the field. Subsequent to the report, measurements were taken of the Low Level Dissolver trays in use at the time of discovery. Using the same methodology used to determine the initial reportability of the event, the moderation upset was reevaluated for the as-built tray dimensions. The resulting k-effective was 0.94, which is below the safety limit of 0.95 in BWXT's license for a HEU system. Evaluation of the as-built tray dimensions demonstrated although there was a loss or degradation of Items Relied On For Safety, BWXT did not fail to meet the performance requirement of 10 CFR 70.61. BWXT is therefore withdrawing the 10 CFR 70, Appendix A, (b)(2) notification, #44711." The licensee notified the NRC Resident Inspector. Notified R2DO (Hopper), NMSS EO (Benner), and Fuels OUO Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-12-28
44710 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-12-10 10:37 | 2008-12-10 14:35 | 2008-12-10 | OFFSITE NOTIFICATION MADE DUE TO MINOR OIL SPILL "On December 10, 2008 at approximately 8:30 the control room was notified of an oil sheen in the discharge canal. An Operator was dispatched to assess the condition and its significance. At Approximately 1037 hours the CCR [Central Control Room] was informed that an apparent oil sheen had been observed in the Hudson River. The oil is partially contained by a boom in the outfall structure and the amount of oil released to the river is estimated to be less than one gallon. A sample of the material has been collected to determine what type of substance it is. The source of the apparent sheen is unknown and remains under investigation. In accordance with the Indian Point Spill/Release plan a spill or leak from Indian Point causing a visible sheen in the river as a result of a release of a petroleum product requires notification of the New York State Department of Environmental Conservation and the Coast Guard National Response Center. An environmental cleanup vendor has been contacted for assessment and cleanup. "The NRC resident has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-12-10
44709 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-12-10 13:10 | 2008-12-10 13:49 | 2008-12-10 | CONTRACT EMPLOYEE WITH UNESCORTED ACCESS FAILED TO DISCLOSE FELONY CHARGE A contract employee with unescorted plant access failed to disclose a felony charge. The NRC Resident Inspector will be notified by the licensee. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-12-10
44708 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2008-11-16 18:27 | 2008-12-10 13:02 | 2008-12-10 | INVALID ACTUATION OF AN EMERGENCY DIESEL GENERATOR "This notification of a system actuation is provided in accordance with 10 CFR 50.73(a)(2)(iv)(A). The Licensee is providing a telephone notification to the NRC Operations Center in accordance with 10 CFR 50.73(a)(1) instead of submitting a written Licensee Event Report, as the system actuation was invalid and was not the result of an actuation of the reactor protection system when the reactor was critical. The event involved the invalid actuation of 'Emergency AC electrical power systems, including: emergency diesel generators' as discussed in 10 CFR 50.73(a)(2)(iv)(B). "At 1827 on November 16, 2008, with Calvert Cliffs Unit 2 operating at approximately 100% power, the Train A (2A) Emergency Diesel Generator (EDG) automatically started from the standby condition. The automatic start was caused by a degraded switch in the start circuit for the EDG. The 2A EDG successfully started and functioned properly, but did not automatically connect to the associated bus ('21' 4KV Bus) because no bus undervoltage signal was present. The 2A EDG start is considered to be invalid, as the start signal was not generated in response to actual plant conditions or parameters satisfying the requirements for initiation of the EDG start. The start was also not the result of an intentional manual action. "The 2A EDG was removed from service and the Station Blackout diesel generator was aligned to '21' 4KV Bus. "Following replacement of the degraded switch, the 2A EDG was tested and returned to Service at 2030 on November 17, 2008. "The 2B EDG remained operable during this event. "The licensee notified the NRC Resident Inspector." The degraded switch was in the EDG room and had degraded resulting in high resistance i.e. simulated an open circuit, which started the diesel. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-12-10
44707 | 0 | DOW AGROSCIENCES |  |  |  |  | 2008-12-09 | 2008-12-09 16:30 | 2008-12-09 | LOST TRITIUM EXIT SIGNS "[This is] notification of two missing tritium exit signs from Dow AgroSciences, LLC. The signs were confirmed to be missing and potentially disposed of as hazardous waste on 12/9/2008. "The two self luminous tritium signs were manufactured by Isolite: Model Number: 2040-01R-12, Serial Number: A67502, manufacture date July 3, 1996. Model Number: 2040-01R-12, Serial Number: A67503, manufacture date July 3, 1996. At the time of notification the activity for each sign would be 4748.59 mCi. At the time of removal of the signs the activity would have been 5023.79 mCi, each. "The two exit signs were to be replaced by the Radiation Safety Officer and the Site Operation Manager and it was discovered that they had previously been replaced by a Site Manager. This Site Manager, who is no longer with the company, had replaced the above signs with new self luminous signs on 12/6/2007. The RSO and Site Operation Manager contacted waste management to confirm potential disposal and confirmed that work had been performed on 12/6/07 for sign replacement. Currently the RSO and Site Manager are investigating the disposal path of the signs as it is not documented that the signs were returned to the manufacturer. The RSO has notified the Radiation Safety Chair, the Environmental Health and Safety Leader, and the Site Operation Leader. A full root cause investigation is scheduled for December 11, 2008. A final notification report will be submitted within 30 days as required by the NRC." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-12-09
44706 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-11-30 | 2008-12-09 13:48 | 2008-12-09 | AGREEMENT STATE - FIRE IN MANUFACTURING FACILITY CONTAINING FIXED NUCLEAR GAUGES "N.C. Radiation Protection Section has confirmed the N.C. Division of Emergency Management and local law enforcement were included in initial notifications and remain engaged in the ongoing event evaluation. "N.C. Radiation Protection Section was notified on 30 November 08 by an unrecorded source from UNIMIN Corporation that there was a major fire in one of their mineral processing facilities in Spruce Pine, NC. Initial reports from the licensee indicate four industrial nuclear gauges containing Cs-137 sealed sources (3 gauges contain 2 mCi each and the fourth contains 50 mCi) were present in the facility at the time of the fire. The damage to the facility exceeds $200,000 and the facility will be out of operation for over one week, so this incident is a reportable event under NC Code 15A NCAC 11.1646(a)(3) & (4). "Command of the site was taken by the Bureau of Alcohol, Tobacco and Firearms (for fire investigation). Preliminary radiation surveys of the exterior of the facility indicated radiation levels equivalent to background. An inspector from N.C. Radiation Protection was dispatched to the scene on 4 December 08, but was not allowed access to the interior of the facility or to any records maintained by the RSO of UNIMIN Corporation. The inspector was allowed to examine and survey the exterior of the affected facility; he found the structural damage to be significant and that radiation levels about the perimeter of the affected facility were background. The UNIMIN RSO has been able to visually identify three of the four gauges from a vantage point exterior to the facility. Security at this facility is adequate. "The investigation will be continued on 12/9 or 12/10 by the inspector from the N.C. Radiation Protection Section." North Carolina Report # NC-08-51. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-12-12
44705 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-12-08 02:19 | 2008-12-08 15:19 | 2008-12-08 | PROCESS GAS LEAK DETECTION SYSTEM INOPERABLE "At 0219 CST, on 12-08-08 the Plant Shift Superintendent (PSS) was notified that the C-333 Unit 6 Cell 5 UF6 Release Detection (PGLD) System would not test fire during routine testing. Operators found that the READY, MANUAL, and POWER lights for this system were properly illuminated. This PGLD System contains detectors that cover only C-333 Unit 6 Cell 5 which was operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell are operable during steady state operations above atmospheric pressure. With the Unit 6 Cell 5 PGLD system inoperable, none of the required cell heads were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.B.1 was entered and a continuous smoke watch was put in place within one hour. "Engineering has determined, by analyzing the failed component, that the system would not have been able to perform its intended safety function when this condition was discovered. This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." As of the time of the report, the problem has been corrected and the system returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-12-08
44704 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-01 | 2008-12-08 12:40 | 2008-12-08 | AGREEMENT STATE - TEXAS - REPORT OF MISSING GAUGE CONTAINING 2 CURIE CESIUM-137 SOURCE The following was received from the Texas Department of State Health via e-mail: "The gauge was discovered missing after Agency attempts to collect fees. Gauge registrant had provided self evaluation reports indicating they possessed the gauge and, after being contacted, admitted it was missing. The company had 2 gauges. The second was returned to Thermo Scientific. "The missing gauge is reported to contain 1 curie of Cs-137. However, the manufacturer's information indicates it held 2 curies. A site investigation will be performed 12/09/08. The source information follows: Manufacturer: Thermo MeasureTech (Now Thermo Fisher Scientific), Model: 5203, Serial Number: B996, Isotope: Cs-137, Activity: 2 Ci, Source serial number: GK3804." The State of Texas is reporting this as their equivalent to NRC regulation 20.2201(a)(1)(i); reports of theft or loss of licensed materials > 1000 X App. C value. A representative of the State of Texas (Robert Free) was contacted and it was determined that the date that the gauge went missing or the circumstances are unknown at this time. The licensee is a dredging company that used the density gauge for underwater dredging activities associated with installing underwater pipelines. Texas report I-8587 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-12-11
44703 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-12-07 20:10 | 2008-12-07 23:52 | 2009-01-23 | INADVERTENT EDG START "On 12/7/08 at 2010 CST, Emergency Diesel Generator 2 was started manually from its local control cabinet. The diesel started and operated as designed upon operation of the local Emergency Start Push button. This was an inadvertent start of the diesel during an alarm test on the local engine panel. The alarm test and emergency start push buttons are in close proximity and of similar design and color. The diesel has since been shutdown and returned to a standby condition. The Emergency Diesel Generator remains capable of performing its designed function and was considered operable throughout the evolution. Therefore this report is being made in reference to 10CFR 50.72(b)(3)(iv)(A) . "The licensee notified the NRC Resident Inspector." * * * RETRACTION AT 1549 EST ON 12/10/2008 FROM ERICK MATZKE TO MARK ABRAMOVITZ * * * "On 12/7/2008, Fort Calhoun reported an inadvertent start of a diesel generator (event Number 44703). Based on a detailed review of NUREG-1022, this event has been determined not to be reportable under 10 CFR 50.72(b)(3)(iv)(A) . As reported, the diesel generator was not intentionally manually started by the operator. Therefore, this event was an invalid actuation of the safety system and this notification is being retracted. An appropriate report will be forthcoming as required by 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1)." The licensee notified the NRC Resident Inspector. Notified the R4DO (Cain). * * * RETRACTION WITHDRAWN AT 1125 EST ON 1/23/2009 FROM ERICK MATZKE TO VINCE KLCO "As allowed by 10 CFR 50.73(a)(1), the following information is provided: "On December 7, 2008, an equipment operator inadvertently started emergency diesel generator 1 using the local Emergency Start push button. The operator was distracted and failed to apply appropriate self checking. "This report is being made under 10 CFR50.73(a)(2)(iv)(A): "a) The train that was actuated was diesel generator train 2. "b) The train actuation was complete. The diesel started and operated as designed. The associated emergency bus was not deenergized so the diesel did not connect to the bus. "c) As previously noted, the diesel started and functioned successfully for the plant conditions at the time." The licensee notified the NRC Resident Inspector. Notified the R4DO (Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-12-08
44702 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-12-07 14:05 | 2008-12-07 15:49 | 2008-12-07 | SPILL OF FUEL OIL "The Control Room was informed by Turkey Point Fossil Environmental personnel that they contacted the Florida Department of Environmental Management and Florida State Warning Point due to a spill of fuel oil at Turkey Point Fossil Units 1 and 2. The spill was approximately 50 gallons of bunker C fuel oil and went into a storm drain and into the cooling canal system. The state agency notifications were completed at 1417 on December 7, 2008. "The NRC Senior Resident has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-12-07
44701 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-12-06 11:26 | 2008-12-06 13:22 | 2008-12-06 | OFFSITE NOTIFICATION DUE TO WASTE WATER DISCHARGE "This 4-hour Non-Emergency notification to the NRC is being made based on a notification to another government agency per 10 CFR 50.72(h)(2)(xi). "On December 6, 2008 at 1253 the Control Room was informed by Turkey Point Fossil Environmental personnel that they contacted the Florida Department of Environmental Management and Florida State Warning Point due to overflowing an ash pit for the Turkey Point Fossil Units 1 and 2. The overflow was of industrial waste water with a volume of approximately 2250 gallons and allowed directly into the cooling canal system. The state agency notifications were completed at 1128 on December 6, 2008. The overflow was stopped by equalizing the level between each ash pit. "The NRC Senior Resident has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-12-06
44700 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-12-05 04:27 | 2008-12-06 13:18 | 2008-12-06 | UNPLANNED CONTAMINATION "During a transfer of uranyl nitrate, solution entered a column overflow. Less than one (1) liter of solution leaked from a fitting on the overflow line and contaminated process equipment primarily in an area inaccessible to personnel. The event is being reported because decontamination could not be completed within 24-hours. "The area was isolated and personnel access was restricted. Cleanup activities were initiated and decontamination was performed in areas accessible to personnel. Decontamination of remaining areas [are] ongoing." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2008-12-12
44699 | 0 | OLSSON ASSOCIATES |  |  |  |  | 2008-12-05 16:15 | 2008-12-05 18:13 | 2008-12-05 | DAMAGED TROXLER MOISTURE DENSITY GAUGE "[The following narrative describes a damage event to [a] Troxler 3440 (SN 37660) which occurred at about 4:15PM (CST) on 12/5/08. The event occurred in Greene County, Missouri, on Route J approximately 4 miles North of US 60 Hwy, approximately 4 miles east of US 65, SE of Springfield, Missouri. "The project is a roadway reconstruction. [The licensee] employee was in the process of performing a compaction test with the gauge when an inattentive scraper operator nearly ran [the licensee] over, but did run over the gauge. The employee cordoned off the area and ceased all work in the area. An initial visual assessment of the gauge indicated that both the Americium and Cesium sources were intact. A field wipe test is being performed to verify whether or not the sources have been damaged. No results are available at the time of this report. What is currently known is that the gauge sustained such damage that the base plate was dislodged from the bottom of the gauge and that the tungsten sliding block/source shield also became dislodged. If the sources are not damaged, attempts will be made to remove a portion of the probe (with the Cesium source intact), re-insert it in the top of the source shield, re-insert the source back into the gauge, wrap the gauge with duct tape to secure the sources, put the gauge back into the carrying case, and transport the gauge back to the office storage location for further processing instructions. "[Licensee] additional updates will follow." Typical Troxler gauges of this series contain a source of 8 mCi Cs-137 and 40 mCi Am/Be. * * * UPDATE FROM CURT MADER TO VINCE KLCO AT 2300 EST ON 12/05/2008 "At around 7:00PM (CST) a field wipe test indicated that there was no damage/contamination of either radioactive material source. The gauge was put back into the storage case and transported back to the office storage location. The top portion of the handle had to be sawed off in order to retract the probe source back into the tungsten/sliding block housing. The base cover plate was hammered back into shape and was screwed back onto the base of the gauge. "[The licensee office Radiation Safety Officer] will be traveling to Springfield, MO tomorrow to assess the situation. Pictures will be taken and another wipe test will be performed and sent to Troxler Electronics in preparation of shipping the gauge back to them for decommissioning." Notified R3DO (Mike Kunowski) and FSME (Rebecca Tadesse). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-12-05
44698 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-12-04 21:18 | 2008-12-05 00:21 | 2008-12-05 | UNPLANNED HPCI INOPERABILITY "On December 4, 2008 at 1735 during steam line warming as part of a planned HPCI pump and valve surveillance, a 4 hour Limiting Condition for Operation was entered for the HPCl Steam Supply Outboard Isolation Valve Bypass Valve (E4150F600) per LCO 3.6.1.3 with the action being to isolate the penetration. This was due to abnormal indications observed from the Main Control Room during movement of the valve. "On December 4, 2008 at 2118, unplanned HPCI inoperability occurred due to isolating the HPCI Steam Supply Inboard Isolation Valve (E4150F002) to satisfy LCO 3.6.1.3 1 for the HPCI Steam Supply Outboard Isolation Valve Bypass Valve (E4150F600) inoperability. A 14 day LCO was entered for HPCI per LCO 3.5.1. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function to mitigate the consequences of an accident based on loss of a single train safety system. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-12-05
44697 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-12-02 16:15 | 2008-12-04 17:53 | 2008-12-05 | AGREEMENT STATE REPORT- SOURCE FAILS TO RETRACT "On the evening of 12/2/08, Varian, a service contractor, had completed a successful source exchange on a Nordion GammaMedPlus Brachytherapy device, serial # H600447. That same evening, the new source wire became jammed during the third position verification test procedure. The source would not retract using the electronic devices provided on the machine. The source was manually retracted to the shielded position by a service technician within a few minutes of the event. The source, cable, and associated equipment have been removed from the device. They have been packaged for shipment to the manufacturer in England for further examination. The dose estimate to retract the source to the safe position is approximately 35 millirem. The source was a 9.12 curie Iridium (Ir) - 192 source model # VS2000. The source serial number was not available. The source is currently stored in a transportation container. The manufacturer believes that a small piece of debris prevented the source from fully retracting. "The licensee stated that they will provide the state with a written report by 12/9/08. Additional information will be forwarded to the NRC as it is received." Texas Incident Number: I-8586 * * * UPDATE FROM ART TUCKER TO JOE O'HARA AT 0953 ON 12/5/08 * * * The following was provided from the state via e-mail: "The Radiation Safety Office for Varian Medical Systems Inc. contacted the [Texas Department of State Health Services] Agency and stated that the device involved was a VariSource Brachytherapy HDR Remote Afterloader (SSD # CA-0661-D-103-S) and not a Nordion GammaMedPlus Brachytherapy device. All other information is correct." Notified R4DO (Proulx) and FSME (Einberg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | MAT | [5 empty] | 0 | 2008-12-04
44696 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-12-04 15:15 | 2008-12-04 16:12 | 2008-12-05 | OFFSITE REQUEST FOR LAW ENFORCEMENT ASSISTANCE INVOLVING AN UNDENTIFIED SUBSTANCE "[A] small plastic bag containing an unknown white powder substance was discovered inside the Turkey Point Nuclear Station protected area. Miami-Dade Police Department was contacted for evaluation of the substance. The contents of the bag were taken into the custody of Miami-Dade Police. At 1515 the site was notified that the substance had been determined to be baby powder and that outside agencies have been notified for threat evaluation. "Outside agencies that were contacted [by the licensee] include Miami Dade County Hazardous Material Division, Miami Dade County Emergency Operations Center, State of Florida Emergency Operations Center, Department of Homeland Security and Federal Bureau of Investigations." The licensee contacted the NRC Resident Inspector. * * * UPDATE FROM DEWEY BARROW TO VINCE KLCO ON 12/05/08 AT 1410 * * * This update is being made to clarify the second paragraph regarding notification of outside agencies. The licensee initially contacted the Miami-Dade Police Department who then contacted the identified outside agencies. Notified R2DO (Robert Haag) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-12-04
44695 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-12-04 12:46 | 2008-12-04 13:44 | 2008-12-04 | CONTRACT EMPLOYEE TESTED POSITIVE FOR MARIJUANA ON INITIAL DRUG SCREEN Contract employee tested positive for marijuana on initial drug screen. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-12-04
44694 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-12-02 17:00 | 2008-12-03 08:12 | 2008-12-03 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE "Driver blacked out while transporting soil moisture density gauge. The outer case was damaged, one handle pulled off and container was hanging out of pick up bed. Gauge itself was not damaged and was still properly secured. Due to the driver being by himself and incapacitated, gauge was no longer under licensee's control. Driver was transported to hospital and released. Gauge will be leak tested prior to being put back into service. No further action will be taken on this incident." Troxler gauge model number is 35802. Serial number unknown. Isotopes: 40 mCi of Am-241/Be and 8 mCi of Cs-137. Location of accident was 1987 Scenic Gulf, San Dustin, FL. Florida Incident Number - FL08-143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-12-08
44693 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-12-02 16:45 | 2008-12-02 20:03 | 2008-12-02 | INADVERTENT ACUATION OF EMERGENCY SIRENS "At approximately 1645 CST, on December 2, 2008, personnel from the City of Red Wing inadvertently activated the sirens from the backup unit for the City of Red Wing. Twenty-six (26) of the 117 sirens in the 10 mile Emergency Planning Zone (EPZ) were activated for approximately two minutes. No press release is planned." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-12-02
44692 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2008-12-02 16:20 | 2008-12-02 19:36 | 2008-12-03 | LOSS OF ONE (1) EMERGENCY SIREN "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On December 2, 2008, at approximately 1620 Mountain Standard Time (MST), the Palo Verde Emergency Planning Department discovered that public warning system siren No. 17 was not responding, and therefore, is out of service. The loss of siren No. 17 could potentially impact a population of approximately 1106 people in the 5-mile emergency planning zone (EPZ). "Since the loss of siren No. 17 could impair Arizona Public Service Company's ability to inform greater than 5% of the population within the EPZ, this notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). If an event occurs while siren No. 17 is out of service, the Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area. The MCSO is prepared to implement this contingency should it become necessary. "Troubleshooting to determine the cause of the failure will start tomorrow morning (December 3, 2008). "The NRC Resident Inspector has been notified of siren No. 17 being out of service and this ENS call." * * * UPDATE FROM TIM GAFFNEY TO DONALD NORWOOD AT 1531 EST, 12/03/2008 * * * "Siren 17 was returned to service on Wednesday, December 3, 2008, at 0829 MST." Notified R4DO (Proulx). | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-12-02
44691 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-12-02 15:15 | 2008-12-02 16:04 | 2008-12-02 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for illegal drugs during a follow-up fitness-for-duty test. The employee's access to the plant has been denied. Contact the Headquarters' Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2008-12-02
44690 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-11-22 14:00 | 2008-12-01 12:18 | 2008-12-01 | AGREEMENT STATE REPORT - RADIUM VIALS DISCOVERED IN HOME "The Bureau of Radiation Protection (BRP) received a call through our 24-hour answering service, at 2:00 PM on Saturday, November 22, 2008. The caller, from Harrison, Ohio indicated that she purchased birth stones from an internet auction house a couple of weeks ago. However, it wasn't until Friday evening, November 21, 2008 that she opened a plastic drawer (part of what was purchase) and found 3 vials indicating radium. The caller then proceeded to do some research of radium on the internet and decided to call ODH the next day. She indicated the vials have been isolated and will not be touched until BRP staff can assess the radiological hazard (if any.) BRP indicated that we would like to send a health physicist to her house in the next couple of hours to survey the vials, her home, and assess her exposure. "Health Physicist 3, Eric Denison was contacted. He picked up the response vehicle and survey equipment. He arrived at the caller's home ([Deleted], Harrison, Ohio 45030) at approximately 7:00 PM. "Survey results showed no radioactive contamination on the caller and none found on her clothes, in her bathroom, and none found in other areas where there would have been the possibility/expectation of radioactive contamination. The HP3 indicated that the 1" reading on the side of the vials located in the garage indicates 15mR/hr. "It appears from the surveys there is not a spread of radioactive contamination that had us concerned from the onset of the first phone call. The impact appears to be minimal and limited to the radium vials. The 3 radium vials are to be isolated, locked in a tool box in the garage, until an appropriate disposal can be arranged. The HP 3 finished remaining surveys and provided the caller a summary of what he has found, including bureau contact information. "Attached are two pictures from our response to the radium discovery. The first gives an idea of the size of the vials as compared to the metal case and the nitrile glove under the case. The second gives a closer view of the third vial. The case is approximately 7 inches long and perhaps 2.5 inches wide. I apologize for not getting a ruler or coin into the pictures for size comparison. "The label on the first vial is almost completely gone, and the label on the second is partially gone. The label on the third is almost intact. I did not notice any writings or markings other than the printing, but did not take time to examine them closely. The labels read: 'Radium - Chimie', 'Teufen - App.', 'Qual. No.', 'Nuance'. "When presented by the owner, the vials were contained in the metal watch case shown in the photos. Dose rate as measured with a Bicron MicroRem was approximately 15 mRem/hr at a distance of 1 inch from the top center of the case. Smear wipes showed no removable contamination on the exterior of the case. On opening the case, HP3 found the vials wrapped loosely in a plastic zipper bag (but not inside the bag). HP3 removed the vials and arranged them for the photographs. HP3 did not smear the vials or the inside of the case. "[Individual] told BRP she has no way of paying for the appropriate disposal of the radium vials. BRP told [Individual] at the time we would try to get USEPA to take possession at no cost to her. ODH BRP contacted USEPA orphan sources program to see if they would be willing to dispose of the radium vials. USEPA confirmed that they will take possession and dispose of the radium vials found at a residence in Harrison, Ohio. ODH informed the resident, [Individual], and indicated that she could expect a call from USEPA. "ODH-BRP contacted Jim Mitchell at USEPA (orphan sources unit) Chicago, to follow-up on our email we sent them on Monday. We indicated to Jim that ODH will need to be involved in this as they move forward. USEPA agreed and looks forward to the cooperation. "USEPA has contacted [Individual] and arranged for USEPA to take possession on Thursday 12/4/08 at 10:00 AM. ODH is currently still investigating where the radium came from. USEPA response will also include their investigation unit as they want to pursue how and where the radium was obtained. ODH indicated to USEPA we have the same concern and will need to be included when they meet the resident on Thursday. "USEPA currently believes their team to include: Gene Jablonowski - Health Physicist Chicago Office, Bill Ryzek - USEPA investigator Chicago Office, Steve Renninger - Cincinnati Office, John Sherod - Cincinnati Office. "ODH will meet USEPA at the residence: Eric Denison - HP 3, Stephen Helmer." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2008-12-04
44689 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2008-11-30 01:58 | 2008-11-30 08:22 | 2008-11-30 | ACCIDENT MITIGATION - CREFS INOPERABLE "On 30 November 08 at 0158, the Control Room Emergency Filtration System (CREFS) was declared inoperable due to a degraded Control Room Envelope (CRE). A CRE boundary door was found to be stuck partially open. With this door not fully closed and latched, reasonable assurance that CREFS would fulfill its safety function could not be established. "The CRE door is a support features for CREFS at CNS. This is a single train system and per 10CFR50.72(b)(3)(v)(D) an 8 hour report is required due to the fact that at the time of discovery this condition could have prevented the fulfillment of the safety function of an SSC [Structure, System & Components] that is required to mitigate the consequences of an accident. "The door was returned to a fully closed and latched position at the time of discovery, and CREFS was returned to operable status. Administrative controls are in place to ensure the door closes and latches until repairs can be performed." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-11-30
44688 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2008-11-28 21:01 | 2008-11-28 23:04 | 2008-11-29 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TRANSFORMER FAULT "At 98% power, a reactor scram occurred due to a Main Transformer fault. The plant is currently stable in the Hot Shutdown Mode. Isolation Condensers initiated as part of this event are currently in Standby Mode. This event is reportable in accordance with 10CFR50.72(b)(2) and (b)(3) and the Station Reportability Manual section SAF 1.6 and SAF 1.7." The cause of the transformer fault is unknown and under investigation. There was no fire or explosion associated with the fault. All rods inserted during the scram. As a result of the transient, one electromatic relief valve lifted and subsequently reseated. There were no other isolations or safety equipment actuations during the transient. The station electrical system is in its normal shutdown lineup with offsite power available. Decay heat is being removed via the turbine bypass valves to the main condenser. Pressure is currently at 700 psi with water level being maintained at 160" via the main feed system. The licensee has notified the NRC Resident Inspector and will be notifying the State of New Jersey. * * * * UPDATE FROM CARL SUCHTING TO JOHN KNOKE AT 0017 EDT ON 11/29/08 * * * * " Notification performed to NJDEP of fish mortality following a reactor scram. As of this report, one dead bluefish spotted and three distressed bluefish spotted." Licensee has notified the NRC Resident Inspector. Notified R1DO (Doerflein). | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) |  | 0 | 2008-11-28
44687 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2008-11-28 10:15 | 2008-11-28 14:56 | 2008-11-28 | AGREEMENT STATE - MARYLAND - DAMAGED TROXLER NUCLEAR DENSITY GAUGE A representative for the state of Maryland Radiological Health Program reported that a Troxler nuclear density gauge was damaged when run over by construction equipment. The gauge, a Troxler 3430 (8 mCi Cs-137 and 40 mCi Am-241/Be; S/N 39041) was left unattended and was inadvertently run over by a large roller. The licensee secured the scene of the incident and contacted the state of Maryland. The state inspector found that the gauge had been extensively damaged with the source rod exposed. The state called in a Radiological Service Organization (RSO) contractor to assist in the source rod recovery. The source was successfully retrieved and placed into a shielded container and taken to the RSO's facility for ultimate disposal. There was no indication of breach of the sources or contamination as a result of this event. The state plans to follow-up with the licensee regarding failure to maintaining control over the Troxler while in use. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2008-12-03
44686 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2008-11-26 13:06 | 2008-11-26 15:52 | 2008-11-26 | LOSS OF EMERGENCY COMMUNICATIONS LINES "On 11-26-2008, at 13:06 EST, both Control Rooms were notified by Emergency Planning Department that the following phone notification systems are out of service: RECs [Radiological Emergency Communications System] line, ENS line and HPN line. Also, three dedicated '754' prefix lines in the TSC are currently inoperable. Site Information Technology Department personnel are working with communications equipment vendor, Verizon, to resolve the issues. " State and local authorities and the NRC Resident Inspector have been notified. * * * UPDATE AT 1612 EST ON 11/26/08 FROM SHEEHAN TO HUFFMAN * * * The RECs, ENS, and HPN lines have been returned to service with the exception of a line to the State Warning Point in Albany NY. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-26
44685 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-11-26 12:00 | 2008-11-26 15:12 | 2008-11-26 | AUTOMATIC REACTOR SCRAM DUE TO EHC MALFUNCTION "At 12:00 hours EST, an apparent Electro-Hydraulic Control (EHC) system malfunction while synchronizing the Main Generator to the grid resulted in a Group 1 Main Steam Isolation Valve (MSIVs) closure on low reactor pressure and a subsequent automatic reactor scram. "Preliminary investigation of the automatic scram signal indicates that Main Steam Line Low Pressure Instruments (B21-PT-N015 A thru D) sensed low steam line pressure after the Main Generator was paralleled to the grid. This resulted in the closure of all MSIVs. Closure of MSIVs in Mode 1 results in an automatic reactor scram. "All control rods fully inserted. With the exception of the EHC system, all systems responded as designed. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) due to the Reactor Protection System (RPS) actuation and 10CFR 50,72(b)(3)(iv)(A) due to the Primary Containment Isolation System (PCIS) Groups 1, 2, and 6 actuations. "Unit 2 was not affected by this event and remains at 100% power." Reactor Pressure is 844 psig, reactor temperature is 526 degrees Fahrenheit. MSIV's remain shut. Decay heat was removed via MSIV bypass lines. RCIC actuated for a period of time for level control but has been secured. CRD pumps are providing makeup water. No SRV's or relief valves lifted. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-11-26
44684 | 0 | TYCO ELECTRONICS |  |  |  |  | 2008-09-28 | 2008-11-25 15:23 | 2008-11-25 | RELAY FAILED TO ACTUATE AS A RESULT OF INCORRECT RECYLE SPRING Florida Power and Light reported to Tyco that during normal operation one nuclear relay failed to actuate. Tyco investigated and determined that a Tyco electronic relay, E7024 style 4 pole off delay, has an incorrect recycle spring installed into the relay. The incorrect recycle spring causes the relay to fail to actuate. The following was provided by the licensee via fax: "(i) Name and address of the individual providing the information: Scott Daubert, Quality Assurance Manager, Tyco Electronics - CII of the Global Aerospace Defense and Marine Division, 1396 Charlotte Highway, Fairview, NC USA:28730. "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity that contains a deviation or failure to comply; Item supplied are E7024 relays with serial numbers beginning with 0808 through 0835. Certificates of Conformance stating exact relay description and serial numbers will be sent to affected customers with notification by December 16, 2008. Tyco sold this safety-related item for specified and unspecified applications. The customers for which Tyco had insufficient information to complete the Part 21 evaluation are listed [below]. "(iii) Identification of the firm constructing the facility or supplying the basic component that contains a deviation or a failure to comply: Tyco Electronics, 1396 Charlotte Highway, Fairview N,C, USA 28730 "(iv") Nature of the defect or safety hazard that could be created by such a deviation or failure to comply: If an incorrect recycle spring is place into the relay, the off-delay timing could be longer than desired. "(v) The date on which the information of such a deviation or failure to comply was obtained. Tyco Electronics made the determination of the existence of this condition in September 2008. Notice of Limited E7000 Relay Recall will be issued to the customers by 16 December 2008. . "(vi) In case of a basic component, which contains a deviation or failure to comply, the locations of all such Components in use or being supplied? Customers that purchased affected safety-related items from Tyco Electronics for unspecified applications are identified [below]. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action (note, these are actions specifically associated with the identified deviation or failure to comply; The lot of springs in question have been used. No further defects have been found within current stock. A go/no-go gauge has been developed for use in the production line to verify the free length of the recycle spring prior to installation. This will be completed on each spring until we can develop a method to color code the two springs. Customers that purchased affected safety-related items from Tyco Electronics for unspecified applications are identified [below]. "(viii) Any advice related to the deviation or failure to comply about the facility, activity, or basic component that has been, is being given to purchasers or licensees: Based on our evaluation this issue is expected to have a low potential to produce a significant safety concern. However, Tyco Electronics does not have sufficient information to perform an evaluation for unspecified applications. Therefore customers receiving the recall notification should return affected relays for inspection and rework." Affected plants are as follows: Farley Nuclear, Oyster Creek, Fermi, Waterford, Limerick, Peach Bottom, Turkey Point, Harris, and Brown's Ferry. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2008-11-25
44683 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-11-21 | 2008-11-25 14:08 | 2008-11-25 | AGREEMENT STATE REPORT - LEAKING ELECTRON CAPTURE SOURCE The following information was received from the State of California via email: "A leak test of a generally licensed 9.78 mCi Nickel-63 Electron Capture Source, Serial Number NH285 28.17, manufactured by QSA Global , Inc., indicated 0.0053 uCi of Nickel-63 contamination. The source was stored in room 20D of the Space Sciences Laboratory at the University of California at Berkeley (UCB). The source was taken out of service and repackaged until the investigation by UCB has been completed. A second wipe of the source was taken and was negative." California 5010 Number (Date Notified): 112108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-11-28
44682 | -1 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2008-10-17 15:46 | 2008-11-24 19:34 | 2009-01-22 | EXCEEDENCE OF NITRATE SEWERING LIMIT "AREVA NP's Richland plant wastewater effluent is continuously sampled for uranium and regulated chemicals. Chemical discharge limits are set by the City of Richland as part of the plant's Industrial Wastewater Discharge Permit. The liquid effluent 24-hour composite sample for October 13 indicated a total nitrate discharge of 1759 pounds, exceeding the daily maximum permit limit of 1300 pounds. While the laboratory analysis on the effluent sample was re-run to confirm the exceedence, the elevated discharge is inconsistent with discharge quantities that would have been predicted by either upstream process samples or nitric acid utilization, both of which would have predicted discharges in the range of slightly over 800 pounds of nitrate. Nitrate discharges for the subsequent two days (October 14 and 15) were 641 and 886 pounds nitrate, respectively. "The October 13 permit violation (revealed via October 16 lab analysis) was reported to the City of Richland on October 17 within 24 hours of confirmation in accordance with permit requirements. Follow-up written notification was provided to NRC Region II for informational purposes in accordance with the Richland site's NRC special nuclear materials license. "Environmental significance of this single day exceedence is low; the plant's overall daily average nitrate discharge for the month was 564 pounds, well below the applicable daily average permit limit of 1000 pounds. The City of Richland sewage treatment plant was not adversely impacted; that plant does not have a comparable limit on its nitrate discharges." * * * RETRACTION AT 1923 ON 1/21/09 FROM LOREN MAAS TO MARK ABRAMOVITZ * * * "The purpose of this correspondence is to officially retract the subject event report filed by AREVA's Richland, Washington fuel fabrication facility. The report was filed under the Concurrent Reports provision of 10 CFR 70 Appendix A in that the Richland plant had exceeded its daily nitrate sewering limit in its City of Richland industrial wastewater discharge permit, an occurrence requiring notification of the city. "Based on subsequent discussions with inspection staff and management at NRC Region II, and consistent with reporting guidance in Section 3.2.12 of NUREG-1022, Revision 2, it has been determined that this event does not rise to the level intended for concurrent NRC Operations Center notification under 10 CFR 70 Appendix A. Accordingly, NRC Region II has requested that AREVA retract the subject report. "Environmental significance of this single day exceedence is low; the plant's overall daily average nitrate discharge for the month was 564 pounds, well below the applicable daily average permit limit of 1000 pounds. The City of Richland sewage treatment plant was not adversely impacted; that plant does not have a comparable limit on its nitrate discharges." Notified the R2DO (Musser) and NMSS (Davis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-11-24
44681 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-11-23 16:00 | 2008-11-24 13:20 | 2008-11-24 | STOLEN TROXLER MOISTURE DENSITY GAUGE "While at the office, Site002, on Sunday, November 23, 2008, the licensee had a truck with a gauge secured in the bed which was stolen by cutting the chain and lock. The employees had left to go to a jobsite and upon returning to the office noticed that the gauge had been stolen. The Dallas Police Department was notified and a report was filed. The Agency was notified at the start of business on Monday, November 24, 2008. The gauge was a Troxler 3430 (S/N 334330) and had two sources, 8mCi of Cs-137 (S/N 750-8953) and 40mCi of Am-241 (S/N 471455)." TX Incident #- I-8582 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-11-27
44680 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-11-23 12:00 | 2008-11-23 18:13 | 2008-11-23 | PRESSURE BOUNDARY LEAK "During performance of Unit 1 vessel leak test in accordance with 1-SI-3.3.1.A - ASME Section XI System Leakage Test of the Reactor Pressure Vessel and Associated Piping, a pressure boundary leak was discovered on an instrument line connected to the reactor pressure vessel. This instrument line is a ASME Code Class 1 equivalent component (nozzle safe end) on pressure vessel nozzle N11B and connecting upstream of primary containment penetration X-29B. This caused entry into Technical Requirements Manual (TRM) 3.4.3 - Structural Integrity - Condition A - in which the applicability is at all times and the required action is to immediately restore the structural integrity of the affected component to within its limit or maintain the reactor in MODE 4 or 5 or the reactor coolant system less than 50?F above the minimum temperature required by NDT considerations, until each indication of a defect has been investigated and evaluated. The plant is currently in MODE 4. "This event is reportable within 8 hours under 10CFR50.72 (b)(3)(ii)(A) Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. This event is also a reportable within 60 days under 10CFR50.73(a)(2)(ii)(A) any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. The NRC Resident Inspector has been notified. This condition has been documented in the BFN Corrective Action program as PER# 157918. "Unit 2 and 3 remain at 100% power and are not affected by this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-11-23
44679 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-11-22 10:18 | 2008-11-22 12:26 | 2008-11-22 | MANUAL REACTOR SCRAM AFTER FEED PUMP TRIP "Manual Rx Scram initiated due to a loss of condensate/feedwater. Condensate Booster Pump 1A tripped due to low suction pressure and then both Reactor Feed-pumps tripped. Both HPCI and RCIC initiated on low level and restored reactor water level to normal band 5 to 50 inches. "Both Reactor Water Recirculation Pumps tripped due to low level at RWL [Reactor Water Level] - 60". Lowest RWL was approximately minus 70 inches and a group two isolation occurred at RWL 3 inches. All group two 2 valves closed as required. "The cause of the low condensate booster suction pressure is under investigation." Rods fully inserted on the scram. No safety or relief valves lifted after the scram. Reactor water level is being maintained with normal feed and decay heat is being removed to the main condenser. The plant is in its normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2008-11-22
44678 | 0 | NOAA |  |  |  |  | 2008-11-18 | 2008-11-21 18:04 | 2008-11-21 | LEAKING SEALED SOURCE "On the morning of Nov. 18, 2008, routine semiannual ECD [Electron Capture Device] leak tests were conducted in the FRD [Field Research Division] laboratory at 1750 Foote Dr., Idaho Falls, ID. A wipe test on the inlets and outlets of the above source showed the presence of 0.011 microcuries of contamination. The wipe was counted on a Ludlum 3030 Alpha Beta Sample Counter that was specifically calibrated for Ni-63 by the Idaho National Laboratory Health Physics Instrumentation Laboratory. Annual calibration was completed on Nov. 12, 2008. The limit of detection for the instrument was calculated as 0.00031 microcurie of Ni-63. "When the high count was observed, the smear was immediately sealed in a ziplock plastic bag. The work area where the wipe was done was immediately checked for contamination. Tools (tweezers, pens, notepad) used, table tops, gloves, and the Ludlum instrument itself were wiped with smears and each one counted. The counts on all smears were much less than the instrument limit of detection indicating zero activity. "Once it was established that no measurable contamination was present in the environment, steps were taken to isolate the detector. Immediately after the wipe test was completed, all inlets and outlets were recapped and the detector replaced in the locked cabinet where it had been stored. The detector was then removed from the cabinet again and all six sides of the rectangular housing were wiped with a smear. This was counted and showed zero activity indicating that no contamination was on the outside of the detector housing. The detector was placed in a plastic ziplock bag and put in a paint can. The plastic bag containing the smear that counted high was also placed in the can. The can was closed and the outside wiped and counted, again showing zero activity. Further wipe tests were then conducted on the inside of the storage cabinet where the detector was stored, the tables around the gas chromatograph (GC) where the detector was last used and the interior surfaces of the GC. All counts indicated zero activity. Based on these contamination tests, we believe that all leakage is contained within the device which is isolated in the paint can. There was no exposure to the public and neglible exposure to the personnel conducting the leak tests. "The detector had been taken out of service on August 23, 2007. It had passed all wipe tests prior to that date. The detector remains in the paint can in a locked metal cabinet inside the FRD laboratory. It will remain out of service until it can be repaired. We have contacted the manufacturer and other companies and are investigating options for repair of the unit. "Source identification: Valco model 140BN Electron Capture Detector (ECD), serial number N206 (General License device, Sealed Source Registry No. TX-658-D-102-G, 5 millicuries Ni-63)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2008-11-21
44677 | 0 | NEVADA STATE HEALTH DEPARTMENT |  |  |  |  | 2008-11-21 | 2008-11-21 17:43 | 2008-11-21 | AGREEMENT STATE REPORT - THYROID SCAN ADMINISTERED TO THE WRONG PATIENT Nevada Physicians Imaging, the licensee, reported to the Nevada State Department of Health that they inadvertently administered 220 microCi of I-123 to the wrong patient. Patient A (the correct patient) was scheduled to receive a thyroid scan. Patient B (the wrong patient) shared the same name as Patient A and was scheduled to receive treatment at the same time. As a result, Patient B underwent a thyroid scan intended for Patient A. It is unknown what diagnostic procedure Patient B was intended to receive. The patient has not been notified of the incorrect treatment. The licensee was in the process of notifying the prescribing physician. The State of Nevada will investigate this incident after receiving the licensee's report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2008-11-27
44676 | 0 | MALLINCKRODT |  |  |  |  | 2008-11-21 13:25 | 2008-11-21 14:27 | 2008-11-21 | LOST I-131 MEDICAL PHARMACEUTICAL 10 packages of medical pharmaceuticals were shipped on 11/19/2008 from Mallinckrodt in Maryland Heights, MO to destinations in Virginia, Maryland, and Pennsylvania. One package did not arrive at the destination: a Mallinckrodt pharmacy in Folcroft, PA. Three couriers were used to ship the packages: transport from Mallinckrodt to the airport, ship by air, and transport to the pharmacies. All of the couriers have searched for the missing package without success. Source: I-131, 109 mCi THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-11-21
44675 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-11-21 11:08 | 2008-11-21 14:08 | 2008-11-21 | OFFSITE NOTIFICATION AND MEDIA BRIEFING DUE TO POTENTIAL DISCOVERY OF OFFSHORE FAULT NEAR PLANT "As part of the ongoing seismic monitoring program, PG&E [Pacific Gas & Electric] in conjunction with the US Geological Survey (USGS) is studying a pattern of seismic activity in close proximity to the Diablo Canyon Power Plant (DCPP). The discovered pattern of seismic activity suggests a potential offshore fault near DCPP. PG&E and the USGS were previously unaware of this potential fault. Initial evaluation shows that the potential fault is closer to DCPP and much smaller than the Hosgri fault, which is the current bounding seismic feature for DCPP. "Initial assessment indicates that the ground motion from this potential fault is expected to be bounded by the existing seismic design basis for DCPP. The possible impact of this potential fault, including potential ground deformation is the subject of an ongoing evaluation. Given the available data, PG&E and the USGS estimate that it will take up to a year to determine if a seismic fault exists. "This issue was discussed with US NRC Region IV and Office of US NRC Nuclear Reactor Regulation on November 21, 2008. PG&E is planning a media briefing." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-11-21
44674 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-10-14 11:06 | 2008-11-21 11:42 | 2008-11-21 | FAULTY VOLTAGE REGULATOR CAUSES HALF SCRAM "On 10/14/2008 at approximately 1106 [EDT], the James A. FitzPatrick Nuclear Power Plant was operating at approximately 99% power in Mode 1. The 'A' Reactor Protective System (RPS) Motor-Generator (MG) Set tripped. This resulted in a half-scram signal and Group II Primary Containment Isolation System [PCIS] actuation. The Group II PCIS isolation actuated valves in multiple systems. "During the event all systems operated as designed. "Power was restored to 'A' RPS using the alternate power supply and the Group II PCIS isolation was reset. "The cause of the event was determined to be a failure of the 'A' RPS MG Set voltage regulator. The voltage regulator was replaced and the RPS System was returned to its normal line-up. Initial troubleshooting on the failed voltage regulator determined that a Silicone Control Rectifier failed. The voltage regulator was sent off-site for further analysis to determine the cause of failure. The event is reportable under 10 CFR 50.73(a)(2)(iv)(A) 'Any event or condition that resulted in manual or automatic actuation of ...(B)(2) general containment isolation signals affecting containment isolation valves in more than one system'. A telephone notification is being made in lieu of an LER, pursuant to 10 CFR 50.73 (a)(1) as an invalid signal." The voltage regulator had been replaced approximately three weeks before this failure. (See EN #44673) The licensee notified the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-11-21
44673 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-09-25 02:41 | 2008-11-21 11:42 | 2008-11-21 | LOOSE CONNECTION CAUSES HALF SCRAM WHILE SHUTDOWN "On 9/25/2008 at approximately 0241 [EDT], the James A. Fitzpatrick Nuclear Power Plant was Shutdown in the refueling mode. The 'A' Reactor Protective System (RPS) Motor-Generator (MG) Set tripped. This resulted in a half-scram signal and Group II Primary Containment Isolation System [PCIS] actuation. The Group II PCIS isolation actuated valves in multiple systems. "During the event all systems operated as designed. "Power was restored to 'A' RPS using the alternate power supply and the Group II PCIS isolation was reset. "The cause of the event was determined to be a loose connection on the 'A' RPS MG Set voltage regulator. The Voltage regulator was replaced and the RPS System was returned to its normal line-up. "The event is reportable under 10 CFR 50.73(a)(2)(iv)(A) 'Any event or condition that resulted in manual or automatic actuation of ... (B)(2) general containment isolation signals affecting containment isolation valves in more than one system'. A telephone notification is being made in lieu of an LER, pursuant to 10 CFR 50.73 (a)(1) as an invalid signal." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-11-21
44672 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-11-20 16:57 | 2008-11-20 21:21 | 2008-11-20 | UNEXPECTED HIGH PRESSURE COOLANT INJECTION ISOLATION DURING TEST "The High Pressure Coolant Injection (HPCI) system was declared inoperable on 11/20/08 at 1657 EST due to a Group 4 isolation signal generated during scheduled surveillance testing in accordance with PNPS [Pilgrim Nuclear Power Station] Procedure 8.M.2-2.5.3, Attachment 1. The HPCI testing was stopped to determine the cause of the isolation which was not part of the planned evolution. HPCI isolation was reset, and HPCI was restored to standby lineup at 1804 EST. This event is an eight-hour notification. Efforts are ongoing to determine the cause of the error during testing. "This event had no adverse effect to the health and/or safety of the public. "The licensee has notified the NRC Resident Inspector of this event. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) due to the loss of a single train system required to mitigate the consequences of an accident." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-11-20
44671 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2008-11-20 12:30 | 2008-11-20 18:24 | 2008-12-24 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM INOPERABLE "On 20 Nov 08 at 1230, the Control Room Emergency Filtration System (CREFS) was declared inoperable due to a report that a non-running Control Room supply fan discharge damper was found partially open. Per the System Operating Procedure, the idle fan's discharge damper must be fully closed to assure operability. With the damper not closed, reasonable assurance that CREFS would fulfill its safety function could not be established. "With the Idle Control Room supply fan discharge damper not in the closed position, some portion of the air discharged from the operating Control Room supply fan will go backwards through the idle supply fan to the suction side of both supply fans. The CREFS fan discharges to the Control Room supply fan suctions. With CREFS in this as-found line-up, there is no assurance that the flow through CREFS is high enough to meet the design requirements assumed in control room occupant dose calculations. "The Control Room supply fans and discharge dampers are required support features for CREFS at CNS. This is a single train system and per 10CFR50.72(b)(3)(v)(D) an 8 hour report is required due to the fact that at the time of discovery this condition could have prevented the fulfillment of the safety function of an SSC that is required to mitigate the consequences of an accident. "The licensee notified the NRC Resident Inspector. "The damper was returned to a fully closed position at the time of discovery, and CREFS was returned to operable status." * * * RETRACTION PROVIDED BY DAVID VANDERKAMP TO JASON KOZAL AT 1054 ON 12/24/08 * * * "This notification is being made to retract Event Notification EN# 44671 which reported a loss of safety function due to the unplanned inoperability of the Control Room Emergency Filtration (CREF) system. The CREF system was declared inoperable due to the non-running control room supply fan discharge damper found partially open on November 20, 2008. Cooper Nuclear Station has determined through further evaluation that while the CREF system was procedurally required to be declared inoperable, the ability of the CREF system to perform its safety function was not lost. "Testing was performed on December 19, 2008, with the non-running control room supply fan discharge damper aligned in the as-found condition (~25% open) of November 20, 2008 and again tested with the damper aligned to 50% open. Technical Specifications surveillance flow requirements were met in both tests. Using the results of the test and inspection of the discharge damper it has been concluded that during the ten days the damper was out of position, the CREF system was still capable of performing its safety function and satisfying Technical Specifications requirements." Notified R4DO (Werner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-11-20
44670 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2008-10-28 | 2008-11-20 17:20 | 2008-11-20 | PART 21 - 18" VALVE ASSEMBLY BEARINGS NOT DEDICATED PARTS The following report was received via facsimile: "Items provided to Duke Energy - Oconee per Fisher Order Number 033-B800163810, Items 010A- 10L (Duke Energy Order DP16655). This equipment included 18" CL150 Fisher A31A valve assemblies (quantity 12). The equipment is identified by Fisher Serial Numbers 16986219 through 16986230 (Duke Energy Item Number DMV-1409). "Fisher Controls has determined that the subject items were provided with parts that were not properly processed per active valve requirements specified by the Duke Energy Order DP16655. Specifically, Fisher provided commercial grade bearings and thrust bearings instead of commercial grade dedicated items per EPRI 5652. "We are reviewing the situation and will pursue a corrective action investigation to prevent problems like this in the future. "Arrangements have been made with Duke Energy to retrofit the correctly processed parts on the subject serial numbers. This is a formal notification; Duke Energy was notified of this situation on October 28, 2008." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2008-11-20
44669 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-11-13 09:25 | 2008-11-20 14:24 | 2008-11-20 | AGREEMENT STATE REPORT - DISCONNECTED RADIOGRAPHY SOURCE The following report was received via facsimile: "On November 13, 2008, around 9:25AM at the Louisiana Technical College - T.H. Harris Campus, Nondestructive Testing Department had a misconnection on an Amertest 660B camera with serial number 1641 from the control cable to the source assembly. The camera had a 43.9 Ci source of Ir-192 with serial number 48634B. The students cranked the source out to do the area survey. After completion of the survey, they tried to return the source to it's shielded position. At that time, they could not return it back to the shielded position. The RSO was notified and determined it could possibly be a misconnect. QSA Global was called to retrieve the source. QSA Global retrieved the source and performed further evaluation. The camera and source were returned to QSA Global. QSA Global determined that it could possibly be a defective male connection on the source assembly. All safety procedures were followed. According to the facility, none of the students were in any kind of danger of being overexposed." LA Event Report: LA0800024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-11-25
44668 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2008-11-19 16:00 | 2008-11-19 21:04 | 2008-11-21 | RADIOACTIVE CONTAMINATION GREATER THAN EXPECTED "10CFR70, Appendix A: A condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed. "The residual radioactivity contained within these buildings is primarily in the form of surface contamination. The results of previous characterization data indicate that the residual mass was approximately 250 grams of U-235. However, the preliminary results of more recent characterization surveys and sampling have provided information that suggests the inventory of residual mass may be higher than previously estimated. "Based on the results of recent radiological surveys performed within the process buildings, small quantities of uranium contamination have been identified in partially dismantled piping and ventilation filter housings. The potential for exposure to workers and to members of the public is minimal since the uranium is present in the form of contamination fixed to interior surfaces of the building, piping and interiors of equipment that remains within the building. "Recent radiological surveys performed within the process buildings have revealed the potential for small quantities of uranium contamination in partially dismantled piping and ventilation filter housings. These radiological surveys were performed to gather additional information to support work planning associated with building demolition. This condition does not represent degradation or failure of structures, systems, equipment, components, or activities of personnel relied on to prevent potential accidents or mitigate their consequences. "No structures, systems, equipment, components are relied upon to prevent potential accidents. The activities of personnel have been curtailed to include only the performance of radiological characterization necessary to refine and complete the estimate of the U-235 mass. "Additional actions taken by the licensee in response to the event: 1. Restricted access to the buildings during non-work hours. 2. Limited access to the building during working hours to those personnel performing radiological characterization activities necessary to refine and complete the estimate of the U¼235 mass, and those engaged in minor maintenance activities not associated with the interior surfaces of piping and equipment. 3. Provided instructions to personnel allowed access that piping, remaining equipment and any other component that may contain residual U-235 are not to be disturbed in any manner except for actions necessary to support completion of radiological contamination estimates; re-configuration of these shall not occur." The licensee suspects that the contamination is in the order of 700g U-235. Contact readings were less than 1.5 mR/hr. * * * UPDATE FROM GERRY COUTURE TO HOWIE CROUCH ON 11/21/08 @ 1819 EST * * * "As a result of further discussions and preliminary evaluations, Westinghouse wishes to provide a revised report pursuant to 10 CFR Section 70.50(b)(i). Section 70.24 requires that each licensee authorized to possess special nuclear material in specified quantities maintain in each area in which such special nuclear material is handled, used, or stored, a criticality monitoring system. Further specific guidance is contained in Regulatory Guide 3.71 approved by the NRC Staff. As previously reported, the process building or specific areas within may potentially contain more than the threshold amount of special nuclear material to trigger this requirement. If so, a report is required pursuant to the cited section in that previously installed criticality monitoring equipment has been disabled, i.e., removed, and such equipment would be required by regulation. "This report is being made provisionally as there is insufficient time to definitively determine whether the entry conditions for the building as a whole have been met, i.e., whether 700 grams of uranium-235 are stored therein, and whether the building can be considered to be comprised of separate areas which could each be evaluated for the need to have criticality monitoring provisions. This report under 10 CFR 70.50(b)(2)(i) is subject to being withdrawn with an appropriate explanation and evaluation, if it is determined that the reporting threshold had not been met. "Additional actions taken by the licensee in response to the event: "1. Issued a Stop Work Order and assured all necessary personnel have been briefed to restrict access and all work activities associated with the Process Building. "2. Procuring necessary instrumentation to utilize as the regulatory required equipment and upon concurrence from NRC, proceed with the radiological characterization of the Process Building. "Discussions [are] ongoing with representatives of the USNRC Headquarters and Region III." Notified R3DO (Hills) and NMSS EO (Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 3 | MO | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-11-19
44667 | 0 | WALTER REED ARMY MEDICAL CENTER |  |  |  |  | 2008-11-14 09:00 | 2008-11-19 13:08 | 2008-11-19 | BRACHYTHERAPY SEEDS TEMPORARILY LOST AND UNACCOUNTED FOR "On 10 NOV 08, a patient was admitted for a brachytherapy treatment. The patient received 77.8 mCi of Ir-192 in the form of eight nylon ribbons, each ribbon containing 7 seeds, for a total of 56 seeds (each seed containing 1.39 mCi of Iridium-192). "The initial dose rate was 50 cGy/hour with a prescribed dose of 4500 cGy to be delivered over a 90 hour treatment time. "On 14 NOV 08 at 0900, when the sources were scheduled to be removed, it was discovered that three ribbons (containing 29.2 mCi of Ir-192) were missing. It was later learned that the ribbons were improperly removed from the room when a physician improperly changed the bandage on the patient (the ribbons were stuck to the bandage with tape). "A search was made of the trash compactor located on the back loading dock. The compactor had just been unloaded at 0600 hours on 14 NOV 08. A survey of the trash compactor discovered the sources (all three ribbons with all 21 seeds) at 1210 [hrs.] on 14 NOV 08. Hence, the sources were placed in the compactor between 0600 and 0900 on 14 NOV 08. "Verification of the sources was visually made by the therapy physicist (the sources did not have serial numbers or other indentifying markings). As a precaution, leak tests were performed on the previously missing sources and the results did not indicate any detectable activity. "Based upon interviews of the medical and the housekeeping staff, the following events occurred: "a. The physician improperly removed the bandage (and the sources stuck to the bandage with tape) and threw it in the trash can located within the room.. "b. The housekeeping staff improperly entered the patient's room and removed the trash from the trash can, placing it in a larger barrel. The barrel was then taken to the loading dock and emptied into the trash compactor. All of this occurred between 0600 and 0900. The compactor is situated in an unoccupied area of the back loading dock (no break areas or smoking areas). "c. The maximally exposed individual in this scenario was the housekeeping worker who removed the trash and took it to the compactor on the loading dock: i. The dose rate at one meter from the sources was measured as 13 mR/h. Ii. The sources were assumed to be 0.5 meters from the custodial worker. Iii. The transit time from the room to the compactor was 20 minutes (based upon interview with the custodial worker). Iv. The estimated dose to the worker is 17.3 mRem [based on a provided calculation]. "A complete investigation is being made of the incident and will be reported at the next scheduled meeting of the Walter Reed Army Medical Center Radiation Safety Committee currently scheduled for 4 DEC 08." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-11-19
44666 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2008-11-19 04:25 | 2008-11-19 06:59 | 2008-11-19 | AUTOMATIC REACTOR TRIP "On 11/19/08 at 0425 CST was operating at 100 power when the reactor tripped with no complications. All safety systems operated properly with the plant in Hot Standby. The cause of the reactor trip is under investigation. There is no radioactive release from the site." Uncomplicated trip event. Farley Unit 1 is shutdown with all rods in. No relief valves lifted. All other safety related systems are operable. There are no EDG's running. Reactor Pressure is 2247 psig; reactor temperature is 551 degrees Fahrenheit. Decay heat path is via turbine bypass valves to the condenser. AFW is feeding the S/G's. No ECCS systems injected. There is no affect on Unit 2. Licensee is investigating a potential fault in the switchyard. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-11-19
44665 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-11-03 10:42 | 2008-11-18 17:08 | 2008-11-18 | CONTROL RODS DRIFT OUT WHILE SHUTDOWN "On 11/03/2008, with Unit 3 shut down and all control rods in, an unexpected drift of three control rods out from their full-in position occurred. The immediate cause of this event was high control rod drive (CRD) cooling and exhaust water header pressures as the final group of hydraulic control unit (HCU) valves were being isolated. At the time, Operations personnel were in the process of completing the isolation of the CRD HCUs by closing the (101) Insert Riser Isolation Valve and (102) Withdraw Riser Isolation Valve on each HCU with a CRD pump in operation and the CRD charging water header isolated. "A control rod drift alarm was received in the Unit 3 control room, followed by several rod position indication system (RPIS) indications that the associated control rods had drifted from position 00 (full-in) to their 'over travel-in' position. Later, all indications returned to the full-in position, with the exception of three CRDs. These three CRDs settled at final positions 06, 16, and 18, respectively. Immediate corrective actions were taken to re-open the 101 valve for each of the three CRDs, allowing the control rod to re-insert to full-in. The 101 valve was then re-closed. Calculations by nuclear engineering identified that the reactor remained subcritical for the actual plant conditions and that there was no risk of fuel damage. "Initial review of the event by Exelon determined that it was not reportable. "After additional review and evaluation, the decision was made to conservatively report the event pursuant to 10 CFR 50.72 (b)(3)(v), 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function.' A root cause investigation is underway to determine the cause. The industry has been notified via the operating experience process on November 7, 2008. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2008-11-18
44664 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-11-18 03:08 | 2008-11-18 13:19 | 2008-11-21 | FIRE WATER SPRINKLER SYSTEM OUT OF SERVICE "At 0308 CST, on 11/18/2008, the Plant Shift Superintendent was notified that the C-337 High Pressure Fire Water (HPFW) Sprinkler System D-9 had been inspected by Fire Services and six sprinkler heads had visible corrosion on them. The system configuration was evaluated using EN-C-822-99-047, 'Effects of Impaired Sprinkler Heads on System Operability' and determined that with these heads impaired, a portion of the building would not have sufficient sprinkler coverage. The HPFW system is required to be operable according to TSR LCO 2.4.4.5. HPFW system D-9 was declared inoperable and TSR LCO 2.4.4.5 Required Action B was implemented for the area without sprinkler coverage. Based on past testing results, there is a possibility that the heads would have been able to perform their specified safety function. Once the heads are removed from the system, testing will be performed to determine the true affect on operability. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Senior Resident Inspector has been notified of this event." The site has implemented hourly fire patrols while this impairment is in affect. * * * RETRACTION FROM TONY HUDSON TO HOWIE CROUCH @1536 EST ON 11/21/08 * * * "The affected sprinkler heads were removed and subjected to testing in the plant laboratory. A total of nine heads (three of these heads were previously identified with corrosion) were removed and tested with five of the nine actuating as designed. Using these results, the plant's fire protection engineer concluded that adequate sprinkler coverage existed prior to the discovery and the system would have performed as designed to a fire demand." The licensee has notified the NRC Resident Inspector. Notified R2DO (Guthrie) and NMSS EO (Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-11-18
44663 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2008-09-18 | 2008-11-18 08:53 | 2008-11-18 | TREATMENT SITE DOSE LESS THAN PRESCRIBED "A medical event is reported for one patient treated by the VA New York Harbor Healthcare System in Brooklyn, New York. The event was discovered November 17, 2008. The basis for this event is that the D90 dose to the treatment site was slightly less than 80% of the prescribed dose. The treatment involved permanent implant prostate brachytherapy using Iodine-125 seeds. The patient implant date was September 18, 2008. A supplemental implant procedure was performed to achieve an acceptable D90. Adverse effects on the patient are not expected from this medical event. "A 15-day written report of this medical event will be submitted to NRC Region III. We have notified our NRC Project Manager, Cassandra Frazier (NRC Region III) of this event. "Department of Veterans Affairs has a Master Materials License (MML) from the NRC: License No. 03-23853-01VA. Permits are issued under the MML to VA facilities. VHA permit number of permittee involved in event: Permit No. 31-62892-03. Address of permittee involved in this event: New York Harbor Healthcare System, 800 Poly Place, Brooklyn, New York, 11209." A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NY | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-11-24
44662 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-11-17 09:25 | 2008-11-17 10:48 | 2008-11-17 | UNUSUAL EVENT DECLARED DUE TO FIRE IN PROTECTED AREA LASTING GREATER THAN 15 MINUTES Grand Gulf declared an unusual event at 0925 CST based on a fire in the protected area lasting longer than 15 minutes. The fire was discovered at 0911 CST under the B reactor feedwater pump. The fire involved oil accumulated under the feedwater pump. The fire brigade responded and extinguished the fire at 0935 CST. The B reactor feedwater pump was tripped offline and reactor power was reduced to 48% power due to the reduction in feedwater flow. The reactor is stable and there is no ongoing threat from the fire. There is no apparent damage to plant equipment and the cause of the oil leak is unknown at this time. The licensee plans to exit the UE when the licensee confirms there is no concern from fire reflash. The license has notified the required State and local authorities. The NRC Resident Inspector has been notified. * * * UPDATE FROM PAT BLUDAU TO JOHN KNOKE AT 1300 EST ON 11/17/08 * * * "Fire confirmed at 0911 CST in 'B' Reactor Feed Pump Turbine room. Plant power was reduced by Control Room; then "B" Reactor Feed Pump Turbine was tripped in order for the Fire Brigade to combat the fire. Unusual Event declared due to Fire in Protected Area lasting greater than 15 minutes. (HU4). Fire reported out at 0935. No external assistance is needed. Unusual Event terminated at 1134 CST." Licensee has notified the NRC Resident Inspector, and state and local agencies. Notified R4 RA (Collins), R4 (Cain), NRR (Leeds), NRR (Thorp), IRD (Grant), FEMA (Barden), DHS (Moore). | 48 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | MS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-11-17
44661 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-10-16 09:07 | 2008-11-17 10:26 | 2008-11-17 | INVALID ACTUATION OF STEAM DRIVEN AUX FEED PUMP "On October 16, 2008 during a routine clearance restoration activity, two solenoid-operated steam supply isolation valves on one of the three steam lines to the steam-driven Auxiliary Feedwater Pump (2FWE-P22) unexpectedly opened at Beaver Valley Power Station (BVPS) Unit No.2, admitting steam to and causing this pump to commence rotating. The control room operator monitoring the plant quickly recognized the unwarranted system response and attempted to terminate steam flow to the auxiliary feedwater pump by re-closing the two unexpectedly open steam supply isolation valves from the control room. At the same time, the local operator performing the restoration activity of opening a separate manual upstream steam isolation valve also recognized the unwarranted system response (by hearing too much steam flow through the manual valve) and also terminated steam flow to the pump by re-closing the upstream manual isolation valve. The total time that this pump rotated was less than approximately 30 seconds and the plant computer indicated that no auxiliary feedwater was actually pumped into any of the steam generators. Neither of the other two Auxiliary Feedwater System motor-driven pumps were actuated at BVPS Unit No.2. "The design for these two solenoid-operated isolation valves are susceptible to briefly popping open if steam is initially introduced too rapidly. These valves fail open with no power and are pilot-operated solenoid-actuated to close. An initial large steam rush can briefly overcome the solenoid force holding the valve shut. This is what occurred on October 16, 2008. Therefore, this brief rotation of the steam-driven Auxiliary Feedwater Pump was not initiated by a valid actuation signal. "This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since it involved a train-level actuation of the PWR auxiliary feedwater system as listed in 10 CFR 50.73(a)(2)(iv)(B)(6). This actuation was not part of a pre-planned sequence and did not occur with system properly removed from service. "However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification instead of submitting a written Licensee Event Report since the actuation of the Auxiliary Feedwater System train was not generated by a valid actuation." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-11-17
44660 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2008-11-17 05:51 | 2008-11-17 09:21 | 2008-11-17 | MANUAL REACTOR SCRAM DUE TO HIGH TURBINE VIBRATION "At 0551 hours EST, on November 17, 2008, the H. B. Robinson Steam Electric Plant, Unit No. 2, reactor was manually tripped from approximately 78% power due to high vibrations detected on the main turbine. The reactor trip was initiated in accordance with Abnormal Operating Procedure, AOP-006, "Turbine Eccentricity / Vibration." At approximately 0230 hours EST, it was noticed that turbine vibration on the No. 9 bearing was at approximately 10.9 mils and increasing. At 0516 hours EST, the No. 9 bearing was at about 13.5 mils and still increasing. A power reduction from 100% power was commenced in accordance with Operating Procedure, OP-105, "Maneuvering the Plant when Greater than 25% Power." At approximately 0551 hours EST, with power level at approximately 78%, the No. 9 bearing vibrations reached the trip criterion of 14 mils and the reactor was tripped in accordance with AOP-006. "Path-1, which is the flow chart based on the Westinghouse Owners Group Emergency Response Guideline E-0 for reactor trip response, and Procedures EPP-4, "Reactor Trip Response," and GP-004, "Post Trip Stabilization," were used after initiation of the reactor trip. The auxiliary feedwater system started automatically, as expected, in response to steam generator level changes after the reactor trip. It was also noted that the "B" Main Feedwater Pump had tripped. The cause of the main feedwater pump trip has not been determined and is under investigation. The primary system and steam generator power operated relief valves and safety valves did not actuate during this event. The main feedwater system, main steam system, and condenser remained available during the event and are currently being used for decay heat removal. The normal post-trip electrical configuration is providing power to the required buses and the offsite electrical system is stable at this time. The emergency diesel generators are operable. The unit is currently stable in MODE 3. An estimated restart date has not yet been established. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) for reactor protection system actuation and 10 CFR 50.72(b)(3)(iv)(A) for automatic actuation of the auxiliary feedwater system." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-11-17
44659 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2008-11-14 07:00 | 2008-11-14 09:41 | 2008-11-14 | LOSS OF ERDADS "This notification is being made due to an unplanned loss of ERDADS communication to the NRC for greater than one hour. "At 0700 on November 14, 2008, the Unit 2 Control Room noted that the information from ERDADS did not appear to be updating. Notifications were made and Engineering and Operations responded to investigate. The B train of ERDADS failed at 0357 and the backup A train did not auto transfer as expected. The B train was manually failed over and the A train assumed control at 0730. The B train was rebooted and has assumed the standby position. "The system is currently functioning as expected and all communications have been restored." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-14
44658 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-11-13 20:31 | 2008-11-13 21:43 | 2008-11-14 | LOSS OF PROMPT NOTIFICATION CAPABILITY "At approximately 2031 Eastern time, Jacksonville National Weather service has notified Plant Hatch that the capability to broadcast prompt notification messages is not available at this time due to problems with the phone service. Emergency Preparedness personnel have been contacted to ensure proper notifications have been made. Security has notified state and local agencies along with Information Technology (IT) group of the problem." The licensee has notified NRC Resident Inspector. * * * UPDATE FROM SCOTT BRITT TO JOE O'HARA AT 0410 ON 11/14/08 * * * At 2315 on 11/13/08, the National Weather Service notified the licensee that the notification network is available. However, the National Weather Service cannot guarantee that the system will remain operational due to on-going maintenance activities on the system. The licensee is monitoring the notification network and will provide an update once the maintenance is complete and system reliability is fully restored. Notified R2DO(Bonser) * * * UPDATE FROM BILL DUZALL TO JOHN KNOKE AT 1440 EST ON 11/14/08 * * * Troubleshooting the system has been completed. Although the system was restored at 2315 EST on 11/13/08, the verification that the system would maintain operability was not completed until 1440 EST on 11/14/08. The licensee has notified NRC Resident Inspector. Notified R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-13
44657 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-11-13 10:49 | 2008-11-13 12:16 | 2008-11-18 | AGREEMENT STATE REPORT - BREACHED 90 MILLICURIE CS-137 SOURCE "Ludlum-Sweetwater just called [state] to report a breached source. A 90 milliCurie cesium-137 source was cut open in the machine shop about 45 minutes ago. [A company representative] believes most of the contamination was contained to the machine shop area with a small amount being tracked to different parts of the plant. "Workers were machining a piece of metal and did not realize it had a source in it. The workers were using a grinder and cutting on what they thought was a spacer. The source was to be mounted into a pig and used as a calibration source. "The licensee needs assistance [from the state] with the names of companies licensed to assist with clean up." Texas Incident Number: I-8580 UPDATE ON 11/14/2008 AT 1427 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received from the state via e-mail: "On 11/13/08, Ludlum Instruments, a Texas licensee located in Sweetwater, Texas, reported that an employee accidentally breached a small Cesium (Cs) - 137 source while modifying a piece of calibration equipment. An [State of Texas] agency inspector was dispatched to the scene to investigate. Initial reports were that 40 or more employees were involved and that contamination had been spread by foot traffic through the facility. "The inspector provided the following information. "Ludlum has contracted an out-of-state company (Energy Solutions) to perform assessment and decontamination activities resulting from the breach of the 90 mCi Cesium (Cs) -137 source. The company will perform initial assessments over the weekend and begin operations Monday. Our [State of Texas] inspector reported that contamination levels were fairly low with some spots reading approximately five times background levels. That would equate to about 10,000 - 15,000 counts per minute on a scintillation detector. "Ludlum has also contacted the Department of Energy's Radiation Emergency Assistance Center /Training Site for guidance on assessing possible internal deposition of material. Urine specimens are being collected for analysis to determine the presence of Cs-137. "Overall, it appears that Ludlum acted quickly and responsibly in reporting and containing the contamination once it was discovered. We will continue to monitor the situation as the assessment and cleanup progresses. "Ludlum has issued a press release and the story is being reported in the D/FW [Dallas/Fort Worth] area. "Conversation with the Radiation Safety Officer (RSO) at Ludlum on November 14, 2008, provided the following information: "The whole facility is currently posted and controlled as a Contaminated Area. The area is isolated and posted 'Do Not Enter.' There has been some decontamination done by Ludlum, but they are going to wait for the contractor to assess the areas before removing barriers. Energy Solutions is due to arrive at the facility this afternoon (11/14/08). They should start work as soon as they receive reciprocity from the State of Texas. The RSO stated that they were in contact with our [State of Texas] Radioactive Materials Group Manager to expedite the reciprocity. They anticipate allowing some workers to return to work on Monday. "The RSO stated that they have four individuals of concern currently. Oak Ridge recommended 24-hour in-vitro bioassays samples for those four individuals. No one was sent home contaminated. Two individuals were concerned that they may have taken contamination home. The homes were surveyed and no contamination was detected. "Ludlum will begin reenactments and dose studies for the workers involved next week. "The source was a gamma gauging source, AEA technology Model number CDC.800 source. The Cs-137 sources is an inorganic pellet, fired at high temperature to bond the Cs -137 in the ceramic pellet. The serial number has not yet been provided. It is currently believed that 30 to 40 percent of the 90 millicuries contained in the source was removed by the grinding operation. "The RSO stated that a group was working on some calibrations and noted the background in their area was slowly increasing. At first they thought someone who had received a medical procedure was the cause, but tracked the source of the elevated dose rates to the individuals grinding on the source. "The RSO stated that they had not conducted any air sampling of the area as they do not have the equipment necessary to do so. They will rely on bioassay results for internal dose assessments." Notified R4DO (Whitten) and FSME (Flannery). * * * UPDATE ON 11/14/2008 AT 1603 FROM ART TUCKER TO MARK ABRAMOVITZ * * * "The Radiation Safety Officer states that the source was cut in half and that no grinder was involved in the process. She also stated that the calculated decayed activity of the source before it was damaged was 80 millicuries. The remaining sections of the source were assayed and the activity remaining is 48 millicuries. It is believed that the majority of the activity released is in the area of the saw. The source is 0.24 inches in diameter and 0.32 inches long and a cumulative wall thickness of 0.05 inches." Notified the R4DO (Whitten) and FSME (McConnell). * * * UPDATE ON 11/18/2008 AT 1123 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "The Radiation Safety Officer (RSO) at Ludlum reported that the contractor should have a full compliment of workers and instruments today and that cleanup work should be in full swing later today. The RSO also stated that she had incorrectly stated that a cutter was used to cut the source in two. It was a grinder as first reported. "The four workers identified as having potential body burdens have provided urinalysis samples and will receive whole body counts (WBC) at Comanche Nuclear Power Station on November 19, 2008. Ludlum currently intends to provide all of their workers with WBC. "The facility is a 60,000 square foot facility. It is divided into several areas most having their own air handling system. Currently, the contamination appears to be mostly on the floor in areas out side the work area. No survey information is available in the work area where the source was breached." Notified the R4DO (Cain) and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-11-18
44656 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2008-11-12 16:55 | 2008-11-13 11:17 | 2008-11-24 | CONTROLLED SUBSTANCE FOUND WITHIN PROTECTED AREA. A controlled substance was found within the protected area. Contact the Headquarters' Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM CLARKSON TO KNOKE AT 1418 EST ON 11/14/08 * * * A non-licensed, contract employee was found in possession of a controlled substance. The contract employee's access to the plant has been terminated. Contact the Headquarters' Operations Officer for additional details. The R2DO (Bonser) was notified. * * * UPDATE FROM NEWMAN TO SNYDER AT 1834 ON 11/24/08 * * * The material was turned over to and tested by the Oconee County Sheriff's Office (OCS). On 11/24/08 at 1500 hours OCS informed site security that the test result was positive. The investigation into this matter is continuing. Notified R2DO (Guthrie). | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2008-11-13
44655 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-11-13 00:20 | 2008-11-13 03:22 | 2008-11-13 | OIL SPILL FROM CIRCULATING WATER PUMP OIL SIGHT GLASS LINE "On November 13, 2008, at 0020 CST, the State of Nebraska, Department of Environmental Quality and National Response Center were notified by Omaha Public Power District's Fort Calhoun Nuclear Station of an oil spill due to a crack in upper pump bearing sight glass line for 'C' Circulating Water Pump, CW-1C. The spill involved a small quantity of oil estimated to be less than one gallon to the intake Structure sump with trace amounts discharged to the Missouri River. Per Fort Calhoun Nuclear Stations' National Pollutant Discharge Elimination System (NPDES) permit, the notifications were made and samples were taken for offsite analysis to determine if the quantity discharged involved an actual violation of the discharge permit. "This notification is being made in accordance with 10 CFR 72.75 (b) (2) (xi), 4 hour non-emergency notification due to a notification being made to a Government Agency (State of Nebraska, Department of Environmental Quality and National Response Center)." The licensee notified NRC Resident Inspector. The licensee also notified the Nebraska Department of Environmental Quality and the National Response Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-11-13
44654 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-11-13 01:02 | 2008-11-13 03:04 | 2008-11-13 | LOSS OF NATIONAL WEATHER SERVICE PROMPT NOTIFICATION MESSAGES "At approximately 0102 eastern time, Jacksonville National Weather service has notified Plant Hatch that the capability to broadcast prompt notification messages is NOT available at this time due to problems with the phone service. Emergency Preparedness personnel [DELETED] have been contacted to ensure proper notifications have been made. Security has notified state and local agencies along with Information Technology (IT) group of the problem. At 0145, Jacksonville National Weather service has reported that the problem with the phone service has been resolved and that the broadcast system has been restored. All agencies have been made aware of the NWS system return to service." The licensee notified Georgia EMA, Appling County, Jeff Davis County, Tattnall County, and Toombs County. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-13
44653 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2008-11-12 | 2008-11-12 09:59 | 2008-11-12 | ALL DIMENSIONALLY VERIFIED COMMERCIAL GRADE ITEMS PROCESSED PER FISHER MANUFAC. PROCEDURE FMP 2K28 "Commercial grade items processed per FMP 2K28 (Fisher Processing Level D) may not address all the critical characteristics needed to determine if the item can be designated by the utility as a basic component. By accepting 10CFR21 on the order for Level D items, there is the implication that the item can be used as a basic component without further evaluation by the utility. "During the latest NUPIC audit, it was pointed out that although FMP 2K28 specifically states that, 'This process does not verify the material or designate the item for use as a basic component,' 10CFR21 is only applicable to basic components. "FMP 2K28 is intended to provide dimensional verification only for items where material verification was not readily available through Method 1 discussed in EPRI 5652. Parts provided per Level D are normally elastomer materials (diaphragms, o-rings, etc.) or packing and gasket materials. If a utility decides material verification is a critical characteristic, Fisher assumes that the utility will perform a material evaluation as required prior to designating an item as a basic component. "In conclusion, Fisher assumed 10CFR21 responsibility because of defect reporting requirements but did not intend to imply that items processed to FMP 2K28 (Fisher Processing Level D) were capable of becoming a basic component without further evaluation by the purchaser. "In the future, Fisher will no longer be able to accept 10CFR21 responsibility for parts processed to FMP 2K28 (Fisher Processing Level D). "Fisher will also accommodate those orders requiring dedication traditionally offered as Level D through development and us of additional methods described in EPRI 5652." Potentially affected sites are: Ameren, Arizona Public Service, Arkansas Nuclear, Beaver Valley, Brunswick, Callaway, Calvert Cliffs, Catawba, Comanche Peak, Con Edison, Consumers Energy, Cook, Cooper, CP&L, Crystal River, Davis Besse, Detroit Edison, Dominion Energy, Dominion Power, Duke Energy, Duquesne, Entergy, Exelon, Fermi, Florida Power, G.E. Nuclear, Ginna, Harris, Hatch, Indian Point, Hatch, Kewaunee, Maine Yankee, McGuire, Millstone, Monticello, New York Power Authority, Niagara Mohawk, Nine Mile Point, North Anna, Northeast Nuclear, Oconee, Oyster Creek, Palo Verde, PECA, Perry, Progress Energy, PSE&G, Rochester Gas & Electric, Salem, San Onofre, Shearon Harris, Southern California Edison, South Texas Project, Surry, Texas Utilities, Turkey Point, V.C. Summer, Virginia Power, Vermont Yankee, Waterford, Watts Bar, Westinghouse Electric Corp, Wisconsin Public Service, Wisconsin Electric Power, Wolf Creek, XCEL Energy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2008-11-12
44652 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-11-11 18:46 | 2008-11-11 22:30 | 2008-11-11 | MANUAL REACTOR TRIP DUE TO A FEEDPUMP TRIP "At 1846 the reactor was manually tripped due to 'B' Main Feed Pump [MFP] trip on low lube oil pressure. The plant was operating at 97 percent [power] when annunciation was received that 'B' MFP was experiencing low lube oil pressure. Subsequently the 'B' MFP tripped on low lube oil pressure. The operating crew manually tripped the reactor per procedure OTO-AE-00001. The Auxiliary Feedwater System automatically actuated. All control rods fully inserted during the event and all safety systems responded as designed. The unit is removing decay heat using steam dumps to the Main Condenser. No primary relief valves or Main Steam relief valves lifted during the event. [The licensee is] currently investigating low lube oil pressure on 'B' MFP. Aux Feed is supplying make up to the steam generators." The plant is in normal electrical shutdown line-ups. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-11-11
44651 | 0 | HAMPTON UNIVERSITY |  |  |  |  | 2008-07-31 | 2008-11-10 13:44 | 2008-11-10 | LOST SOURCE An 8.6 microCi Th-228 licensed source (Isotope Products Lab 535-24-1) of the Physics Department at Hampton University has been identified as lost. As of July 31, 2008, several attempts in trying to locate the source have failed. The licensee contacted NRC Region 1. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-11-10
44650 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-11-10 10:00 | 2008-11-10 10:51 | 2008-11-10 | AGREEMENT STATE REPORT - STOLEN XRF DEVICE A XRF Device is a portable device used for lead paint analysis / testing. "This device contains approx. 15 millicuries of Co-57." "The device was stolen from the cab of a pick up truck [in Hyde County] between Thursday night (11/06/08) and Friday night (11/07/08). The theft has been reported to the Hyde County Sherriff's Department. Notification has also been provided to the device manufacturer. "While this device represents licensed radioactive material designated to require specific storage and use criteria, the NC Radiation Protection section does not believe the device represents an opportunity for malicious actions. "The NC Radiation Protection Section will be working with the licensee (and LLEA as needed) to attempt recovery of the device." NC Incident No. 08-50 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-11-13
44649 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-11-09 18:21 | 2008-11-09 23:29 | 2008-11-09 | REACTOR TRIP BREAKERS OPENED MANUALLY DUE TO INDICATED DROPPED CONTROL ROD "On 11/19/08 at 1821 with unit 2 in Mode 3, the unit 2 reactor trip breakers were opened from the Main Control Room (MCR) due to indications of a Shutdown Bank "A" Rod E-11 dropping into the Reactor Core. At the time the reactor trip breakers were opened, the MCR Operators were in the process of withdrawing Shutdown Banks in preparations for entry into Mode 2. All other Shutdown Banks and Control Banks were inserted at the time the reactor trip breakers were opened. In addition, a Feedwater Isolation Signal was generated as designed. All safety related equipment operated as designed. "The Plant is being maintained in Mode 3 at NOT/NOP, approximately 547 F and 2235 psig, with AFW supplying the S/G's and Steam Dumps to Main Condenser removing decay heat. "No primary system or steam generator safety valves opened due to this trip. "An investigation has been initiated to determine the cause of the indications of Shutdown Bank 'A' Rod E-11 dropping into the Reactor Core." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-11-09
44648 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-11-09 15:30 | 2008-11-09 20:44 | 2008-11-11 | TECHNICAL SUPPORT CENTER HVAC OUT OF SERVICE "The TSC Normal HVAC (A-1563-A7-001) and Normal Chilled Water Pump (A-1564-P7-001) tripped for unknown reasons after approximately 10 minutes of operation following restoration to normal from surveillance 14400A-1. "This report is being made per Technical Requirements Manual 13.13.1, action B.2. With the TSC Normal HVAC and Chilled Water Pump inoperable, the Functionality of the TSC has been lost due to inability to maintain proper climate control. The alternate TSC facility is available and actions are being taken to return the TSC to Functional status with a high priority. The NRC Resident Inspector has been notified." * * * UPDATE ON 11/11/2008 AT 1534 FROM STEPHEN HARRIS TO MARK ABRAMOVITZ * * * The TSC Emergency Response Facility was restored to Operable status on 11/11/2008 at 1442. The licensee notified the NRC Resident Inspector. Notified the R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-09
44647 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-11-09 11:08 | 2008-11-09 12:08 | 2008-11-09 | MANUAL REACTOR SCRAM DUE TO SPURIOUS SRV OPENING "One hour reportable event based on a safety relief valve (SRV) failure to close (NUREG 0626 and NUREG 0660). "On 11/09/08 at approximately 11:08 with Unit 2 at 100% steady state power SRV 2-B21-F013H spuriously failed full open with no operator action or testing in progress. The valve's control switch was cycled as required by Abnormal Operating Procedure AOP-30 with no success. At 1113 the valve was successfully closed by pulling the associated fuses. At 1117, a manual reactor scram was inserted based on a Torus temperature of 109.8 degrees F (Technical Specifications require a scram to be inserted at 110 degrees F). All control rods [fully] inserted from the manual scram signal. Reactor water level lowered to Low Level 2 resulting in Primary Containment Isolation System (PCIS) isolations of Groups 2, 3, 6, and 8. In addition, this resulted in a Reactor Core Isolation Cooling (RCIC) system actuation and injection into the reactor. The High Pressure Coolant Injection (HPCI) system actuated but did not inject because reactor water level recovered. An Alternate Rod Insertion signal was received, the Standby Gas Treatment (SBGT) system initiated, and the Reactor Recirculation Pumps tripped as designed. "Plant safety systems responded as designed to the transient. "[Licensee] investigations are underway to determine the cause of the SRV failure." Reactor decay heat is being removed through the main turbine bypass valves to the condenser. Reactor make-up is being maintained by the normal feedwater system. The plant is in its normal shutdown electrical lineup supplied by offsite power. The diesel generators are available for service to the plant. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | OTHER UNSPEC REQMNT | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2008-11-09
44646 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-11-08 08:35 | 2008-11-08 09:06 | 2008-11-08 | OSC INOPERABLE DUE TO PLANNED MAINTENANCE ON MOTOR CONTROL CENTER "Planned maintenance activities are being performed today (November 8, 2008) on the Hatch Nuclear Plant's 1C 4160V Bus (1R22-S003) Frame 5 under work order number 1041640301. The planned work will remove power from 1R24-SO34 and 1R24-SPO60 which will affect the Unit 1 Service Building and Unit 2 Service Building Annex. This will deenergize power to the Primary Operations Support Center (OSC) rendering the OSC non-functional. (TRM - Section T 3.10.1 EMERGENCY RESPONSE FACILITIES) during the performance of this work activity. "The specific work is to replace the breaker in frame 5 of 1C 4160V Bus (1R22-S-003) and perform routine preventative maintenance on 1R24-S034 and 2R24-S050 (Work Order # 1041641101) while they are de-energized to minimize future out of service time. This work activity is planned to be performed expeditiously and will be completed within 10 hours. If an emergency were to occur, it is estimated that power can be restored in approximately 1 hour. If an emergency condition occurs that requires activation of the OSC, the Alternate OSC in the Simulator Building will be used in accordance with plant procedure 73EP-EIP-021-0, Alternate Operations Support center (OSC) Activation, until power is restored. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects the emergency response facility." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 11/8/2008 AT 1614 FROM EDWIN URQUHART TO MARK ABRAQMOVITZ * * * At 1602 EST, power was restored to the OSC Motor Control Center. Notified the R2DO (Widmann). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-08
44645 | -1 | PALISADES | 1 |  |  | [1] CE | 2008-11-07 14:41 | 2008-11-07 22:00 | 2008-12-30 | LOAD CALULATIONS FOR EDG WERE INCORRECT "During a review it was determined that the Diesel Generator load calculation (EA-ELEC-LDTAB-005) did not account for worst case load from the Containment Air Cooler Fan Motors (V-1A, V-2A, V-3A). Initial review indicates that with the worst case fan motor loading, Diesel Generator 1-2 could be loaded beyond its 2 hour rating following a Loss of Coolant Accident (LOCA) during the time period prior to Recirculation Actuation (RAS). "The horsepower loading for the motors used in the Diesel Generator load calculation was based on the original specification for the motors. In 1993 calculation EA-DPAL93-110 was done to determine the impact of partial flooding of the air coolers coils on the cooling fan performance. The 1993 calculation calculated a fan motor load that was higher than what is used in the diesel generator load calculation. However, the diesel generator load calculation was not updated as a result of the 1993 calculation. "The higher motor power requirement is 17 kW per fan. There are 3 Containment Air Cooler fans loaded on Diesel Generator 1-2. The extra loading, when combined with the possible additional load from operating the diesel generator at increased frequency, raises the calculated load to 2782 kW, which is above the 2 hour rating of 2750 kW. The overload only applies during a time segment of the diesel generator load profile prior to RAS. This could result in the loss of the diesel generator. "There is only 1 Containment Air Cooler Fan Motor (V4A) loaded on Diesel Generator 1-1 and has 121 kW margin available. Therefore, there is no concern about overloading Diesel Generator 1-1. "Placed hand switches (42-299CS & 42-277CS) for Turbine Generator Emergency Air Side Seal Oil Backup Pump (P-23) and Turbine Turning Gear Oil Pump (P-26) in Pull-To-Lock position, which prevents the pumps from automatically starting. This reduces the potential load on 1-2 D/G by 71 kW. This restores the load on the diesel to within the margin." Licensee has notified the NRC Resident Inspector * * * RETRACTION AT 1416 EST ON 12/30/08 FROM DAVIS TO HUFFMAN * * * "Entergy Nuclear Operations Inc. (ENO) is retracting Event Notification EN #44645 which reported a loss of a safety function due to the 1-2 emergency diesel generator (EDG) load calculation not accounting for the worst-case load from the containment air cooler fan motors. The initial review indicated that, with the worst-case fan motor loading, the 1-2 EDG could have been loaded beyond the 2750 kW two-hour peak loading limits following a loss-of-coolant accident during the time period prior to a recirculation actuation signal. This condition may have caused 1-2 EDG to become inoperable, and could have prevented fulfillment of a safety function. "In a subsequent evaluation of loading capability, completed on December 18, 2008, ENO determined the 1-2 EDG was operable. The EDGs are rated for 2750 kW two-hour peak operation. It was determined that the postulated peak load for the 1-2 EDG would have been 2819 kW for a period of approximately thirty-eight minutes. However, based on engineering information obtained from the vendor of the 1-2 EDG, Fairbanks-Morris Engine, and reviewed by ENO, the 1-2 EDG could have been operated up to 2830 kW for fifty minutes before any susceptibility to damage might occur. In addition, under the peak loading condition of 2819 kW, the speed of the 1-2 EDG would have remained above the Technical Specification limit of 59.5 Hz. The subsequent review confirmed that the safety function would have been fulfilled. Therefore, ENO is retracting this event notification." The licensee has notified the NRC Resident Inspector. R3DO (Cameron) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-11-07
44644 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2008-11-07 18:00 | 2008-11-07 18:01 | 2008-11-08 | PLANNED LOSS OF EMERGENCY PHONE SERVICE "The Emergency Notification System (ENS), Emergency Response Data System (ERDS), Health Physics Network (HPN), Protective Measures Counterpart Link (PMCL), Reactor Safety Counterpart Link (RSCL), and site commercial telephone lines are being removed from service for a planned maintenance outage. The outage is scheduled for duration of 12 hours. The plant radio system, plant page system and 3-digit OMNI phone system are unaffected by the maintenance. "Temporary telephone lines have been assigned to the Peach Bottom Emergency Telephone System (ETS) to support station communications to and from the NRC. The ENS and ERDS lines in the Peach Bottom MCR and TSC and the HPN, RSCL and PMCL in the TSC will all have off-site dial capability throughout the outage. The NRC HOO has been provided the temporary numbers to be used to contact the station during this phone outage. "This is an 8-hour reportable event per 10 CFR 50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of plant systems will not be affected due to this planned action. "The licensee has informed the NRC Resident Inspector." * * * UPDATE FROM C.J.CAMPBELL TO JOE O'HARA AT 0211 ON 11/8/08 * * * "As of midnight, the maintenance is complete, and the phone service has been returned to service. " The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-07
44643 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-11-07 09:00 | 2008-11-07 15:36 | 2008-11-07 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was transmitted by the state via facsimile: "Licensee called the Agency [Massachusetts] to report a stolen Troxler gauge, model # 3440 and serial # 21550. Gauge user had the locked transport case and the locked gauge stored inside a personal vehicle for the purpose of driving to a work site scheduled for 11/7/08. The vehicle was parked in Hubbardston, MA overnight (11/6 - 11/7/08). In the morning of 11/7/08, it was discovered that the personal vehicle had been broken into and the transport case and gauge was missing and presumed stolen. Other personal vehicles in the local area also had been broken into on the same night." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-11-12
44641 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-11-07 15:08 | 2008-11-07 15:36 | 2008-11-07 | SAFEGUARDS EVENT - PHYSICAL SECURITY Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-11-07
44640 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-11-07 13:37 | 2008-11-07 15:24 | 2008-11-07 | FITNESS FOR DUTY A licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2008-11-07
44639 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2008-11-07 07:00 | 2008-11-07 14:21 | 2008-11-07 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "On November 7, at 7:00 AM the Illinois Emergency Management Agency's Communications Center contacted our [Illinois Emergency Mgmt. Agency] Radiation Duty Officer to advise they had been told of a theft of radioactive material. The report was filed by the Radiation Safety Officer of GSG Material Testing Inc. A portable moisture density gauge had been stolen from their temporary worksite in Chicago during the night. The Troxler model 3430 (s/n 35592) had been forcibly removed from a construction trailer at 704 West 42nd Street, Chicago, IL. The gauge contains two sources; 9 milliCi Cs-137and 40 milliCi Am-241:Be. The call to the IEMA Comm Ctr came from the licensee's Radiation Safety Officer [DELETED]. The gauge was last seen in the trailer yesterday at the close of business. The Chicago Police Department was contacted and had arrived at the scene to complete a report. Evidence at the scene indicated thieves had entered by bending bars which were over a window and then breaking the glass. They had ransacked the trailer looking for items of worth. They broke the lock on the transport container which held the gauge and then removed the gauge from the trailer. The licensee indicated that, contrary to instructions, the field technician assigned the gauge had left the device in the trailer. The RSO also indicated that during today's police interview, they were advised that the trailer had a previous break-in a few months prior, of which they were unaware. The Agency [Illinois Emergency Mgmt. Agency] is awaiting additional information from the licensee before potentially taking enforcement action. A reactive inspection may be justified. We [Illinois Emergency Mgmt. Agency] are considering this matter open." Illinois Report Number: IL0800065 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2008-11-12
44638 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2008-11-07 08:34 | 2008-11-07 12:05 | 2008-11-07 | AUTOMATIC REACTOR TRIP "At 0834 on 11-7-08, Oconee Nuclear Station (ONS) Unit 3 experienced an automatic reactor trip due to a reactor protective systems (RPS) actuation. ONS Unit 3 post trip parameters are normal. Main Feedwater remained in service following the event and Emergency Feedwater was not required and remained available. Electrical power automatically transferred to the Startup power source from the switchyard and emergency AC power sources were not required and remained available. The cause of the RPS actuation and automatic reactor trip are under investigation. "ONS Unit 1 remained at 100% power with no issues following the ONS Unit 3 reactor trip. ONS Unit 2 remained in No-Mode. No other safety systems have actuated or exhibited abnormal behavior. Therefore, the safety significance of this condition is low." All control rods fully inserted during this event. The unit is removing decay heat to the main condenser. No primary relief valves lifted and Main Steam relief valves cycled following the trip. There are no Steam Generator tube leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-11-07
44637 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-11-07 09:55 | 2008-11-07 11:31 | 2008-11-07 | DISCHARGE OF BIODEGRADABLE OIL INTO INTAKE BAY "Observation of discharge of Terasolve 146 biodegradable fish oil into the Delaware river at the 11B Circulating Water Pump intake bay. The discharge was from a dewatering pump leak that was stopped. The fish oil has dissipated. The amount was 2 - 3 oz." The licensee has notified the NRC Resident Inspector. The licensee will notify Lower Alloways Creek Township. R1DO (Hansell) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-11-07
44636 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2008-11-06 15:10 | 2008-11-07 08:58 | 2008-11-07 | LOST X-RAY ANALYZER CONTAINING CADMIUM-109 AND IRON-55 "On November 6, 2008, at 1510, IDPH received a call from Keokuk Steel Castings, Registration No.: 3325-1-56-XRF that a TN Technology X-ray Fluorescent Analyzer, model 9266, serial number B837, containing 5 mCi of Cadmium-109 and 45 mCi of Iron-55, was missing. "The licensee was returning the device to Thermo Scientific for disposal. On 2/26/08, the licensee shipped the device via UPS. "On 6/3/08, the licensee was contacted by Thermo Scientific that the device never arrived. "The licensee contacted UPS and on 7/7/08, a Tracer Investigation was opened. UPS never located the package (tracking no. 1Z5421030340748497). "IDPH contacted a UPS Supervisor who stated that the last known location of the package was Des Moines, Iowa, and the UPS investigation was closed on 7/16/08. He was asked to reopen the file and to look one more time for the package. He called back and stated that the device could not be located in Des Moines. IDPH and UPS consider the case closed." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2008-11-12
44635 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2008-11-06 20:27 | 2008-11-06 21:49 | 2008-11-06 | TECH SPEC REQUIRED SHUTDOWN REQUIRED DUE TO FAILED SURVEILLANCE TEST "Nine Mile Point (NMP) Unit 1 initiated a Technical Specification (TS) shutdown at 2027. "During a normal Instrumentation Surveillance Test, a relay for Emergency Condenser (ECCS) Initiation failed to meet its acceptance criteria (at 1245). This placed the plant in an action statement that required placing a channel trip in for the affected relay channel in 24 hours. "To perform the relay replacement NMP Unit 1 entered 1 hour TS shutdown Limiting Condition of Operation at 1928. At 2027 Shutdown of the plant was initiated by lowering reactor recirculation flow and thus reactor power. At 2031, relay replacement was completed, [at] 2038 plant returned to full power operations. "The plant remained in 24 hour action statement until post maintenance testing was completed at 2124." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-11-06
44634 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2008-11-06 08:56 | 2008-11-06 16:27 | 2008-11-06 | DEFECT FOUND IN BUSSMAN FUSES "On November 6, 2008, Nebraska Public Power District (NPPD) completed a reportability determination which concluded that a batch of Bussmann fuses with a date code of J47 contained an underlying fabrication vulnerability that could result in a premature failure of the fuse. NPPD has concluded this condition is reportable per 10 CFR Part 21, since the underlying vulnerability could create a substantial safety hazard. The fuses are Commercial Grade items dedicated by NPPD for use at the Cooper Nuclear Station (CNS). The fuses are shipped directly from an authorized Bussmann facility to CNS. The fuse purchasing description is as follows: FUSE ; 10 AMP ; 250VAC ; ONE-TIME ; 50KA I.R. ; GENERAL PUPOSE ; Manufacturer Part Number NON-10. These fuses, with batch code of J47, have been determined by independent analysis to contain a poor solder joint internal to the fuse. "These fuses are authorized by NPPD for use in both safety related and non safety related applications. The applicable dedication package identifies one of the safety functions as 'Fuses are required to conduct the design basis load current without interruption.' If the fuses were installed without the condition being detected and failed upon valid demand of associated circuit, the mission of the associated safety related equipment may not have been accomplished. However, since the fuses were found, the safety function of the installed fuses is maintained and the associated equipment remains operable based on specific instructions for maintaining the fuses in place until replacement. Therefore, this condition is NOT reportable under 10 CFR 50.72 or 50.73. However, installation could have occurred and remained undetected, thus introducing a common mode failure in certain applications, thus fulfilling the definition of a Substantial Safety Hazard as defined by 10 CFR Part 21. Based on independent analysis of fuse mode of failure, the defect may not be necessarily detected upon installation. Since the fuses were stocked in unrestricted spares for essential applications, 10 CFR Part 21 applies, and the condition is reportable under 10 CFR 21.21. The Responsible Corporate Officer has been notified of this condition per 10 CFR 21.21 (d)(3)(i) on November 6, 2008 at 08:56 AM, CST. Pursuant to 10 CFR 21.21 (d)(3)(ii) written notification is due to the NRC within 30 days of this notification." Forty fuses were in the defective lot of which 15 are still installed in plant systems: Circ Water, RCIC, Emergency Diesel Generator 2, air removal and 4160 VAC diesel start breaker circuitry. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 21.21 |  |  |  | 0 | 2008-11-06
44633 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-11-06 11:15 | 2008-11-06 14:47 | 2008-11-06 | OFFSITE NOTIFICATION OF A DISCHARGE TO THE MISSISSIPPI RIVER "On November 6, 2008 at 11:15, Operations was notified that results of an October 20, 2008 oil and grease weekly sample from a plant sump discharge to the Mississippi River exceeded the National Pollution Discharge Elimination System (NPDES) daily maximum allowable value of 15ppm. The October monthly average oil and grease NPDES of 10ppm was also exceeded. The Minnesota Pollution Control Agency is being notified." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-11-06
44632 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-11-05 22:54 | 2008-11-06 00:59 | 2008-11-06 | BOTH TRAINS OF CONTROL ROOM EMERGENCY AIR TEMPERATURE CONTROL DECLARED INOP "WBN Unit 1 initiated a Tech Spec required shutdown at 2254 on 11/05/08. The plant entered TS 3.0.3 at 2135 on 11/05/08 due to both trains of Control Room Emergency Air Temperature Control (CREATCS) being declared inoperable. Initially Train 'B' CREATCS was inoperable due to the scheduled maintenance of Train 'B' auxiliary air system. With one train of Aux Air inoperable this renders that respective train of CREATCS inoperable. During this planned maintenance the 'A' train CREATCS chiller lost ability to cool the Main Control Room due to a failure in the control circuitry. This rendered 'A' train inoperable which led to entry into TS 3.0.3 for both trains CREATCS being inoperable. The plant exited TS 3.0.3 at 2345 on 11/05/08 upon completion of Post Maintenance Testing on the train 'B' Aux Air system and return to operability of the 'B' train Aux Air and therefore the 'B' train of CREATCS. The planned plant shutdown was stopped upon exit of TS 3.0.3 at 2345 11/05/08 and Rx power restored to 100%." The licensee notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-11-06
44631 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-11-04 17:24 | 2008-11-05 13:23 | 2008-11-05 | AGREEMENT STATE - LOST TROXLER GAUGE The following information was provided by the state via facsimile: "The following information was reported to the Radiation Management Unit (RMU) of the Colorado Department of Public Health and Environment (CDPHE) by the acting RSO of a Colorado Licensee - Earth Engineering Consultants, Inc (EEC) - pertaining to a lost/stolen moisture density gauge. "[On November 04, 2008] After taking a series of density tests of aggregate base course material for a new roadway on Jacoby Farms 5th Filing development project in Windsor, Colorado, (site location is on the north side of State Highway 392 and east 17th Street in Windsor, CO), the field technician placed gauge on his bumper, transferred the results onto his field paperwork, visited with the project supervisor and discussed the results, then entered his truck to complete additional paperwork, and received a call on his cell phone for his next project assignment. Time elapsed and the technician failed to secure the gauge back into the lock box within the pick-up truck. After realizing his dilemma, the technician immediately stopped the truck and began a search for the missing gauge. Phone calls were made to the project foreman, and an extensive search took place re-tracking the steps and paths taken. [The licensee] called the Health Department Radiation [Management Unit] and left several messages informing the state [of the missing Troxler]. "At approximately 11:45 AM on 11/5/08, CDPHE RMU followed up with the licensee via phone regarding the incident, at that time the licensee reported that he believed that the gauge had been recovered/found and had been dropped off at an area fire department by a member of the public last evening (11/4/08). The licensee indicated they were sending someone to the fire department to verify this and retrieve the gauge. The licensee indicated that the gauge was scratched but appeared to be intact and confirmed they would inspect the gauge and survey it. The licensee indicated that they would be sending the gauge to a local gauge repair company for leak testing and repair (as applicable). The CDPHE RMU is awaiting final confirmation/information from the licensee." * * * UPDATE PROVIDED BY JAMES JARVIS TO JASON KOZAL VIA FAX ON 11/5/08 AT 1804 * * * The following information was provided by the state via facsimile: " At approximately 13:15 hours [MST on 11/5/08] the Radiation Management Unit (RMU) of the Colorado Department of Public Health and Environment (CDPHE) received confirmation that the moisture density gauge lost during the evening of 11/4/08 has been recovered and is now in possession of the licensee. The gauge and its radioactive materials were out of the licensee control for less than 24 hours. During a portion of the time the gauge was missing it was in the possession of a local fire department. The CDPHE RMU does not expect any impact to any members of the public as a result of the temporarily lost gauge due to the short duration of possession. "Upon recovery, the licensee performed a visual inspection and radiological survey and has confirmed that the radioactive materials are present and intact. The gauge has been transferred to a local licensed gauge service provider where a leak test and through examination will be performed." Notified the R4DO (Campbell), FSME (Suber), and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-11-10
44630 | 0 | GEORGIA DEPARTMENT OF NATURAL RESOU |  |  |  |  | 2008-11-05 10:45 | 2008-11-05 15:20 | 2008-11-05 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE "On 11/5/2008 at approximately 10:45 am, the licensee had a Troxler moisture-density gauge (Model 3430, S/N 33839) on the ground in the "standardize" mode (sources shielded) when it was run over by heavy mechanical equipment. Licensee staff roped off the area around the gauge and maintained surveillance of the gauge until the RSO and consultant arrived. Based on a radiation survey, there was no apparent loss of shielding integrity. Results of leak tests on the sealed sources are pending. Gauge was transported back to the licensee's office for further evaluation and likely return to Troxler." Amount of activity: 8 mCi (Cs-137) and 40 mCi (Am-241) Georgia Report Number: GA-2008-461 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | MAT | [5 empty] | 0 | 2008-11-05
44629 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-11-05 00:57 | 2008-11-05 05:44 | 2008-11-05 | EMERGENCY DIESEL GENERATOR START DUE TO UNEXPECTED ESF SIGNAL "This is an 8-hour notification to report a valid ESF signal to start the 1A Emergency Diesel Generator that occurred on 11/5/08 at 0057. Salem Unit 1 is in Mode 5, with core cooling being provided by 12 RHR pump. The Reactor Coolant System is being maintained at 173 F and 315 PSIG with a pressurizer level of 35 percent. The operating crew was performing a load shed surveillance test for a single component IAW test plan. The test plan used the Safeguards Equipment Cabinet (SEC) test pushbuttons to verify the equipment's response to a load shed signal. When the 1A SEC test pushbutton was actuated in addition to testing the single component it opened the in-feed breaker to the 1A 4KV vital bus and the bus was de-energized and loaded in blackout conditions. All equipment functioned as designed and core cooling was unaffected and remained in-service from 12 RHR pump powered from 1B 4KV bus. Investigation revealed the test plan did not take into account all components operated by the test pushbutton and the test pushbutton operated as designed. The 1A 4KV vital bus was restored to off-site power and the 1A EDG was restored to a standby condition. There were no personnel injured during the event. "The NRC Resident Inspector has been notified." LAC Township was notified by the licensee. Notified R1DO (Caruso). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-11-05
44628 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-11-04 | 2008-11-04 10:42 | 2008-11-04 | AGREEMENT STATE - UNREPORTED FETAL OVEREXPOSURES "During a routine inspection at Rocky Mountain Cancer Centers, Colorado License, two fetal overexposures were identified that had not been reported to the Department. "The first case occurred on 8/23/05, and involved a PET/CT scan where the patient was injected with 16.3 mCi of FDG (F-18). After the procedure, the patient discovered she was pregnant. The fetal exposure was estimated to be 1.5 rem. The licensee determined the risk of congenital abnormalities to be negligible. "The second case occurred on 11/28/06 and also involved a PET/CT scan where the patient was injected with 11.9 mCi of FDG (F-18). After the procedure, the patient discovered she was pregnant. The fetal exposure was estimated to be 1.02 rem. The licensee determined the risk of congenital abnormalities to be negligible. "No other details are available at this time. "Additional information will be reported through NMED as it becomes available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-11-10
44627 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-11-03 23:22 | 2008-11-04 02:58 | 2008-11-05 | MANUAL REACTOR TRIP DUE TO FEEDWATER REG VALVE FAILURE "On 11/3/08 at 2322, Unit 2 was manually tripped due to the failure of Loop 4 Feed Water Reg. Valve (FRV Controller). Manual control was attempted to control level in Loop 4 Steam Generator (S/G); however, Loop 4 FRV failed to respond. A manual Reactor Trip was initiated as a result of this failure. In addition, Auxiliary Feedwater (AFW) initiated as required due to a Feedwater isolation signal "The Loop 4 FRV did isolate from the Feedwater isolation signal. "The Plant is being maintained in Mode 3 at NOT/NOP, 547 F and 2235 psig, with AFW supplying the S/G's and Steam Dumps removing decay heat. "Additionally, Unit 2 has an indication of a primary leak inside lower containment. The leak rate is calculated to be approximately 2.0 gallons per minute. Based on current indications, the leak is suspected to be from a Pressurizer level transmitter "No primary system or steam generator safety valves opened due to this trip. An investigation has been initiated to determine the cause of the Loop 4 Feed Water Reg. Valve (FRV Controller) failure and the source of the approximately 2.0 gallons per minute primary leak. A recovery plan will be developed." Pressurizer (PRZ) level is stable. All safety related systems are available and OPERABLE for safe plant shutdown. There is no impact on Unit 1. The loop 2 S/G blowdown sample line valve did not go closed as expected on the Feedwater isolation signal. The licensee is taking action to isolate it. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LARRY PRUETT TO JOE O'HARA AT 0001 ON 11/5/08 * * * "The Sequoyah Nuclear Plant Unit - 2 reactor coolant system unidentified leakage was terminated on Nov. 4, 2008 @ 2205 hours when a manual valve was closed isolating the reactor coolant system from the leak location." The licensee closed the root valve to the PZR pressure channel 2-VLV-68-446A. The licensee will notify the NRC Resident Inspector. Notified R2DO(Desai) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-11-04
44626 | -1 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-11-03 06:52 | 2008-11-03 14:43 | 2008-11-18 | RECIRC LOOP TEMPERATURE ELEMENT FAILED "On 11/3/08 at 0652 Shutdown Cooling (SDC) was lost on Dresden Unit 3 when the Recirc Loop Temperature Element (3-0260-13B) failed upscale. Unit 3 was in the process of initial cooldown for entry into a refueling outage. Actual Recirc loop temperature was about 217 degrees F based on alternate indications. The temperature element (3-0260-13B) remained upscale for several minutes before returning to its previous value. The failed element was jumpered out and SDC was restarted. This event is reportable under 10CFR 50.72(b)(3)(v)(B)." The licensee notified NRC Resident Inspector. RETRACTION ON 11/18/2008 AT 1214 FROM RANDY WROBLEWSKI TO MARK ABRAMOVITZ * * * "On November 3, 2008 shutdown cooling was lost on Dresden Unit 3 when the Reactor Recirculation System Loop Temperature Element (3-0260-13B) failed upscale. Plant operators immediately recognized the condition, and implemented an existing operations procedure to re-establish shutdown cooling flow and ensure that the Shutdown Cooling System continued to fulfill the safety function of residual heat removal. The Shutdown Cooling System is a manually initiated, non-safety related system that is not credited for mitigation of any event or accident in Dresden's safety analyses. The implementation of an existing procedure to restore shutdown cooling system flow in a short period of time (i.e., less than 10 minutes in this case), by the Main Control Room operators trained on the procedure, provides reasonable assurance that the system continued to fulfill its safety function. Therefore, Exelon Generation Company, LLC has determined that this event is not reportable under 10CFR 50.72(b)(3)(v)(B) and is retracting ENS Report 44626." The licensee notified the NRC Resident Inspector. Notified the R3DO (O'Brien). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-11-03
44625 | 0 | MISSISSIPPI STATE DEPARTMENT OF HEA |  |  |  |  | 2008-10-21 | 2008-11-03 13:10 | 2009-01-21 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS "On October 21, 2008, Mississippi State Department of Health was notified by Rich Dailey, RSO for Wal-Mart that two (2) exit signs, each containing 11.5 Ci of H-3, were missing from the Wal-Mart store in Hernando, Mississippi. On October 27, 2008, DRH informed the RSO for Wal-Mart that the exit signs were exempt from state regulations but to send in a written notification report. The following devices were reported missing from Wal-Mart: "1. Exit sign form store (#05419) located at 2600 McIngvale Road, Hernando, Mississippi 38632, Serial Number - Unknown, Manufacturer - Isolite, activity - 11.5 Ci of tritium at time of manufacture. "2. Exit sign form store (#05419) located at 2600 McIngvale Road, Hernando, Mississippi 38632, Serial Number - Unknown, Manufacturer - Isolite, activity - 11.5 Ci of tritium at time of manufacture." * * * UPDATE FROM JAYSON MOAK TO JOE O'HARA VIA E-MAIL ON 1/21/09 AT 1534 * * * "The State of Mississippi was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 307 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the State of Mississippi. The Wal-Mart representative informed the State Office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The State of Mississippi was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content where known. " Notified R4DO(Farnholtz), FSME(Burgess), and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | MAT | [5 empty] | 0 | 2008-11-03
44624 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-11-03 02:07 | 2008-11-03 04:35 | 2008-12-31 | MANUALLY OPENED REACTOR TRIP CIRCUIT BREAKERS TO INSERT CONTROL BANK "B" "Manually opened reactor trip breakers in Mode 5 to insert control bank 'B' due to blown fuse in rod control cabinet." Licensee was moving control rod bank "B" following I & C work, and the control rod bank failed to move as expected. All other control rod banks were inserted into the core at the time of the event. EDG's and offsite power sources are OPERABLE, and there is no increase in plant risk. The licensee will inform the NRC Resident Inspector. * * * RETRACTION ON 12/31/08 AT 1326 FROM RICK ABBOTT TO PETE SNYDER * * * "Regarding the NRC Event Number 44624 conveyed November 3, 2008, McGuire Nuclear Station has determined that manually opening the reactor trip breakers was not reportable and hereby retracts this notification. Upon further consideration it was determined that manually opening the reactor trip breakers was a conservative decision to fully insert control rods based on the failure mechanism causing a single rod to drop to the fully inserted position. Manual actuation of the reactor trip breakers was not required by abnormal procedures and was performed only after consultation between operations, engineering and senior station management agreed that this was the preferred option. Therefore, the decision to manually open the reactor trip breakers is considered to be a preplanned actuation of the reactor protection system and is not reportable." The licensee informed the NRC Resident Inspector. Notified R2DO (M. Lesser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-11-03
44623 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-11-02 15:50 | 2008-11-02 20:33 | 2008-11-02 | HPCI SYSTEM DECLARED INOPERABLE DUE TO CONTROLLER FAILURE "The Unit 1 MCR [Main Control Room] HPCI [High Pressure Coolant Injection] flow indicator was observed oscillating just above zero gpm with periodic spikes to approximately 50% of scale (3000 gpm) with a concurrent drop in flow controller output signal while in standby. There were no activities in progress on or near the HPCI system when the oscillation and instrument spikes occurred. Walkdown of the instrument rack and HPCI room equipment found no abnormalities. The HPCI system was declared inoperable at 1550 hours 11/2/2008 (14 day Shutdown LCO). Troubleshooting is in progress to determine the cause of the flow oscillations. "The HPCI system is considered available as there are no indications of controller failure that would impact operation in manual flow control mode. "Unit 1 RCIC, and all other ECCS systems remain OPERABLE." The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-11-02
44622 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2008-11-02 08:30 | 2008-11-02 08:16 | 2008-11-02 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT OF SERVICE FOR PLANNED MAINTENANCE "The Perry Nuclear Power Plant will be taking the Plant Computer out of service for scheduled maintenance which will take ERDS out of service. From 0830 hours EST, on November 2, 2008, for approximately 6 hours, personnel will be resetting computer time from EDT to EST and [will] troubleshoot the Plant Computer. During this planned maintenance, the Safety Parameter Display System (SPDS) and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) [will] be unavailable. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Plant Branch Exchange, the Off Premise Exchange, and various redundant infra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. A follow-up notification will be made when the activities are completed and the equipment is restored. The [NRC] Resident Inspector has been notified." * * * UPDATE FROM JIM CASE TO JOHN KNOKE AT 1530 EST ON 11/02/08 * * * The Plant Computer was put back in operation at 1525 EST. Notified R3DO (Kozak) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-11-02
44621 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-11-01 08:37 | 2008-11-01 14:36 | 2008-11-01 | PROCESS GAS LEAK DETECTION SYSTEM NOT FUNCTIONING CORRECTLY "At 0837 CDT, on 11-01-08 the Plant Shift Superintendent (PSS) was notified that the Process Gas Leak Detection (PGLD) system for C-333 Unit 5 Cell 3 was not functioning as required. An operator was preparing to test fire the system as required by TSR SR 2.4.4.1-1 when it was discovered that the Ready light was not illuminated. This PGLD system contains detectors that cover C-333 Unit 5 Cell 3 and Section 1 and 2 of the cell bypass piping. At the time of this failure, Unit 5 Cell 3 and some areas of Sections 1 and 2 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell and in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 5 Cell 3 PGLD system inoperable, none of the required cell heads and only 2 of the required 3 heads in Sections 1 and 2 of the cell bypass were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.B.1 and 2.4.4.1.C.1 were entered and a continuous smoke watch was put in place within one hour. Engineering has determined that the system would not have been able to perform its intended safely function with the Ready light not illuminated. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event." PGDP Assessment and Tracking Report No. ATR.08-3142; PGDP Event Report No. PAD-2008.034; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-11-01
44620 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-10-02 | 2008-10-31 17:31 | 2008-10-31 | AGREEMENT STATE REPORT INVOLVING A STUCK RADIOGRAPHY SOURCE The following information was received from the State of California via email: "On 10/30/08 the Vallero Refinery, Benicia, CA, informed the RHB of an incident that happened on 10/02/08 during radiography operations performed by T.C. Inspections at their refinery. On the night shift of October 2, 2008, a radiographer, two assistants, and a technician were performing radiography on Tank # 1795. After cranking the source out, the magnetic stand holding the collimator fell and was suspended by a rope from the top. This left the camera, crank, and collimator dangling from the tank. The collimator was about 40 feet up, the crank was hanging down and accessible from the lowered man-lift, so the radiographer tried to crank the source in, but realized that the source was stuck due to a kink in the guide tube. The radiographer approached the collimator using a man-lift and was able to straighten the guide tube and crank the source into the shielded position. The radiographer was very close to the source for approximately 1 minute. It has taken about 5 minutes from the ground to get the source back into the shielded position. The radiographer's pocket dosimeter was off scale. His dosimeter was processed and the whole body dose indicated 843 Mr." California 5010 Number (Date Notified): 103008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-11-05
44619 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2008-10-30 10:45 | 2008-10-31 16:52 | 2008-11-12 | AGREEMENT STATE REPORT - ACCIDENTIAL EXPOSURE TO I-131 "A veterinarian was exposed to Iodine-131 after administering a dose to a cat. The incident occurred on Thursday, October 30, at about 10:45 AM. The (19 millicuries of I-131) dose had been given to the cat, and the user accidentally poked his left index finger with the syringe which contained a residue of I-131. The user's protective glove was penetrated by the needle, but the needle did not appear to have penetrated the skin. The user contacted the RSO a few minutes after the incident. Efforts were made to remove or displace the radioactive Iodine with partial success, reducing the beta measurements about 50%. The licensee estimated that about 20 nanocuries of I-131 were remaining after efforts to decontaminate. Finger swabs show a very small amount 0.5 nanocuries or less) of removable contamination. The contamination is concentrated on an area less than 1 mm square on the user's left index finger near the tip. The user's fingertip is being kept bandaged to prevent spread of contamination. "The licensee contacted DEQ promptly after the initial response. The exposed individual was taken to the University Medical Center where the physician is giving treatment based on NCRP 65. Nonradioactive iodine is being administered in an attempt to block absorption by the thyroid. "Since the skin did not appear to be penetrated, the licensee believed that there would be no internal dose, but the exposed individual was directed to collect his urine for analysis. This report to NRC was held up in anticipation of the results. Analysis of the exposed individual's urine (about 2 liters collected overnight) shows a distinct I-131 peak that the licensee preliminarily estimated at about 90 picocuries/liter. A longer count with more precision is being made. The exposed individual will continue to collect all urine for analysis for at least five days. "The situation has been complicated by the death of an immediate relative of the RSO. A Certified Health Physicist who is on the University Radiation Safety Committee is now acting for the RSO." * * * UPDATE PROVIDED BY MIKE BRODERICK TO JASON KOZAL ON 11/12/08 AT 1110 EST * * * The following was provided by the licensee via e-mail: "The licensee has conducted an extensive follow-up investigation, including collection an analysis of urine for five days, and bioassay of the individual's thyroid. The licensee calculated a thyroid dose of 2.1 mrem for the incident, not enough to have measurable health effects. It is not clear whether the Iodine was absorbed through an undetected skin puncture or through direct skin absorption. The licensee is working with DEQ to analyze their process to minimize the chances of a similar future incident." Notified R4DO (Whitten), and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2008-11-06
44618 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-10-31 12:52 | 2008-10-31 13:45 | 2008-10-31 | MANUAL REACTOR TRIP DUE TO ROD CONTROL MALFUNCTION "Initial conditions: Low Power Physics Testing after outage. Performing Dynamic Rod Worth measurements. Single dropped rod (K-2) on Control Bank B occurred after movement disagreement between rod groups. Entered AP-14, 'Rod Control Malfunction'. Performed a manual reactor trip and manual start of Auxiliary Feedwater as directed by Normal Operating Procedures for unit shutdown. Feedwater isolation occurred due to Low T-Ave concurrent with reactor trip." All control rods were fully inserted. Licensee has notified NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-10-31
44617 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2008-10-13 | 2008-10-31 12:41 | 2008-10-31 | AGREEMENT STATE REPORT - 3 MISSING EXIT SIGNS "The General Licensee (Wal-Mart, Inc.) notified the Agency [state] on October 13, that three of their facilities were missing one exit sign each. Sign SN# 339982 manufactured by SRB contained 20 Curies of tritium when manufactured and was located at the Goodyear facility, (08-012). Sign SN# 277684 by SRB contained 20 curies of tritium when manufactured and was located at the Nogales facility, (08-013). Also the inventory date for these two signs was not provided. The sign at the Tucson facility did not have any information on the manufacturer, the amount of tritium or the date when last inventoried, (08-014). The general licensee does not have any information regarding as to when these signs went missing. The general licensee does not believe they were damaged in their facilities. The Agency continues to look for the source." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2008-11-05
44616 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-10-30 09:30 | 2008-10-30 16:40 | 2008-10-30 | NON-FUNCTIONAL STEAM EXCLUSION BARRIER "On 10/30/08 at 0930 an RP Technician transiting though a steam exclusion door found a kickplate degraded. The kickplate is held on by two screws and one screw was missing. When the door was opened, the kickplate rotated and became lodged in the staircase grating. This prevented the door from closing until the technician physically lifted the plate out of the way to close the door. The door was open for less than a minute. This kickplate is not part of the door seal itself so when the door is closed it is functional. The kick plate was taped up as a temporary fix and access was restricted through the door until permanent repairs were complete. Permanent repairs were completed on the door at 1116 on 10/30/08. While the door was open and could not close automatically, the barrier was non-functional. In accordance with TRM 3.0.9 Section A.1 all equipment supported by that steam exclusion barrier was immediately declared inoperable. This zone includes both trains of ECCS and support equipment (i.e., SI, RHR, ICS, CCW, etc ). TS 3.0.c was entered and exited during the time the door was open with both trains of ECCS inoperable. "Therefore, this is reportable under 10 CFR 50.72 (b)(3)(v), 'Any event or condition that at the time of discovery could have prevented the fulfillment of a safety function', and under 10 CFR 50.72(b)(3)(ii)(B) 'any event or condition that results in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety'." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2008-10-30
44615 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-10-30 14:17 | 2008-10-30 16:23 | 2008-10-30 | REACTOR MANUALLY TRIPPED DUE TO FAILURE IN ROD CONTROL SYSTEM "During the performance of 030 (post refueling start-up testing), control rods were being inserted for dynamic rod worth measurement. An urgent failure occurred in the rod control system which caused Group 1 rods in Control Bank A to stop inserting while Group 2 rods continued to insert. "Reactor was manually tripped following the receipt of rod control alarms due to rod misalignment within Control Bank A. All rods inserted as expected." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-10-30
44614 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-10-30 | 2008-10-30 14:13 | 2009-01-29 | AGREEMENT STATE REPORT - DAMAGED EXIT SIGNS. "On 10/30/08 the Agency [state] received a written report of damaged Tritium exit signs from Richard Dailey, RSO of Wal-Mart Stores. The 2 exit signs, manufactured by SRB Lite, are identified as S/N's 249470 and 249477 each containing 20 curies. "During an inventory on 9/29/08 at the Northampton store, Wal-Mart's contractor discovered 2 damaged signs that failed the glow test. Additionally, one of the signs, S/N 249477, had a cracked face plate. Interviews with the store manager and associates indicated the signs were probably damaged during a recent remodel project. Wal-Mart hired Dade Moeller to assess the radiological impact of the damaged signs. A wipe survey was performed and the survey indicated no high levels of contamination. The signs were packaged per the protocols of Isolite, a specific licensee authorized to receive Tritium exit signs for disposal and transferred to Isolite. Wal-Mart will send the Agency a report of the transfers." * * * UPDATE FROM JOHN SUMARES TO JOE O'HARA VIA EMAIL AT 0838 ON 1/29/09 * * * "On January 28, 2009, the [Commonwealth of Massachusetts] has received a report of these transfers, completed this NMED report, and considers this event to be closed." MA NMED# 080732 Notified R1DO( W.Schmidt) and FSME (M. Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-11-04
44613 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2008-10-30 00:20 | 2008-10-30 05:10 | 2008-10-30 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT OF SERVICE "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii) as a condition that results in a major loss of emergency offsite communications capability. On October 30, 2008, at approximately 0020 hours EDT, 120 VAC non-essential electrical power was lost to the plant computer due to high temperature in the computer room (approximately 80 degrees F). This resulted in the Integrated Computer System (ICS), the Safety Parameter Display System (SPDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) being out of service. "At 0028 hours, back-up computer room ventilation equipment was placed in service, and at 0040 hours, the electrical system high temperature shutdown was reset with the computer room temperature at 77 degrees F. At 0217 hours, the computer room high temperature alarm was reset with the room at 72 degrees F. The 120 VAC electrical power was restored to the plant computer room at approximately 0245 hours. The ICS, SPDS, and CADAP equipment functions are in process of restoration. Restoration is expected during dayshift hrs. on 10/30/08. A follow up to this notification will be made when ERDS is restored. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DAVE O'DONNELL TO JOE O'HARA AT 1406 EDT ON 10/30/08 * * * The ERDS system has been tested and restored to service. The NRC Resident Inspector has been notified. Notified R3DO(Kozak). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-30
44612 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2008-10-29 19:15 | 2008-10-29 22:37 | 2008-10-29 | OFFSITE NOTIFICATION DUE TO A SPILL OF A HAZARDOUS SUBSTANCE "The State of New Jersey was notified of a spill to the ground of a hazardous substance. A tube leak in a new radwaste heat exchanger caused an expansion tank to overflow resulting in less than one (1) gallon of water containing corrosion inhibiting chemicals to be discharged to the ground. The heat exchanger and the new radwaste service water system were removed from service, stopping the leak. Initial samples did not detect radioactivity in the water. Cleanup of the spill is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-10-29
44611 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-10-29 20:50 | 2008-10-29 21:31 | 2008-10-29 | UNUSUAL EVENT - FIRE IN HP CALIBRATION LAB At 2050 EDT a fire was discovered on the 2nd floor of an outbuilding inside a Health Physics calibration lab inside the protected area. The fire was reported as starting in a "drawer or cabinet" in the room. Plymouth Fire Department was notified and responded along with the on-site fire brigade. An Unusual Event was declared at 2058 EDT. The fire was extinguished at 2109 EDT. A re-flash watch was established. Electrical breakers to the room were opened. Health Physics personnel determined that no sources had been impacted by the fire and that no radiological concerns existed. The licensee notified the Commonwealth of Massachusetts and local authorities. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOSEPH BRACKEN TO DONALD NORWOOD AT 2229 EDT 10/29/2008 * * * The licensee has terminated the Unusual Event as of 2202 EDT on 10/29/2008. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-10-29
44610 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-10-29 15:00 | 2008-10-29 17:03 | 2008-10-29 | OFFSITE NOTIFICATION DUE TO HYDRAULIC FLUID SPILL "On October 29, 2008 at 1500 EDT, eight ounces of biodegradable hydraulic fluid (product name EnviroLogic 132) was spilled into the water outside the General Service Water (GSW) intake from Lake Erie. Cleanup activities were initiated immediately, and the spill was cleaned up within 20 minutes. All of the fluid was cleaned up. Reports were made to the Michigan Department of Environmental Quality (MDEQ) Pollution Emergency Alert System and the Primary Public Safety Answering Point (9-1-1). Media interest may be expected. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-10-29
44609 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-10-28 09:00 | 2008-10-28 17:09 | 2008-10-30 | CS-137 SOURCE DISCONNECTED FROM LEVEL DETECTOR OPERATING ROD "At 1515 on 10/28/08, the Agency was notified by the licensee of an event involving a Thermo Measure Tech Model 5191 level measurement gauge. The licensee had noted that the gauge was no longer reading properly and sent a maintenance crew to the area to perform repairs. While conducting repairs, an individual from the safety group came by to perform radiation surveys. The survey indicated elevated levels of radiation so the safety representative had the area evacuated and roped off. The licensee contacted the manufacturer who sent technicians to the facility to investigate. They found that radiation levels were in fact elevated and determined that the source had separated from the operating rod. The source is still located in the gauge housing, but is not currently shielded. The source is a 260 milliCurie (calculated based on decay) Cesium (Cs) -137 source. The licensee has started their investigation including time and distance studies with workers who were in the area. The gauge is located in an area of the plant not frequented by workers. The manufacturer is scheduled to remove the gauge from the vessel and send it to their facilities for further inspection on 10/29/08." * * * UPDATE FROM ART TUCKER TO PETE SNYDER ON 10/30/08 AT 0833 EDT * * * The Agreement State of Texas provided the following information via e-mail: "The licensee contacted the [Texas Department of State Health Services (TDSHS)] on October 29, 2008, and informed them that the gauge had been removed from the tank it was mounted on by the manufacturer. The Cs-137 source was found in the gauge housing. The gauge and source were packaged for transportation back to the manufacturer's facility for inspection and repair. The [TDSHS] will be provided the results of the inspection when it is completed." Texas Event Number: I - 8576. Notified R4DO (Spitzberg), FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-10-31
44608 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-10-28 08:49 | 2008-10-28 14:15 | 2008-10-28 | PROCESS GAS LEAK DETECTION SYSTEM INOPERABLE "At 0849 CDST, on 10-28-08 the Plant Shift Superintendent (PSS) was notified that an alarm was received for the C-337 Unit 1 Cell 2 UF6 Release Detection (PGLD) System. Operators responded and found that the READY and MANUAL lights for this system were not illuminated. This PGLD System contains detectors that cover C-337 Unit 1 Cell 2 and Section 1 of the cell bypass piping. At the time of this alarm, Unit 1 Cell 2 and some areas of Sections 1 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell and in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 1 Cell 2 PGLD system inoperable, none of the required cell heads and only 2 of the required 3 heads in Sections 1 of the cell bypass were operable. This PGLD System was declared inoperable. TSR LCO 2.4.4.1.A.1 and 2.4.4.1.C.1 were entered and a continuous smoke watch was put in place within one hour. Engineering has determined that the system would not have been able to perform its intended safety function when this alarm came in. This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "PGDP Event Report No. PAD-2008-033. "The NRC Resident lnspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-10-28
44607 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2008-10-21 | 2008-10-28 11:48 | 2008-10-28 | MISSING TRITIUM EXIT SIGNS The state provided the following via e-mail: "On October 21, 2008 the Oklahoma Department of Environmental Quality was notified of missing GL radioactive material by the environmental services manager for Wal-Mart. The devices are Tritium exit sign (TES) light modules. The last known location for these TES were in Wal-Mart stores identified below. The Corporation had inventoried TES in Wal-Mart stores several weeks earlier. When company employees prepared to remove the TES's for disposal, they were unable to locate three of the TES. Information concerning the TES follows. "Store # 00130, 1000 West Shawnee St., Muskogee, OK 30316, Serial# - Unknown, Manufacturer -Unknown, Curie Content - Unknown "Store # 03295, 6310 South Elm Place, Broken Arrow, OK 74011, Serial# - Unknown, Manufacturer -Unknown, Curie Content - Unknown "Store # 03295, 6310 South Elm Place, Broken Arrow, OK 74011, Serial# - 277852, Manufacturer -Isolite, Curie Content - 20" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2008-10-31
44606 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2008-10-28 09:00 | 2008-10-28 12:28 | 2008-10-31 | MAINTENANCE ON PUBLIC PROMPT NOTIFICATION SYSTEM EMERGENCY SIRENS "The following event description is based on information currently available. If through subsequent reviews of the event, additional information is identified that is pertinent to this event or alters the information being provided at the time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "From October 28, 2008 until October 31, 2008, Palo Verde personnel will be performing maintenance on public prompt notification system sirens. One siren at a time will be removed from service, and will be restored prior to continuing to the next siren. "Siren #42 provides notification to approximately 558 members of the public within 5 miles of Palo Verde. "Siren #44 provides notification to approximately 210 members of the public within 5 miles of Palo Verde. "Siren #25 provides notification to approximately 302 members of the public within 5 miles of Palo Verde. "Siren #23 provides notification to approximately 498 members of the public within 5 miles of Palo Verde. "Siren #22 provides notification to approximately 855 members of the public within 5 miles of Palo Verde. "Siren #18 provides notification to approximately 396 members of the public within 5 miles of Palo Verde "Siren #17 provides notification to approximately 1106 members of the public within 5 miles of Palo Verde. "Siren #36 provides notification to approximately 301 members of the public within 5 miles of Palo Verde. "Siren #15 provides notification to approximately 940 members of the public within 5 to 10 miles of Palo Verde. "Each of these are considered by Palo Verde to be a 'large segment of the population.' "The Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles, during an actual event, with loud speakers to alert persons within the affected area when sirens are inoperable. "There are no events in progress that require siren operation. A follow-up call will be placed when the affected sirens are returned to service. "The NRC Resident Inspector has been notified of the siren maintenance and this ENS call." These sirens are utility owned. * * * UPDATE AT 1335 EDT ON 10/31/08 FROM FARA BURDICK TO S. SANDIN * * * The following information was received as an update to this report: "This is an update of ENS call # 44606. At this time, maintenance on the Palo Verde public prompt notification for sirens identified in ENS #44606, has been completed, siren testing was successful and the sirens are operable and in service at this time. "The NRC Resident Inspector has been notified of the siren maintenance and this ENS call." Notified R4DO (Spitzberg). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-28
44605 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-10-25 23:42 | 2008-10-27 19:21 | 2008-10-27 | VALID SAFETY INJECTION SIGNAL DUE TO MAINTENANCE ERROR "At approximately 2342 on 10/25/2006, while performing maintenance on the solid state protection system in Mode 5 cold shutdown, Unit 2 received an automatic safety injection signal which resulted in all three ESF Diesel Generators starting and a containment ventilation isolation and containment phase A isolation. All safety injection pumps were in pull-to-lock per plant conditions so that the pumps did not start and no water was discharged into the reactor coolant system. As a result, the ESF Diesel Generators started but did not load as designed. The residual heat removal pumps were stripped from the ESF electrical busses due to the actuation. The first residual heat removal pump was restored within 4 minutes upon the loss of residual heat removal cooling and the second pump was restored within 6 minutes. The residual heat removal system heat exchangers were bypassed at the time of the event and the plant was being allowed to heat up. "The cause of the automatic safety injection signal was an inadvertent removal of the block for the low pressurizer pressure safety injection system during the maintenance. Therefore, the signal was a valid signal initiated in response to a parameter satisfying the requirements for initiation of the safety function of the system. "Although the actuation was the result of a valid signal, safety injection was not required in this Cold Shutdown Mode of Operation. "This notification is being made under 10CFR50.72(b)(3)(iv) as an event that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section. "This actuation was initially determined to be due to an invalid signal. Upon further review, it was determined at 1745 on 10/27/08 that the actuation was due of a valid signal." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-10-27
44604 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-10-27 02:39 | 2008-10-27 16:45 | 2008-10-27 | CONCURRENT NOTIFICATION TO NRC OF PCB SPILL "At 1400, on 10/27/2008 CDT, the Plant Shift Superintendent was informed that EPA Region IV and the Kentucky Department of Environmental Protection had been notified of a PCB spill which occurred within the C-333 process building. "This event is reportable as 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials.' "The NRC Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRCÀ08À3077: PGDP Event Report No. PAD-2008-032" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-10-27
44603 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-10-27 12:06 | 2008-10-27 12:53 | 2008-10-27 | ALERT DECLARED DUE TO OXYGEN DEFICIENT ATMOSPHERE IN A VITAL AREA "At 1206 on 27 October 2008 PPL Susquehanna, LLC, declared an Alert (classification OA7) for an oxygen deficient atmosphere for a room in the Unit 2 Reactor Building. The oxygen deficient atmosphere occurred in the Unit 2 RHR Division 2 Pump Room during maintenance activities. Personnel evacuated this room. Activation of the Emergency plan is reportable under 10CFR50.72(a)(3)." The licensee made all notifications as required to state and local responders. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM CHARLIE RIGSBY TO JOE O'HARA AT 1741 ON 10/27/08 * * * The ALERT was terminated at 1726 EDT based upon re-establishment of a suitable atmosphere. The licensee notified the State, local agencies, and the NRC Resident Inspector. R1DO(Cobey), NRR EO(Giitter), and IRD(McDermott) notified. Notifications to DHS, FEMA, DOE, USDA, HHS were also made by the NRC Operations Center. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-10-27
44602 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2008-10-27 03:03 | 2008-10-27 04:48 | 2008-10-28 | UNUSUAL EVENT DECLARED DUE TO EXPLOSION IN THE PROTECTED AREA "Quad Cities Station has declared an Unusual Event under EAL HU6 due to an explosion in the protected area. The radwaste floor drain surge tank building has physical damage after reports of an explosion in the area. The building is located outside the vital area West of the Turbine building. There are no reports of fire in the area. First responders are on the scene and assessing the situation. This event is being reported under 10 CFR 50.72.(a)." The licensee stated that there were no injuries or release of radioactive material and no impact on the reactors. The damage was to block structure of the radwaste floor drain surge tank building but the radwaste tank itself was not impacted. The cause of the explosion is still unknown but appears to be related to a buildup of some kind of hydrocarbon gas. No offsite assistance from the fire department has been requested by the licensee. The explosion was reported to occur at 0242 CDT. The States of Illinois and Iowa have been notified. The licensee has also notified local authorities and will notify the NRC Resident Inspector. * * * UPDATE FROM CURT STEFFES TO DONALD NORWOOD AT 1655 EDT 10/28/08 * * * "Unusual Event - Termination "This is an update to EN #44602. "On October 27, 2008, at 0303 hours CDT, Quad Cities declared an Unusual Event under EAL HU6 due to an explosion in the protected area. The radwaste floor drain surge tank building incurred physical damage. A walkdown of the area confirmed that the explosion had no impact on any safety related structures or components. There were no injuries. The combustible atmosphere in the surge tank building has been attributed to the accumulation of methane gas, which originated in the surge tank. Actions have been initiated to purge and monitor the surge tank atmosphere to ensure conditions will not deteriorate. "Conditions no longer meet an emergency action level, the event was terminated at 1530 CDT hours on October 28, 2008. "A press release will be issued on the termination of the Unusual Event." The licensee has notified the NRC Resident Inspector, Illinois EMA, Illinois REAC, Iowa EMD, Scott County - Iowa, and Clinton County - Iowa. Notified R3RA (Caldwell), R3DO (Kozak), NRR EO (Skeen), IRD (Gott). DHS (Hill), and FEMA (Blankenship). | 97 | 97 | 0 | 98 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-10-27
44601 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-10-26 11:25 | 2008-10-26 15:40 | 2008-10-26 | AUTOMATIC REACTOR SCRAM AND ISOLATION DUE TO TURBINE TRIP "Actuation of RPS with reactor critical. Reactor Scram occurred at 11:25 am, 10/26/08 from approximately 50% CTP (core thermal power). "A turbine/generator trip and automatic RPS reactor scram on TCV [turbine control valve] fast closure occurred. Exact cause of turbine/generator trip is not known at this time. All withdrawn control rods fully inserted to position 00. "Reactor Water Level 3 (11.4") was reached which is an RPS Scram Setpoint and also a setpoint for Group 2 (RHR to Radwaste) and Group 3 (Shutdown Cooling Isolation). No valves isolated in these systems due to their being in their normally closed position. Lowest reactor water level reached was -3" Wide Range. "Appropriate off normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached, and no ECCS or DG initiation occurred. All safety systems performed as expected. "MSIVs remained open and no SRV's lifted. Main Condenser and pressure control system remained in service. Currently, reactor water level is being maintained by the condensate system in normal level band and reactor pressure is being controlled to limit cooldown." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-10-26
44600 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2008-10-24 | 2008-10-24 15:34 | 2008-10-29 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following information was received via facsimile. "The SC [South Carolina] Department of Health and Environmental Control was notified on Friday, October 24, 2008 at 12:05 p.m. that a Humboldt Model 5001 portable moisture density gauge had been lost, along with the licensee's company vehicle. [DELETED], Columbia Radiation Safety Officer, and [DELETED], Corporate RSO, notified the Department that a gauge technician had been in possession of the truck and portable gauge on Thursday, October 23. The technician apparently decided to go out for a 'night on the town' with the company vehicle/gauge and became highly intoxicated. As a result of this, per [DELETED] and [DELETED], the technician does not recall where the truck with the gauge was left. The technician called a fellow MACTEC employee this morning who then picked him up at his hotel. The keys to the MACTEC truck were in the possession of the errant technician so it has been assumed that the truck with the gauge secured in the truck bed is parked at a local nightspot. The technician has been questioned but can shed no light on where the truck is at this time. The licensee has called the police department to notify them of the situation. They have also called the city and county to rule out the possibility that the truck was towed overnight. No report of this vehicle being towed was on file. The licensee currently has four company trucks out looking for the lost vehicle and gauge. "As more information is available, this notice will be updated. The licensee was advised that a written report detailing this event must be submitted to the Department within 30 days. The event is open and pending further investigation by the licensee and the Department. Updates will be made through the national NMED system." Humboldt 5001 moisture density gauges nominally contain 10 mCi Cs-137 and 40 mCi Am:Be. * * * UPDATE PROVEDED BY MELINDA BRADSHAW TO VINCE KLCO ON 10/29/08 AT 1152 * * * The following was provided by the state via telephone: MACTEC located both the lost portable moisture density gauge and the truck. Based on inspection, it was determined that the gauge is undamaged. The licensee will submit a report. Notified R1DO (Cobey), FSME (Burgess) and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2008-10-29
44599 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-10-22 | 2008-10-24 14:46 | 2008-10-28 | AGREEMENT STATE REPORT - EXCESS DOSE TO THE FETUS OF A PREGNANT PATIENT The licensee notified the State of Georgia on 10/23/2008 regarding a dose of greater than 500 mrem administered to the fetus of a pregnant patient. The apparent unintended dose was identified by the licensee on 10/22/08. The State of Georgia is attempting to contact the licensee for additional follow-up details and a report related to this event. * * * UPDATE RECEIVED VIA FAX FROM IRENE BENNETT TO JOE O'HARA AT 1531 ON 10/27/08 * * * The following information was provided to the State of Georgia by the licensee: "The patient was administered the radiopharmaceutical on October 13, 2008. Our facility was informed of the patients pregnancy on October 22, 2008. The RSO and our consulting medical physicists were notified. A dose calculation was performed and it was determined that the embryo/fetus received an effective dose equivalent in excess of 500 millirem. "The patient was scheduled for a Nuclear Cardiology treadmill stress test on October 13, 2008. The patient was asked by the staff if she was pregnant per facility policy. The patient indicated that she was not pregnant. This was documented by our staff. The patient was administered 10 mCi Tc-99m Myoview for resting procedure and 30 mCi Tc-99m Myoview for stress. The patient subsequently determined she was pregnant and notified us as described above. "The patient withheld information regarding pregnancy and fertility medication when asked prior to the study. The dose to the conceptus is estimated to be approximately 1.12 rad with an uncertainty factor of 50 percent. Determination of dose is limited by patient habitus and metabolic parameters. "The prescribing physician was notified October 23, 2008 at 9:34 AM and stated that she will notify the primary physician and patient." Notified R1DO(Cobey) and FSME(Mauer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-10-29
44598 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2008-10-23 21:26 | 2008-10-24 00:48 | 2008-10-24 | MANUAL REACTOR SCRAM DUE TO LOSS OF THE ELECTRONIC PRESSURE REGULATOR "Control Room Operators observed slight [reactor] pressure rise during panel walk down. Investigation of pressure indication led Control room staff to determine that [the] EPR (Electronic Pressure Regulator) was not functioning properly (noise in the output signal). Control Room Staff entered Special Operating Procedure for failed pressure regulator. EPR could not be moved and this was confirmed by operators in the field. Control Room Staff [then] inserted a manual scram. "Immediately after the scram reactor water level reached a low of 36", Emergency Operating Procedures for Level (EOP-2) were entered. HPCI initiated on the turbine trip to control water level. After the turbine tripped, all turbine bypass valves failed open; MSIVs (main steam isolation valve) were manually shut to control pressure. [The] EPR eventually disengaged from control, allowing the operator control of the turbine bypass valves. MSIVs were then reopened. [The] Scram has been reset. [The] turbine driven shaft pump did not initially disengage, pump [was] manually tripped after turbine speed reduced to 1500 rpm. All other systems responded correctly. "[The] plant is not currently in any SOPs or EOPs and is proceeding to cold shutdown using normal operating procedures." All control rods fully inserted as expected. The plant is in a normal shutdown electrical lineup. At the time of the event, containment spray loop 1-12 was out of service for routine surveillance. The plant is currently cooling down and is at 365 psi. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-10-24
44597 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-10-23 18:00 | 2008-10-23 18:25 | 2008-10-24 | INFORMATION ONLY NOTIFICATION REGARDING PLANT SHUTDOWN "This is an information only notification that Beaver Valley Power Station Unit No. 2 has initiated a plant shutdown as of 1800 on 10/23/08, a proactive measure, to complete repairs on the Train 'A' Low Head Safety Injection (LHSI) Pump 2SIS-P21A. On 10/19/08 at 2326, Beaver Valley Power Station Unit No. 2 removed 2SIS-P21A from service for routine preventive maintenance. Technical Specification 3.5.2, Condition A was entered during this maintenance activity with the Required Action A.1 to restore 2SIS-P21A to operable status within 72 hours (2326 on 10/22/08). On 10/20/08, during this maintenance; the pump shaft was unable to be rotated by hand after approximately 3/4 revolution. The pump was then disassembled and the apparent cause was determined to be that the pump rotating assembly was not centralized in the casing bore resulting in minimal clearance between the pump wear rings. On 10/22/08, First Energy Nuclear Operating Company (FENOC) requested enforcement discretion from the NRC to permit an additional 36 hours of time to complete repairs on the pump. The NRC verbally granted FENOC's request for enforcement discretion on 10/22/08 at 1105. The enforcement discretion period will expire on 10/24/08 at 1126. Since unexpected difficulties have delayed the reassembly of the pump, FENOC management decided to proactively shutdown Beaver Valley Power Station Unit No.2 beginning at 1800 on 10/23/08. While pump reassembly and testing to restore operability may still be completed by the end of the enforcement discretion period, FENOC management determined that it was more prudent to shutdown the unit at this time so that the Operations crews are not placed under undue time pressure to reach Mode 3 conditions. "The licensee notified the NRC Resident Inspector." * * * UPDATE PROVIDED BY DANIEL SCHWER TO JASON KOZAL ON 10/24/08 AT 0922 * * * "This 4-hour notification is to report that Beaver Valley Power Station Unit No. 2 has initiated a manual reactor shutdown at 0600 on 10/24/08 in accordance with Technical Specification 3.5.2, 'ECCS - Operating'. On 10/19/08 at 2326 Beaver Valley Power Station Unit No. 2 removed 2SIS-P21A (Train 'A' Low Head Safety Injection [LHSI] Pump) from service for routine preventive maintenance. Technical Specification 3.5.2 was not met during this maintenance activity for two operable trains of Emergency Core Cooing System and Condition A was entered with the Required Action A.1 to restore 2SIS-P21A to operable status within 72 hours (2326 on 10/22/08). Problems were unexpectedly encountered during this maintenance; the pump shaft was unable to be rotated by hand after approximately 3/4 revolution. The pump was disassembled and the apparent cause was determined to be that the pump rotating assembly was not centralized in the casing bore resulting in minimal clearance between the pump wear rings. On 10/22/08 FirstEnergy Nuclear Operating Company requested enforcement discretion from the NRC to permit an additional 36 hours of time to complete reassembly of the pump. The NRC verbally granted FENOC's request for enforcement discretion on 10/22/08 at 1105. The enforcement discretion period would have expired on 10/24/08 at 1126. Since unexpected difficulties have delayed the reassembly of the pump, FENOC management decided to proactively shutdown Beaver Valley Power Station Unit No.2 beginning at 1800 on 10/23/08 (reference Information Only EN#44597). Beaver Valley Power Station Unit No. 2 entered Mode 3 at 0519 on 10/24/08 as part of the planned controlled shutdown. On 10/24/08 at 0600, Technical Specification 3.5.2, Condition B was entered based on a determination that the projected work completion time for restoring 2SIS-P21A to operable status would not meet the conditions of the enforcement discretion. Technical Specification 3.5.2, Required Action B.1 was met since the plant was in Mode 3, the plant is continuing the cooldown to be in Mode 4 within 12 hours per Required Action B.2. This event is being reported as a Technical Specification required shutdown pursuant to 10CFR50.72(b)(2)(i). "No radiological release occurred due to this event. "The licensee notified the NRC Resident Inspector." Notified R1DO (Cahill). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY | PLANT S/D REQD BY TS |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  |  | 50.72(b)(2)(i) |  |  | 0 | 2008-10-23
44596 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2008-10-23 09:00 | 2008-10-23 11:59 | 2008-10-23 | OFFSITE NOTIFICATION DUE TO SUMP DISCHARGE LINE LEAKAGE "This is a report of a situation, related to the protection of the environment, for which a notification to other government agencies is being made, as described in 10 CFR 50.72(b)(2)(xi). "On October 22, 2008, excavation within the Protected Area was ongoing to identify a leak in the Fire Protection System. At approximately 1600 hours, the Turbine and Water Treatment Building sump discharge line was identified as leaking. This three-inch carbon steel pipe routes the sump discharge to the settling basins, where it is eventually discharged via a monitored outfall to the environment. "The cause of the leakage is unknown, but due to the condition of the piping, it is believed to have existed prior to the excavation activities. The amount of leakage is therefore conservatively assumed to be more than 100 gallons, but this cannot be quantified at this time. Analysis of a water sample from the sump discharge line leak determined that the water leaking from the pipe contains approximately 37,500 picocuries per liter (pCi/l) tritium. These tritium levels are consistent with tritium levels in the Condensate/Feedwater Systems in the Turbine Building. "Actions are underway to remove the piping from service and re-route the sump pump discharge. Analysis of routine groundwater well samples taken earlier this month is being expedited, and additional well samples are being planned. "The State of Ohio, Lucas County and Ottawa County government agencies were contacted regarding the above information at 0900 on October 23, 2008. The Resident Inspector has also been briefed on the issue." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-10-23
44595 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-10-23 07:20 | 2008-10-23 11:44 | 2008-10-23 | AUTOMATIC REACTOR SCRAM WITH MANUAL RCIC INITIATION "'A' Reactor Feed Pump speed decreased to zero with no trip signal evident in the Control Room for the 'A' Reactor Feed Pump. The reactor scrammed due to loss of feedwater flow on a Level 3 (11.4") RPS scram signal as designed. Operators implemented appropriate off normal event procedures to mitigate the transient with all systems responding as designed. Lowest reactor water level observed was -35" wide range. All withdrawn control rods fully inserted to position '00'. The Reactor Core Isolation Cooling System was manually initiated and was used to restore water level to within the normal band. No ECCS initiations were received and all systems responded as designed. Additionally, no SRVs lifted as a result of this event. "Level 3 is also a setpoint for Group 2 (RHR to Radwaste) and Group 3 (Shutdown Cooling Isolation) automatic isolation. No valves isolated in these systems due to them being in their normally CLOSED position prior to the event. Currently, reactor water level is being maintained by the condensate system in normal level band and reactor pressure is being controlled to limit cool down." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-10-23
44594 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-10-22 18:50 | 2008-10-22 21:42 | 2008-10-22 | WORKER TRANSPORTED TO LOCAL HOSPITAL "A potentially contaminated individual was transported to the Salem County Memorial Hospital by the on-site Fire Protection personnel. The individual had been working in Unit One containment and collapsed. The individual was surveyed en-route to the hospital and was determined to be-not contaminated. The individual remains at the hospital and is undergoing testing and evaluation. Salem Unit One remains defueled with spent fuel cooling in-service." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2008-10-22
44593 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-10-22 12:17 | 2008-10-22 17:42 | 2008-12-12 | RCIC DECLARED INOPERABLE DUE TO AGING CONCERN OF SEVERAL FLOW CONTROLLER COMPONENTS "On October 22, 2008, at 1217 hours, with the reactor at 100% core thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNPS) conservatively declared the Reactor Core Isolation Cooling System (RCIC) inoperable in response to a concern regarding the reliability of aged capacitors that are installed in the RCIC flow controller. "As background, the RCIC flow controller was calibrated and successfully tested on October 7th, 2008 as part of normal surveillance activities, however several of the capacitors installed in the controller were noted to be between 21 to 30 years of age. Industry recommended replacement interval for the capacitors is typically between 7 to 10 years of age. PNPS engineering review in conjunction with Entergy fleet consultation concluded today (10/22) that there was no definitive technical bases to provide a reasonable expectation that the RCIC flow controller function can be assured throughout it's mission time due to the capacitor aging concern. Therefore, RCIC was declared inoperable and a 14 day limiting condition for operability action statement was entered in accordance with TS 3.5.D.1. A replacement controller is being prepared for installation, with post maintenance testing projected to be completed by 2100 hours this evening. Ultimately the suspect controller will be the subject of further evaluation and this notification will be updated as appropriate. "This notification has no impact on the health and safety of the public. "The NRC Senior Resident Inspector is onsite and has been notified. "This is an 8 hour notification made in accordance with 50.72(b)(3)(v)(D)." * * * RETRACTION AT 1435 EST ON 12/12/2008 FROM JOHN WHALEY TO DONALD NORWOOD * * * "Basis for Retraction: Event Notification 44593 was conservatively made to ensure that the eight-hour non-emergency reporting requirements of 10 CFR 50.72 were satisfied pending the evaluation of RCIC System operability. "On 10/22/08, RCIC flow controller FIC-1340-1 was declared inoperable due to engineering uncertainty for controller operability. The controller's electrolytic capacitors appeared to be aged beyond the expected useful life, and the resultant degrading power supply voltage indicated that the controller may not operate for the required FSAR mission time of eight hours. "The controller was replaced on 10/23/08 with a refurbished controller and subsequent post-maintenance RCIC system flow testing demonstrated RCIC system operability. "The controller that was removed from service was evaluated. Controller bench testing was performed on 11/6 and 11/7, 2008. This testing demonstrated that the controller could provide a full demand output signal for a minimum of 15 continuous hours. During this testing, it was also determined that the power supply output voltage was not degrading. "Based on this post-service controller testing, and the successful in-service RCIC flow controller calibration and system performance test conducted on 10/07/08, the controller was operable when installed. The RCIC system was capable of performing its intended safety functions and would have started and supplied design basis flow to the reactor vessel under design basis conditions. Thus there would have [been] no impact on nuclear safety. Therefore, this event was not reportable pursuant to 10CFR50.72(b)(3)(v)(D). "Event Number 44593, made on 10/22/2008, is being retracted." The licensee notified the NRC Resident Inspector. Notified R1DO (Bellamy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-10-22
44592 | 0 | SCIENTECH |  |  |  |  | 2008-10-15 | 2008-10-22 14:50 | 2008-10-22 | POWER SUPPLIES MANUFACTURED WITH UNAUTHORIZED CAPACITOR DELIVERED TO H.B. ROBINSON "On October 15. 2008, Ensign Power Systems. Inc. of Loveland, Colorado informed Scientech of a defect. An internal audit had revealed that some Model 9061-01 power supplies provided to Scientech for use in their safety related line of NUSI modules had been inadvertently manufactured with an unauthorized part. "The design required the use of two capacitors in the power line filter. When Ensign attempted to purchase the required parts, their supplier made an unauthorized substitution of capacitors. These capacitors are virtually identical, and the packaging was labeled with the correct Ensign Power Systems part number. "Scientech immediately put a HOLD on all shipments of modules with Ensign power supplies until it could be verified that they were built using the correct parts. (Complete 10/15/08) "Scientech located all Ensign power supplies in house and isolated them. (Complete 10/16/08) "Scientech notified H. B. Robinson that some of the twelve modules contain power supplies with unauthorized parts. (Complete 10/16/08) "Scientech is working with H. B. Robinson to replace the eight Ensign power supplies with [authorized] parts. (in progress) "Scientech will return all affected power supplies to Ensign for installation of the approved components. "Scientech will review the revised Ensign receipt inspection procedures to assure that they are robust enough to prevent reoccurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | ID | OTH | PAR | 21.21 |  |  |  | 0 | 2008-10-22
44591 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-10-22 12:40 | 2008-10-22 14:57 | 2008-10-22 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The state faxed the following report "We [state] received a phone call today from the RSO of Acuren Inspections (RML- 997-01). On October 21, 2008, a two-man crew was making radiography shots at a field location near the intersection of County Roads 59 and 70, east of Eaton, CO. "The incident involved an Amersham 660 camera, with an Ir-192 source with an estimated 24 Ci of activity. "While making a shot, the pipe fell and resulted in a kink in the guide tube that prevented the source from being retracted. The crew cranked the source back into the collimator and called the RSO, who responded. Upon arrival, the RSO placed bags of shot over the collimator and used pliers to straighten the guide tube and safely retract the source into the camera. The RSO received a dose of zero mrem. The radiographer had a total dose for the day of 20 mrem, and the assistant had a total dose for the day of 68 mrem. "A written report is being prepared by the licensee and will be forthcoming." Incident Report I08-019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-10-27
44590 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-10-22 12:17 | 2008-10-22 13:35 | 2008-10-22 | CONCURRENT REPORT CONCERNING NRC NEWS RELEASE "In response to media inquiries concerning the NRC's news release involving a notice of violation and proposed civil penalty, Babcock & Wilcox Company responded for BWXT with the attached information to media representatives from Lynchburg News & Advance and the Associated Press out of West Virginia. As requested the NRC news release is also attached. "B&W Response to NRC's Notice of Violation: The incident occurred when an operator responded to a spill of hydrofluoric acid using an incorrect neutralizing chemical. As a result, the operator incurred an injury to his eyes. "As noted in the Nuclear Regulatory Commission's (NRC) Notice of Violation, the actions of the employee, his coworkers and our onsite emergency team after the hydrofluoric acid exposure occurred ensured that the employee was not seriously injured as a result of this incident. This fact is confirmed by the statements of four independent medical opinions; one of these physicians was independently contracted by the NRC. "The company [BWXT] acknowledges that this incident identified weaknesses in our spill response procedures and chemical labeling practices. Corrective actions have been developed to address these weaknesses. The company will submit a written response to the NRC within 30 days." The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-10-22
44589 | 0 | SAINT MARY'S MEDICAL CENTER |  |  |  |  | 2008-10-15 14:00 | 2008-10-22 10:15 | 2008-10-22 | OVEREXPOSURE TO ESOPHAGUS DURING MEDICAL PROCEDURE The patient was being treated for a thyroid condition with a capsule of I-131 (150 milliCi). The procedure involved the patient swallowing the capsule to position it near the thyroid. During the procedure the capsule became lodged in the patient's throat due to an esophageal obstruction. The staff attempted to aid in passing the capsule by having the patient drink soda and eat applesauce. The capsule eventually passed the obstruction after approximately 2 1/2 hours. The estimated dose to the esophagus was 1000 Rads. The calculated dose to the esophagus is 1786 Rads. The patient is following-up with a physician today and at that time will be notified of the overexposure. The potential adverse effects of this dose are esophagitis (inflammation of the lining of the esophagus) and radiation fibrosis. The licensee initially investigated this event shortly after it occurred and at the time contacted NRC R2 (Gabriel). At that time, based on the information that was available (mainly time the device was lodged in the patients esophagus), this event was deemed not reportable. When new information became available to the licensee the event was determined to be reportable. A Medical Event may indicate potential problems in a medical facilities use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | WV | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2008-10-28
44588 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-10-21 20:51 | 2008-10-22 01:44 | 2008-10-22 | UNIT 2 MANUAL REACTOR TRIP DUE TO JELLYFISH INTRUSION "On October 21, 2008, with both units operating at 100% power, Operators manually actuated the Unit 2 reactor protection system (RPS/reactor trip) due to high differential pressure (DP) across the circulating water pumps' intake traveling screens. The high DP resulted from a rapid influx of jellyfish. All systems responded as designed. All control rods fully inserted. Auxiliary feedwater actuated as designed. The grid is stable with power being supplied by 230 Kv startup power. Diesel generator (DG) 2-2 and 2-3 are operable in standby. DG 2-1 is inoperable due to scheduled maintenance. The traveling screens for the safety-related auxiliary saltwater system (ASW) are not degraded and are managing the influx of jellyfish with no significantly elevated DP. Unit 2 is stable in Mode 3 at normal operating temperature and pressure. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'RPS actuation,' and 50.72(b)(3)(iv)(A), 'Specified System Actuation.' "Operators reduced power on Unit 1 in response to the potential loss of normal flow to the condenser due to the jellyfish influx on the traveling screens. Currently, the traveling screens are maintaining DP within limits and the unit is stable at 50% power. "Unit 2 decay heat removal is being performed by Auxiliary Feed Water to four steam generators blowing down via the 10% steam dumps to atmosphere." No other safety related equipment was out of service at the time of the trip. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JOHN WHESTLER TO JASON KOZAL ON 10/22/08 AT 0726 * * * The licensee issued a press release regarding this issue. Notified R4DO (Deese). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) |  | 0 | 2008-10-22
44587 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-10-21 19:44 | 2008-10-21 23:45 | 2008-10-21 | FAILURE OF 250V DC HPCI INJECTION VALVE UNDERVOLTAGE RELAY "A 250 Volt DC undervoltage relay for HPCI injection valve MO-2301-8 failed. The reason for the failure is still under investigation. The injection valve is a normally closed valve that opens on an initiation signal. The failure of the under voltage relay would prevent the HPCI injection valve (MO-2301-8) from opening and would prevent HPCI from performing its safety function. Pilgrim Station has entered a 14 day LCO due to Technical Specification 3.5.C.2." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-10-21
44586 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-10-21 | 2008-10-21 23:27 | 2008-10-21 | UNANALYZED CONDITION DURING DESIGN BASIS FIRE IN AREA A-27 OF AUXILIARY BUILDING "During a design-basis fire in area A-27 (2026' level Auxiliary Building) actions designated in OFN KC-016, FIRE RESPONSE, remove safety-related 125 VDC Power from the B Train Pressurizer PORV, BB PCV-456A, by opening fused disconnects NK0404 and NK0405. The intent of this action is to remove all power from the affected cable tray. This action removes control power to several safety-related components, which are assumed to remain available to the Control Room since the analyzed fire in area A-27 relies on the B Train to maintain safe-shutdown conditions. "Opening NK0404 and NK0405 and removing control power fm the assumed safe-shutdown train was not fully analyzed as to the impact on Control Room Actions and subsequent affects on availability of the assumed safe-shutdown train. "Actions taken or planned: 1) Fire detection and suppression in area A-27 are functional. 2) Established an hourly firewatch in area A-27 per the AP 10-104, Breach Authorizations. 3) Changed OFN KC-016, FIRE RESPONSE, to isolate the specific fused disconnect for BB PCV-456A, NK4421, and added a note to the operator to be aware that the PORV could reopen due to a cable-to-cable hot short." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-10-21
44585 | 0 | BALDOR ELECTRIC CO. |  |  |  |  | 2008-10-20 | 2008-10-21 16:58 | 2008-10-21 | BALDOR MOTORS WITH ENDRING HEAT DAMAGE Two motors were discovered to have endring heat damage. These two motors have been returned to Baldor. Six more motors from the same purchase order remain out. These six motors have been recalled by Baldor. Location of these six motors is unknown at the present time. These motors were manufactured for use in Flowserve Limitorque motor operated valve operators. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2008-10-21
44584 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-10-21 13:02 | 2008-10-21 17:06 | 2008-10-22 | IROFS FAILURE IN AREA 600 "Area 600 uses a flammable gas as part of its operation. IROFS FIRE6-6 is a control that prevents the flammable gas from exiting the main process equipment and being released into an attached glovebox. FIRE6-6 makes use of a dual door system, only one door is allowed to be open at a time and the chamber between the doors is purged. The accident scenario of concern is release of the flammable gas into the glovebox and an explosion in the building. IROFS FIRE6-8, 6-1 and 6-9 ensure an inert gas purge occurs prior to opening the main process equipment to the glovebox and are also credited as IROFS. "The equipment associated with FIRE6-6 is designated as Safety Related Equipment (SRE) and is functionally tested annually. The test was performed on October 21, 2008. The test failed because when one door was open, the 2nd door opened slightly (approx 1 inch). Though there are mitigating factors such as potential dilution of the flammable gas through the glovebox ventilation system, it was determined that IROFS FIRE6-6 was degraded and that the performance criteria of 10CFR70.61 were not met. "The event occurred due to a degraded IROFS that was discovered during a periodic functional test. Initial investigation indicates that a failed position switch is the cause. [The potential health and safety consequences are] a potential explosion in a glovebox and release of radiological material and exposure to the worker. No actual explosion or radiological exposure occurred. "Discussed situation with Safety management and with NRC Resident Inspector. Operations has locked out the flammable gas supply on Area 600 until the equipment associated with FIRE6-6 is fixed and the SRE test passes." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-10-23
44583 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-10-21 | 2008-10-21 16:12 | 2009-01-12 | ARKANSAS AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was provided by the State of Arkansas via email: "Wal-Mart stores notified the state of Arkansas of one missing tritium exit sign discovered during a world wide inventory of their stores. The exit sign was last seen during a Spring 2008 inventory. The following device was reported missing: 1. Exit sign from a store (#468) located at 133 Arkansas Blvd., Texarkana, AR 71854, Serial number - 248464, manufacturer - SRB, activity - 20 Ci of tritium at time of manufacture. * * * UPDATE PROVIDED BY STEVE MACK TO JASON KOZAL ON 11/12/08 AT 1030 EST * * * The following was provided by the state via e-mail: "The following devices were reported missing: "1. Exit sign from a store located in Hot Springs Village, AR. Serial number - 273316, manufacturer - Isolite, Activity - 11.5 Ci of tritium at time of manufacture." Notified R4DO (Whiten), FSME (Burgess) and ILTAB via e-mail. * * * UPDATE PROVIDED BY STEVE MACK TO PETE SNYDER ON 1/12/09 AT 1537 EST * * * The following was provided by the state via e-mail: "Wal-Mart's records show that 159 Tritium Exit Signs (Serial Numbers provided to the State of Arkansas) were shipped to various store locations within the State of Arkansas; however, none of these signs [which are general licensed materials] were located during the inventory at the stores. Wal-Mart had no prior information indicating that these signs had been transferred to another location. In addition to the physical searches conducted by Wal-Mart's contractor, Wal-Mart reviewed the shipment and inventory records, but was not able to learn any additional information about the location or condition of the lost signs. "As a result of those investigations and the data collected over the course of Wal-Mart's nationwide inventory, Wal-Mart determined that these signs are lost. Wal-Mart notified the State of Arkansas immediately by phone. At this time, Wal-Mart has no additional information regarding the whereabouts of these signs; they remain lost. "This is Wal-Mart's final report reconciling all previously unaccounted for signs." Notified R4DO (Lantz), FSME (Turtil) and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44582 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-10-20 11:10 | 2008-10-20 19:07 | 2008-10-20 | 24 HOUR FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive for alcohol during a For-Cause fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2008-10-20
44581 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-10-18 11:25 | 2008-10-18 16:43 | 2008-10-18 | BOTH BORON INJECTION TANK INLET VALVES INOPERABLE. "At 11:25 on 10/18/08 it was identified that 2-SI-MOV-2867A and 2-SIÀMOV-2867B, Boron Injection Tank (BIT) Inlet valves were both inoperable. This resulted In less than 100% of the equivalent to a single operable ECCS train being available (TS 3.5.2.C). "2-SI-MOV-2867A was made inoperable on 10/17/08 at 23:26 for troubleshooting. Subsequently 2-SI-MOV-2867B became inoperable on 10/18/08 at 03:26 because its emergency power supply was inoperable for maintenance. At that time TS 3.0.3 was applicable with 13 hours to reach MODE 4 and 37 hours to reach MODE 5. "On 10/18/08 at 12:05 2-SI-MOV-2867A was made available and TS 3.0.3 action was cleared. The emergency power supply for 2-SI-MOV-2867B was made operable on 10/18/08 at 13:35." NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-10-18
44580 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2008-10-18 06:08 | 2008-10-18 06:59 | 2008-10-18 | ACTUAL INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Inadvertent introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-10-18
44579 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-10-17 16:15 | 2008-10-17 20:45 | 2008-10-17 | INADVERTENT TRANSFER OF UNSAMPLED DISCARD SOLUTION "Transfer of low uranium concentration discard solution from Tank WF03 to Waste Water Treatment Facility (WWTF) Tank 29 without final sample and analysis due to inadvertently opening incorrect valve. "There were no actual or potential safety consequences to workers, the public, or the environment. "Solution from discard Tank WF04 had been sampled and analyzed and was approved for transfer to WWTF Tank 29. An incorrect valve was opened and low uranium concentration solution was transferred from discard Tank WF03 to WWTF Tank 29 without final sample and analysis. All sources into the discard tanks (WF03 and WF04) are routed through an in-line uranium concentration monitor. "Remaining SSC's were available and reliable. Solution in discard Tank WF03 had passed through an in-line uranium concentration monitor which would have stopped the transfer if a high uranium concentration was present. "Solution in discard Tank WF03 and WWTF Tank 29 were sampled. Both uranium concentration results are low. The solution in discard Tank WF03 would have met sample analysis requirements. "The safety significance is low due to the low mass and concentration of U-235. In-line monitor was also present which would have prevented transfer of high concentration solution into discard Tank WF03. "The control is to sample and analyze solution prior to transfer to WWTF. The deficiency in this case is the failure to perform those actions prior to discard. "Event was identified and entered into Problem Identification, Resolution and Correction System (PIRCS) - PIRCS #15829. Investigation is underway. Both the discard Tank WF03 and the WWTF Tank 29 were sampled." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.74 APP. A |  |  |  | 0 | 2008-10-21
44578 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-09-17 | 2008-10-17 17:48 | 2008-10-17 | AGREEMENT STATE REPORT - DOSE TO UNINTENDED TISSUES The State of Florida was notified on 10/17/2008 by the licensee's Medical Physicist regarding a dose of 3400 cGy (3400 rad) administered to unintended tissues during several breast cancer therapy treatments over the period of September 10 - 17, 2008. The apparent unintended dose was identified on 10/16/2008, when the patient reported to the licensee symptoms of erythma (skin reddening) to the breast not intended to be treated. Specifically, the patient was being treated for breast cancer with an Ir-192 High Dose Rate (HDR) Afterloader unit (source strength, manufacturer, and model unknown at the time of this report). When the erythema was reported by the patient, the Medical Physicist reviewed the records and determined that the HDR Afterloader was mis-programmed such that the source stopped 10 centimeters short of the intended tumor bed in the right breast. As a result, the entire dose intended for the tumor bed was administered to the left breast that was not intended to be treated. The State of Florida did not currently have information regarding any potential long term effects for the patient due to this event. The State of Florida will dispatch an inspector to the facility early next week to follow-up on this event. A written report of this event will be provide by the State at that time. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-10-22
44577 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2008-10-09 | 2008-10-17 15:35 | 2008-10-17 | AGREEMENT STATE REPORT - 50 PERCENT UNDERADMINISTRATION OF YTTRIUM-90 The state provided in the following information via e-mail: "On 10/10/08, licensee's RSO notified DRH [Division of Radiological Health] of a Yttrium-90 SIR-Spheres medical event. The reportable event involved the administration of 54 mCi of SIR-Spheres for one patient with approximately 27 mCi instilled into both the right and left hepatic arteries. After instilling approximately 27 mCi of Yttrium-90 SIR Spheres based on radiation readings into the right hepatic artery, a smaller catheter for the left hepatic artery was used due to anatomy and to get to the segment feeding the tumor. While attempting to instill the Yttrium-90 SIR Spheres into the left hepatic artery over-pressurization caused the three (3) way valve in the containment box to give way and resulted in the release of a therapeutic dose of Yttrium-90 SIR Spheres into the delivery system containment box as per design. Due to the release of the second part of the dose into the containment box only approximately 50% of the dose was able to be administered. The procedure was terminated and the delivery box was bagged and held for decay-in-storage. Personnel in the room were monitored for contamination and the room was surveyed and released. The patient was released with no harmful effects foreseeable by the Radiation Oncologist. The patient and referring physician were notified of additional future treatment. "Licensee suggested the incident may have been caused by the size of the catheter, a kink in the catheter, or a smaller syringe being used by the interventional radiologist putting increased pressure on the 3 way valve. As a result of the medical event the licensee's treatment team will review the delivery system setup before pressure is applied to ensure the flow of the SIR-Spheres will not be impeded within the catheter." License No.: MS-MBL-01 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2008-10-22
44576 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-10-16 | 2008-10-17 13:39 | 2008-11-04 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN A Wal-Mart store at 14 S. Main Street in Swainsboro GA notified the State of Georgia that a tritium exit sign that had been held in storage was missing. The store had previously removed its tritium signs and was storing them for eventual return to the manufacturer. During an inventory of the signs, one was discovered to be missing. The sign is generally licensed by the State. The sign was manufactured by Isolite with 11.5 curies of tritium. The State of Georgia did not have the serial number of the sign. * * * UPDATE FROM ERIC JAMESON TO JOE O'HARA AT 1353 ON 10/21/08 * * * A Wal-Mart store at 6065 Jonesboro Road in Morrow, GA notified the State of Georgia that two tritium exit signs were missing. The signs were manufactured by SRB with 20 Curies each S/N 279368 and S/N 282787. Additionally, a Wal-Mart store at 3886 Highway 17 in Toccoa, GA. had one tritium exit sign missing. The sign was manufactured by Isolite with 11.5 curies of tritium. The State of Georgia did not have the serial number of the sign. The signs are generally licensed by the State. Notified R1DO(Cahill), FSME(Burgess), and ILTAB via E-mail * * * UPDATE FROM ERIC JAMESON TO DONALD NORWOOD AT 1533 ON 10/27/08 * * * A Wal-Mart store at 2427 Gresham Road, Atlanta, GA reported on 10/22/08 one missing tritium exit sign. The sign was manufactured by Isolite, S/N unknown, Activity unknown. A Wal-Mart store at 3040 Norman Drive, Valdosta, GA reported on 10/24/08 one missing tritium exit sign. The sign was manufactured by Isolite, S/N 269809, Activity 11.5 curies. A Wal-Mart store at 1569 North Expressway, Griffin, GA reported on 10/24/08 one missing tritium exit sign. The sign was manufactured by SRB, S/N 278658, Activity 20 curies. A Wal-Mart store at 1099 Indian Drive, Eastman, GA reported on 10/24/08 two missing tritium exit signs. The first sign was manufactured by Isolite, S/N 297971, Activity 11.5 curies. The second sign was manufactured by Isolite, S/N 297990, Activity 12.5 curies. Notified R1DO (Cahill), FSME (Mauer), and ILTAB (Ahern) via E-Mail. * * * UPDATE FROM ERIC JAMESON TO JASON KOZAL AT 1557 ON 11/04/08 * * * Two more signs reported missing: A store located at 4221 Atlanta Highway, Loganville, GA Manufacturer - SRB, Serial Number - 310084, Activity - 20 Ci. A store located at 4798 Jimmy Lee Smith Parkway, Hiram, GA Manufacturer - SRB, Serial Number - 273972, Activity - 20 Ci. Notified R1DO (Caruso), FSME EO (Burgess) and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-10-22
44575 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-10-16 | 2008-10-17 11:29 | 2009-01-16 | AGREEMENT STATE REPORT - LOSS OF SIX TRITIUM EXIT SIGNS "On 10/16/08 the Agency received 2 telephone calls from Rich Dailey, RSO of Wal-Mart. During the first call Rich Dailey reported the loss of 2 tritium exit signs, S/N 249447 & 249454, from the Wal-Mart store in Quincy [MA]. During the second call Rich Dailey reported the loss of 4 tritium exit signs from the Wal-Mart store in Halifax [MA]. Rich Dailey stated that Wal-Mart is conducting a replacement of all tritium signs. In the Spring of 2008 these exit signs were inventoried. In October 2008, prior to replacement, the signs could not be located. All of the exit signs were manufactured by `SRB Lite' and contain 20 curies of H-3. Rich Dailey will send a written report to the Agency at a later date." * * * UPDATE ON 10/28/08 AT 0957 EDT FROM DAILEY TO KLCO * * * The following information was received via facsimile: "On October 22, 2008 Wal-Mart Stores reported four missing tritium exit signs at 300 Colony Place, Plymouth, MA. The signs were discovered missing on October 21, 2008. The serial numbers and manufacturer were unknown." Notified FSME(Burgess), R1DO(Cobey) and ILTAB via email. * * * UPDATE ON 1/16/08 AT 1130 EST FROM SUMARES TO HUFFMAN * * * The following information was received from the State via facsimile: The State of Massachusetts was notified by a Wal-Mart corporate representative located in Bentonville, AR, indicating that Wal-Mart was unable to account for 887 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout the state. The Wal-Mart representative informed the state office that Wal-Mart had exhausted searching for the tritium exit signs and considered them to be lost and/or missing. The state was provided a listing from corporate Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers, and curie content where known. Notified FSME (McIntosh), R1DO (Burritt), and ILTAB THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-10-22
44574 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2008-10-17 08:00 | 2008-10-17 09:33 | 2009-01-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS Wal-Mart Corporate Office reported a total of 2 tritium exit signs missing from one store in Iowa. Store management and maintenance personnel have conducted a search and have determined that the signs are not on the premises. Wal-Mart is declaring these signs to be missing. Wal-Mart Corporate office notified the Iowa Department of Public Health The device information is as follows: 1. Location: Mason City, Iowa. Manufacturer - SRB Technology, Serial number - 263251, Curie content - 20. 2. Location: Mason City, Iowa. Manufacturer - SRB Technology, Serial number - 263223, Curie content - 20. * * * UPDATE ON 1/7/2009 AT 1004 FROM RANDAL DAHLIN TO MARK ABRAMOVITZ * * * "The State of Iowa was notified by the Bentonville, AR, Wal-Mart Project Manager regarding an additional 168 missing Tritium Exit Signs (TES) in the state. This notification occurred on January 6, 2009 at 2:30 pm. The Wal-Mart representative informed this office that Wal-Mart had exhausted all possibilities for location of these signs. The State of Iowa considers these Tritium Exit Signs to be lost and/or missing." Notified the R3DO (Duncan) and FSME (Turtil), ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2009-01-16
44573 | 0 | FROEHLING & ROBERTSON, INC. |  |  |  |  | 2008-10-16 15:00 | 2008-10-17 08:40 | 2008-10-17 | TRANSPORTATION ACCIDENT INVOLVING RADIOACTIVE MATERIALS IN VIRGINIA The licensee's Radiation Safety Officer (RSO) reported that on 10/16/2008, at approximately 1500 EDT, a licensee truck transporting a Troxler 3400 Series moisture density gauge, flipped over in the Monitor-Merrimac Bridge Tunnel, near Newport News, VA. This series of Troxler gauge typically contains 8 mCi Cs-137 and 40 mCi Am/Be. The RSO indicated that it was reported that the handle on the case, in which the gauge was secured, was damaged in the accident. The RSO did not have any indications of elevated or abnormal radiation or contamination levels from the gauge after the accident. The driver of the truck was injured in the accident (broken arm). At the time of this report, the gauge was in the possession of the licensee, and the licensee is conducting follow-up surveys. Notified Virginia Radioactive Materials Program, DOT (NRC), DOE, and DHS. * * * UPDATED AT 1155 EDT ON 10/17/2008 FROM W. BRIODY TO P. SNYDER * * * The licensee RSO reported that follow-up surveys and visual inspection of the gauge found no abnormal radiation levels, and no apparent damage to the gauge itself. The licensee will send the gauge to the manufacturer (Troxler) for further evaluation and/or repair. Notified R1DO (T. Jackson), FSME EO (Einberg), NMSS EO (Regan), IRD Mgr (J. Grant). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | TRA | [5 empty] | 0 | 2008-10-17
44572 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-10-16 13:17 | 2008-10-16 15:40 | 2008-10-16 | UNANALYZED CONDITION RELATED TO CERTAIN FIRE CONDITIONS "While performing an extent of condition review resulting from the unanalyzed condition related to certain fire conditions identified in Event Notification #44482, another situation was identified in which, under certain fire conditions, the ability to meet the performance criteria of the approved fire protection program may be challenged. "Specifically, it was postulated under certain fire conditions affecting the relay room, the ability to maintain pressurizer level within the indicated range may be challenged due to spurious opening of pressurizer vent and reactor head vent valves. "Compensatory actions to address the fire in the area of concern are in place. (1-hour Fire Watch). "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). "NRC Resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-10-16
44571 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2008-10-16 10:30 | 2008-10-16 12:38 | 2008-10-16 | LOSS OF EMERGENCY COMMUNICATIONS CAPABILITY (ERDS) "At 1030 [EDT] on 10/16/08, Emergency Planning personnel discovered that both ERDS [Emergency Response Data System] links (modems) were not functioning. The cause of the failure is unknown at this time and is being investigated by onsite technicians. The Emergency Notification System (ENS) was verified to be functioning properly. Loss of either ERDS link is considered a major loss of emergency communication capability and is reportable under 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-16
44570 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-10-16 11:00 | 2008-10-16 11:58 | 2008-10-17 | PARTIAL UNAVAILABILITY OF TSC VENTILATION AIR CONDITIONING SYSTEM FOR SCHEDULED MAINTENANCE "At 1100 on Thursday, October 16, 2008, a portion of the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system air conditioning was removed from service for maintenance on the Non-Essential Service Water System (NESW). The NESW system supports 3 of the 4 air conditioning units for the Technical Support Center. The filtration system will remain available, and an air conditioning unit which is not supported by NESW will remain in service. "Under certain accident conditions the TSC may become unavailable due to the inability of the ventilation system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system maintenance is scheduled to complete at 1800 on Thursday, October 16, 2008. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." * * * UPDATE ON 10/17/08 AT 0526 FROM BEN HUFFMAN TO PETE SNYDER * * * "The TSC ventilation system air conditioning was returned to functional status at 0525 on Friday, October 17, 2008. This follow up notification is being made to provide closure from the initial notification under 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." The licensee notified the NRC Resident Inspector. Notified R3DO (Phillips). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-16
44569 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2008-10-15 14:40 | 2008-10-16 07:47 | 2008-10-16 | OFFSITE NOTIFICATION TO SC-DHEC "On October 14, 2008, Westinghouse received the vendor chemical laboratory analysis for the Total Suspended Solids (TSS) parameter result for the October 1st, 2008, NPDES liquid effluent 24-hour composite sample. The sample result indicated that the wastewater discharged from the Westinghouse Columbia plant to the Congaree River during the 24-hour period preceding the October 1st sampling contained 64.07 pounds of TSS, which exceeds the Daily Maximum permit limit of 64.0 pounds per day. "Preliminary information indicates the parameter exceeded the permit limit due to dredging of lagoon solids during the week preceding the October 1st sample. It should be noted that process samples taken the day before did not indicate a problem with TSS prior to discharge. Typical averages for TSS in 2008 are 12.3 pounds per day, which is well below the permit daily average limit of 32 pounds per day. The dredging campaign has since been completed, and the following weekly sample analysis (dated October 8, 2008), indicates that TSS values are back to normal, around 15 pounds. "Liquid discharges from the Columbia Plant are regulated with regard to chemical pollutants through the SC-DHEC/EPA administered NPDES permit SC#0001848. WEC is required to notify SC-DHEC of non-compliance conditions which exceed any daily maximum effluent limitation. ' Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made shall be reported to the NRC Operations Center concurrent to the news release or other notification.' "Liquid discharges from the Columbia Plant are regulated with regard to chemical parameters through the SC-DHEC/EPA NPDES Permit #SC0001848. "Liquid effluent discharges are being temporarily halted while reviews are being conducted to verify no potential for recurrence of the event. The event will be entered into the plant's Corrective Action Process and a thorough review will be performed to identify the cause of the event. The problem was identified by Westinghouse EH&S personnel. At no time was the health or safety to any employee or member of the public in jeopardy. SC-DHEC has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-10-16
44568 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-10-16 01:56 | 2008-10-16 03:33 | 2008-10-16 | NON-FUNCTIONAL TECHNICAL SUPPORT CENTER "During normal surveillance testing of the U1 Control Room radiation monitors, the Technical Support Center Emergency Filtration Unit did not automatically start as required upon initiation of a High CR Radiation Signal. Additionally, the filtration unit could not be manually started from the TSC HVAC Control panel. "This report is being made per Technical Requirements Manual 13.13.1, action B.2. With the Technical Support Center Emergency Filtration Unit inoperable, the functionality of the Technical Support Center has been lost. The alternate TSC facility is available and actions are being taken to return the TSC to Functional status with a high priority. "The NRC resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-16
44567 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-09-09 06:46 | 2008-10-15 15:03 | 2008-10-15 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "On 09/09/08 at approximately 0646 hours, with both Susquehanna Units in Mode 1 (U1-94.4% power, U2-100% power), Susquehanna experienced a temporary loss of its Transformer 10 (T-10) offsite power source due to lightning storms in the area. The loss of T-10, combined with a failure of Tie Breaker OA105-02 automatic closure logic, (caused by a breaker contact problem that has subsequently been corrected) resulted in the de-energization of Startup Bus 10 (normally powered through T-10). With this electrical transient, some 4.16 kV emergency busses normally powered by Startup Bus 10 experienced a short (~0.5 sec) electrical perturbation as the busses transferred to their alternate (Startup Bus 20) power source. This momentary power disruption resulted in numerous containment isolations. These isolations, on both Unit 1 and Unit 2, included: (1) Reactor Building Chilled Water to the Reactor Recirculation pumps, (2) Reactor Water Sample valves, (3) Instrument Gas TIP Indexer Isolation valves, (4) Drywell Equipment Drain Tank/Drywell Floor Drain Isolation valves, and (5) the 'A' and 'B' Containment Radiation Monitors. "Because plant conditions necessary to prompt a containment isolation were not present, this event constitutes an invalid system actuation and is reportable under 10 CFR 50.73(a)(2)(iv)(A). The condition meets the criteria of 10 CFR 50.73(a)(2)(iv)(B)(2) because the electrical anomaly affected containment isolation valves in more than one system. This notification is being provided via a 60-day optional phone call as permitted under 10 CFR 50.73(a)(1) in lieu of a written LER. "Valves affected by the invalid signal fulfilled their isolation function by successfully closing. There were no challenges to the Reactor as a result of this event. Transformer 10 was successfully re-energized in under an hour. All affected 4.16 kV emergency busses were transferred back to their normal power supply within 78 minutes of the initial event." The NRC Resident Inspector will be notified. | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-10-15
44566 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-07-08 | 2008-10-15 14:13 | 2008-10-15 | SOURCE FOUND IN TRASH LOAD IN MAINE "Trash load was returned to MA after setting off detectors in Maine. "On 7/25/08, it was reported to the agency that the source of radiation was identified as a 6 mCi Radium source. The only identifying marks on the source were 'Textron.' The source is a metallic disk 0.5 inch thick and 0.5 inch in diameter. Contact has been made with CRPCD to dispose of the source under their orphan source program. "Source is stored securely at AKS site pending disposal. "Event originally reported as DOT approval ME-MA-08-01." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-10-20
44565 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-10-14 05:00 | 2008-10-14 05:12 | 2008-10-14 | TECHNICAL SUPPORT CENTER REMOVED FROM OPERATION FOR MAINTENANCE "Fermi 2 is removing, on October 14, 2008, the Technical Support Center (TSC) heating, ventilation, and air conditioning system from operation to facilitate maintenance activities. During this work, the facility will not be available for emergency use. Fermi is making this notification in accordance with 10CFR 50.72(b)(3)(xiii). In the event TSC activation is necessary, the Emergency Offsite Facility (EOF) will be utilized. Activation and use of the EOF as a backup for the TSC is included in Fermi's Radiological Emergency Response Preparedness Plan, and drills have been held performing both the TSC and EOF functions from the EOF. Fermi will notify the NRC upon completion of this work which is expected to be approximately one day. The Licensee will notify the NRC Resident Inspector." * * * UPDATE FROM G. MILLER TO JOE O'HARA AT 1616 EDT ON 10/14/08 * * * "Preventative Maintenance Activities on the TSC HVAC system have been completed. The TSC is now available for use." The licensee will notify the NRC Resident Inspector. Notified R3DO(Phillips). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-14
44564 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2008-10-11 22:36 | 2008-10-11 23:35 | 2008-10-12 | TURBINE TRIP/ AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR LEVEL At 2236 on 10/11/08 while reducing power for a planned refueling outage, "C" Steam Generator water level decreased and the turbine tripped. The reactor tripped on the turbine trip. Auxiliary feedwater initiated as expected and decay heat is being removed via the condenser steam dumps. All control rods fully inserted. No significant safety equipment is out of service and all safety buses are being supplied by offsite power. Emergency Diesel generators are available if needed. No PORVs or primary/secondary relief valves lifted. The licensee is evaluating cause of steam generator level excursion. Unit 2 is unaffected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-10-12
44563 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-10-11 11:51 | 2008-10-11 16:31 | 2008-10-11 | CONTROLLED SUBSTANCE FOUND IN THE PROTECTED AREA Licensee personnel found an unattended controlled substance inside the protected area. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2008-10-11
44562 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-10-11 05:45 | 2008-10-11 10:23 | 2009-03-16 | UNANALYZED CONDITION DUE TO VENDOR CALCULATION ERROR "Turkey Point received notification of an error in a vendor calculation methodology regarding the containment building heat transfer. This calculation is used to support containment temperature and pressure as well as heat input to the Component Cooling Water system under design basis accident conditions. "While validating a new analysis model, it was discovered that the Turkey Point containment steel liner was not included in the analysis of record. This is a non-conservative error in that less heat would be expected to be transferred to the external environment with the presence of the liner. The initial evaluation of the error indicates that at the maximum allowable Ultimate Heat Sink (Intake) temperature, Containment pressure, long-term Containment temperature and Component Cooling Water return temperature could exceed licensing basis limits during a design basis accident. "Preliminary analysis indicates that under current Ultimate Heat Sink conditions, operability requirements are met." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1642 ON 3/16/09 FROM MCKEE TO HUFFMAN * * * "The purpose of this update is to retract EN #44562 submitted to the NRC Operations Center on October 11, 2008. "FPL has performed a detailed evaluation of the impact of errors identified by Westinghouse in the Loss of Coolant Accident (LOCA) containment analysis of record on the operation of Turkey Point Units 3 and 4. The evaluation took into consideration actual ultimate heat sink (intake cooling water - ICW) temperatures, and removed conservatisms used in the LOCA containment integrity analysis and Component Cooling Water (CCW) system analysis. The evaluation confirmed that the Units 3 and 4 containment structures were capable of performing the safety function required by the Technical Specifications. Additionally, after removal of conservatisms in conjunction with a minimum CCW heat exchanger heat removal capability consistent with an ICW temperature of 95 degrees F, and an assumed CCW heat exchanger tube resistance, the long term containment temperature and CCW return temperature would not have exceeded licensing basis limits during a design basis accident. "The evaluation determined that Turkey Point Units 3 and 4 were not in an unanalyzed condition that significantly degraded plant safety as a result of the containment integrity analysis error and this event is not reportable under 10CFR50.72(b)(3)(ii)(B) criteria. Therefore, EN #44562 is retracted. "The evaluation described above is documented in the Corrective Action Program in report 2008-31338 ." The licensee will notify the NRC Resident Inspector. Notified R2DO(Nease). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-10-11
44561 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-10-11 05:08 | 2008-10-11 10:07 | 2008-10-12 | STEAM GENERATOR WATER LEVEL TRIP ACTUATION INITIATED REACTOR TRIP SYSTEM "During plant shutdown to begin a scheduled refueling outage, with the plant at 0% power in Mode 3, an actuation of the reactor trip system (RTS) occurred when a steam generator (S/G) Low-Low water level trip inadvertently occurred during recovery from a feedwater isolation actuation that had previously occurred in response to a steam generator high water level trip condition. "At approximately 0500 hours, plant operators were closing the main steam isolation valves (MSIVs) for plant shutdown. Once the MSIVs were closed, the reactor coolant system (RCS) cooldown rate decreased significantly. The 'A' atmosphere steam dump valve (ASD) was then opened. Shortly after the ASD was opened, the MSIV was also opened. With both the MSIV and ASD open, however, the 'A' S/G water level swelled until the P-14 S/G Hi Level protective interlock setpoint was reached, resulting in a feedwater isolation (FWIS) actuation at 0505 hours. "Subsequent to the FWIS actuation, plant operators took action to recover from the FWIS in accordance with off-normal operating procedure OTO-SA-00001, 'Engineered Safety Feature Actuation Verification and Restoration.' The motor-driven auxiliary feedwater pumps were started to restore S/G water level. However, S/G water level lowered rapidly in response to the cold auxiliary feedwater flow to the S/G. A S/G Low-Low water level trip signal was then reached on the 'A' S/G, thus resulting in a reactor trip system actuation at 0508 hours. All systems functioned normally in response to plant conditions." The NRC Senior Resident Inspector has been informed. * * * UPDATE AT 0239 EDT ON 10/12/08 FROM FRED BIANCO TO VINCE KLCO * * * "This report is an update to information reported under ENS notification 44561. The original notification reported a valid reactor trip system actuation as a 4-hour notification under 10CFR50.72(b)(2)(iv)(B). The correct reporting requirement is 10CFR50.72(b)(3)(iv)(A), an 8-hour notification, as the plant was in Mode 4 with the reactor subcritical at the time of the event. "The [NRC] Resident Inspector will be notified." Notified R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-10-11
44560 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-10-11 00:49 | 2008-10-11 02:47 | 2008-10-11 | DISCOVERY OF AN AFTER-THE-FACT NOTIFICATION OF UNUSUAL EVENT "At 0049 on 10/11/08 Letdown Relief valve BG8117 lifted prior to set point, resulting in Pressurizer water inventory being diverted to the Pressurizer Relief Tank. Letdown was isolated within 13 minutes, isolating the leakage. Upon review of the level trends of the Pressurizer Relief Tank level changes, approximately 574 gallons were diverted from the Reactor Coolant system. This would result in an RCS leakage rate of 44 gpm of RCS Identified Leakage. At the time that the calculation of leakage rate was discovered, it was immediately recognized that this met the requirements for EAL 4R, 'RCS Identified Leakage greater than 25 gpm'. As a result of identification that the criteria of an EAL was exceeded, and no longer existed, a notification was made to the NRC Operation Center in accordance with 10 CFR50.72(a)(1)(i)." Licensee has notified NRC Resident Inspector and will notify state and local agencies on the next business day. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW | [5 empty] | 0 | 2008-10-11
44559 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-10-09 13:45 | 2008-10-10 17:40 | 2008-11-14 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was provided by the state via e-mail: "Wal-Mart Corporate Office reported a total of 8 tritium exit signs missing from various stores in Ohio. These signs were removed from service and were being held pending return to the manufacturer for disposal. The signs were discovered missing on or about October 8, 2008 at each store. Store management and maintenance personnel have conducted a search at each store and have determined that the signs are not on the premises. Wal-Mart is declaring these signs to be missing. "Wal-Mart Corporate office notified the Ohio department of health by phone at approximately 1:45 PM on October 9, 2008, and followed with a written description of the signs on October 10, 2008." The device information is as follows: 1. Location: Store number 01495 Huber Heights, Manufacturer - Isolite, Serial number - 272778, Curie content - 11.5. 2. Location: Store number 01724 Millersburg, Manufacturer - Isolite, Serial number - 260634, Curie content - 20. 3. Location: Store number 02441 Hamilton, Manufacturer - Isolite, Serial number - Unknown, Curie content - 11.5. 4. Location: Store number 02441 Hamilton, Manufacturer - Isolite, Serial number - 338664, Curie content - 11.5. 5. Location: Store number 02441 Hamilton, Manufacturer - Isolite, Serial number - 365140, Curie content - 11.5. 6. Location: Store number 03656 Cincinnati, Manufacturer - Isolite, Serial number - Unknown, Curie content - 11.5. 7. Location: Store number 03656 Cincinnati, Manufacturer - Isolite, Serial number - 362582, Curie content - 11.5. 8. Location: Store number 6327 Warren, Manufacturer - Isolite, Serial number - Unknown, Curie content - 11.5. Ohio report number - OH080007 * * * UPDATE ON 11/7/2008 AT 1205 FROM MICHAEL SNEE TO MARK ABRAMOVITZ * * * Received from the state of Ohio via e-mail: A tritium exit sign was reported missing from the Wal-Mart store in Centerville, OH. The Isolite sign (S/N 318793) contained 11.5 Curies of tritium and was reported to Ohio at 1000 on 11/7/2008. Ohio Report Number: OH080009 Notified R3DO (Cameron) and FSME (Suber). * * * UPDATE ON 11/12/2008 AT 1205 FROM MICHAEL SNEE TO JOHN KNOKE * * * Received from the state of Ohio via e-mail: Two Tritium exit signs were reported missing from the Wal-Mart store in Middletown, OH. The SRB Technologies signs (S/N 280511) & (S/N 280548) contained unknown activity, and was reported to Ohio at 1230 on 11/12/2008. Ohio Report Number: OH0800011 Notified R3DO (Hills) and FSME (Suber), ILTAB email * * * UPDATE ON 11/12/2008 AT 1205 FROM MICHAEL SNEE TO JOHN KNOKE * * * Received from the state of Ohio via e-mail: A Tritium exit sign was reported missing from the Wal-Mart store in Newark, OH. The SRB Technologies sign (S/N 268804) contained 20 Ci of Tritium, and was reported to Ohio at 1230 on 11/12/2008. Ohio Report Number: OH0800013 Notified R3DO (Hills) and FSME (Suber). ILTAB email * * * UPDATE ON 11/12/2008 AT 1205 FROM MICHAEL SNEE TO JOHN KNOKE * * * Received from the state of Ohio via e-mail: A Tritium exit sign was reported missing from the Wal-Mart store in Mount Vernon, OH. The Isolite sign (S/N 293419) contained 11.5 Ci of Tritium, and was reported to Ohio at 1230 on 11/12/2008. Ohio Report Number: OH0800012 Notified R3DO (Hills) and FSME (Suber). ILTAB email * * * UPDATE ON 11/14/2008 AT 1329 FROM MICHAEL SNEE TO MARK ABRAMOVITZ * * * The following information was received from the state of Ohio via e-mail: Two additional lost Tritium exit signs were reported missing at store #5104 in Moraine, OH. The signs were manufactured by SRB with serial numbers 300242 and 300243. Each sign contained 20 Ci of Tritium. Notified the R1DO (Krohn), FSME (Flannery) and ILTAB (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2008-10-15
44558 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-10-09 15:37 | 2008-10-10 14:20 | 2008-10-10 | 24-HOURS BULLETIN 91-01 REPORT INVOLVING FAILURE TO VISUALLY INSPECT STORAGE CYLINDERS The following information is provided without quotation for readability: DESCRIPTION: On 10/09/08 at 1537 hours it was determined that procedure CP4-CU-CH6430, "In Storage Fissile Cylinder Inspection", does not fully meet the periodic inspection requirements of NCSA GEN-003. GEN-003 requires inspection every four years of all thick wall cylinders that contained fissile material since they were last washed on the inside of the cylinder. Only cylinders that were filled with fissile material on their last fill have been identified for inspection. Cylinders filled with fissile material, emptied and subsequently filled with non-fissile material and emptied, have not been inspected as required. Approximately 73 Cylinders that have contained fissile material since their last washing have not been inspected in violation of the requirement of NCSA GEN-003, these cylinders could contain residual nonvolatile material referred to as heel. Potentially the residual heel could contain fissile material. Double contingency is maintained by implementing two independent controls on one parameter (moderation). The first leg of double contingency relies on the design of the cylinder to ensure moderation control. Cylinders are designed to the requirements of ANSI N14.1 and ensure that it is unlikely for the cylinder wall to breach and allow water intrusion. This control on moderation was not violated. The second leg of double contingency relied on inspections every 4 years of the cylinder wall, valve, and plug for abnormal corrosion. This control ensures that in the event of a cylinder breach, it is unlikely that sufficient moderation to cause a criticality will enter the cylinder before it is identified and mitigated. Since the cylinders were not inspected within the 4 year time frame as required, this control on moderation was violated. The NRC Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-08-2918; PGDP Event Report No. PAD-2008-31; NRC Worksheet No. 44558. SAFETY SIGNIFICANCE OF EVENTS: Although a control requiring inspection of the cylinders every 4 years was violated, no cylinder breaches occurred. Later inspections identified no cylinder integrity issues, moderation control was lost and double contingency was not maintained. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): In order for a criticality to be possible, more than 10kgs of water would have to enter a breach in a cylinder which contains more than a critical mass of material enriched to greater than 1.0 wt% 235U. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS) : There were 73 cylinders which were not inspected as required. These cylinders had at one time held fissile material. The cylinders were emptied except for a small residual heel and then filled with non-fissile material. The non-fissile material was then emptied leaving only the residual heel in the cylinder. Cylinder heels are typically less than 50 pounds. Assay is always less than 5.5% enrichment. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: NCSA GEN-003 requires cylinders containing material enriched to greater than or equal to 1.0 wt % 235U to be inspected every 4 years to identify significant signs of degraded cylinder wall, valve and plug. These cylinders were filled with fissile material, emptied and then subsequently filled with non-fissile material and then emptied again, but were not inspected within the four year requirement. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED : Cylinders have been inspected per the CP4-CU-CH6430 and the identified cylinders were found to comply with NCSA GEN-003. * * * UPDATE AT 1750 EDT ON 10/10/08 FROM BILLY WALLACE TO STEVE SANDIN VIA FAX * * * On 10/10/08 at 1500 CDT, an additional 8 cylinders were discovered which had not been properly inspected. The additional cylinders were of a different size than the initial cylinders found, but fall under the same requirement. The additional cylinders have been inspected and all met the NCSA requirements. Notified R2DO (Shaeffer) and NMSS (McCartin). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-10-10
44557 | 0 | CARBOLINE COMPANY |  |  |  |  | 2008-10-10 | 2008-10-10 10:41 | 2008-10-10 | PART 21 - BATCH OF CARBOZINC 11 SG IS NONCOMPLIANT IN CURE ISSUES "Carboline Company is notifying certain companies that a potential safety related noncompliance deviation in a basic component as defined in 10 CFR Part 21. The noncompliance involves a batch of Carbozine 11 SG Base that is not curing properly. It forms a poor quality film. "A customer notified Carboline of concerns regarding the cure of a particular batch of Carbozine 11 SG. Technical Service originally felt it was application related and worked with the customer. An internal report was opened once cure issues remained after working with their technical department. An analysis of the batch by our plant Quality Control was requested; the results did not confirm the problem. Material was then sent into Saint Louis R&D for additional analysis. On Tuesday, October 8, 2008 the analytical evaluation was reviewed by the product chemist and the batch cure issues were confirmed. "The batch was placed on hold and reports have been run to determine where the batch has been shipped. Carboline is requesting that the affected companies review their stock of Carbozine 11 SG and return any material with the batch number of 8G9892L. Further work is being done to determine the cause of cure issues with this batch of Carbozine 11 SG. At this time, Carboline has confirmed that this material is not curing properly and forms a poor quality film." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MO | OTH | PAR | 21.21 |  |  |  | 0 | 2008-10-10
44556 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2008-10-09 11:05 | 2008-10-10 09:00 | 2008-10-10 | AGREEMENT STATE REPORT - SOURCE CARRIER DETACHED FROM SOURCE HOLDER "The SC Department of Health and Environment Control was notified on Thursday, October 9, 2008, at 1105 hrs, that a source carrier from Ohmart/Vega Model SHLM-B2, s/n 66590, containing 500 mCi of Cs-137, had been inadvertently detached from the source holder at 1030 hrs on October 9, 2008. The Facility RSO stated that personnel were attempting to lock out the source when the source carrier was detached from the source holder. The state responded to the scene and arrived at 1326 hrs. The area around the gauge had been properly roped off and the source carrier had been placed on a gear box platform below the source holder. The inspector surveyed the barricaded areas and all readings were 2 mR/hr or less. The facility RSO stated that he had contacted Ohmart/Vega and the Field Service Representative was enroute to secure the source carrier. The inspector advised Facility RSO to maintain physical control of the barricaded areas until the source carrier had been secured. The facility RSO stated that the barricaded areas would be controlled to prevent unauthorized access. The inspector was contacted by the Field Service Representative at 1830 hrs on October 9, 2008, and he stated that he had secured the source carrier in the source holder and the source holder had been secured in a locked storage area. The Field Service Representative stated that he would return to the facility within the next week to package and ship the source holder back to Ohmart/Vega for further evaluation to determine why the source carrier detached from the source holder. "The facility RSO was advised by the state to submit a written report detailing this event to the Department within 30 days. The event is open and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2008-10-15
44555 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-10-08 | 2008-10-09 16:32 | 2008-10-09 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS Wal-mart stores notified the state of Georgia of two missing exit tritium exit signs discovered during a world wide inventory of their stores. The following devices were reported missing: 1. Exit sign from a store (#787) located at 7050 HW 85, Riverdale, GA. Serial number - 269198, manufacturer - Safetylite, activity - 11.5 Ci of tritium. 2. Exit sign from a store (#787) located at 7050 HW 85, Riverdale, GA. Serial number - unknown, manufacturer - unknown, activity - unknown. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-10-14
44554 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-10-09 12:54 | 2008-10-09 16:08 | 2008-10-09 | EMERGENCY DIESEL GENERATOR AND AUXILLARY FEEDWATER ACTUATION DUE TO BUS UNDERVOLTAGE "On October 9, 2008, during scheduled monthly testing per surveillance procedure 3-PT-M62C, '480 volt Undervoltage Degraded Grid Protection System Bus 6A Functional,' the normal supply power to 480 volt safeguards Bus 6A de-energized resulting in the start and load of Bus 6A by the 32 Emergency Diesel Generator (EDG), and the actuation of the '33' motor driven Auxiliary Feedwater Pump (AFWP), and the '32' steam driven AFWP. All equipment performed as designed. Auxiliary feedwater (AFW) was injected into the Steam Generators (SG). Core reactivity changes as a result of AFW injection resulted in an 0.1% increase in reactor power. SG level change from normal of approximately 1-2% with no actuation of SG alarms, no challenge to automatic control, and no rod movement. No significant change to the Nuclear Instrumentation was observed. Normal supply power was restored to bus 6A and the EDG-32 returned to Auto. Investigation into the cause of the event is in progress. Unit 2 was unaffected and is at 100% power." The licensee notified the NRC Resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-10-09
44553 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-10-08 | 2008-10-08 14:36 | 2008-10-08 | AGREEMENT STATE REPORT - LOST TRITIUM SIGN The state submitted the following report via e-mail: "Received notification on 10/8/2008 that an 'Ice Light' tritium exit sign was discovered lost by the Wal-Mart store located in North Reading, Massachusetts. The exit sign either contained 11 or 20 Curies of H-3." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-10-13
44552 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-09-30 07:00 | 2008-10-08 11:30 | 2008-10-21 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECTED FROM CONTROL CABLE Washington state submitted the following report via e-mail: "A licensee reported to the Department of Health (DOH) that an industrial radiography (IR) source had become disconnected from the control cable that prevented the retrieval of the source back into its safe shielded position. The exposure device is a QSA Global Sigma 880 with a 97 Curie Iridium-192 source. The source disconnect occurred at 7:00 AM 9/30/08 at a construction site three miles northeast of Moses Lake, Washington. The President and Radiation Safety Officer (RSO) of the licensed IR company are on scene with 12 company employees to correct the situation. The radiographer had previously made several exposures on pipe welds earlier in the day before the disconnect occurred. The source remained at the end of the guide tube, in the collimator, when the radiographer tried to retract it into the device. The radiographer tried this several times. A large area at the construction site has been secured by barricades and the IR personnel are guarding the radiation area. At present, it appears that personnel have not received any elevated or unusual exposure as a result of the disconnect. The IR company is working with the Office of Radiation Protection and the radiography device manufacturer to develop a plan to retrieve the source. DOH staff were sent to the location to assure radiation safety procedures are followed and independent measurements are made." Washington Report: WA080073 * * * UPDATE PROVIDED AT 1415 EDT ON 10/21/08 VIA EMAIL FROM ARDEN SCROGGS TO JEFF ROTTON * * * The following information was obtained from the State of Washington via email: "DOH staff went to the incident site at 1:30 p.m. on the day of the event. They assisted the IR company RSO establish the planned special exposure recovery plan. About 2:30 p.m. the construction-site safety officers were briefed on the recovery plan. Materials and equipment needed for the plan were assembled and at 3:35 they began the recovery operation. The plan included using a site crane and operator to extricate the camera, guide tube, collimator with source from the work scaffolding. The IR equipment was moved to a better location in an area away from the construction site. At 4:26 p.m. the camera and source were placed into a lead lined steel skiff-box and lifted to an area between a high dirt bank and tall concrete retaining wall. The new location was roped off and secured by the IR personnel. The actual recovery began at about 6:30. The IR drive cable was modified as the manufacturer recommended by filing two sides of the attachment fitting. Several attempts were made to hook onto the source pigtail. At around 9:30 the source was successfully pulled back into and locked in the camera. Surveys indicated the source was successfully placed into the shielded position. Pocket dosimeter readings for the four IR employees that were directly involved with the recovery indicated 10, 45, and 52 mRem. None of the construction workers received an exposure above background. The camera, with the source and associated equipment involved with the disconnect, was sent to the manufacturer for evaluation to determine why the equipment failed to operate as designed. "On October 1, 2008, the DOH Radioactive Materials' supervisor and the IR program lead staff went to the site to follow-up with the investigation and to close the event. While on site, they addressed an assembly of 800 craft construction workers. Several asked questions about the incident and voiced their concerns for the potential exposure they may have received. DOH staff also talked directly to several individuals before and after the briefing. A large majority of the construction workers seemed to understand that their health and safety had not been affected as a result of the incident. "[The State] has subsequently heard that the manufacturer (QSA Global) had determined that the pigtail connector had an engineering defect that allowed that connection to part from the drive cable causing the disconnect." Notified FSME (Burgess) and R4DO (Deese) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-10-13
44551 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-10-07 14:27 | 2008-10-08 11:40 | 2008-10-08 | AGREEMENT STATE REPORT - LOST EXIT SIGNS CONTAINING TRITIUM "I [state] received a call from a Wal-Mart Representative on 10/7/08 at 2:27pm on the Colorado Emergency Response and Incident Reporting Line to report three (3) exit signs containing tritium have been lost from two different Wal-Mart locations in the Denver area. Wal-Mart is in the midst of a nationwide effort to replace old tritium containing signs and its believed these signs have been removed but not accounted for during this process. "One sign is missing from a Wal-Mart store in Aurora located at 5650 S. Chambers Rd. Serial number of the sign is 274282. "Two signs are missing from a Wal-Mart store in Lakewood located at 7455 W. Colfax. Ave. Serial numbers of signs from that store are 280691 and 280712. "Each sign is believed to have contained 10.5 - 11.0 curies of tritium." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-10-13
44550 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2008-10-08 04:30 | 2008-10-08 09:23 | 2008-10-08 | ACTUAL INTRODUCTION OF CONTRABAND INTO A PLANT VITAL AREA Actual introduction of contraband into vital area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-10-08
44549 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-10-07 20:00 | 2008-10-07 23:13 | 2008-10-07 | INJURED, CONTAMINATED INDIVIDUAL TRANSPORTED TO HOSPITAL "A contractor fell and was injured while working inside the condenser. He was working in a contaminated area and is being transported via ambulance to River Regional hospital. The individual's protective clothing was slightly contaminated but his body was not contaminated. The State of Mississippi and Claiborne County are government agencies that have been notified of this incident." The individual's protective clothing read approximately 80 counts above background. A Radiation Protection technician is accompanying the contractor to the hospital. He is suspected to have suffered a broken ankle and broken arm. The licensee is investigating the accident. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2008-10-07
44548 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2008-10-07 | 2008-10-07 19:59 | 2009-07-23 | MEDICAL EVENTS DUE TO DOSE RECEIVED LESS THAN PRESCRIBED DOSE "In response to medical events discovered at the VA Medical Center Philadelphia, which have been reported under Event Number 44219, reviews are ongoing of samples of patient charts from other VA facilities with permanent prostate iodine-125 seed implant brachytherapy programs. "As the result of these ongoing reviews, medical events were discovered on October 7, 2008, for 6 patients treated at the VA Medical Center in Cincinnati, Ohio. "These 6 medical events involved seed distributions in the patients that resulted in D90 doses less than 80% of the prescribed doses. These circumstances were interpreted to meet the definition of a medical event under 10 CFR 35.3045. "A 15-day written report on these 6 medical events will be submitted to NRC Region III. We have notified our NRC Project Manager, Cassandra Frazier (NRC Region III), of these medical events." * * * UPDATE AT 1520 EDT ON 07/23/09 FROM ED LEIDHOLDT TO S. SANDIN * * * "Following the notification of the NRC on October 7, 2008, of the six medical events described in Event Report No. 44548, the NHPP initiated a reactive inspection on October 16, 2008. As a result of this inspection and related clinical reviews, the NHPP is notifying NRC of one additional medical event at the Cincinnati VA Medical Center, for a total of 7 medical events at this facility. This event, also involving prostate brachytherapy with I-125 seeds, was discovered on July 22, 2009. Like the previous six medical events, this additional medical event involves a D90 dose less than 80% of the prescribed dose. "We note that the D90 doses for all seven events were based upon CT scans performed one day after the implants, when the prostate is subject to edema from the procedure which often causes underestimation of the true D90. Furthermore, the prescribed doses were 160 gray, instead of the more common 145 gray. Thus, most if not all of these patients likely received clinically adequate dose distributions, despite the percent-wise slightly low D90s. Adverse biological effects to these patients are not expected. "The facility has notified the patient. "A written report on this additional medical event will be submitted to NRC Region III pursuant to 10 CFR 35.3045. We will notify the NRC Project Manager, Cassandra Frazier, of NRC Region III." Notified R3DO (Hills) and FSME EO (Villamar). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | OH | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-10-13
44547 | 0 | WAL-MART |  |  |  |  | 2008-10-07 | 2008-10-07 16:54 | 2009-01-16 | LOST TRITIUM EXIT SIGNS Wal-Mart is conducting a worldwide audit of their tritium exit signs. This morning they discovered three missing signs. The first missing sign was located at the store in Noblesville, Indiana. The serial number is 301651, manufacturer unknown. Curie content unknown. The sign was last inventoried in the spring of 2008. The second sign was located at the store in Charlotte, Michigan. The serial number and manufacturer were unknown. Curie content unknown. The sign was last inventoried in the spring of 2008. The third sign was located at the store in Yankton, South Dakota. The serial number is 293214, manufacturer unknown. Curie content unknown. The sign was last inventoried in the spring of 2008. All three stores were searched for the signs without success. * * * UPDATE PROVIDED BY RICHARD DALEY TO JASON KOZAL ON 10/09/08 AT 1308 * * * Three additional signs were discovered missing in the state of Michigan: 1. At a store located at 995 Razorback Dr., Houghton, MI 49931. The serial number is unknown, the manufacturer is Isolite (11.5 Ci of tritium). 2. At a store located at 10772 West Carson City Rd., Greenville, MI 48838. The serial number is unknown, the manufacturer is Isolite (11.5 Ci of tritium). 3. At a store located at 7021 SW Nedge Ave, Portage, MI 49002. The serial number is 357889, the manufacturer is Isolite (11.5 Ci of tritium). All three stores were searched for the signs without success. Notified R3DO (Lara), and FSME (Burgess) and ILTAB via email. * * * UPDATE AT 1400 EDT ON 10/10/08 FROM RICH DAILEY TO S. SANDIN * * * An additional missing exit sign was identified during the on-going inventory. The exit sign was manufactured by SRB and contained 20 Ci of tritium, S/N 280802. It was last inventoried in Spring 2008 at Wal-Mart Store #5039 which is located in Camden, DE. Notified R3DO (Lara), FSME (Einberg) and ILTAB via email. * * * UPDATE AT 1422 EDT ON 10/14/08 FROM RICH DAILEY TO JOE O'HARA * * * An additional missing exit sign was identified during the on-going inventory. The exit sign was manufactured by SRB and contained 20 Ci of tritium, S/N 277880. It was last inventoried in Spring 2008 at Wal-Mart Store #1833 which is located in Fredericksburg, VA. Notified R1DO (Jackson), R3DO (Phillips), FSME (Vontill) and ILTAB via email. * * * UPDATE AT 1305 EDT ON 10/21/08 FROM RICH DAILEY TO JEFF ROTTON * * * Two additional missing exit signs were identified during the on-going inventory. 1. 1 sign at store #566, 1115 American Way, Booneville, IN 75237. The exit sign was manufactured by SRB and contained 20 Ci of tritium, S/N 306432. 2. 1 sign at store #3548, 910 Walcott Street, Waterbury, CT 06705. The exit sign was manufactured by SRB and contained 20 Ci of tritium, S/N 266092. Notified FSME (Burgess), R3DO (Hironori Peterson), R1DO (Cahill), and ILTAB via email. * * * UPDATE ON 10/24/08 AT 1735 EDT FROM DAILEY TO KLCO * * * Wal-Mart Corporate Office reported a total of 2 tritium exit signs missing from one store in Missouri. Store management and maintenance personnel have conducted a search and have determined that the signs are not on the premises. Wal-Mart last inventoried these signs April 2008 and is declaring these signs to be missing. The device information is as follows: 1. Location: Dexter, Missouri, Serial number - 314882, Curie content - 11.5. 2. Location: Dexter, Missouri, Serial number - 314890, Curie content - Unknown. Notified FSME (Mauer), R4DO (Deese) and ILTAB via email. * * * UPDATE ON 10/28/08 AT 0900 EDT FROM DAILEY TO KLCO * * * Wal-Mart Corporate Office reported a tritium exit sign missing from a store in Virginia. Store management and maintenance personnel have conducted a search and have determined that the signs are not on the premises. Wal-Mart last inventoried these signs April 2008 and is declaring these signs to be missing. The device information is as follows: 1. Location: Norton, Virginia, Serial number - 316467, Curie content - 11.5. Notified FSME (Einberg), R1DO (Cobey) and ILTAB via email. * * * UPDATE ON 10/29/08 AT 1713 EDT FROM DAILEY TO KOZAL * * * Wal-Mart Corporate Office reported a total of 3 tritium exit signs missing from two stores in Michigan, and 1 sign from a store in Indiana. Store management and maintenance personnel have conducted a search and have determined that the signs are not on the premises. Wal-Mart last inventoried these signs April 2008 and is declaring these signs to be missing. The device information is as follows: 1. Store number 1791 Location: 7083 West 48th Street, Freemont, MI 49412, Serial Number: Unknown, Manufacturer - Isolite, Activity - 11.5 Ci. 2. Store number 1791 Location: 7083 West 48th Street, Freemont, MI 49412, Serial Number: 256573, Manufacturer - Isolite, Activity - 11.5 Ci. 3. Store number 2238 Location: 1879 East Sherman Blvd., Muskegon, MI 49444 Serial Number: 254487, Manufacturer - SRB, Activity - 20 Ci. 4. Store number 2339 Location: 2801 North Western Ave, West Lafayette, IN 47906, Serial Number: 295648, Manufacturer - Isolite, Activity - 11.5 Ci. Notified FSME (Einberg), R3DO (Kozak) and ILTAB via email. * * * UPDATE ON 11/05/08 AT 1828 EST FROM DAILEY TO KLCO * * * Wal-Mart Corporate Office reported a total of 2 tritium exit signs missing from one store in Hawaii and 1 sign from a store in Connecticut. Store management and maintenance personnel have conducted a search and have determined that the signs are not on the premises. The device information is as follows: 1. Store number 5274 Location: 1131 Kuala Street, Pearl City, HI 96782, Serial Number: 33526, Manufacturer - Isolite, Activity - 11.5 Ci. 2. Store number 2331 Location: 155 Waterford Parkway North, Waterford, CT 06385, Serial Number: 286501, Manufacturer -SBR, Activity - Unknown Notified FSME (Suber), R4DO (Campbell), R1DO (Caruso) and ILTAB via email. * * * UPDATE ON 11/11/08 AT 0818 EST FROM DAILEY TO KOZAL * * * Wal-Mart Corporate Office reported a total of 2 tritium exit signs missing. One in New Jersey and 1 sign from a store in Virginia. Store management and maintenance personnel have conducted a search and have determined that the signs are not on the premises. The device information is as follows: 1. Store number 1742 Location: 3501 Rt 42, Turnersville, NJ 08012 Serial number: 162266, Manufacturer: Foreverlight, Activity: Unknown. 2. Store number 1726 Location: 171 Burgess Road, Harrisonburg, VA 22801 Serial number: 288780, Manufacturer: SRB, Activity: 20 Ci. Notified FSME (Suber), R1DO (Trapp) and ILTAB via email. * * * UPDATE ON 11/12/08 AT 1432 EST FROM WENDY WIDENER TO JOHN KNOKE * * * 1. Store number 2449 Location: Ave Rafael Cordero Caguas, Puerto Rico 00725 Serial number, Manufacturer and Activity Unknown. 2. Store number 3219 Location: 731 East Rochambeau Rd Williamsburg, VA 23188 Serial number: 275031, Manufacturer: SRB, Activity: Unknown 3. Store number 4755 Location: 750 Ke'eaumoku St. Honolulu, HI 96814 Serial number: 315483, Manufacturer: Isolite, Activity: Unknown. 4. Store number 4755 Location: 750 Ke'eaumoku St. Honolulu, HI 96814 Serial number: 315484, Manufacturer: Isolite, Activity: Unknown. Notified R1DO (Trapp) and R4DO (Whitten), FSME (Burgess), ILTAB email * * * UPDATE ON 11/13/08 AT 1229 EST FROM WENDY WIDENER TO JOHN KNOKE * * * 1. Store number 1811 Location: 1170 North Military Hwy Norfolk, VA 23502 Serial number, 294096 Manufacturer SRB Activity Unknown. 2.Store number 1811 Location: 1170 North Military Hwy Norfolk, VA 23502 Serial number, 294111 Manufacturer SRB Activity Unknown. 3. Store number 3734 Location: 1207 Princeton Street Vermillion, SD 57069 Serial number Unknown, Manufacturer: Isolite, Activity: Unknown. Notified R1DO (Trapp) and R4DO (Whitten), FSME (Burgess), ILTAB by email * * * UPDATE AT 0928 EST ON 12/1/08 FROM WENDY WIDENER TO S. SANDIN * * * 1. Store number 2518 Location: 700 Marketplace Blvd., Hamilton, NJ 08691 Serial number, 280984 Manufacturer SRB Activity 20 Ci Tritium. Notified R1DO (Doerflein), FSME (Burgess) and ILTAB via email. * * * UPDATE AT 1555 EST ON 1/5/09 FROM W. WIDENER TO W. HUFFMAN * * * A Wal-Mart corporate representative reported that Wal-Mart was unable to account for an additional 2439 tritium exit signs (which are general licensed materials) that were used at one time in Wal-Mart stores throughout 14 non-agreement States and the Commonwealth of Puerto Rico. Wal-Mart had previously reported between September 16 and December 1, 2008, to the NRC a total of 29 unaccounted for tritium exit signs in several of the non-agreement states (see also EN #44495). The Wal-Mart representative informed the NRC that they had exhausted their search for the tritium exit signs and considered them to be lost and/or missing. The NRC was provided a listing from Wal-Mart of the store locations along with information on the tritium exit sign manufacturers, model and serial numbers and curie content if known. Notified R1DO (Burritt), R2DO (Blamey), R3DO (Duncan), R4DO (Lantz), FSME EO (Burgess) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2009-01-16
44546 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-10-07 06:35 | 2008-10-07 13:13 | 2008-10-07 | SPECIFIED SYSTEM ACTUATION DUE TO LOSS OF POWER DURING TESTING "On October 7, 2008 at approximately 0635, the James A. FitzPatrick Nuclear Power Plant was shutdown and operating in the Cold Shutdown mode (Mode 4). Testing was in progress on the trip and lockout (86) relay associated with circuit breaker 71-10402, normal station service transformer T-4 feeder breaker to electrical bus 10400. While technicians were performing the test, the 10400 bus, which was feeding power to the 10600 Emergency Bus, lost power. This loss of power to the 10600 bus resulted in an automatic actuation of the 'B' and 'D' Emergency Diesel Generators. The generators started, force paralleled, and closed in to the 10600 Bus as designed. As a result of the loss of the 10600 bus the 'B' Reactor Protection System (RPS) also lost power resulting in a half scram signal and a Group II Primary Containment Isolation System (PCIS) actuation. This actuation resulted in closing containment isolation valves in multiple systems and isolating Reactor Water Clean-up (RWCU). Based on these system actuations the event is reportable under Criterion 10 CFR 50.72(b)(3)(iv). "The event has been entered into the corrective action program and a Licensee Event Report (LER) will be filed within 60 days as required by 10 CFR 50.73(a)(2)(iv). "The [NRC] Resident Inspector has been briefed and the State Public Service Commission (PSC) will also be notified." At the time of the event, the 'B' shutdown cooling system was in service. Shutdown cooling was lost for approximately 35 minutes which resulted in a 6 degree rise in water temperature. At that time, the licensee calculated 19.5 hours to boil. Shutdown cooling has been restored. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-10-07
44545 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-10-06 22:24 | 2008-10-07 03:01 | 2008-10-07 | UNEXPECTED REACTOR CORE ISOLATION COOLING ISOLATION DURING TEST "During performance of PNPS Procedure 8.M.2-2.6.3 Attachment 1 step (65) the RCIC System isolated on a Group 5 signal when relay contact blocking devices (boots) were removed. All isolations went to completion. This isolation was not part of the planned evolution. "The Group 5 isolation was reset and RCIC was placed in stand by line-up at 2327 on 10/6/2008. Investigation is continuing." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-10-07
44544 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-10-06 14:15 | 2008-10-06 16:08 | 2008-10-06 | POTENTIAL SAFEGUARDS VULNERABILITY The licensee discovered a potential failure in a safequard system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operation Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2008-10-07
44543 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-10-06 | 2008-10-06 12:52 | 2008-11-07 | TEXAS AGREEMENT STATE REPORT- SOURCE RETRACTOR FAILED TO FUNCTION The following information was received from the State of Texas via e-mail: "While servicing the level gauge [Ohmart Model A2102, Cs-137], an Ohmart technician discovered that the source retractor failed to function. The source is extended into a polymer vessel and is functioning normally while source is extended. Ohmart will recover the source and remove it from service. The licensee will arrange for disposal and discontinue use of the source." Texas Report I-8570. * * * UPDATE ON 11/7/2008 AT 1138 FROM ART TUCKER TO MARK ABRAMOVITZ * * * This report from the state of Texas was received via e-mail: "The licensee provided the Agency with a report on the investigation they conducted into the cause for the failure of the source to retract into the source holder on November 4, 2008. That report provided the following information. "The gauge has been in place on the vessel since 1998. It appears that the source has not been retracted back into the source holder in a number of years. The source well is three feet deep and the total clearance between the source and the well wall is 0.322 inches. "The source well is in a section of the vessel that contains a very thick, almost hardened, polymer material. The vessel was initially used to contain a polymer slurry, but the vessel's use was changed shortly after start up. This change resulted in the hardened polymer to form in the vessel. These actions all took place prior to the current owner taking possession of the facility. "The licensee had tried to retract the source back into the source holder, but it only moved a distance of between 12 and 18 inches before it became stuck. The manufacturer's technician was able to move the source back to the end of the source well. This is the normal position for the source. It is believed that the weight of the polymer over the years has caused the well to bow to a point where it now limits the movement of the source. "The licensee intends to remove and dispose of the source during a scheduled outage in 2009. The gauge is located at a height of 12 feet above grade. Dose rates taken at a height of 8 feet indicate a dose rate of 0.01 to 0.1 millirem per hour. "Additional information regarding accessibility and occupancy of this area has been requested by the state." Notified the R4DO (Campbell) and FSME (Suber). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-10-09
44542 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-10-06 04:45 | 2008-10-06 04:49 | 2008-10-06 | UNAVAILABILITY OF TSC VENTILATION SYSTEM AND CHARCOAL FILTER FOR SCHEDULED MAINTENANCE "At 0445 on Monday, October 6, 2008, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system and charcoal filter was removed from service for scheduled preventive maintenance. The charcoal bed filtration system is also out of service in support of the maintenance on the TSC ventilation system. "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "The TSC ventilation system maintenance is scheduled to complete at 16:00 on Monday, October 6,2008. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." * * * UPDATE AT 1630 EDT ON 10/06/08 FROM TOD KASPAR TO HOWIE CROUCH * * * "The TSC Ventilation System and Charcoal Filter was returned to functional status at 14:35 on Monday, October 6, 2008. "This follow up notification is being made to provide closure from the initial notification under 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lara). | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-10-06
44541 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-10-05 04:31 | 2008-10-05 12:17 | 2008-10-05 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE "During repair activities associated with the HPCI NUMAC [Nuclear Measurement Analysis And Control] display, the NUMAC drawer failed upon restoration of power. The drawer failure resulted in HPCI isolation signal and [HPCI] turbine trip signal. At the time the HPCI isolation valve was de-energized as planned so the isolation did not occur, but the failure mode resulted in a [HPCI] turbine trip signal, which resulted in an unavailability and inoperability of HPCI. The condition existed for 29 minutes during maintenance activities. Repair activities were unsuccessful and the NUMAC is still inoperable." The event occurred during the restoration of the HPCI steam leak detection system. The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-10-05
44540 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-10-04 22:08 | 2008-10-05 01:16 | 2008-10-05 | REACTOR SCRAM FOLLOWING REVERSE POWER SIGNAL ON MAIN GENERATOR "On 10/04/08 at 2008 [CDT] the Unit 2 reactor scrammed due to turbine generator reverse power signal on the Main Generator. The cause of the reverse power signal is unknown and the investigation is continuing. All systems responded as expected to the generator reverse power signal. Reactor pressure was automatically controlled by the Main Turbine bypass valves. No Emergency Core Cooling System (ECCS), nor Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached, and reactor water level is being automatically controlled by the feedwater system. This report is being made as required by 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The licensee characterized the scram as uncomplicated. All control rods fully inserted. No safety valves lifted during the transient. All safety systems were available at the time of the scram. There were no impacts on Units 1 or 3. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-10-05
44539 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2008-10-03 18:21 | 2008-10-03 19:52 | 2008-10-17 | TRUCK SHIPMENT EXTERNAL RADIATION LEVELS EXCEED LIMITS "Received Shipment from Pilgrim Station of temporary lead shielding that exceeds 10 CFR 20 requirements for a non-exclusive use limited quantity shipment of 0.5 mR on contact. "Receipt inspection readings of the last container in the shipment measured between 1.3 mR and 1.85 mR (taken via 3 readings, using 3 separate meters and 2 different technicians). "Per 10CFR20 subpart 1906 paragraph D, which states: (d) The licensee shall immediately notify the final delivery carrier and the NRC Operations Center (301-816-5100), by telephone, when -- (1) Removable radioactive surface contamination exceeds the limits of section 71.87(i) of this chapter; or (2) External radiation levels exceed the limits of section 71.47 of this chapter." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 10/17/2008 AT 1309 EDT FROM D. MAY TO R. ALEXANDER * * * "NRC Notification 44539 was conservatively made due to conservative procedural guidance. "10 CFR 20.1906(d)(2) requires immediate notification of the final delivery carrier and the NRC Operations Center when external radioactive levels exceed the limits of section 71.47 of this chapter. The reporting threshold contained in 10 CFR 71.47 is 200 mR [per hour] at any point on the external surface of the package. Since actual measured levels were between 1.3 mR [per hour] and 1.85 mR [per hour] this event is not reportable. "ENS Event Number 44539, made on 10/03/08, is being retracted." The NRC Resident Inspector will be notified by the licensee of this retraction. Notified R1DO (Jackson) & NMSS EO (Regan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2008-10-03
44538 | 0 | NAMCO |  |  |  |  | 2008-09-19 | 2008-10-03 14:06 | 2008-10-03 | PART 21 REPORT - THREAD SEALANT The following information was received from NAMCO via facsimile: "On September 19, 2008, Namco determined that it had shipped product that did not meet the customer purchase order requirements. Namco supplied clear thread sealant instead of white thread sealant. The thread sealants are the same except that the white has an additional pigmentation additive. Namco began an evaluation and on September 29, 2008, determined that it did not have the capability to determine the impact to the supplied users. Therefore in accordance with 10CFR Part 21, Namco provided notification [to the NRC and the affected licensees]." Namco has reviewed previous purchase orders of thread sealant and determined that the affected users are TVA-Watts Bar Nuclear Plant, Dominion Nuclear Connecticut, Ameren-Callaway Plant and Alabama Power-Farley Nuclear Plant. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2008-10-03
44537 | 0 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2008-09-08 | 2008-10-03 14:45 | 2008-10-03 | LOST I-125 SEED "One I-125 sealed source ('seed') intended for permanent prostate implantation on 9/8/08 cannot be located definitively inside the patient or inside the hospital and is assumed lost. The calibrated activity was 0.481 mCi on 8/25/08. "On the morning of 9/8/08, a permanent prostate implant was performed in our high dose rate (HDR) treatment room in Radiation Oncology under sterile conditions. The implant was to consist of 62 seeds, in twenty needles each containing a varying number of seeds of 0.408 milliCurie of I-125. Seventy I-125 seeds were ordered and pre-loaded in a cartridge and were received sterilized from Isotron. Prior to treatment, one of the seeds was expelled from the cartridge and used for calibration. It was stored in a separate shielded container, and not used in the patient treatment. "The written directive and treatment plan intended implantation of 62 I-125 seeds into a patient's prostate for the treatment of cancer. Using the Nucletron seedSelectron remote afterloading system, each needle was placed under ultrasonic guidance in the patient's prostate. The seedSelectron was connected to each needle and the seeds ejected from the cartridge into the needle. This procedure was performed for each of the twenty needles with only one needle being implanted at a time injecting a total of 62 seeds. The treatment progressed normally as planned and was successfully completed. At the conclusion of the treatment, X-rays were taken to verify the number of seeds implanted, and the count of 61 instead of 62 was confirmed radiographically. Prior to exiting the room, all staff (radiation oncologist, nurse, physicist, brachytherapy specialist) completed the routine required survey which included the soles of the shoes. "The residual seeds in the cartridge were x-rayed and seven I-125 seeds were identified by at least 3 medical physicists. At least 3 medical physicists and the authorized user examined the patient's x-rays, and each could clearly identify only 61 seeds in the patient. The one I-125 seed used for calibration was accounted for in the inventory. The patient was scheduled to return for bi-plane views on 9/10/08, so that additional radiographs could potentially identify the missing seed. When the patient returned on 9/10/08, he had excreted four I-125 seeds which were properly handled and placed in the secure designated storage area. On the follow up x-rays, only 57 seeds were clearly identified. The anatomy surrounding the prostate was also imaged, but only 57 seeds were clearly identified. The entire pelvic region, abdomen and chest were also imaged with no results. It is possible that the seed may have migrated to an area inside the patient which was not included on the follow up x-rays. "The pre-loaded cartridge of seeds was not x-rayed prior to the treatment, so the presence of all 70 seeds was not confirmed prior to the treatment. It is conceivable that only 69 seeds were shipped. We contacted Isotron and they provided us with their documentation showing that they shipped 70 seeds. "The most probable disposition is that the seed is located inside the patient, but has migrated to an area which does not allow us to confirm its presence radiographically. The second most likely explanation is that we only received 69 seeds instead of 70 seeds. It is unlikely that the seed is lost inside our HDR suite, given the normal progression of the implantation procedure and the thoroughness of our search. It is very unlikely that the seed was disposed of in the landfill or sewer, since it was not detected when the team of medical physicists individually surveyed each item of linen and trash, and thoroughly surveyed the sink. "No exposure of individuals to radiation from the one missing I-125 in restricted and unrestricted areas is expected. "A thorough search was initiated immediately, using a pancake thin end window Geiger-Mueller detector in the micro-R/hr range (Ludlum Model 14C, calibrated on June 4, 2008). The surgical table, floor, each item of trash, each item of linen and all personnel were carefully surveyed. All cartridges and needles were rechecked several times. A thorough survey of the surgical table was conducted, urine collection bag and patient (even near the pelvis, although exposure from the implant made detection in this vicinity unlikely). The low survey readings in adjacent areas of the patient made it unlikely that the seeds were on the patient. The patient was released and removed from the HDR room and transferred to Phase I recovery. The survey also included the entire entrance hallway to the HDR room and the radiation oncologist's office. The Radiation Safety Officer designate for Radiation Oncology was notified and an additional survey of the room was conducted with the Johnson survey instrument (GSM-15) with a plastic scintillator (GLE-1), calibrated with an I-125 source on January 4, 2008. The surface of the floor including the small cracks in the floor covering and at the baseboards was surveyed. Each item of trash and linen was checked separately. The Corporate Radiation Safety Officer was notified and conducted an independent search with the Johnson survey instrument which included the entire floor, baseboards, sink, each item of equipment in the HDR room, the linen and trash. When nothing was found, the room was released so that patient treatments could be resumed in the room. A repeat survey of the patient using a Geiger-Mueller detector in the microR/hr range (Victoreen model 190 with pancake probe, calibrated April 24, 2008) as well as the areas surrounding the patient, trash and linens was performed in the Phase I area. All readings were low indicating the source was not in the vicinity. The patient was then discharged to Phase II. A survey including the patient, stretcher, linens, trash, urinary catheter, urinary bag and area was performed in Phase II. Low readings were again observed indicating the source was not in the area. The unused seeds were returned to the locked cabinet in the other HDR room for inventory and storage. "Procedures or measures that have been, or will be, adopted to ensure against a recurrence of the loss of licensed material: (1) All personnel involved with prostate implants will receive refresher training regarding proper procedure. (2) An image of the loaded cassette will be taken to verify the receipt of the correct number of seeds. This image will be retained along with the patient records. In the event the seed count on the image does not agree with the count per the manufacturer, the situation will be reconciled prior to treatment. (3) Every effort will be made to obtain a seed count that accounts for all of the seeds received from the manufacturer prior to the discharge of the patient." The licensee has reported this event to NRC Region III. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-10-03
44536 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-10-03 | 2008-10-03 11:40 | 2008-10-17 | AGREEMENT STATE REPORT - DEFECTIVE COMPONENT THAT COULD POTENTIALLY CAUSE A SUBSTANTIAL SAFETY HAZARD The following information was received from the State of Massachusetts via email: "Prompted by a reported event, Event Number 44434, QSA Global conducted an investigation of a Model 660B camera. QSA Global concluded that the root cause of the event was a defective component on the pigtail of the camera, and has determined that more cameras contain these defective components which could contribute to future events. " "This defect could give the user the false impression that the source is connected to the drive cable when there is only a partial connection. The operations manual does require that the user check the connection prior to use and when this is done, there is no problem. However if the user does not do a check of the connection, it may not be secure and may cause the source to disconnect in the guide tube. "The defective component was reported to the State of Massachusetts under Massachusetts code 105 CMR 120.142(B)(2)(a). The defective component is a female source connector, QSA part number 55042-1. This defect was only found in lot 0731300805. QSA sold six Co-60 sources [Model 424-14] and 659 Ir-192 [Model 424-9] sources that utilized connectors from this lot. One Co-60 source will be returned to QSA for evaluation due to a source retrieval event. "[QSA Global] Corrective Actions: Customers who had received the other five Co-60 source wires from the suspected lot were contacted and arrangements were made to make a field inspection of these sources by QSA Global staff for the potential defect. Any defective source wires would be recommended to the customer for return and replacement by QSA Global. "Customers who had received one of the 659 Ir-192 source wires that contained the suspected lot were notified and advised of this potential condition. These customers were provided with [a] notification which re-enforces the need to ensure a solid connection between the drive cable and the source prior to making any source exposures. The customer notification letter includes inspections the customer should make to determine if their source may contain this defect and advises the customer to contact QSA Global if a source is suspected of being defective to arrange for source replacement. "It was decided that the supplier of the defective lot would be removed from the approved supplier list pending further evaluation of their production processes. This will prevent their use as a supplier for components (including Class A components) until their evaluation and re-approval at a later date." * * * UPDATE ON 10/17/08 AT 1036 EDT FROM J. SUMARES TO R. ALEXANDER * * * "On 10/13/08, QSA Global notified the Agency [Massachusetts Radiation Control Program] of a second Part 21 defect for the Model 550 connector that created a source disconnect in WA [Washington], reference event notification #44552. The defect was discovered on a second component of the 550 connector, the inner sleeve. The circular recess for the ball of the male connector was undersized per specifications and prevented the ball to fully seat into the female connector and making it easier for the source wire to disconnect. "QSA Global submitted a preliminary report for the inner sleeve stating: "1. All inventory of connectors using this defective lot of sleeves were 100% re-tested and defective parts were removed from inventory. "2. As of 10/15/08, affected customers are being notified of potential problems and will be advised to conduct inspections of male to female connections of the Model 550 connector to ensure a full engagement. Any suspect connections may be returned to QSA for evaluation and replacement. "3. All remaining lots of components (sleeves, other components) from this supplier are quarantined for re-inspection or scrap. "4. This supplier has been suspended from use. "Further evaluation and investigations of the inner sleeves are on-going." Notified FSME (Einberg & Jankovich), R1DO (Jackson), R2DO (Vias), R3DO (Phillips), & R4DO (Hay) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-10-08
44535 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-09-29 13:00 | 2008-10-03 10:58 | 2008-10-21 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO EXTREMITIES A radiographer working for METCO was performing radiography operations at CB & I Fabricators in Houston TX. He was moving the radiography camera (a SPEC 150 with a 85 curie Ir-192 source) from one location to another. He removed the nipple off the front of the camera to test the guide tube and his dosimetry started alarming. He observed that the source had come out of the camera about 1/2 inch. At the same time, he inadvertently dropped the camera plug. He picked up the plug and unsuccessfully made two attempts to push the source back in with the plug. He then left the front of the camera and went around and turned the crank and got the source back into the shielded position and then inserted the plug. He then notified appropriate personnel. METCO sent his dosimetry off and the results came back with a whole body exposure of 946 millirem on October 1. The RSO discussed the details of the event with the radiographer and reenacted the event to attempt to estimate the radiographer's hand exposure because to the close proximity of the source to the hand during the event. Based on the time and distance of the source to the hand, it was estimated that the exposure to the radiographer's right hand may be somewhere between 66 and 282 rem. METCO has called in a consultant to get a more accurate assessment of the exposure to the hand. The radiographer's work for the rest of the year has been suspended. His hand does not exhibit any eurythemia. No information is available on whether blood work or medical study will be obtained. Texas will wait for the licensee's final report before it completes and independent investigation of the event. Texas Report I-8569 * * * UPDATE PROVIDED AT 1210 EDT ON 10/21/08 FROM ART TUCKER VIA EMAIL TO JEFF ROTTON * * * The following information was received from the State of Texas via email: "The licensee provided the final dose estimate for the individual involved in this event. The licensee used conservative times established in several reenactments of the event, NCRP publications, and the source manufacturers information to calculate the dose estimate. The estimate to the individual's right hand is 233.71 Rem SDE. The State of Texas calculated the dose to be 235.65 Rem SDE. This individual's TEDE dose was measured at 2.762 Rem for the 2008 calendar year. Notified FSME (Burgess) and R4DO (Deese). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-10-08
44533 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-10-02 09:15 | 2008-10-02 12:03 | 2008-10-02 | POSITIVE FITNESS FOR DUTY TEST A non-licensed contract employee supervisor had a confirmed positive for alcohol during a follow up fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2008-10-02
44532 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-09-30 16:00 | 2008-10-01 12:30 | 2008-10-01 | POSITIVE RANDOM FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access for the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.719 |  |  |  | 0 | 2008-10-06
44531 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-09-25 | 2008-10-01 12:24 | 2008-10-16 | CALIFORNIA AGREEMENT STATE REPORT - LEAKING NI-63 SOURCE "On September 25, 2008, a leak test was performed on a nickel-63 source in an Electron Capture Device (ECD) which was found to have removable contamination of 89 nanoCuries, which is above the reporting requirement of 5 nanoCuries in CA Title 17, section 30275. The ECD is not in service, it has been in storage for two years and in the Environmental Health and Safety waste facility [at the University of California - San Diego (UCSD)], awaiting disposal. We [the California Department of Public Health] have notified UCSD to return the device to Agilent Technologies, in Delaware for their analysis. "Manufacturer: Hewlett Packard; original activity: 15 mCi; current activity: 13.44 mCi; reference date 12/1/1992, source model number G1223A, serial number F5350. "SSD registry NR-0348-D-111-B, currently made by Agilent Technologies in Delaware under NRC authority. "Gas Chromatograph Information: Manufacturer- Hewlett Packard, Model 5890 Series II." The State of California considers this a potential Part 21 issue. California Incident Number: 5010-093008. * * * UPDATE RECEIVED VIA E-MAIL FROM B. HAMRICK TO JOE O'HARA AT 1257 EDT ON 10/16/08 * * * "This is to update the report made 10/1/08 regarding a leaking Agilent Ni-63 source. After review, it was determined that this event is not a 24-hour reportable event for the California Agreement State program, and should have been reported pursuant to 10 CFR 31.5 (30-day report). By copy of this email, we are also notifying Randy Erickson, in Region IV, since the event may require NRC review, because the SS&D sheet for this source was issued by NRC to an NRC licensee." Notified R4DO(Hay), FSME(VonTill) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-10-06
44530 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2008-09-30 19:42 | 2008-09-30 20:44 | 2008-09-30 | LOSS OF PRIMARY OFFSITE NOTIFICATION CAPABILITY "Loss of the Ames Hill NOAA transmitter [due to an] interrupted phone link between Albany and Ames Hill. Caused by a 'corruption' of the AT&T phone line between Albany and Ames Hill. This condition interrupted/interfered with the radio [frequency] link between WTSA radio station and the Ames Hill transmitter. "Turn[ed] off corrupting phone lines interfering with radio frequency communications between Ames Hill transmitter and WTSA radio station. AT&T [was] contacted to repair phone line." The normal configuration is the phone line is used for the primary signal and the radio link to WTSA radio station is for backup capability. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE @ 2214 EDT ON 9/30/08 FROM JEFFRIES TO CROUCH * * * The licensee reported that offsite notification capability was restored at 2105 EDT by disconnecting the corrupted phone line which automatically switched the radio signal to WTSA radio station as the primary signal for activation. The radio station performed a silent test to verify functionality. The licensee will be notifying the NRC Resident Inspector of this update. Notified R1DO (White). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-30
44529 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-09-29 | 2008-09-30 16:50 | 2008-10-23 | WASHINGTON AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The State of Washington provided the following information via e-mail: "The licensee reported to the Washington State Department of Health (DOH) that a Troxler 3440 nuclear density gauge, serial number 28433, with 8 mCi of Cs-137 and 40 mCi of Am-241/Be, was struck by a truck at a landfill site at about 12:45 p.m. on 9/29/08. The gauge was struck while the operator was taking measurements with the source rod extended into the soil. It was reported that a truck tried to skim by the operator and gauge, narrowly missing the operator and hitting the gauge. The truck caught the gauge handle breaking it and the guide rod from the gauge. The source rod and the rest of the gauge remained intact and in place. The licensee field engineer and lead gauge operator went to the scene to assist with the incident. Since the handle was broken from the gauge, the source rod was placed back into the gauge by turning the gauge on its side and striking the bottom of source rod with a mallet. This action caused the source rod to move completely out of the top of the gauge. The lead individual put the source rod into a bucket and found a max reading of 20 mR/hr. The lead [operator] returned the source rod back into the shielded position in the gauge and secured [it] in place with duct tape. Additional wraps of duct tape were made around the top and bottom of the gauge to keep the source rod from coming out again. A reading of 2.4 mR/hr was found on contact with the gauge with the licensees' TroxAlert. Additional readings were taken on the bucket and the testing site indicating background readings. The gauge was placed back into the transport case and taken to the licensed storage location prior to determining its final disposition. DOH staff will visit the licensee to make confirmatory measurements and start an investigation." Washington Report Number: WA080072 * * * UPDATE PROVIDED AT 1717 EDT ON 10/23/08 FROM STATE (CLARK) TO JEFF ROTTON * * * The following information was provided by the State of Washington via email: "Two DOH staff visited the licensed storage location and investigated the incident on 09/30/08. After interviewing the operator, the field engineer and the RSO, the staff inspected the damaged gauge. The gauge was removed from its transport box and placed on a table for inspection. The gauge had been duct taped with the source rod in position to keep the shutter closed. The majority of the gauge was intact; a small piece of the T handle had been broken off and was separate from the gauge. DOH staff surveyed the gauge with several instruments. An Eberline RO-2 (serial number 2587, cal date 05-07-08) reported a surface contact reading of 6 mR/hr. A Ludlum 2363 neutron/gamma instrument reported a surface contact rate of 5 mRem/hr. The gauge was then turned over and the orifice was surveyed. The Eberline reported 20-22 mR/hr, which is higher than normal, and the Ludlum reported 13 mRem/hr. The shutter appeared to be only 3/4 closed. The T handle was manipulated to return the shutter to a completely closed position and duct taped into place. The orifice of the gauge than read 4 mR/hr with the Eberline. DOH staff than took two swabs, one of the sources (with rod extended) and one in the transport case. Both swabs were taken out of the area and surveyed with RADALERT Inspector SN 21089. The swabs did not indicate any contamination so it appears the cesium source was not leaking. The gauge was then carefully placed back into its transit box and the box was surveyed at a distance of one meter to determine the transport index (TI). A TI of 0.6 was marked on the label. The gauge was shipped back to Troxler for repair and leak testing." Notified R4DO (Deese) and FSME (Mauer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-10-03
44528 | 0 | HALLIBURTON ENERGY SERVICES INC |  |  |  |  | 2008-09-30 | 2008-09-30 16:09 | 2008-12-05 | SOURCES LOST AT SEA WITH DRILLING RIG "Please accept this as the preliminary notification of two devices which are currently being searched for as a result of the recent hurricane activity in the Gulf of Mexico. The devices are located on drilling rig ENSCO 74 however the rig has not been located. The rig owner is currently searching for the rig. The status was reported as follows: Ensco 74 "Legs are still on location leaning over. Legs appear to have broken off below barge. "Rig has not been located yet. "Since rig was in SMI 149 this block is close to deeper water and may be afloat or on bottom. [NOTE: this location is off the Louisiana coast] "This rig has two densometer V32-0571 with source XA-417 and W25-599 with source DB-455 both are 10 mCi Cs-137 sources. I will advise when the rig is located either above or below water." * * * UPDATE RECEIVED VIA E-MAIL FROM S. WOODS TO V. KLCO AT 1520 EST ON 12/05/08 * * * "Ensco Offshore Company has abandoned the search efforts for their rig the Ensco 74 which the two below referenced devices were located. With that information, we do not believe that the devices will be recovered and should be considered lost due to the hurricane activity." Notified R4DO (D. Proulx) and FSME (C. Einberg) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-09-30
44527 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-09-29 10:09 | 2008-09-29 15:15 | 2008-09-29 | OFFSITE NOTIFICATION DUE TO DISCHARGE OF OIL INTO NAVIGABLE WATERS "Notified by the Operations Incident Commander at 1009 CDT that a sheen of oil is visible on the Kankakee River north of the Goose Lake pumping station. It is estimated that 1 gallon may have been discharged to the Kankakee River. "The leak was from a temporary diesel driven pump that was in place due to the recent flooding in the area. The pump has been secured and has been moved from the area. "Notified the Illinois Emergency [Management] Agency (IEMA) of the fuel oil spill to the Kankakee River. IEMA incident report number H20081478. Reported to Agent [DELETED] at 1023 CDT. "Notified the National Emergency Response Center of the oil spill to the Kankakee River. Incident report #885611. Reported to [DELETED] at 1055 CDT." The licensee made the reports based on the requirements of the Federal Water Pollution Act, Section 311(b)(5), 40 CFR 110.5 and 40 CFR 112.4. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 94 | 0 | 0 | 94 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-09-29
44526 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2008-09-29 09:18 | 2008-09-29 14:45 | 2008-09-29 | LOSS OF INTERNAL PHONE SYSTEMS "A loss of internal phone systems was experienced at the station on 9/29/08 at 0918. This loss included the ENS phone line. Compensatory measures using cellular phones were established with the NRC. The phone outage did not affect the emergency plan state and local notification system. This event had no adverse affect on plant operations. Intermittent phone outages are expected until the issue is resolved. Maintenance is ongoing to investigate and correct the cause." The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-29
44525 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2008-09-27 21:51 | 2008-09-28 02:35 | 2008-09-28 | UNIT 3 REACTOR MANUALLY TRIPPED FOLLOWING AUTOMATIC TURBINE TRIP ON HIGH VIBRATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS under the reporting requirements of 10CFR50.73. "On September 27, 2008, at approximately 21:51 Mountain Standard Time (MST) Palo Verde Unit 3 operators manually tripped the reactor from approximately 34% rated thermal power in response to an automatic trip of the main turbine. The unit was being shutdown from 100% power due to a chemistry excursion in the secondary plant. Following the manual reactor trip all CEAs fully inserted into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 3 is stable at normal operating temperature and pressure in Mode 3. Decay heat removal is via the Steam Generators and Main Feedwater to the Main Condenser using the Steam Bypass Control System. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The main turbine tripped on high vibration. "The Senior Resident Inspector was informed of the Unit 3 reactor trip." | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-09-28
44524 | -1 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2008-09-26 | 2008-09-26 18:15 | 2008-12-02 | MEDICAL DOSE LESS THAN 80% OF PRESCRIBED DOSE "In response to medical events discovered at the VA Medical Center Philadelphia, which have been reported under Event Number 44219, reviews are ongoing of samples of patient charts from other VA facilities with permanent prostate seed implant brachytherapy programs. "As the result of these ongoing reviews, possible medical events were discovered on September 26, 2008, for 3 patients treated at the VA Medical Center in Washington DC. "These 3 possible medical events involved seed distributions in the patients that may result in D90 doses less than 80% of the prescribed doses. These circumstances may meet the definition of a medical event under 10 CFR 35.3045. (The D90 is the dose that covers 90% of the volume of the prostate.) "The VHA National Health Physics Program will ensure that the medical center follows NRC requirements for notification of the patients. These treatments and their possible effects on the patients will be reviewed by medical experts. "A 15-day written report on these 3 possible medical events will be submitted to NRC Region III pursuant to 10 CFR 35.3045. We will notify our NRC Project Manager, Cassandra Frazier (NRC Region III), of these possible medical events. "The US Department of Veterans Affairs has a Master Materials License (MML) from the NRC: License No. 03-23853-01VA. Permits are issued under the MML to VA facilities. The VA submits reports to the NRC through the VHA's National Health Physics Program office located in North Little Rock, AR. "Address of permittee involved in this event: VA Medical Center, 50 Irving Street NW, Washington DC 20422. "The VHA permit number of the permittee involved in event: Permit No. 08-00942-05." * * * UPDATE AT 1030 EST ON 12/02/08 FROM THOMAS HUSTON TO S. SANDIN * * * The licensee is retracting this report based on the following: "We are making this notification to retract medical events reported earlier under Event No. 44524. During a reactive inspection, the VA Medical Center in Washington, DC, provided the VHA National Health Physics Program with revised dose information indicating D90 doses were greater than 80% of the prescribed dose for all three patient treatments. "We will notify our NRC Project Manager (Cassandra Frazier, Region III) of this retraction." Notified R3DO (Kunowski) and FSME (Burgess). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-10-02
44523 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-09-26 | 2008-09-26 17:24 | 2008-09-26 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "The licensee's Radiation Safety Officer (RSO) called and informed the Agency [Texas Department of State Health Services] that a moisture density gauge had been damaged while it was being used at a work site. The worker had stored the sources in the safe condition and left the gauge at the side of the road he was working on to get a drink of water. Before he returned to the gauge, it was struck by a truck passing by on the road and the gauge rod on the top side of the gauge was bent and the gauge case was damaged. The sources both remained shielded. A service company (Component Sales) has been called to pick up the gauge and conduct an inspection of the device. The gauge is a Troxler Model 3440 ser # 23586 containing a 8 millicurie Cesium (Cs) 137 source and a 40 millicurie Americium (Am) - 241 Beryllium source." Texas Incident # I-8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-10-01
44522 | 0 | VA MEDICAL CENTER JACKSON |  |  |  |  | 2008-09-24 | 2008-09-25 20:12 | 2008-12-17 | MEDICAL DOSE LESS THAN 80% OF PRESCRIBED DOSE "In response to medical events discovered at the VA Medical Center Philadelphia, which have been reported under Event Number 44219, reviews are ongoing of samples of patient charts from other VA facilities with permanent prostate seed implant brachytherapy programs. "As the result of these ongoing reviews, possible medical events were discovered on September 24, 2008, for 7 patients treated at the VA Medical Center in Jackson, Mississippi. "These 7 possible medical events involved seed distributions in the patients that may result in D90 doses less than 80% of the prescribed doses. These circumstances are interpreted as meeting the definition of a medical event under 10 CFR 35.3045. (The D90 is the dose that covers 90% of the volume of the prostate.) "The VHA National Health Physics Program will ensure that the medical center follows NRC requirements for notification of the patients. These treatments and their possible effects on the patients are under review by medical experts. "A 15-day written report of these 7 possible medical events will be submitted to NRC Region III. We will notify our NRC Project Manager, Cassandra Frazier (NRC Region III), of these possible medical events. "Additional Information "Department of Veterans Affairs has a Master Materials License (MML) from the NRC: License No. 03-23853-01VA. Permits are issued under the MML to VA facilities. The VA submits reports to the NRC through the VHA's National Health Physics Program office located in North Little Rock, AR. "Address of permittee involved in this event: VA Medical Center, 1500 East Woodrow Wilson Drive, Jackson, Mississippi 39216. "VHA permit number of permittee involved in event: Permit No. 23-08786-01." * * * UPDATE AT 1945 ON 10/8/2008 FROM EDWIN LEIDHOLDT TO MARK ABRAMOVITZ * * * "This report is an update to Event Report Number 44522. As the result of an ongoing review, an additional possible medical event was discovered on October 7, 2008. This brings the total number of possible medical events to eight (8) under Event Report Number 44522. The circumstances are similar to those previously reported for this event number. "A 15-day written report of this additional medical event will be submitted to NRC Region III. We will notify our NRC Project Manager, Cassandra Frazier (NRC Region III) of this additional possible medical event." Notified the R3DO (Lara) and FSME (Einberg). * * * UPDATE AT 1058 EDT ON 10/30/08 FROM HUSTON TO CROUCH * * * "This report is an update to Event No. 44522. An additional medical event was discovered on October 29, 2008, for a patient treated at the VA Medical Center in Jackson, Mississippi. "This medical event involved a patient who had undergone permanent implant prostate seed brachytherapy using iodine-125 seeds. The resulting seed distribution in the patient was associated with a D90 dose to the treatment site that was less than 80% of the prescribed dose. The circumstances were interpreted to meet the definition of a medical event under 10 CFR 35.3045(a)(1). "A total of eight (8) events have been previously reported to the NRC under this event number. This additional event brings the total number of events to nine (9) for this facility. "A 15-day written report on this additional medical event will be submitted to NRC Region III. I have notified our NRC Project Manager, Cassandra Frazier (NRC Region III), of this additional medical event." Notified R3DO (Kozak) and FSME (Burgess). * * * UPDATE AT 1235 EST ON 12/17/08 FROM HUSTON TO CROUCH * * * "This report is an update to Event No. 44522. One additional medical event was discovered on December 16, 2008, for a patient treated at the VA Medical Center, Jackson, Mississippi. "This medical event involved a patient who had undergone permanent implant prostate seed brachytherapy using iodine-125 seeds. The resulting seed distribution in the patient was associated with a D90 dose to the treatment site that was less than 80% of the prescribed dose. The circumstances were interpreted to meet the definition of a medical event under 10 CFR 35.3045(a)(1). "A total of nine (9) events have been previously reported to the NRC under this event number. This additional event brings the total number of events to ten (10) for this facility. "A 15-day written report on this additional medical event will be submitted to NRC Region III. We have notified our NRC Project Manager, Cassandra Frazier (NRC Region III), of this additional medical event." Notified R3DO (Skokowski) and FSME (Flannery). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | MS | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-10-01
44521 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2008-09-25 07:20 | 2008-09-25 20:03 | 2008-09-25 | 24 HOUR NOTIFICATION OF THE DISCOVERY THAT A SPARK ARRESTOR FOR HEPA FILTER FIRE CONTROL WAS NOT INSTALLED Event Description "At 0720 hours on 9/25/2008, the Engineer responsible for the HVAC system informed a member of the EHS&L ISA Staff that the K-3 ventilation system did not have one of the two required wire-mesh spark arrestors, which we believe had never been installed. Safety Significance "The safety significance of this condition is low. The missing wire-mesh spark arrestor is one of the components of IROFS [Item Relied On For Safety] 4530, which is one of two IROFS associated with an intermediate consequence environmental release as defined in 10CFR 70.61. The initiating event for this accident sequence includes failure of IROFS 4502 (control of combustible material and ignition sources) and a resulting fire that destroys a primary HEPA filter. This initiating event is listed as a 100-year event in the facility ISA. IROFS 4530 is expected to prevent a significant radiological release if the initiating event, a small fire that destroys a primary filter, occurs thereby challenging the integrity of the final bank of HEPA filters. The components of IROFS 4530 include HEPA filters which meet the resistance to heated air and spot flame resistance requirements of sections FC-5150 and 5160 respectively of ASME AG-1, and wire-mesh spark arrestors between the primary and final HEPA filters. "ASME AG-1 section FC-5150 requires filters meeting this design criterion to be exposed to air heated to 700 +/- 50 degrees for not less than 5 minutes without catching fire. Section FC-5160 requires filters meeting this design criterion to have the frame, filter media, filter pack, and sealing materials exposed to a 2.5 inch blue flame (1750 +/- 50 degrees F) for not less than 5 minutes without sustaining combustion. "In addition, if these IROFS are not available to perform their function, the enabling condition needed for an intermediate environmental consequence event is more than a total of 116 kg of uranium be present in the primary and final HEPA filters involved in the postulated fire. The uranium is conservatively assumed to be relatively higher activity blended low-enriched uranium (BLEU), i.e. high enriched uranium blended down to 5% 235U or less. The likelihood of all the uranium on the filters being BLEU material is low. "Since 1995, primary HEPA filters in the K-3 system have been replaced over 1,600 times. Of these, only 6 have contained more than 2 kg of U. The highest contained about 2.7 kg. Immediate Corrective Actions "The differential pressures of the HEPA filters in the K-3 system were verified to be in acceptable ranges, indicating normal loading. "A fire-watch was instituted to further limit potential ignition sources and to assure minimal amounts of combustible materials are used near, or in areas serviced by, the K-3 system. "Wire-mesh to be used in fabricating a spark arrestor has been ordered for expedited installation. Planned Actions "A wire-mesh spark arrestor is expected to be installed Saturday, October 4." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-09-25
44520 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2008-09-25 08:45 | 2008-09-25 17:52 | 2008-09-26 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A moisture density gauge was stolen from the J.A. Cesare company in Henderson, NV between 0300 and 0500 on 9/25/2008. A state investigator is at the scene but has not reported details of the theft at this time. Serial Number: MD90204856 Sources: 10 mCi Cs-137 and 50 mCi Am-241/Be Additional information will be reported on 9/26/2008. * * * UPDATE ON 9/26/08 AT 1713 EDT FROM MATUS TO HUFFMAN * * * The State reports that the stolen moisture density gauge has been recovered by police at a pawn shop. The gauge had not been tampered with and has been returned to the licensee's RSO. It was determined that the gauge was left in a company vehicle in the licensee's parking lot when it was originally stolen. The State also noted that the gauge was actually a CPN Model MC-1DR (preliminary information had indicated that the gauge was a Troxler). Notified R4DO (Jones), FSME (Tadesse), and ILTAB (e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2008-09-30
44519 | 0 | MALLINCKRODT INC |  |  |  |  | 2008-09-21 | 2008-09-25 17:00 | 2008-09-25 | IODINE-131 CAPSULE IN SHIELDED CONTAINER MISSING DURING SHIPMENT Mallinckrodt reports that four Iodine-131 capsules were packaged and shipped to a consignee in Panama City, Panama on September 20, 2008. Each of the four capsules contained 18.7 millicuries of I-131 and were package separately in approximately 20 lb shielded containers. The shipment departed on a flight from St. Louis Airport which arrived in Miami, Florida at which point the packages were transferred to another flight that departed Miami and arrived at Panama City at approximately 1900 EDT on September 20, 2008. The tracking Airway Bill for the shipment indicates that only 3 of the 4 capsule packages arrived at Panama City. The licensee has requested a trace on the missing package. In addition, the airlines warehouses in St. Louis, Miami, and Panama City have been searched. The licensee is also pursuing a search of the customs warehouse in Panama City. At this time, the licensee considers that one of the I-131 capsules is missing in shipment. There is minimal risk to the public as long as the capsule remains in the shielded container. The short half-life of the I-131 would put the current content of the capsule at about 11 millicuries. The licensee continues to work with the shipping airline to attempt to locate the package. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-09-25
44518 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-09-17 03:20 | 2008-09-25 16:07 | 2008-09-25 | AGREEMENT STATE REPORT - SHIELDING PLATE FELL OFF KR-85 MEASURING DEVICE "On September 17, 2008, at 3:20 a.m. the Radiation Safety Officer for Georgia-Pacific called the answering service for radiation incidents after hours. He stated that the screws on a Honeywell Measurex unit, model 4201 had backed out and a shielding plate fell off leaving a 1 Ci Kr-85 source exposed. He stated that the operator had roped off the area around the paper machine to prevent access and exposure. The operator described the time and distance to the source and it was determined that any exposure would have been minimal. Honeywell International, license LA-10814-L01 was contacted for servicing and packaging of the unit. The service tech was to be at the facility September 17, 2008 around 4:00 p.m. because he was traveling from out of state. The facility will follow up with a report and additional information concerning this incident." Louisiana Incident: LA0800019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-09-30
44517 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-07-31 19:30 | 2008-09-25 13:34 | 2008-09-25 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES DUE TO A POWER FAILURE "On July 31, 2008, at 7:30 p.m. CDT, power was lost on the reactor protection system (RPS) bus A. The plant was operating at 100 percent power at the time. The loss of RPS bus A interrupted power to the containment isolation actuation circuitry. This caused the Division 1 containment isolation valves in various balance-of-plant systems to automatically close, as designed. Plant operators implemented recovery procedures to shift RPS A to its alternate power supply, and restore the systems affected by the isolation to service. The containment isolation valves were confirmed to have actuated as required. Plant capacity was not interrupted by the containment isolation signal. "The normal power supply for each RPS bus is a dedicated motor-generator set. The output of that generator is routed to the bus via two Electrical Protection Assembly (EPA) breakers arranged in series. Each EPA breaker has an internal power supply supporting the various trip functions designed into the breaker. Troubleshooting activities determined that the power supply in the upstream EPA breaker between the motor-generator set and the A RPS bus had failed, causing the undervoltage function of that EPA to actuate. The cause of the failure of the power supply has not been determined. This event is being reported in accordance with 10CFR50.73(a)(1) and 10CFR50.73(a)(2)(iv)(A) as an invalid actuation of the division 1 containment isolation actuation system." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-09-25
44516 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-09-23 15:00 | 2008-09-23 19:25 | 2008-09-23 | DEGRADED CONDITION DUE TO RECIRC NOZZLE WELD AXIAL CRACK "On September 23, 2008 at approximately 1500 [EDT] the James A. FitzPatrick Nuclear Power Plant was shutdown and operating in the refueling mode (Mode 5). During an ISI inspection of the dissimilar metal weld on recirc nozzle N2-C, an indication was identified. Preliminary analysis of the data indicates a flaw in the nozzle weld that extends into the 'butter', is axially oriented, approximately 0.5 inches in length and 0.4 inches in depth. There is no approved method for predicting crack growth in axially oriented flaws. Therefore, the flaw can not evaluated in accordance with ASME Section XI. This deficiency meets reporting criterion 10 CFR 50.72(b)(3)(ii). "At this time four of the eight N2 Recirc Nozzles have been inspected with no other flaws or indications identified. The remaining four N2 Nozzles are being inspected during this outage. "The event has been entered into the corrective action program and a Licensee Event Report (LER) will be filed within 60 Days as required by 10 CFR 50.73(a)(2)(ii). "The NRC Resident Inspector has been briefed and the state Public Service Commission (PSC) will also be notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-09-23
44515 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-09-23 09:37 | 2008-09-23 15:22 | 2008-09-23 | SAFETY EQUIPMENT FAILURE DUE TO LOSS OF POWER "At 0937 CDST, on 09/23/08 the Plant Shift Superintendent (PSS) was notified that C-315 (tails withdrawal facility) had lost power due to a fault on a 14 KV feeder. As a result of the power loss, the C-315 High Voltage Process Gas Leak Detection (PGLD) System was rendered inoperable. This PGLD System contains detectors that cover the C-315 UF6 condensers, accumulators, and piping heated housing. At the time of this loss of power, these areas were operating above atmospheric pressure. TSR 2.3.4.4 requires that all of detector heads in this system be operable during operations above atmospheric pressure. This PGLD System was declared inoperable. TSR LCO 2.3.4.4.A.1 was entered and a continuous smoke watch was put in place within one hour. This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand; and, c.) no redundant equipment is available and operable to perform the required safety function. Once the source of the fault was identified, power was restored to the C-315 facility. The High Voltage PGLD system was tested, and the system was declared operable. Power was restored at 1039 hours and the High Voltage PGLD System was declared operable at 1118 hours. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-08-2371; PGDP Event Report No. PAD-2008-29; Responsible Division: Operations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-09-23
44514 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-09-23 12:15 | 2008-09-23 13:01 | 2008-09-23 | MEDIA INQUIRY CONCERNING UPCOMING LICENSEE PERFORMANCE REVIEW "Below are the responses to questions BWXT received from [DELETED] at the News & Advance of Lynchburg, VA, and the BWXT responses. "Q: In the past year, there have been a number of 'notices of violation' from NRC regarding events at BWXT. Several of these violations or apparent violations involved Raschig Ring-filled Vacuum Cleaners - one overturned from a forklift last year and spilled some nuclear material; later there was a situation in which one of the RRVCs did not have enough raschig rings in it, etc.-and one other incident involved an employee being splashed with a solution that contained some nuclear material. In what ways has the company responded to these events? What measures have been taken to correct procedures and prevent further occurrences? "A: The company has performed detailed incident investigations and identified corrective actions to prevent reoccurrence of these types of incidents. For example, in the case of the RRVCs we have developed and are implementing a new vacuum cleaner design that no longer requires the use of Raschig rings. In the case of the chemical spill, the company has strengthened its chemical spill response procedures. "Q: How does the company anticipate the performance review to go? "A: We appreciate the opportunity to receive feedback from the NRC on our performance on an annual basis. This feedback is valuable to us as we strive to continuously improve our operating and safety performance. We look forward to discussing our safety and operational successes and improvements at the meeting. "Q: Some of BWXT's operations are classified; Do you know how detailed the performance review presentation will be? "A: For specifics about the NRC's presentation, it would be better to contact the NRC. I can tell you that the information we plan to present will be detailed enough to explain our successes and improvements without revealing any classified information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-10-01
44513 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-09-23 07:30 | 2008-09-23 07:34 | 2008-09-23 | EMERGENCY OPERATING FACILITY UNAVAILABLE "PPL Susquehanna is installing a backup diesel to supply power to the Emergency Operating Facility (EOF) during loss of power conditions. A power outage is required to tie-in the transfer switch for the new power supply. The scope of work includes connection of offsite power to a new transformer, connection from the transformer to the transfer switch and connection of power from the transfer switch to the building's distribution panel. This power outage, which is expected to be approximately 3 hours, is required to make final connections and to test the new service. "During the outage, temporary power will be supplied to the phone lines only. HVAC, lighting and computer terminals will be without power. This condition is a loss of emergency response capability and is reportable to the NRC as an 8 hour ENS notification per 10CFR50.72(b)(3)(xiii)." The licensee contacted the NRC Resident Inspector. * * * UPDATE FROM R. KLINEFELTER TO J. KNOKE AT 1303 EDT ON 09/23/08 * * * This is a follow-up courtesy notification to EN# 44513. As of 12:20, on 09/23/08, power has been restored to the Susquehanna Emergency Operating Facility (EOF). Licensee has notified the NRC Resident Inspector and the state. Notified R1DO (Conte) | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-23
44512 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-03-28 | 2008-09-22 15:50 | 2008-09-22 | NEBRASKA AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN "Fagen Inc. built the bioenergy facility in Fairmont, [NE]. Fagen Inc. purchased a number of tritium exit signs for the facility. After the facility was built, Fagan Inc. turned the facility over to Advance BioEnergy. Advance BioEngery did an inventory of the signs in the facility [on 03/28/08] and discovered a missing sign (SRB Technologies, Model BX020BK, Serial #C061355) [contains 17.5 curies of tritium]. "Advance BioEnergy contacted Fagen Inc. concerning the missing exit sign. Fagen contacted the supplier and, other sites that Fagen had done work at. They have not been able to locate the sign. Fagen has discontinued using tritium exit signs in facilities they construct. Item Number: NE080008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-09-25
44511 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-01-03 | 2008-09-22 15:50 | 2008-09-22 | NEBRASKA AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN "Fagen Inc. built the bioenergy facility in Ord, NE. Fagen Inc. purchased a number of tritium exit signs for the facility. After the facility was built, Fagan Inc. turned the facility over to VeraSun. VeraSun did an inventory [on 01/03/08] of the signs in the facility and discovered a missing sign (SRB Technologies, Model BX-20BK, Serial #C056713) [contains 20 curies of tritium]. "VeraSun contacted Fagen Inc. concerning the missing exit sign. Fagen contacted the supplier and other sites that Fagen had done work at. They have not been able to locate the sign. Fagen has discontinued using tritium exit signs in facilities they construct." NE Item Number: NE080007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-09-25
44510 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-09-17 | 2008-09-22 14:41 | 2008-09-22 | AGREEMENT STATE REPORT - SMOKE DETECTOR FAILED TO OPERATE PROPERLY Licensee was testing the smoke detector outside the vault that houses the irradiator. The detector failed to operate. The irradiator (1645 kCi of Co-60) was not in operation at the time of the test. This is being reported under 10 CFR 30.50 (b)(2). NE Report # NE080009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-09-25
44509 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-09-22 06:00 | 2008-09-22 06:02 | 2008-09-22 | TECHNICAL SUPPORT CENTER AND OPERATIONAL SUPPORT CENTER UNAVAILABLE "Unavailability of TSC/OSC Charcoal Filter for Scheduled Maintenance. "At 0600 on Monday, September 22, 2008, the Pilgrim Nuclear Power Station (PNPS) Technical Support Center (TSC) / Operational Support Center (OSC) ventilation system charcoal was removed from service for planned charcoal bed maintenance. The balance of the TSC/OSC ventilation is not affected by the charcoal bed maintenance and remains available. "Under certain accident conditions the TSC/OSC may become unavailable due to inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC/OSC personnel to the Emergency Operations Facility (EOF) and to the Chiltonville Training Center. "Charcoal filter maintenance is scheduled to be completed by 1700 hours on Monday September 22, 2008. "The licensee will be notifying the NRC Senior Resident Inspector. "This notification is being made in accordance with 10CFR50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE AT 1437 EDT ON 09/22/08 FROM BRUCE CHENARD TO JEFF ROTTON * * * "The TSC/OSC ventilation system was returned to functional status on Monday, September 22, 2008. "This follow-up notification is being made to provide closure from the initial notification under 10CFR50.72 (b)(3)(xiii) due to the loss of an emergency response facility. "The licensee has notified the NRC Resident Inspector." The licensee also notified the State of Massachusetts Emergency Management Agency. Notified R1DO (Conte) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-22
44508 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-09-20 21:35 | 2008-09-21 02:13 | 2008-09-21 | UNPLANNED LOSS OF SHUTDOWN COOLING DUE TO CONTAINMENT ISOLATION "On Saturday, September 20, 2008, Monticello Nuclear Generating Plant (MNGP) experienced an actuation of the following systems: Reactor Protection System (with the reactor shutdown), Containment Isolation, and Emergency Diesel Generators. "The apparent cause of the actuation was a pressure pulse in the reference leg of a Reactor level instrument that resulted when a CRD [Control Rod Drive] pump was started without the reference leg backfill system isolated from the CRD system. "This notification is being made in accordance with 10CFR50.72(b)(3)(iv)(A)." Due to the containment isolation, shutdown cooling was lost for approximately 90 minutes. Initial reactor temperature was ~95 degrees when the isolation occurred. When shutdown cooling was restored, reactor temperature had increased to ~120 degrees. The Emergency Diesel Generators started but did not load. The diesels have been restored to normal standby status. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-09-21
44507 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-09-20 20:18 | 2008-09-20 20:31 | 2008-09-21 | UNIT 1 MANUAL REACTOR TRIP FROM 100% POWER DUE TO A FIRE IN THE MAIN TURBINE D.C. Cook Unit 1 declared an Unusual Event (EAL H4 & H5) due to a fire in the Main Turbine. The reactor was manually tripped from 100 percent. The fire occurred at the upper level of the turbine building (Level 633), and was extinguished by the fire suppression system and local fire brigade. Three fire pumps are running at this time. No injuries were reported. All rods fully inserted, auxiliary feed water initiated and decay heat is being removed via atmospheric relief valves. Unit 1 is currently shutdown and stable in Mode 3, Hot Standby. Main steam stop valves are closed. Main condenser vacuum was broke. Unit 2 was not affected. All Unit 1 safety-related equipment is in-service and available. The licensee is currently assessing the extent of damage. The licensee will inform the NRC Resident Inspector. Notified DOE (Morrone), USDA (Shaf) and HHS (Mammarelli) that the NRC entered Monitoring Mode at 2045 EDT. * * * UPDATE AT 0005 EDT ON 09/21/08 FROM BRADDOCK LEWIS TO V. KLCO * * * "On September 20, 2008 at [2005] the DC Cook Unit 1 Reactor was manually tripped after a malfunction occurred on the main turbine generator causing high vibration. A fire in the Unit 1 Main Generator resulted from this malfunction. A Notification of Unusual Event was declared September 20, 2008 at [2018] due to Event classifications H-4, Fire within the protected area not extinguished within 15 minutes and H-5, Toxic or Flammable gas release affecting plant operation. The Unit 1 Main Generator Fire was reported extinguished at September 20, 2008 at [2028]. "The Unit 1 plant trip was uncomplicated and all Automatic Control systems functioned as expected. All control rods inserted on the Reactor trip. The Turbine and both Motor Driven Auxiliary Feedwater pumps automatically started and fed all four Steam Generators as designed. The Steam Generator Stop Valves were manually closed to arrest plant cooldown. The cause of the Main Generator fire has not yet been determined, but the investigation is ongoing. No radiological release resulted from this event. "This event is being reported as a four hour report required by 10CFR50.72(b)(2)(iv)(B) due to the Reactor Protection System automatic actuation and as an eight hour report required by 10CFR50.72(b)(3)(iv)(A) for the automatic actuation of the Auxiliary Feedwater system. The Notification of Unusual Event was reported separately. "Unit 1 is stable in Mode 3. Shutdown Margin was satisfactorily verified. The main condenser was isolated as the primary heat sink. Steam Generator Power Operated Relief Valves are removing core decay heat in automatic control due to breaking main condenser vacuum. Main condenser vacuum was broken to stop the Unit 1 main turbine generator due to high vibration. Preparations are in progress to cooldown Unit 1 to Mode 5, Cold Shutdown. "The Fire Suppression Water System was actuated and one of two 565,000 gallon tanks was drained. The second 565,000 gallon Fire Suppression Water tank was placed in service to restore the Fire Suppression Water system function." The licensee notified the NRC Resident Inspector, local and state authorities. The licensee will likely make a press release. Notified R3RA (Caldwell) and NRR (Galloway). * * * UPDATE PROVIDED BY PAUL LEONARD TO JASON KOZAL AT 0414 ON 09/21/08 * * * At 0409 the licensee terminated from the Notice of Unusual Event. The licensee has established the forced outage recovery team. No fires exist and no conditions conducive to fires exist due to the event. The licensee has established the integrity of the fire protection system. Notified R3RA (Caldwell), R3DO (Stone), NRR (Galloway), IRD (Grant), DHS (Jason), DOE (Maroni), FEMA (Sweetser), USDA (Phillip), and HHS (Nathan). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2008-09-20
44506 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-09-20 09:06 | 2008-09-20 11:30 | 2008-09-20 | REACTOR TRIP DUE TO TURBINE TRIP "At 0906 EDT Watts Bar Unit 1 experienced a Reactor trip in response to a Turbine trip. This caused an automatic AFW Pump start from P-4 coincident with Lo Tave signal. First indications are that the Exciter Field Breaker tripped open. The cause is under investigation. All ESF systems responded as designed with no other issues. The plant is currently stable and is being maintained in Mode 3. Plans for plant restart are pending awaiting the cause investigation." All control rods fully inserted into the core. Plant decay heat removal is through the steam dumps to the main condenser. The offsite power is available and lined up to plant system loads. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-09-20
44505 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-09-18 17:00 | 2008-09-19 15:10 | 2008-09-19 | AGREEMENT STATE REPORT - LEAKING SOURCE IN GAS CHROMATOGRAPH "On September 18, 2008, at 5:00pm, the state received a telephone call from the RSO of Nektar Therapeutics that their Aglent Technology gas chromatograph containing generally licensed source is leaking. This notification is based on the swipe test results report from their swipe test laboratory. Source Serial Number U8663, had a confirmed a positive wipe test result of 137,362 DPM which is a result of 0.0619 micro curies/sample. "The RSO stored the gas chromatograph in a secured locked storage room where the storage is posted with 'Caution Radioactive Material'". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-09-24
44504 | 0 | SPECTRUM TECHNOLOGIES |  |  |  |  | 2008-09-15 | 2008-09-19 11:01 | 2008-09-19 | PART 21 - SIEMENS MODEL 353 PROCESS CONTROLLER TRANSFORMER FAILURE The following information was received via facsimile. "The defect concerns a decreased reliability of the transformer within the controller. The failure of the transformer can cause the controller to not power up when energized or to unexpectedly shut down during normal operation." This notification is for the following controller models shipped between 2/21/2007 and 4/21/2008: 353A, Kit A TGX:353A, Kit B 16353-68 Controller Board Kits for Design Level A TGX:16353-302 Controller Board Kit for Design Level B Affected licensees are Florida Power and Light (Duane Arnold) and Duke Energy (Oconee). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2008-09-19
44503 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-09-18 18:48 | 2008-09-18 21:11 | 2008-11-12 | HPCI INOPERABLE DUE TO MISSING INSULATION "At 1848 on 09/18/2008, the control room was notified by system engineering that insulation was missing from the bottom of the HPCI turbine that could result in nearby electronic components being subjected to higher than design temperatures. This could challenge the ability of the HPCI system to perform its design function for the prescribed mission times. The condition does not prevent the high pressure coolant injection system from automatically starting and injecting during an accident. The longer term ability of the system to continue to inject is challenged by the existing condition. "The HPCI system was immediately declared inoperable while engineering continues to evaluate the condition to determine if an actual loss of design function has occurred. "This is being reported as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident in accordance with 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 11/12/2008 AT 1616 FROM MARTIN LICHTNER TO MARK ABRAMOVITZ * * * "On September 18, 2008, PPL Susquehanna LLC reported a potential loss of the HPCI safety function under the provisions of 10CFR50.72(b)(3)(v)(D). The report was made when it was discovered that insulation was missing from the bottom of the Unit 2 HPCI turbine. This situation raised concerns that increased area temperatures could adversely affect nearby electronic equipment needed to support long-term HPCI operation. A subsequent investigation has determined that all potentially affected components were rated for operation at temperatures greater than those anticipated during HPCI operation with the missing insulation. An additional physical inspection confirmed that there was no abnormal discoloration or visible signs of accelerated thermal aging on the components and wires in question. It has therefore been concluded that HPCI operability had not been impacted by the missing insulation. Accordingly, the loss of safety function reported on September 18th under ENS # 44503 is being retracted. The insulation has since been restored to the HPCI turbine." The licensee notified the NRC Resident Inspector. Notified the R1DO (Trapp). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-09-18
44502 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-09-18 14:15 | 2008-09-18 17:31 | 2008-09-18 | OFFSITE NOTIFICATION TO MIAMI-DADE COUNTY DUE TO SPILL "While moving a battery a forklift punctured a battery cell and sulfuric acid leaked onto the asphalt. The spill was less than 10 gallons and was on a non-permeable surface. The spill was contained, neutralized and cleaned up. "Under the Specific Conditions of PTN's Industrial Waste Annual Operating Permit with Miami-Dade County all spills are reportable within 4 hours. The spill occurred about 1415 on 9/18/08. The notification to Miami-Dade County Department of Environmental Resource Management (DERM) at 1700 EDT on 9/18/08." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-09-18
44501 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-08-21 13:15 | 2008-09-18 15:45 | 2008-09-18 | AGREEMENT STATE REPORT - REPORTABLE QUANITY OF RA-226 FOUND IN SCRAP YARD "A shipment of ferrous scrap metal from a small scrap metal yard set off the radiation alarms at the entrance to the major regional scrap metal and exporting facility. It was immediately rejected, but the Agency (state of MA) was not notified for almost two hours. An Agency investigator responded and traced the shipment back to a smaller scrap yard across town. The operator of the facility had isolated the rejected shipment and was trying to locate their consultant. Upon surveying the roll-off, the Agency investigator tentatively identified the shipment as containing Radium. The background was recorded as 0.06 millirem/hour and the highest reading was measured as 0.1 millirem/hour. "This company was advised to acquire the services of a competent health physics consultant to arrange for the separation, storage and legal disposition of the radioactive material; and this was agreed upon without hesitation. Their hired consultant responded to the facility on August 25, 2008; and after collecting a spectrum and necessary measurements for identification purposes, separated one metal device from the roll-off, packaged it in a five gallon drum and had the facility operators secure it on-site depending disposal arrangements. Subsequently, the consultant has confirmed the presence of 12 microcuries of Radium-226. Legal transfer and disposition of this radioactive material is pending." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-09-23
44500 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-09-11 | 2008-09-17 17:39 | 2008-09-18 | GREATER THAN PRESCRIBED DOSE ADMINSTERED TO PATIENT "On Wednesday, September 17, 2008, [a Certified Nuclear Medical Technologist] at Universal Health Services of Rancho Springs, Inc., contacted RHB about a diagnostic misadministration, which had occurred on September 11, 2008. The patient was prescribed a 7 milliCurie dose of Tc-99m Hebrofenin for a Hepatobiliary study (HIDA). At approximately 2:10 P.M. on September 11, 2008, the patient was given a dose of 22 milliCuries of Tc-99m Sestamibi, used for cardiac studies. The dose given was 50% greater than the intended dose. No additional Tc-99m was given since the image required was obtained with the dose that was actually given. The technician had grabbed the wrong syringe from the dose cart. The reason given for the misadministration was a heavy workload. The corrective actions to be taken to prevent a recurrence were to implement new procedures for radiopharmaceutical labeling and handling and to reinstruct personnel. Since the dose administered to the patient was 50% greater than the prescribed dose, the reportability of this event is 24 hours. This event will be investigated by RHB South." California Report #5010-091708 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION AT 1044 ON 9/18/2008 FROM DELIA AQUINO TO MARK ABRAMOVITZ * * * The following report was received via e-mail: The state of California is retracting this event. "After additional review, we determined that it was not actually a reportable event." The dose the individual received did not meet the threshold necessary to be reportable under 10CFR35.3045 - Medical Event. Notified the R4DO (Pick) and FSME (Einberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-09-23
44499 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-09-17 | 2008-09-17 13:52 | 2008-09-17 | AGREEMENT STATE REPORT - BROKEN GAUGE "On September 17, 2008 the licensee reported that a[n] Ohmart/Vega (OV) model SH-F1 has a sheared bolt on the shutter handle which prevents it from closing. This device (S/N 1297GK) contains 20mCi of Cs-137 in a model OV A-2100 sealed source capsule. The manufacturer has been notified and will see to the proper repair or replacement of the gauge. No public exposures are likely to approach regulatory limits and the vessel has been posted to prevent entry." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-09-22
44498 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-09-17 10:17 | 2008-09-17 11:40 | 2008-09-21 | UNUSUAL EVENT DUE TO LOSS OF SHUTDOWN COOLING Monticello lost the 1R offsite power transformer due to an industrial accident that grounded the bus and resulted in a fatality of an employee onsite. At the time of this event, the 2R offsite transformer was already out of service due to a previous event (see EN #44484). This effectively resulted in a loss of all normal offsite power. The 1AR safety related offsite power source remained available and the safety related buses are energized and diesels are available. However, shutdown cooling was lost during the event due to a Group 2 isolation and cannot be restored. The shutdown cooling suction isolation valves #2020 and #2030 have power but until the Group 2 logic can be reset the valves cannot be reopened. The licensee needs to repower the RPS bus to reset the logic. Based on the uncertainty in reestablishing shutdown cooling an Unusual Event was declared based on Emergency Director judgment (EAL HU5.1). Current reactor coolant temperature is approximately 110 degrees with a heatup rate of about 20 degrees an hour. State and local authorities and the NRC resident inspector have been notified. The licensee will likely be making a press release. * * * UPDATE AT 1417 EDT ON 09/17/08 FROM CORY JASKOWIAK TO S. SANDIN * * * "On Wednesday, September 17, 2008 Monticello Nuclear Generating Plant (MNGP) experienced a loss of power to the station transformer resulting in a valid actuation of the following systems: Reactor Protection System (with the reactor shutdown), Containment Isolation, and Emergency Diesel Generators. "The cause of the loss of power was due to contact of a 115kV transmission line by a manlift. A vendor employee was electrocuted. On-site Medical Emergency Response personnel responded until the individual was transported to North Memorial Medical Center. The individual was pronounced dead at North Memorial Medical Center. "Notifications of offsite agencies and a media press release are in progress. 'This notification is being made in accordance 10CFR50.72(b)(2)(xi) and 10CFR50.72(b)(3)(iv)(A).' "Licensee notified the NRC Resident Inspector." Notified R3IRC (Garza) * * * UPDATE AT 1715 EDT ON 09/17/08 FROM R. BAUMER TO S. SANDIN * * * "This is a follow-up to Event notification #44498. The station has completed notifications to off-site agencies and to the media. The station continues to troubleshoot and restore plant equipment and respond to media inquiries. "NUE update - As of 1113 CDT shutdown cooling was restored." Notified R3 IRC. * * * UPDATE AT 1220 EDT ON 9/21/08 FROM DAN NORHEIM TO JOHN KNOKE * * * "Monticello Nuclear Generating Plant exited their Notification of Unusual Event at 1100 CDT on 9/21/08. The exit criteria is supported on the following information: (1) This event did not result in the loss or potential loss of a fission product barrier and did not change the status of the current fuel condition. All three fission barriers are intact and were maintained throughout the event. (2) There were no radiation releases as a result of the event. (3) Restoration of plant loads including shutdown cooling onto a normal offsite power source (the 1R transformer) has been completed. (4) The 1R transformer offsite power source was recovered and is being protected. Protection of the 1R transformer will continue until availability of the other offsite power source supplied from the 2RS/2R transformers has been restored. (5) Shutdown cooling is in service. (6) The site organization challenges in response to the injury event and loss of decay heat removal are no longer present." The licensee has notified the NRC Resident Inspector, as well as state and local agencies. A media release will be issued. Notified R3DO (Stone), NRR EO (Galloway), IRD MOC (Clark), OPA (Burnell), DHS (S. Moore), and FEMA (D. Fuller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2008-09-17
44497 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-09-16 | 2008-09-16 20:55 | 2008-09-16 | HIGH CONDUCTIVITY IN A POOL IRRADIATOR "At 8:14 am on September 16, 2008, the radiation safety officer (RSO) called to report the pool water conductivity was above 100 microsiemens per centimeter on September 6, 2008. On September 4, 2008 the licensee noted some product (honey) had leaked out of the container into the pool. They thought this small amount of contaminate would be cleared out of the pool once it circulated through the water purifying tanks, however, the conductivity continued to increase until September 6, 2008 [when] it reached 120 microsiemens per centimeter. The licensee did not realize this was a reportable event per 10 CFR 36.83(a)(10) until he spoke to his corporate RSO last night (9-15-08). He then reported the incident to us [State of California] this morning. The licensee has been continuing to work to reduce the conductivity by adding new water purifying tanks. As of today, the water is still too cloudy to see the sources in the pool and the conductivity is at 57 microsiemens per centimeter and is continuing to reduce each day. Corrective actions to be taken include refresher training for the RSO to review the regulatory requirements for reportable events and instruction to customers regarding the correct packaging of their product so they do not have a similar incident in the future. The RSO will be providing the Department with a written report within 30 day as required and will continue to mitigate the conductivity and clarity of the pool water until it has reduced to normal levels. The licensee will notify us when the conductivity and clarity is at normal levels." California Report Number - 091608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-09-19
44496 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2008-09-16 14:00 | 2008-09-16 19:23 | 2008-09-16 | MANUAL REACTOR TRIP DURING TROUBLESHOOTING OF CONTROL ROD DRIVE MECHANISM MOTOR GENERATORS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On September 16, 2008 at approximately 1400 hours Mountain Standard Time (MST) Palo Verde Nuclear Station Unit 3 experienced a manual reactor trip. At the time of the trip trouble shooting efforts were in progress to investigate abnormalities with the control element drive mechanism (CEDM) motor generators (MG). The MGs (2 - 100% each) normally operate in parallel to supply the necessary power to grip, move and hold the control element assemblies (CEA). During the trouble shooting activities the 'B' MG was removed from service. The 'A' MG initially provided power to the CEDMs but did not maintain the power. "As a result of the pre-job briefing contingency actions, a manual reactor trip was ordered. "All CEAs fully inserted into the core. No other emergency actuation signals were initiated and none were required. Off site power provided power to the class buses during and after the event. Decay heat removal is being provided by the steam bypass control system to the main condenser. No major equipment was inoperable prior to the event that contributed to the event. "The unit is in Mode 3, Hot Standby, at normal temperature and pressure. "The cause of the MG abnormality is under investigation." Normal feedwater remained in service providing water to the steam generators. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-09-16
44495 | 0 | WALMART STORES |  |  |  |  | 2008-09-16 | 2008-09-16 17:10 | 2008-09-16 | LOST TRITIUM EXIT SIGNS The licensee reported two tritium exit signs missing from stores in Crawfordsville, IN (SN 368230, manufacturer -Isolite, Activity - approximately 10 Ci) and South Hill, VA (SN 320031, manufacturer - unknown, activity - unknown). The missing signs were identified during a remove and replacement effort of the tritium exit signs company wide. Both signs were accounted for in an inventory of the signs in the spring of 2008. An investigation was performed by company personnel to determine the disposition of the signs. Upon completion of the investigation it was determined that the signs could not be located and their final disposition was unknown. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-09-16
44494 | 0 | NATIONAL OCEANIC AND ATMOSPHERIC AD |  |  |  |  | 2008-08-28 16:00 | 2008-09-16 16:36 | 2008-09-16 | THREE UNACCOUNTED FOR NICKEL-63 SOURCES "Two Hewlett Packard (HP) gas chromatographs with three HP Nickel-63 detectors at a source strength of 15 millicuries each were determined to be missing from their stored warehouse (Building #4) at NOAA ESRL laboratory in Boulder, CO by [the licensee] on 29 March 2007. A search was begun with the belief that the sources had been moved or used by someone in the NOAA facility because Building #4 was used as a temporary post office for about one year and [NOAA] boxes may have been moved to other locations on the site. The serial numbers of the missing sources were L1231 and L1941 in an HP model 5890 II GC with serial number 2518A05469, and M2087 in another HP model 5890 II GC with serial number 2518A05471. [NOAA] use[s] the ECDs in a worldwide network to measure atmospheric substances (freons) that destroy stratospheric ozone. The network includes stations at Pt. Barrow, Alaska; Niwot Ridge, Colorado; Mauna Loa, Hawaii; American Samoa, and South Pole, Antarctica. Source serial #s L1231 and L1941 were last wipe tested on 24 July 2001. The GC containing those sources was then retired from service at Niwot Ridge and placed in storage on 20 August 2001. Source serial# M2087 was last wipe tested on 7 February 2000. The GC containing those sources was retired from service from American Samoa and placed in storage. On 9 August 2002, all sources were moved to Building #4 for long term storage. They were not wipe tested further since they were inactive. "Building #4 is locked 24 hours, seven days a week, and occasionally left opened during working hours without security monitors or staff members in the storage area. The Boulder DoC campus is guarded with access control, but not fenced in. The following activities were investigated to locate the three missing stored sources: "(1). The Department of Commerce Laboratories in Boulder stores all excess property in Building #4 to make it ready for transport to the Denver Federal Center for posting of availability of excess property to all government agencies. If the excess property was not transferred to another government agency over a year period, then it will be sold to general public. The thought was that the shipper had taken the instruments with their sources by accident to the Denver Federal Center. We contacted the shipper and the Denver Federal Center, and both reported that they were never picked up prior to 2007. The procedure also requires that each piece of excessed property be sealed with plastic on a pallet with paper work attached, so this possibility was ruled out in 2007. "(2). [The licensee] contacted all current employees in the group to make sure that the sources were not loaned out. Nothing was discovered. "(3). [The licensee] contacted all past employees in the group to make sure that they had not borrowed the sources without our knowledge. Nothing was discovered. (4). [The licensee] contacted HP, now Agilent Technologies, to see if anyone reported the instruments with the sealed sources as being serviced. Nothing was discovered. "(5). [An employee] of ESRL/GMD contacted all observatory staff and inspected all spares parts at our observatories (except American Samoa) over the past year to see if they were there. This required a year for someone from our group to visit each site, including South Pole since it is only opened three months each year. Nothing was discovered. "(6). [The licensee] contacted LabX, a web site where used laboratory equipment is sold, to see if the instruments with the missing sources were sold on LabX. Nothing was discovered. "(7). Many members of the NOAA/ESRL/GMD searched the complete DoC site and all rental storage facilities in Boulder were completed on 15 August 2008. Nothing was discovered. "[The licensee] concluded that these three sources were lost on 28 August 2008 after investigating all of the leads above. The probable outcome is that the sources and their instruments were moved out of NOAA property in Boulder. They are either misplaced or stolen. [The licensee] only contacted one used instrument web site, LabX, a[n] eBay type service, ---they only providing a listing service. In the used instrument market, these instruments are being sold for as high as $12K each. They are the most expensive items that [the NOAA] group currently stores. They are sealed low level beta sources. There is little or no risk to any individuals that worked with them and they do not create a problem for the public at large." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | CO | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-09-16
44493 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2008-09-16 | 2008-09-16 15:02 | 2008-09-16 | RADIOGRAPHY CAMERA SOURCE FAILED TO RETURN TO SAFE POSITION "On September 12, [the] RSO for Team Industrial Svcs. called to advise that an irregularity had occurred during a routine radiography shot [deleted]. A radiography crew had been working at the Archer Daniels Midland facility in Decatur, Illinois to perform a panoramic shot within a 5 inch thick steel vessel. Following the shot, the 100 Ci Co-60 source failed to return to the safe position within the camera. The crew called their local RSO, [deleted] and requested assistance. During [the local RSO's] travel to the site, the crew secured the Fabrication Shop where the vessel was located. [The local RSO's] first actions at the site were to confirm the area was secured and the appropriate barriers were in place such that exposures to any other individuals remained below regulatory limits for members of the public. (Prior to the work beginning, the area had been evacuated and remained that way during the duration of the event). The shot was described as a 'panoramic, horizontal shot at ground level that did not require support equipment.' The lead radiographer's pocket dosimeter at the time of the notification showed a total of 50 milliR for that day's activities. Preliminary evaluation by the crew suggested the source had become disconnected in that the expected number of 'cranks' on the drive cable exceeded the number necessary to return the source to the camera from the 14 foot length guide tube with extension and there was no evident increase in radiation exposure rate as had been expected from the camera. The manufacturer of the equipment/source, QSA Global, was contacted immediately and had been asked to be on 'standby' in the event their assistance for a source recovery is necessary. Team Industrial Services is authorized to perform source retrievals and has adequate procedures/equipment for that activity for when they choose to attempt a recovery on their own. "Later, [the corporate RSO] reported that [the local RSO] confirmed the source disconnect at the scene by separating the guide tube from the camera and cranking the drive cable back to the camera. Additional lead and steel shielding was brought into the area via a remote overhead crane in the Fabrication Shop to allow for more direct observation. Dose rate at the camera location was measured as 200 milliR/h unshielded. With a leaded barrier, the dose rate was brought down to 100 milliR/h at the camera. The dose rate was further reduced by extending the crank assembly an additional 15 feet away from the camera. Based on technical instruction from QSA Global's expert, source recovery was attempted by modifying the connector on a drive cable that was then attached to the crank and threaded back through the camera. Team [Industrial Services] imposed a conservative 200 milliR total dose limit for the recovery operation and 500 milliR/h dose rate limit for area occupancy during [the local RSO's] attempts. "After 2 hours of attempts to recover [the source] were unsuccessful, the maximum exposure received at that point was 60 milliR. Over twenty attempts took place however, positive connection with the source 'pigtail' could not be confirmed. A reevaluation of the arrangement suggested that the extension guide tube should be removed and the overall guide tube length be made more straight by remotely partially withdrawing the main guide tube from the vessel. Following those changes and a break, another attempt was made which was successful. The source was secured within the camera and no immediate damage to the source was evident from a field wipe test which showed background levels of radiation. The maximum recorded exposure to recovery personnel was approximately 140 milliR as measured by DRD. All associated equipment was returned to Team Industrial's permanent storage facility in Roxana, IL that same night by 23:00. Plans are to return the source with camera, drive cable and guide tubes to the manufacturer for further analysis as to a potential cause of the event. The radiography crew reported that prior to the days events, routine checks showed the equipment was in properly operating condition. They further insist that a 'misconnect' where the drive cable was not properly connected to the source did not occur in this case. The licensee has been advised that a 30 day report to the Agency is required. This item will remain open pending receipt of that report and the analysis of the manufacturer as to the state of the returned equipment." Illinois Report Number: IL080051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2008-09-19
44492 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-09-16 07:34 | 2008-09-16 13:09 | 2008-09-16 | LOSS OF SHUTDOWN COOLING CAPABILITY "On September 16, 2008 at 0734 the James A, FitzPatrick Nuclear Power Plant was shutdown and operating in the refueling mode (Mode 5), when shutdown cooling was lost. Shutdown cooling was lost while hanging a tagout on the Reactor Protection System (RPS). When removing fuses as directed by the tagout, isolation logic for Shutdown Cooling suction salve 10MOV-18 was actuated. This Suction Valve isolates the common shutdown cooling suction line to all Residual Heat Removal (RHR) Pumps. At the time of the isolation cavity flood-up was in progress and the time to boil was greater than 5.5 hours. The appropriate Technical Specification LCO Actions were entered and shutdown cooling was restored at 08:27. "Power was restored to RPS and work in that system has been suspended pending the results our investigation into the cause of the event. Also additional controls have been established to review any electrical jumper/ protective tagging interactions prior to installation. "The event has been entered into the corrective action program and a Licensee Event Report (LER) will be filed within 60 Days as required by 10 CFR 50.73(a)(2)(v). "The resident inspector has been briefed and the state Public Service Commission (PSC) will also be notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-09-16
44491 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2008-09-15 | 2008-09-15 16:39 | 2008-09-16 | LOSS OF EMERGENCY NOTIFICATION SIRENS DUE TO HIGH WINDS "On September 15, 2008 a severe windstorm moved through Oswego County and resulted in local area power outages. Seven (7) of thirty-seven (37) emergency notifications sirens are out of service. Tracking for station reporting criteria of 'four or more sirens out of service for 12 hours or more' was initiated at 02:44 with seven sirens out of service at that time. Five of the original seven out of service sirens remain out and two additional sirens have subsequently lost power. "Sirens affected provide coverage to Oswego County. The sirens are utility owned and shared with the James A. FitzPatrick site. "In the event the sirens are needed, the County has it's Hype-Reach (911 call back system) on standby. "10 CFR 50.72(b)(3)(xiii) requires reporting within 8 hours when a significant portion of the emergency communication system has been lost. The site emergency procedures defines loss of 4 or more sirens for 12 hours or 19 or more sirens for 1 hour as a significant loss of emergency communications. Since the restoration activities did not result in restoring the siren system to less than 4 sirens out of service by 14:44 this reporting criteria is met. "The event has been entered into the corrective action program and the resident inspector has been briefed. "There are no other adverse impacts to the station based on this event." * * * UPDATE PROVIDED BY SCOTT BURNS TO JASON KOZAL ON 9/16/08 AT 1226 * * * The licensee reported that 5 sirens were returned to service. There is no completion time for return to service of the remaining 3 sirens. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY SCOTT BURNS TO DAN LIVERMORE ON 9/16/08 AT 1620 * * * The licensee reported that at 1150 on 09/16/2008, all emergency sirens were returned to service and are now operable. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-15
44490 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-09-15 02:44 | 2008-09-15 16:02 | 2008-09-16 | LOSS OF EMERGENCY NOTIFICATION SIRENS DUE TO HIGH WINDS "On September 15, 2008 with the James A. FitzPatrick Nuclear Power Plant Shutdown for refueling, a severe windstorm moved through Oswego County and resulted in local area power outages. Seven (7) of thirty-seven (37) emergency notifications sirens are out of service. Tracking for station reporting criteria of 'four or more sirens out of service for 12 hours or more' was initiated at 02:44 with seven sirens out of service at that time. Five of the original seven out of service sirens remain out and two additional sirens have subsequently lost power. "Sirens affected provide coverage to Oswego County. The sirens are utility owned and shared with the Nine Mile Point site. "In the event the sirens are needed, the County has it's Hype-Reach (911 call back system) on standby. "10 CFR 50.72(b)(3)(xiii) requires reporting within 8 hours when a significant portion of the emergency communication system has been lost. The site emergency procedures defines loss of 4 or more sirens for 12 hours or 19 or more sirens for 1 hour as a significant loss of emergency communications. Since the restoration activities did not result in restoring the siren system to less than 4 sirens out of service by 14:44 this reporting criteria is met. "The event has been entered into the corrective action program and the resident inspector has been briefed and the state PSC will also be notified." * * * UPDATE PROVIDED BY GENE DORMAN TO JASON KOZAL ON 09/16/08 AT 1309 * * * The licensee reported that emergency notification system was restored to less than 4 sirens out of service on 9/15/08 at 2022. The availability of the emergency notification system is less than the reporting criteria. Three sirens remain out of service. The NRC Resident Inspector was notified. * * * UPDATE PROVIDED BY GENE DORMAN TO DAN LIVERMORE ON 9/16/08 AT 1625 * * * The licensee reported that at 1150 on 09/16/2008, all emergency sirens were returned to service and are now operable. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-15
44489 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2008-09-15 10:00 | 2008-09-15 14:51 | 2008-09-15 | FITNESS FOR DUTY - ILLEGAL DRUGS A non-licensed employee with occasional supervisory responsibilities had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's site access was suspended. Contact the Headquarters Operations Officer for details. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2008-09-15
44488 | 0 | MISSOURI BAPTIST MEDICAL CENTER |  |  |  |  | 2008-08-14 10:30 | 2008-09-15 14:15 | 2008-09-15 | UNACCOUNTED FOR IODINE-125 SEED FOLLOWING IMPLANT PROCEDURE On August 14, 2008, a procedure to implant 94 Iodine-125 seeds was performed on a patient at the Missouri Baptist Medical Center. A quantity of 100 seeds was taken from inventory for this procedure. Upon completion of the procedure a count of the non-implanted seeds revealed that only 5 seeds were remaining, not six as expected. The missing seed had an activity of 0.493 mCi on the date of implant. The licensee performed a survey of the operating room on August 14, 2008, and a CT of the patient. The missing seed could not be accounted for. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-09-15
44487 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-09-15 08:00 | 2008-09-15 12:45 | 2008-09-18 | LOSS OF EMERGENCY SIRENS DUE TO POWER OUTAGES CAUSED BY HIGH WINDS "At approximately 0800 on 09/15/2008, it was determined that 55 of 119 Beaver Valley Power Station (BVPS) Emergency Offsite Sirens were inoperable. The apparent cause is loss of power to the sirens due to numerous power outages in the surrounding area. High winds from the remnants of Hurricane Ike passed through the surrounding area overnight. The weather has since returned to normal conditions. BVPS has validated that backup route alerting capability is in place for Columbiana County, Ohio and Hancock County, West Virginia. Beaver County, Pennsylvania is in process of verifying backup route alerting capability for the affected areas. This event is being reported as a Loss of Emergency Preparedness Capabilities pursuant to 10CFR50.72(b)(3)(xiii). "The NRC resident inspector has been notified. Updates on the status of siren restoration will be provided to the NRC resident inspector on an ongoing basis. Periodic updates to the NRC Headquarters' Operations Center will also be provided." * * * UPDATE PROVIDED BY BARRY SOMMER TO DAN LIVERMORE ON 09/16/2008 AT 1713 * * * "As of 1450 hours on 09/16/2008, 23 of the 119 Beaver Valley Power Station (BVPS) Emergency Offsite Sirens remain inoperable. There may be some variability of the number of inoperable sirens due to ongoing storm restoration activities. Backup route alerting capability remains in effect for the areas served by the inoperable sirens, "Updates on the status of siren restoration will be provided to the NRC resident inspector on an ongoing basis. Periodic updates to the NRC Headquarters' Operations Center will also be provided." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JAMES LUTZ TO JOHN KNOKE ON 09/18/2008 AT 1512 * * * "Update to EN# 44487. As of 1330 hours on 09/18/2008, 8 of the 119 Beaver Valley Power Station (BVPS) Emergency Offsite Sirens remain inoperable. The remaining 8 inoperable sirens no longer represent a major loss of emergency preparedness capabilities. Backup route alerting capability remains in effect for the areas served by the inoperable sirens and the licensee will continue to monitor restoration status. "Updates on the status of siren restoration will be provided to the NRC resident inspector on an ongoing basis." The licensee has notified the NRC Resident Inspector and state and local officials. Notified R1DO (Dimitriadis). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-15
44486 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-09-14 10:24 | 2008-09-14 11:58 | 2008-09-14 | COURTESY NOTIFICATION DUE TO SEVERE WEATHER DAMAGE AND EMERGENCY OPERATION CENTER ACTIVATION Site experienced high winds and sustained weather related damage to mobile offices and isolated site power outages. Plant wide assessment in progress. Plant systems are still operational and have not been impacted by the wind damage. No chemical hazards have been identified at this time. AC power was lost to the offsite Public Warning System sirens, but battery power available for 72 hours. Licensee has requested expedited action from the electric utility company to return AC power to the siren system. The site EOC was activated to assist the on shift personnel with weather damage assessment and the licensee was in an Unclassified Emergency. The licensee notified the McCracken County Sheriff's Dispatch office, Kentucky Division of Emergency Management, and the DOE Oak Ridge Operations Center. * * * UPDATE PROVIDED AT 1339 EDT ON 09/14/08 FROM STEVE WAGNER TO JEFF ROTTON * * * Licensee provided a courtesy notification that they had terminated their unclassified emergency at 1232 CDT and deactivated their EOC. All damage to the site was minor and they have established recovery teams. The licensee notified the NRC Resident Inspector. Notified IRDMOC (McMurtray), R2DO (Payne) and NMSS EO (Brach) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-09-14
44485 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2008-09-14 02:41 | 2008-09-14 06:07 | 2008-09-14 | DROPPED CONTROL ELEMENT RESULTING IN ENTRY INTO TECHNICAL SPECIFICATION REQUIRED SHUTDOWN LCO "At 23:45 on 9/13/08, one control element assembly (CEA) dropped to the bottom of the core from the upper electrical limit. Technical Specification LCO 3.1.3.1 Action e. was entered. The CEA was not able to be realigned with the other CEA's in its group within the time constraints of the COLR. Technical Specification LCO 3.1.3.1 Action f. was entered and a down power to 70% was initiated. Actions to repair and retrieve the CEA could not be completed within the time constraint of LCO 3.1.3.1 Action f. and a shutdown was commenced to comply with Technical Specifications at 0241 on 9/14/08. The CEA was recovered and restored to OPERABLE at 0258 on 9/14/08 and the shutdown was halted. The plant is currently being returned to full power operation. This four hour non-emergency report is being made pursuant to 10 CFR 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by Technical Specifications.'" The licensee notified the NRC Resident Inspector. | 68 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-09-14
44484 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-09-11 22:47 | 2008-09-12 01:54 | 2008-09-12 | REACTOR SCRAM AND ISOLATION DUE TO TRANSFORMER LOCKOUT While the 1R transformer was out of service for maintenance, the 2R transformer experienced a lockout resulting in a loss of normal offsite power, a reactor scram, and a Group 1, 2 and 3 isolation. All rods fully inserted as expected. The cause of the 2R transformer lockout is unknown at this time. After initiation, the high pressure coolant injection (HPCI) system would not trip at the high reactor water level set point +48", as required. The operators then manually isolated the HPCI steam lines. Plant decay heat removal is with the reactor core isolation cooling (RCIC) system and the safety relief valves. Torus cooling is in service. The vital electrical busses are being supplied by the 1AR transformer. Efforts are underway to restore the 1R transformer to service, and subsequently the non-vital busses. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY KIM HOFFMAN TO JASON KOZAL AT 0655 ON 09/12/08 * * * The HPCI system was declared inoperable and isolated due to failure to automatically trip at +48" Reactor Water Level. The HPCI steam supply valves were automatically closed to remove HPCI from service. In addition, the HPCI turbine trip failed to trip with the turbine trip push button. The cause of the trip failure is unknown at this time. The licensee is continuing to investigate. HPCI did automatically start as designed and injected to the reactor vessel as designed. However, HPCI failed to trip at High Reactor Water Level as required. "Additionally, the Automatic Depressurization System (ADS) timer showed erratic indication following the event. The ADS timer was inhibited to prevent automatic action. ADS is inoperable, but manual steam relief valve operation remains available." The licensee will notify the NRC Resident Inspector. Notified R3DO (Passehl), NRR EO (Ross-Lee), and IRD (McMurtray). * * * UPDATE PROVIDED BY SCHREIFELS TO CROUCH AT 1656 EDT ON 09/12/08 * * * "A [second] Group 2 isolation signal was received when reactor water level lowered below +9 [inches] [while pumping drywell sumps]. All Group 2 valves except the drywell sump isolation valves were closed due to a previously reported Group 2 signal. The drywell sump valves had been opened to allow manual pumpdown of the sumps. The sump valves closed as expected." Licensee notified the NRC Resident Inspector. Notified R3DO (Passehl). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | POT RHR INOP |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  | 0 | 2008-09-12
44483 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2008-09-11 21:35 | 2008-09-11 22:45 | 2008-09-11 | OFFSITE NOTIFICATION DUE TO WORK-RELATED FATALITY "On Tuesday, September 9, 2008 a maintenance contractor suffered an apparent heart attack at approximately 0900. On site Medical Emergency Response personnel responded until ambulatory transport to Oconee Medical Center and then Greenville Memorial Hospital. On Thursday, September 11, 2008 at 1755 he passed away at Greenville Memorial Hospital. "At 2135 on September 11, 2008, Oconee Environmental Health and Safety notified OSHA due to the death of an Oconee contractor. This notification is being made in accordance with Duke Energy Corporation administrative procedures due to notification of a federal agency. "Licensee notified the NRC Resident Inspector." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-09-17
44482 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-09-11 12:00 | 2008-09-11 18:55 | 2008-09-11 | UNANALYZED CONDITION RELATED TO CERTAIN FIRE CONDITIONS "During an NRC [Triennial Fire] Inspection, a condition was identified in which, under certain fire conditions, possible damage scenarios, and required operator actions, the ability to meet the performance criteria of the approved fire protection program may be challenged. Specifically it was postulated under certain fire conditions affecting the relay room, the ability to maintain pressurizer level within indicated range (high) may be challenged due a spurious opening of a pressurizer power operated relief valve. "Compensatory actions to address the fire in the area of concern are in place. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-09-11
44481 | -1 | WOMACK ARMY MEDICAL CENTER |  |  |  |  | 2008-08-30 15:24 | 2008-09-11 16:10 | 2008-09-12 | SURFACE CONTAMINATION ON RECEIVED PACKAGE EXCEEDING LIMITS At 1600 EDT on 09/11/08, the RSO was notified of a contamination event by the Chief of Nuclear Medicine who was also notified today by the technician involved. The event occurred on Saturday, 08/30/08 at 1524 EDT when a technician received a Technetium 99 package from Cardinal Health in Fayetteville, NC for patient treatment. Initial swipe survey of package external surfaces showed 13,000 dpm of gamma contamination. Package was decontaminated to 1620 dpm and stored in the Hot Lab to decay and picked up on Monday, 09/01/08, by Cardinal Health with no contamination. The hospital is not aware of any internal contamination from the package, but will get a full statement from the technician involved on 09/13/08. Cardinal Health will be notified of the contamination issue on 09/13/08. * * * RETRACTION PROVIDED AT 1630 EDT ON 09/12/08 FROM CAPT BALDOCK TO JEFF ROTTON * * * Further investigation and discussion with NRC Region 1 DNMS (Michelle Simmons) has determined that the event is not reportable since the contamination level was below the maximum permissible limit of 220 dpm/sq cm for beta and gamma emitters. Notified R1DO (Lorson) and FSME (Luehman). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | NC | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2008-09-11
44480 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-09-10 17:11 | 2008-09-10 19:30 | 2008-09-10 | TECHNICAL SUPPORT CENTER HVAC EMERGENCY BACKUP POWER SOURCE OUT OF SERVICE "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action B.2. The functionality of the Technical Support Center has been lost due to the failure of the TSC HVAC emergency backup power source. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with a high priority. "The NRC resident Inspector has been notified." | 100 | 93 | 0 | 100 | 93 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-10
44479 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-07-25 | 2008-09-10 15:05 | 2008-09-10 | AGREEMENT STATE REPORT - TWO WORKERS BRIEFLY EXPOSED TO CESIUM SOURCE "Jacksonville inspection office was called to report that today 25 July 2008 at 1:30pm, two workers from Georgia Pacific were briefly and inadvertently exposed to an unlocked beam from a Cesium-137 source. Source is part of a 50,000 gal. storage vessel. It was reported that the maximum dose received by the workers was 0.0104 rem to hands only. "Investigation found that Georgia-Pacific did not follow proper procedures. Corrective action consists of training, and revising walk down sheets to provide verification and documentation of the lockout. This office will take no further action on this incident." The source strength was 1098 mCi. This is Florida Incident Number FL08-110. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-09-15
44478 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2008-09-08 19:15 | 2008-09-09 20:16 | 2008-09-09 | NON LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL "At approximately 1915 PDT on September 8, 2008 at Columbia Generating Station a non-licensed supervisor was determined to be unfit for scheduled work due to the consumption of alcohol based on a preliminary for cause test. The individual was not allowed to take the watch. The incident is being evaluated in accordance with station procedures and policies. This event is being reported pursuant to 10 CFR 26.[719]. "The NRC resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2008-09-09
44477 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-08-06 | 2008-09-09 11:22 | 2008-09-09 | AGREEMENT STATE REPORT - MISSING PALLADIUM 103 SEEDS The State of Florida provided the following information via facsimile: "21st Oncology was performing a medical procedure under the license of North Okaloosa Medical Center on 9 July 2008. Pd-103 with 114 seeds (126.5 mCi as of July 9, 2008) were used. Source strength was thought to be too low for procedure. Seeds were put in a lock box at the surgery center. Seeds were visually checked as present on 11 July 2008. "Seeds were sent back to Triad Radiopharmaceutical on 25 July 2008. Triad reported that shipping container was empty upon receipt at their facility on 6 Aug. 2008. Facility was thoroughly searched and also the dumpster. Surgery Center was under renovation between 11 July and 25 July. Some discrepancy between charge nurse and Med. Physicist if lock box was locked after 11 July. "Radioactive Materials Office will investigate." This report is also identified as Florida Incident Number FL08-127. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-09-12
44476 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-08-17 | 2008-09-09 09:46 | 2008-09-09 | AGREEMENT STATE - INDUSTRIAL RADIOGRAPHER OVEREXPOSURE The following was provided by the state via facsimile: "On August 19, 2008, Hi Tech Testing reported an overexposure to an industrial radiographer. On August 17, 2008, two industrial radiographers noticed that their pocket dosimeters were 'off scale'. Their film badges were sent to Landauer for emergency processing and it was determined that one of the radiographer's dose for August 2008 was 3.719 rem. Adding this to the year to date dose for this radiographer gave the radiographer a year to date dose of 5.776 rem for 2008. Hi Tech Testing investigated the incident and determined that the radiographers were not using a survey meter or performing a proper survey after each exposure. The following corrective action was taken for this incident: The radiographer that had the excessive exposure has had his employment with Hi Tech Testing terminated. Hi Tech Testing also had a mandatory company safety meeting concerning this incident." Louisiana report number - LA0800017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-09-12
44475 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-09-09 05:30 | 2008-09-09 10:24 | 2008-09-09 | OFFSITE NOTIFICATION DUE TO CAR ACCIDENT "At approximately 0530 CDT hours, a car accident occurred on the driveway of the parking lot at the Prairie Island Nuclear Plant. The driver of the vehicle was not a plant employee. The driver left the scene of the accident. Plant security and local law enforcement are investigating. No press release is planned." The licensee notified the NRC Resident Inspector, the Emergency Management agencies of Goodhue, Dakota, and Pierce counties, the State of Wisconsin and the Prairie Island Tribal council. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-09-09
44474 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-09-08 | 2008-09-09 09:04 | 2008-09-09 | AGREEMENT STATE - AMERICIUM 241 LEVELING DEVICE MISSING "On September 9, 2008, the Agency was notified by the Radiation Safety Officer (RSO) that while conducting source leak surveys on installed generally licensed devices, a device containing 100 millicuries of Americium (Am) - 241 could not be located. The device was installed on a component that had been removed from the product line and placed in an area of the facility frequented by vagrants. The area where the device had been stored had been vandalized and much of the steel and copper from various components had been removed. The RSO stated that all other sources listed on their license were installed on components still in operation and were verified intact. The facility has increased its security and their security team is searching for the source. Additional information will follow as it is obtained." Texas Incident #: I 8554 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-09-12
44473 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-09-09 06:45 | 2008-09-09 07:40 | 2008-09-18 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO VITAL AREA Attempted introduction of contraband into vital area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION AT 1529 EDT ON 09/18/08 FROM PAUL UNDERWOOD TO JEFF ROTTON * * * Licensee review determined that event was not reportable. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified the R2DO (Ernstes). Notified Part 73.71 group via email. | 85 | 100 | 0 | 85 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-09-09
44472 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-09-08 07:30 | 2008-09-08 12:34 | 2008-09-08 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The licensee discovered that a Troxler moisture/density gauge was stolen sometime between 1600 CDT on 09/07/08 and 0730 CDT on 09/08/08. This was a Troxler Model 3430, S/N 29518 with two sources of 10mCi, Cs-137 and 40mCi, AmBe-241 stolen from a FUGRO consultants Inc. employee from a private residence in Waco, TX. This was reported to the Cities of Waco and Woodway Police Departments and filed under case # 08-21954 for the former. Please refer to TX incident # I-8551. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-09-11
44471 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-09-07 17:20 | 2008-09-07 23:12 | 2008-09-07 | PARTIAL LOSS OF OFFSITE COMMUNICATION CAPABILITY CAUSED BY AN UNPLANNED POWER OUTAGE "On 09/07/2008 at 1720 CDT, Browns Ferry Nuclear Plant experienced a partial loss of offsite communication to include the Emergency Notification System to the NRC, normal phone communication to offsite, the Operations Duty Specialist ring down phone to Chattanooga and the satellite phone to offsite located in the control room. This loss of communications was the result of an unplanned electrical power outage due to loss of temporary diesel generator supplying power to the communications network. The control room indications and assessment capability were not affected. Cell phones and the Health Physics Radio Network were available to be used onsite to communicate offsite. The plant radio system and sound powered phones were unaffected and plant staff communication capability was available. "Communication capability was restored at 1758 CDT 09/07/2008. "Operation of Unit 1, Unit 2 and Unit 3 was not affected by the event. "The NRC Sr. Resident Inspector has been notified. "This event is reportable under 10CFR50.72(b)(3)(xiii), 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System or offsite notification system.'" | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-09-07
44470 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-09-07 08:05 | 2008-09-07 14:45 | 2008-10-31 | ISOLATION CONDENSER DECLARED INOPERABLE FOLLOWING SURVEILLANCE TESTING "Unit 2 Isolation Condenser did not meet acceptance criteria per DOS 1300-01 Isolation Condenser 5 year heat removal capability test. This is a single train system and cannot fulfill its safety function. The Isolation Condenser is a single train system. The function of the IC System is to respond to main steam SAFETY ANALYSES line isolation events by providing core cooling to the reactor. The IC System is an Engineered Safety Feature System, and credit is taken in the loss of feedwater transient analysis for IC System operation." Unit 2 entered a 14-day TS LCO A/S 3.5.3 at 0249 CDT on 09/07/08 after declaring the IC System Inoperable. The Action Statement (A/S) requires restoration of the IC System to Operable status within 14 days or place the unit in hot shutdown within 12 hrs followed by entry into cold shutdown in the following 24 hrs. The licensee is performing maintenance to adjust the cooling flow valve stroke time in order to re-test and exit the LCO A/S. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1318 EDT ON 10/31/08 FROM SCOTT BRILEY TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this notification is to retract ENS notification 44470 made on September 7, 2008 for Dresden Nuclear Power Station. After further evaluation, Dresden has determined that the Isolation Condenser did successfully pass its 5-year heat removal test on September 7, 2008. The evaluation corrected the steam flow rate based on a more accurate instrument and calculated the heat removal rate by multiplying the mass flow rate through the Isolation Condenser times the difference in enthalpy between the steam going to the condenser and the condensate leaving the condenser. Therefore, the Isolation Condenser was capable of performing its safety function and the ENS report is being retracted." The licensee informed the NRC Resident Inspector. Notified R3DO (Kozak). | 0 | 67 | 0 | 0 | 67 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-09-07
44469 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2008-09-02 | 2008-09-05 20:45 | 2008-10-02 | AGREEMENT STATE - OVEREXPOSURE FROM STUCK RADIOGRAPHY SOURCE The following information was provided by the State of Oklahoma via e-mail: "On Tuesday, September 2, radiographers were doing pipeline weld testing near Ardmore, Oklahoma. They were operating in a three man team, the radiographer (who held a current Texas card) would move ahead of the group dropping off film at each weld. Assistant #1 moved behind him putting the film in place on each weld. Assistant #2 followed with the radiography camera balanced behind him on the seat of a 4-wheeled All Terrain Vehicle (ATV) and would position the camera and take the shots at each weld. The camera and guide tube where not disassembled between shots. "At approximately 10 AM Tuesday, the camera fell off the ATV while being transported, and the guide tube bent where it attaches to the camera. One of the assistants was able to straighten the guide tube, and they were able to crank the source in and out, though with increased resistance. They continued working with this guide tube, though they report they had another guide tube available at the site. "At approximately Noon Tuesday, assistant #2 decided the terrain near the next weld was too rugged to drive the ATV over, so he dismounted and disassembled the radiography setup to carry it to the weld. When he unscrewed the guide tube, he saw the cable inside, and realized the source was not secured inside the camera. The crew was able to retract the source into the camera. Assistant #2's pocket dosimeter was reading off scale. When his alarming rate meter was tested, it did not work. The utilization log for the morning states that the alarming rate meter did work when checked out in the morning. State investigators could not get the alarming rate meter to work, and they believe the batteries are dead, though they did not test to confirm that. Assistant #2 had a survey meter, but was not checking it at the time of the incident. Note that state investigators found that the crew had two calibrated survey meters, but one of them was damaged and not operational. The crew states that the meter was working at the time of the incident, but had been damaged on Friday morning as the other two crew members continued to work. "Assistant #2 ceased work, and his badge was sent for emergency processing. The badge provider reports a whole body dose of 16 rem. A representative of the company contacted the state of Oklahoma shortly after receiving the report. The company did not contact Oklahoma before receiving the report. The company states that Louisiana has been informed of the incident. "Assistant #2 states that he rode the ATV with the camera on the seat of the ATV behind him. Distance from the camera to his body was about one foot, and it is believed that this is similar to the distance from the source to his body. He estimates that he spent 2-3 minutes riding this way between the prior shot and the time he noticed that the source was not properly retracted. The crew states that film from prior shots has been developed and shows no anomalies or signs of overexposure. The crew states that Assistant #2 was the only person who worked with the camera from the time the tube was damaged till the incident was discovered. Assistant #2 states he does not remember whether his badge was on his front pocket or back pocket. If it was worn on his front pocket, the dose reported for him is probably lower than his actual dose. "A representative of the company is coming from Louisiana to Oklahoma to return Assistant #2 to Louisiana. Oklahoma will encourage the company to have him examined by a physician with a strong radiation background, seeking the advice of the state of Louisiana on a suitable physician. "The above is a preliminary report based on telephonic communication with DEQ inspectors in the field, and is basically all that is known at this time. It has not been reviewed by the inspectors. DEQ will investigate, do enforcement, and keep NRC and Louisiana informed of the progress of our investigation." The State noted that Nondestructive and Visual Inspection dba NVI has a Louisiana License (LA-5601 L01) out of Houma, Louisiana and had been operating in Oklahoma under reciprocity. The company home office has been heavily affected by Hurricane Gustav and company staff stated that they had just returned to their office for the first time on 9/5/08. * * * UPDATE FROM LOUISIANA DEPT. OF ENVIRONMENTAL QUALITY (RICHARD PENROD) TO PETE SNYDER ON 9/8/08 AT 1050 EDT * * * The State of Louisiana provided the following information via facsimile: This event has been identified State of Louisiana Event Report ID No. LA0800018. * * * UPDATE FROM MIKE BRODERICK TO PETE SNYDER ON 9/8/08 AT 1040 AND 1144 EDT * * * The following is a summary of information provided by the State of Oklahoma via e-mail: The source strength and isotope of the source referred to in the original report was 111 curies of Ir-192. The State of Louisiana requested blood work be done on the exposed individual. The company RSO had been unable to find a physician to do the work in Louisiana because of the recent tropical storm but did solicit help from REAC T/S where blood samples were sent for evaluation on 9/8/08. Notified R4DO (Walker) and FSME (Flannery). * * * UPDATE FROM MIKE BRODERICK TO PETE SNYDER ON 9/10/08 AT 1036 AND 1226 EDT * * * "The last sentence of the [9/8/08 update] (about blood samples being sent to REACT/S on 9/8) is incorrect. No blood samples have been sent to REACT/S. "There are actually two different sets of blood samples, one (several samples) to be processed locally, and one (a single sample) to be processed by REACT/S. REACT/S has sent the special container needed to the licensee in Louisiana, and the blood sample will be drawn on Monday and shipped overnight to Oak Ridge for processing." "[On 9/9/08] the affected individual saw an occupational physician and the blood samples were drawn. The licensee [will] provide these results to DEQ and REACT/S as soon as they are available. The physician inspected the individual for signs of acute radiation exposure and found none. "The licensee RSO reports that he spoke to the exposed individual by phone." The individual did not report any symptoms. Notified R4DO (Walker) and FSME (Flannery). * * * UPDATE AT 1714 ON 10/2/2008 FROM MIKE BRODERICK TO MARK ABRAMOVITZ * * * Received from the state via e-mail: "REACT/S reports their Cytogenic dosimetry estimate for the exposed individual is 0 to 30 rem, with a most likely result of 11 rem. This is consistent with the 16 rem reported already." Notified the R4DO (Bywater) and FSME (Bradford). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-09-10
44468 | 0 | US AIR FORCE |  |  |  |  | 2008-06-04 | 2008-09-05 19:50 | 2008-09-05 | REPORT INVOLVING A PATIENT WITH AN UNDETECTED PREGNANCY WHO RECEIVED THERAPEUTIC I-131 TREATMENT On 06/02/08, a female patient was tested for pregnancy prior to receiving a therapeutic Iodine-131 (I-131) dose at the Wilford Hall Medical Center located on Lackland AFB near San Antonio, TX. The serum screening result was negative. A dose of 149.2 millicuries I-131 was subsequently administered on 06/04/08 with no complications. On 08/13/08, the patient was informed she was pregnant. Follow-up consultation with the REAC (Radiation Emergency Assistance Center) and calculations determined that the dose to the fetus was approximately 31.5 Rad. However, since the incident occurred early in the zygote phase of development there is no anticipated adverse consequences. The Air Force Radioisotope Committee was notified of this incident on 08/27/08. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.3047(a) |  |  |  | 0 | 2008-09-05
44467 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-09-05 17:00 | 2008-09-05 18:52 | 2008-09-05 | OFFSITE NOTIFICATION TO THE EPA AS REQUIRED DUE TO A REFRIGERANT APPLIANCE REPAIR DELAY "In accordance with Title 40 Code of Federal Regulations, Part 82, Subpart F, Wolf Creek Nuclear Operating Corporation (WCNOC) reported a refrigerant appliance repair delay to the US Environmental Protection Agency - Region 7. This unit involved is subject to the 15% leak rate threshold and the 30-day repair requirement applicable to a comfort-cooling appliance. WCNOC has requested additional time be permitted to conduct the required repairs on this appliance due to the unavailability of parts. The appliance is located at the Wolf Creek Generating Station, on the roof of the building that houses the maintenance support staff." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-09-05
44466 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-09-05 16:00 | 2008-09-05 16:14 | 2008-09-05 | SAFEGUARDS REPORT - UNAUTHORIZED ACCESS BASED ON FAILURE TO DISCLOSE INFORMATION Actual entry of an unauthorized person into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-09-05
44465 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2008-07-23 23:25 | 2008-09-05 08:45 | 2008-09-05 | INVALID SYSTEM ACTUATION DUE TO LOSS OF ONE OFFSITE POWER CIRCUIT TO SAFETY BUSES "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Units 2 and 3 Primary Containment Isolation Systems (PCIS). On 7/23/08, at approximately 2325 hours, Units 2 and 3 experienced invalid Primary Containment Isolation System (PCIS) partial isolations. Unit 2 experienced an outboard PCIS Group II isolation, while Unit 3 experienced inboard and outboard PCIS Group II isolations. The isolations involved various process lines including Reactor Water Cleanup (RWCU), Containment Atmospheric Control (CAC) / Containment Atmospheric Dilution (CAD), Drywell Sumps, and Containment Instrument Nitrogen. The Units 2 and 3 PCIS isolations were reset by approximately 2350 hours in accordance with procedures. All required isolation valves operated as designed. "The invalid PCIS isolations were a result of a fast transfer on associated 4 kV safety-related electrical buses for Units 2 and 3 caused by a loss of one of the two off-site power circuits that supply the 4 kV buses. This fast transfer resulted in a momentary voltage transient on electrical power supplies to the logic for the Units 2 and 3 PCIS. The two station off-site power circuits are fed from three offsite sources. The loss of the offsite power circuit was caused by failure of the 'A' phase of the '#1' transformer, which is associated with one of the three offsite power sources. This transformer is located at the North Substation. The transformer automatically isolated as a result of a fire associated with this transformer and resulted in the loss of two of the three offsite power sources. Subsequent to fire extinguishment, appropriate electrical switching was performed and the offsite power circuit was returned to an operable status by 0650 hours on 7/24/08. "This issue has been entered into the site Corrective Action Program (CR 799684, 811332) for evaluation and implementation of further corrective actions including determining why two offsite sources were lost as a result of the transformer failure. The NRC resident has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-09-05
44464 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-08-08 | 2008-09-04 18:13 | 2008-09-04 | AGREEMENT STATE REPORT INVOLVING A LOST OR STOLEN TRITIUM EXIT SIGN The following report was received via email from the State of Washington: "On August 22, 2008 the department received a report of missing GL radioactive material by a property manager of an apartment building in Seattle, Washington. The device is a Tritium exit sign light module, manufactured by Shield Source Incorporated of Ontario, Canada. Calculations indicate that on August 27, 2008, the source activity was 251 GBq (6.8 curies) of Hydrogen-3. The last known location of the device and radioactive source was in an apartment building located at 1535 Bellevue Ave, Seattle, Washington. The device was discovered missing by the apartment manager's maintenance staff sometime around August 8, 2008. When the maintenance person called an exit sign distributor to order a replacement exit sign, the distributor told the individual to report the missing exit sign to the department. "Keywords: MATERIAL STOLEN AND NOT RECOVERED "Form of Radioactive Material: SEALED SOURCE "Manufacturer: SHIELD SOURCE INC "Model Number: NR "Radionuclide or Voltage (kVp/MeV): H-3 "Source Use: SELF LUMINOUS Activity: 6.8 Ci [or] 251.6 GBq "Device Name: RADIOLUMINESCENT SIGN "Manufacturer: SHIELD SOURCE INC "Model Number: EITHER 101 OR 201 "Reference Number: WA-08-059" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-09-09
44463 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-09-03 23:43 | 2008-09-04 05:04 | 2008-09-04 | FAILURE OF DAMPERS TO AUTO CLOSE "Due to RPS A Circuit Protector surveillance testing, a transfer of 'A' Reactor Protection System from alternate power supply back to the 1A RPS MG-set was required. An expected group 6 containment isolation signal was received during the power transfer. Upon review of plant status to ensure systems responded as expected, it was determined that reactor ventilation zone exhaust dampers 1-DMP-64-42 and 1-DMP-64-43 (Inboard and Outboard Reactor Zone Exhaust Dampers) failed to auto-close. Isolation of these dampers is a required safety function. "The dampers were administratively closed and deactivated in accordance with plant technical specification 3.6.4.2 action B. At the time of this report the cause for failure to auto close has not been determined." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2008-09-04
44462 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-09-03 13:36 | 2008-09-03 15:02 | 2008-09-03 | SAFEGUARDS REPORT - SECURITY MEASURES MODIFIED DUE TO INCLEMENT WEATHER The licensee provided a 1 hour report in accordance with Chapter 19 of the Physical Security Plan to report changes to the Physical Security Plan based on inclement weather conditions. Compensatory action have been taken. Contact the HOO for additional information. The NRC Resident Inspector has been notified. * * * UPDATE AT 1617 EDT ON 9/3/08 FROM BROWN TO HUFFMAN * * * The licensee restored the normal security features of the Physical Security Plan effective 1415 CDT based on passing of inclement weather conditions. The NRC Resident Inspector will be notified. R4DO (Jones) notified and an e-mail of this report was also sent to the NRC 73.71 group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW | [5 empty] | 1 | 2008-09-03
44461 | -1 | QUEENS MEDICAL CENTER |  |  |  |  | 2008-06-02 | 2008-09-03 14:01 | 2008-09-05 | POTENTIAL MISADMINISTRATION GREATER THAN 20% OF PRESCRIBED DOSE The RSO performed a quarterly audit on 9/2/08 and discovered that a misadministration greater than 20% of prescribed dose and greater than 50 Rem to the lung tissue occurred on 6/2/08. The prescribed dose was 1.0 ml of P-32 chromic phosphate into two separate syringe applications. The technician prepared the first P-32 dose into syringe "A" and recorded into the written record after calibrated assay as 1.3 ml and performed the same procedure for the second dose which was recorded into the written record as 1.0 ml into syringe "B". The first dose in syringe "A" exceeded the allowable dose. Both syringe applications were given to the patient into separate lung tube injections. The prescribing physician and authorized user have been notified. It is not known if the patient has been notified. * * * RETRACTION AT 1545 EDT ON 9/5/08 FROM OYTOMARI TO SANDIN * * * Based on further review of this event by the licensee, it was determined that the total dose to the lung was less than 50 Rem. As a result, the event does not meet reportability criteria under 10CFR35.3045. The licensee has reviewed its conclusion with NRC Region 4 inspectors (Whitten and Munoz). R4DO (Jones) and FSME (Turtil) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-09-05
44460 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-15 | 2008-09-03 12:49 | 2008-09-03 | AGREEMENT STATE REPORT - IRRADIATOR CRANK MECHANISM FAILURE "On 9/2/08 at 16:30, the [Texas Department of State Health Services] received a letter from the licensee stating that on 8/15/08, they were unable to move the source head on a U.S. Nuclear Model E-0103 Irradiator. The device contains a Cesium (Cs) - 137 source with an estimated activity of 2251 curies and is used in research irradiation of in vitro samples. The source is fully shielded. Dose rates and contamination surveys conducted on the source head were normal. The unit has been taken out of service awaiting repairs." TX Incident # I-8547 * * * UPDATE RECEIVED FROM ART TUCKER TO JOE O'HARA VIA E-MAIL AT 1538 ON 9/3/08 * * * "The RSO called at 1444 and stated that he had some corrected information. He stated that the device contained two 2660 curie Cs 137 sources installed in 1975 and manufactured on 2/15/68 making the current activity 1045 curies each. He stated that the device had been repaired, but was still trying to find out when." Notified R4DO(Jones), FSME(Turtil). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-09-08
44459 | 0 | HUNTINGTON TESTING SERVICES |  |  |  |  | 2008-08-20 21:00 | 2008-09-03 11:26 | 2008-09-03 | SAFETY EQUIPMENT FAILURE On August 20, 2008, radiographers from Huntington Testing Services were performing radiography on a tank at the Clifty Creek Power Plant, located in Madison, Indiana, when a magnetic base fell and crimped the camera guide tube. At the time the damage to the guide tube occurred, the source was in the collimator. The crimped tube would not allow the radiographer to retract the source back into the shielded position. The radiographer immediately established a boundary and covered the source with lead shot bags, then contacted the Radiation Safety Officer (RSO). When the RSO arrived at the location, he was able to repair the guide tube enough to enable the source to be retracted into the shielded position. The camera was then transported back to the Louisville, Ky office of Huntington Testing Services. The guide tube has been replaced and the camera is available for service. The licensee is investigating the incident to determine corrective actions. There were no overexposures as a result of this incident. The camera was temporarily transferred from Huntington Testing Services' Kentucky license to their NRC license (issued in West Virginia) since Kentucky and Indiana do not have reciprocity. The camera is a QSA Global 880 Sigma, serial number S1453 with a 85.3 Curie Ir-192 current source strength. Source strength at manufacture date was 103.9 Curies. The source serial number is 48578B. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-09-03
44458 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-09-02 16:48 | 2008-09-02 17:55 | 2008-09-02 | OFFSITE NOTIFICATION DUE TO POTENTIAL WATER FLEA REPRODUCTION RATE DECREASE "The quarterly National Pollutant Discharge Elimination System whole effluent toxicity testing for outfall #002 failed for August 2008. This required notification to the South Carolina Environmental Agency. The system is the Conventional Waste (WC) system. The licensee will be contacting the NRC Resident Inspector. "A toxicity report is being performed by an outside lab." The licensee took a water flea controlled sample and determined that the water flea reproduction rate in the sample is not the same as the rate in the discharge stream. The licensee will also inform York County, Gaston County, Mecklenberg County, and the State of North Carolina. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-09-02
44457 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-09-01 18:02 | 2008-09-01 23:33 | 2008-09-01 | PLANNED MANUAL PLANT SHUTDOWN DUE TO GRID CONDITIONS "Voluntary Report of Planned Manual Plant Shutdown. At 1802 on September 1, 2008, River Bend Station [RBS] completed a planned manual shutdown of the unit. This shutdown was determined to be necessary based on the conditions of the grid due to Hurricane Gustav. Evaluation of grid conditions determined that removing the unit from power operation would improve the reliability of the grid and thus the decision was made to shutdown. Offsite power was declared inoperable at 1520 on September 1 based on notification of grid status by the grid operator. It is expected that offsite power will be restored to an operable status within the 24 hour LCO Required Action Completion Time. In addition, damage to turbine building siding was reported. Assessment of this condition is being conducted. RBS had previously activated the Outage Control Center prior to the arrival of Hurricane Gustav. Additional resources are available on site to respond to plant conditions. A comprehensive assessment of the condition of the plant and other site facilities will be completed prior to restart. At this time, a schedule for restart has not been established." The licensee contacted the NRC Resident Inspector. | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2008-09-02
44456 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-09-01 10:35 | 2008-09-01 17:03 | 2008-09-01 | SHUTDOWN DUE TO EMERGENCY DIESEL GENERATOR SHORTING RING CRACKS "On September 1, 2008, at about 1035 PDT, Southern California Edison (SCE) began a planned shutdown of San Onofre Unit 3. This shutdown is in anticipation of exceeding the Allowed Outage Time (AOT) of 14 days of Technical Specification 3.8.1 Action B.4 for an inoperable Diesel Generator (Train B). The AOT is due to expire on September 2, 2008 at about 0200. If the system cannot be restored within the allowed outage time, a plant shutdown is required. The initiation of this shutdown is being reported in accordance with 10CFR50.72(b)(2)(i). "An inspection of the DG generator revealed cracks in the shorting ring, requiring replacement of the generator. Post maintenance testing performed after replacement revealed anomalous readings. SCE determined that problem identification, repair and post test could not be performed before expiration of the AOT. Consequently, shutdown has been initiated. "At the initiation of the shutdown, SONGS Unit 3 was operating at full power. SONGS Unit 2 is operating at approximately 99 percent power. "The NRC Resident Inspectors have been briefed on the shutdown plans and will be provided with a copy of this report." | 0 | 0 | 46 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-09-01
44455 | 0 | WATERFORD | 3 |  |  | [3] CE | 2008-09-01 06:27 | 2008-09-01 07:44 | 2008-09-01 | SAFEGUARDS REPORTS - SECURITY MEASURES MODIFIED DUE TO HURRICANE GUSTAV Specific security measures have been temporarily suspended or modified due to imminent severe/hazardous weather conditions associated with hurricane Gustav. Alternate security measures have been initiated when and where possible based on weather limitations and personnel safety concerns. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JERRY GRUBB TO PETE SNYDER AT 2156 ON 9/1/08 * * * Specific security measures have returned to normal. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-09-01
44454 | 0 | WATERFORD | 3 |  |  | [3] CE | 2008-08-31 23:00 | 2008-09-01 00:16 | 2008-09-04 | NOTIFICATION OF UNUSUAL EVENT DUE TO HURRICANE WARNING ONSITE Site declared a notification of unusual event under HU6/ EAL 7. The site is predicted to experience hurricane force winds from Gustav. As a conservative measure, the plant shutdown was completed at 2232 CDT. The licensee has notified the NRC Resident Inspector, state and local emergency management agencies. Notified DHS (Hill) and FEMA (Blankenship). * * * UPDATE AT 0126 ON 9/4/2008 FROM JERRY GRUBB TO MARK ABRAMOVITZ * * * The site has exited the Notification of Unusual Event (NUE) at 0021 CDT because 1) grid stability has been restored, 2) HU6/EAL 7 is no longer applicable (Hurricane Gustav is no longer affecting the site), and 3) the NUE for leakage greater than 25 gpm (SU7/EAL 2) is no longer applicable (entered at 0726 on 9/1/2008 and terminated at 0729 on 9/1/2008). The reactor is in mode-4 (Hot Shutdown). Notified the R4DO (Jones), NRR (Blount), IRD (Gott), DHS (Dub), and FEMA (Casto). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 4 | LA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-09-01
44453 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-08-30 15:03 | 2008-08-30 17:47 | 2008-08-30 | TURBINE ELECTRO-HYDRAULIC CONTROL MALFUNCTION LEADS TO REACTOR SCRAM "At 1503 hours EDT, an Electro-Hydraulic Control (EHC) system malfunction caused the Unit 2 Main Turbine bypass valves (BPV) to start cycling. Initially, BPV 1 partially opened and closed followed shortly thereafter by four BPVs going full open. At that time the order was given to insert a manual scram. An automatic scram signal occurred just as the operator was beginning to insert the manual scram. "Preliminary investigation of the automatic scram signal indicates that it was initiated by low Relay Emergency Trip Supply (RETS) pressure to the main turbine control valves due to the EHC malfunction. Reactor water level momentarily dropped below Low Level during the response. This resulted in Primary Containment Isolation System (PCIS) Group 2 and Group 6 isolations, as expected. "All control rods fully inserted. All systems responded as designed. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) due to the Reactor Protection System actuation and 10 CFR 50.72(b)(3)(iv)(A) due to the PCIS Group 2 and Group 6 actuations. "Unit 1 was not affected by this event and remains at 100% power. The NRC resident inspector has been notified." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-08-30
44452 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-29 | 2008-08-29 15:18 | 2008-08-29 | AGREEMENT STATE REPORT - LEVEL GAUGE SHUTTER MALFUNCTION "On 8/29/08, Incident Investigation Program received a letter from the licensee stating that on June 23, 2008 while conducting their routine surveillance, a Ohmart/VEGA level gauge used on their vent stack for level detection failed the inspection when the shutter mechanism failed to close fully. An inspection of the gauge found that a bolt on the operating handle had sheared and the shutter would not close. The gauge contains one 200 millicurie Cesium (Cs) - 137 source serial # M-7089. The licensee has contacted the manufacturer and is working with them to schedule the repair of the gauge. Surveys conducted by the licensee has determined that dose rates in the area of the gauge are normal and do not pose a risk of exposures to their workers. The source has been labeled 'Do Not Operate - Contact Site RSO'." This event is also identified as Texas event number I-8546. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-09-03
44451 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2008-08-28 16:10 | 2008-08-29 12:43 | 2008-09-02 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE "On the afternoon of August 28, 2008 at approximately 4:10 pm, the [Alabama Department of Public Health (ADPH)] received a call [from the] RSO for Birmingham Engineering and Construction Company (BECC). [The RSO] advised [ADPH] that one of his technicians had lost a Troxler model 3440 (serial number 17775) containing Cs-137 and Am-241/Be radioactive sources somewhere in the Birmingham area. "As described by [the RSO], the technician placed the gauge on the back of his pickup without properly securing it in the transport container. After completing his paperwork, he then proceeded to drive back to the office forgetting that the device had not been properly secured. Upon return to the office, the technician realized the mistake. Information made available to the writer indicates that the gauge was discovered missing at approximately 2:00 pm. At that time, [the RSO] was notified and personnel from BECC immediately conducted a search of the job site and route taken by the technician. The route started from the job site at the Grants Mill Road exit on I-459 traveling southbound to I-65 northbound to Lakeshore Drive where the licensee's office is located. The tailgate to the truck was not closed, the device was not in the transport container but the gauge shutter was closed and locked. [The RSO] further indicated that he had called the State Troopers and they indicated that no gauge had been reported found. [The RSO] indicated that he had not yet called city police. "The writer then contacted [ADPH] and advised them of the incident. Through conversations, it was determined that BECC needed to contact the police and put out a press release, Also, it was determined that the local EMA Director needed to be advised of the incident. [ADPH] committed to calling the RSO back and relaying this information, [an ADPH representative] also indicated that he would notify the Jefferson County Director. "The writer had no additional conversation with licensee personnel." * * * UPDATE FROM STATE OF ALABAMA (VIA E-MAIL) TO KLCO ON 9/02/08 AT 1027 EDT * * * "On Friday 29 August 2008 Alabama reported that a Troxler Model 3440 device had been lost from a pickup truck the afternoon before in Birmingham, Alabama. "On Sunday afternoon 31 August 2008 an individual reported to the Irondale, Alabama (part of greater Birmingham) Police Dept that they had found the device and wished to claim the reward. The device is now in the possession of the licensee, BECC, Inc. It was apparently undamaged save for a few scratches. The licensee did a leak test on the device and is awaiting results from lab. "The State of Alabama is awaiting the licensee's 30 day report and corrective actions. A decision on enforcement actions will be made after review of the licensee's response." Notified R1DO (Dwyer), FSME EO (Burgess) and ILTAB (via e-mail) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2008-09-03
44450 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2008-08-29 10:07 | 2008-08-29 10:50 | 2008-08-29 | UNANALYZED CONDITION RELATED TO CERTAIN FIRE CONDITIONS "During an engineering review, a condition was identified in which, under certain fire conditions, possible damage scenarios, and required operator actions, the ability to meet the performance criteria of the approved fire protection program may be challenged. Specifically it was postulated under certain fire conditions affecting the control room, the ability to maintain pressurizer level within the indicated range (high) may be challenged leading to water relief through the pressurizer safety valves. The pressurizer safety valves are not qualified for water relief. "Compensatory actions to address the risk of fire in areas of concern are in place. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii). "The NRC Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-08-29
44449 | 0 | UNIVERSITY OF VA MEDICAL CENTER |  |  |  |  | 2008-08-28 16:00 | 2008-08-29 10:47 | 2008-08-29 | MEDICAL EVENT - PRESCRIBED DOSE DIFFERED GREATER THAN 20% "Male patient was treated Thursday August 28, 2008 with 'TheraSpheres [TS]' (a Y-90 pure beta-emitting Nordion microsphere product for liver cancer treatment). The procedure began at about 1600 hours. The written directive specified a radiation dose to the right liver lobe of 92 Gy. This required the implantation into the right liver lobe of 1.83 GBq of Y-90 at 4 PM. "Y-90 operations are guided by a written procedural check-list which is read out aloud in the Operating Room in a step-by-step fashion during every operation. Unfortunately, the [authorized user, (AU)] failed to carry out a step which had been read out aloud to him which required that a blue stopcock in the delivery device be turned toward the delivery device's 'waste vial'. Note: When the blue stopcock is turned toward the 'waste vial' the flow is from the 'source vial' to patient. Otherwise, flow is to the 'waste vial.' "When [the AU] began the 'source vial' flushing sequence, he saw that flow in the delivery device's transparent tubing was going from the 'source vial' to the 'waste vial' (instead of to the patient). He then turned the blue stopcock to the correct position and continued the flushing sequences. Unfortunately, about 2/3 of the initial activity in the 'source vial' had been diverted to the waste vial during the start of the first flushing sequence. The flushing sequences were repeated several times until no further reduction was observed in the delivery device dose-rate indicators (normally, flushing ceases when the two dose-rate meters indicate 0.0 Mr/h). As per procedure, the 'waste vial,' together with contaminated tubing, stopcocks, catheters and gloves were placed in a plexiglass-shielded waste 'mayo' jar and its dose-rate measured at a distance of 30 cm between jar and meter. Note: The Y-90 activity in the waste jar is determined by a ratio calculation involving the dose-rate measured with the source vial within the plexiglass shield located at 30 cm from the survey meter. (Most beta particles are absorbed in the mayo jar and plexiglass shield. Survey meter measures X-rays produced by the ~1 MeV particles, and not the beta particles). "From the waste container measurements it appears that 0.68 GBq were implanted into the patient's [right (RT)] liver, with 0.12 GBq going to the patient's lungs. The calculated dose to the RT liver is 34.3 Gy and to the lungs it is 13.2 Gy. The dose delivered to the target is low by about 63%. This, then, is a medical event requiring notifications. "Note: There was no leakage from the delivery device, its tubes, catheters, stopcocks, therefore, there was no contamination to be cleaned up. All other procedural steps were completed as required by our procedures. The OR and the personnel exiting it were checked for contamination and none was found. "This scenario, of an accidental diversion of activity to the delivery device's waste vial, has occurred at other institutions. This was RSO's motivation, many months ago, to change the print color of this procedural step from black to red, and to alert the AU to this possibility. This event was due to a simple mistake that may be resolved when a newer version of a TS delivery device is introduced by Nordion in the near future." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-09-03
44448 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-08-28 11:43 | 2008-08-28 17:35 | 2008-08-29 | LEAK IN HIGH PRESSURE FIRE WATER SYSTEM "At 1143, on 8/28/08, the Plant Shift Superintendent was notified of a large water leak on High Pressure Fire Water system (HPFW) A-12 in building C-333 due to a piping rupture. The HPFW system provides water for fire suppression to the plant's process buildings. A-12 is 1 of 66 HPFW systems in this process building. Leak analysis indicates the HPFW system A-12 would not have been able to perform its intended safety function while the leak was occurring. The leak was determined to be between the process building and the post indicating valve (PIV). The PIV for this system was closed which isolated the leak. Required TSR LCO actions have been and are being performed. This is being reported as an event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and no redundant equipment is available. "The NRC Senior Resident Inspector has been notified of this event." * * * UPDATE PROVIDED BY ROD COOK TO JASON KOZAL ON 8/29/08 AT 1611 * * * "On 8/29/08, the Kentucky Department of Water (KDOW) was notified that approximately 30,000 gallons of recirculating water (RCW) from the HPFW system containing 4 ppm phosphorus residual was discharged through Outfall 9. RCW discharge to Outfall 9 is reportable to KDOW as a bypass of a treatment system that causes an exceedance of a permit limit per 401 KAR 5:065 Section 1(12)(f). "The NRC Senior Resident Inspector has been notified of this event." Notified R2DO (Nease) and NMSS EO (Mamish). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | OTHER UNSPEC REQMNT | [8 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-08-28
44447 | 0 | PHARMALOGIC |  |  |  |  | 2008-08-28 03:00 | 2008-08-28 15:30 | 2008-08-28 | CONTAMINATION EVENT DUE TO BROKEN TC-99m VIAL The licensee was incubating six vials of Tc-99m (Cardiolite brand 1500 millicuries each) in the iodine room. At the end of the incubation period the technician removed the first five vials without incident. The sixth vial was attempted to be removed. When the tongs touched the vial the technician heard a sound that indicated that the vial had broken. The technician called the pharmacist over to verify the break. A cleanup was initiated. The pharmacist's lab coat was contaminated, the technician's lab coat, shirt, and dosimeter were contaminated, and an additional technicians' lab coat was contaminated. All contaminated items were removed and stored. The contamination was contained in the iodine room. Removable surface contamination was cleaned up. The RSO did a survey of the personnel and the technician directly involved in the incident had a small amount of contamination on her hands and her hair was reading 10 mr/hr on contact. The RSO instructed the technician to return to home, shower to remove the remaining contamination and bag her clothes and return to work. Upon returning the employee was cleared of contamination, but her clothes were reading above background. The licensee cleanup strategy for the iodine room is to allow it to decay as the half-life of Tc-99m is 6 hours. The licensee notified Region 2 (David Collins, Rebecca Nease) and was directed to Region 1 (Powell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | WV | HOS | [5 empty] | 0 | 2008-08-28
44446 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2008-08-28 13:48 | 2008-08-28 14:13 | 2008-08-28 | UNUSUAL EVENT DECLARED DUE TO LOSS OF COMMUNICATIONS WITH OFFSITE AGENCIES At 1348 EST the licensee declared an Unusual Event and entered EAL 7.3.2 due to the loss of the ability to communicate with offsite organizations. The loss of communications was due to a maintenance worker opening the wrong breaker. This caused the loss of all land based phone lines in the control room, the satellite phones and ERDS. The power was restored and the EAL was exited at 1414. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAN DEAN TO PETE SNYDER AT 1930 ON 8/28/08 * * * "Ginna Station is updating the Unusual Event classification and declaration made at 1348 hours on August 28th, 2008. Information received following termination of the event at 1414 hours, shows that two telephones were available in the Control Room during the entire event. At the time of the classification, the Shift Manager did not have this information." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-08-28
44445 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2008-08-28 | 2008-08-28 13:48 | 2008-08-28 | REPLACEMENT DIAPHRAGM FAILURES DUE INADEQUATE CURE AND OPERATION OVER MAXIMUM PRESSURE "Fisher was recently notified by Luminant, Comanche Peak SES of two replacement diaphragm failures. These diaphragms had been in service for approximately 3.1 years. "The diaphragms lost frictional flange retention in a progressive type failure which transferred retention stress to the bolt/diaphragm interfaces and caused localized stresses great enough to initiate rupture. Rupture propagation occurred catastrophically in multiple directions and rapid loss of actuator pressure resulted and consequently, opening of the valve." This is applicable to all Fisher size 80, type 657 and 657NS sliding stem valve actuators sold to the nuclear industry by Fisher Controls International LLC that are equipped with nitrile/nylon diaphragms (Fisher part number 1R6375X0072). It is unknown what plants in addition to Comanche Peak are affected by this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2008-08-28
44444 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2008-08-27 10:00 | 2008-08-28 11:29 | 2008-08-28 | UNPLANNED CONTAMINATION EVENT "An unplanned contamination event occurred on August 27, 2008. The event is reportable in accordance with 10CFR40.60 subparagraph (1) based on an unplanned event that resulted in additional radiological controls or by prohibiting entry into the area. The 24 hour period ended at 10:00 a.m. on August 28, 2008. The additional control imposed is to wear air purifying respirators on the second floor of the feed materials building. Air samples from the second floor analyzed and the airborne radioactivity average is approximately 6.7e-11 microCuries/ml. The airborne contamination is natural uranium ore concentrates and the physical form is a light dusty material." The area of contamination is in the Feed Material building while using the prepared feed mill. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2008-08-28
44443 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-08-28 06:15 | 2008-08-28 08:31 | 2008-08-28 | OFFSITE NOTIFICATION DUE TO SMALL OIL SPILL INTO INTAKE BAY During a diver inspection of 0A SX [Essential Service Water] Makeup pump intake structure, hydraulic oil was spilled into the intake bay. The oil was Envirologic 146, a natural ester based hydraulic oil. It is believed a total of approximately 2 gallons of oil leaked from the pump into the intake bay. Approximately 6 inch - 12 inch oil sheen was seen on the Rock River. Oil booms used to capture spilled oil. Oil spill was contained at 0710 CDT. Licensee notified the National Response Center, Illinois Emergency Management Agency, and Ogle county Emergency Services Disaster Agency. The licensee notified the NRC Resident Inspector. National Response Center Report #: 882049 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-28
44442 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-08-28 04:47 | 2008-08-28 05:33 | 2008-08-28 | UNUSUAL EVENT - INTERNAL FLOODING IN SERVICE WATER INTAKE STRUCTURE "Licensee entered into Unusual Event due to EAL 9.7.1, which is internal flooding in excess of sump handling capability affecting safety related areas of the plant. "Failure of the sump pump level switches in the active Service Water Intake Structure (SWIS) bay resulted in several inches of water on the floor and receipt of a SWIS 'Pump Room Flooded' alarm. There was no excessive leakage from the service water system and no damage to safety related systems in the room. Sump pumps are now operating and level in the SWIS bay is lowering. "All safety related systems are operable except for the 'A' Diesel Area Panel Room Supply Fan, which is cleared and tagged for scheduled maintenance." Licensee will notify the NRC Resident Inspector and has notified the states of New Jersey and Delaware and the local township. * * * UPDATE PROVIDED AT 0746 EDT ON 08/28/08 FROM DAN KLINGER TO JEFF ROTTON * * * At 0736 EDT the licensee terminated the Unusual Event. The SWIS sump pumps are working as designed using the sump pump level switch. The sump pumps are running and lowering level (approximately 0.75 inches remains on the SWIS floor). The licensee has notified the State of New Jersey and Delaware Emergency Response organizations and will be notifying the NRC Resident Inspector. Notified R1DO (Powell), NRR EO (Thorp), IRD MOC (McDermott), DHS (McKentry), and FEMA (Sweetser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-08-28
44441 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2008-08-27 09:50 | 2008-08-27 14:18 | 2008-08-27 | OFFSITE NOTIFICATION AND PRESS RELEASE DUE TO INADVERTENT AIRING OF A EMERGENCY BROADCAST MESSAGE "On August 27, 2008 at 0950 CDT, a local radio station (in Clinton, Iowa) mistakenly activated an emergency broadcast message concerning the Quad Cities Station. The inadvertent broadcast message occurred during the radio station's participation in a scheduled Quad Cities Station emergency planning exercise. The radio station has announced a correction to the message and rebroadcasted the correct information. Exelon has notified county and state officials and issued a news release. This event is being reported under 10 CFR 50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 99 | 98 | 0 | 99 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-27
44440 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2008-08-26 08:14 | 2008-08-26 09:27 | 2008-08-26 | ERDS AND SPDS OUT OF SERVICE DUE TO PLANT COMPUTER MAINTENANCE "The Perry Nuclear Power Plant took the Plant Computer out of service for scheduled maintenance which will take ERDS out of service. From 0814 hours EDT, on August 26, 2008 for approximately 6 hours personnel will be performing disk maintenance activities on the Plant Computer. During this planned maintenance, the Safety Parameter Display System (SPDS) and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. The unavailability period is necessary to replace a disk drive. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Plant Branch Exchange, the Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. A follow-up notification will be made when the activities are completed and the equipment is restored. The resident inspector has been notified." * * * UPDATE PROVIDED AT 1425 EDT ON 08/26/08 FROM MIKE BROGAN TO JEFF ROTTON * * * Computer maintenance is complete and the Plant Computer has been restored to service. SPDS, CADAP and ERDS are available. The licensee will notify the NRC Resident Inspector. Notified R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-08-26
44439 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-06-28 19:04 | 2008-08-25 16:27 | 2008-08-25 | 60-DAY OPTIONAL REPORT FOR AN INVALID ACTUATION OF UNIT 1 TDAFW PUMP "This report describes an invalid actuation of the Unit 1 Turbine Driven Auxiliary Feedwater (TDAFW) pump that occurred on June 28, 2008. This report is being made in accordance with 10CFR50.73(a)(1), which states, in part, 'In the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than actuation of the Reactor Protection System (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' "On June 28, 2008, Comanche Peak Nuclear Power Plant Unit 1 was in Mode 1 operating at 100% power. At 1904 CDT, the steam supply valve from Main Steam Line 1-04 to the TDAFW pump opened due to a failed diaphragm. Turbine load was subsequently reduced from 1207MWe to 1150MWe per Operations procedures. The upstream isolation valve for the steam supply to the TDAFW pump was closed and the TDAFW pump was stopped. Unit 1 was returned to full power at 2120 CDT and the failed diaphragm was subsequently replaced. "The specific train and system that actuated was the third AFW train on Unit 1. The train actuation was complete and during the TDAFW start the system started and functioned correctly." The licensee has notified the NRC Resident Inspector. | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-08-25
44438 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2008-08-24 15:57 | 2008-08-24 18:03 | 2008-08-24 | MANUAL REACTOR TRIP DUE TO FEEDWATER FLOW OSCILLATIONS "The 'A' Condensate Pump became uncoupled, lowering Condensate flow. Operators began to manually lower reactor power to maintain deaerator level. Reactor power was lowered to approximately 62 percent. At this power, [feedwater] flow oscillations began and were excessive. With these flow oscillations increasing the decision was made to manually trip the Reactor. The Reactor was manually tripped at 1557 hours. There were no safety system actuations other than RPS (Manual). The plant is stable in a normal post trip configuration." All control rods inserted into the core during the reactor trip. Offsite power is available and powering safety loads. The steam generator safeties lifted during the transient and reseated. There is no known primary to secondary leakage. Decay heat is being removed via steam dumps to the condenser using normal feedwater to the steam generator. The emergency feedwater system was not initiated during the reactor trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-08-24
44437 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2008-08-22 16:20 | 2008-08-22 20:02 | 2008-08-22 | OFFSITE NOTIFICATION DUE TO HYDRAZINE SPILL "At 1620 EDT, the following off-site agencies were notified of approximately 1.8 gallons of 35 weight-percent Hydrazine spillage into the storm drain system: National Response Center, State Emergency Response Commission, and Florida Department of Environmental Protection. The storm drain system discharges to an on-site settling pond. The amount of Hydrazine spilled was greater than the reportable quantity of 0.34 gallons of 35 weight-percent hydrazine. The leak has been identified and stopped, area has been cleaned. Notification due to 10CFR50.72(b)(2)(xi), due to notification of off-site agencies." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-22
44436 | 0 | U.S.ARMY |  |  |  |  | 2008-03-21 | 2008-08-22 17:36 | 2008-08-22 | MISSING CHEMICAL AGENT ALARM DETECTOR "On March 21, 2008 a MSARNG [Mississippi State Army Reserve National Guard] unit from Jackson, Mississippi at the United States Property & Fiscal Office (USP & FO) receiving warehouse loaded 60 M43A1 alarms for delivery to the United States Property & Fiscal Office (USP & FO) at Camp Shelby, MS. Inventory of the M43A1's was conducted at the time of packaging the detectors in Jackson, MS. All 60 M43A1's were packaged into a single white shipping container and loaded into a trailer. The shipping container was banded shut and secured inside the towed trailer. The trailer was locked during transport in an Army vehicle. The trailer containing the M43A1's was received at Camp Shelby on or about April 8, 2008. The shipping container was not tampered with and was still closed when received at Camp Shelby. An inventory was conducted at the USP & FO, Camp Shelby and it was discovered that one M43A1 detector was missing. On May 22, 2008 a financial liability investigation of property loss was initiated by the Mississippi National Guard. The Army conducted a financial investigation liability loss that was completed on August 19, 2008. The missing alarm detector was reported to the licensee on June 19, 2008. A physical search was conducted at Camp Shelby warehouse and Jackson warehouse locations with negative results. On July 18th the NGB U.S Property and Fiscal Office in Flowood Mississippi issued a memorandum dated July 18, 2008 directing a physical inventory be conducted at all USP& FO's within the state of Mississippi to search for the missing M43A1 detector. On August 19, 2008 the physical search was completed with negative results. On August 21, 2008 the Army fiscal officer performed one last search for the device at the warehouse in Camp Shelby, MS with negative results." Based on discussion with the license RSO (Radiation Safety Officer) the lost chemical agent alarm detector activity is 250 micro-curie of Am-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-08-22
44435 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-08-21 22:30 | 2008-08-22 14:46 | 2008-08-22 | MATERIALS CONTROL & ACCOUNTABILITY ALARM PROCEDURE INITIATED "10CFR74.57(f)(2) requires notification within 24 hours that an MC&A [Material Control & Accountability] alarm resolution procedure has been initiated. Because an alarm investigation was initiated, a notification to the NRC Operations Center was made. Additional sampling later indicated the value was below the abrupt alarm value and this was communicated to the NRC Operations Center. There is no indication that a material loss has occurred. "There were no actual or potential safety consequences to workers, the public, or the environment. MC&A alarm tests were run as specified by applicable procedures and requirements. Based on the alarm test for the Building 333 Oxide Dissolution area, the alarm test value was exceeded. Additional sampling later indicated that the input minus the output value is below the alarm value. An investigation was initiated and additional sampling has indicated that the input minus the output value is below the alarm value." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2008-08-26
44434 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-22 12:00 | 2008-08-22 14:10 | 2008-08-22 | AGREEMENT STATE REPORT - SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA The following information was received from the State of Minnesota via email: "Licensee was performing radiography on steam pipes in a bunker under the road (temporary jobsite). The bunker is accessed by two manholes in the street. At approximately 10:40 a.m. on 8/21/08 the licensee had a disconnect. The assistant under the supervision of the radiographer was cranking the source in, but did not feel it lock into place. The radiographer used the survey meter while the assistant cranked in and out. The readings on the survey meter did not change so they knew they had a disconnect and called the RSO. "The RSO was notified at approximately 11:00 a.m. The RSO and another employee (former RSO) went to the scene. When they arrived onsite the readings at the manhole entrances were 80 mR/hr and 150 mR/hr, a couple of feet to the sides was background. The radiographer had roped off the area around the manhole entrances and the roped area was maintained until the RSO arrived on-site. "The RSO, former RSO, and radiographer used telescopic poles to manipulate the camera, and guide tube into a position where the could lower bags filled with lead shot to shield the source. They were then able to enter the bunker and use a 'fishing' cable run through the camera and guide tube to grab the source. They exited the bunker and pulled the 'fishing' cable back until the source locked into the camera. "The RSO and other employee were wearing dosimeters, direct reading dosimeters (DRDs), and alarming rate meters. At the end of the retrieval the RSO and former RSO had reading on there DRDs of 30 - 35 mR each. The radiographer had a reading on his DRD of 25 mR. "In looking at the pig tail after the incident, the licensee thinks there is a faulty pig tail connection. The connection between the drive cable and pig tail needed to be forced to get connected, but once connected 'felt sloppy.' The licensee contacted the manufacturer and will be returning the source and cables to the manufacturer for investigation." "Camera: QSA 660B" "Source: QSA 424-9, Ir-192, 142 Ci" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2008-08-27
44433 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2008-08-20 06:00 | 2008-08-22 14:36 | 2008-08-22 | UNANTICIPATED OR EMERGENCY DISCHARGE OF WASTE WATER OR CHEMICAL SUBSTANCES "Plant Technical Specifications, Appendix B, Section 4.1, Unusual or Important Environmental Events, states that the NRC Operations Center will be notified within 72 hours as described in 10 CFR 50.72 for an unanticipated or emergency discharge of waste water or chemical substances. This notification is due to an unanticipated emergency discharge of storm drain waste water beginning 8/20/08 at approximately 0600 due to Tropical Storm Fay. A 30 day letter detailing the event to the NRC is also required. "On 8/20/08, St Lucie Plant water levels in all of the plant storm water basins and Unit 1 Condenser Pit experienced a significant level increase received due to approximately 15 inches of precipitation from Tropical Storm Fay. Over the next 24 hours the site pumped approximately 23 million gallons of water from the storm water basins into the intake canal from an approved outfall (008). The water level in the basin has decreased 8.7 feet to 6.7 feet. Pumping activities will continue until we reach a level of 5 feet in the pond. The total estimated amount of water expected to be discharged from outfall-008 is 40 million gallons. "Chemistry obtained samples from the storm basin and Condenser Pit both and the samples were determined not to contain radioactivity. The non-radiological analysis will be forthcoming from an offsite laboratory (the FPL 45th street lab), however no oil sheen was observed prior to any discharge. The lab results will be included in the 30 day NRC letter detailing the event. "The DEP [ Department of Environemntal Protection] was contacted and a verbal request was made and consent received to pump water from the U- I condenser pit to the intake canal. A final report will be sent to the DEP when pumping is concluded identifying total volumes and water profiles. The Plant NPDES permit does not regulate the volume of water discharged from 008. "As a result of the Unit 1 Condenser Pit flooding, secondary Condensate and Feedwater chemistry levels sodium and chloride levels increased to Plant Action Level 3 conditions which require the Unit to be shutdown to at least Mode 2 conditions. Due to End of Cycle conditions and Xenon build-in, the Unit was shutdown and is currently in Mode 3. The Turbine was manually tripped and the Control Rods were driven to All Rods In, i.e., there was no reactor trip or RPS / AFAS actuation. Residual reactor heat is being removed by Atmospheric Dump Valves and Auxiliary Feedwater is providing makeup to the S/Gs. Repairs are being implemented to prevent Condenser Pit flooding and secondary inleakage. Unit 2 operations was not affected by this event. Off-Site power remained available during this event." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2008-08-22
44432 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2008-08-21 16:06 | 2008-08-21 22:30 | 2008-08-21 | AUTOMATIC REACTOR SCRAM DUE TO A MAIN TURBINE TRIP "Following a downpower to 65% for maintenance on one of the reactor feedwater turbines, a main turbine digital electro-hydraulic (DEH) quadvoter valve, that had failed a previous surveillance, was replaced. During the operability testing of the new DEH quadvoter valve, a leak developed. DEH reservoir level dropped 8 inches (approx. 52 gal) and tripped the main turbine on low DEH pressure. An automatic reactor trip occurred due the main turbine trip. All rods fully inserted. RPV pressure was controlled using the bypass valves and main steam line drains. No SRV's opened. RPV level was maintained using the feedwater and condensate system in the normal RPV level band. All other safety systems operated as designed. Off-site power is available. Three emergency diesel generators are operable and available." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-08-21
44431 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-08-18 22:37 | 2008-08-21 13:42 | 2008-08-21 | LOSS OF COMMUNICATION WITH ERDS "At approximately 1000 on August 21, 2008, with the James A. Fitzpatrick (JAF) Nuclear Power Plant operating at 96.5% reactor power, the Information Technology (IT) Department determined the interface between the plant information computer and the Emergency Response Data System (ERDS) was not working properly. The discovery was made when responding to an IT Help Call. The data transfer file for the data currently available in ERDS is time stamped 2237 08/18/08. We have confirmed that the ERDS Line is not malfunctioning and the plant computer is operating normally. Trouble shooting on the interface between the plant computer and ERDS is in progress. "10 CFR 50.72(b)(3)(xiii) requires reporting within 8 hours when a significant portion of the emergency communication system has been lost. Based on the requirement in 10 CFR 50.72(a)(4) to activate ERDS within 1 hour of declaring an Alert, Site Area, or General Area Emergency. JAF has determined that this event meets criterion 10 CFR 50.72(b)(3)(xiii). In the event of an Emergency the designated NRC Communicator would be available to provide plant data to the NRC. "At this time the ERDS System has been restored." Licensee has notified the NRC Resident Inspector and the state. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-08-21
44430 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-08-20 16:41 | 2008-08-21 08:19 | 2008-09-15 | MASSACHUSETTS AGREEMENT STATE REPORT - RADIATION GREATER THAN TEN TIMES LIMIT "[A] technician working with a 113 Ci Ir-192 source set off high radiation alarms at [the QSA Global facility] which caused the immediate evacuation of the building. Radiation surveys outside the building indicated a dose rate of approximately 3 Mr/hr at a distance of 25 feet from the exterior of the building. Radiation safety staff performed a source retrieval to recover the source and place it in a shielded container; the building was reoccupied approximately 30 minutes later. "Preliminary investigation of the technician indicated his electronic dosimeter (worn on the side of the body closest to the source) showed an exposure of 720 mRem. The technician was not wearing his extremity ring badge at the time, however the radiation safety officer calculated a maximum exposure to the tips of the maximally exposed fingers to be approximately 2 Rem. Dosimetry for both the technician involved and another that was nearby when the incident occurred have been sent to the vendor for immediate processing. "Radiation Safety staff from QSA are performing additional investigations and will report back to the [MA Radiation Control Program Office] when more information becomes available." State of Massachusetts was notified by the licensee of this incident at 0621 on August 21, 2008. * * * UPDATE ON 9/15/2008 AT 0843 FROM ROBERT GALLAGHAR TO MARK ABRAMOVITZ * * * "The Massachusetts Radiation Control Program (RCP) has received the 30 day report from the licensee, QSA Global. This report confirms that the event which occurred on August 20, 2008 was not an overexposure event. The licensee reported levels of radiation in an unrestricted area in excess of ten times the limits specified in 105 CMR 120.221. This report was provided to the Agency (RCP) pursuant to 105 CMR 120.283." Notified R1DO (Dimitriadis) and FSME (White). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-08-26
44429 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-08-19 | 2008-08-20 16:36 | 2008-08-20 | AGREEMENT STATE REPORT - FIRE IN RESEARCH LABORATORY This information was received from the state via fax: "The afternoon of 8/19/2008 DHS [Department of Health Services] staff became aware a fire had occurred at a licensee facility the previous evening. Reports indicated the local fire department and hazardous materials teams had responded to a fire in a molecular biology lab on the campus of the University of Wisconsin - Madison. The fire was extinguished within 15 minutes. Reports also indicated the Hazardous Incident Team used instruments to rule out the presence of any radioactive materials. Although no contamination was detected, fire equipment was rinsed with water to remove any reside from the fire. "DHS contacted the licensee. The licensee indicated staff members from radiation safety had responded to the incident the next morning. The research lab performs molecular biology research using P-32. The safety department staff performed surveys of the fire scene and identified areas of contamination on the floor. The areas had been decontaminated. Initial information from the licensee indicates approximately 0.5 to 0.7 millicuries of P-32 in waste containers was involved. "The licensee did not report the incident to DHS. DHS inspectors were dispatched to investigate." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-08-25
44428 | -1 | OAKWOOD HOSPITAL & MEDICAL CENTER |  |  |  |  | 2008-06-03 11:14 | 2008-08-20 15:16 | 2008-08-21 | MEDICAL EVENT - PRESCRIBED DOSE DIFFERED BY MORE THAN 20 PERCENT "A written directive, signed and dated on 5/30/08 by an authorized user was prepared. The directive noted that 2.0 mCi of I-131 was prescribed to be given orally on 6/3/08, for the performance of a Whole Body Scan to a patient previously diagnosed with thyroid carcinoma. An order of 2.0 mCi of Na I-131 was placed with Anazao Health on 5/30/08. On 6/02/08 at 1300 hours, an order of 2.17 mCi was dispensed by Anazao Health to Oakwood Hospital & Medical Center. A dosage calibration sheet from Anazao Health was supplied. On 6/03/08 the patient was properly identified, a negative pregnancy status was confirmed and the dosage assayed. A recorded dosage of 2.7 mCi was recorded in the hot lab computer and on the front of the written directive form. The hot lab computer with technologist data input produced a printed label of 2.7 mCi as of 6/03/08 at 1114 hours. However, at the time of dosage administration the calculated dosage available was 2.00 mCi. "The dosage was administered to the patient and the patient was released with written radiation safety instructions for return 48 hours post administration for performance of the actual scan. At interview today, the technologist confirms that all administrative dosage information was recorded by her and her alone. She could not give any reason as to why a dosage of 2.7 mCi could or would have been administered or recorded. "A recreation of these events today notes that the hot lab computer advises the technologist that the +/-20% threshold has been exceeded with a visual warning which can be bypassed upon consultation with the authorized user. We can find no documentation of a consultation and neither the authorized user nor the technologist can confirm that one took place. A conservative estimate of organ and EDE doses was made using ICRP 53 and an ultra conservative estimate of a thyroid uptake of 5%." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION PROVIDED AT 1050 EDT ON 08/21/08 FROM CHAD MORGAN TO JEFF ROTTON * * * "Upon further investigation we have determined that a Medical Event did not occur at Oakwood Hospital and Medical Center. We do believe that a documentation error did occur instead and have taken steps internally to prevent a reoccurrence (see below). We would like to retract our report of a medical event. This is due to the following conclusions: * A written directive, signed and dated on 5/30/08 by an authorized user was prepared. *The directive noted that 2.0 mCi of I-131 was prescribed to be given orally on 6/3/08, for the performance of a Whole Body Scan to a patient previously diagnosed with thyroid carcinoma. *An order of 2.0 mCi of Na I-131 was placed with Anazao Health on 5/30/08. *On 6/02/08 at 1300 hours, an order of 2.17 mCi was dispensed by Anazao Health to Oakwood Hospital & Medical Center. A dosage calibration sheet from Anazao Health was supplied. "Upon further investigation, at the time of dosage administration the calculated dosage available was 2.00 mCi, though the documentation states the dosage given was 2.7mCi. We believe the documentation to be in error and not the actual dose given to the patient. "Measures to Prevent Reoccurrence: 1. Prior to dosage administration, all documentation will be verified by either a second certified nuclear medicine technologist or an authorized user via review and signature on the written directive. 2. Extensive re-education for all technical staff will be conducted concerning the written directive program and patient release requirements. 3. A written internal time-out retrospective audit will be conducted on a random number of directives on a monthly basis. 4. Medical Physics Consultants, Inc. will continue to perform a full quarterly written directive program audit. "Summary: It is our belief that the correct patient received the correct prescribed dosage for the ordered procedure, however our internal documentation notes otherwise. This documentation error would not constitute a Medical Event ." Notified R3DO (Sonia Burgess) and FSME (Michele Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-08-26
44427 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-17 10:00 | 2008-08-20 08:57 | 2008-08-20 | TEXAS AGREEMENT STATE REPORT - SURFACE CONTAMINATION AT LUFTHANSA CARGO FACILITY The following information was provided by the State of Texas via email: " On 8/18/08 at 0655 CDT, [State of Texas] received a call from the answering service at approximately 10 PM on 8/17/08 requesting that [the State] call Lufthansa Cargo at DFW Airport. [State] contacted [Deleted] and he [reported] that customs had been at their facility and had found a spot on their concrete floor reading 132 microrem. The area [approximately 16' x 20' ] had been used to store a container from Protechnics out of Houston, Texas. The package had originated from Spectro Services in Albuquerque, NM. The package had been sent on to Germany on 8/14/08. The radionuclide was identified as Iridium (Ir) - 192 by the Dallas Fort Worth Fire Department. The area is currently roped off and posted no entry. A decontamination service [was scheduled] to decontaminate the area Monday 8/18/08 in the afternoon. [Deleted] agreed to contact us when the area was decontaminated. Copies of the surveys conducted were also requested. An Agency inspector performed a survey of the area and identified the contamination as Ir - 192. On 8/19/08 at 1410 CDT, NNSI was been contracted to decontaminate the area. The contractor states that the area should be released by this evening. "Contamination appears to be in the form of dust. Several packages were in the contaminated area and were decontaminated prior to releasing for shipment. The contamination is readily removable. NNSI stated that they were going to survey the transportation area in Houston. The shipper stated that they had surveyed the location in Houston (Transaction Packaging 2928 B Greens Rd Suite 250) where the package was stored waiting to be sent to Dallas/Fort Worth and found no direct readings above background. NNSI has not provided the Agency with any of their readings. The original survey conducted by the state inspector found removable contamination levels of 4000 cpm/smear on 8/18/08 in the area in question. Shoes of all workers who could have traveled thru the area were surveyed and found to be free of contamination. "The package originated in Albuquerque NM and was flown from there thru Memphis, TN To Houston, TX and then trucked to Dallas Fort Worth airport. "The material first considered as the source was Ir - 192 tracer material. Surveys of the package when it arrived in Germany indicated that there was no contamination outside of the package. An engineer is waiting for the package in India. He will survey the package, then open the package to verify that there has been no damage. The engineer will take pictures of the boxes and forward to the Agency. There was a statement from NNSI that they had heard that there may have been a problem with the package in Houston and that it may have been over packed. Protechniques stated that this was not true. "An Agency inspector will survey the transport trailer used to move the material to DFW on 8/20/08. "The material first thought to create the problem was packaged in 20 mil vials, placed inside a lead shield, which was placed inside a plastic bag and placed in a DOT shipping container. "The Agency has requested the records on all RAM passing thru this facility in the last 90 days from Lufthansa Cargo." Texas Incident number: I-8536 * * * UPDATE ON 8/20/08 AT 1221 FROM A. TUCKER TO V. KLCO * * * " At 0915, NNSI reported that the area at Lufthansa Cargo was released for unrestricted use at 9 PM on 8/19/08. They also reported that they conducted surveys at Lufthansa's warehouse in Houston, Texas and found no uncontrolled radioactive material. " Notified R4DO (V. Gaddy) and FSME (M. Burgess) and e-mailed OIP (S. Dembek). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-08-25
44426 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-19 | 2008-08-19 16:13 | 2008-08-19 | AGREEMENT STATE REPORT - PATIENT TREATMENT CALCULATION "Hospital cited for current calibration of SR-90 eye applicator. During previous inspection, after calibration, recalculation of recent treatments indicated 3 patients received 50% overdose over the past year. RSO reports Oncologist and referring physician were pleased with patients response to treatment." Texas Incident # I 8539 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-08-25
44425 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-08-19 11:10 | 2008-08-19 17:27 | 2008-08-19 | ALTERNATE SAFE SHUTDOWN LOCAL START CAPABILITY OF ALL FOUR EMERGENCY DIESEL GENERATORS MAY NOT BE AVAILABLE UNDER CERTAIN CONDITIONS "On August 18, 2008, during biennial (i.e., every two years) non-Technical Specification related testing, Emergency Diesel Generator (EDG) No. 4 failed to start from the EDG local control panel. This occurred with the EDG aligned for Alternate Safe Shutdown (ASSD) response versus its normal alignment. The purpose of the testing is to confirm that the EDG control logic is isolated from the control room and only operable via local controls. Based on troubleshooting activities, it was discovered that this failure to start was due to improper wiring in the circuitry associated with the EDG lockout relay. The improper wiring was introduced by a modification performed on all four EDGs in 2007. "At 1110 hours Eastern Daylight Time (EDT) on August 19, 2008, it was concluded that this condition impacted the ability of EDG Nos. 2, 3, and 4 to perform their intended ASSD function. The 2007, modification affected the termination point for the power to the EDG lockout relay reset coil. Per the modification, this termination point was incorrectly connected to the downstream side of the alternate shutdown isolation switch which results in a loss of power to the lockout reset when the switch is placed in local control. Therefore, in the unlikely event of a fire, an induced failure could potentially initiate a lockout signal which could not be reset from the EDG local control panel. Although the modification was installed on all four EDGs, only the local control of EDGs 2, 3, and 4 is credited in the safe shutdown analysis. "This condition does not affect the Technical Specification operability of the EDGs and they remain fully capable of performing their intended design basis accident response functions. "The NRC Resident Inspector has been notified." Compensatory fire watches have been established and an engineering change package to correct the condition is being developed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-08-19
44424 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2008-08-17 18:00 | 2008-08-19 14:49 | 2008-08-19 | AGREEMENT STATE REPORT - LOSS OF Ir-192 SEEDS "At 1:30pm on Monday, August 18, 2008, a Maryland Department of the Environment radioactive material licensee, Greater Baltimore Medical Center, reported by phone to MDE RHP a loss of 5 Iridium-192 seeds of 0.59 millicuries each seed. The seeds were in a ribbon implanted in a cancer patient's neck along with 5 other strands of seeds. Numerous checks and plain films were obtained to verify correct location. The seeds had been implanted on Wednesday, August 13, 2008 and were checked daily. The loss of a strand of seeds was discovered on Sunday, August 17, 2008 at approximately 6pm, when the seeds strands were being removed. "Investigative action: The patient was moved to a new room. The licensee reports extensive monitoring of all linens, surfaces, sink drain, other rooms in the unit, nurses station, hallways and the loading dock, where trash was monitored (even though a monitor is located on the loading dock.) A relative's car was also monitored. Being that the patient shaved with a non-electric razor, the outcome of the investigation was that during shaving the strand must have come loose and had fallen into the toilet. "The RSO and radiation oncologists and physicists were involved in the investigation. Preventive action is for two radiation workers, (i.e. physician and physicist) to independently check the button crimped on the end of the ribbon strand to insure that the ribbon cannot slide out of the catheter. "The written report from the licensee was received by fax on August 19, 2008, at 3:33 pm. Further investigation by MDE RHP is pending." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2008-08-25
44423 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2008-08-19 09:05 | 2008-08-19 15:07 | 2008-08-19 | ROD CONTROL SYSTEM MALFUNCTIONED "On August 19, 2008, with the Unit shut down in Mode 3, post maintenance testing was being performed for the Digital Rod Position Indication System. While performing this test a 'Rod Control Urgent Failure' alarm was received upon initial withdrawal of Control Bank-C. All other control and shutdown banks remained fully inserted in the core. Local inspection revealed a phase failure on movable gripper coils in a power cabinet. In accordance with plant procedures, at 0905 hours, a manual reactor trip was initiated by operators opening the reactor trip breakers. All Safety Systems functioned as designed and Rod Control System repairs are in progress. "This event posed no significant safety implications because the reactor was subcritical when the reactor trip breakers were opened. Compliance with all Technical Specification requirements was maintained. The health and safety of the public were not affected by this event." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-08-19
44422 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-15 | 2008-08-19 13:31 | 2008-08-19 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "On Friday, August 15, 2008, the agency [State of Texas] received a phone call left as a message for an employee out on leave that a moisture density gauge [Humbolt model 5001EZ] was stolen after it was left at a work site. It was apparently left out of the transport case and the technician was distracted with other duties. When the employee returned there was no trace of the device. "The RSO stated that a full investigation will be performed to ascertain how the instrument was left unattended and the local law enforcement authorities have been notified. A $300 reward has been offered for return of the device. Incident Investigation Program (IIP) has notified LEA and pawn brokers to be on alert for stolen device. "Company (and State Agency) will conduct a thorough investigation. Protocols for proper storage and handling of gauges will be stressed at a future safety meeting and all employees will receive training on the consequences of mishandling company property. "Sealed sources :Radionuclide(s): 10 mCi, Cs-137 & 40 mCi, Am/Be-241 Serial Numbers: device 515; Cs-137, 8567GF; Am-241, NJ00479" TX-I-8541 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-08-22
44421 | -1 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-08-19 06:10 | 2008-08-19 11:30 | 2008-08-20 | FITNESS FOR DUTY A non-licensed PG&E employee was inattentive to his responsibilities, and was relieved of his duties. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM T. GRAF TO V. KLCO AT 1232 EDT ON 8/20/08 * * * " After review of the circumstances and Reg. Guide 5.62, the licensee believes the event is loggable." The licensee will notify the NRC Resident Inspector. Notified R4DO (Gaddy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2008-08-19
44420 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-08-17 09:02 | 2008-08-17 13:11 | 2008-08-17 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO INABILILTY TO PERFORM A REQUIRED RCS LEAK RATE VERIFICATION "During the 2000 CDT pumping of the Drywell Floor Drain Sump on 08/16/2008, the pumps failed to pump as indicated by the integrator reading zero with the pump running. The sump pump was running for approximately 2-3 minutes with the integrator showing no flow. The pump typically auto stops after approximately 30 seconds; since this did not happen, it appears to be a flow restriction and not an integrator problem. 3A DWFDS pump was started first and then 3B DWFDS pump was attempted with no flow noted for either pump. "Both the 3-2001-105 and -106 valves indicated OPEN. Both sump pump breakers were verified ON and a local visual inspection of the 3-2001-105 and -106 valves was performed to verify proper operation. Troubleshooting has determined that the 3-2001-105 valve is failing to OPEN. "The 3-2001-105 is a primary containment isolation valve and is currently CLOSED. "TS SR 3.4.4.1 requires RCS leakage verification 1 [time per] 12 hours and was last completed at 1600 CDT on 08/16/2008. "Unit 3 Shutdown was initiated at 0902 hours." The shutdown of Unit 3 was halted at 30% power while the licensee pursued an NOED (Notice of Enforcement Discretion) with NRC. The NRC Resident Inspector has been notified. The licensee will also notified the State. | 0 | 0 | 30 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-08-17
44419 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-08-17 00:12 | 2008-08-17 03:37 | 2008-08-17 | UNUSUAL EVENT DECLARED DUE TO FIRE IN MAIN BANK TRANFORMER At 0012 the licensee declared a Notice of Unusual Event due to a fire in Main Bank Transformer. The licensee is fighting the fire along with offsite assistance from CAL FIRE. The unit is shutdown and stable in mode 3. All control rods fully inserted on the trip. Decay heat is being removed via auxiliary feedwater to the steam generators steaming to the main condenser via the main condenser steam dumps. Emergency buses remain powered via offsite power with emergency diesel generators available if required. The licensee will notify the NRC Resident Inspector. Notified DHS (Barnes), FEMA (Blankenship). * * * UPDATE FROM J. DILLIS TO J. KOZAL AT 0501 EDT ON 8/17/08 * * * The fire is out. Plant personnel are assessing the damage in the main transformer area. The plant is stable in mode 3. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM J. DILLIS TO P. SNYDER AT 0542 EDT ON 8/17/08 * * * The licensee has terminated the Notice of Unusual Event at 0231 PDT due to the fact that the fire was out and no reflash occurred. The plant remains stable in mode 3. The licensee will notify the NRC Resident Inspector. Notified R4DO (Lantz), IRD (McMurtray), NRR EO (Wermiel), R4 (Collins), NRR (Grobe), DHS (Wallace), FEMA (Biscoe). * * * UPDATE FROM M. KENNEDY TO J. KOZAL AT 1038 EDT ON 8/17/08 * * * "This is an update of the Notification of Unusual Event due to Fire in the 'C' phase of the main bank transformer, and Automatic Reactor Trip. This update is to report automatic actuation of the auxiliary feedwater system (AFW) and is being reported as an 8-hour non-emergency event in accordance with 10 CFR 50.72(b)(3)(iv)(A) 'System Actuation.' "The unit is stable in mode 3 (Hot Standby) with offsite power being supplied to all buses via the 230 Kv startup circuit. All rods fully inserted on the reactor trip. All systems performed as designed. Operators are preparing to place the unit in Mode 5, while preparing to assess the damage to the 500 Kv transformer. All emergency diesel generators remain operable in standby. "Unit 1 was unaffected by this event and remains at 100% power. "This notification also constitutes a late 4 hour notification for the RPS actuation. "To summarize, on August 16, 2008, at 2356 PDT, the 'C' phase 500 Kv transformer failed resulting in a fire and an automatic reactor trip, and automatic actuation of AFW. An unusual event was declared on August 17, 2008, at 0012 PDT due to the fire. Cal Fire was called to assist and support the on-site fire brigade. The fire was extinguished and the NUE was downgraded at 0231 PDT." The NRC Resident Inspector has been notified as well as State and local government agencies. The licensee intends to issue a press release. R4DO (Lantz) notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  | 0 | 2008-08-17
44418 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-08-15 16:04 | 2008-08-15 17:41 | 2008-08-15 | SHUT DOWN REQUIRED BY TECHNICAL SPECIFICATIONS "Administratively entered technical specification 3.0.3 and complying with the action statement." A 0.19 gpm leak developed from a structural weld crack on the charging system (4B reactor coolant pump seal injection line). This leak is isolable. The cause of the crack is being evaluated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-08-15
44417 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-08-15 10:11 | 2008-08-15 17:10 | 2008-08-18 | INCIDENT REPORT ON UNRESOLVED MATERIAL DISCREPANCY ALARM "10 CFR 74.57(c) requires notification of any MC&A (Material Control and Accountability) alarm that remains unresolved beyond the time period specified for its resolution in the licensee's Fundamental Nuclear Material Control Plan. In the Solvent Extraction area of Building 333, [there is an abrupt alarm value.] When the alarm test was run on 8/15/2008, the input minus output value [exceeded the abrupt alarm value.] The investigation is completed but the alarm is not resolved. Measurement data for one of the inputs is the most assignable cause. Although an assignable cause was not identified, there is no indication that a material loss has occurred." The affected solvent extraction process has been shutdown by the license while alarm resolution is in progress. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2008-08-18
44416 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 1999-01-01 | 2008-08-15 14:38 | 2008-08-15 | AGREEMENT STATE - SMALL QUANTITY OF SPECIAL NUCLEAR MATERIAL UNACCOUNTED FOR "On August 12, 2008 UC Berkeley requested a meeting with RHB to provide information regarding their findings that they had not maintained adequate control of their SNM. Specifically they were unable to locate 17 grams of elemental uranium enriched to 43% in the isotope of U 235. The reason for the problem was considered to be inadequate material accounting practices for the period since 1978, due to inadequate methodology, apparently records were not maintained for the day-to-day consumption of uranium for research and subsequent discard of uranium that occurred routinely. There were no records to indicate use. Therefore this material is considered as 'material unaccounted for' (MUF) and an ongoing investigation is in progress to determine the disposition of the material between 1994 and 1997. Seventeen grams would equal about 15 pellets the size of a small pencil eraser. "The licensee informed NRC HOO of this issue, as information on 8/13/08. The licensee also informed RHB on 8/13/08. "The licensee clarified that this was a notification pursuant to 10 CFR 20.2201 at 1700 on 8/14/08 regarding their inability to locate this material. An investigation is ongoing to reconcile the records regarding lost or missing material at UC Berkeley. California Report Number: 081308 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-08-20
44415 | 0 | WEST VIRGINIA PAVING |  |  |  |  | 2008-08-15 06:00 | 2008-08-15 10:07 | 2008-08-15 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM THE BED OF A TRUCK An authorized gauge user while working at a jobsite site in McDowell County, WV stayed overnight at a motel in Grundy, VA which is just across the state line. Sometime between 2200 hours on 8/14/08 and 0600 hours on 8/15/08, a Troxler Model 3440 (S/N 27535) containing two sources, i.e., 8 millicuries Cs-137 and 40 millicuries Am-241/Be, was stolen from the bed of the employee's pickup truck. The Troxler gauge was locked inside its case and contained inside a locked transport box chained and bolted to the bed of the truck. The chain had been cut and the lock on the transport box broken to remove both the Troxler gauge and its case. The licensee notified the NRC Region I Office (Marie Miller) and filed a police report with the Grundy City Police department who are investigating the theft. The licensee has made no determination whether a reward will be offered. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-08-15
44414 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2008-08-14 10:00 | 2008-08-14 16:23 | 2008-08-14 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received from the state via fax: "Event Description: The South Carolina Department of Health and Environmental Control was notified on Thursday, August 14, 2008, at 1039 hrs, that a Troxler 3440 gauge, s/n 25120, containing 8 mCi of Cs-137 and 40 mCi of Am-241:Be, had been damaged at 1000 hrs on August 14, 2008. [DELETED], Senior Quality Control Specialist, stated that the gauge had been damaged by a steel wheel roller. Inspector [DELETED] responded to the scene and arrived at 1221 hrs. The area around the gauge had been properly roped off and the source rod was locked in its shielded position. The gauge was flipped and the control rod had broken free of the unit. The inspector surveyed the gauge and confirmed that the material was still within its proper containers. The gauge was returned to its transport container, and the inspector advised [DELETED] to return the gauge to its permanent storage location, secure it from further use, and to contact the manufacturer for further instruction regarding disposal. "Mr. [DELETED] was advised by Mr. [DELETED] to submit a written report detailing this event to the Department within 30 days. The event is open and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2008-08-19
44413 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-08-14 | 2008-08-14 15:17 | 2008-08-14 | AGREEMENT STATE REPORT - LOST SEALED SOURCE The following information was received via e-mail from the State of California: "On June 2, 2008, a routine inspection was performed on NOVA R&D, Inc. (RML # 5446-33). The licensee was issued a Notice of Violation for not performing the leak test on the sealed source (Am/Be, S/N 77C6654, 10 mCi on 3/7/90) after November 16, 2004. According to the written response, received August 14, 2008, the licensee performed a physical inventory of the radioactive sealed sources after the routine inspection and determined that the Am/Be sealed source was missing from the ground safe where the other sealed sources are stored. A thorough search for the source was conducted, but the Am/Be source was not located. The licensee is still trying to find the source in the facility and also searching for any documentation of proper disposal." California Rpt #081408 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-08-19
44412 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-08-14 | 2008-08-14 12:52 | 2008-08-14 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following information was provided by facsimile from the State of Florida: "Troxler gauge [Model 3430 s/n 30064 with 40 mCi Am-241/Be s/n 47 - 27059 and 10 mCi Cs-137 s/n 750-5034] was stolen from back of company's truck at a private residence, sometime between 0030 and 0430 on 14 Aug 2008. Company will offer reward. Company might possibly contact the press. Orlando area office will investigate." FL Report FL08-122 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-08-19
44411 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-08-13 15:49 | 2008-08-13 17:17 | 2008-08-13 | HYDRAULIC OIL SPILLED INTO LAKE WYLIE DISCHARGE CANAL "Notification to SCDHEC [South Carolina Department of Health and Environmental Controls] and the National Response Center [# 880488] due to a release of approximately 0.5 gallons of hydraulic fluid to Lake Wylie Discharge Canal from a hydraulic line failure on a piece of equipment. "The hydraulic fluid reached Lake Wylie via yard drain. The fluid reaching Lake Wylie was contained by oil booms in place in the discharge canal." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-13
44410 | 0 | RANCHO SECO | 1 |  |  | [1] B&W-L-LP | 2008-08-13 | 2008-08-13 17:50 | 2008-08-14 | UNAUTHORIZED PROTECTED AREA ENTRY Actual entry of an unauthorized person into the protected area around ISFSI. Contact the NRC Operations Officer for additional details. * * * UPDATE AT 2153 EDT ON 8/14/08 FROM SCHELOSKSY TO HUFFMAN * * * Additional information related to unauthorized protected area entry. Contact the NRC Operations Officer for additional details. R4DO (Lantz) notified. 73.71 Group e-mailed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-08-13
44409 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-08-13 09:31 | 2008-08-13 16:36 | 2008-08-13 | FITNESS FOR DUTY A licensed employee had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2008-08-13
44408 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-08-01 | 2008-08-12 12:41 | 2008-08-12 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the state via e-mail: "The Creston Public School purchased two self-luminous signs in 1990. The signs were SRB model Betalux E 10 with 9.75 curies of tritium in each sign. The school did an inventory in 2005. The School did not return its annual inventory in 2006. The school was dissolved in May of 2006 and the property was transferred to Leigh Public School. Leigh Public Schools informed the Agency [Nebraska Division of Radioactive materials] that the property was transferred to the Village of Creston. Representatives of the Village of Creston, speculate that the school was possibly left unlocked and unattended for a period time and during that time period the signs were removed. The disposition of the signs is unknown. The Agency made numerous attempts to determine the status of the signs and ultimately the Agency determined that the signs are lost." The licensee discovered that the signs were missing on 01/01/2008. Manufacturer: SRB Technologies Inc Serial Number: 13152 and 13153 Nebraska event NE080006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-08-15
44407 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2008-08-11 07:00 | 2008-08-12 09:11 | 2008-08-12 | UTAH AGREEMENT STATE REPORT - FIXED GAUGE BROKEN SHUTTER "The Utah Division of Radiation Control was notified by service personnel on 08/11/2008 at approximately 10:00 a.m. MDST and spoke with the licensee regarding the incident at 5:00 p.m. MDST. The RSO was attempting to close the shutter of a fixed gauge on the 'Syn Tower' so that maintenance personnel could work inside the vessel. [Ohmart, model SH-F1, serial number LS-620]. The device shutter resisted turning when the RSO attempted to close the gauge. The RSO then 'tapped lightly' on the shutter handle with a bolt to get it to turn. It turned slightly and the RSO put the bolt down to turn the shutter handle by hand. Both of the shutter handle screws sheared off and the shutter could not be closed. An authorized service licensee was able to close the shutter while the gauge was in place. The gauge was then removed and taken offsite for repair by an individual licensed to perform these services. The RSO has completed the manufacturer's 40 hour training course." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2008-08-15
44406 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-11 14:16 | 2008-08-12 09:08 | 2008-08-12 | TEXAS AGREEMENT STATE REPORT - BADGE INDICATES OVEREXPOSURE "On August 11, 2008, the agency received written notification from the Radiation Safety Officer (RSO) that a worker's quarterly film badge showed a reading of 40,080 mrem. Additional processing by the provider left the assessment as indeterminate however actual personnel exposure is beyond reality since the licensee is an operator [of] moisture density gauges only. A preliminary investigation has shown that the operator did not maliciously expose or tamper with the dosimeter and there was nothing unusual about the conditions of storage. "The RSO stated that a full investigation will be performed to ascertain how the dosimeter received such extensive radiation exposure." The State of Texas will be conducting an on-site investigation. Texas Report Number: I-8533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-08-15
44405 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2008-08-06 18:40 | 2008-08-11 19:19 | 2008-08-11 | AGREEMENT STATE REPORT - BROKEN SHUTTER ON FIXED GAUGE The state provided the following via facsimile: "During a shift change for the Euclid drivers, the crusher operator went to the bottom of the crusher and attempted to close the shutter of an Ohmart fixed gauge, [Model SH-F2, serial number 1849CG], containing 1000 mCi of Cs-137, but although the handle turned, the shutter did not close. The operator indicated that there had been no resistance when the shutter handle was turned. One of two screws in the shutter handle was broken and therefore the shutter would not turn when the handle was turned. The last time the shutter was closed was on July 3, 2008. It is unknown at this time when or how the screw was broken. This device will be repaired by an individual specifically licensed by the Utah Division of Radiation Control to perform such service." Utah report number: UT080002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2008-08-14
44404 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2008-08-11 00:49 | 2008-08-11 04:21 | 2008-08-11 | MANUAL REACTOR TRIP DUE TO DEGRADING CONDENSER VACUUM "At 0049 EDT on 8/11/2008, the Harris Nuclear Plant was manually scrammed from 21% power due to indications of degrading condenser vacuum. At the time, a reactor shutdown was in progress with indications of a degraded condenser boot seal. The unit was stabilized in Mode 3 with no additional equipment failures or other complications." The reactor is currently at normal operating pressure and temperature. The highest vacuum observed was 8". All rods inserted into the core after the manual trip. Auxiliary feed water did not start as a result of the trip. Steam generator level is being maintained via normal feed water flow path. Decay heat is being removed via the steam dumps to atmosphere. There is no known primary to secondary leakage. No power-operated or manual reliefs lifted during the transient. The grid is stable and loads are being supplied via the station start-up transformer. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-08-11
44403 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2008-08-09 06:28 | 2008-08-09 07:18 | 2008-08-21 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA The licensee reported an attempt to introduce contraband into the protected area. The NRC resident inspector will be notified. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION PROVIDED AT 0924 ON 08/21/08 FROM ARNIE CRIBB TO JEFF ROTTON * * * After investigation of the incident, licensee has determined that there was no malevolent intent and hereby retracts the original notification. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO( Rose), ILTAB (Hahn) and Part 73.71 Group (via email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-08-09
44402 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2008-08-09 02:04 | 2008-08-09 05:24 | 2008-08-09 | MANUAL REACTOR SCRAM DUE TO FAILURE OF REHEAT STOP VALVE TO OPEN DURING TURBINE VALVE TESTING "While performing main turbine reheat stop valve surveillance testing, Reheat Stop Valve 1RV 1A failed to reopen simultaneously with a Moisture Separator C high level alarm. Plant alarm response procedures require a reactor scram in this situation. Operating crew inserted a manual scram at 0204 CDT. Immediately after the scram, RPV level responded as expected and dropped below the Group 2 containment isolation setpoint. All rods inserted fully. RPV level is being controlled with RFP A and the startup valves. RPV pressure is being controlled on the bypass valves. The Group 2 isolation was complete with no anomalies. "This report is being submitted pursuant to 50.72(b)(2) for RPS actuation (4 hour report) and 50.72(b)(3) for a valid Group 2 isolation (8 hour report)." The scram was characterized as uncomplicated. The lowest reactor vessel water level reached was - 20 inches. No safeties lifted during the transient and all systems functioned as required. The cause of the reheat stop valve failure to reopen is under investigation. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 69 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-08-09
44401 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2008-08-08 15:20 | 2008-08-08 20:50 | 2008-08-08 | OFFSITE NOTIFICATION TO MARICOPA COUNTY ENVIRONMENTAL SERVICES "Arizona Public Service Co. made an offsite notification to Maricopa County Environmental Services at 1520 MST on 8/8/08 to report a loss of power to the Palo Verde Nuclear Generating Station drinking water supply pumps. The pumps were out of service on 8/8/08 between the hours of 0532 and 0620 MST. Full service has been restored." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-08
44400 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-08-08 05:05 | 2008-08-08 17:43 | 2008-08-08 | REACTOR SHUTDOWN DUE TO SMALL STEAM LEAK "This is a Voluntary Notification in accordance with NUREG 1022 Section 2.7 of a controlled shutdown that can be considered to be of Generic Interest to the NRC and is not reportable otherwise per 10CFR50.72 or 10CFR50.73. Operations performed the controlled shutdown of Browns Ferry Unit 1 this morning in order to isolate and repair a small steam leak. The leak was determined to be from a Code Class 2 piping thermo-well located in the Unit 1 Steam Tunnel. The controlled shutdown was uneventful with all systems responding as expected. There was no impact to the health and safety of the public. "Units 2 and 3 were operating at 50% power when Unit 1 was shutdown and were not affected by this event. "The Senior NRC Resident Inspector has been notified of this Voluntary Notification." | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW | [5 empty] | 0 | 2008-08-08
44399 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-08-07 12:30 | 2008-08-08 16:01 | 2008-08-08 | DEGRADED PRINCIPAL SAFETY BARRIER "This is a late non-emergency notification to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(ii)(A) due to the degradation of a principal safety barrier. "A flaw in a weld in a 3/4 inch test connection off the seal water injection line for the 4B reactor coolant pump was identified at approximately 1230 during a containment entry on August 7, 2008. The flaw is leaking at the rate of approximately 0.14 gpm (current total), it [the leak] is isolable, and the leakage is currently considered as unidentified leakage from the reactor coolant system. The Technical Specification limit for unidentified leakage is 1.0 gpm. "Currently, the leak is being monitored while repair options are evaluated." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-08-08
44398 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-08-05 | 2008-08-08 13:38 | 2008-08-08 | LOST RADIOACTIVE MATERIAL FOUND IN SCRAP YARD "Material received at scrap yard on August 5, 2008. Wisconsin DHS verified via phone that material was locked in a secure location from members of the public. On August 7, 2008 DHS investigated the radioactive material, a compacted 55 gallon drum with multiple pieces of scrap inside drum. A mini-spec GR-135DN was used to determine the source of radiation as Ra-226. Radiation exposure and contamination surveys were conducted on the outside of the compacted drum. The maximum exposure observed was 500 uRem/hr. The contamination survey on the drum found no contamination. DHS staff tried to locate the source of radiation inside the drum where the highest radiation levels were located. During the attempt, several pieces of scrap were removed and surveyed and no radiation above background except for one piece that read above background. Material was properly tagged and bagged. The staffs gloved hands were frisked and contamination was present. Individual doffed gloves and re-performed hand frisk and no contamination was found. The staff halted any further handling activities at this time to prevent any possible spread of contamination. The material was properly tagged, bagged and stored at the scrap yard in a locked holding area that is not accessible by members of the public. DHS is exploring options to properly dispose of this radioactive material." State Event Report: WI080008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-08-13
44397 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-08-07 14:00 | 2008-08-08 11:29 | 2008-08-08 | AGREEMENT STATE REPORT - UNDEREXPOSURE DURING HDR MEDICAL TREATMENT DUE TO EQUIPMENT MALFUNCTION The State received notification of a possible medical event due to an equipment malfunction. The licensee was treating a patient for rectal cancer using an HDR Nucleotron Micro Select Model 105.999 Serial 31776. The prescribed treatment consisted of the administration of 29 catheter doses of Iridium-192. During the 12th catheter dose, an equipment malfunction caused a failure of the administered treatment. The failure mode was Code 200 - "No radiation detected." The failure mode caused the unit to stop treatment by not proceeding to the next catheter. Nucleotron immediately contacted. A service technician is expected to arrive on 8/8/08 for repair of the device. Once the HDR unit is repaired, the treatment plan and written directive will be modified and treatment of the patient resumed. Patient and physician have been advised of the treatment interruption and no adverse impact is expected. The State of Ohio plans to send an inspector to the facility on 8/11/08. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2008-08-13
44396 | 0 | ARMED FORCES RADIOBIOLOGY RSCH INST |  |  |  | 1100 KW TRIGA MARK-F | 2008-07-29 10:13 | 2008-08-08 09:57 | 2008-08-08 | TECHNICAL SPECIFICATION VIOLATION - LOW POWER OPERATION WITHOUT GAS STACK MONITOR IN SERVICE Technical Specification 3.5.1 requires that the Gas Stack Radiation Monitor be in service when the AFRRI reactor is at power. Based upon a licensee review of the operations log book on August 5, the licensee discovered that the reactor had operated at a low power level for a short duration while the Gas Stack Monitor was out of service. Specifically, a K-excess calculation was conducted at 10:13 EDT on 7/29/08 at a power level of 5 watts. While this activity was in progress, the Gas Stack Rad Monitor was inoperable for maintenance reasons and had not been verified to be in service as required by technical specifications and procedures. The K-excess calculation was completed and the reactor shutdown by 10:17 EDT (duration of TS violation was approximately 4 minutes). The licensee has provided remedial training to facility operators. The NRC project manager was notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MD | NPR | [5 empty] | 0 | 2008-08-08
44395 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-08-08 04:00 | 2008-08-08 09:46 | 2008-10-28 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE "At 0828, the Agency [state] received a call from the Radiation Safety Officer (RSO) for GME Engineering Consulting Incorporated, stating that Troxler model # 3411 moisture/density (M/D) gauge containing a Cesium (Cs) - 137 source and an Americium (Am) - 241 source had been stolen out of one of their trucks parked at their facility. The technician had returned from a job at about 4:00 AM and went into the office to make copies of some of his documents. When he returned to the truck, he found the lock used to secure the M/D gauge in the truck bed had been cut, and the M/D gauge and transport case were both missing. The cable used in association with the lock to secure the gauge was also damaged. The technician reported the event to his RSO, who notified the Agency. Local Law Enforcement has been informed of the event. The RSO stated that he would supply additional information on the event to the Agency via e-mail. "The Agency received the following update information. The gauge serial # is 9389 containing one 8.3 millicurie Cs-137 source serial # 40-6732, and one 40.0 millicurie Am-241 source serial # 47-5906. The police arrived at the office at about 9:30 AM and obtained fingerprints from the technician's truck and opened a case file. The Dallas police case number is 245096V." Texas Incident Report # I-8532 * * * UPDATE PROVIDED BY ART TUCKER TO JASON KOZAL ON 10/28/08 AT 1748 * * * The following was provided by the state via e-mail: "The Agency was contacted on 10/28/08 by an individual stating that a moisture/density gauge was for sale on the web site Ebay. The individual stated that he notified the individual selling the gauge that he needed a license to do so. The individual selling the gauge stated that he had bought it at a pawn shop and that it would have to be OK if the pawn shop sold it. An Agency investigator looked the item up on Ebay and found a serial number and service contractor's name. This gauge had been reported stolen in the State of Texas in August, 2008. The service contractor was contacted and provided the name of the licensee who owned the gauge. The Radiation Safety Officer for the licensee confirmed that based on the serial number of the gauge it was one of his. A fax was sent to Ebay requesting assistance in locating the seller. The seller became concerned about the legal ramifications of possessing the gauge and returned it to the pawn shop. The licensee was informed that the gauge had been returned to the pawn shop. The licensee informed the Agency of this. The Agency arranged for an inspector to meet an individual from the licensee to retrieve the gauge. The gauge was turned over to the licensee by the pawn shop owner. The gauge appears to be undamaged. The licensee will send the gauge to the manufacturer for inspection and leak test." Notified R4DO (Spitzberg), FSME (Einberg), ILTAB (via e-mail), and Mexico (via fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-08-13
44394 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-08-07 16:00 | 2008-08-07 19:21 | 2008-08-07 | OFFSITE NOTIFICATION TO SOUTH CAROLINA ENVIRONMENTAL AGENCY "The quarterly National Pollutant Discharge Elimination System whole effluent toxicity testing for outfall #002 failed for July 2008. This required notification to the South Carolina Environmental Agency." The system was the Conventional Waste (WC). The licensee will be notifying the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-07
44393 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-08-07 16:00 | 2008-08-07 17:26 | 2008-08-07 | CIVIL DISTURBANCE AT THE NORTH ANNA NUCLEAR INFORMATION CENTER "At 1430 hours on 8-7-08, approximately 20 individuals from a group identified as the Southeast Convergence for Climate Action arrived at the North Anna Nuclear Information Center (NANIC) and initiated a civil disturbance within the center. [The NANIC is located just inside the Owner Controlled Area]. When the NANIC closed at 1600 hours, 8 of the individuals refused to leave the building. Local Law enforcement informed the individuals that they would be placed under arrest, and 2 individuals exited the area. The remaining 6 individuals were detained by Local Law Enforcement Officers and removed from Dominion property." Licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2008-08-07
44392 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-08-07 07:00 | 2008-08-07 16:46 | 2008-08-07 | POWER REDUCED TO COMPLY WITH RIVER WATER QUALITY STANDARDS "On August 7, 2008 Browns Ferry Nuclear Plant Units 1, 2, & 3 reduced reactor power to 50 percent to ensure continued thermal compliance with water quality standards as regulated by the Alabama Department of Environmental Management. This was caused by an unexpected failure of cooling tower components, rendering the cooling towers unavailable. Plant Operations continues to monitor river conditions and may take further actions as required to maintain compliance. "There were no safety systems challenged during the power reductions. "This is an informational report based on media interest. TVA does not expect to make an official news release. The NRC Resident Inspector was notified." | 50 | 50 | 50 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW | [5 empty] | 0 | 2008-08-07
44391 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-08-07 13:50 | 2008-08-07 14:47 | 2008-08-07 | DISCOVERY OF INAPPROPRIATE UNESCORTED ACCESS GRANTED TO LICENSEE EMPLOYEE Actual entry into a protected area of an individual that had gained unescorted access through withholding information during the badging process. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-08-07
44390 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-08-07 12:15 | 2008-08-07 12:13 | 2008-08-07 | UNAVAILABILITY OF TECHNICAL SUPPORT CENTER "At 1215 EDT on Thursday, August 7, 2008, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system charcoal filter was removed from service for scheduled preventive maintenance on one of the TSC air conditioning systems. The charcoal bed filtration system is also out of service in support of the maintenance on the air conditioning system. "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. Air conditioning system maintenance is scheduled to complete at 1515 EDT on Thursday, August 7, 2008. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility. The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM BRAD LEWIS TO JOHN KNOKE AT 1657 EDT ON 08/07/08 * * * "The TSC air conditioning system was returned to functional status at 16:25 on Thursday, August 7, 2008. "This follow up notification is being made to provide closure from the initial notification under 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." The licensee has notified the NRC Resident Inspector. Notified R3DO (David Hills) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-08-07
44389 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2008-07-15 | 2008-08-07 10:18 | 2008-08-07 | EXTERNAL CONTAMINATION FOUND ON A RADIOPHARMACEUTICAL DELIVERY PACKAGE "The package was received July 15, 2008 by the VA Medical Center in Fayetteville, North Carolina. "The VHA National Health Physics Program was notified of the event on August 7, 2008, at 9:30 AM ET. "A wipe test performed on the external surface of the package upon receipt on July 15, 2008 indicated a removable contamination level of 254 [disintegrations per minute per square centimeter] as compared to the regulatory limit of 220 [disintegrations per minute per square centimeter]. Surveys inside the package did not indicate elevated contamination. "The package contained radiopharmaceuticals with Tc-99m and was shipped from Cardinal Health in Fayetteville, North Carolina. The vendor/shipper also serves as the delivery carrier. The shipper/delivery carrier was immediately notified of the contaminated package after the receipt survey on July 15, 2008 by a nuclear medicine technologist at the VA Medical Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | NC | HOS |  | 20.1906(d)(2) |  |  |  | 0 | 2008-08-07
44388 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-08-07 02:28 | 2008-08-07 04:12 | 2008-08-07 | TRIP FROM 50% POWER FOLLOWING LOW PRESSURE HEATER STRING ISOLATION "On August 7, 2008 at 0228 EDT, TVA was reducing reactor power in preparation for a planned reactor shut down. While at approximately 50% power, the feedwater system isolated due to high levels in the low pressure heater strings. Based on the condition stated, the reactor was manually scrammed. All systems functioned as designed in response to the scram. The plant is currently being maintained in Mode 3 Hot Standby condition." All control rods fully inserted on the manual trip. Decay heat is being removed via auxiliary feedwater to the steam generators steaming to the main condenser. Offsite power is supplying safety buses and emergency diesel generators are available if required. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-08-07
44387 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2008-08-06 18:40 | 2008-08-06 21:09 | 2008-08-08 | SAFETY PARAMETER DISPLAY SYSTEM ASSESSMENT LOST "This 8-hour non-emergency report is being made based upon requirements of 10CFR50.72(b)(3)(xiii) which states, 'The licensee shall notify the NRC as soon as practical and in all cases within eight hours of the occurrence of any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)'. "At 18:40 ET on Wednesday, August 06, 2008, the Reactor Operator At-the-Controls (OATC) discovered that the Safety Parameter Display System (SPDS) Computer Display was not updating data. This was discovered during periodic Control Room panel walkdowns. "The last data update on the SPDS display was at 20:02 ET on Tuesday, August 05, 2008. "All other Plant Process Computer functions are available. Information Technology Department personnel will be investigating the cause of the loss of SPDS capability, which is currently unknown. "No other Control Room emergency assessment capabilities have been adversely affected. All Control Room panel indicators and annunciators are responding properly." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0935 ON 08/08/08 FROM BRIAN FINCH TO JEFF ROTTON * * * "On Wednesday, August 06, 2008 at 2151 EDT, the Plant Process Computer (PPC) was shutdown and successfully restarted at 2318 EDT. Upon restart, SPDS was verified operable." The licensee notified the NRC Resident Inspector. Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-08-06
44386 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-08-06 14:20 | 2008-08-06 16:47 | 2008-08-06 | INADVERTANT ACTUATION OF EMERGENCY SIRENS "At approximately 1420 CDT on August 6, 2008, a Dakota County Communications Center Shift Supervisor inadvertently activated the Dakota County sirens from the primary unit during conduct of a vendor requested silent siren test. The licensee was notified of the siren activation by the vendor. Seven of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for less than one minute. No press release is planned by Xcel Energy." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-08-06
44385 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-08-05 20:29 | 2008-08-05 22:27 | 2008-08-05 | TECH SPEC REQUIRED SHUTDOWN DUE TO EXCESSIVE UNIDENTIFIED LEAKAGE "On August 5, 2008, a planned shutdown was in progress to repair a control rod drive mechanism due to excessive leakage (within Tech Spec identified leakage limits). During the shutdown, the site experienced excessive unidentified leakage of approximately four gallons per minute for short periods following charging pump starts, due to leakage past the letdown relief valve. [this first occurred at 1629] As a result of the plant shutdown, and not being in a steady state condition, PCS leakage is unable to be definitively determined. Limiting Condition of Operation 3.4.13 was entered at 1629 hrs. The plant was in Mode 3 at 1955 hrs. The Tech Spec requirement is to restore leakage to within limits within 4 hours. If not within limits within 4 hours, be in Mode 3 within 6 hours (August 6, 2008 at 0229 hours) and be in Mode 5 within 36 hours (August 7, 2008 at 0829 hrs). This event is being reported as a 4-hour non-emergency report in accordance with 10 CFR 50.72(b)(2)(i), Tech Spec required shutdown." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-08-05
44384 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-08-04 18:45 | 2008-08-04 22:00 | 2008-08-08 | LOSS OF 84 OF 94 EMERGENCY SIRENS DUE TO INCLEMENT WEATHER "At approximately 1830, a severe thunderstorm moved through Ogle County. At 1845, 84 of 94 emergency sirens for Byron Station became inoperable. There is currently no estimated time of repair due to the severe number of power outages." Sirens affected provide coverage for Ogle County (population ~52,000) and a small portion of Winnebago County (population ~296,000). These are utility owned sirens. These sirens are not shared with other sites. In the event of a need for the sirens, a contingency plan using a "route alert" by the state will be implemented. There are no off-site power or grid concerns. The NRC Resident Inspector was notified by the licensee. No other state or local government agencies have been notified by the licensee. * * * UPDATE ON 8/5/08 AT 0321 FROM GODBY TO SNYDER * * * Troubleshooting and restoration activities continue for the emergency sirens. Presently 73 of 94 sirens remain inoperable. Notified R3DO (Hills). * * * UPDATE AT 0645 ON 8/5/2008 FROM STEVE GODBY TO MARK ABRAMOVITZ * * * At this time, 44 of the sirens are still inoperable. The licensee estimates that all sirens will be operable by 1800 CDT today. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 0902 EDT ON 8/5/2008 FROM GREG BALESTRIERI TO MARK ABRAMOVITZ * * * At 0755 CDT, 55 sirens were inoperable. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 1258 EDT ON 8/5/2008 FROM GREG BALESTRIERI TO S. SANDIN * * * At 1155 CDT, 48 sirens were inoperable. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 1713 EDT ON 8/5/2008 FROM GREG BALESTRIERI TO S. SANDIN * * * At 1500 CDT, 46 sirens were inoperable. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 1933 EDT ON 8/5/2008 FROM JIM LYNDE TO S. SANDIN * * * Six (6) more sirens have been returned to service. Forty (40) sirens remain inoperable. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 2255 EDT ON 8/5/2008 FROM JIM LYNDE TO J. KOZAL * * * Seven (7) more sirens have been returned to service. Thirty-three (33) sirens remain inoperable. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 0757 EDT ON 8/6/2008 FROM MARTY WOLFE TO J. ROTTON * * * As of 0600 CDT on 08/06/08, four (4) more sirens have been returned to service. Twenty-nine (29) sirens remain inoperable with estimate of greater than 24 hours before restoration. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). * * * UPDATE AT 2345 ON 8/6/2008 FROM BRIAN HERRING TO MARK ABRAMOVITZ * * * At 2200 CDT 8/6/2008, 17 sirens are still inoperable. The estimated time to repair the remaining sirens is approximately 24 hour. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills) via e-mail. * * * UPDATE AT 1542 ON 8/8/2008 FROM MIKE LINBEMANN TO JOHN KNOKE * * * As of 1432 CDT on 08/08/08 all emergency sirens for Byron Station are operable. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-08-04
44383 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-08-04 12:00 | 2008-08-04 14:17 | 2008-08-04 | SPECIFIED SYSTEM ACTUATION - BOTH AUXILIARY BOILER FEEDWATER PUMPS STARTED UNEXPECTEDLY "On August 4, 2008 at approximately 1200 hours, both motor driven auxiliary boiler feed pumps automatically started during the performance of procedure 3PT-M13B1, 'Reactor Protection Logic Channel Functional Test Train B'. Operations secured the pumps and returned them to auto at approximately 1207 hours. The event did result in water addition to the steam generators but Operations did not observe any reactivity changes on the nuclear instrumentation. The cause of the event is under investigation." Operators did observe a 2% increase in steam generator water level but no limits or alarms were approached. The licensee has notified the NRC Resident Inspector and New York State Public Service Commission. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-08-04
44382 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-08-04 08:12 | 2008-08-04 13:14 | 2008-08-04 | 24 HOUR FITNESS FOR DUTY REPORT A non-licensed contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The contract employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2008-08-04
44381 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2008-08-04 09:46 | 2008-08-04 11:07 | 2008-08-04 | PLANNED LOSS OF ERDS FOR PROCESS COMPUTER UPGRADE "The Callaway Plant Process Computer is being upgraded to a newer system. This implementation period is expected to start on August 4, 2008 and last approximately 14 days. During the implementation time for this upgrade, the Emergency Response Data System (ERDS) system will be out of service. Compensatory actions for emergency situations have been established. "This event is reportable per 10 CFR50.72(b)(3)(xiii) since this constitutes a loss of ERDS for the duration of the evolution." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-08-04
44380 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2008-08-03 03:52 | 2008-08-03 05:29 | 2008-08-04 | UNUSUAL EVENT - HYDRAZINE LEAK IN NON-VITAL AREA OF THE TURBINE BUILDING "A hydrazine leak has occurred in the Unit 1 Turbine Building sump area approaching levels (IDLH) Immediately Dangerous to Life and Health. An NUE was declared @ 0352 CST. At this point, the leak is not within or contiguous to any vital areas. The area has been evacuated, accountability is complete, and no injuries have resulted due to the leak." The leak is ongoing in the area of the condensate and heater drain pumps. The licensee stopped adding hydrazine to the condensate at 1800 CDT on 8/2/2008. The licensee notified the NRC Resident Inspector * * * UPDATE RECEIVED ON 08/03/08 AT 2340 EDT FROM JENSEN TO NORWOOD * * * Licensee terminated from Unusual Event EAL HU3.1, Release of Toxic or flammable gases deemed detrimental to normal operation of the plant at 2220 hours CDT. Criteria used to exit - Three (3) consecutive air samples had less than detectable limits of hydrazine for the entire area. No press release scheduled. Current plant condition - Mode 1, 100% power. Licensee notified NRC Resident Inspector, State, Local, and tribal authorities. Notified NRR EO (Samson Lee), IRD (McDermott), R3DO (Pelke), DHS (Frost), and FEMA (LaForty). * * * UPDATE RECEIVED AT 1034 EDT ON 08/04/08 FROM JOHN KEMPKES TO JEFF ROTTON * * * At 2345 CDT on 08/03/08, the licensee issued a press release for the termination of the NUE and the return to full power of Prairie Island Unit 1. The licensee notified the NRC Resident Inspector, the state, and local emergency response organizations. Notified the R3DO (Pelke). | 28 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-08-03
44379 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-07-31 13:45 | 2008-07-31 21:59 | 2008-07-31 | POSTULATED HIGH-ENERGY LINE BREAK THAT COULD DISABLE BOTH TRAINS OF COMPONENT COOLING "At 1345 Prairie Island staff declared both trains of Unit 2 Component Cooling (CC) system inoperable due to discovery that a postulated high energy line break (HELB) in the Turbine Building that could fail a CC line in the turbine building that would affect both trains of CC. The inoperability of Unit 2 CC caused entry into Technical Specification LCO 3.0.3. The CC line in question is not automatically isolated on a safety injection signal and the loss of CC inventory would eventually affect both trains of CC. Since a Unit 2 HELB could directly result in a loss of both trains of CC (a system that is required to meet the single failure criterion), the CC system does not meet the single failure criterion in the as-found configuration. Thus, in accordance with the guidance in NUREG 1022, this condition is reportable per 10 CFR 50.72(b)(3)(ii). "The CC line in the Turbine Building was isolated at 1614 on 7/31/08 returning Unit 2 CC to operable status. Unit 2 remained at 100% power." The isolated line went to a chemistry lab cooler that can be isolated during operation. The condition was discovered during a high-energy line break vulnerability walk-down. A similar line on Unit 1 was already isolated. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-07-31
44378 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-04-01 | 2008-07-31 18:11 | 2008-07-31 | AGREEMENT STATE REPORT - LOSS OF LESS THAN CAT 3 LEVEL Gd-153 SOURCES "The licensee disposed of an ADAC camera in April 2008 and inadvertently failed to remove the 2 Gd-153 sources, isotope products serial numbers E2-886 and E2-890, which contained 250 mCi (9.25 GBq) each as of May 2007. The Gd sources were contained within lead shielding in the device. The sources in their shielding do not present a hazard. Currently, each of the unshielded sources would present a hazard with an exposure rate of about 124 mr/hr at one foot. Currently, the sources have decayed to around 67 mCi (134 mCi total). As of 7/31/2008, the licensee has not been successful in locating the sources. "According to the licensee, Norcal, a company that performs installation and removal of medical devices, removed the ADAC Vantage camera, and disposed of it sometime in April 2008 to a Waste Transfer Station, Waste Management, in San Leandro. "Waste Management was contacted and provided the names of the 2 metal recycling companies they would have used to recycle the metal. DC Metals and ALCO metals were both contacted and stated that they do not have any such device at their facility. They indicated if they had received it, the gamma camera would have been recycled to scrap metal very quickly. "The RSO stated that she just learned of this incident after their consultant had asked them last week for information regarding the disposition of the two 250 mCi Gd- 153 sources. After checking, they learned the sources had not been removed and were missing. The licensee is investigating to try and determine the location of the missing two Gd-153 sources." Per report, the discovery date of this event was 7/24/2008. California Report #073008. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-08-05
44377 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2008-07-31 08:17 | 2008-07-31 11:03 | 2008-07-31 | REACTOR TRIP DURING TESTING "Unit one (1) experienced a reactor trip during SP-1003 Analog Protection Functional Test. The yellow Tave channel was in test when the red Tave channel bistable failed causing an OTDT reactor trip. Applicable emergency operating procedures were entered and completed. The plant is now implementing 1C1.3, the normal plant shutdown procedure. "All systems performed as expected with exception of 11 turbine driven auxiliary feed (AFW) pump auto started and tripped 50 seconds later on low suction / discharge pressure which the plant is continuing to investigate. All rods inserted and all other AFW system components are operating as expected." Decay heat removal is from Main and Auxiliary Feedwater to the Steam Dump system. No safety or relief valves actuated. The plant is in a normal electrical lineup. The licensee notified the NRC Resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-07-31
44376 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2008-07-28 07:00 | 2008-07-31 10:57 | 2008-07-31 | AGREEMENT STATE REPORT - BROKEN SHUTTER ON FIXED GAUGE The state provided the following information via fax: "The shutter on an Ohmart fixed gauge, (Model SH-F2, serial number 1404CG), containing 1000 mCi of Cs-137 needed to be closed for maintenance to be performed on other equipment. When maintenance personnel tried to close the shutter, the shutter would not move to the closed position. Maintenance personnel tried to force the shutter closed and one of the screws for the operating handle broke. The shutter still would not close. The licensee removed the gauge from service, shielded the device, and had the device repaired by an authorized licensee." Utah event number: UT080001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2008-08-05
44375 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-07-30 14:31 | 2008-07-30 17:29 | 2008-07-30 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The following report was provide by the State of Texas via e-mail: "On 7/30/08 at about 1620 CDT the Agency was notified by a licensee that a moisture/density gauge was being returned from a work location in the city of Rowlett, Texas to its normal storage location via a truck when the user remembered he had left the gauge on the tail gate of the truck outside of it's transportation container. The individual stopped the truck and went to the back of the truck to retrieve the gauge. The gauge was no longer on the tailgate. The individual drove back to the work location via the same path he had traveled, but did not find the gauge on the road or near the road surface. He stated that he found no evidence that the gauge had been hit by a vehicle. After returning to the work location, the individual called his company RSO, who in turn called the State of Texas. The RSO also contacted the City of Rowett Police Department and notified them of the event. The RSO then dispatched four additional trucks to search the area for the gauge. The gauge is a Troxler model 3430 M/D gauge serial #25249 containing one 8 millicurie Cs-137 source ser#75-8052, and one 40 millicurie Am 241 source ser #47-21519. The individual using the gauge stated that he had not traveled for more than 10 minutes before he realized that he had not secured the gauge properly. The RSO stated that they would continue to search for the gauge and notify the State when it is found." The State noted that the source rod had been in the shielded position and locked when it was placed on the tailgate. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-08-04
44374 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-07-29 14:00 | 2008-07-29 19:09 | 2008-07-29 | PRESS RELEASE CONCERNING IMPACT OF EARTHQUAKE ON SOUTHERN CALIFORNIA EDISON ASSETS On July 29, 2008, SCE issued a press release regarding the earthquake that occurred on the same day. Along with information on other facilities, the press release included information on San Onofre Nuclear Power Plant and stated: "The earthquake was felt at the San Onofre Nuclear Generating Station site. There were no safety issues reported and no indications of any damage. The plant continues to operate normally." The NRC Resident Inspector has been notified. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-07-29
44373 | 0 | ENGINEERING CONSULTING SERVICES |  |  |  |  | 2008-07-29 14:00 | 2008-07-29 15:38 | 2008-07-29 | MOISTURE DENSITY GAUGE RUN OVER BY COMPACTOR At approximately 1400 EDT on 07/29/08 a CPN moisture density gauge, model #MC1DR - S/N M36056763, containing a Cs-137 10mCi and Am-241:Be 50 mCi source was run over by a compactor at a construction site at 7152 Heller Loop in Springfield, VA. The sources remained in the safe stored position during the incident, however, the Cesium source rod was broken off. The device was secured and removed from the construction site after a rad survey confirmed readings less than 0.4 mr/hr at 1 meter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-07-29
44372 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2008-07-24 14:00 | 2008-07-29 14:30 | 2008-07-29 | TEST REACTOR EXCEEDED LICENSED POWER LIMIT DURING CALIBRATION "Performing calorimetric power calibration of nuclear instruments with a new fuel element installed per SOP-44. Indicated power was 230kW. Calculated power after 70 minutes was 281kW, in excess of licensed power of 250kW. Also, due to miscalibration the 110% scrams on linear and percent power would not occur until an actual power of 124%. Reactor power was lowered and another calibration confirmed the error. The reactor was shutdown and the NRR Project Manager (Dan Hughes) was called." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2008-07-29
44371 | 0 | MEMORIAL HOSPITAL - SHERIDAN, WY |  |  |  |  | 2008-07-18 10:00 | 2008-07-28 14:26 | 2008-07-28 | MEDICAL ERROR - WRONG CHEMICAL USED IN PATIENT TREATMENT On the date described [07/18/08] an outpatient reported to the Nuclear Medicine Department for a Nuclear Medicine whole body bone scan. The technician drew up and injected the patient with 24.3 mCi mTc99 Sestamibi, I.V. instead of the proper cold kit which would have been Medronate. The error was not discovered until the patient returned 3 hours later for scanning and it was observed that the isotope was not properly tagged. Upon investigation, the reason for the poor tag was discovered. The patient was informed as well as the Department Manager, and the on-duty staff Radiologist. It was agreed by all that the patient would return on 07/21/08 to perform the study properly. According to the Radiation Absorbed Dose Table, the patient received the following: Gallbladder Wall - 1.6 Rads, Small Intestine - 2.4 Rads, Upper Large Intestine Wall - 4.32 Rads, Lower Large Intestine Wall - 3.12 Rads, Stomach Wall - 0.48 Rads, Heart Wall - 0.40 Rads, Kidneys - 1.6 Rads, Liver - 0.48 Rads, Lungs - 0.24 Rads, Bone Surfaces - 0.56 Rads, Thyroid - 0.56, Testes - 0.24 Rads, Red Marrow - 0.40 Rads, Urinary Bladder Wall - 1.6 Rads, Total Body - 0.40 Rads. It is believed that there was no ill effect on the patient. The technician has been re-instructed on the extreme importance of checking all the labels previous to preparing, drawing up and delivering any radioisotopes. The licensee is still in the process of confirming that the ordering physician has been notified of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2008-07-31
44370 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2008-07-28 08:50 | 2008-07-28 13:32 | 2008-07-28 | OFFSITE NOTIFICATION DUE TO A SODIUM HYPOCHLORITE SPILL "At approximately 0850 [CDT] on July 28, 2008 Xcel Energy notified the State of Minnesota's Duty Officer of a 53 gallon 12% Sodium Hypochlorite spill at the Prairie Island plant. The spill was due to a leak in the chemical piping. The release was stopped but only partially contained within the berms of the building. Some of the Sodium Hypochlorite seeped through the berms concrete walls and into the environment. The amount escaping the containment berm was less than the reportable quantity but was being reported since a portion did reach the soil." The licensee informed both the State and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-07-28
44369 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-07-25 | 2008-07-28 11:20 | 2008-07-28 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION This report was received from the state by facsimile. "On July 25, 2008, TEAM Industrial Services reported that a source was stuck in the guide tube and could not be returned to the shielded position. The industrial radiography camera involved is a AEA 880 Delta with serial number D2847. The source involved is an AEA source with serial number 45020B that is 49.8 Ci of Ir-192. While the source was in the collimator, the stand that was being used to x-ray welds fell on the guide tube. The radiographers attempted to return the source to the shielded position but could not. The radiographers then returned the source to the collimator and set up a 1 mr/hr boundary around the source. They called the Radiation Safety Officer for TEAM. TEAM contacted QSA Global to retrieve the Ir-192 source. The source was retrieved on July 25, 2008 at 5:30 PM. The guide tube and stand have been taken out of service. The camera and crank-outs are being sent to QSA Global to be inspected." Event Report ID: LA0800016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-07-31
44368 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-08-01 | 2008-07-28 10:46 | 2008-07-28 | AGREEMENT STATE REPORT - NUCLEAR GAUGE MALFUNCTION This report was received from the state by facsimile. "Exxon Mobil Chemical Company had an incident occur in August of 2005 and did not report the event. The event was discovered while an inspector was performing a reciprocity inspection on Ronan Engineering at Exxon on July 9, 2008. Ronan was contacted to package a nuclear gauge for transport and disposal. In August 2005, Exxon had a problem with a ThermoMeasure Tech 'SA-10' device that contained four 1000 mCi sources of Cs-137. The sources were QSA model CDC.93 with serial numbers 4421GN, 4424GN, 4425GN, and 4426GN in a rod configuration. In August 2005, the sources could not be returned to the shielded position to perform a shutter check. The facility returned the sources to the normal detent position for operation and continued to use the gauge. Ronan Engineering determined that the sources were encountering friction from the vessel source well. The vessel source well is part of the vessel and not part of the Ronan gauge. The gauge and sources were safely returned to the source holder, locked out, surveyed and leak tested on July 11, 2008. The gauge was shipped to ThermoMeasure Tech on July 11, 2008 for disposal." Event Report ID: LA0800015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-07-31
44367 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-07-27 03:40 | 2008-07-27 08:30 | 2008-07-27 | CABLE TRAY FIRE NEAR COOLING TOWER "C" SWITCHGEAR "Security notified Limestone County Sheriffs dispatch at 0340 CDT that Browns Ferry had experienced a fire and arc-over event at the area of cooling tower switchgear 'C'. "At about 0225 CDT a fault occurred in the cable tray between the 161 kV supply transformer and the 4 kV cooling tower 'C' switchgear resulting in clearing of the 161 kV line and a subsequent fire. The fire was extinguished at 0236 CDT by on-site responders. At 0340 CDT, Limestone County Sheriff department was contacted by site security and informed of the event and asked to increase patrols in the area of the county road adjacent to Browns Ferry. It was known that the event was likely due to operational issues and not sabotage but the final determination had not been made at that time. Limestone County Sheriff was contacted again at 0520 CDT and informed that the problem was operational and that their assistance is not required. "There are no safety related plant equipment reportability issues resulting from this event. The reportability is solely due to notification of an outside agency. "This condition is reportable within 4 hours according to 10 CFR 50.72(b)(2)(xi). Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an onsite fatality or inadvertent release of radioactive contaminated materials." Licensee has notified NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-07-27
44366 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2008-07-25 16:00 | 2008-07-25 16:24 | 2008-07-25 | STATE AGENCY NOTIFIED OF DISCHARGE OF AMMONIA EXCEEDING STATE LIMITS "Reason for Notification: On 7/25/08, chemical laboratory analysis of the NPDES liquid effluent 24-Hour composite sample indicated that the wastewater discharged from the Columbia plant during the previous 24 hour period contained 115.9 lbs of ammonia which exceeds the Daily Maximum Discharge Limit for Ammonia of 100 lbs/day. The average for ammonia discharge this month is approximately 20 lbs/day and is within the permit monthly average of 50 lbs/day. "Liquid discharges from the Columbia Plant are regulated with regard to chemical pollutants through the SC-DHEC/EPA administered NPDES Permit #SC 0001848. WEC is required to notify SC-DHEC within 24 hours of becoming aware of non-compliance with effluent limitations. "Notification is being made based on 10CFR70 Appendix A, Section (c), Concurrent Reports: 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made, shall be reported to the NRC Operations Center concurrent to the news release or other notification.' "Summary of Activity: Following recognition of the problem, Westinghouse has immediately responded to terminate flow of process wastewater. Discharge of process waste will be resumed following verification that discharges will meet permit limits. This event is entered into the plant Corrective Action Process. (CAPS#08-207-0011). "Conclusions: Problem was self identified by Westinghouse personnel. At no time was the health or safety to any employee or member of the public in jeopardy." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-07-25
44365 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-07-25 09:17 | 2008-07-25 14:07 | 2008-07-25 | POSITIVE RANDOM FITNESS FOR DUTY TEST "A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. "The licensee notified the NRC Resident Inspector. "This event is being reported pursuant to 10 CFR 26.719 (b)(2)(ii)." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2008-07-25
44364 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2008-07-21 18:20 | 2008-07-25 10:57 | 2008-07-28 | AGREEMENT STATE REPORT - POTENTIAL OCCUPATIONAL OVEREXPOSURE On July 22, 2008, the State of Maryland was informed by the Teletherapy Operations Manager for Neutron Products, Inc. that one of their teletherapy service engineers performing an Alcyon Co-60 source exchange in Brazil had received a potential overexposure. During the source exchange, the engineer's electronic dosimeter alarmed. Immediate actions were taken to properly secure the source. Preliminary dosimetry readings for the service engineer indicated a potential whole body exposure of approximately 5,211 mrem and extremity reading at the right wrist exceeding 10R (off scale high). The service engineer's film badge was sent for immediate processing to Global Dosimetry with expected results available for evaluation by Thursday, 7/24. The results from Global Dosimetry for the service engineer prior to the incident are as follows: Monthly whole body (DDE, mrem) - 13,465 + 92 (Jan. - May) = 13,557 Left wrist (SDE, mrem) - 73,356 + 236 (Jan. - May) = 73,592 Right wrist (SDE, mrem) - 746 + 488 (Jan. - May) = 1,234 Brazilian regulatory personnel were onsite at the hospital at the time the incident occurred and were briefed within one (1) hour by the service engineer. * * * UPDATE FROM ALAN JACOBSON TO JOHN KNOKE AT 0739 EDT ON 07/28/08 * * * "Per our telephone conversation of today [between the state and the licensee], this is to update our initial verbal and written Twenty-Four Hour Notifications made July 22, 2008 regarding the incident in Sao Paulo, Brazil, and to summarize our employee's written account thereof. "On July 21, 2008 at approximately 6:20 pm EDT, Neutron Products employee #502, informed us via telephone that he may have received an over-exposure while performing a source exchange on an Alcyon II teletherapy unit located in Sao Paulo, Brazil. On July 21, 2008, employee #502 and a radiation worker from Brazil were in the process of transferring the expended cobalt-60 source from the Alcyon II unit into Neutron's transfer cask in accordance with Specification P-9, Appendix XI. After engaging the source holder with the removal tool, #502 transferred the source holder from the Alcyon II unit head into the transfer cask. Once the source holder was in the transfer cask, #502 continued making preparations to complete the removal sequence. "Employee #502 had completed all the steps of the removal sequence and was in the process of removing the removal tool from the transfer cask, when it was determined by audible alarms and before the tool was completely out of the cask, that the cobalt-60 source was still connected to the end of the removal tool. At that point, #502 reinserted the removal tool back into the cask and repeated the steps again to make sure that the Source was disengaged from the removal tool. Once he was sure that the source was no longer attached to the removal tool, the tool was removed from the cask, and all the covers installed. The transfer cask now contains both the expended and new sources. "Immediately after the container was secured, both men read their SRD's and reported their dose as follows: #502: WB-5,211 mrem, Left Wrist-300 mrem, and Right Wrist-off Scale (10R dosimeter); Brazilian Worker: WB-533 mrem, Left Wrist-off scale (10R dosimeter), and, Right Wrist-4,100 mrem. The TLD's were sent via FED-EX to Global Dosimetry Solutions in Irvine, CA, for emergency reading and the results are as follows: #502: Monthly WB DDE-13,465 mrem, Quarterly WB DDE-11,126 mrem, Left Wrist SDE-73,356 mrem, and Right Wrist SDE-746 mrem. Brazilian Worker: Monthly WB DDE-702 mrem, Quarterly WB DDE-1,559 mrem, Left Wrist SDE-3,030 mrem, and Right Wrist SDE-8,542 mrem. "Employee #502 will be returning home sometime this weekend. He will not be involved in any radiation work for the remainder of the year." Notified R1DO (Trapp) and FSME (M. Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2008-07-30
44363 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-07-24 15:02 | 2008-07-24 15:03 | 2008-07-24 | TECH SPEC REQUIRED SHUTDOWN DUE TO LOSS OF ESSENTIAL RAW COOLING WATER PUMP WITH 2 EDG'S OOS "WBN Unit 1 experienced a failure of the B-A ERCW pump on July 21, 2008, at 2:46 p.m. EDT. The plant entered LCD 3.7.8, Condition A, for one ERCW train inoperable and LCD 3.8.1, Condition C, with two required DGs in Train A inoperable concurrently. Required Actions for LCO 3.7.8 and LCD 3.8.1 required restoration of the inoperable ERCW train and one DG to OPERABLE status in 72 hours, respectively. Plant shutdown was initiated in accordance with LCD 3.7.8, Condition B and LCD 3.8.1, Condition G when the above Required Actions were not met. The root cause of the pump failure is unknown at this time. An event team has been set-up to determine cause of pump failure. Currently, the unit is performing a control shutdown, and all systems are functioning as expected." The licensee does not expect the ERCW pump to be returned to service and will downpower at 15% per hour. The licensee expects to be in Mode 3 by 2030 EDT. All required safety systems for safe shutdown are operable. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BEN HUNT TO JOE O'HARA AT 2046 ON 7/24/08 * * * "The TS required shutdown has been terminated on 7/24/08 at 1910 EDT, based on the receipt of an Emergency TS change. The plant exited LCO 3.8.1, Condition C and LCO 3.7.8, Condition A, and entered new LCO 3.7.8, Condition C. The revised TS will allow continued operation for an additional 7 days based, in part, on the implementation of an NRC approved Temporary Alternation. It is expected that the failed ERCW pump will be repaired within the new 10 day allowed outage time as specified in the Emergency TS change for LCO 3.7.8, Condition C (3 days were already used due to the inoperability of the B-A ERCW Pump occurred on 7/21, this leaves approximately 7 days left in the new action time.)" The licensee notified the NRC Resident Inspector. Notified R2DO(Lesser). | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-07-24
44362 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-07-23 17:08 | 2008-07-23 20:20 | 2008-07-23 | OFFSITE NOTIFICATION OF OIL SPILL TO FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION "At 1708 EDT on 7/23/08, the Control Room was notified that a 900ml initial baseline sample from a potential ground water monitoring well contained 120ml of oil. During the sample, it was also noted that the well was partially filled with debris. This well is not part of the site ground water monitoring program. There was no indication that any oil has entered the storm drain system. "Although the quantity of oil recovered does not exceed any EPA regulations, a courtesy notification was made to the Florida Department of Environmental Protection at 1723 EDT on 7/23/08. "This 4-hour NRC notification is being made based on a notification to an off-site government agency." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-07-23
44361 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-07-23 10:35 | 2008-07-23 16:32 | 2008-07-23 | AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE The following information was provided by the State via e-mail: "On July 23, 2008, at approximately 10:35 a.m., [the] RSO for Harrington Geotechnical Engineering, Inc., notified RHB about a nuclear gauge (CPN model MC-3 S/N M35116478, 10 mCi Cs-137, 50 mCi Am:Be-241) that had been stolen at a residence (in Westminster, CA 92683, located near the intersection of Magnolia St. and McFadden Ave.) sometime between 8:00 a.m. and 8:30 a.m. Due to an urgent personal need, the operator left the truck outside the residence, with the gauge locked to the bed of the truck by a cable. The cable was cut by the perpetrator to remove the transport case containing the gauge. The Westminster Police Department was notified and a police report was generated (report number 08-06699). The RSO stated that the residence of the operator was in an area that had some gang activity. The RSO was informed of the requirement for a written report within 30-days. The RSO stated that he would place an ad in the newspaper and to offer a reward for the gauge. RHB will investigate this incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-07-28
44360 | 0 | CALUMET TECHNICAL SERVICES |  |  |  |  | 2008-07-22 09:30 | 2008-07-23 09:38 | 2008-07-23 | SAFETY EQUIPMENT FAILURE While conducting radiography at the Stiglitz Park Tank Farm in Lake County, Indiana, the radiographer noticed that the source failed to retract with the drive cable in his radiography camera. Upon noticing the detached source, the radiographer immediately covered the source with lead blankets and established an area boundary around the source. He then contacted the Radiation Safety Officer (RSO) who dispatched personnel to the site. There were no reported overexposures to radiography personnel as a result of this incident. Licensee radiographers were able to retrieve the source, place it back into the camera, and transport the source and camera back to the licensee's main facility. They inspected the camera, source, drive cable and connector and did not find any damage. They were not able to determine why the source became disconnected. They reconnected the source to the camera, functionally tested it satisfactorily, and placed the camera back into service. The licensee did not have the camera vendor inspect or test the device. The camera is an Amersham model 880, serial number D4044 with a 65 Curie Ir-192 source, serial number 45541B. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-07-23
44359 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2008-07-22 18:45 | 2008-07-22 20:30 | 2008-07-22 | OIL RELEASE TO THE ENVIRONMENT "At 1845 an oil sheen was noticed at the discharge canal of Unit #2. A slight oil sheen has reached the Hudson River. Estimated discharge is less than 1 gallon. The source is run-off from a parking lot and other paved areas due to recent heavy rain. Oil content is lessening in the runoff. "The licensee notified the following organizations: USCG National Response Center (Report #878141), NY Department of Environmental Conservation, and the Westchester County Department of Health. "Cleanup is being coordinated with Miller Environmental as required." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2008-07-22
44358 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2008-07-21 20:58 | 2008-07-22 04:10 | 2008-07-22 | LOSS OF ACCIDENT MITIGATION CAPABILITIES DUE TO TWO EMERGENCY DIESEL GENERATORS OUT OF SERVICE "On 7/20/08 at 1757, the 1B Emergency Diesel generator was voluntarily removed from service for a planned exhaust header replacement. The 1B Emergency Diesel remains out of service and is anticipated to be returned to service on 7/26/08. "On 7/21/08 at 2058, the 1-2A Emergency Diesel generator was declared inoperable due to excessive amounts of water present in the diesel lube oil system. "The combination of these two diesels being out of service results in two emergency diesels, one in each train, being inoperable for Farley Unit One. This represents a Unit One loss of safety function for mitigating the consequences of an accident in the event of a loss of off-site power. "Farley Unit Two is affected only by the 1-2A Emergency Diesel and is maintaining a B-Train Emergency Diesel operable. "The 1-2A Emergency Diesel is suspected of having a lube oil heat exchanger tube leak. Confirmation of the tube leak and repairs are anticipated to take three to four days." The loss of two EDGs places Unit One in an 8-hr plant shutdown action statement which will require the unit to initiate shutdown by 0458 CDT on July 22, 2008 and be in hot standby by 1058 CDT. Unit Two is in a 10-day non-shutdown action statement as a result of the loss of the 1-2A Emergency Diesel Generator. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM HOBSON TO KNOKE AT 1009 ON 07/22/08 * * * "On 7/20/08 at 1757, the 1 B Emergency Diesel Generator was voluntarily removed from service for a planned exhaust header replacement. "On 7/21/08 at 2058, the 1-2A emergency Diesel Generator was declared inoperable per Technical Specification 3.8.1 due to excessive amounts of water present in the diesel lube oil system. "The combination of both diesels out of service required entry into Technical Specification 3.8.1 Condition E. With both an 'A' train and a 'B' train Emergency Diesel Generators inoperable, a loss of safety function exists. A technical specification required shutdown from Mode 1 to Mode 3 was commenced at 0541 CST in accordance with Technical Specification 3.8.1 Condition F. Unit 1 is required to be in Mode 3 prior to 1058 CST. "Unit 2 is affected by the 1-2A Emergency Diesel Generator being removed from service. However, there is no loss of safety function on Unit 2 because the B train Emergency Diesel Generator is operable. Unit 2 remains in Mode 1, 100% power." Licensee will notify the NRC Resident Inspector. Notified R2DO (Blamey) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | PLANT S/D REQD BY TS |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(2)(i) |  |  | 0 | 2008-07-22
44357 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-07-21 09:08 | 2008-07-21 12:32 | 2008-07-21 | UNUSUAL EVENT DECLARED - UNABLE TO VALIDATE A FIRE ALARM WITHIN 15 MINUTES The licensee received a fire alarm (smoke alarm) for the Auxiliary Building Ventilation Room at 0853 PDT. An operator was dispatched to visually inspect the area of the fire alarm. The area was not able to be accessed due to a high delta pressure across the door. Operators were not able to access the area within 15 minutes of receiving the alarm and declared EAL HU 2.1 at 0908 PDT. A maintenance worker in the area of the alarm opened the door from the other side and an operator was able to visually inspect the area. The area was free of smoke and fire and the Unusual Event was exited at 0915 PDT. The licensee performed required notifications to the State of California and the local government. The NRC Resident Inspector was notified. * * * UPDATE AT 1602 EDT ON 7/21/08 FROM NIMIK TO HUFFMAN * * * The licensee plans to issue a press release concerning the Unusual Event. The NRC Resident Inspector will be notified. R4DO (Deese) informed. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2008-07-21
44356 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-07-20 12:20 | 2008-07-20 19:00 | 2008-07-20 | FAILURE OF PROCESS GAS LEAK DETECTION SYSTEM "At 1230 CDST, on 07-20-08 the Plant Shift Superintendent (PSS) was notified that C-315 had received an audible alarm with no visual indications. Moments later an alarm was received in C-331 for the C-315 High Voltage Process Gas Leak Detection System. Operators responded by contacting C-315 to inquire about the alarm. C-315 operators checked the system and found that the READY light for this system was not illuminated. This PGLD System contains detectors that cover the C-315 UF6 condensers, accumulators, and piping heated housing. At the time of this alarm, the areas were operating above atmospheric pressure. TSR 2.3.4.4 requires that all of detector heads in this system be operable during operations above atmospheric pressure. Operators responding to the system tried to test fire the system heads however the system would not respond and then they discovered the READY light to be off. This PGLD System was declared inoperable, TSR LCO 2.3.4.4.A.1 was entered and a continuous smoke watch was put in place within one hour. Engineering has determined that the system would not have been able to perform its intended safety function when this alarm came in. This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-07-20
44355 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-07-18 08:00 | 2008-07-18 19:36 | 2008-07-19 | EMERGENCY OPERATIONS FACILITY INOPERABLE FOR MAINTENANCE WORK "Southern California Edison (SCE) has scheduled maintenance for the electrical system of the San Onofre Emergency Operations Facility (EOF), for Saturday, July 19, 2008. While the maintenance is being performed, the EOF will be inoperable. The EOF outage is expected to begin at 0800 PDT and last approximately 4 hours. "The alternate EOF, located in Irvine, CA, will be available should SCE need to respond to an Emergency Event. "The Emergency Recall System, which is housed in the EOF, will be out of service while the maintenance is performed. Should recall of the Emergency Response Organization (ERO) be necessary during the EOF outage, SCE will utilize alternate methods (contained in existing site procedures) for activating the ERO. "This planned EOF outage is being reported in accordance with 10CFR50.72(b)(3)(xiii). "At the time of this report, Unit 2 and Unit 3 were operating at about 98 per cent and 100 per cent, respectively. "The NRC Resident Inspector has been notified of this report and will be provided a copy." * * * UPDATE PROVIDED BY SUSAN GARDNER TO JASON KOZAL ON 7/19/08 AT 1705 * * * "The Emergency Operations Facility was returned to service on July 19, 2008 at 1240 PDT. "The NRC Resident Inspector will be notified of this occurrence and will be provided with a copy of this report." Notified R4DO (Johnson). | 0 | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-07-18
44354 | -1 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-07-17 11:41 | 2008-07-17 19:53 | 2008-09-10 | DEGRADED CONTROL ROOM VENTILATION ENVELOPE "At 1141 on Thursday, July 17, 2008, Braidwood Station determined that the Control Room Envelope (CRE) boundary had a degraded condition based on data obtained during performance of differential pressure testing performed in accordance with Technical Specification (TS) 5.5.18, 'Control Room Envelope Habitability Program.' Degradation of the CRE boundary was identified that could have prevented the Control Room (VC) Ventilation Filtration System from performing its safety function due to the potential for a greater amount of unfiltered inleakage into the CRE than assumed in the licensing basis analysis for Design Basis Accident consequences. The differential pressure test results identified slightly negative pressures as compared to outside air in some areas of the CRE that do not include spaces that control room occupants inhabit during accident conditions. "In accordance with the requirements of TS 3.7.10, 'VC Filtration System,' Condition B, mitigating actions have been implemented to lessen the effect on CRE occupants from the potential hazards of a radiological or chemical event or a challenge from smoke. Actions are in progress to resolve the CRE degraded condition. "This event is being reported under 10CFR50.72(b)(3)(v)(D) as an 8-hour report as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. A Licensee Event Report will be submitted under 10CFR50.73(a)(2)(v). "The licensee informed the NRC resident." * * * UPDATE AT 1300 EDT ON 09/10/08 FROM RYAN FRUTH TO S. SANDIN * * * The licensee is retracting this report based on the following: "On July 17, 2008, NRC Notification 44354 was conservatively made pursuant to 10 CFR 50.72(b)(3)(v)(D) related to the failure of a control room envelope (CRE) differential pressure test. This was the first time this test methodology had been used at Braidwood Station. Specifically, based on the test results, the unfiltered CRE inleakage could not be confirmed as being bounded by the values assumed within the accident dose analyses and hence the Control Room Ventilation (VC) Filtration System could have been prevented from performing its specified safety function. Subsequent evaluation has determined that the VC Filtration System was capable of performing its specified safety function to maintain CRE habitability, since the identified condition would not have resulted in a greater amount of unfiltered inleakage into the CRE than assumed in the licensing bases analyses. Therefore, this event notification is being retracted. "The causes for the test failure were attributable to an incorrect test methodology and minor CRE boundary imperfections that had existed since plant construction. These CRE minor imperfections were present during performance of the last CRE unfiltered air inleakage test performed in 2004, which produced acceptable results. Both of these causes were corrected and the test reperformed with acceptable results. "Evaluation of this event notification is documented in the corrective action program. "The NRC resident has been notified of this retraction." Notified R3DO (Passehl). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-07-17
44353 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-07-14 | 2008-07-17 12:05 | 2008-07-17 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO DOSE LESS THAN PRESCRIBED DOSE The following report was received from the State of Wisconsin via facsimile: "On 7/14/2008, a patient was simulated and treatment planning performed for High Dose Rate (Ir-192) partial breast irradiation to the right breast using a Contura (SenoRx) balloon. The authorized user prescribed a dose of 3.65 Gy per fraction x 9 fractions for a total dose of 32.85 Gy to the Planning Target Volume. After the planning was done, the length of each of the five catheters was measured by the Nucletron Source Position Simulator. The readings were found to be 1154 each. The treatment file in the High Dose Rate treatment console was modified from its default value of 1500 to 1154 and patient was treated. The patient was treated in the High Dose Rate machine located in Room 'A'. "On 7/15/08, the patient was scheduled to be treated in the High Dose Rate machine located in Room 'B'. Since the sources are different in activity, total time check was performed, at which time, the medical physicists also compared the measured lengths with a second patient under treatment with the Contura balloon in Room 'B'. At this point they noted the difference in the measured lengths between the two cases. The medical physicist checked the Source Position Simulator and noticed that there was an obstruction at the 1154 reading. The review of the actual delivered dose during the first fraction revealed that the source did not enter the patient's body and thus the negative impact was mitigated. A small region of the skin surface received some radiation dose, but the clinical impact is insignificant. The incident was immediately reported to the primary Radiation Oncologist and the Authorized User. The licensee states that no long-term, permanent side effects are anticipated as a result of the medical event. "Due to the licensee's investigation of the Source Position Simulator revealing that a welded junction in the cable of this measuring device was kinked, it was immediately replaced with a new one. The licensee has also developed a new Quality Assurance form which will be exclusively used for Contura balloons and which incorporates the expected length for the five catheters. Department of Health Services (DHS) staff have been dispatched to investigate this incident." Wisconsin Report Number: WI080017 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-07-23
44352 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-06-09 16:31 | 2008-07-17 10:48 | 2008-07-17 | 60 DAY REPORT - INVALID ACTUATION OF MAIN STEAM ISOLATION SYSTEM "This 60-day optional report, as allowed by 10 CFR 50.73 (a)(1), is being made under the reporting requirement in 10 CFR 50.73 (a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Main Steam (SM) System. On June 9, 2008, at 1631 with Unit 1 in Mode 5, an invalid signal was generated on Train B of the SM system during Engineered Safety Features testing. During the performance of returning the Solid State Protection System (SSPS) to 'normal', the SSPSB mode selector switch was placed to operate. A Unit 1 Feedwater and Main Steam isolation occurred. Part of the 'return to normal' sequence is to place the SSPS Input Error Inhibit switch to the inhibit position. The technician failed to insure the inhibit switch 'snapped' into position and trip signals were generated when the Output Test relay switch was placed to Operate. The SM system was returned to standby readiness. This was considered a partial system/train actuation. During this event, the SM system performed as expected. This event was entered into the site specific corrective action program for resolution." The licensee has notified the NRC Resident Inspector, and will be notifying the State, local and other government agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-07-17
44351 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-07-16 15:16 | 2008-07-16 23:15 | 2008-07-16 | POTENTIAL FIRE PROPAGATION BETWEEN ROOMS COULD AFFECT APPENDIX R SAFE SHUTDOWN "A potential exists for a fire in the South Area of the Auxiliary Feedwater (AFW) room to propagate to the Vital Switchgear (VSG) room. A fire in the South Area of the AFW room could cause a short circuit in a cable that traverses the AFW room and the VSG room, causing ignition of the cable. The Point Beach Safe Shutdown Analysis assumes a fire in a single fire area. A fire in South Area of the AFW Room, credits AFW pumps P-38B & 2P-29 for providing AFW to both unit's steam generators. A fire in the VSG Room, credits AFW pumps 1 P-29 & 2P-29 for providing AFW to both unit's steam generators. "A fire in both the South Area of the AFW room and VSG room could potentially cause three of the four AFW pumps to be unavailable, which does not meet the requirements for Appendix R safe shutdown. "The potential for a fire affecting two fire areas is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B). Compensatory measures have been implemented. Licensee investigations are continuing." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-07-16
44350 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-07-16 | 2008-07-16 16:22 | 2008-07-16 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following report was submitted by the State via e-mail: "Licensee's truck was parked at a fast food restaurant, which happens to be part of the work site, while the employee was inside getting a late lunch. The [Troxler 3440A, S/N 26057] gauge was in its transport box and secured to the bed of the pick up with two cables and two locks. At approximately 3 p.m. thieves using a bolt cutter tried to cut the cables. When they couldn't, they cut the locks and took the gauge. The keys were not with the gauge. Hialeah PD is investigating. A witness provided the make of the car and a partial plate number. Licensee will submit a written report and after 48 hours consider offering a reward for the return of the gauge. Florida is investigating." This gauge contains an 8 mCi Cs-137 source and a 40 mCi Am-141/Be source. Florida report number FL-08-104 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-07-21
44349 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-07-15 18:15 | 2008-07-16 15:34 | 2008-07-16 | AGREEMENT STATE REPORT - RADIATION EXPOSURE TO NON-OCCUPATIONAL WORKER Rayonier Performance Fibers is a pulp mill that utilizes a Berthold Model 2653.100-001 density gauge with a 24 millicuries Cesium-137 for measures paper density and thickness on its process line. The company employed a contract welder to perform some structural welding in the vicinity of the gauge. Another company employee noted that the welder was in a radiation restricted area and had him leave the area immediately. The RSO was notified who then informed the State of Georgia. Based on preliminary information, it appears that even though the process had been shutdown, the gauge shutter was still open for reasons unknown. The licensee's initial estimate of the welder's exposure based on his time and location is 36 millirem whole body. The State of Georgia's investigation is in progress. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-07-21
44348 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2008-07-14 02:35 | 2008-07-16 12:09 | 2008-07-16 | AGREEMENT STATE REPORT - CRUSHED MOISTURE DENSITY GAUGE "Approximately 02:35 a.m. on 7-14-08, an employee who coordinates nuclear gauge use with W. G. Yates & Sons Construction Company notified MEMA that a Troxler 4640-B thin lift density gauge had been crushed by an 18-wheeler truck when the truck drove through the cone barrier. The Gauge contents were scattered over a 10 ft X 10 ft area in the middle of highway 49 South, Richland, Mississippi. MEMA then notified [redacted] Director of Radiological Health at approximately 3:03 a.m. "[The director] picked up the gauge parts off Highway 49 South and packed them in the original shipping container with dirt. Surveys were conducted of the accident scene revealing only background readings after the gauge parts were put back into the gauge box. At 4:10 a.m., [the director] reported to MEMA the contents of the crushed gauge and that one lane of traffic was open on Highway 49 South in Richland, Mississippi. Confiscation of the gauge by the Division of Radiological Health was reported to MEMA at 4:38 a.m., when [the director] was leaving the accident site. "[The director] returned with the gauge to Radiological Health at approximately 8:30 a.m., on 7-14-08. Pictures of the crushed gauge were taken by [a Senior Health Physicist of the] Division of Radiological Health. Then the gauge was surveyed and placed in a lead storage cask. Surveys revealed 600 Mr/hr at 6 in from the gauge source rod. "The RSO for W. G. Yates & Sons Construction Company was contacted by [the director] and asked to give a report on how the accident happened. The report issued to the Mississippi State Department of Health / Division of Radiological Health was received 7-15-08. In summary, the RSO said work was being performed on two of the three South bound lanes of Highway 49 South. The center and right hand lanes of Highway 49 South were blocked off with cones. The RSO said one employee on site walked away from his profiler machine which was in the center lane of Highway 49 South to ask another employee about the measurements from the thin lift density gauge, also located in the center lane of Highway 49 South. Standing approximately 5 feet from the gauge, they witnessed an 18 wheeler veer from the left hand lane and travel to the center lane crossing the cone barrier. The driver of the 18-wheeler veered further to the right of the profile machine which was in the center lane of the highway. One employee's truck was parked in the right hand lane while he was taking readings from the profile machine. Upon approaching the employees truck, the 18-wheeler veered back into the center lane from the right hand lane and crushed the thin lift density gauge. Both employees were uninjured. "Upon further review of the accident, the authorized user for the thin lift density gauge was trained and certificates are on file with the Division of Radiological Health. The gauge was also last leak tested on 11/1/07. The RSO said three employees with W. G. Yates & Sons Construction company who were involved in the accident have had there badges sent in for processing. "Accident site surveys revealed the source was still in the gauge. Additional site surveys revealed only background readings. The gauge was confiscated by DRH. "Isotope(s): Cesium-137; "Activity: 8 mCi." This is Mississippi Event Number MS08008. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2008-07-21
44347 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-06-02 06:24 | 2008-07-16 09:49 | 2008-07-16 | INVALID SYSTEM ACTUATION OF DIVISION 1 CONTAINMENT ISOLATION VALVES "On June 2, 2008 at 6:24 a.m. CDT power was lost on the reactor protection system (RPS) bus 'A'. The plant was operating at 100 percent power at the time. The loss of RPS bus 'A' interrupted power to containment isolation actuation circuitry. This caused the Division 1 containment isolation valves in various balance of plant systems to automatically close, as designed. Plant operators implemented recovery procedures to shift RPS 'A' to its alternate power supply, and restore the systems affected by the isolation. The containment isolation valves were confirmed to have actuated as required. Plant capacity was not interrupted by the containment isolation signal. "As their primary power source, each RPS bus is supplied by its own motor generator set. The investigation of this event found that two resistors on a circuit card in the voltage regulator on the 'A' RPS motor-generator set failed. This had the effect of causing the generator voltage to fluctuate significantly, resulting in a automatic trip of the generator output breaker and a loss of power on the bus. "This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an invalid actuation of the Division I containment isolation actuation system." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-07-16
44346 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2008-07-15 08:53 | 2008-07-15 10:33 | 2008-07-15 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO SAFEGUARDS MATERIAL Safeguards system degradation related to the control of safeguards information. Immediate compensatory actions were taken to recover and accounted for the information. Contact the HOO for additional details. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-07-15
44345 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-07-14 08:30 | 2008-07-14 13:57 | 2008-08-05 | ITEM RELIED ON FOR SAFETY (IROFS) DISCOVERED INOPERABLE "NOX (nitrogen dioxide, nitric oxide, etc) detection is IROFS BUND-17 for the LEU [Low Enriched Uranium] portion of the BPF facility. This IROFS is one of the two controls used to prevent chemical occupational exposure to NOX emissions due to the U-natural dissolution operation. The NOX detector alarms prior to exceeding 5 ppm NOX to allow operations to perform monitoring and/or evacuation actions. On July 11, 2008, it was identified that the calibration gas used to functionally test the NOX detector has expired. The calibration expiration date was September 2007. The prior functional test of the NOX detector was performed on January 11, 2008. Due to use of expired calibration gas, it was determined that the NOX detector (IROFS BPF-43) has been in a degraded condition since the last functional test (January 2008). "A 2nd IROFS is credited in the NOX accident sequence but, with degradation of IROFS BUND-17, the performance criteria of 10 CFR 70.61 were not met. "No actual emissions have been identified. "The event occurred due to a degraded management measure, specifically a periodic function test. Improved calibration verifications have recently been implemented; this improved check identified the problem of the expired calibration gas." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1241 EDT ON 8/5/08 FROM E.A. SENTER TO S. SANDIN * * * The licensee is retracting this report based on the following: "On July 14, 2008, NFS made a 24-hour report (NRC Event No. 44345) to the operations center based on 10CFR70, Appendix A, Paragraph (a)(2). 10CFR70, Appendix A, Paragraph (a)(2) requires a 24-hour report for loss or degradation of an item relied on for safety (IROFS) that results in failure to meet the performance requirement of Sec. 70.61. The report was made due to expired calibration gas being used to functionally test the IROFS BUND-17 Nox (nitrogen dioxide, nitric oxide, etc) detector. "After calibrating the detector with in-date calibration gas, it was determined that the NOX detector was actually set to alarm at a much more conservative part per million reading than the normal alarm setting. Therefore there was no degradation of the IROFS BUND-17, but rather an increased level of protection had been applied since the last functional test in January 2008. Based on this information, it is requested that this event report be retracted." Notified R2DO (Hooper), NMSS (Tschiltz) and Fuels OUO Gp via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 0 | 2008-07-14
44344 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-07-11 11:30 | 2008-07-11 15:54 | 2008-08-05 | ITEM RELIED ON FOR SAFETY DISCOVERED INOPERABLE "NOX (nitrogen dioxide, nitric oxide, etc) detection is IROFS [Item Relied On For Safety] BPF-43 for the BPF facility. This IROFS is one of the two controls used to prevent chemical occupational exposure to NOX emissions due to the U-Aluminum Bowl Cleaning operations. The NOX detector alarms prior to exceeding 5 ppm NOX to allow Operations to perform monitoring and/or evacuation actions. On July 11, 2008 it was identified that the calibration gas used to functionally test the NOX detector has expired. The calibration expiration date was September 2007. The prior functional test of the NOX detector was performed on January 24, 2008. Due to use of expired calibration gas, it was determined that the NOX detector (IROFS BPF-43) has been in a degraded condition since the last functional test (January 2008). "The other IROFS credited in the ISA Summary for this accident is BUA-43, (power is automatically removed from caustic pumps securing sodium hydroxide flow to U-Aluminum dissolvers upon low sodium nitrate flow as detected by flow switches). From late May until early July of 2008, these flow switches were not functioning correctly, so written and approved compensatory measures were implemented. However, per NFS procedure, these temporary compensatory measures were not incorporated into the ISA Summary so were not available to help meet the performance criteria of 10 CFR 70.61. Since IROFS BPF-43 was in a degraded condition during this time period, performance criteria were not met." The licensee has ceased operations in the affected building. The functional test performed in January 2008 utilized the out-of-date calibration gas. The functional test previous to the functional test performed in January 2008 was performed in July 2007. The licensee has had no indication or evidence that NOX emissions occurred during the degraded condition period. The licensee is investigating this incident to determine further controls required to prevent reoccurrence. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1241 EDT ON 8/5/08 FROM E.A. SENTER TO S. SANDIN * * * The licensee is retracting this report based on the following: "On July 11, 2008, NFS made a 24-hour report (NRC Event No. 44344) to the operations center based on 10CFR70, Appendix A, Paragraph (a)(2). 10CFR70, Appendix A, Paragraph (a)(2) requires a 24-hour report for loss or degradation of an item relied on for safety (IROFS) that results in failure to meet the performance requirement of Sec. 70.61. The report was made due to expired calibration gas being used to functionally test the IROFS BPF-43 Nox (nitrogen dioxide, nitric oxide, etc) detector. "After calibrating the detector with in-date calibration gas, it was determined that the NOX detector was actually set to alarm at a much more conservative part per million reading than the normal alarm setting. Therefore there was no degradation of the IROFS BPF-43, but rather an increased level of protection had been applied since the last functional test in January 2008. Based on this information, it is requested that this event report be retracted." Notified R2DO (Hooper), NMSS (Tschiltz) and Fuels OUO Gp via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 0 | 2008-07-15
44343 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-05-01 | 2008-07-11 12:08 | 2008-07-11 | AGREEMENT STATE REPORT - LOST TRITIUM SIGNS This report was submitted by Nebraska via e-mail: "The general licensee, which is a large food processing facility, did its annual inventory in May of 2008. Four Tritium exit signs were discovered missing during the inventory. Sign 1 was in a high traffic forklift area. The sign was protruding from the wall at a right angle. The licensee thinks that it was likely knocked off and disposed of improperly in regular trash. Signs 2 and 3 were colocated in the same holder. They were in an area of construction and maintenance. The licensee can not find them. They may have been disposed of improperly in regular trash but the licensee was unable to determine how they were disposed of. Sign 4 was located in a warehouse overhead area and was likely knocked down via forklift traffic. It was improperly disposed of in regular trash. This general licensee will communicate to all hourly, salaried and outside contractors the importance of maintaining control of the exit signs and notifying appropriate people in the event they become dislodged, or need to be removed or relocated. The licensee will increase inspections on the signs in their current locations in order to verify that signs are still there. The general licensee will begin systematically changing out a set number of the signs each year with nonradioactive materials until all are removed from their facility." Nebraska Event Date: 1/2/2008 Nebraska Discovery Date: 5/1/2008 Nebraska Report Date: 6/13/2008 Nebraska Report Number: NE080005 Activity per sign: 17.51 Ci Manufacturer: SRB Technologies Inc. Device Name: Radioluminescent Sign Model BXU20SW S/N: 217815 Model BXU20SW S/N: 217885 Model BXU20SW S/N: 217886 Model B100U20S S/N: 220072 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-07-16
44342 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-07-10 15:38 | 2008-07-10 16:18 | 2008-07-10 | LOSS OF EMERGENCY ASSESSMENT CAPABILITIES DUE TO PLANT COMPUTER FAILURE "At 0738 hours on 07/10/08, reactor operators noticed that information on displays of the Plant Integrated Computer System were not periodically updating. Investigation by computer maintenance personnel was initiated. Reactor power was reduced 1 % to ensure compliance with license limits. As of 1538 hours, reliable operation of the computer was not restored. "This computer system also performs the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) functions. Redundant, normal control room indications are still available to the operators. "Since the Unit 1 SPDS and ERDS computer system were not reliable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and therefore reportable under 10CFR50.72(b)(3)(xiii)." Prior to this event, plant personnel were performing plant computer modifications. Compensatory measures are in place to provide emergency assessment data should an event occurs that requires it. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JIM HUFFORD TO JOHN KNOKE AT2052 EDT ON 07/10/08 * * * "This is a follow-up courtesy notification to EN# 44342. As of 2017 on 07/10/08, Unit 1 ERDS and PICSY were fully restored to normal operation. Unit 1 reactor power was returned to full power of 94.4% as of 2042 on 7/10/08." The licensee has notified the NRC Resident Inspector. Notified R1DO (Art Burritt) | 93 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-07-10
44341 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-11-07 | 2008-07-10 15:44 | 2008-07-10 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE Received report via email: "On November 8, 2007, the licensee left a voice-mail message stating a moisture density gauge (Troxler Model 3430, S/N 29865), with a nominal 8 mCi of Cs-137 and 40 mCi of Am-241, had been run over the night before at a construction site. The cesium source was originally reported to be locked in its shielded position, although it was later discovered that the source was shielded, but not lockable. The electronics were severely damaged. While the gauge was being used at the construction site, the user stepped away, and the gauge was run over by a piece of heavy machinery." California Event # 110807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-07-15
44340 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2008-07-09 | 2008-07-09 17:03 | 2008-10-02 | NORTH DAKOTA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE FROM RADIOGRAPHY CAMERA Midwest Industrial X-ray, Inc. was performing radiography at an ethanol plant in Casselton County, ND. After taking a shot, the radiographer was retracting the source when it became detached. The radiographer covered the source with a lead blanket and contacted the company Radiation Safety Officer. The camera contained a 24.5 Ci Ir-192 source. The licensee transported the source back to their facility. The licensee performed calculations that indicated the radiographer received approximately 4 Rem exposure while securing the source. No calculations were reported concerning the assistant radiographer. The calculations performed by the State of North Dakota indicate that the radiographer received greater than 5 Rem. Both individual's film badges were sent to Landauer laboratories for processing. The State of North Dakota will be investigating this incident. * * * UPDATE FROM DAN HARMAN VIA EMAIL TO J. KNOKE AT 1725 EDT ON 07/10/08 * * * "The doses for the lead radiographer are as follows: The badge reading for this monitoring period (June 20 - Jul 8) 575 mR. The yearly total deep dose is 827 mR." Notified FSME (Lewis) and R4DO (Hay) * * * UPDATE ON 7/14/2008 AT 1900 FROM DANIEL HARMAN TO MARK ABRAMOVITZ * * * This agreement state report update was received via e-mail: "Initial Assumption: the source was full exposed in the source tube between the camera and the collimator; the exposure time estimate was 2 minutes; estimated average distance to source was 0.3 meters; gamma constant = 0.59; source strength = 24.5 Ci; and estimated exposure was 5.3 mR. "Investigation Results - Hardware: The camera was a QSA 660B. Maintenance had been performed on this camera two days prior to this event. The source became detached from the wire and lodged inside the camera at or near the connection between the camera and the guide tube. The survey meters used were NDS-2000. Both had recently been calibrated. The one that failed had been sent in for repair in November 2007. The RA-500 worn by [the assistant radiographer] had been sent in twice for repair. We will follow up with asking the company to review the maintenance records for these two devices to determine if they should be replaced ahead of schedule. "Investigation Results - Personnel and Dose update: the primary person exposed was [the assistant radiographer]. By Thursday afternoon his annual badge exposure data had been compiled, including the expose for this event. This data is as follows: deep total - 825 mR, lens - 839 mR and Shallow - 835 mR. The badge for the period June 20 - July 19 was read by Landauer on July 11, 2008, and indicated 575 mR. Dosimeter data for the badge period showed a dose of 88 mR. The badge reading - the badge period dosimeter data shows an exposure of 487 mR for this event. "There were four other personnel involved in the actual event and source retrieval. They are (job lead radiographer, dose: 40 mR); (radiographer, dose: 40 mR), (intern, dose: 32 mR) and (RSO, dose: 55 mR). These data were taken from the pocket dosimeters. "Investigation Results - Source Recovery: There are some inconsistencies between what was stated to have happened and what the investigators believe could have happened. Most relate to positions with respect to the camera/source. We expect to have these resolved by Friday, July 18, 2008." Notified FSME (Lewis) and R4DO (Johnson). * * * UPDATE @ 1750 EDT ON 10/2/08 FROM DAN HARMAN TO HOWIE CROUCH VIA EMAIL * * * "Investigation Results - Hardware: The QSA Model 660B camera and control cable was returned to QSA for evaluation. QSA's evaluation determined the problem was a 'misconnect' not a 'disconnect' of the source assembly from the drive cable. The 'misconnect' was due to wear on the plug assembly, the male connector and the apparent age of the drive cable. "The NDS 2000 survey meter used by [the assistant radiographer] failed to respond due to a loose battery connection. "The Alarm Rate Meter worn by [the assistant radiographer] failed to alarm. This meter had been sent to NDS to have the audio transducer replaced in December and was calibrated at that time. After the incident, the meter was tested in Midwest's lab and the meter did not chirp until 750 mR/hr and was continuous at 1000 mR/hr. According to NDS, this is a 'Low Battery' indication. The rate meter [the assistant radiographer] used did not have a low battery indicator light. "Investigation Results - Conclusions: 1) The alarm rate meter failed due to a low battery condition. 2) The survey meter failed due to a battery disconnect. 3) [The assistant radiographer] read his survey meter while on the platform, next to the camera, saw it read '0', but did not realize the significance of the reading and get off the platform and back on the ground. "The survey meter was repaired and the battery was replaced in the alarm rate meter. Both devices were returned to service. "Investigation Results - Department Actions: The North Dakota Department of Health considers this investigation closed. No penalties will be assessed against Midwest Industrial X-Ray, Inc." Notified R4DO (Bywater) and FSME EO (Bradford). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2008-07-14
44339 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-07-07 14:22 | 2008-07-07 16:54 | 2008-09-10 | FAILURE OF THE ALERT NOTIFICATION SYSTEM Alert Notification sirens (60 of 67) failed to operate properly and therefore required licensee to report this per 10 CFR 50.72(b)(3)(xiii). All Emergency Planning Zone counties have been notified and placed on backup route alerting, which means notification will be performed by local authorities. Investigation of this matter is ongoing. Licensee has notified NRC Resident Inspector. * * * UPDATE FROM MICHAEL RICHARDSON TO JOHN KNOKE AT 1435 EDT ON 07/08/08 * * * A bad radio in the test shop created interference with the Alert Notification sirens, thus preventing them from operating properly. At 1425 EDT all Emergency Planning Zone counties were notified and the backup route alerting was cancelled. The sirens were tested satisfactorily multiple times. Licensee has notified NRC Resident Inspector. Notified R2DO (Guthrie) * * *RETRACTION PROVIDED AT 1744 EDT ON 09/10/08 FROM ROGER DEHART TO JEFF ROTTON * * * Telecom investigation revealed that all 67 ANS sirens were in fact available and ANS siren failure did not occur. The polling feature of the ANS sirens feedback signal experienced radio interference from a standby radio. This interference in the feedback system of the radio/siren system did not interfere with the activation of the sirens. The ANS sirens were fully functional and available during this time, therefore notification 44339 is being retracted. The licensee notified the NRC Resident Inspector. Notified R2DO (Payne) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-07-07
44338 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-06-27 | 2008-07-07 12:33 | 2008-07-07 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR The state submitted this report via fax: "On June 27, 2008 a representative of Georgia Pacific called to report the loss of an NRD static master ionizing unit Model 2u500 containing 500uCi of Po-210. A written report was received on July 7, 2008. These units have no serial number associated with them. They are used to control static on analytical balances. The balance with the missing static bar was put in a storage area for the lab. The probable disposition of the static bar is that it was either returned to the manufacturer or accidentally disposed of in the facility trash, which goes to the Winnebago County landfill. No exposure to individuals is probable. The general licensee conducted on extensive search of their facility, and instituted new procedures to prevent reoccurrence." Wisconsin event: WI080007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-07-10
44337 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-07-04 08:39 | 2008-07-04 10:04 | 2008-07-04 | AUTOMATIC REACTOR SCRAM ON TURBINE TRIP "A Turbine Trip greater than 30% power caused a Reactor Trip (Scram), both Recirculation Pumps tripped. A low level [Reactor Vessel Water Level] of approximately 2 inches caused a Group 2 containment valve isolation signal, all valves closed as required. "The cause of the Turbine Trip is under investigation" All control rods fully inserted with no ECCS actuations. Unit 1 is currently stable in mode 3 (Hot Shutdown) with decay heat being removed via the bypass. Following the scram, one SRV lifted and reseated. At the time of the transient, an EHC pump autostart was in progress, however, there is no indication that this was the cause of the turbine trip. Unit 1 is in a normal shutdown electrical lineup. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-07-04
44336 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-07-03 19:45 | 2008-07-03 21:42 | 2008-07-04 | SODIUM HYPOCHLORITE LEAK "At 1945 Point Beach declared a UE based on HU 3.1, 'Report or detection of toxic or flammable gases that has or could enter the site area boundary in amounts that can affect NORMAL PLANT OPERATIONS.' "This Emergency Action Level (EAL) was entered based on a confirmed Sodium Hypochlorite tank leak to the tanks diked area. The leak is located below the current tank level and will continue to drain to the dike until equilibrium level is reached. The dike is designed to contain the entire tank contents. There are no signs of any leakage outside of the dike. The vapors in the immediate area are not significant at this time and extra ventilation has been provided by opening an overhead roll up door in the area. The NRC Senior Resident Inspector has been notified." The sodium hypochlorite is used in the screen house to chlorinate the service water and circulating water systems to eliminate Zebra Mussels. The concrete diked area is designed to contain the entire contents of the tank. * * * UPDATE AT 0831EDT ON 7/4/08 FROM KILE HESS TO S. SANDIN * * * "At 0646 [CDT] on 7/4/08 Point Beach terminated the UE that was declared at 1945 CDT on 7/3/08, based on HU 3.1. The leaking Sodium Hypochlorite tank and leak control dike have been drained and the over flow leak control area cleaned. The hazard no longer exists and the area has been released to normal access." The licensee informed State and local agencies and the NRC Resident Inspector. Notified R3DO (Kozak), EO (Brown), IRD (Gott), FEMA (Canupp) and DEHS (Inzer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-07-03
44335 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-07-02 12:04 | 2008-07-03 14:11 | 2008-07-03 | AGREEMENT STATE REPORT - LESS THAN 10% OF PRESCRIBED DOSE DELIVERED "A medical event occurred at 12:04 pm on July 2, 2008. The licensee is Baylor University Medical Center, License Number L01290. "The unsealed source is Y-90 Therasphere microspheres for treatment of liver cancer. The prescribed dose is 100 Gray, and the prescribed dose range is from 95 Gray to 105 Gray. "The activity of the Y-90 Therasphere microspheres was verified at 9:13 am - with 13.4 mCi in the vial - using the dose calibrator as per the manufacturer instructions. However when the dose was delivered the 3 way stop-cock was set erroneously and almost the entire dose was collected in the vent vial. Attempts to recover and deliver the misdirected dose was very limited. Post-administration, the residual activity in the original dose vial, the vent vial, and contaminated effects (catheter line, tubing, needles, towels, gauze pads, etc) totaled 12.046 mCi normalized to the 9:13 am verification time. Therefore, the estimated administered activity was approximately 1.3 mCi, administered on 2-July-2008 at 12:04 pm. This translates to approximately 8.7 Gray delivered to the treatment site (Liver Tumor). "Essentially only 8.7% of the prescribed dose was delivered. The licensee is continuing the investigation." Texas event report I-8522 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-07-09
44334 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2008-07-03 05:40 | 2008-07-03 09:06 | 2008-07-03 | LOSS OF COMMERCIAL TELEPHONE AND DEDICATED EP LANDLINES "Reportable Event SAF 1.10 "Major loss of offsite communications capability was experienced at 0540 on 7/3/08. Conventional phones and the EP [Emergency Preparedness] notification lines were lost. Cell phones were available for offsite communications. Offsite communications capability via landlines was restored at 0550 on 7/3/08 with the exception of EP lines, however the ability to contact State and Local authorities using landlines was verified at 0621 on 7/3/08. At 0714 on 7/3/08 the auto ring down EP lines were restored and tested. Source of the problem appears to be failure of Verizon equipment offsite to automatically transfer to alternate when one path was interrupted by a car pole accident." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-07-03
44333 | 0 | HELEN NEWBERRY JOY HOSPITAL |  |  |  |  | 2008-07-02 15:00 | 2008-07-02 16:40 | 2008-07-03 | MOLYBDENUM-99 PACKAGE WITH EXTERNAL CONTAMINATION A nuclear medicine technologist from Helen Newberry Joy Hospital reported receiving a package containing a Molybdenum-99 generator (148 GBq) that had an external radiation of 30 mR/hr and 23,985 dpm (with a background of 11695 dpm). The external contamination was removable using a wipe test. The Molybdenum generator will not be used until next Tuesday and will be stored in a room requiring entry through three locked doors. The Nuclear Technologist will be informing the package carrier of the contamination. He was uncertain where the packaged originated or who the licensed shipper of the package was at the time of the report but would attempt to determine the information and contact the responsible party. * * * UPDATE BY HUFFMAN AT 0930 EDT ON 7/3/08 * * * Thi event was updated to make some minor editorial corrections and clarifications. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2008-07-02
44332 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-06-24 | 2008-07-02 15:00 | 2008-07-02 | WASHINGTON AGREEMENT STATE REPORT - LEAKING CS-137 SEALED SOURCE The following information was provided via email from the State of Washington: "On June 26th, WSU reported that a Cesium-137 sealed source used to test operation of radiation detection instrumentation was found, by WSU staff, to be leaking. The source had recently been used at a WSU research facility. The staff noticed that two of the detectors were indicating higher than expected radiation readings after the source had been returned to storage. Subsequently, WSU staff found the radiation detection instrumentation they had been testing had become contaminated. The source appears to have been abraded during use. "The source, an Isotope Products Lab, model not yet known, Serial Number 687-87-7 and its wooden storage box were taken out of service when the leak was discovered. The source and box are scheduled for disposal as radioactive waste. WSU staff are looking into the specific cause of the abrasion. WSU will then determine if additional corrective actions will be made to keep this from reoccurring. "The licensee reported that surveys were performed in all areas where the source had been used and stored. Three WSU staff were found to have between 200 to 300 counts per minute of contamination on their fingers. WSU staff also found contamination levels of up to 300 counts per minute on a hand-rail and other associated equipment in the facility. Decontamination of the staff, areas and equipment was successfully performed. "Notification Reporting Criteria: WAC 246-221-265, leaking source. "Isotope and Activity involved: Cs-137 check source, 0.37 MBq (10 microcuries) as of February 1, 2000. "Finger contamination was noted, but no overexposures should be realized. "Washington State Report WA-08-046." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-07-07
44331 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-05-31 | 2008-07-01 16:10 | 2008-07-01 | AGREEMENT STATE - POSSIBLE OVEREXPOSURE "Emory University Health Physics Department received notification of a film badge reading with a Beta Dose Reading of 49919mR. This report is only preliminary at this point." Period of exposure: 5/1/2008 to 5/31/2008 Deep Dose: 240 mR Lens Dose: 240 mR Beta Dose: 49919 mR "The assigned shallow dose was changed to 50,160 mrem due to the beta reading of 49,919 mrem. The other doses, including the ring badge reading, are not out of line with what she and her coworkers in PET-CT receive regularly. "[The employee] typically only works with [F-18]FDG [fleurodeoxyglucose]. These readings are consistent with a contaminated badge. I will confer with Landauer as to whether contamination with FDG might result in a reading like this, as I suspect." The employee is currently vacationing out of the country and will return July 10, 2008. The investigation will be completed at that time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-07-04
44330 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-06-23 | 2008-07-01 15:50 | 2008-07-01 | AGREEMENT STATE - LEAKING STATIC ELIMINATOR SOURCES The state submitted this report via e-mail. "Seagate leases static discharging (elimination) devices from a licensed manufacturer, NRD LLC. These static dischargers are Po-210 based alpha emitters. Seagate employees noticed oxidation/discoloration on these static discharges within 2-3 months after installation in their clean rooms. They were concerned about possible flaking of any particulates onto their micro sensitive products and cost of swapping the devices more frequently than every 12 months (lease period). Seagate removed these units from the clean rooms and wipe tested them and sent them for processing to Sterling & Associates. On 6/23/08, the CIH from Sterling & Associates informed Seagate that 4 of the 5 fans exhibiting discoloration, exceeded the limit (0.005 microcuries) 'leaking' with sample results ranging from 0.009-0.01 microcuries. These units included Model # P-2063 with S/Ns A2FD498 (0.02 microcuries), A2FH895 (0.01 microcuries), A2FD505 (0.02 microcuries) & A2FH915 (.009 microcuries). In addition, the remaining 12 fans sampled collectively showed results of 0.3 microcuries. All these 12 units were same Model # P-2063. After the findings, Seagate wipe tested 5 more units (1 brand new, 1 clean looking, & 3 discolored) and the nearby work areas of leaking sources, and the results were non-detect. Seagate notified NRD and all the units that were tested (5+12) were shipped to NRD for further verification. NRD believed that the wipe sampling of the unit, if not done properly might affect the ultra-thin gold encapsulation layer and thereby pick up some imbedded Po-210. "07/01/08 - Per NRD RSO, they still have not received the units from Seagate. He also stated that these units contain a very thin layer of plating and if wipes are not done properly, wipes will pick up imbedded Po-210 indicating contamination. NRD will be wipe testing all the units as soon as they are received and will be calling RHB to notify their findings." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-07-04
44329 | 0 | KAKIVIK ASSET MANAGEMENT, LLC |  |  |  |  | 2008-06-23 20:00 | 2008-06-30 17:23 | 2008-06-30 | PREMATURE LOCKING OF INC IR-100 EXPOSURE DEVICE "On June 23rd at approximately 8 p.m., at a temporary job site [located at a refinery in Sinclair, Wyoming] a Kakivik Asset Management radiography crew experienced the premature tripping of the automatic locking device on a INC IR-100 exposure device. "During retraction of the source it was noted that the locking device had returned to the trapped position. When the crank handles were moved back and forth to insure that it had, it was noted that the source traveled back out of the exposure device. The radiographer immediately took control of the cranks and the assistant moved back to the unrestricted area. The source was returned to the collimator and the lock reset to capture the source. Upon retraction the event occurred again. This happened three times. "The radiographer with help from other crew members established a secure unrestricted area. The Night Supervisor, the Lead Radiographer and RSO were notified. Prior to their arrival the radiographer on-site turned the key and this effectively left the source in the camera but not in the safe and secure position. "The radiography was being performed at a fabrication shop during a turnaround and the RSO made the decision to have the exposure device placed in the lead lined transportation box and moved to a more secure location away from the General Public. "The vehicle was surveyed and the radiation levels for the driver were < 1 mR/Hr. The vehicle was locked and placed under constant surveillance until INC [manufacturer] could be contacted. RSO contacted INC at 7 a.m. the following morning and explained the situation. Their RSO indicated that the Lead Radiographer under his guidance could reset the lock and secure the source in the safe and secure position. This was accomplished successfully. "Kakivik's Material License (#50-27667-01) does allow for the retrieval of sources. "At no time was the General Public in any danger of coming into the restricted area. "The lead radiographer, radiographer and assistant radiographer received 80, 65 and 55 Mr on the 23rd of June respectively and 80, 25 and 5 Mr on the 24th. [Doses for the lead radiographer on the 23 and 24th June were accumulated during event response. Doses for the radiographer and the assistant radiographer were a mix of normal radiography and event response on 23 June, and doses on 24 June were due to event response.] "The camera has been removed from service and returned to INC for evaluation. The camera received annual maintenance at the INC facilities November 5, 2007." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-06-30
44328 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-06-09 | 2008-06-30 14:14 | 2008-06-30 | WASHINGTON AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT The following information was received from the State of Washington via email: "On 9 June 2008 a patient presented for a prescribed bone scan (normally, Tc-99m, 30mCi, MDP), but instead received 23mCi of Tc-99m Sestamibi (heart scan). "The dose was administered. No useful imaging or diagnostic information could be obtained from this procedure. The bone scan will be rescheduled. The licensee will submit a written report, containing cause and proposed corrective actions within 15 days. The licensee's written report dated 23 June 2008 indicates the cause to be human error by the nuclear medicine technologist. The licensee believes current procedures in place are adequate, providing staff adheres to those procedures. The technologist in question will now 'take a time out' prior to each injection to review the dose to be injected, the dose ordered, and to fully and thoroughly check the markings in place on syringes and vials to prevent such an occurrence. No media attention thus far. "According to the manufacturer's product insert, the patient in this case could be expected to receive a maximum of: 4.14R to the Upper Large Intestinal Wall (the most for any single organ), and a whole body dose of 383 mR. No physical consequences are anticipated." Licensee notified patient and referring physician. * * * UPDATE ON 06/30/2008 AT 1644 EST FROM FSME (ZELAC) TO ROTTON * * * The NRC has reviewed this event and determined it is not a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-07-06
44327 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-06-28 00:29 | 2008-06-28 16:59 | 2008-06-28 | POSITIVE FOR CAUSE FITNESS FOR DUTY TEST A non-licensed employee had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's access to the plant has been placed on hold. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2008-06-28
44326 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2008-06-28 11:46 | 2008-06-28 12:54 | 2008-06-28 | MANUAL REACTOR TRIP DUE TO LOSS OF BOTH FEEDWATER PUMPS At 1146, the reactor was manually tripped due to a feedwater transient that was caused by a loss of both feedwater pumps. The exact cause of the loss of both feedwater pumps is still being investigated. Prior to the reactor trip, the licensee was performing main turbine stop valve testing and during that testing received an isolation of extraction steam. On the manual reactor trip, all control rods fully inserted. No RCS PORVs or reactor safety valves lifted. The steam generator atmospheric dump valves did lift and reseat. Decay heat is being removed to the condenser via the turbine dump valves. Auxiliary Feedwater (AFW) initiated and fed the steam generators after the loss of both main feedwater (MFW) pumps. MFW was restored and is controlling steam generator levels. AFW has been secured. The electric plant is in a normal shutdown lineup and the EDGs are available. There was no effect on Unit 3. The licensee has notified the NRC Resident Inspector, Connecticut Department of Environmental Protection, and all local emergency response organizations. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-06-28
44325 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-06-27 21:12 | 2008-06-28 10:10 | 2008-06-28 | CONCURRENT REPORT INVOLVING DERAILMENT OF TRAIN CARRYING WASTE FROM BWXT The licensee was notified at 2112 EDT on 6/27/08 about a train derailment in Atchison, Kansas that was carrying some low level waste from BWXT. Among the derailed cars were 3 cars containing dried sludge from the final effluent pond classified as LSA-1. There was no release or damage involving the waste material. Each of the 3 rail cars contained approximately 3000 cubic feet (9000 cubic feet total) with a total rad content of approximately 60 millicuries Uranium per car (180 millicuries total). The cars never tipped over and have been placed back on tracks. Pending satisfactory results of a safety inspection of the cars, the waste will continue on to its final destination at the Energy Solutions facility in Clive, Utah. BWXT does not plan to issue a press release at this time but notified the NRC based on the potential for public interest. Several local articles about the derailment have been posted on the internet but no direct inquiries from the press have been received by BWXT at this time. The licensee will also notify NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-07-01
44324 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-06-27 15:00 | 2008-06-27 18:46 | 2008-06-27 | PROCEDURE CHANGE INITIATED TO SUPPORT TSC HABITABILITY DOSE CALCULATION "At 1500 on Friday, June 27, 2008, upon review of a calculation performed to demonstrate the TSC habitability requirements; a determination was made that a procedure change was required to support the assumptions in the calculation. The identified procedure change was effective at 1800 on June 27, 2008. Based on implementation of the procedure change, the TSC is now considered functional, but degraded. "This issue has been entered into the Corrective Action Program. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-27
44323 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-06-27 14:30 | 2008-06-27 16:53 | 2008-06-30 | GROUP PAGE VIA INTERACTIVE NOTIFICATION SYSTEM IS NOT OPERATIONAL "On June 27, 2008 at 1430 CDT, Fort Calhoun Station (FCS) performed testing of the group paging system via the Interactive Notification System (INS) . The group page did not perform as designed. Further investigation and testing of the group page manually resulted in the same issue. It has been determined that the group page function is not operational. "FCS has implemented backup manual callout process for the emergency response organization. Therefore emergency facility activation may take longer than normal. Troubleshooting efforts are ongoing." Licensee has notified NRC Resident Inspector. * * * UPDATE FROM GUINN TO CROUCH @ 1023 EDT ON 6/30/08 * * * "Troubleshooting revealed a hard drive failure for the paging system. On June 27, 2008, the paging system was tested satisfactorily at 2145. System is fully functional. " The licensee has notified the NRC Resident Inspector. Notified R4DO (Bywater). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-27
44322 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2008-06-27 | 2008-06-27 16:51 | 2008-06-27 | PART 21 NOTIFICATION - PERFORMANCE AFFECTED ON 3" CL150 FISHER V150 VALVE ASSEMBLIES "Purpose: The purpose of this Fisher Information Notice (FIN) is to alert FPL that as of 20 June, 2008, Fisher Controls International LLC became aware of the possibility of a situation which may affect the performance of the applicable equipment. "Equipment Affected by This Information Notice: Items provided to FPL - Turkey Point per Fisher Order Number 010-A001017058,Item 0001, (FPL Order 00108848, Rev. 3). This equipment included 3" CL150 Fisher V150 valve assemblies (quantity 2). The equipment is identified by Fisher Serial Numbers 18497294 and 18497295 (FPL Tag Number 04224971). "Applicability: This notice applies only to the subject equipment supplied by Fisher Controls International LLC, identified above, that was provided to FPL-Turkey Point. Fisher Controls has determined that the subject items did not meet the material requirements specified by the FPL Order 00108848, Rev. 3. Specifically the discrepancies are: * TFE packing was provided instead of graphite packing. * TCM seal rings were provided instead of HD metal seal rings. The difference in these parts will also require that a different seal protector ring be provided." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2008-06-27
44321 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-06-23 | 2008-06-27 11:33 | 2008-06-27 | POTENTIAL UNDERDOSE TO PATIENT UNDERGOING WHOLE BODY RADIATION The following report was received from the state via e-mail: "On June 25, 2008 at approximately 3 pm, RHB received preliminary notification of a medical event, which occurred June 23, 2008, involving a 50% under-dose to a patient undergoing whole-body irradiation with a Co-60 teletherapy unit. The event was discovered at approximately 2 pm on June 25, 2008. RHB held the initial report to NRC until additional details could be provided by the licensee, who was still reviewing the situation with the radiation oncology department. The prescription was for total body irradiation at 17.12 minutes AP (anterior posterior), then 17.13 minutes AP, then 17.12 minutes PA (posterior anterior), then 17.13 minutes PA, for a total of 34.25 minutes AP and 34.25 minutes PA, and a total of 300 cGy. The therapist only treated 17.13 minutes AP and 17.13 minutes PA for a total dose of 150 cGy. The patient was seen by the attending physician on 6/25/08, with no known medical effects observed. There is currently no plan to re-treat the patient per the attending physician. The licensee is following up with a written report. "5010 Number - 062508" The attending physician and patient have been notified. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-07-03
44320 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2008-05-09 21:32 | 2008-06-27 10:34 | 2008-06-27 | INVALID AUXILIARY FEEDWATER SYSTEM ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1). "On May 9, 2008, while in a refueling outage, an invalid actuation of the 'A' Auxiliary Feedwater train occurred while performing the Turbine Trip and Auxiliary Governor Solenoids Operability Check. "The cause of the event was a failure of the 'A' Motor Driven Auxiliary Feedwater Pump (MDAFWP) bypass control relay, 63XT3-TDA. The relay failed to operate as designed under the system conditions and configuration specified by the procedure, resulting in an actuation signal. No actual plant condition existed which required an Auxiliary Feedwater actuation. "The event resulted in the complete actuation of the 'A' Motor Driven Auxiliary Feedwater train. All equipment functioned as designed for the existing plant configuration. Relay 63XT3-TDA was replaced and retested per the appropriate R. E. Ginna work control processes." The licensee notified the NRC Resident Inspection. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-06-27
44319 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-06-26 11:33 | 2008-06-26 21:34 | 2008-06-26 | 10 CFR 26.719 FITNESS-FOR-DUTY - SITE ACCESS SUSPENDED A random FFD drug and alcohol test on a licensee supervisor indicated the presence of alcohol, although the blood alcohol content was below the limit of a positive test. As a prudent measure the Medical Review Officer recommended that the individual be further evaluated. The individual's site access to the plant has been suspended pending completion of that evaluation. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2008-06-26
44318 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-06-26 17:32 | 2008-06-26 18:10 | 2008-06-26 | REACTOR TRIP DUE TO LOSS OF 1B REACTOR COOLANT PUMP "Loss of 1B Reactor Coolant Pump caused Reactor Trip from 100%. 50G (Overcurrent relays) were picked up on the Safety Breaker and the 6900V supply breaker. Automatic actuation of the motor driven [and turbine driven] Auxiliary Feed Pumps occurred as expected." All control rods fully inserted on the reactor trip. The steam generators water level is being maintained by the AFW system. Decay heat is being removed to the main condenser via the turbine dump valves. RCS PORV lifted and reseated. The electrical plant is in a normal shutdown lineup and the EDGs are available. There is no affect on Unit 2 due to this event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-06-26
44317 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2008-06-24 14:00 | 2008-06-24 16:04 | 2008-06-24 | OFFSITE NOTIFICATION TO OSHA "At 1400 on June 24, 2008, Oconee Environmental Health and Safety personnel determined that an OSHA notification was required due to the death (off-site) of an Oconee employee while traveling on company business. OSHA was subsequently notified at 1430 on June 24, 2008. This notification is being made in accordance with Duke administrative procedures due to notification of a federal agency." The licensee notified the NRC Resident Inspector. The death was due to a medical condition. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-06-24
44316 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2008-06-24 14:10 | 2008-06-24 15:52 | 2008-06-24 | 1-HOUR SAFEGUARDS REPORT INVOLVING DEGRADATION IN A SAFEGUARDS SYSTEM The licensee identified a significant degradation in a safeguards system. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-06-24
44315 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 1993-03-05 | 2008-06-24 13:12 | 2008-06-24 | AGREEMENT STATE REPORT INVOLVING DISCOVERY OF A MISSING SOURCE AT A SCRAP YARD The following information was received from the State of California via email: "At approximately 1400 hours on Friday, June 20th, Adams Steel reported that a truck from Ecology Auto Parts had alarmed their gate radiation monitors. The truck read 2 millirem per hour at 5 feet away, and about 30 microrem per hour at 20 feet away. The South RM ICE office dispatched an inspector to identify the isotope and assist in isolating the source. The inspector identified the isotope as Cs-137 (nominally 8 mCi), in one of the shrink-wrapped pallets of recyclable metals. Upon removing the shrink wrap, the source rod, index rod, and handle of a moisture-density gauge was identified. The inspector placed the source end of the device in a lead pig, secured the pig in another container, and transferred the device to the radiation control program's southern radioactive materials storage area. Wipes of the other materials on the pallet showed no contamination, and a leak test of the source showed no leakage. "The device is part of a Troxler 3430 moisture-density gauge. The americium source was not found. The serial number is 20007. The device originally belonged to United Testing and Inspection, who had reported it stolen March 5, 1993. At that time, the licensee offered a reward for the device, filed a police report, investigated the incident, and took corrective actions (review of all security procedures with employees, upgraded locks on storage area, and limited direct access to the storage area)." CA 5010 Number (Date Notified) - 062008. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-06-27
44314 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2008-06-23 14:20 | 2008-06-23 15:07 | 2008-06-23 | OFFSITE NOTIFICATION DUE TO MINOR OIL SPILL "Oil spill detected in outfall structure of joint operating units IP2 and IP3. Oil pool contained by partial boom in place at outfall structure. Slight rainbow sheen detected after outfall structure in Hudson River." The source of the leak is unknown. The licensee has made arrangements for remediation and has informed the U.S. Coast Guard National Response Center, State of New York and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-06-23
44313 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-06-23 10:35 | 2008-06-23 11:28 | 2008-06-23 | ONLY ONE SAFETY ITEM AVAILABLE FOR SAFETY FOR GREATER THAN 8 HOURS "I. EVENT DESCRIPTION: In April of this year, BWXT replaced the recirculation columns on the High Level Trough Dissolvers in the Uranium Recovery Facility. The columns were processed out of the area according to standard waste handling procedures for disposal. An NMC technician raised a concern as the columns were checked by BWXT Security before placement into a SeaLand container. The technician believed the response of Security's monitor was overly sensitive compared to the assigned 235-U values based on calculations. NMC immediately placed a hold on the columns. "The columns were later moved into the Decon Area of BWXT's Waste Treatment Facility where they were stored for approximately three weeks. The Decon area is posted by Nuclear Criticality Safety for 100 grams of 235-U. NMC personnel conducted subsequent NDA field measurements of the columns and estimated an accumulation of approximately 695 grams 235-U in four of the columns. The Decon Area was immediately secured and a Radiation Work Permit (RWP) generated to clean and reevaluate the columns in the Uranium Recovery's Maintenance area. "The four columns were relocated to the Recovery Maintenance area where they were cleaned according to the instructions in the RWP. NDA measurements of the columns and cleaning materials indicated a total 235-U content of 577 grams. The Limiting Condition for Operation (LCO) in the Decon Area is 400 grams. The Item Relied On For Safety (IROFS) for control of mass was degraded. "II. EVALUATION OF THE EVENT: The safety basis for the Decon Area takes credit for two IROFS, control of mass and moderation. The control for mass was degraded. Although the LCO for 235-U mass was exceeded by 177 grams, this was less than the fully reflected, optimally moderated minimum critical mass of approximately 800 grams. A criticality was not credible in this scenario. There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. The amount of 235-U present in the columns was less than the minimum critical mass of approximately 800 grams. However, with the degradation of one IROFS and only one remaining, double contingency could no longer be assured. "III. NOTIFICATION REQUIREMENTS: BWXT is making this 1 hour report in accordance with 10 CFR 70, Appendix A, (a)(5) - Loss of controls such that only one item relied on for safety, as documented in the Integrated Analysis Summary, remains available and reliable to prevent a nuclear criticality accident, and has been in this state for greater than eight hours. "IV. STATUS OF CORRECTIVE ACTIONS: An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2008-06-23
44312 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2008-06-16 14:13 | 2008-06-23 11:01 | 2008-06-23 | REPLACEMENT BREAKER CHARGING MOTORS FAILED MINIMUM VOLTAGE TEST "Event: On June 16, 2008, Duke Energy (Duke) completed a reportability determination which concluded that a defect associated with 10 electric charging motors for breakers is reportable under Part 21. This is a legacy issue from May 22, 2000, which was re-evaluated as a result of an assessment of Oconee's Part 21 processes. The motors were procured as safety-related from Asea Brown Boveri (ABB) (Florence, SC location) on February 22, 2000, ABB Part# 709799T11. The motors were received on March 9, 2000 and subsequently, breaker personnel identified the part number on the replacement motors did not agree with the existing motors. When installed in a breaker for testing, the replacement motors did not function at the required minimum 90VDC. Duke will provide follow up written notification within 30 days pursuant to Part 21.21(d)(3)(ii). "Initial Safety Significance: None. The motors were never placed in service. However, the evaluation concluded because of the safely related applications for which the motors were intended, the defect could have resulted in a significant safety hazard had the motor(s) been placed in service." The licensee verified that this part was not used at other Duke nuclear plants. The licensee notified the NRC Resident Inspector and the ABB Project Manager for Oconee. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2008-06-23
44311 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-06-23 03:00 | 2008-06-23 03:26 | 2008-06-27 | LOSS OF EMERGENCY RESPONSE CAPABILITY - TSC IS UNAVAILABLE "UNAVAILABILITY OF TSC CHARCOAL FILTER FOR SCHEDULED MAINTENANCE "At 0300 on Monday, June 23,2008, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system charcoal filter was removed from service for planned charcoal bed maintenance. The balance of the TSC ventilation is not affected by the charcoal bed maintenance and remains available. "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "Charcoal filter maintenance is scheduled to complete at 1000 on Wednesday, June 25, 2008. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." * * * UPDATE AT 1455EDT ON 06/24/08 FROM SCOTT SCHNEIDER TO S. SANDIN * * * At 0905 on Tuesday, June 24, 2008, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system charcoal filter was removed from service for planned charcoal bed maintenance. The balance of the TSC ventilation is not affected by the charcoal bed maintenance and remains available. The charcoal filter was removed from service at 0300 on Monday, June 23, 2008 (as previously reported via EN # 44311), and subsequently restored to available status at 1614. "Under certain accident conditions the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "Charcoal filter maintenance is scheduled to complete at 1300 on Wednesday, June 25, 2008. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss an emergency response facility." Notified R3DO (Lipa). * * * UPDATE PROVIDED BY DEAN BRUCK TO JASON KOZAL AT 1846 ON 6/27/08 * * * "The planned maintenance and testing was completed. The TSC Ventilation system was returned to service at 2045 EDT on 06/26/08. "The licensee notified the NRC Senior Resident Inspector." Notified R3DO (Lipa). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-23
44310 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-06-20 23:25 | 2008-06-21 21:35 | 2008-06-21 | NOTIFICATION TO KENTUCKY ERT DUE TO EXCEEDING PERMIT LIMITS AT OUTFALL "At 1750, 6/21/2008 CDT, the Kentucky Emergency Response Team (Report Number 2008-2125) was notified of the following issue. The C-637 RCW (Recirculating Water) 'H' Supply loop was being repaired and a residual RCW leak from the valve vault was being pumped back to the pump house basin when the portable pump shutdown causing an overflow condition at a Commonwealth of Kentucky permitted outfall 002. The Commonwealth of Kentucky's permit limit for the outfall is 1 mg/L for total phosphorus and the chlorine level is to be below detectable limits. Contrary to this, the total phosphorus level was slightly above 1 mg/L and residual chlorine was approximately 0.1to 0.3 mg/L. Control of the RCW leak in the valve vault was re-established. "This event is reportable as 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials.' "The NRC Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-08-1840: PGDP Event Report No. PAD-2008-20:" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | OFFSITE NOTIFICATION/NEWS REL | [8 empty] | NON EMERGENCY | 2 | KY | FUE |  |  | PART 70 APP A (c) |  |  | 0 | 2008-06-21
44309 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-06-19 17:35 | 2008-06-20 00:15 | 2008-06-20 | CONTROL ROOM VENTILATION INOPERABLE "At 17:35 hours on June 19, 2008, the Control Room authorized post maintenance testing following replacement of solenoid valves affecting the 2B Control Room Emergency Ventilation (CREV) subsystem. This testing was required to restore this Subsystem to OPERABLE following maintenance. This test inputs a Simulated high radiation signal into the logic for Control Building HVAC system and ensures that the Control Room Emergency Ventilation subsystem automatically aligns to the Radiation/Smoke Protection mode. During performance of this test, the Control Building Exhaust Fan Damper (2D) failed to close and the associated Control Building Exhaust Fan failed to trip as expected. These functions are required to occur to maintain a positive pressure in the Control Building during a high radiation in the Control Building ventilation intake plenum or during smoke intrusion into the Control Building. Since Brunswick has a shared control room, Unit 1 and Unit 2 entered Technical Specification (TS) 3.7.3,'Control Room Emergency Ventilation (CREV) System,' Required Action B.1 (i.e., be in Mode 3 within 12 hours). "At 1910, the 2A Control Room Emergency Ventilation (CREV) subsystem was manually placed in the Radiation/Smoke Protection mode. This action fulfilled the Control Room Emergency Ventilation safety function and allowed the 2A Control Room Emergency Ventilation (CREV) subsystem to be declared OPERABLE. Required Action B.1 of Technical Specification (TS) 3.7.3 (be in Mode 3 within 12 hours) was exited. "This report applies to both Units 1 and 2 and is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The condition with the Control Building Exhaust Damper (20) is intermittent. The solenoid valve for this damper was recently replaced on 5/3/2008. The post maintenance test included ensuring this damper would close on demand and was completed satisfactory. In addition, this same test was performed on the other division of CREV logic on 5/17/2008, the Control Building Exhaust Damper and Exhaust Fan functioned as required. In addition, the exhaust damper and fan operated properly, when manually operated from the Control Room, while manually placing the CREV system in service. "All systems functioned as required except for the Control Building exhaust fan. "2A Control Building Emergency Ventilation (CREV) subsystem placed in the Radiation/Smoke. The NRC Resident Inspector has been notified. Repair options for the Control Building Exhaust Damper are being developed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-06-20
44308 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2008-06-19 | 2008-06-19 15:48 | 2008-06-19 | AGREEMENT STATE REPORT INVOLVING AN IMPROPERLY STORED/ACCOUNTED FOR TROXLER GAUGE The following information was received from the State of Oklahoma via email: "Ramey Enterprises was licensed for portable gauges, and held radioactive materials license OK-21291-01, which expired 1/31/2005. The license authorized possession of portable soil moisture density gauges containing Cesium and Americium. The licensee is located at 505 East 19th street in Owasso, OK. Ramey retained their radioactive material and continued to operate after the license expired. DEQ initiated enforcement action, leading to issuance of a consent order in late 2007 which involved payment of a penalty spread over three payments and submission of a new application, following which DEQ would issue a new license. Ramey stopped making the penalty payments and the Ramey RSO did not respond to DEQ attempts at telephone contact. A DEQ inspector visited the property on 6/19/08 to verify the security of the radioactive material. The inspector could not locate anyone at the facility office, and investigated the property to see if he could find a facility employee to assist him. He found an unlocked door and opened it to see if he could find an employee. The investigator had his survey meter out and turned on, and noticed that the meter reacted in the area of the door. He found a wooden chest with a Yellow II RAM transportation label. Outside the chest, his meter read about 10 mrem/hour. The chest was not chained, locked, or secured in any way. He attempted to call a cell phone belonging to the facility RSO, and the RSO answered. She was unavailable, but arranged for another employee to contact the inspector and provide assistance. When the employee arrived, the inspector and the employee opened the chest and found a Radium-beryllium portable gauge (details provided below). Radiation levels outside the shutter were approximately 50 mrem/hr. Measurements of a wipe of the closed shutter did not reveal any removable contamination. The RaBe gauge was not listed on the previous license, nor the new license application, and the facility staff denies any prior knowledge of the gauge's presence. Facility staff will secure the gauge properly. The inspector verified that the previously-known Cs/AmBe gauges were still present chained in their storage area. The licensee has acknowledged their responsibility to ensure that the RaBe gauge is secure. Troxler Model 2401 Device s/n 1498 mfr date 9/16/71 1.9 millicurie radium beryllium s/n unknown "Troxler reports the gauge was sold to another engineering consulting firm in 1973. That firm no longer has a radioactive materials license. There is no known connection between the original purchaser and the present property, and how or when the gauge ended up in possession of Ramey is unknown at this time. "The above is a preliminary notice based on a telephonic report from the inspector in the field." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2008-06-24
44307 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-06-13 04:00 | 2008-06-19 14:11 | 2008-11-06 | AGREEMENT STATE REPORT INVOLVING A VEHICLE TRANSPORTING RADIOACTIVE MATERIAL On 6/13/08, a Cardinal Health vehicle transporting Tc-99m and I-131 was involved in a vehicle accident on Route 495N. The vehicle overturned spilling eleven (11) shipping containers onto the roadway. The containers were not damaged and no radioactive material was released on the roadway or to the surrounding environment. The rad material was returned to the Cardinal Health facility in Woburn, MA. The licensee notified the National Response Center and the Commonwealth of Massachusetts. * * * UPDATE FROM ROBERT GALLAGHER TO DONALD NORWOOD 11/06/2008 AT 0916 HRS * * * "The following is submitted as additional information for NMED Item No. 080358 (EN44307): "The licensee, Cardinal Health Nuclear Pharmacy, provided the Massachusetts Radiation Control Program with corrective actions they have taken to preclude a recurrence of this event. The corrective actions include retraining all delivery personnel (performed on June 18, 2008) on the importance of remaining alert while transporting radioactive materials. Delivery personnel were instructed not to work longer hours prior to the start of their delivery route." Notified R1DO (Caruso) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-06-24
44306 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-06-18 14:12 | 2008-06-19 12:58 | 2008-06-19 | 24-HR CERTIFICATE OF COMPLIANCE VIOLATION REPORT "Entergy discovered on June 18, 2008 at 1412 that, due to an error in the Cask Loader Database, four spent fuel casks were loaded in a manner not in compliance with the Certificate of Compliance (CofC). As discussed below, this event is not safety significant since all cask design limits (e.g., heat load, radiation levels, and criticality) continue to be met although some specific spent fuel assemblies loaded were outside of the conservative individual fuel assembly limits specified in the CofC. "Specifically, during a data update of the Cask Loader Database, it was discovered that four HI-STORM 100 model casks had been loaded with spent fuel bundles that exceeded the Certificate of Compliance (CoC) limits. The four casks involved are F16D003AD, F16D003AE, F16D003AF, and F16D003AG. Verification of the database has determined that 34 of fuel assemblies loaded in these four casks exceeded the maximum allowed Decay Heat per Fuel Storage Location Limit and/or the Fuel Burnup Limit as specified in the CofC Section 2.4 when the assemblies were loaded into the casks. This condition is reportable in accordance with CofC Section 22. "CAUSE: The preliminary cause is an error in the Cask Loader Database. The database had incorrect bundle exposures for these assemblies. The Cask Loader Database is used to select fuel to load in each cask. The assembly exposures in the Cask Loader Database are used to ensure assemblies selected for loading into fuel casks meet the applicable exposure and cooling time limits provided in the Certificate of Compliance. "SAFETY SIGNIFICANCE: It has been verified that currently the decay heat loads for all assemblies are less than the CofC limits. All casks are below the cask total heat load limit of 28.19 kW and all cooling features for the casks are functioning properly. Since the total heat loads in the casks are below the required limits, the structural integrity of the casks is not challenged. A preliminary evaluation of the as loaded configurations was performed on the four casks. This evaluation concludes that fuel cladding in the affected casks is not adversely affected since the fuel cladding temperature will not exceed the fuel cladding design limit of 400 degrees centigrade. "Furthermore, the fuel assembly exposure assumed in the dose calculations bounds the exposure of the loaded fuel assemblies. Radiation levels of stored casks are within Cask Technical Specification limits and there are no radiation anomalies. Reactivity parameters are not affected by the errors identified. "There has been no impact on occupational dose and all surveillance parameters are within acceptance limits. All four casks are currently considered operable and performing their intended safety function." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW | [5 empty] | 0 | 2008-06-19
44305 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-06-18 20:15 | 2008-06-19 05:00 | 2008-06-19 | METEORLOGICAL MIXING CALCULATIONS UNAVAILABLE "This is an 8-hour non-emergency event notification in accordance with 10 CFR 50.72(b)(3)(xiii) due to a loss of emergency assessment capability. On June 18, 2008, at approximately 2015 PDT, the backup meteorological tower 60-meter air temperature indication failed. The primary meteorological tower is also unavailable. This results in a loss of the delta temperature function. This delta temperature function would be used to determine air mixing for offsite does calculations in the event of an emergency. Without actual delta temperature data, procedures specify conservative assumptions for determining air mixing. "Other meteorological functions (10-meter temperature, wind speed and wind direction, and 60-meter wind speed and wind direction) remain functional." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-19
44304 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-06-17 16:30 | 2008-06-18 17:40 | 2008-06-18 | AGREEMENT STATE - DAMAGE TO TROXLER MOISTURE DENSITY GAUGE The Washington State Department of Health, Office of Radiation Protection provided the following report via e-mail: "The Licensee was working with a Troxler Model 3430, portable moisture density gauge, serial number 19739, having a 10 millicurie, Cesium-137 and a 40 millicurie, Americium-241/Beryllium sealed sources. The work was being done at a temporary job-site near Walla Walla, Washington. The gauge operator was taking measurements with the Cs-137 source rod inserted into the test hole. The operator walked away from the gauge to look for the next test site. While the operator was away, the gauge was struck by a front-end loader. The gauge operator cordoned off the area and contacted the Radiation Safety Officer. The RSO then contacted the Office of Radiation Protection (ORP) to make a verbal report. Two ORP staff were already in the vicinity and were rerouted to the incident scene. When staff arrived they reported the gauge had been visibly damaged. The plastic exterior was smashed with the source rod still in the test hole. The gauge's guide rod with the handle had been sheared-off by the front-end loader. ORP staff were able to push the source rod back into the gauge's shielded position. They also took a wipe sample from the source rod, the gauge exterior, and surveyed the soil where the source rod had been. No contamination was found. The gauge was placed back into its transport box. ORP staff took dose-rate readings on the outside of the box and found normal levels. The gauge was taken to the licensee's storage facility in Walla Walla where it awaits shipping instructions for returning it to Troxler. "The Licensee is being cited by DOH for not keeping the gauge under constant surveillance and control while away from an approved storage location." Washington Report WA-08-040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-06-23
44303 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2007-07-20 | 2008-06-18 08:28 | 2008-06-18 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The state provided the following information via e-mail: "The Department contacted the general licensee because the annual fee for the general license was overdue for two self illuminating signs. The signs were from Best Lighting (Model SLTURW10)(Serial # 166473 and 166474) with 7.03 curies [each] of H3 (in June of 2006). The general licensee hired an individual to remove the signs from the dining room and put them into the storage room in the cafÚ during July of 2007. "The general licensee went to the storage room in the second week of August 2007 to retrieve some stored items. Items were missing and additionally the two exit signs were also missing. The general licensee tried to contact the man who she hired to move the supplies and equipment. She did not find a phone listing. She sent him a letter to the address he had given her and the letter was returned as no such address." Nebraska event number: NE080003. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-06-23
44302 | 0 | BECKMAN COULTER, INC. |  |  |  |  | 2008-06-13 | 2008-06-17 12:45 | 2008-06-17 | SCINTILLATION COUNTER SEALED SOURCE FOUND LEAKING A 30 ÁCi (microcurie) Cs-137 sealed source failed a leak test performed on 6/13/08. The leak test results measured 526 cpm with 54 cpm background with no contamination present. The source is used in a Beckman Coulter Scintillation Counter Model LS6500, S/N 7070809 at the Scripps Institute of Oceanography located in La Jolla, CA. The source will be returned to the Corporate Office in Fullerton, CA for disposal. The licensee also notified the State of California Rad Health Branch of this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-06-17
44301 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-06-17 05:43 | 2008-06-17 07:43 | 2008-06-17 | TSC HVAC SYSTEM RENDERED NONFUNCTIONAL "Work Order Number 1050889203 will perform maintenance on 1R24-S026 - 600/208V MCC. The specific work is to remove the LA 600 Breakers in frames 1C & 5C to take measurements for replacement breakers. The removal and measurement of the two breakers will be performed by two work crews simultaneously to minimize out of service time. In order to perform this work activity, the power will be removed from 1R24-S026 which also supplies power to the TSC HVAC rendering it nonfunctional during the performance of this work activity. This work activity is planned to be performed and completed within a 12 hour work shift with 2 hours scheduled for establishing and removing the clearances for a total of 14 hours. During the time this activity is being performed, the TSC air handling unit, TSC condensing unit, TSC filter train, and the fan unit for the TSC filter train will not be available for operation. As such, the TSC HVAC will be rendered nonfunctional during the performance of this work activity. "If an emergency declaration is made requiring activation of the TSC during the time this work activity is being performed it will take approximately (3-6) hours to return the equipment back to an operable status dependent on the stage of the work activity at the time the emergency occurs. Plans are to utilize the TSC for any declared emergency during the time these work activities are being performed, as long as radiological conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to relocate to the Control Room and TSC support personnel to relocate to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC." Licensee notified NRC Resident Inspector. * * * UPDATED AT 1545EDT ON 06/17/08 FROM BARRY COLEMAN TO S. SANDIN * * * At 1500EDT the MCC was re-energized and the HVAC equipment confirmed operable at 1518EDT on 06/17/08. The licensee will inform the NRC Resident Inspector. Notified R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-17
44300 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-05-16 | 2008-06-16 19:26 | 2008-07-07 | AGREEMENT STATE REPORT - LOST OR STOLEN THICKNESS GAUGE This information was received from the state via e-mail: "A PA licensee, Carlisle Syntec, Inc. (CSI) in Carlisle, PA has reported that a NDC Infrared Engineering gauge model #102X, serial # 4076, GL#1933-70GL, containing a 80 milliCurie (mCi) (or 80,000 uCi) sealed source of Americium-241 (Am-241) was shipped via FedEx Ground and found to be missing from the transport container upon arrival at its destination. The gauge was shipped from the licensee's facility in Carlisle, PA, to the manufacturer (NDC Infrared Engineering Inc.) in Irwindale, CA on May 13, 2008. The empty box arrived in Irwindale on May 16, 2008. The manufacturer notified FedEx Ground and the licensee on May 16, 2008 to set up a trace; FedEx Ground claim [REDACTED]. "The Commonwealth's Bureau of Radiation Protection (BRP) was notified of the incident at 4PM on June 13, 2008 by a CSI employee, with no details, other than a radioactive gauge was lost by FedEx. That employee noted the Radiation Safety Officer was out on sick leave. BRP followed-up on June 16, 2008 with CSI to ascertain the above information. CSI uses other NDC radioactive gauges, and a reactive inspection is being planned. "This is the initial formal notification to DEP management, PEMA / state EOC, PA HS, PSP, PennDOT, NRC HQs Ops Center and Region I, et al. A NRC NMED report is being drafted." * * * UPDATE VIA EMAIL FROM DAVID ALLARD TO JOHN KNOKE AT 2014 EDT ON 07/07/08 * * * "FedEx searched all the locations of transfer this package went through by requesting a review of the overgoods in each location. Overgoods are the items or materials that become loose from their packages during transit that cannot be linked to the correct package. Overgoods areas were searched from 5/16 to 5/27/2008. The tracking number for this package is [REDACTED] and the claim number for the loss is [REDACTED]. More information when available. This Event will remain an open and unresolved lost source." Notified R1DO (Burritt), R4DO (Hay), FSME (Persinko), and ILTAB (Whitney) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2008-06-19
44299 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-06-14 02:00 | 2008-06-14 19:19 | 2008-06-14 | AGREEMENT STATE REPORT - STOLEN THERMOMEASURE GAUGE The State of Louisiana reported the theft of a Thermomeasure Model 5715 1C gauge containing a 100 mCurie CS-137 source (S/N B5633). The gauge was in a truck in a fenced parking area for the licensee (B J Services). The theft was discovered around 0200 CDT on 6/14/08 but the last time the gauge was accounted for was on 6/11/08. The theft has been reported to the police. The State of Louisiana is investigating. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-06-18
44298 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2008-06-13 13:28 | 2008-06-13 15:13 | 2008-07-02 | AGREEMENT STATE REPORT - PORTABLE GAUGE MISSING IN TRANSIT The following report was received from the State via facsimile: "The South Carolina Department of Health and Environmental Control was notified at 1:28 p.m. on June 13, 2008 by the licensee that a package containing a radioactive source was lost by Fed-Ex. The sealed source contains 80 mCi of Am-241 and is used in an NDC Systems Model 104 portable gauge. The package was shipped from Macon, GA on June 5th. On June 11th, the licensee received the shipping label, with no package attached, at the licensee's office on Corporate Road in Charleston, SC. The licensee contacted Fed-Ex on the 11th where Fed-Ex then placed a trace on the package which they indicated could take 48 hours. The 48 hour time frame has expired and Fed-Ex has indicated that they cannot find the package but they are continuing their search through various warehouses. Fed-Ex still has the package listed as "in route to its destination". The licensee has also notified the Georgia radiation control program. This event is open pending the results of the licensee's and Department's investigation. Notifications and updates will be made through the NMED system." * * UPDATE FROM JIM PETERSON TO JOHN KNOKE AT 1432 EDT ON 07/02/08 * * FedEx has found the missing sealed source at their warehouse. Notified R1DO (Bellamy), FSME EO (Zelac) and ILTAB via Email THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2008-06-18
44297 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-06-13 07:30 | 2008-06-13 15:01 | 2008-06-13 | 10 CFR 26.719 FITNESS-FOR-DUTY - UNLICENSED CONTRACT SUPERVISOR FAILED RANDOM DRUG TEST A non-licensed contract employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2008-06-13
44296 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2008-05-31 12:06 | 2008-06-13 13:47 | 2008-06-13 | 60-DAY REPORT INVOLVING AN INVALID GROUP II PRIMARY CONTAINMENT ISOLATION "At 1206 On May 31, 2008, with the James A. FitzPatrick Nuclear Power Plant operating at 100% reactor power, Reactor Building (RB) Radiation Monitor 17RM-452A failed resulting in a Group II Primary Containment Isolation. "The failure resulted in actuation of the RB ventilation system isolation logic, start-up of the 'A- Standby Gas Treatment (SBGT) System, and a Half PCIS Group II Isolation. Operations department personnel verified that all expected isolations occurred and Radiation Protection verified that radiation levels in the Reactor Building were normal. "The reactor remained at 100% power throughout the event. While the isolation signal was falsely generated by the failure of the Radiation Monitor the actuation logic functioned properly and the plant equipment responded as designed. There were no other equipment failures associated with this event and neither plant operation nor the health and safety of the public were affected by this event. "The condition meets the reporting criteria of 10 CFR 50.73 (a)(2)(iv)(a) because the failure of the RB Radiation Monitor constitutes an invalid signal which resulted in a general Containment isolation signal affecting containment Isolation valves in more than one system ('A' SBGT, 'A' H2/02 Exosensors, 'A' Drywall Cam, 'A' Containment Atmosphere Dilution (CAD), 'A' PCP Vent and Purge). Since the signal was invalid this event meets the criteria in 10 CFR 50.73 (a)(1) for being reported as a 60-day phone call rather than as an LER. "The event has been entered into the corrective action program and the resident inspector has been briefed. The results of the Equipment Failure Evaluation are not yet available." The licensee also notified the State of New York of this report. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-06-13
44295 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2008-06-13 11:00 | 2008-06-13 12:05 | 2008-06-13 | PART 21 REPORT INVOLVING COMMERCIAL GRADE RELAY CONTACTS CONTAINING POTENTIAL DEFECTS The following Part 21 notification was received via fax: "On June 13, 2008, AmerGen Energy Company, LLC (AmerGen) completed a reportability determination which concluded that relay contacts contained an underlying design vulnerability that created a failure mode, and were reportable under Part 21, since the underlying vulnerability could create a substantial safety hazard. The relay contacts are Commercial Grade items dedicated by AmerGen. The relay contacts are provided by Joslyn Clark Controls Inc. (formerly AO Smith) as Normally Closed (N/C) open top contact assemblies (part numbers KPM-44, KPM-46, KPM-6A, and KPM-4A). These contacts are used in safety related applications, primarily in the engineered safeguards actuation system (ESAS). They are also used in safety related applications in the makeup/high pressure injection (HPI) system, main steam system, and the heat sink protection system (HSPS). "The underlying vulnerability associated with the N/C Joslyn Clark contact is the design of the nylon contact arm. The design allows the contact to become configured incorrectly during assembly or following maintenance. If installed improperly, the moving contactor can hang up on the lip of the slot in the nylon actuator. The hang up results in failure of the contact to fully close and perform its function. "Following proper assembly, the N/C Joslyn Clark contacts will not become hung-up during normal relay operation. "As a result of this exposed design vulnerability, the Commercial Grade Dedication (CGD) plans as well as the maintenance procedures have been enhanced to prevent a relay from being placed into service with an improperly configured contact. Extent of condition reviews performed to date on relays installed in the plant, have not identified any of these deficiencies. "The NRC resident inspector was notified of this part 21 notification by the licensee." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 21.21 |  |  |  | 0 | 2008-06-13
44294 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-04-14 13:08 | 2008-06-13 11:01 | 2008-06-13 | INADVERTANT DEENERGIZATION OF GROUP SIX LOGIC CIRCUIT "This is a 60 day telephone notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) describing an invalid actuation of general containment isolation signal (Group 6) affecting more than one system. "On April 14, 2008 at 1308 hours Central Daylight Time (CDT), with Unit 3 in mode 4, an unanticipated Group 6 primary containment isolation signal (PCIS) was generated during the placement of a clearance. During the placement of the clearance, plant personnel removed a fuse which deenergized Group 6 PCIS logic. This resulted in the auto start of train A of the control room ventilation system, auto start of trains A and C of the standby gas treatment (SGT) systems, and the isolation of the reactor zone and refuel zone normal ventilation systems. "All systems responded according to plant design. Train B of the SGT system did not auto start because only the A channel PCIS was affected during the implementation of the clearance. Train B of SGT is only affected by the B channel PCIS logic. By 1444 hours CDT, the fuse was reinstalled, the affected systems were returned to standby readiness. There were no safety consequences or impact to the health and safety to the public. The event was entered into TVA's corrective action program. The reference corrective action document is PER 142243. "The Senior Resident inspector had been notified of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-06-13
44293 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-06-13 01:46 | 2008-06-13 02:14 | 2008-06-13 | UNUSUAL EVENT DUE TO PARTIAL LOSS OF ANNUNCIATORS The licensee is investigating a loss of greater than 75% of their annunciator indications. The annunciators lost include alarms for ECCS divisions 1 & 2, Reactor Control Panels, and electrical panels. "All normal methods of monitoring plant systems are available." Compensatory measures are being initiated. The plant is stable at 100% power and all maintenance has been stopped. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RALPH KOMBOL TO MARK ABRAMOVITZ AT 0612 ON 6/13/08 * * * Troubleshooting revealed the "C" MUX to be the cause of the problem. "C" MUX was removed from service and the redundant unit is now supplying input. Based on satisfactory testing the Shift Manager terminated the Unusual Event. The licensee informed the NRC Resident Inspector. Notified R3DO (Louden), IRD (McDermott, Gott), DHS (J. Craig), FEMA (J. Dunker), DOE (R. Foot), USDA (R Leadbetter), HHS (Y. Mammarelli), Canada (L. Colligan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-06-13
44292 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-06-12 13:45 | 2008-06-12 17:06 | 2008-06-12 | UNAVAILABILITY OF EMERGENCY OPERATIONS FACILITY "At 1345 on Thursday, June 12, 2008, the Cook Nuclear Plant (CNP) Buchanan Office Building was conservatively evacuated due to the presence of a solvent vapor in the building. The Buchanan Office Building houses both the Emergency Operations Facility (EOF) and Joint Information Center (JIC). "The Buchanan Office Building has been ventilated and has been verified inhabitable by Safety and Health personnel. The Emergency Operations Facility and Joint Information Center access was restored at 1530 on Thursday, June 12, 2008. Further investigation concluded that the concentration of the solvent vapor was never at a level that would have mandated evacuation. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of offsite response capability. The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-12
44291 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2008-06-12 11:30 | 2008-06-12 15:19 | 2008-07-01 | UNUSUAL EVENT DECLARED DUE TO A MAJOR LOSS OF RESPONSE AND COMMUNICATIONS CAPABILITY "At 1130CDT on 6/12/2008, the Duane Arnold Energy Center was informed due to flooding in the local area that access to the Joint Information Center (JIC), the Offsite Radiological Analytical Laboratory (ORAL), the Offsite Relocation and Reassembly Area (ORRA), and the Emergency Operations Facility (EOF) have been lost. This constitutes a reportable condition per 10CFR50.72(b)(3)(xiii) due to the major loss of offsite response capability. The ORAL function will be maintained by the Iowa State Hygienics Lab. At the present time the remaining facilities are being relocated or moved to the Linn County Emergency Operations Center (EOC) located at the Kirkwood Community College Campus. Also, although multiple roads in the area are closed due to high water level, evacuation capability in the EPZ is being maintained. Also, at 1256CDT on 6/12/2008, Duane Arnold Energy Center was informed that local commercial phone service through the Palo phone system has been lost. This service also includes our ability to fax and access the internet. We have also lost our FTS2001 ENS connection. Again, per 10CFR50.72(b)(3)(xiii) this represents a major loss of offsite communication capability. Offsite communications is being maintained currently thorough our microwave and cell phone systems. Onsite communications are possible through our in house PBX and page system. Contingency plans are in effect to setup a mobile satellite uplink that would include voice and data capability." The NRC Resident Inspector has been informed. * * * UPDATE AT 1629EDT ON 06/12/08 FROM DOUG PETERSON TO S. SANDIN * * * "At 1430CDT on 6/12/2008, Duane Arnold Energy Center lost communications capability via commercial phone line, FT2001 ENS system and the microwave phone system. This meets the threshold criteria of an EAL classification of an Unusual Event. At 1440CDT the Shift Manager declared that Unusual Event and notifications were made to Linn County Emergency Management Agency, Benton County Emergency Management Agency and the Iowa Homeland Security Emergency Management Division. Currently, offsite communication is still possible via our installed cell phone and satellite systems and onsite communications remain possible via our PBX and page system." The NRC Resident Inspector has been informed. Notified ET Member (B. Mallet), all IRD Management (B. McDermott, W. Gott, M. Leach), Commissioners' Staffs (D. Skeen, T. Hipschman, S. Baggett, J. Thoma, D. Coe), EDO Staff (J. Adams), PAO (E. Brenner), OCA (D. Decker), RDOs (R. Summers, B. Bonser, P. Louden, G. Miller), FEMA, DOE, USDA, and HHS. * * * UPDATE AT 1428EDT ON 06/19/08 FROM MARK GILBERT TO J. KNOKE * * * "On 6/12/2008 at 1444 FPLE-DAEC declared an unusual event (SU6.2) due to loss of all offsite communication. These systems included the FTS 2001, microwave phone lines, and commercial phone lines due to flooding of the Palo, Iowa phone station. Since that date FPLE-DAEC has reestablished two of the three offsite communication methods. The microwave telephone system has been restored and the commercial phone lines have been restored through a new exchange through the town of Shellsburg, Iowa, which was not affected by the flood. With these two lines of offsite communications reestablished the DAEC will de-escalate from the Unusual event from the loss of offsite communication. "FPLE-Duane Arnold will be issuing a press release stating the unusual event has been cancelled. The NRC senior resident inspector has been notified and the state of Iowa, Linn County, and Benton county will be notified." The licensee exited the Unusual Event at 1428 EDT on 06/19/08. Notified R3DO (Kunowski), NRR EO (Fred Brown), IRD MOC (Bill Gott), DHS, and FEMA. * * * UPDATE ON 7/1/08 AT 1640 FROM SCOTT AREBAUGH TO MARK ABRAMOVITZ * * * Multiple power sources are now available to the Emergency Operations Facility. The licensee notified the NRC Resident Inspector. Notified the R3DO (Kozak). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | IA | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(xiii) |  |  | 0 | 2008-06-12
44290 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2008-06-12 00:40 | 2008-06-12 05:48 | 2008-06-17 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM IDENTIFIED INOPERABLE DURING SURVEILLANCE "Unit 2 HPCI was declared inoperable during the performance of a scheduled surveillance test. HPCI failed to develop the required discharge pressure to meet its design function." Reactor Core Isolation Cooling (RCIC) is available. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVE FOSS TO JOHN KNOKE AT 0954 ON 06/17/08 * * * "The purpose of this notification is to retract a previous report made on 6/12/08 at 0549 hours (EN# 44290). On 6/12/08, the High Pressure Coolant Injection (HPCI) system was declared inoperable as a result of the performance of a routine Surveillance Test (ST). During the ST, the HPCI pump discharge pressure did not achieve the acceptance criteria of greater than or equal to 1258 psig. The highest indicated pressure achieved during the ST was approximately 1230 psig. Therefore, notification of this issue to the NRC on 6/12/08 as a loss of the HPCI safety function was initially made as a result of the belief that the HPCI system was inoperable due to inadequate discharge pressure. HPCI was maintained in an available status as troubleshooting began. "During subsequent troubleshooting on 6/12/08, it was determined that the Main Control Room HPCI discharge pressure indicator (i.e., the pressure indicator used during the ST) was reading approximately 65 psig low. Therefore, the pressure indicator used during the ST indicated a low value for discharge pressure. Based on this, the actual HPCI discharge pressure during the ST was acceptable. The pressure indicator was recalibrated and the HPCI ST was re-performed successfully. HPCI was declared operable by 1805 hours on 6/12/08. "Based on the above, there were no unplanned loss of the safety function for the HPCI system. Therefore, the initial ENS notification is being retracted. " Licensee has notified NRC Resident Inspector. Notified R1DO (Schmidt) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-06-12
44289 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2008-06-12 00:21 | 2008-06-12 01:21 | 2008-06-12 | ALERT DECLARED DUE TO TORNADO IMPACTING REACTOR BUILDING ONSITE The research reactor building at the Kansas State University was damaged due to a tornado onsite. There is extensive damage to the building. The reactor was shutdown properly earlier in the day. There is no damage to the reactor. There is a loss of power onsite however, this type of reactor requires no active cooling. The reactor is shutdown and stable. * * * UPDATE AT 0555 ON 6/12/08 FROM PAUL WHALEY TO PETE SNYDER * * * The Alert condition at the site has been terminated. Conditions requiring entry into the Alert have been rectified. Notified IRD (Gott), R4DO(Miller), EDO (Mallett), DHS (Jason Craig), FEMA (Mike LaForty), DOE (Thomas Yates), USDA (Rob Leadbetter), and HHS (Harry Peagler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EMERGENCY DECLARED | [9 empty] | ALERT | 4 | KS | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-06-12
44288 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2008-06-11 22:15 | 2008-06-11 23:52 | 2008-06-23 | PRECAUTIONS TAKEN DUE TO A TORNADO WARNING Precautions were taken due to a tornado warning in accordance with 10CFR50.54(x). Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE 1143EDT ON 6/23/08 FROM DAVID NELSON MADSEN TO MARK ABRAMOVITZ * * * The licensee is correcting their report to retract the reporting requirement with respect to 10CFR50.54(x). Notified R4DO(Proulx). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-06-12
44287 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-06-11 14:05 | 2008-06-11 23:48 | 2008-06-12 | IDENTIFICATION OF A POTENTIAL ISSUE WITH ACCUMULATOR DRAIN VALVES "On June 11, 2008 at 1405 PDT, licensed plant operators entered Technical Specification (TS) 3.0.3 on Units 1 and 2 due to identification of a potential ASCO solenoid valve failure that could initiate draining if the safety injection system accumulators following a small break Loss-of-Coolant-Accident (LOCA). "ASCO Model 8316 and 8321 pilot-operated solenoid valves over 12 years old are susceptible to a potential shuttle ('insert' per vendor documentation) malfunction. The malfunction is that with greater than 12 years of service and a loss of minimum operating pressure differential (MPOD), the shuttle (or insert) could reposition and fail to return to the desired position. This MPOD related reposition could result following instrument air pressure loss and subsequent restoration to containment following a postulated small break LOCA. Diablo Canyon Power Plant (DCPP) Units 1 and 2 each have four susceptible ASCO solenoid valve locations used as drain valves for each of the four safety injection system accumulators per unit. "DCPP is reviewing the performance of the ASCO solenoids based on a plant problem report and subsequent discussion with the vendor. The safety significance of this event is low as there was no actual accumulator drain valve failure. Although PG&E is still evaluating the potential degradation mechanism and failure mode of these valves, TS 3.03 was conservatively entered base on the potential for malfunction of these valves. "On June 11, 2008, at 1610 PDT licensed plant operators exited TS 3.0.3 following isolation of the suspect accumulator drain lines. A licensee event report will be issued for this event. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-06-12
44286 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-06-11 | 2008-06-11 20:14 | 2008-06-13 | AGREEMENT STATE REPORT - RECOVERED NUCLEAR MATERIAL The state provided this information via e-mail: "It was reported today by [Pennsylvania Department of Radiation Protection] staff, that an orphan radioactive source was found in a lot of equipment and materials that had been acquired years prior from a bankrupt firm. The source is in Lake City, PA, and was inspected today for radionuclide identification, external exposure rates, and possible leakage. The source is in storage and appears to be in a shielded configuration (~ 3 mR/h contact with the device; background outside the storage area), no leakage was detected. [The source is contained in an industrial density gauge.] Information is still being gathered, but it apparently has been in storage for years. It was identified as a Cesium-137 source, activity noted as 100 millicuries (mCi) in 1979, thus, with a 30 year half-life, is now about 50 mCi. BRP is working with the owner and external agencies and organizations (i.e., NRC, DOE and CRCPD) to ensure the source remains secure, and, proper transfer and/or disposal is performed in a timely manner. There are also some records of prior ownership available, which may possibly assist in cost recovery with this abandoned 'generally licensed' (GL) source. An initial NRC 'NMED report' will be filed shortly. " * * * UPDATE AT 1730EDT ON 06/13/08 FROM D. ALLARD TO NRC OPS CENTER VIA EMAIL * * * The state provided this information via e-mail: "Working with CRCPD, a health physics service provider was hired to take the Oakes Machine Corp density gauge. The cabinet was opened and a KayRay Model 7062P, Cs-137 source housing was found; serial # 7825. It contained an original activity of 100 mCi (May1978). CRCPD has arranged for transfer to another licensed firm, who will recycle or dispose of the source. BRP will submit a NMED report to NRC." Notified R1DO (Summers) and FSME (Mauer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2008-06-16
44285 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-06-11 18:35 | 2008-06-11 20:11 | 2008-06-11 | SAFEGUARDS DEGRADATION DUE TO WEATHER CONDITIONS The licensee took actions involving the security posture in response to local adverse weather conditions, and has taken compensatory measures. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM JOSEPH STIVERS TO KARL DIEDERICH ON 6/11/08 AT 2117 EDT * * * Local adverse weather conditions abated, and as of 2010 CDT, the normal security posture was resumed. Notified R4DO (G. Miller) and ILTAB via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-06-11
44284 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2008-06-11 17:03 | 2008-06-11 18:48 | 2008-06-11 | HPCS DECLARED INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. During steady state operations, a Division 3 AC ground alarm was received, followed by a trip of the 2VD05C Division 3 switchgear room / Core Standby Cooling System (CSCS) Pump Room Supply Fan. Division 3 supplies power to the High Pressure [Core Spray] (HPCS), which is a single-train system. Although the system remained functional and capable of vessel injection following the failure, the HPCS system and its associated power supplies were declared inoperable based on long-term temperature considerations. At 1703, the circuit breaker for the HPCS injection valve, which is a Primary Containment Isolation Valve (PCIV), was opened and the valve deenergized in the closed position to comply with Technical Specifications. Disabling the injection valve affects the safety function of the system (HPCS), and this is reportable as an 8-hour ENS notification. "The cause of the ventilation fan motor trip has been determined to be a motor fault. Replacement of the fan motor is in progress." This event places the plant in a 14-day LCO per Technical Specification 3.5.1. Repairs are expected to be completed by 0700 on 6/12/08. The Reactor Core Isolation Cooling (RCIC) system is operable. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-06-11
44283 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-06-10 22:55 | 2008-06-11 00:59 | 2008-06-11 | 54 OF 165 EMERGENCY SIRENS INOPERABLE DUE TO POWER OUTAGE "On June 10, 2008, at 2255 hours it was determined that 54 of the 165 Limerick Generating Station's Emergency Offsite Sirens were inoperable due to a loss of power. The loss was a result of heavy storms which passed through the area resulting in power outages throughout the region. Efforts are underway to restore power to the affected sirens." The licensee notified the NRC Resident Inspector * * * UPDATE FROM BRANDON SHULTZ TO HOWIE CROUCH AT 1709 EDT ON 6/11/08 * * * "On June 11, 2008 at 1645 restoration efforts have recovered 44 of the 54 sirens rendered inoperable by the storm. The remaining 10 inoperable sirens no longer represents a major loss of emergency preparedness capabilities. Restoration of power to the remaining inoperable sirens continues under normal prioritization and using routine siren operating and maintenance procedures." No completion time was provided concerning repair of the remaining sirens. The licensee will be notifying the NRC Resident Inspector. Notified R1DO (Summers). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-11
44282 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-06-10 10:11 | 2008-06-10 18:04 | 2008-06-10 | LOSS OF THE SAFETY PARAMETER DISPLAY SYSTEM "At 10:11 today, 10 June 08, CPNPP [Comanche Peak Nuclear Power Plant] Unit 1 plant computer suffered a power supply failure. The failure of this power supply resulted in a loss of the SPDS (Safety Parameter Display System). Loss of the SPDS meets the 8-hr. reporting requirements of 10CFR50.72(b)(3)(xiii)." Troubleshooting and repair of the plant computer power supply is in progress. Repairs are estimated to be complete at 2100 CDT. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-10
44281 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  |  | 2008-06-09 | 2008-06-10 15:11 | 2008-06-26 | UNPLANNED CONTAMINATION On June 9, 2008, the Radiation Safety Officer (RSO) was notified that a vial containing standard reference material was discovered broken in one of the research laboratories. The reference material contained numerous isotopes of plutonium. It has not been determined how or when the breakage occurred. National Institute of Standards and Technology (NIST) Health Physics personnel responded to the area and determined that low levels of contamination were spread outside of the laboratory into the adjoining hallway. At this time, the hallway has be decontaminated. The lab is isolated and will be undergoing decontamination. The two researchers who discovered the broken vial were contaminated on their hands and were properly decontaminated. They will be undergoing bioassay and urinalysis to determine if an uptake occurred. Air samples were taken in the lab and are in the process of being counted to determine if an airborne problem existed. The NIST RSO contacted NRC Region IV (Cain and Campbell). * * * UPDATE AT 0038 ON 6/26/2008 FROM LARRY GRIMM TO MARK ABRAMOVITZ * * * Received from the National Institute of Standards and Technology via e-mail. "Since the initial incident report, NIST has done the following to mitigate the incident. "1. NIST Boulder requested assistance from NIST Gaithersburg. Management sent expert Health Physics and Occupational Health and Safety personnel, as well as radiation detection equipment to Boulder. "2. Hallways and areas potentially affected by the spill were again thoroughly surveyed to assure that no contamination existed outside the affected, sealed laboratory. This survey found two minor contamination spots in a stairwell, which easily cleaned up with soap and water. One office, which had contamination known from the earliest survey (Tuesday morning 6/10/08) was sealed pending future decontamination. "3. Air monitoring equipment was installed in the adjacent hallway as a precaution in the unlikely event of air leakage from the contaminated laboratory. To date, airborne contamination has not been detected by this equipment nor has any airborne contamination been detected by other subsequently installed air monitoring equipment outside of the contaminated laboratory. "4. Bioassay tests were initiated on personnel either known to have trace external contamination or determined to be potentially contaminated. Small sample bioassay tests have shown no internal contamination of individuals; however NIST is awaiting the results of more sophisticated bioassay tests. "5. Using personal protective equipment, NIST Health Physicists made entries to the contaminated laboratory on 6/14/08 and 6/15/08 to investigate the cause and extent of the spill. They found contamination in the laboratory sink and subsequently learned that a researcher who worked directly with the plutonium sample had used that sink to wash his hands during the incident. This prompted NIST to alert city wastewater officials of a potential discharge of plutonium from the sink to the sanitary sewer system. "6. For help in determining what might have been released to the sanitary sewer NIST requested help from the National Nuclear Security Administration's Radiological Assistance Program (RAP) on 6/16/08. RAP and its associated Department of Energy TRIAGE team have the ability to determine radioactive material activity quantities by taking radiation measurements with sophisticated equipment and computer programs. "7. Further bioassays samples were collected from individuals and sent out for analysis. NIST is awaiting the results of these tests. Some individuals have also received additional medical tests on the advice of physicians specializing in exposure to plutonium. "8. Planning with RAP personnel for entry to the laboratory ensued and the RAP team arrived 6/20/08. Entry occurred the same day and the RAP team collected the necessary data. The subsequent report of the RAP/TRIAGE analysis as well as NIST radiation measurements and calculations on dose rate data indicates that at least 76% - 87% of the spilled material can be accounted for. As many smaller areas of contamination have not been analyzed, NIST expects that more of the material will be accounted for during future entries and testing. "9. Prior to entering the contaminated laboratory, air sampling had not shown airborne contamination. In the course of repeated entries to the contaminated lab room, air sampling equipment placed by the RAP team detected airborne contamination, likely as a result of the team's activities. The team ceased operations and subsequent air sampling showed that radiation readings had returned to normal background levels in the spill room laboratory. Since responding to the incident, NIST Health Physicists have monitored and found no evidence of any releases of contaminated air to the atmosphere." Notified the R4DO (Proulx) and FSME (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 4 | CO | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2008-06-10
44280 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-06-09 20:07 | 2008-06-10 01:52 | 2008-06-12 | EMERGENCY OPERATIONS FACILITY POWER OUTAGE "The Emergency Operations Facility (EOF) became unavailable when a storm took down the power line supplying the building that houses the EOF. The emergency diesel generator failed to start, leaving the EOF without power. Notification being made in accordance with 10CFR50.72(b)(3)(xiii). If EOF actuation is necessary, the alternate EOF will be utilized." The licensee is investigating the failure of the backup emergency diesel generator to start. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0335 ON 6/12/2008 FROM JIM KONRAD TO MARK ABRAMOVITZ * * * Power had been restored to the EOF at the time of the initial notification. Power was unavailable on 6/9/2008 from 2007 to 2312, a period of three hours and five minutes. The licensee notified the NRC Resident Inspector. Notified the R3DO (Louden). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-10
44279 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2008-06-10 02:00 | 2008-06-10 01:29 | 2008-06-11 | EMERGENCY RESPONSE DATA SYSTEM WILL BE TAKEN OUT OF SERVICE "The Perry Nuclear Power Plant will be taking the ERDS out of service for scheduled maintenance. From approximately 0200 hours EDT, on June 10, 2008, until 2000 hours EDT, on June 10, 2008, personnel will be performing cleaning and inspection activities on the 120 VAC Emergency Response Information System (ERIS) Computer Power Center. During this planned preventive maintenance, the Integrated Computer System, the Safety Parameter Display System (SPDS), and the automatic mode calculation of the Computer Aided Dose assessment program (CADAP) will incur approximately two periods of unavailability of approximately two hours each. The unavailability periods are necessary to align a temporary power supply and reconnect the 120 VAC ERIS Computer Power Center upon completion of the activities. "The dose assessment function will be maintained during the brief out of service time periods by manual input of data into CADAP and, if required, by manual calculation. In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Plant Branch Exchange, the Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The ability to open and maintain on 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the two periods of unavailability. This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. A follow-up notification will be made when the activities are completed and the equipment is restored. The Resident Inspector has been notified." * * * UPDATE FROM DAVE O'DONNELL TO JOE O'HARA AT 1514 ON 6/10/08 * * * ERDS is still in service and will not be restored to normal until tomorrow 6/11/08. The scheduled maintenance on the normal power supply today was delayed. Notified R3DO(Lipa) * * * UPDATE FROM DAVE O'DONNELL TO KARL DIEDERICH AT 1710 ON 6/11/08 * * * ERDS was on a temporary power supply. ERDS restored to normal power supply at 1650. Notified R3DO (Louden). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-06-10
44278 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-04-23 15:56 | 2008-06-09 13:27 | 2008-06-09 | 60-DAY OPTIONAL NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "On April 23, 2008, at 3:56 p.m. CDT, power was lost on the reactor protection system (RPS) bus 'B'. The plant was operating at 100 percent power at the time. The loss of RPS bus 'B' interrupted power to the containment isolation actuation circuitry. This caused the Division 2 containment isolation valves in various balance-of-plant systems to automatically close, as designed. Plant operators implemented recovery procedures to shift RPS 'B' to its alternate power supply, and restore the systems affected by the isolation to service. The containment isolation valves were confirmed to have actuated as required. Plant [generating] capacity was not interrupted by the containment isolation signal. "The investigation of this event did not conclusively determine the cause of the loss of RPS bus 'B'. At the time of the event, scheduled maintenance was in progress to replace a relay which had contacts in the RPS 'B' circuitry. It is postulated that during this work, the technician inadvertently contacted part of the relay case while re-terminating the wiring, causing a short-circuit which blew a fuse in the circuit. This caused the output breaker on the RPS 'B' motor-generator set to trip, which de-energized the bus. "This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an invalid actuation of the Division 2 containment isolation actuation system." The loss of RPS 'B' also caused a half-scram signal to be generated. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-06-09
44277 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2008-06-08 12:30 | 2008-06-08 13:25 | 2008-06-08 | OFFSITE NOTIFICATION OF HYDRAZINE RELEASE "At 1230 on 6/8/08 Notification was made to Maryland Department of Environment and the National Response Center due to approximately 31 gallons of 35% hydrazine solution having leaked into the storm drains. The leak was due to an apparent discharge check valve failure combined with a pump failure at the GE demineralized water make up truck." The leak was isolated upon discovery. No adverse impact from the release is expected. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-06-08
44276 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2008-06-07 08:18 | 2008-06-07 11:19 | 2008-06-07 | MANUAL REACTOR TRIP FOLLOWING THE TRIP OF A CONDENSATE PUMP "On 6/7/08 at 0818 hours, an unplanned manual reactor trip was initiated on St. Lucie Unit 2 from 100% power due to a trip of the 2B Condensate Pump, which led to a trip of the 2B Main Feedwater Pump (MFP) and decreasing Steam Generator (S/G) levels. The reactor was manually tripped due to decreasing S/G levels. "Following the reactor trip, EOP-1, Standard Post Trip Actions and EOP-2, Reactor Trip Recovery procedures were completed and Unit 2 was stabilized in Mode 3. All control rods fully inserted. The Main Steam Safety Valves lifted as expected. Feedwater to the S/Gs was initially supplied by the 2A [MFP] until Auxiliary Feedwater Actuation System (AFAS) actuated as expected on low S/G level. Subsequently, the Auxiliary Feedwater Pumps restored S/G levels. Unit 2 electrical requirements were provided from offsite power. Other than the trip of the 2B Condensate Pump (initiating event) there were no major equipment failures. Unit 1 was not affected by this event. The grid is stable." Decay heat is being removed by the Auxiliary Feedwater Pumps feeding the S/Gs steaming to the bypass valves in the Condenser. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-06-07
44275 | 0 | BON SECOURS VIRGINIA HEALTH SOURCE |  |  |  |  | 2008-05-01 10:00 | 2008-06-06 15:07 | 2008-06-06 | MEDICAL EVENT - EXCESS SKIN EXPOSURE DURING TREATMENT A women was prescribed a breast cancer treatment using an HDR mammosite balloon brachytherapy. The dose was delivered in 10 fractions using Iridium - 192 seeds. During administration of the first fraction, the physicist received an alarm from the HDR computer, the alarm was overridden based on the judgment of the physicist at the time of the event and the treatment was completed. Additional fraction treatments were also completed as intended. Subsequent review of the first treatment and the cause of the alarm indicated that a medical event may have occurred. The alarm was indicating that the seed placement was dislodged by 2 centimeters. The physicist thought at the time that the alarm was indicating the seed dislodged by only 2 millimeters. The treatment calculations were revisited and the dislodgment of the seed by 2 centimeters put the seed at the skin entry point of the application catheter. This resulted in an under dose to the target site and an overdose to the skin. Preliminary calculations estimate that the skin in a 7 mm diameter around the catheter entry point may have received a dose of 3700 centigrays based on the strength of the seed (4.47 curies) and the dwell time. The patient will be notified of the event. The patient's doctor will continue to monitor the skin for any ill effects. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-06-12
44274 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2008-06-05 23:56 | 2008-06-06 05:40 | 2008-06-06 | TECH SPEC REQUIRED SHUTDOWN DUE TO LEAK IN SAFETY INJECTION TANK VENT LINE "On Thursday June 5, 2008 at 2356 MST Palo Verde Nuclear Station Unit 1 initiated a normal reactor shutdown to comply with condition C of Technical Specification (TS) LCO 3.5.1 and to facilitate a weld repair on a nitrogen leak found on the Safety Injection Tank (SIT) 1A vent line. "LCO 3.5.1 requires that all four SITs be operable in Modes 1 and 2. On June 5, 2008, at 0225 hours MST, Unit 1 entered Condition B which provides allowance for one SIT to be inoperable for a 24 hour period. The SIT will not be restored to operable status within the TS required 24 hour period, therefore, Condition C will be applicable at 0225 MST on June 6 2008. Condition C requires shutdown to Mode 3 in six hours and to reduce pressurizer pressure to less than 1837 psia within 12 hours. "On June 06 at 0148 hours MST, Unit 1 was manually tripped from approximately 20% power. The shutdown did not result in a release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. The primary plant is being stabilized in Mode 3 in forced circulation with both steam generators used for heat removal. Unit 1 is stable at normal operating temperature and pressure in Mode 3." S/G's are being feed via main feed. All other safety related systems are operable. Decay heat is via SBC system to the condenser. There is no impact on the other units. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-06-06
44273 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2008-06-05 22:56 | 2008-06-06 04:48 | 2008-06-06 | REACTOR TRIP DUE TO LOW COOLING FLOW TO MAIN GENERATOR RECTIFIER "During the performance of stator water low flow testing a turbine trip and subsequent Reactor trip occurred on low cooling flow to the main generator rectifier. An Automatic Emergency Feedwater actuation signal occurred on low steam generator level due to unit trip. This is an expected actuation for a turbine/reactor trip from 100% power. The Engineered Safety Function Actuation operated as designed. "On the Unit trip, the main feedwater pumps exhibited large rpm oscillations. Operators tripped one of the non-safety related main feed pumps, and placed the second in manual which stabilized the main feedwater system. When conditions allowed, operators placed the operating main feed pump in automatic control." All rods fully inserted successfully. All emergency systems operated as required. No PORV's or Safety valves lifted during this event. Auxiliary Feedwater system is available, but not in use at this time. RCPs are in operation transferring decay heat to steam generators. Main steam is being directed to main condenser via bypass. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2008-06-06
44272 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-06-05 | 2008-06-05 17:31 | 2008-06-05 | AGREEMENT STATE REPORT - PACKAGE EXTERNAL CONTAMINATION LIMITS EXCEEDED The State provided the following information via email: "On June 5, 2008, Thomas Gray and Associates (TGA), a California licensee, contacted the [California Radiologic Health Branch] office to report the receipt of a package containing H-3 and C-14, which exceeded the external contamination limits in 10 CFR 71.87(i). TGA received 8 drums of waste from Metabasis Therapeutics in La Jolla California on May 31, 2008, at just after 1700 hours, as TGA was closing up for the weekend. On Monday, June 2, 2008, TGA wiped the incoming shipment, and after reviewing the results of the LSC analysis on June 3, 2008, found approximately 100,000 per 100 sq-cm H-3 contamination on the external surface of one drum. There were lesser amounts of external contamination on two of the other drums. The three drums were immediately overpacked and isolated at TGA's facility, and the carrier was notified the next day, on June 4, 2008 at about 1300-1400 hours. This incident is being investigated by the San Diego County office that contracts with RHB for inspection and compliance. CA Report 060508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-06-10
44271 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-06-05 | 2008-06-05 14:08 | 2008-06-05 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The licensee discovered a leaking sealed source while performing a routine leak check. The source, a Ni-63 used in a Gas Chromatograph (SN U0915), was discovered to have loose surface contamination in the area around the source. The licensee discovered .006 microCuries of contamination in the area with a limit of .005 microCuries. There was no additional contamination found. The licensee decontaminated the device and is prepping it for disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-06-10
44270 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-06-05 10:07 | 2008-06-05 11:53 | 2008-06-05 | NEWS INQUIRY FROM LOCAL MEDIA OUTLET "Below are the responses to questions BWXT received from [a reporter] at the News & Advance of Lynchburg, VA, regarding the closure of the Barnwell Facility in South Carolina. "Q: I understand that the Nuclear Regulatory Commission has announced new guidelines for the storage of low-level radioactive material since the disposal site in Barnwell, S.C. plans to close. Does B&W ever use the Barnwell Facility for any disposal needs, or will that facility's closure affect B&W operations here in any way? If so, I'd like to discuss those potential effects and perhaps write an article about the issue." "A: Annually, the B&W Lynchburg facility generates approximately 15 to 20 cubic feet of Class B and C waste, which was disposed of at the Barnwell site in South Carolina. However, the Lynchburg facility has not been significantly impacted by Barnwell's closure." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-06-09
44269 | 0 | BUREAU VERITAS NORTH AMERICAN |  |  |  |  | 2008-06-05 06:00 | 2008-06-05 09:23 | 2008-06-06 | STOLEN TROXLER DENSITY GAUGE The licensee reported that a Troxler Moisture Density Gauge Model 3430, S/N 23648, was stolen. The gauge contains 8 mCuries Cs-137, 40mCuries Am-241/Be. The gauge was secured in a Toyota Tacoma Pickup Truck, New Jersey Tag # KV128K parked in front of the employees residence at 77 Williams Avenue in Jersey City , New Jersey. When the employee went to the vehicle this morning, he noticed the vehicle had been stolen. The employee reported it to the Jersey City Police Department (Case #17076-08). The company is requesting assistance from LLEA to aid in recovery of the vehicle and gauge. * * * UPDATE FROM TOM CHAPMAN TO JOE O'HARA AT 0915 ON 6/6/08 * * * The LLEA recovered the gauge and vehicle this morning and placed two individuals under arrest as suspects in the theft. The licensee has custody of the gauge and it appears to be intact with no damage. It will be sent off for formal leak testing/inspection. The licensee has notified Region I (J.Joustra). Notified R1DO(Henderson), FSME(Zelac), and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-06-05
44268 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2008-06-04 17:30 | 2008-06-04 21:10 | 2008-06-04 | MANUAL REACTOR TRIP FOLLOWING LOSS OF MAIN FEEDWATER PUMP "On 6/4/2008 at 17:30 hrs an unplanned manual reactor trip was initiated on St. Lucie Unit 2 from 100% power due to a trip of the 2B Heater Drain pump leading to a trip of the 2A Main Feedwater Pump and decreasing S/G levels. The Reactor was manually tripped due to decreasing Steam Generator levels. "Following the reactor trip, EOP-1, Standard Post Trip Actions, and EOP-2, Reactor Trip Recovery procedures were completed and Unit 2 was stabilized in Mode 3. All control rods fully inserted. The S/G Safety Valves lifted and the last valve reseated at 950 psig. Feedwater to the S/G was supplied by the 2B Main FW Pumps and then the Auxiliary Feedwater Pumps. Unit 2 electrical requirements are provided from offsite power. All safe shutdown equipment operated as expected. There were no major equipment failures. Unit 1 was not affected by this event. The Grid is stable." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-06-04
44267 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2008-06-04 18:11 | 2008-06-04 20:05 | 2008-06-10 | OFFSITE NOTIFICATION DUE TO FLOOD WATCH "On June 4, 2008 at 18:11 hours, Clinton Lake level reached 694 feet 0 inches (mean sea level). Normal lake level is 690 feet 0 inches. Per Clinton Power Station (CPS) procedure 4303.02, 'Abnormal Lake Level,' the CPS Main Dam - Emergency Action Plan requires that a 'Flood Watch' be declared. This resulted in a notification to the DeWitt County Sheriff's Department that occurred at 18:14 hours. Lake level continues to slowly rise due to the heavy rains received in the area for the past several days. Expected peak is approximately [694 feet 6 inches]. Mitigating measures are currently being instituted as a precautionary measure in the screen house, per CPS procedures." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1058 EDT ON 6/10/2008 FROM MAX KIER TO MARK ABRAMOVITZ * * * The licensee has terminated their flood watch at 0900 CDT. The licensee will notify the NRC Resident Inspector and has notified the DeWitt County Sheriff. Notified the R3DO (Lipa). | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-06-04
44266 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-05-07 | 2008-06-04 14:05 | 2008-06-04 | LOUISIANA AGREEMENT STATE REPORT - BROKEN TRITIUM EXIT SIGNS On May, 7, 2008, Wal-Mart reported six broken Tritium Exit Signs (TES). Three TES were located at a store in Baker, LA and three were located in a store in Baton Rouge, LA. Wal-Mart has hired Shaw Group, Inc. for its company-wide program to inventory and manage TES. Shaw Group performed decontamination of the affected stores and shipped the broken TES to a licensed source disposal facility. All the TES were located in non-public areas of the stores. LA Event Report: LA0800013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-06-09
44265 | 0 | CONNECTICUT DEPT. OF PUBLIC HEALTH |  |  |  |  | 2008-05-06 | 2008-06-04 13:59 | 2008-06-14 | MISSING NI-63 ELECTRON CAPTURE DEVICE The Connecticut Department of Public Health Laboratories reported that they were unable to locate a general license Electron Capture Device Ni-63 source. Source serial number is 3359 and was 14.5 mCi in July, 1975. The last known wipe test of the source was in 2001, conducted when the license was transferred from Thermo-Finnegan to Thermo-Fisher Scientific. The last inventory that positively identified the source was conducted in 2004. Connecticut Department of Public Health possessed the device under general license RC:708101. In May, 2008, the end-user was assembling all known unused sources for proper disposal when they determined that the Ni-63 source was missing. They have performed an extensive search of their facility but have not been able to locate the source. The end-user will be notifying Thermo-Fisher Scientific. * * * UPDATED ON 6/14/08 AT 2100 EDT BY HUFFMAN TO CORRECT NRC LICENSE INFORMATION * * * THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-06-04
44264 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-06-03 | 2008-06-04 13:36 | 2008-06-04 | AGREEMENT STATE REPORT - RADIOPHARMACEUTICALS DELIVERY VEHICLE ACCIDENT The State provided the following information via facsimile: "On June 3, 2008, a Cardinal Health delivery vehicle carrying nuclear medicine doses was involved in a vehicle accident. Some of the ammo boxes containing the syringe pigs opened, however the syringe pigs remained intact. No radioactive material was spilled or leaked during this accident." Louisiana Report: LA0800012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-06-09
44263 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-06-04 02:57 | 2008-06-04 07:58 | 2008-06-06 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On 6/04/08 at 0257, the High Pressure Coolant Injection (HPCI) system was declared inoperable. The HPCI pump was placed in service to evaluate HPCI pump start performance. The HPCI pump tripped on low suction pressure when started. An Event Response Team is assembled to investigate the cause of the low suction trip of HPCI. "Loss of the HPCI system is reportable under 10 CFR 50.72(b)(3)(v) as loss of a single train safety system required to mitigate the consequences of an accident. No additional Emergency Core Cooling Systems or Safety Related equipment was inoperable during this time period." The licensee is in a 14 day LCO due to TS 3.5.1. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/6/08 AT 1933 EST FROM LITKETT TO HUFFMAN * * * "The purpose of this notification is to retract a previous report made on 6/04/08 at 0758 (EN# 44263). The High Pressure Coolant Injection (HPCI) system was declared inoperable. The HPCI pump was placed in service to evaluate HPCI pump start performance. The HPCI pump received a momentary low suction pressure trip signal in the test configuration alignment. "Since the initial report, failure mode cause technical evaluation has determined that the HPCI was always able to satisfy its design safety function. Additional instrumentation was added and data collected from seven HPCI test runs was analyzed. As evidenced by the successful completion of its IST test and the detailed review of multiple HPCI runs, the HPCI system was always able to perform its design function because: --- HPCI restarted on its own with no operator action. --- HPCI would meet its injection time requirements. --- Required flows and required pressures were reached on all HPCI runs . "Therefore HPCI was never inoperable. "The NRC resident has been informed of the retraction." R1DO (Henderson) notified. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-06-04
44262 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-06-03 13:13 | 2008-06-03 19:26 | 2008-06-03 | LOSS OF CONTROL ROOM EMERGENCY VENTILLATION SYSTEM FOR 12 MINUTES "At 1259 hours on June 3, 2008, the Control Room authorized replacement of solenoid valve 1-VA-SV-928, affecting the Unit 1 Cable Spread Room Supply / Exhaust Fan Dampers. This work rendered two subsystems of the Control Room Emergency Ventilation (CREV) system inoperable. Because Brunswick has a shared control room, Unit 1 and Unit 2 entered Technical Specification (TS) 3.7.3, 'Control Room Emergency Ventilation (CREV) System,' Required Action 5.1 (i.e., be in Mode 3 within 12 hours). "At 1313 hours the three Control Room Air Conditioning subsystems, required by TS 3.7.4, 'Control Room Air Conditioning (AC) System,' tripped during the performance of this planned preventive maintenance activity. Unit 1 and Unit 2 entered TS 3.7.4, Required Action E.1 (i.e., enter LC0 3.0.3 immediately). At 1325 hours, following replacement of solenoid valve 1-VA-SV-928, the Control Room AC subsystems were restored to operable status and LCO 3.0.3 was exited. CREV system operability was restored at 1333 hours. "No power reduction took place as a result of the LCO 3.0.3 entry. This report applies to both Units 1 and 2 and is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The condition existed for 12 minutes. Prior to the maintenance activity, the potential for loss of the Control Room AC system and established compensatory actions to be taken in the event of the loss were briefed. Plant staff took immediate actions to return the Control Room AC subsystems to service. For the brief time the Control Room subsystems were inoperable, performance of plant personnel and equipment in the Control Room was not adversely affected. The maximum Control Room back panel temperature during this event was approximately 73 degrees F. "Operability of the Control Room AC system was restored at 1325 hours, following replacement of solenoid valve 1-VA-SV-928. CREV system operability was restored at 1333 hours. Further solenoid valve replacements affecting Control Building Emergency Ventilation have been placed on hold pending the completion of the loss of Control Room AC subsystem investigation." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-06-03
44261 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-06-03 09:30 | 2008-06-03 13:42 | 2008-06-03 | CALIFORNIA AGREEMENT STATE REPORT - LOST I-125 BRACHYTHERAPY SEEDS The following information was received from the State of California Radiologic Health Branch [RHB] via email: "On Tuesday, June 3, 2008, RHB was notified by NRC Region IV of an incident involving a California licensee. A package had been shipped by the California licensee to an Illinois licensee. The package should have contained 23 iodine-125 seeds used for brachytherapy, with activities of approximately 0.425 millicuries each. Upon receipt, the outer package was undamaged, but was reading 460 millirem/hour on contact. When the package was opened, the inner shielded container was open and some of the seeds were out of the shielded container, and at the bottom of the shipping container. The IL licensee could only account for 19 of the 23 seeds. They notified the IL radiation control program, and contacted [the carrier]. The IL licensee has surveyed the delivery truck, and the loading dock. They are in the process of surveying the [carrier's] terminal at Chicago's O'Hare airport. The California licensee that made the shipment is a small surgical center. Based on the information from IL, the package was not prepared for shipment in accordance with the instructions provided by the IL licensee, and vibrations during the shipment appear to have caused the shielded container to open during the shipment, releasing some of the seeds. RHB will be investigating the root cause of this incident and corrective actions with the California licensee." CA Incident Number 5010-060308 * * * UPDATE FROM BARBARA HAMRICK TO HOWIE CROUCH VIA EMAIL ON 6/3/08 @ 1626 HRS. EDT * * * "As of 1:02 pm PDT, we [RHB] received notification from the IL radiation control program that their licensee found the four missing I-125 seeds at the licensed facility in IL, among other packages received that morning. All seeds are now accounted for. California will continue to investigate the root cause of this incident." Notified R4DO (Whitten) and FSME EO (Chang). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-06-06