40030 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-07-29 14:01 | 2003-07-29 14:48 | 2003-07-29 | UNIT 1 DECLARED AN UNUSUAL EVENT DUE TO THE LOSS OF 500KV OFFSITE POWER "Experienced breaker failure of 500 KV 1-5 breaker. The protective function of this took out 500 KV bus section 1. All 4 KV vital buses deenergized and were repowered by the emergency diesel generators. Also 2 of 4 group buses deenergized. Auxiliary feedwater pumps started on steam generator low levels. This all resulted in a reactor trip. The source of the failure has yet to be determined. Reactor coolant temperature is being controlled by turbine bypass valves." The licensee informed state/local agencies and the NRC resident inspector. * * * UPDATE ON 7/29/03 AT 1803 EDT FROM NOEL KEMM TO BILL GOTT * * * "500 KV bus section one energized. 4KV vital bus 1B energized from offsite power by 13 station power transformer. Restoration of 1A and 1C 4KV vital buses from offsite power in progress. Initial problem appears to be a ground problem with 1-5 500 KV breaker and subsequent breaker failure relay scheme." The licensee has notified the NRC Resident Inspector and Region 1 IRC. * * * UPDATE ON 7/29/03 AT 2103 EDT FROM MARK FIOCCO TO GERRY WAIG * * * "Current Plant Status: 500 KV Bus section one energized . 4KV vital buses 1B and 1C energized from offsite power by 13 station power transformer. Restoration of 1A 4KV vital bus from offsite power in progress." The licensee has not notified the NRC Resident Inspector. The HQ Operatiions Officer notified NRC Region 1 IRC. * * * UPDATE ON 7/29/03 AT 2201 EDT FROM MARK FIOCCO TO GERRY WAIG * * * "Status Update: All 4KV vital buses energized from 13 station power transformer. Restoration of second source of offsite AC power is in progress. Making preparation to terminate Unusual Event." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 7/29/03 AT 2211 EDT FROM MARK FIOCCO TO GERRY WAIG * * * The Licensee terminated Notice of Unusual Event (NOUE) on 07/29/03 at 2211 hours EDT. The licensee has notified the NRC Resident Inspector. The HQ Operatiions Officer notified FEMA (Butch Stiendurf) and DHS (Ed Welch) of the NOUE termination. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-07-29
40029 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2003-07-28 18:54 | 2003-07-29 01:42 | 2003-07-29 | RPS ACTUATION, SPECIFIED SYSTEM ACTUATION "On July 28, 2003, at approximately 18:54 Mountain Standard Time (MST) Palo Verde Unit 3 experienced an automatic reactor trip on low DNBR [Departure from Nucleate Boiling Ratio] from approximately 98% rated thermal power due to reduced reactor coolant system flow when the main turbine tripped during a grid perturbation. Unit 3 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. The operators initiated a manual Main Steam Isolation System (MSIS) actuation, in accordance with the emergency operations procedures in response to the loss of forced reactor coolant system flow. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 3 is stabilizing at approximately 520 degrees F and 2150 psia pressure in Mode 3. The reactor coolant system remains in natural circulation with heat removal via the atmospheric dump valves and feedwater from the essential auxiliary feedwater system. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "Palo Verde Units 1 and 2 also observed the grid perturbation, but are continuing to operate in Mode 1 at approximately 98% rated thermal power. The cause of the perturbation is believed to be associated with switching in a nearby Hassayampa yard by Salt River Project. A fossil power plant in the vicinity also tripped off line during the grid perturbation event. "The [NRC] Senior Resident Inspector was informed of the Unit 3 reactor trip and this notification. The Senior Resident Inspector has arrived on-site to observe response to the reactor trip." * * * UPDATE 1437 EDT ON 7/29/03 FROM RAY BUZARD TO S. SANDIN * * * The following information was provided as an update: "This is a follow-up notification to the automatic reactor trip event reported on July 28, 2003 (ENS # 40029) for Palo Verde Unit 3. The plant remains stable in Mode 3 at approximately 585 degrees and 2250 psia. Reactor coolant system (RCS) forced circulation has been restored with two reactor coolant pumps (RCP) in operation. Heat removal remains via the atmospheric dump valves and the non-essential auxiliary feedwater pump is supplying steam generator feedwater. Off-site power has been restored and is supplying non-class loads. "An RCS leak of approximately 1.7 gallons per minute has been identified through the seal on RCP 2A. Vacuum has been restored to the main condenser and activities are in progress to cool the plant down to Mode 5, Cold Shutdown, using the steam bypass control system, to facilitate RCP 2A seal replacement. The date of restart has not been established. "The Resident Inspector was informed of this notification." Notified R4DO(Shaffer). | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-07-29
40028 | 0 | MFG, INC. |  |  |  |  | 2003-07-28 15:00 | 2003-07-28 18:34 | 2003-07-28 | POTENTIALLY DAMAGED TROXLER MOISTURE DENSITY GAUGE At approximately 1500 PDT on 7/28/03 a rubber tire compactor ran over a Troxler Model 3440, Serial No. 31827, gauge containing an 8 millicurie Cs-137 and a 40 millicurie Am-241:Be source. The sources were in the safe position at the time the incident occurred. The licensee performed rad surveys and did not observe any abnormal rad readings. The manufacturer was contacted and requested a photograph to evaluate any potential damage. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | ID | MAT | [5 empty] | 0 | 2003-07-28
40027 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-07-23 | 2003-07-28 15:45 | 2003-07-28 | INAPPROPRIATE TRANSFER OF LICENSED MATERIAL DURING REPAIR On 7/23/03, Oklahoma Department of Environmental Quality was informed by a representative of the Colorado Department of Health, a Mr. James Jarvis, that a Ludlum TWC 3250, Serial No. 6201, device containing a 1.5 curie Cs-137 source had been delivered to Stewart Instruments in Ardmore, Oklahoma for refurbishing of the electronics package. Normally, the electronic package is disconnected from the source for maintenance. However, the Colorado licensee, i.e., Tube Body Inspection located in Ft. Morgan, Colorado, [Colorado licensee No. 76201], had delivered the device intact. The Stewart Instruments principal [owner] recognized that he did not have a licensee to possess the material but, due to extensive past experience working with these devices, took appropriate steps to ensure proper handling. Oklahoma inspectors visited the storage location and were satisfied with the existing arrangements for temporary storage, i.e., locked public storage location. The Colorado licensee has been contacted and requested to remove the device from Oklahoma. Tube Body Inspection is in the process of terminating their Colorado license and is making arrangements to transfer this device to a California firm. However, according to the Oklahoma State representative, the California company is not licensed to possess this material. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2003-07-31
40026 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-07-21 11:00 | 2003-07-28 15:45 | 2003-07-28 | FIRE DAMAGE TO NUCLEAR DENSITY GAUGE At approximately 1100 CDT on 7/21/03, a fire at the Conoco Phillips Ponca City facility damaged the shielding on a Kay-Ray Model 7063P, Serial No. 24829, Density Meter containing a 200 millicurie Cs-137 sealed source. A preliminary survey of the device found a slight increase in rad levels near the top of the source holder indicating that the lead shield had melted and shifted slightly. Wipe tests found no evidence of source leakage. The manufacturer, Thermo Measure Tech, was contacted to make arrangements to remove the damaged gauge from the site on 7/30 and return it to their Round Rock, Texas facility for examination/repair. There was no radiation exposure associated with this incident to any plant personnel or emergency responders. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2003-07-31
40025 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-07-28 12:12 | 2003-07-28 14:05 | 2003-07-28 | SAFEGUARDS 1-HOUR REPORT The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 7/28/03 AT 1743 EDT FROM DAVID LANTZ TO GERRY WAIG * * * "Consistent with guidance outlined in Generic Letter 91-03, Reporting of Safeguards Events, this call [event] is being retracted." The licensee has notified the NRC Resident Inspector. Notified R4DO (Mark Shaffer), TAT (Roberta Warren). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-07-28
40024 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2003-07-28 07:30 | 2003-07-28 11:58 | 2003-07-28 | SCRAP ZIRCONIUM RODS SHIPPED TO RECYCLER IN CANADA CONTAINING U-235 FUEL PELLETS Between 3-4 weeks ago Westinghouse Hematite shipped approximately 18,000 scrap zirconium rods to Mississauga Metals and Alloys, Inc. in Brampton, Ontario, Canada for recycling. Scrap zirconium rods require a 100% visual inspection prior to shipment offsite to ensure that they do not contain any fuel pellets. Last Thursday on 7/24/03, the recycler discovered thirty-six (36) U-235 pellets (4.2 w/o) after processing about 25% of the scrap rods. The individual at Mississauga responsible for contacting Westinghouse did not return to work until Monday and, thus, Westinghouse was not informed until 0730 CDT on 7/28/03. The pellets contain a total of six (6) grams U-235. Westinghouse is dispatching staff to the recycling facility to assist in determining appropriate corrective actions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 3 | MO | FUE |  | 74.11(a) |  |  |  | 0 | 2003-07-29
40023 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-07-26 21:39 | 2003-07-27 02:14 | 2003-07-27 | LOSS OF POWER TO 4160 V BUS DUE TO A GROUND FAULT "A ground fault on the tertiary winding of 10 TR Substation Transformer resulted in a loss of power to Unit 2 Safeguard 4160 V Bus 26. Bus 26 Load Sequencer automatically initiated voltage restoration to re-power the bus from 2RY Station Reserve Transformer. Load Sequencer operation also generated automatic load rejection and load restoration of Bus 26 loads." All safeguards loads on Bus 26 that would have been rejected by the sequencer were not running. Containment fan cooling units were restored. Manually restored reactor coolant pump seal injection. Tertiary Cooling Systems that provide flow to the cooling towers are still off. All other systems functioned as required. The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-07-27
40022 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-07-25 13:18 | 2003-07-25 14:54 | 2003-07-25 | AUTOMATIC AUXILIARY FEEDWATER ACTUATION DUE TO MAIN FEEDWATER PUMP TRIP While at 12% power, the operating Main Feedwater Pump "2-B" tripped on low suction pressure, possibly due to an entrained air bubble in one of the feedwater heaters. This resulted in an automatic AFW signal due to a loss of all feedwater (the "2-A" MFW was in the tripped condition since it was not required). Operators manually tripped the Main Turbine to minimize steam demand and stabilize the plant. All systems functioned as required. The licensee notified the NRC resident inspector. | 0 | 1 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Startup | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-07-25
40021 | 0 | FEDERAL MOGUL |  |  |  |  | 2003-07-25 | 2003-07-25 14:30 | 2003-07-25 | SOURCE MISSING FROM FIXED LOCATION GENERAL LICENSE THICKNESS GAUGE Federal Mogul Corporation at their South Bend, Indiana facility produces teflon coated pistons. In the production process, a fixed gauge manufactured by Oxford Instruments is employed to measure the teflon coating thickness using a beta backscatter probe. The gauge was last calibrated on 12/02 at which time the technician noted two (2) screws were missing on the faceplate. However, no repairs were made at that time. Earlier this year technicians replaced the missing screws not realizing that the source had fallen out and was no longer in the instrument. A survey and search of the area did not identify or recover the source. The instrument is a model GM-2, S/N 610130P, containing less than 1200 microCuries Promethium-147. Call the Headquarter Operations Officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-07-25
40020 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2003-07-14 | 2003-07-25 13:09 | 2003-08-07 | AGREEMENT STATE REPORT INVOLVING MISSING IODINE-125 SEEDS On 7/22/03 Rex Healthcare personnel discovered that five (5) I-125 seeds (activity 0.384 milliCuries/ea for a total of 1.9 milliCuries) were missing. The licensee conducted a search of the area between 7/22 and 7/24/03 with negative results. NC Incident No.: 03-32 *****UPDATE ON 8/7/03 AT 1405 FROM JEFFRIES TO LAURA***** At 10:30 EDT on 8/7/03, the licensee found the 5 missing I-125 seeds in the hospital. The seeds were found contained in a loading apparatus between two autoclave valves. The licensee is doing an additional review to evaluate any potential radiological exposures. Notified NMSS (D. Broaddus) and R2DO (S. Cahill). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2003-07-30
40019 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-07-25 09:00 | 2003-07-25 13:00 | 2003-08-13 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "[The licensee] got in late from work, and failed to take the gauge to storage location but instead left the gauge in the back of his pickup and covered it. The gauge was covered inside the camper shell. Sometime between 11 PM on 7/24/03 and 1:00 AM on 7/25/03, the pickup was stolen from it's parking location. The Sacramento Police were notified on 7/25/03 and the licensee will be placing an advertisement in the Sacramento Bee [newspaper], offering a reward for the stolen gauge. "The Stolen gauge was a CPN 131, Model 503 DR, serial number H35126508 containing 50 millicuries of Americium 241 Beryllium." *****UPDATE 8/12/03 AT 12:46 GREGER TO LAURA***** "The stolen nuclear gauge reported in Event # 030603 [NMED Database number] was found in a business dumpster in Sacramento, the city in which it was stolen, on August 3, 2003 by a member of the public. Both the gauge and the truck in which the gauge was stored overnight (inside a camper shell) was stolen from a private residence. The truck has not been recovered. The gauge was found inside its protective transportation case. The lock on the transportation case had been removed, but the gauge remained locked (radioactive source not exposed). The individual finding the gauge stated he had seen the newspaper ad offering a reward for return of the gauge. The gauge will be tested for radioactive leakage before being returned to service. Enforcement action is being taken against the gauge company for failing to properly store the gauge." Notified NMSS (J. Hickey) and R4DO (Phil Harrell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-07-30
40018 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-07-19 | 2003-07-25 12:17 | 2003-07-25 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED OPERATOR A licensed operator tested negative during a for-cause test after reporting he had taken a controlled substance without a prescription. The licensee has removed the individual from watchstanding duties and will determine corrective actions. The licensee will inform the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2003-07-25
40017 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-06-25 12:00 | 2003-07-25 11:03 | 2003-07-25 | INCORRECT PATIENT GIVEN A DOSE "On June 25, 2003, a nuclear medicine technologist gave a 243 microcurie iodine-123 capsule to the wrong patient. There were two patients with the same last name and middle initial but different first names in the outpatient waiting room. The wrong patient responded when the technologist took the patient into the nuclear medicine department, explained the procedure, and had him fill out a thyroid questionnaire. After the patient swallowed the capsule, he informed the technologist that he was not at the hospital for a thyroid study. The patient was informed of the misadministration. The licensee did not report whether the referring physician was informed. "Cause: The technologist failed to fully identify the patient. "Corrective Action: The technologist was counseled. To prevent a recurrence, the technologists will question the patient's full name and match their date of birth in the future. The technologist will also ask the patient what examination or procedure they are scheduled for before initiating any test." Texas Incident No.: I-8042. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-07-30
40016 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-07-08 10:08 | 2003-07-24 17:25 | 2003-07-24 | REACTOR CORE ISOLATION COOLING [RCIC] RENDERED INOPERABLE DURING SURVEILLANCE TESTING The following is a portion of a fax submitted by the licensee: "This ENS notification is made to report that on July 8, 2003 at 10:08 PDT Reactor Core Isolation Cooling was rendered inoperable when its inboard containment isolation valve inadvertently closed during the performance of a routine surveillance procedure. The surveillance test was discontinued and plant operators entered the appropriate Technical Specification Action Statements. The RCIC system was restored to its normal standby lineup and declared operable within one hour. "Initially the event was not considered reportable to the NRC based on guidance contained in NUREG 1022, 'Event Reporting Guidelines,' and NRC Regulatory Issue Summary (RIS) 2001-14, 'Position on Reportability Requirements for Reactor Core Isolation Cooling System Failure.' RIS 2001-14 indicates that RCIC failures are not reportable unless the RCIC system is specifically credited in the plant's Final Safety Analysis Report for mitigating the consequences of a control rod drop accident (CRDA). The initial conclusion was that RCIC at Columbia Generating Station was mentioned but not credited in the FSAR Chapter 15 Control Rod Drop Analysis. After further review, it has been decided that the current licensing basis and docketed correspondence is not clear regarding RCIC credit for CRDA mitigation. Therefore, Columbia Generating Station has decided to conservatively report this event under 10 CFR 50.72(b)(3)(v)(D). A follow-up LER will be issued under 10 CFR 50.73(a)(2)(v)(D)." The licensee's corrective action is under review. The licensee has notified the NRC Resident Inspector. | 73 | 0 | 0 | 73 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-07-24
40015 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2003-07-23 23:00 | 2003-07-24 15:57 | 2003-07-24 | LEAK IN FIRE PROTECTION SYSTEM TO HF [HEXAFLUORIDE] MITIGATION TOWERS During a training exercise at the HF mitigation towers of the Honeywell Metropolis Site, a leak was discovered in the Fire Protection System that feeds water to the towers. The leak occurred in underground water piping between the Feeds Material building and the Fluorine Production Plant. Personnel made initial leak discovery by water coming up to the surface. The Fluorine Production Plant was not in operation at the time of the leak. Upon discovery, plant personnel isolated the leak by closing system valves. The Fluorine Production Plant has been isolated from the Fire Protection System by these closures. Compensatory measures (fire watch, temporary piping) are in place to ensure fire protection in the Fluorine Production Plant during repair of the piping. All safety systems for licensed material at the plant fed by the Fire Protection System are still operable. The repair is estimated to take 2-3 days. There was no chemical or radiological release. The licensee is investigating the cause of the leak. The licensee notified their NRC contact at Paducah GDP. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2003-07-24
40014 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2003-07-24 05:57 | 2003-07-24 09:32 | 2003-07-24 | AUTOMATIC REACTOR SCRAM DUE TO POWER SUPPLY FAILURE "A power supply failed for three of four main steam line flow instruments for the feedwater level control system. Feedwater level control system responded to the sensed reduction in main steam flow by reducing feedwater flow. The feedwater flow reduction resulted in the reactor recirculation system pumps downshifting to slow speed. At 0557, the reactor protection system automatically tripped on Oscillation Power Range Monitors due to a power/flow mismatch. The operators did not observe any power oscillations. The plant is currently stable with reactor pressure being controlled by the main steam bypass valves and reactor level is being maintained by the feedwater system. " "The reason for the loss of the power supply failure is unknown at this time." Reactor power was initially at 100% when the power failure occurred. After the reactor recirculation pumps downshifted to slow speed reactor power was at 50% when the automatic reactor scram initiated. All rods fully inserted into the core. All emergency core cooling systems and the emergency diesel generators are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-07-24
40013 | -1 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-07-23 10:52 | 2003-07-23 11:45 | 2003-07-30 | LOSS OF CONTROL OF SAFEGUARDS MATERIAL Discovered vulnerability in control of safeguards material for which compensatory measures had not been employed. Immediate compensatory measures taken upon discovery. Licensee contacted NRC Region I (Bellamy) and the State of Connecticut. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 7/30/03 AT 1641 FROM JON BOWER TO BILL GOTT * * * "On July 23, 2003, Haddam Neck reported a loss of control of safeguards material in accordance with 10 CFR 73.71(b)(1). After further review, this event was determined to be not reportable. This determination is consistent with Generic Letter 91-03, "Reporting of Safeguards Events." The event did not involve: the loss of safeguards information that could significantly assist an individual in gaining unauthorized or undetected access to a facility; or that would significantly assist an individual in an act of radiological sabotage or theft of special nuclear material. Thus, Haddam Neck retracts Event Number 40013." Notified R4DO (Noggle) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-07-23
40012 | 0 | U. S. AIR FORCE |  |  |  |  | 2003-07-23 | 2003-07-23 07:49 | 2003-07-23 | LOST OR STOLEN TRITIUM SOURCE EXIT SIGN - U. S. AIR FORCE The licensee reported that an exit sign containing an estimated 20 curie tritium source was determined to missing on July 18, 2003. The exit sign is missing from building 155, Cannon Air Force Base, Clovis, New Mexico. The exit sign serial number is 188945. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-07-23
40011 | 0 | THERMO ELECTRON CORPORATION |  |  |  |  | 2003-05-30 | 2003-07-22 18:13 | 2003-07-22 | PART 21 NOTIFICATION DUE TO POSSIBLE DEFECT WITH THERMO WESTRONICS SERIES 2100C RECORDERS The following report was received via fax: "July 21, 2003 "Subject: Thermo Westronics Model 2100C Series Recorders "This letter is notification of a possible defect associated with Thermo Westronics Series 2100C recorders. The Series 2100C is a DIN size programmable chart recorder utilized in control room applications of Nuclear Power Plants. The recorders in question were manufactured under the Thermo Westronics 10CFR50 Appendix B Quality Program between August 2002 and January 2003. "On or about May 30, 2003, Thermo Electron determined that a random reset anomaly could possibly occur on the Series 2100C recorder. This anomaly surfaced during the manufacture of three (3) commercial grade Series 2100 recorders. When the reset occurs, the recorder must be re-initialized to resume normal function. "The root cause of the anomaly has been traced to a timing issue between the CPU Printed Circuit Board Assembly (PCBA) and the Memory Module. A 27C256 EPROM, used as a decoder on the Memory Module, has changed manufacturers several times during the life of this product. The EPROM as produced by the original manufacturer is no longer available. "Newer versions of this 27C256 EPROM typically function at faster speeds. The faster chip speed can cause a delay in the transition from "send" to "receive"' on the CPU Module and thereby result in the reset. This reset event is random and does not occur on every recorder. "After engineering evaluation, Thermo Electron has incorporated a modification to the CPU PCBA to ensure compatibility with the faster EPROM on the Memory Module. This modification eliminates the timing delay and subsequent possibility of the reset. Future shipments of this CPU Module shall incorporate this modification. "To ensure compatibility on previously installed recorders, the Memory Module shall only be offered as part of a kit that includes the newer version CPU PCBA. "The scope of this notification includes ten (10) Series 2100C safety related recorders, all of which were thoroughly tested and did not exhibit this reset at the time of shipment. However, since it is not possible to determine the exact manufacture date of the 27C256 EPROM used on these recorders, this notification is being issued. . . [Table removed] . "Thermo Electron shall notify listed customers and make arrangements to implement the design modification, either by rework at the Thermo Electron - Houston facility, or by providing replacement kits to the customer site. It is estimated that rework associated with the design modification should be completed within sixty (60) days, or as soon as Thermo Electron has been contacted by the identified customers." The affected sites include Laguna Verde, Mexico, Millstone, Catawba, and McGuire. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2003-07-22
40010 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2003-07-22 13:45 | 2003-07-22 17:33 | 2003-07-22 | AUTOMATIC REACTOR SCRAM DUE TO MAIN GENERATOR PROTECTIVE RELAY ACTUATION "With Unit 2 operating at 100% power, a Main Generator protective relay actuation occurred causing a Main Turbine trip and automatic Reactor Protection System (RPS) actuation. The RPS signal received was Main Turbine Control Valve Fast Closure. RPS functioned as designed and all control rods fully inserted. Group II and III primary containment isolations went to completion and Standby Gas Treatment automatically started when reactor level reached the setpoint of 1" reactor level. "At 1358, with Standby Gas Treatment System in operation, Main Steam Tunnel temperatures rose to the Group I isolation setpoint and a Group I isolation occurred. There was not a steam leak that caused the Group I isolation. Following the Group I isolation, reactor level again lowered to the 1" RPS actuation and Group II/III isolation setpoint. All control rods were fully inserted when this RPS actuation occurred. With containment isolated, HPCI and RCIC were used to control reactor level. "At 1615 hours, while transitioning reactor level control to condensate, a RPS actuation, Group II, and Group III isolation occurred when reactor level reached the setpoint of 1". All control rods were fully inserted at the time. All containment isolation valves that were opened following the initial actuation, isolated as expected. "All primary containment parameters are currently normal. The crew has stabilized the plant and plant recovery actions have commenced. The cause of the Main Generator protective relay actuation is not known at this time." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-07-22
40009 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-07-22 14:56 | 2003-07-22 17:24 | 2003-07-22 | OFFSITE NOTIFICATION TO OTHER GOVERNMENT AGENCIES CONCERNING MINOR OIL SPILL "On 7-22-03 at 1100, approximately 1 gallon of fuel oil was spilled during a diesel generator fuel oil transfer surveillance test due to a leak at a hose connection. It is estimated that 1 quart of fuel oil went into a nearby floor drain. As a result, a visible sheen of oil was observed on a swamp area on plant site. This is a reportable spill to government agencies since there is a visible sheen on "waters of the United States". The US Coast Guard National Response Center was notified at 1456 on 7/22/03 and the Alabama Department of Environmental Management was notified at 1510 on 7/22/03." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-07-22
40008 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-07-22 09:48 | 2003-07-22 16:10 | 2003-08-27 | HELB DOOR NOT LATCHED AS REQUIRED DUE TO PERSONNEL ERROR "A High Energy Line Break (HELB) door was not latched as required. This condition is being reported as an event that could have prevented the fulfillment of a safety function in accordance with 10CFR50.72(b)(3)(v)(A). The door is currently closed." The HELB door which separates two critical Motor Control Center [MCC] areas was unlatched for less than two (2) minutes. The licensee will inform the state representative and has informed the NRC resident inspector. * * * RETRACTION on 08/27/03 at 1216 EDT by R. Sand to John MacKinnon * * * Because plant safety was not significantly degraded, this event is not reportable under the unanalyzed condition criteria based on: (1) the door in either event was in an uncontrolled condition for less than one minute, (2) the door was not materially affected, only operated improperly, (3) the PRA significance of the event was low, and (4) the HELB Barrier door was not open for a period longer than is allowed by station procedural guidance. R3DO (C. Miller) notified. The station continues to review the event in the station's corrective action program. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-07-22
40007 | 0 | WATERFORD | 3 |  |  | [3] CE | 2003-07-21 14:15 | 2003-07-22 11:13 | 2003-07-23 | FITNESS FOR DUTY This is a corrected report reissued to provide the information supplied by the licensee. "A licensed operator tested positive for an illegal substance during a random Fitness for Duty (FFD) test. The results of this test have been reviewed and confirmed by the site's Medical Review Officer. "Immediate action was taken to remove the individual's access to the plant. Other actions required by 10 CFR 26.27(b)(2) and company procedure are also being taken. "A review of the employee's work is being conducted. The individual has not stood watch as a Senior Reactor Operator since 4/18/03. "The NRC Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.73 |  |  |  | 0 | 2003-07-22
40006 | 0 | LANG BROTHERS, Inc. |  |  |  |  | 2003-07-21 07:30 | 2003-07-21 09:39 | 2003-07-21 | STOLEN TROXLER MOISTURE DENSITY GAUGE On Monday morning, July 21, 2003 around 0730 EDT it was discovered that a Troxler Model # 3440 (serial # 18908) moisture density gauge had been stolen from a work site in Parkersburg, WV. The Troxler moisture gauge had been double locked inside a cabinet. Workers reporting to the job site had found that both locks had been pried off and the moisture density gauge was missing. The gauge was in its case. The moisture density gauge was last seen Friday evening, July 18, 2003. The moisture density gauge is owned by Lang Brothers, Inc. which is located in Bridgeport, WV. The Radiation Safety Officer (RSO) did not have the license number of the stolen moisture density with him. He did say that he would notify the local police that the moisture density gauge had been stolen. Troxler Model # 3440 contains 10 millicuries of cesium-137 and 40 millicuries of americium-241/beryllium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | WV | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-07-24
40005 | -1 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2003-07-18 | 2003-07-18 12:13 | 2003-11-18 | PART 21 REPORT INVOLVING IMPACT OF FUEL CHANNEL BOW ON CONTROL ROD BLADES The following is a portion of text received as a fax: "July 18, 2003 "MFN 03-045 "Subject: 60 Day Interim Notification: Impact of Fuel Channel Bow on Control Rod Blade Deviations "Reference: Letter from Jason Post (GENE) to USNRC, 'Interim Surveillance Program for Fuel Channel Bow Monitoring', MFN 03-030 Revision 1, April 30, 2003 "This communication is to inform you that GE Nuclear Energy (GENE) has been evaluating a potentially reportable condition (PRC) on the impact of fuel channel bow on control rod blades. The original channel bow evaluation for increased fuel channel - control rod blade interference did not consider previously evaluated deviations in the control rod blade. Channel bow can cause increased deflection and stresses in control rod blades, which must be considered in control rod blade deviation evaluations. The PRC evaluation is limited to control rod blades delivered to those plants identified in the referenced letter, where an interim surveillance plan for channel bow monitoring is recommended, because those are the only plants where there is a concern about increased fuel channel - control rod blade interference. "As described in the referenced letter, it was determined that BWR/6 and BWR/4 & 5 C-lattice plants with Global Nuclear Fuel (GNF) thick/thin channels potentially have increased channel bow that can cause fuel channel control rod blade interference. An interim surveillance program was provided to augment the surveillance requirements in the plant Technical Specifications until other actions, which mitigate or limit the potential for control rod - fuel channel interference due to channel bow can be identified and implemented. This surveillance program provides early indication of potentially degraded operational performance and assurance that action is taken before reaching excessive levels of control rod interference. This surveillance plan is limited to BWR/6 and BWR/4&5 C-lattice plants with GNF thick/thin channels and GENE control rods. There have been no indications of excessive interference on BWR/2, 3 and 4 D-lattice plants, and as a result, they are excluded from the interim surveillance program. "The PRC evaluation was initiated by GENE on May 19, 2003. GENE will not have completed the evaluation by July 18, 2003, when the 60 day evaluation period expires. Therefore, GENE is submitting this 60 Day Interim Notification under 10CFR21.21(a)(2) to inform the NRC that we are working on the issue, and to commit to report the results of the evaluation no later than September 23, 2003." GE Nuclear Energy has identified the following as affected plants: Clinton, Nine Mile Point 2, Fermi 2, Grand Gulf, River Bend, Limerick 1 & 2 and Perry 1. *****UPDATE ON 9/24/03 AT 0055 FROM POST TO LAURA***** GE submitted its 60 day update letter which indicated no change from previously submitted information. * * * UPDATE ON 11/18/03 @ 2115 BY JASON POST TO GOULD * * * This communication is to inform you that GE Nuclear Energy (GENE) has completed the evaluation of the potentially reportable condition (PRC) identified in References 2 and 3 and has concluded that it is NOT a Reportable Condition under 10CFR21. Channel bow can cause increased deflection and stresses in control rod blades. The impact of channel bow on as-designed control rod blades was considered when the surveillance program identified in Reference 1 was developed_ However, the evaluation did not consider known control rod blade deviations from as-designed conditions that had previously been addressed. The evaluation to determine the impact of channel bow on control rod blade deviations, as reported to the NRC in References 2 and 3, has now been completed. The evaluation concluded that the increased loads from channel bow do not impact the structural integrity of control rods with known deviations from as-designed conditions. Therefore, it does not produce a significant safety hazard or lead to violation of a technical specification safety limit. As described in the Reference 1 letter, it was determined that BWR/6 and BVVR/4 & 5 C-lattice plants with Global Nuclear Fuel (GNF) thick/thin channels are potentially susceptible to increased channel bow that can cause increased fuel channel - control rod blade interference. A surveillance program is recommended per Reference 1 for the potentially susceptible 8 plants listed above. This evaluation examines known deviations from the as-designed condition for original equipment manufactured (OEM) control rod blades and for "DuraLife" and "Marathon" replacement blades in the potentially susceptible plants. The PRC evaluation was initiated by GENE on May 19, 2003. GENE reported the results of the evaluation for OEM blades and "DuraLife" replacement blades in Reference 3. GENE has now completed the evaluation applicable to "Marathon" replacement blades. These evaluations indicate that there is no change from the previous information provided in Reference 1. Therefore, GENE is submitting this Final Notification to inform the NRC that the evaluations have been completed, and to report the GENE conclusion that this is NOT a Reportable Condition per 10CFR21. References: 1. Letter from Jason Post (GENE) to USNRC, "Interim Surveillance Program for Fuel Channel Bow Monitoring", MFN 03-030 Revision 1, April 30, 2003 2. Letter from Jason Post (GENE) to USNRC, "60 Day Interim Notification: Impact of Fuel Channel Bow on Control Rod Blade Deviations," MFN 03-045, July 18, 2003 3. Letter from Jason Post (GENE) to USNRC, "60 Day Interim Notification: Impact of Fuel Channel Bow on Control Rod Blade Deviations," MFN 03-103, September 23, 2003 Notified Reg 1 RDO(Rogge), Reg 3 RDO(Lipa), Reg4 RDO(Kennedy), and NRR(Foster) See related events #39634 and 39806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-07-18
40004 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-07-17 03:35 | 2003-07-17 16:00 | 2003-07-17 | 24-HOUR NRC 91-01 BULLETIN NOTIFICATION INVOLVING LOSS OF CRITICALITY CONTROL The following is a portion of text from a fax submitted by the licensee: "Pump-Out to UNBSS Without Sample Results. "Reason for Notification: An operator pumped out a batch from the clean dissolver to the uranyl nitrate bulk storage tank prior to receiving the required sample results for grams U-235 per liter, percent free acid, and pH. "Double Contingency Protection: Double contingency protection for the bulk storage tank is based on concentration control. Concentration control is based upon maintaining uranyl nitrate that is pumped to the tanks at less than 5 grams U-235/liter. The pH is maintained at a value of less than 2 to ensure that the uranyl nitrate stays in solution. The percent free acid is maintained at greater than 4 percent to ensure that the uranyl nitrate stays in solution and depresses the freezing temperature of the solution to prevent concentration by freezing. "It has been determined that less than previously documented double contingency protection remained for the system and that greater than a safe mass was involved., but a sufficient number of controls that were lost were restored within 4 hours. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criteria for a 24-hour notification. "As Found Condition: See 'Reason for Notification' above. "Summary of Activity: (1) Pump outs to the bulk storage tanks were stopped, (2) Samples for grams U-235/liter, pH, and %free acid were taken to ensure the tanks were in specification, (3) Before the end of the shift, sample results for grants U-235/liter, pH, and %free acid were determined to be acceptable. "Conclusions: (1) Loss of double contingency protection occurred, (2) Greater than a safe mass was involved, (3) At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved, (4) The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures, (5) Notification was the result of an event, not a deficient NCS analysis, (6) A causal analysis will be performed." The licensee attributes the cause of this incident to personnel error. The licensee will inform both NRC Region 2 and the NRC Headquarters PM. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-07-17
40003 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-07-17 | 2003-07-17 15:22 | 2003-07-17 | EPA NOTIFIED OF CHEMICAL RELEASE ONSITE The following is a portion of text in a letter submitted by the licensee on 7/17/03 to the U.S. EPA Region III: "On July 16, 2003 approximately 650 gallons of aluminum nitrate solution leaked from a flange on the chemical feed line from the storage tank at the tank farm. The flange was located immediately outside of the tank containment structure. Apparently the flange gasket failed from excessive pressure due to thermal expansion. The aluminum nitrate solution has a Ph of approximately 1 S.U. due to residual nitric acid from the manufacturing process of that chemical. The majority of the solution leaked onto a grass covered area next to the tank farm. A portion of the solution leaked into the tank containment area as well as an adjacent concrete trench. The limits of the leak were determined by measuring the Ph of the ground with litmus paper, and the leak was neutralized with sodium bicarbonate powder. A layer of topsoil will be removed and disposed of accordingly. Based on the litmus paper Ph test results, there was no evidence that the leak entered a nearby storm drain. "An Unusual Incident Report was written and is currently being evaluated by our Environment, Safeguards, Health & Safety Department as well as the process engineers to better define the cause of the incident and to prevent similar incidents in the future. The flanged connection on the aluminum nitrate line will be replaced by a welded connection, and all other flange gaskets will be replaced with Teflon gaskets. All flanged connections are now within the tank containment structure." The chemical release has no radiological implications. The licensee informed the NRC Headquarters PM (Stout) and will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 1 | 2003-07-17
40002 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-07-17 | 2003-07-17 10:42 | 2003-07-17 | AGREEMENT STATE REPORT - TWO LOST EXIT SIGNS THAT CONTAIN TRITIUM At 1042 EDT on 7/17/03, a Nebraska Radiation Program Radiation Health Specialist reported that a licensee, Hastings State Bank, could not account for two tritium-based exit signs. The bank is buying a building that previously housed a bank. Nebraska State Radiation Program billed the new bank for the materials license associated with the exit signs. The new branch manager of the Hastings Bank was unable to locate the exit signs in question. In April of 1989, each sign contained 4.7 curies of tritium. The State of Nebraska will be visiting the site when the new bank opens in August. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-07-22
40001 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-07-16 22:08 | 2003-07-17 06:57 | 2003-07-17 | UNDECLARED UNUSUAL EVENT At 0501 CDT on 07/17/03 the shift manager determined that a condition existed for 10 minutes the previous evening which met the emergency plan criteria but no emergency was declared. The basis for the emergency class no longer existed at the time of discovery. Upon discovery he notified the NRC Operations Center and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW | [5 empty] | 0 | 2003-07-17
40000 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-07-16 | 2003-07-16 15:18 | 2003-07-16 | 4 LABORATORY SOURCES DISCOVERED MISSING AFTER AN INVENTORY CHECK OF OVER 1200 SOURCES. AGREEMENT STATE REPORT FROM THE STATE OF TEXAS: TEXAS INCIDENT No. I-8037 Licensee: Haliburton Energy Services located in Houston, Texas. Licensee No. L00442-004 "During an exhaustive inventory of over 1200 sources stored at the facility, it was determined that 4 laboratory sources that had formerly belonged to Sperry-Sun, were determined to be missing. The RSO thought that the report required was for a 30- day written report and submitted the same to this Agency. However, the activity of the missing sources are in excess of the reporting requirement for 1000 time the Appendix C value, thus requiring an Immediate Report. The sources from the closure of Haliburton's Fort Worth site, and acquisition of Sperry-Sun sources were being combined and placed in the new Houston storage facility. The four sources: 13 millicuries, Cs-137, Serial No. B-404, Model VD-HP; binary source, 0.01 millicuries Am-241/0.005 millicuries Cs-137, Serial No. LL-223, Model No A3201; binary source, 0.001 millicuries Am-241/0.005 millicuries Cs-137, Serial No. LL-224, Model No. A3201; and 0.01 millicuries, Am-241, Serial No. KK-691, Model No. A3201. All sources are Licensed to Texas Licensee L00442-004, Haliburton Energy Services, Houston, Texas. An exhaustive search of the radioactive materials use/storage locations and non-restricted locations in Building G (MTL); Building C, Manufacturing; Building E, Training; Test pits, TRAC Lab, Building DD, the old Sperry source storage bunker; QC CTN:Lab, Building S and Building AA, failed to locate the sources. This inventory discrepancy has caused Haliburton Energy Services to incorporate all sources into a central database with the capability to track movement of radioactive materials globally." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-07-21
39999 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-07-12 | 2003-07-16 10:57 | 2003-07-16 | STATE OF OHIO REPORTED AN UNDERDOSE DURING A SINUS TREATMENT BY A LICENSEE. During treatment of a patient for a sinus tumor at the James Cancer Center, an intended dose of 1,750 rads of Ir-192 was to be administered, however the patient only received 750 rads. The patient and physician were notified on 7/16/03. They are still investigating the root cause of this medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-07-21
39998 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-07-15 16:00 | 2003-07-15 19:05 | 2003-07-15 | TEMPORARY PROCEDURE TO COMPACT AIR FILTER PAPER NCS FUNCTION WAS NOT REVIEWED OR APPROVED NRC BULLETIN 91-01 24 HOUR NOTIFICATION "Time and Date of Event 23 Jan 2003 - 19 Mar 2003 "Reason for Notification "On January 23rd 2003, the process engineer generated a temporary procedure to compact air filter paper, and did not place the NCS function on review or approval. The temporary procedure was approved and the process was performed, in violation of the bounding assumptions of the LLRW ISA (compact filter paper was the end product). The process engineer later placed the same process in a formal operating procedure that was reviewed by NCS. On February 20th, the NCS reviewer withheld approval of the formal operating procedure since the "proposed" process would violate the bounding assumptions of the ISA and, therefore, require further analysis and an ISA license annex revision before approval could be given. The NCS engineer informed the process engineer that such analysis was necessary and it was placed in the NCS work queue. The process engineer did not inform the NCS engineer that the process had already been performed. When starting the safety analysis on June 30th 2003, the NCS engineer found records of completed filter paper and subsequent investigation revealed the temporary procedure on July 1, 2003. The temporary procedure had been retired on March 19th, although drums of compacted filter media continued to be created in the item control system into at least April 2003. "Double Contingency Protection "The compaction unit is authorized to be used for volume reduction of noncombustible material that was previously determined to be free of gross contamination in the originating area, and verified to be free of gross contamination by the URRS operator before being placed into the compactor. A criticality would be possible only if an excessive accumulation of uranium occurred with sufficient moderating materials. "The compactor system was operated outside there documented safety basis stated in the ISA. A 24- hour notification, therefore, is being issued. "As Found Condition "Drums contained a range of grams U-235 values from near zero to approximately 50 grams U-235. These low gram U-235 values reflect the low Uranium loading in the filter media. The filter paper media is removed from the filters and "tapped" to remove "loose" material, but is not considered to be "free of gross contamination" due to ability to retain imbedded material. "Summary of Activity "1. The process had already been stopped when discovered. "2. The content of each drum was reviewed and found to contain less than 50g U-235. "3. Selected drums were opened and visually inspected. All were in a safe condition. "Conclusions "1. Much less than a safe mass was involved. "2. At no time was the health or safety to any employee or member of the public in jeopardy. "No exposure to hazardous material was involved. "3. The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. "4. Notification was the result of an event, not a deficient NCS analysis. "5. A causal analysis will be performed." The certificate holder informed NRC Region 2 (M. Crespo) of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-07-15
39997 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-07-15 15:15 | 2003-07-15 16:35 | 2003-07-25 | 22 OFFSITE EMERGENCY SIRENS INOPERABLE "South Texas Project is making this eight hour notification IAW 50.72 (b) (3) (xiii) for "Loss of Offsite Response Capability". Currently, due to local power outages, 10 sirens are available and 22 sirens are not available. Compensatory actions are in place to alert the public if necessary. There are three compensatory actions: local law enforcement officials are prepared to respond to areas where the sirens are not available to alert the public, a community alert network is in place to activate a phone tree to local residents and tone alert radios with residents. Power restoration and recovery actions are in progress." State and local officials will be notified of this event by the licensee. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 7/25/03 AT 1112 EDT FROM SCOTT HEAD TO GERRY WAIG * * * The licensee reported that all 22 of the sirens previously reported as "not available" have been returned to service as of 0900 CDT on 7/24/03. All Offsite Notification Sirens are operable and available at this time. Notified NRC Region 4 DO (Troy Pruett). The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-07-15
39996 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2003-07-15 13:40 | 2003-07-15 15:29 | 2003-07-15 | AUTOMATIC REACTOR TRIP "On 07/15/03 at 1340hrs [CDT], the Unit 1 reactor automatically tripped from 100% power upon loss of G-06 rod drive motor-generator (MG) set. Automatic transfer of the G-06 MG set to G-07 MG set did not occur. Automatic initiation of the auxiliary feedwater occurred. The cause of the failure of the G-06 rod drive MG set is being investigated. All systems operated as expected." G-06 rod drive MG set was carrying the load and running in parallel with rod drive MG set G-07 when it started to smoke. Rod drive MG set G-06 did not automatically transfer its load to rod drive MG set G-07. No fire was seen and rod drive MG set G-06 was electrically secured. All rods fully inserted into the core. The first out annunciator for the reactor trip was overtemperature delta temperature trip. The Turbine Driven and both Motor Driven Auxiliary feedwater pumps automatically started as expected. Currently the licensee is using one train of main feedwater to maintain proper steam generator water level. All emergency core cooling systems and the emergency diesel generators are fully operable if needed. The electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-07-15
39994 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-07-13 22:00 | 2003-07-14 01:57 | 2003-07-14 | HPCI SYSTEM INOPERABLE AT FERMI 2 "On 7/13/2003 at 2200 hours, while performing the HPCI Pump Time Response and Operability Test, the HPCI main steam supply outboard containment isolation valve, E4150F003, failed to close. The E4150F003 was declared inoperable and the HPCI main steam supply inboard containment isolation valve, E4150F002, was closed and de-activated per Technical Specifications. Isolating the HPCI main steam supply rendered HPCI inoperable. The E4150F003 the was documented per the site corrective action process. All other ECCS equipment and RCIC are operable. This is being reported under 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. The licensee entered the applicable 14 day LCO for the HPCI system inoperability and initiated maintenance troubleshooting. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-07-14
39993 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-07-11 20:09 | 2003-07-11 23:57 | 2003-07-11 | MANUAL SAFETY INJECTION DUE TO PRESSURIZER LOW LEVEL Unit 2 was in mode 3 with the main feedwater regulating valve controllers in automatic. Upon closure of the reactor trip breakers in preparation for critical approach, the main feed regulating valves opened causing a cooldown of the reactor coolant system (RCS) and pressurizer low level. The operator response sequence included a manual reactor trip and manual safety injection. There was no actual safety injection and the charging pumps made up for the RCS shrinkage due to the cooldown. Steam generator levels remained within their normal band range. A shutdown margin calculations was performed and verified satisfactorily. All plant systems functioned as required and the unit is currently stable in mode 3. The NRC Resident Inspector was in the Control Room during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(A) |  |  |  | 0 | 2003-07-11
39992 | 0 | WASHINGTON UNIVERSITY |  |  |  |  | 2003-07-09 15:30 | 2003-07-11 16:58 | 2003-07-11 | MEDICAL EVENT The Radiation Safety Officer at Washington University reported that an under dose of a radiopharmaceutical (Sm-153 Quadramet) was administered to a patient on 07/09/03. The under dose was discovered at 1600 CDT on 7/10/03 when it was determined that a significant amount of the radiopharmaceutical had leaked from the syringe. The licensee determined that 54 millicuries out of the planned 55.8 millicuries had leaked from the syringe such that less than 4% of the planned dose was administered. The licensee will be notifying the referring physician when he returns to his office on Monday, 07/14/03. The licensee assumes the physician will then notify the patient. The licensee will provide a written report to Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-07-11
39991 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-05-23 17:55 | 2003-07-11 13:30 | 2003-07-11 | INVALID EMERGENCY DIESEL START SIGNAL "The report is being made under 10 CFR 50.73(a)(2)(iv)(A) and is not considered a licensee Event Report. "With the unit in refueling shutdown and defueled, a loss of the 1B DC Electrical Bus occurred during maintenance activities associated with the 1B Main Station Battery performance test. The DC Bus voltage went to zero as a result of the 1B-1 battery charger not assuming the load after the current sharing parallel charger 1B-2 was placed in stand-by. "The Unit 1J Emergency AC Bus degraded and undervoltage protection relays, powered from the 1B DC Bus, deenergized and provided a start signal for the #3 Emergency Diesel Generator (EDG). The #3 EDG started, however, it did not load on the Unit 1J AC Bus due to the loss of control power to Unit 1J AC Bus circuit breakers. The signal to start the #3 EDG on the emergency AC electrical power system was considered invalid because the Unit 1 Emergency AC Bus did not experience an actual degraded/undervoltage condition. "Operations personnel stripped the 1B DC Bus in accordance with abnormal procedures and restored the vital busses via manual transfer switches. Aligning the 1B-2 battery charger to the stripped bus reenergized the 1B DC Bus. "The direct cause of the loss of the 1B DC Bus was the failure of the 1B-1 battery charger to pick up the load on the 1B DC Bus. A root cause evaluation is being performed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-07-11
39990 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-05-16 07:14 | 2003-07-11 13:24 | 2003-07-11 | INVALID EMERGENCY DIESEL START SIGNAL "The report is being made under 10 CFR 50.73(a)(2)(iv)(A) and is not considered a Licensee Event Report. "With the unit in refueling shutdown and defueled, a loss of the 1B DC Electrical Bus occurred during maintenance activities associated with the 1B Battery performance test. The current leads from a load bank to the positive (+) terminal of the 1B Battery were being disconnected. "The Unit 1J Emergency AC Bus degraded and undervoltage protection relays, powered from the 1B DC Bus, deenergized and provided a start signal for the #3 Emergency Diesel Generator (EDG). The #3 EDG started, however, the diesel did not load on the Unit 1J AC Bus due to the loss of control power to Unit 1J AC Bus circuit breakers. The signal to start the #3 EDG on the emergency AC electrical power system was considered invalid because the Unit 1 Emergency AC Bus did not experience an actual degraded/undervoltage condition. "Maintenance, Operations, and Engineering conducted a walkthrough of the restoration actions and step sequence and at 1252 hours, re-energized the 1B DC Bus. At 1550 hours, all loads were restored on 1B DC Bus. "The direct cause of the loss of the 1B DC Bus was the disconnection of the wrong battery discharge cables. A root cause evaluation is being performed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-07-11
39989 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2003-06-29 | 2003-07-10 18:55 | 2003-07-11 | PERSONNEL OVEREXPOSURE Mike Henry from the Louisiana Department of Environmental Quality reported the potential personnel over-exposure due to a loss of control of a 1 Curie Cesium-137 source that came out of a damaged Berthold level gauge (Model # LB7442). The event occurred at the Monsanto Chemical Plant in Luling, LA. The gauge was damaged on 06/29/03 causing the source to come out of its shield. The source was then carried to a planner's desk where it remained until discovery on 07/10/03. The owner of the desk spent approximately 50 to 60 hours in the proximity of his desk during this time. When the source was discovered, the building was evacuated and secured. Medical personnel at Monsanto have contacted the Radiological Emergency Assistance Center, Oak Ridge, TN. Preliminarily, the licensee estimates that the planner may have received a whole body dose of 25 Rem and the person that carried the source may have received 1800 Rem to the hand. Others may have also been exposed. No one has shown signs of sickness or erythema (redness of the skin). A Berthold representative is scheduled to arrive on 07/11/03 to secure the source. Mr. Henry will be traveling to the site to obtain additional information. The State is not requesting NRC assistance at this time. A Commissioners' Assistants brief was held at 1900 EDT 07/10/03. * * * * UPDATE FROM MIKE HENRY TO NRC CONFERENCE CALL 1620 EDT ON 07/11/03 * * * * Mr. Henry provided the following information based on his visit to the Monsanto plant this morning, 07/11/03. A manufacturer's representative for Berthold arrived at the plant and retrieved the source around 0300 CDT 07/11/03. Currently the source is in a shielded pig at the plant site. Blood tests were performed for seven individuals which were favorable with no cell changes noted. These blood tests will be repeated periodically. It was determined that the planner who returned after days off to occupy the desk where the source had been previously left received 39.1 Rem over the calculated 44.7 hours that he occupied the desk during the 10-day period involved. This determination was based on an analysis of his schedule and work habits and on the emissivity of the source. Further dose calculations will be made. The Monsanto company physician is in contact with REAC (Radiological Emergency Assistance Center) in Oak Ridge, TN and has requested their assistance in having a cytogenetic blood study performed for the planner. Preliminarily, it appears that vibration of the centrifuge unit upon which the gauge was mounted may have caused a failure which allowed the source holder with attached source to fall from the gauge. Surveys of the relevant areas and smears taken on the source indicate that no source leakage occurred. Notified R4DO (K. Kennedy), NMSS EO (S. Frant) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-07-15
39988 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-07-10 13:44 | 2003-07-10 15:55 | 2003-07-10 | AUTOMATIC REACTOR TRIP DUE TO MAIN FEEDWATER PUMP TRIP "At 1342, The Unit 2 'B' Main Feedwater Pump tripped, this was followed by an automatic reactor trip at 1344. All Reactor Protection and Safety Systems responded as required. The Unit 2 'B' Heater Drain Tank Pump also tripped during the transient. The 'B' Main Feedwater Pump trip was due to an electrical fault, the cause is unknown at this time. Unit 2 is stable in Mode 3 at this time." Additionally, due to the initial low levels in the Unit 2 Steam Generators due to the Main Feedwater Pump trip, Auxiliary Feed Water initiated as expected. The licensee reported that all rods fully inserted, decay heat is being removed by dumping steam to the main condenser, and no primary or secondary relief valves lifted.. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-07-10
39987 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-07-09 22:00 | 2003-07-10 04:03 | 2003-07-15 | CONTROL ROOM HVAC REFRIGERATION AND CONDENSING UNIT TRIPPED DURING SURVEILLANCE TEST "At 2200 hours on July 9, 2003, the B Control Room HVAC Refrigeration and Condensing Unit (RCU) tripped and would not stay running during surveillance testing. The RCU is a single train system and therefore is reportable per SAF 1.8 and LS-AA-1400, Event Reporting Guidelines Section 3.2.7. The RCU is required to operate during a design basis accident to remove heat from the Main Control Room. The Air Filtration Unit (AFU) of CREVS [Control Room Emergency Ventilation System] remains operable. This places both units in a 30 day LCORA [Limiting Condition for Operation Required Action] per Tech Spec 3.7.5 Required Action A.1." The licensee has notified the NRC Resident Inspector. * * * Retraction on 07/15/03 at 1924 EDT by Dennis Francis taken by MacKinnon * * * "On July 9, 2003, an ENS notification was made regarding the 'B' Control Room HVAC Refrigeration and Condensing Unit Inoperability. The (event) was reported as a condition that would have prevent the fulfillment of a safety function. However, after a review of the actual circumstances it was determined that the system did not trip as was believed at the time of the notification. The system was thought to have tripped because a trip indicator light for the refrigeration compressor in the main control room was illuminated. The breaker was inspected and no adverse condition observed. Further investigation revealed that the trip indicator was illuminated due to the local control switch being in the AUTO-AFTER-START position. Therefore when the compressor would not cycle off due to temperature, the trip indicator would illuminate. Even though the condition does not (affect) operability, it does indicate a false trip indication. Then normal position for this switch is AUTO-AFTER-STOP. In this position the amber trip light indicator will not illuminate when the compressor turns off to low temperature in the main control room. "The switch position of AUTO-AFTER-START did not affect the ability of the system to perform its safety function. Therefore the ENS notification (Ref. EN # 39987) is being retracted." NRC R3DO (RIEMER) notified. The NRC Resident Inspector will be notified of this retraction by the licensee. | 0 | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-07-10
39986 | -1 | UNIVERSITY OF WISCONSIN - MADISON |  |  |  |  | 2003-07-09 13:00 | 2003-07-09 18:07 | 2003-07-17 | MEDICAL EVENT At 1300 CDT on 7/9/03, an underadministration of Yttrium-90 (Y-90) occurred at the University of Wisconsin Hospital in Madison, WI. A patient being treated for secondary liver cancer was to receive a dose of approximately 50 millicuries of Y-90. The dose was delivered using a SIRTECH (Selective Radiation Implantation) to pulse microspheres of Y-90 from a vial into the liver via a needle and catheter. During the procedure, the SIRTECH did not develop enough pressure to deliver the entire dose to the patient, and only about 8 percent of the Y-90 was delivered to the patient (between 3-4 millicuries). The remainder of the Y-90 microspheres were contained within the vial. There was no adverse affect on the patient due to this underadministration, and the licensee is still investigating how to prevent a re-currence. The patient was notified of the underadministration. * * * RETRACTION AT 0615 EDT ON 07/17/03 FROM BRESELL TO GOTT * * * The licensee determined that the technician had misinterpreted the measurement of the Y-90 administered to the patient and determined that the correct amount of Y-90 was administered. Because the correct amount of Y-90 was administered, the licensee is retracting the event. The licensee discussed this with Deborah Piskura, NRC Region III. Notified R3DO (Riemer) and NMSS EO (Pierson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-07-09
39985 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-07-09 01:09 | 2003-07-09 03:05 | 2003-07-09 | AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP BREAKER OPENING WITH INITIATION OF AUXILIARY FEEDWATER SYSTEM AFTER THE TRIP "At 0109 hrs. CDT, Unit 2 reactor tripped due to opening of RCP [Reactor Coolant Pump] 2-04 breaker resulting in "Rx >48% 1/4 loop flow low trip". Cause of the breaker opening is unknown and under investigation. All systems responded as required. Auxiliary Feed Water auto-start occurred due to steam generator shrink, both motor driver AFW pumps and Turbine Driven AFW pump started (ESF)." All rods inserted into the core during the trip. The electrical grid is stable. There were no power-operated or manual relief valve lifts during the transient. The other unit was not affected by the transient. Decay heat is being removed via steam generator blowdown and AFW. The plant is maintaining at NOP/NOT in mode 3 until the cause of the breaker trip is known and repaired. Pressurizer pressure control is in automatic. There is no identified primary-to-secondary leakage. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-07-09
39984 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2003-07-08 10:58 | 2003-07-08 16:42 | 2003-07-08 | LOSS OF COMMUNICATIONS CAPABILITY "At approximately 10:58 hours (EDT) on July 8, 2003, a fiber optic cable that provides service to H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, was removed from service due to highway bridge repairs on State Road 23, Old Camden Road, approximately 1.5 miles west of the plant site. This resulted in the loss of circuits supported by Bellsouth, which includes the selective signaling system for communication with the state and counties, an additional phone system for internal and external communication called ESSX, the NRC T1 link, and dial 9 service from the internal plant telephone system. Communications capability remained available via the on-site PBX telephone service, cellular phone service, satellite phone, and the Progress Energy Voicenet system. "At approximately 09:00 hours [EDT], Bellsouth personnel informed HBRSEP, Unit No. 2, personnel of the plan to temporarily remove the cable from service at approximately 11:00 hours [EDT] in support of the bridge repair work. HBRSEP, Unit No. 2, Emergency Preparedness personnel notified the control room Superintendent of Shift Operations pertaining to the impending communications outage and verified that a cellular phone and satellite phone were available in the control room. The state and county emergency operation centers, warning points, and back-up warning points were notified of the planned communications link outage prior to its removal from service. The fiber optic cable was placed back in service at approximately 14:51 hours [EDT] and the systems were subsequently tested satisfactorily. "This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of offsite communications capability. The capability to provide notification as required was maintained by use of alternate systems, specifically cellular phone, satellite phone, and the Progress Energy Voicenet system. The resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-07-08
39983 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-06-19 | 2003-07-08 15:28 | 2003-07-08 | AGREEMENT STATE REPORT Spill of radioactive material. On 6/19/2003, an employee inadvertently dropped a vial of P-32 on the floor. The container spilled approximately 2900 millicuries of P-32 on the floor while contaminating one employee and several pieces of the licensee's equipment. The employee was decontaminated on site. An initial clean-up wash was performed on the facility. However, the radiation levels remained high. The RSO (Radiation Safety Officer) directed that the floors be covered with 2 sheets of 4 ft by 8 ft plexiglas. In addition, the licensee covered contaminated equipment with lead sheeting to prevent the spread of contamination and elevated radiation levels in the vicinity of the equipment. The licensee is waiting 10 half-lives to release the facility for full use. All personnel entering the area are notified of the contamination and are warned of the radiation levels and potential contamination. The incident was not reported within 24 hours per regulations. Levels exceed release criteria. The incident is being investigated. This incident is being reported under 10 CFR 30.50(b)(1), and Texas requirement 289.202(xx)(7)(A). Texas incident number I-8034. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-07-11
39982 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2003-07-07 23:19 | 2003-07-08 02:52 | 2003-07-08 | AUTOMATIC REACTOR SCRAM AT LaSALLE UNIT 2 DUE TO TRIP OF THE MAIN TURBINE "At 2319 CDT on July 7, 2003 LaSalle Unit 2 Automatically scrammed due to a trip of the main turbine. The main turbine trip was caused by a main generator lockout due to a fault on the "B" phase of the main power disconnect. All rods inserted on the scram. Three safety relief valves actuated in the relief mode on the turbine trip. Both reactor recirc pumps tripped off and all three circulation water pumps tripped off. The main steam line isolation valves and main steam line drains were closed due to the loss of the circulating water pumps. Tech Spec 3.0.3 was entered due to simultaneous inoperability of A, B, and C residual heat removal pumps. "A" residual heat removal pump was declared inoperable due to use in suppression pool cooling. "B" and "C" residual heat removal pumps were inoperable at the beginning of the event for planned [preventive] maintenance on the essential core cooling system ventilation. There were no automatic actuations of ECCS systems and no primary or secondary containment isolation system actuations. There [were] no ECCS injections into the reactor vessel. There were 3 subsequent auto scram signals on low reactor level due to level shrink on SRV closure in pressure control." Unit 2 is currently stable with reactor feedwater being provided by the condensate system and reactor heat removal using SRV steam discharge to the suppression pool. Residual heat removal pumps "A" and "B" are operating to provide suppression pool cooling. "C" residual heat removal pump has been returned to operable status. All emergency diesel generators are available. The licensee also reported that the electrical system transient resulted in the need to reduce power on LaSalle Unit 1 from 100% to ~92% to stabilize condensate booster pump suction pressure. The licensee has notified the NRC Resident Inspector * * * UPDATE ON 7/8/03 AT 1108 EDT FROM DANIEL COVEYOU TO GERRY WAIG * * * "At 0306 [CDT] on 7/8/03 there was an automatic RPS [Reactor Protection System] actuation due to reactor water level 3. At the time of the scram all control rods were already fully inserted. There was no rod movement as a result of the 0306 [CDT] auto reactor scram. The low level condition was a momentary response due to level shrink upon safety relief valve closure. The safety relief valves were being manually operated to control reactor pressure." The licensee has notified the NRC Resident Inspector. Notified R3DO ( Chris Miller) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-07-08
39981 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-07-07 11:00 | 2003-07-07 23:44 | 2003-07-07 | MANUAL ACTUATION OF A SAFETY SYSTEM DUE TO UF6 CYLINDER LEAKAGE "On 07/07/03 at 1100 hrs the Plant Shift Superintendent's (PSS) office was notified by operations personnel at the X344 facility, that during the initiation of UF6 transfer from Autoclave #3 to the daughter cylinder, smoke was observed emitting from between the cylinder valve stem and packing gland. The operator attempted to shut the cylinder valve, but discovered that the stem would continue to turn in the closing direction well beyond its normal expected shut position. Out gassing continued to be observed emitting from between the cylinder valve stem and packing gland. The First Line Manager, observing the evolution, directed the Operator to press the Emergency Closure Button placing autoclave #3 into containment. This was manual actuation of Safety Equipment used to mitigate (prevent) a release of UF6. Emergency Response was initiated and the Gas Release Alarm was activated to evacuate the building, which placed the other in service autoclave into containment. All Air monitoring was less than detectable for HF and below Plant Allowable Limits for Beta and Gamma." Operations notified both the DOE site representative and the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-07-07
39980 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-07-07 15:00 | 2003-07-07 19:32 | 2003-07-07 | UNANALYZED CONDITION "At 1500 on 07/07/2003, Operations received a revised Functional Evaluation concerning a Unit 1 Appendix R Analysis which affected both Units 2 & 3. It was identified that a Reactor Building fire could fault a Recirc Pump Motor Generator (MG) Set supply cable/control power cable and cause a loss of the control power required to trip the breaker. Upon further review, it was determined that the 250v dc control power associated circuit for the Recirc Pump Board breaker trip circuit does not have adequate separation from the 4KV feeder cable to the Recirc Pump MG Set (Unit 3) or the Variable Frequency Drive (Unit 2). A fire propagating to the Cable Spreading Room from the Reactor Building may affect safe shutdown circuits and remains unanalyzed. Roving Fire watches were established in the affected areas on both Units 2 & 3. "This event is reportable as an 8-hour Notification and a 60-day written report in accordance with 10 CFR 50.72 (b)(3)(ii)(B) & 10 CFR 50.73(a)(2)(ii) as 'Any event or condition that results in the Nuclear Power Plant being in an unanalyzed condition that significantly degrades plant safety.'" The licensee notified the NRC Resident Inspector | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-07-07
39979 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2003-06-26 18:00 | 2003-07-07 13:09 | 2003-07-07 | AGREEMENT STATE REPORT "The [Tennessee Division of Radiological Health] was notified on Monday, June 30, 2003 by three employees of RACE [Radiological Assistance, Consulting, & Engineering] of a contamination event that occurred on June 26, 2003. The employees were sorting and segregating materials contaminated with low-level radioactive waste. The waste had been delivered to RACE by a waste broker. The employees ended the shift and frisked for personnel contamination prior to exiting the building. Several employees alarmed the PCM and were decontaminated prior to release. One employee had high levels of skin contamination and underwent several hours of decontamination. Preliminary results from urinalyses are negative according to the licensee. The employees are undergoing whole body counts today. The shop area was closed for routine business and decontaminated. It was opened on Sunday, June 29, 2003. DRH staff from Memphis and Nashville visited the site to begin the investigation. Staff continue to investigate and will continue to keep the NRC informed of the status of our investigation. This incident is reportable under 1200-2-5.141 (2)(c)1(i) of 'State Regulations for Protection Against Radiation.'" Tennessee Report ID: TN-03-100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2003-07-10
39978 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2003-07-06 16:00 | 2003-07-07 11:04 | 2003-07-18 | AGREEMENT STATE REPORT - STOLEN ASPHALT CONTENT OVEN The following is taken from a facsimile sent from the Colorado Department of Health and Environment: On 7/6/03 at 2230 MDT Robin Koons, Colorado State Department of Health and Environment, was notified by the Arapahoe County Hazmat Response Team of the theft of an asphalt content oven at a construction site located on Highway 36, mile marker 119 - 20 miles east of Byers, CO. Arapahoe County Hazmat responded to initiate an investigation into the incident. Initial information and indications pointed to a moisture density gauge being stolen. The moisture density gauge has been found and accounted for. The asphalt content oven contains a 100 milliCurie (plus or minus 10%) Americium 241:Be source. The oven is used to test for oily content in asphalt during road construction process. The area is considered a crime scene and has been secured. Colorado Case Number: 2003-372 * * * UPDATE 1203 EDT ON 7/18/03 FROM TOM PENTECOST TO S. SANDIN * * * Colorado Dept. of Health called to confirm that a report of this incident was made to the NRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2003-07-10
39977 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-07-06 12:50 | 2003-07-06 20:10 | 2003-07-06 | AIR SUPPLY LINE TO CYLINDER SAFETY VALVE ON AN AUTOCLAVE WAS FOUND TO BE DAMAGED "On 07/06/03 at 1250 hrs. The Plant Shift Superintendent's (PSS) office was notified by operations personnel at the X-344 facility, that the air supply line to the Parent Cylinder Safety Valve on Autoclave #4 (Q safety system component) appeared to be severely damaged. The assistant PSS on duty and the Shift Engineer (SE) responded to assess the condition, and determined that the Parent Cylinder Safety Valve air supply line was damaged and would not or could not have performed its intended safety function. At 1310hrs the PSS declared the Parent Cylinder Safety Valve inoperable and directed operations personnel at the X-344 facility to initiate TSR-LCO required actions to place autoclave #4 into mode VII (Shutdown). "The damaged air line had apparently been present during applicable TSR modes, II (Heating), III (Cylinder/Pigtail Operations) and IV (Feeling, Transfer of Sampling). This condition is reportable under 76.120 (c)(2)(ii) and 76.120 (d)(2). The equipment is required by Technical Safety Requirements (TSR) to be available and operable and either should have been operating or should have operated on demand." The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2003-07-06
39976 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-06-19 06:45 | 2003-07-03 18:41 | 2003-07-03 | DAMAGED TEXAS NUCLEAR MODEL 5180A LEVEL GAUGE "An explosion and fire occurred in a distillation unit. The operating units were shut down and the fire was extinguished. A visual inspection of a level gauge installed on a vessel located in the area showed the device was intact with no apparent physical damage except heat discoloration was visible on the device. A preliminary survey found no readings above the regulatory limits. However, an attempt to close the shutter was made and debris and molten materials made the closing difficult. A wipe test was performed with no leakage found. The device and area was barricaded to prevent unauthorized entry. "Consultant Assistance: A radiation technician from Alpha Process Sales inspected the device and the area. Occupancy surveys were made and showed no persons who entered the area received exposures over the allowable limits. "Thermo-Measuretech of Round Rock, TX, an authorized company, removed the device and took possession for disposal. "TX Nuclear Level Gauge TN model 5180A source sn# B380, 500mCi [millicuries] Cs-137" Texas Incident No: I-8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-07-08
39975 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-05-20 14:30 | 2003-07-03 17:59 | 2003-07-03 | OVEREXPOSURE Event occurred on May 20, 2003 between the hours of 0200 and 0230 hours CDT at the Amoco Refinery in Texas City, TX. Overexposure was reported to the Texas Dept. of Health on July 3, 2003. "A radiography source was not cranked into the fully shielded position resulting in a 6.403 R whole body exposure to a radiographer. The radiographer was making wall thickness exposures using a 100 curie cobalt 60 source with a directional collimator. The radiographer made the last exposure for the night, then proceeded to retrieve the film and take it for development in the darkroom. The radiographer believed the pigtail had been fully retracted, however, his initial survey was not conclusive because his survey meter was not turned on. Although the ratemeter was alarming, because of the noise level and the ear plugs, he did not initially hear ratemeter alarming. When he did hear the faint ringing he checked the meter and it was off. When the radiographer turned the meter on and resurveyed the guide tubes, the needle went off-scale. He checked his pocket dosimeter and it was off scale. The radiographer then retracted the pigtail into the fully shielded position. The radiographers reported the event to their management by telephone, then returned to the company shop. "The following day the personnel monitoring badge was sent for emergency processing. The radiographer believes he was exposed for about one minute. "We will provide additional information as it is collected" Source Production & Equipment Company. Source Information: Model G-70 sn# C60-02 101 Curies cobalt-60 on May 29, 2002 (3737GBq) Texas Incident No: I-8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-07-08
39974 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-06-15 14:53 | 2003-07-03 16:41 | 2003-07-03 | INVALID START OF THE AUXILARY FEEDWATER SYSTEM "On 06/15/2003 at 1453 an invalid start of the auxiliary feedwater system occurred. The actuation was caused by a maintenance activity on a common high pressure turbine impulse pressure transmitter. "Both the Train A and B motor-driven auxiliary feedwater pumps were running and the turbine-driven auxiliary feedwater pump started. "Complete train actuation occurred. "The turbine-driven auxiliary feedwater pump start was successful." The NRC Resident Inspector will be notified of this event by the licensee. | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-07-03
39973 | 0 | THREE MILE ISLAND |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP | 2003-07-02 10:56 | 2003-07-02 11:27 | 2003-07-02 | UNUSUAL EVENT DUE TO SWITCHGEAR FIRE IN THE TURBINE BUILDING The licensee declared an unusual event on 7/2/03 at 1056 EDT according to Emergency Action Level No.HU4 due to a fire in the non-vital 480 Volt Motor Control Center switchgear located in turbine building 2-31. The fire was put out at 1125 by the fire brigade and no plant personnel were hurt due to this incident. The Technical Support Center was not activated for this event as Unit 2 is decommissioned. This incident did not impact Unit 1and it remains at full power operations. The licensee is making preparations to de-escalate the unusual event and is in the process of preparing a press release. * * * UPDATE 1255 ON 07/02/03 JIM MCKINNEY TO GOTT * * * The licensee terminated from the unusual event at 1245 on 07/02/03. Notified R1DO (Barkley), NRR (Beckner), DHS Operations Officer, Denver, FEMA (Sullivan), NSIR (Wessman), and PAO (Beecher). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Decommissioned; FMode2: Decommissioned | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-07-02
39972 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-07-01 18:45 | 2003-07-02 00:17 | 2003-08-04 | UNACCOUNTED FOR SECURITY WEAPON Unaccounted for security weapon. Immediate compensatory measures taken upon discovery. TVA security and NRC Resident Inspector notified. Refer to HOO Log for additional details. * * * UPDATE ON 07/02/03 AT 0150 FROM HERBERT EAVES TO ARLON COSTA * * * TVA Police made offsite notification on 07/01/03 at 2300 EDT to the National Crime Information Center pertaining to the unaccounted for security weapon. The NRC Resident Inspector will be notified of this event update. * * * UPDATE on 07/03/03 AT 1526 EDT FROM BONNIE SCHMETZLER TO MACKINNON * * * Security weapon not found on site. Investigation being continued by TVA police. The NRC Resident Inspector will be notified of this update. R2DO (Joel Munday) & NSIR (Roberta Warren) notified. * * * UPDATE ON 08/04/03 AT 1648 FROM MITCH TAGGERT TO ARLON COSTA * * * Unaccounted for security weapon was found. Plant security is investigating the incident. Refer to HOO Log for additional details. The NRC Resident Inspector will be notified. Notified R2DO (James Moorman) and TAS (Matt Kormann). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | INFORMATION ONLY |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-07-02
39971 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2003-07-01 08:00 | 2003-07-01 12:13 | 2003-07-01 | PRESS RELEASE DUE TO SIREN MALFUNCTION The licensee provided the following information via facsimile: "At approximately 0800 (CDT) on July 1, 2003, LaSalle County Station management decided to issue a press release related to a single malfunctioned warning siren. The warning siren had malfunctioned and erroneously operated for nearly 90 minutes early this morning. LaSalle County Generating Station will begin replacing the faulty warning siren's electronics today. The press release is tentatively expected to occur today at 1130 CDT. No other emergency notification systems or sirens malfunctioned. "The siren, located in LaSalle County on East 25th Road approximately one-half mile west of the station, is currently out of service. It is expected to return to service on Wednesday July 2." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-07-01
39970 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-06-30 15:45 | 2003-07-01 00:04 | 2003-08-27 | HIGH ENERGY LINE BREAK (HELB) DOOR NOT LATCHED "On June 30, 2003 at approximately 1545 [CDT] it was identified that a High Energy Line Break (HELB) door separating Divisional Motor Control Centers was not latched as required. It was determined that this condition existed for a maximum of 15 minutes. This condition is being reported as an event or condition that could have prevented the fulfillment of a safety function in accordance with 10 CFR 50.72(b)(3)(v)." The licensee notified the NRC Resident Inspector and the State Emergency Management Agency. * * *RETRACTION on 08/27/03 at 1215 EDT from R. Sand to John MacKinnon * * * Because plant safety was not significantly degraded, this event is not reportable under the unanalyzed condition criteria based on: (1) the door in either event was in an uncontrolled condition for less than one minute, (2) the door was not materially affected, only operated improperly, (3) the PRA significance of the event was low, and (4) the HELB Barrier door was not open for a period than is allowed by station procedural guidance. R3DO (C. Miller) notified. The station continues to review the events in the station's corrective action program. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2003-07-01
39969 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 5000 KW TANK RESEARCH HW | 2003-06-30 06:45 | 2003-06-30 17:44 | 2003-06-30 | OPERATOR ASLEEP AT REACTOR CONTROLS The following was emailed from the licensee to the NRC Project Manager: "The licensee Facility Director called the NRC project manager to report that on 6/29/03 between 0605 EDT and 0645, the operator at the control console fell asleep for approximately 25 minutes. The operator had logged console operations at 0605 and 0645. Other licensee personnel had tried to contact the console operator during this time period without success. The licensee is investigating the event and will review this situation with all reactor operators." This is in violation of 10 CFR 50.54 (k). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | MA | NPR | [5 empty] | 0 | 2003-06-30
39968 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-06-30 17:10 | 2003-06-30 17:30 | 2003-06-30 | TECH SPEC REQUIRED SHUTDOWN On June 30, 2003, at 1710 EDT, Unit 1 reactor power was decreased, initiating a reactor shutdown required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.4 due to Reactor Coolant System (RCS) operational leakage exceeding a TS LCO limit. At 0615 hours, TS LCO 3.4.4 was entered due to an increase in unidentified leakage of greater than 2 gpm (gallons per minute) within the previous 24 hour period. Leakage increased from 0.63 gpm on June 29, 2003 at 2000 EDT, to 2.69 gpm on June 30, 2003 at 0615 EDT. Required Actions from LCO 3.4.4 are to reduce leakage to within TS limits within 8 hours or be in Mode 3 (Hot Shutdown) in 12 hours and Mode 4 (Cold Shutdown) in 36 hours. As of 1700 EDT, leakage could not be reduced to exit the TS LCO Condition. The licensee notified the NRC Resident Inspector. | 92 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-06-30
39967 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-06-30 14:59 | 2003-06-30 17:20 | 2003-06-30 | OFFSITE NOTIFICATION DUE TO FIRE "At 1459 EDT 06/30/03 a fire was reported on Unit II containment. The fire was on wooden staging, and was about the size of a normal campfire. The fire was a result of the disassembly of the Unit II containment dome. Per procedure, the Seabrook Fire Department was called and responded. The fire was extinguished by the Unit II disassembly crew (the onsite fire brigade did not respond because the fire was outside of the Unit I protected area). The Seabrook Fire Department was not used to extinguish the fire. Corporate Communications Group have been in contact with Channel 9 and with the Associated Press. The fire was extinguished at 1535 using prestaged hoses. The fire water was provided by Hydrant #15 of Seabrook Station's Fire Protection System." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-30
39966 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-06-30 15:41 | 2003-06-30 15:54 | 2003-06-30 | UNUSUAL EVENT DECLARED DUE TO SEISMIC EVENT IN THE AREA At 1541 EDT on 6/30/03, Perry Nuclear Plant declared an Unusual Event due to a seismic event. No immediate issues were noticed. The operating-basis earthquake/safe-shutdown annunciator did not alarm, however the plant did receive a seismic panel alarm. The set point for the alarm is 0.005g. There were no unplanned radioactive releases. No protective action recommendations are advised by the licensee. State and local counties (Lake, Geauga and Ashtabula) have been informed. The National Earthquake Information Center has preliminary indications that the earthquake measured 3.4 on the Richter scale at 41.7 N latitude and 81.2 W longitude near Painesville, OH. The licensee has notified the NRC Resident Inspector * * * UPDATE AT 2242 ON 06/30/03 CARMAN TO GOTT * * * Licensee terminated from unusual event. Action needed to terminate from the unusual event was a plant walk down. The licensee completed same with no plant damage identified, no unplanned radiological release, and no planned corrective actions. The licensee notified the NRC Resident and Senior Resident Inspectors. Notified NRR EO (Ruland), DIRO Manager (McGinty), DHS (Murray), FEMA (Stiendurf), and R3DO (Clayton) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-06-30
39965 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-06-30 09:18 | 2003-06-30 14:39 | 2003-06-30 | VALID REACTOR PROTECTION SYSTEM ACTUATION The following information was obtained from the licensee via facsimile: "This event notification is being made to report the valid actuation of the reactor protection system when the reactor was critical, and subsequent reactor scram. On June 30, 2003, [at 0918 PDT], the plant was in Mode 1 at 79% power, when a turbine trip occurred, followed by a reactor scram. The cause of the turbine trip is unknown at this time. All plant systems functioned properly in response to the scram. Operators are proceeding to bring the plant to Mode 4, Cold Shutdown, while investigation into the cause of the transient is completed." During the scram, all rods inserted into the core. There were no lifts of power-operated or manual relief valves during the transient. The electrical grid is stable and powering all safety equipment. There were no other specified system actuations. Decay heat is being removed via the bypass valves to the main condenser. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 79 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-06-30
39964 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2003-06-26 19:17 | 2003-06-30 14:10 | 2003-06-30 | AGREEMENT STATE REPORT FROM LOUISIANA The following was faxed from the Louisiana Department of Environmental Quality: "During industrial radiography, the crank-out assembly got in contact with some hot pipe while the source was cranked out. The heat from the pipe melted the rubber housing on the crank-out assembly. Could not mechanically retract the source. The radiographers isolated the area and kept personnel out until AEA Technology could arrive to retrieve the source. There was no damage to the exposure device or the source. There was no exposure to individuals of the public. The source was 85 curies of Ir-192." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-07-03
39963 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2003-06-27 17:09 | 2003-06-27 21:52 | 2003-06-27 | NON-POWER REACTOR MONITORED RELEASE BELOW 10CFR20 LIMITS WITH SCRAM On 6/27/2003 at 1709 PDT, the licensee received particulate and noble gas monitor alarms on the stack. The readings were 1.0E-6 microcuries/ml noble gas and 1.4E-6 microcuries/ml particulate. The particulate setpoint was 1.0E-8 microcuries/ml. The licensee determined that there was a pin hole fuel leak and three minutes following the stack alarm they received a percent power scram. At 1812 PDT the licensee determined that they did not reach an emergency classification level. The count rate alarm was in for 10 minutes, and the concentration alarm was in for 5 minutes. Offsite concentrations were calculated to be 1.136E-9 microcuries/ml noble gas and 1.605E-9 microcuries/ml particulate. They determined that offsite doses were <0.2 mr/hr during the event. This was an information only call, and they will not be making a press release or contacting Oregon. They are currently investigating the event and have no date for assuming operation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2003-06-27
39962 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-06-27 12:40 | 2003-06-27 13:13 | 2003-06-27 | OFFSITE NOTIFICATION MADE FROM ST. LUCIE TO THE STATE OF FLORIDA "At 1240 EST, (on 6/27/2003) the Florida Department of State, Division of Licensing was contacted (by St. Lucie), due to an inadvertent discharge of a firearm in the PSL Security Building Armory. "At 0613, a contract security officer inadvertently discharged his weapon when it was reloaded following routine maintenance. The accidental weapon discharge was attributed to human error. No injuries resulted from this event. "This non-emergency notification is being made pursuant to 10CFR50.72(xi)." The Florida Department of State, Division of Licensing person contacted was Eileen Kidd (561-640-6144). The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-27
39961 | 0 | HAENGEL & ASSOCIATES ENGINEERING |  |  |  |  | 2003-06-26 | 2003-06-26 13:21 | 2003-06-27 | STOLEN TROXLER GAUGE IN NEWPORT, MICHIGAN The licensee reported that on 6/26/03 at 1200 pm a technician noticed that his parked van, containing a Troxler gauge model 3430, had broken windows and had been vandalized. The chain was cut which was holding a Troxler gauge model 3430 and the gauge was missing. The gauge contains 8 millicuries Cs-137 and 40 millicuries Am-241. Local Police, Troxler and RIII Cassandra Frasier were notified by the licensee. * * * UPDATE 1011 EDT ON 6/27/03 FROM GUS HAENGEL TO S. SANDIN * * * The following additional information was provided for clarification: Haengel & Associates Engineering, Inc is located at 42030 Koppernick Road, Suite 206, in Canton, MI 48187. The Troxler 3430 S/N 20113. The source S/Ns are 75-1375 (8 mCi Cs-137) and 47-15597 (40 mCi Am-241:Be). The theft occurred at an employee's residence located in Newport, MI. The licensee is posting a reward and does anticipate media interest. The local police department is the Monroe County Sheriff's Department. Notified R3DO(Louden) and NMSS(Essig). * * * UPDATE ON 07/07/03 AT 0828 EDT FROM GUSTAVO HAENGEL TO GERRY WAIG * * * The licensee reported that on 07/07/03 at approximately 0825 EDT he was notified by the Monroe County Sheriff's Department that the stolen Troxler gauge had been recovered on 07/06/03. The licensee, Haengel & Associates Engineering, will be picking up the gauge from the police. Notified R3DO (Brent Clayton) and NMSS (Marissa Bailey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-06-26
39960 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2003-06-25 14:30 | 2003-06-25 19:45 | 2003-06-25 | UNANALYZED CONDITION DUE TO DISLODGED ACCESS PANEL IN THE CONTROL BUILDING VENTILATION SYSTEM "An access panel cover for the Control Building Ventilation System supply duct was found to be dislodged on June 24, 2003. The access panel was immediately realigned upon discovery of the condition and secured. The probable cause of the event is that vibration of the ductwork caused the panel closure camlocks to vibrate from a closed position to an open position. A walkdown is being performed to ensure that other access panels are secure. The corrective action to this event will address additional actions to ensure these closure camlocks and other similar camlocks are positively secured to prevent an event recurrence. "The review of the potential impact of this system configuration determined on June 25, 2003 that conditions may have existed as defined in 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D) and that the event requires reporting. On Tuesday, June 25, 2003, further Engineering evaluation determined that the dislodged panel access cover for the Control Building Ventilation System may have reduced the systems capability to maintain a positive pressure in the Control Building Habitability Envelope. This condition could have lead to increased unfiltered in-leakage of airborne radioactive material beyond the previously analyzed condition in the event of a design basis accident. Further analysis may determine that the system would have been able to perform its design basis function. "The NRC Resident Inspector has been notified. No other state, local or other government agencies have been notified. There has been no media press release issued." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-06-25
39959 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-06-25 13:24 | 2003-06-25 14:27 | 2003-06-25 | SMALL OIL SPILL AT HADDAM NECK PROMPTS OFFSITE NOTIFICATION The licensee reported an offsite notification to the Connecticut Department of Environmental Protection concerning a 1 pint oil spill. Apparently, a hydraulic hose on a forklift failed and spilled oil onto the dirt. The licensee indicated they will clean-up the oil spill. Notified R1DO (K. Jenison) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-25
39958 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2003-06-25 10:20 | 2003-06-25 10:45 | 2003-06-26 | DAMAGED TROXLER DENSITY GAUGE At 1020 EDT on 6/25/03, the NC Radiation Protection Section was notified that a portable nuclear gauge being used was run over by a passenger van at the intersection of Faivon and Bucchaneer Roads (near Hwy 40 and the 55 interchange). The Authorized User is on site and has the gauge cordoned off as per emergency procedures require. The van involved in the collision is being detained.. Both the RSO and Alt RSO are enroute to perform surveys (1 hour). NC Radiation Protection Section personnel are responding to the scene to perform surveys (30 mins). The device is described as a Troxler Gauge containing 8 millicuries Cs-137. NC Incident Report No.: 03-27. * * * UPDATE 0952 EDT ON 6/26/03 FROM NC RAD PROTECTION VIA FAX * * * The following additional information was provided by NC: Incident Location: Chapel Hill, NC . Intersection of Faison and Buckner Roads. Take 40 West from Raleigh to the NC54 exit towards Chapel Hill. Take a right onto Meadowmont, then a left onto Sprunt. Follow Sprunt to Weaver Lane and take a right onto Weaver Lane. Take a right on Faison off of Weaver lane, go downhill to the intersection of Faison and Buckner. Brief Description of Incident: Paving contractor in a commercial van was not watching where he was driving and ran over the instrument panel part of a Troxler model 4640B thin lift density gauge. The licensee was performing a standardization count on the gauge at the time of the accident so the source was in the shielded position when it was run over. The gauge was pushed off the standardization plate and dragged about 3 feet. The gauge then rolled onto it's side and the source handle was shoved into the asphalt. The licensee stopped the van and detained it and the driver until the gauge could be surveyed and it was determined that there were no loose source or contamination concerns. The area was cordoned off with pink surveyors' tape and controlled until the gauge and accident area was surveyed and the gauge returned to the Troxler shipping container. Survey results of the gauge done by both the licensee and the NCDENR RAM Branch were consistent with an undamaged gauge. The licensee placed the gauge into the Troxler transportation case for delivery to Troxler for leak testing and servicing. The damage appears to be cosmetic with some damage to be expected to the electronics. Radiological Information: Isotope(s): Cesium-137, Activity: 8 millicuries, Device: Troxler Gauge, model 4640B Notified R2DO (C. Ogle) and NMSS (Broaddus). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2003-06-30
39957 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2003-06-17 | 2003-06-23 17:26 | 2003-06-23 | AGREEMENT STATE REPORT- WRONG PATIENT SELECTED "Today, June 23, 2003, a consultant to Good Shepherd Hospital (IL-01620-01) in Barrington, IL called concerning a reportable medical event [discovery date 06/20/2003]. On June 17th the licensee was scheduled to provide a therapeutic dose of 15 milliCi [milliCuries] of I-131 to a patient by capsule. Instead, the patient received a capsule with an assayed dose of 10.8 milliCi. Apparently, two treatments were scheduled for the day and a second patient was prescribed a dose of 11 milliCi and the technician failed to administer the correct dose to the patient. The second patient did not receive any treatment that day and was rescheduled for last Friday. (A separate call to the pharmacy confirmed two doses were delivered on Tuesday, one of 15 milliCi and a second [dose] of 11 milliCi and another dose of 10 milliCi was provided on Friday.) "At this time, the radiation oncologist does not believe there will be any appreciable effect to the patient, but will continue to follow through with the evaluation to determine if an additional dose is necessary to achieve the optimal results. The licensee has advised the referring physician verbally and in writing. They have determined it would not be appropriate to notify the patient[s] given their condition and medical situation. "The licensee has spoken with the responsible technician about ensuring the correct dose is administered to the correct patient. The licensee is in the process of changes procedures at the site so that two individuals must independently confirm the correct patient identification and dosage information immediately prior to administration. "The licensee was advised as the need for timely reporting or these events and that a formal report must be filed within 15 days as per 32 Ill. Adm. Code 335.1080." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-06-26
39956 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2003-06-23 11:08 | 2003-06-23 15:44 | 2003-06-23 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY AFFECTING PLANT ANNUNCIATORS "This report is being made pursuant to 10 CFR 50.72(b)(3)(xiii), Major loss of emergency assessment capability. Electrical Maintenance Department personnel were removing an Annunciator System power supply inverter as part of pre-planned maintenance. During the removal of the inverter, a short occurred which resulted in the loss of power to all of the Division II powered annunciators (about 50 % of all annunciators). The station entered the abnormal response procedure and took compensatory action for monitoring equipment and plant status. At present, troubleshooting activities are in progress to restore full annunciator capability." All plant systems functioned as required and no other plant systems were affected by this incident. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-23
39955 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-06-22 17:42 | 2003-06-22 21:18 | 2003-06-22 | AUTOMATIC REACTOR TRIP WITH AFW ACTUATION The following information was obtained from the licensee via facsimile: "In order to support maintenance on feeder W-98 [Distribution Line], 345 KV Circuit Breaker #3 was opened. Indian Point 3 remained in service utilizing the feed via 345 KV Circuit Breaker #1. After Con Edison completed maintenance on W-98, at 17:42 [EDT] an attempt was made to close 345 KV Circuit Breaker #3. While attempting to close 345 KV Circuit Breaker #3, a fault occurred, resulting in an automatic Generator Trip, Reactor Trip and Turbine Trip. "Automatic Safety Features operated as required, with all control rods inserting. "Decay heat is being removed by the Steam Generators, with make up provided by Auxiliary Feedwater with steam being relieved to the Main Condenser. "Off site power feeders remained available. Off Site power is currently stable and providing power to all 480 Volt Safeguards Buses. Automatic start and operation of the Emergency Diesel 'G' was not required." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-06-22
39954 | 0 | NUCOR STEEL |  |  |  |  | 2003-06-21 11:50 | 2003-06-21 13:50 | 2003-06-21 | SOURCE HOLDER FRAME AND CONTROL SYSTEM DAMAGED On 6/21/03 at approximately 1150 CST, a source holder frame that houses a 1 Curie Am-241 source was damaged. The licensee, Nucor Steel, uses the source to determine steel strip thickness. The source holder and the source are intact and the source is retracted into the safe position. Only the metal frame that supports the source holder and the source control system was damaged. The manufacturer, Radiometric, has been contacted to repair the frame. The source is exposed using an air signal which is currently locked and tagged out by the licensee. Informed R3DO (Riemer) and NMSS EO (Reamer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2003-06-21
39953 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2003-06-20 11:00 | 2003-06-20 17:50 | 2003-06-27 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the New Mexico Radiation Control Bureau: At 1750 EDT on 06/20/03, the Program Manager of New Mexico's Radiation Control Bureau reported a stolen Troxler Moisture Density Gauge (10 milli-curies CS-137 and 44 milli-curies Am-241). The licensee's employee reported that the gauge was in a box and chained to his truck at 2100 CDT last night, 06/19/03. Today, 06/20/03, at 1100 CDT when the employee reached the worksite in Ruidoso, NM, the gauge was missing. Apparently the chain had been moved enough to open the box. The licensee is Teracon, Lenexa, KS. The licensee was advised to report the incident to local law enforcement. *****UPDATE ON 6/27/03 AT 22:00 EST FROM MILLER TO LAURA***** The stolen gauge was found in a dumpster in Ruidoso, NM at 17:00 MDT on 6/27/03. There was nothing apparently wrong with the gauge assembly except the lock was not on the source rod. The licensee transported the gauge to their nearest facility at Las Cruces for a leak test. The FBI is actively involved in reviewing this theft and has been working with the New Mexico State Police. Apparently, an anonymous caller reported the location of the missing gauge. Notified NMSS EO (T. Essig), R4DO (G. Sanborn) and NSIR-TAT (R. Warren) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2003-06-25
39952 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-06-11 22:00 | 2003-06-20 16:08 | 2003-06-20 | OFFSITE NOTIFICATION TO STATE OF TENNESSEE MADE DUE TO LOSS OF POWER TO EMERGENCY SIRENS The following information was obtained from the licensee via facsimile: "On June 11, 2003, 23 of the 108 emergency sirens were out of service because of a storm passing through the area, causing power outages. The TVA Operations Duty Specialist notified the State of Tennessee of the loss of the sirens. This report is being made to NRC in accordance with 10 CFR 50.72(b)(2)(xi) as a situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been made. As power was restored to the area, the sirens were returned to service. "This report is being made at this time since Sequoyah Operations personnel have become aware that the State of Tennessee was notified by the TVA Operations Duty Specialist on June 11, 2003." The TVA Operations Duty Specialist is based in a location different from the Sequoyah plant. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-20
39951 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2003-06-20 | 2003-06-20 13:42 | 2003-06-20 | AGREEMENT STATE REPORT The following information was received from South Carolina Department of Health and Environmental Control via facsimile: "The SC Department of Health and Environmental Control was notified on June 20, 2003, by a representative from Geo-Systems Design and Testing, that a portable gauging device had been run over by a construction vehicle at a construction work site. The gauge is a Campbell Pacific Nuclear model 131 containing 10 [milliCuries] of cesium-137 and 50 [milliCuries] of Am-241:Be. The licensee is maintaining constant surveillance of the damaged gauge. The extent of damage at this time is unknown but the licensee has indicated the gauge is crushed. State inspectors are responding at this time and are traveling to the scene. Updates to this event will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0 | 2003-06-25
39950 | 0 | HIGH MOUNTAIN RADIOGRAPHERS |  |  |  |  | 2003-06-19 07:15 | 2003-06-19 15:30 | 2003-06-19 | STOLEN VEHICLE THAT CONTAINED RADIOGRAPHY CAMERA High Mountain Radiographers of Casper, WY reported to the NRC Region 4 offices that one of their trucks that contained a Spec-150 Radiography camera was missing and considered stolen. The suspect is an employee of the company in the position of assistant radiographer. The licensee and local law enforcement (Rock Springs, WY Police Department) were unable to locate the truck or the driver this morning. The truck is a white with green accents, 1997 F-250 pickup truck. The truck was last seen at 6 p.m. MDT on 6/18/03 in the possession of the assistant radiographer. The radiography camera contains a 71 Curie Iridium-192. The FBI has been notified. * * * UPDATE AT 21:33 EDT ON 6/19/03 FROM FRAZIER TO GOTT * * * Vehicle and driver have been located in Rock Springs, WY. The radiography camera and source were intact and not tampered with in any way. The licensee has possession of the vehicle. The assistant radiographer is in the custody of local law enforcement personnel. Notified DHS, FEMA, EPA, DOE, FBI, EPA, and USDA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-06-19
39949 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-06-19 07:30 | 2003-06-19 14:30 | 2003-07-11 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE [DELETED] , Director LA County Radiological Health Management of the CA Radiological Health Branch and [DELETED] Senior Health Physicist [DELETED] ) called to report that a Moisture Density Gauge (50 milli-Curies Am-241 and 10 milli-Curies Cs-137) (Manufacture Campbell Pacific, Model MC1, serial # 11114098) was stolen from a truck at 7:30 AM PDT. The truck was at 7-11 in Torrance, California and the driver was inside the 7-11. The driver noticed the missing material after he drove away from the 7-11. The licensee is AGI Geotechnical [DELETED] ). The Torrance Police Department was notified. * * * UPDATE ON 7/10/03 AT 0707 PM VIA EMAIL FROM R. GREGER * * * "On 6/19/03 AGI Geotechnical, a CA licensee, reported the theft that morning of one of its portable nuclear gauges from a convenience store in Torrance, CA. The gauge was taken from the bed of the operator's parked pick-up truck by someone who apparently cut the lock on the chain that locked the gauge to the pickup truck. The licensee reported the theft to the local police department and placed an ad in the local press offering a reward for the return of the gauge. On 7/7/03 the licensee reported having received a call from an individual in response to the reward ad. The individual indicated that he knew who had stolen the gauge and where it was. The licensee retrieved the gauge that day and returned it to its offices in Van Nuys, CA. A state inspector visited the licensee to physically inspect the gauge and confirm its identity. The gauge appeared to be in a normal condition, undamaged, with no evidence of a radiological hazard. However, the transport case for the gauge was cracked in several places and was missing DOT labels, so it would need to be replaced. The licensee will have the gauge checked and leak tested by the manufacturer's service representative to ensure that the radioactive source was not damaged." Notified TAS (Whitney) and R4DO (Kennedy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-06-24
39948 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-06-18 11:44 | 2003-06-18 13:27 | 2003-06-18 | UNIT COMMENCED A TS REQUIRED SHUTDOWN DUE TO AN INOPERABLE EDG "This 4-hour report is being made pursuant to 10CFR50.72(b)(2)(i). A unit shutdown was commenced at 11:44 on June 18, 2003 to comply with Hope Creek Generating Station Technical Specification (TS) 3.8.1.1 due to the inoperability of the 'A' Emergency Diesel Generator (EDG). "On June 15, 2003 at 04:35am, an excessive seal leak from the engine driven jacket water intercooler pump was identified, rendering the 'A' EDG inoperable and warranting entry into ACTION b of TS 3.8.1.1. That action requires the inoperable 'A' EDG to be returned to an operable condition by June 18, 2003 at 04:35. Corrective actions attempted thus far have been unsuccessful at eliminating leakage from the 'A' EDG jacket water intercooler pump seal. Engineering is continuing to evaluate the acceptability of the leakage from the seal. "All other safety related equipment is operable." The Unit is currently at 65% power and anticipates a full shutdown by 1600EDT. The licensee will inform both local agencies and the NRC resident inspector. * * * UPDATE 1725 EDT on 6/18/03 from Steven Nevelos to Bill Gott * * * "UPDATED: As of June 18, 2003 at 16:17, with reactor power at 42%, the unit shutdown to comply with TS 3.8.1.1 was terminated. The 'A' EDG has been declared operable but degraded with compensatory actions in place to maintain EDG operability. Corrective maintenance to repair the machine and eliminate the need for compensatory measures will be planned and performed in a timely manner." The licensee will inform both local agencies and the NRC resident inspector. Notified R1DO (Raymond Lorson). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-06-18
39947 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2003-06-17 16:20 | 2003-06-17 23:35 | 2003-06-17 | HPCS SYSTEM RENDERED INOPERABLE DUE TO PERSONNEL ERROR Text to follow from fax "While performing scheduled maintenance activities on SWP-P2C, Standby Service Water Pump P2C, operators inadvertently removed an adjacent 4160 volt switchgear breaker, E22-ACB002, which supplies the High Pressure Core Spray Pump, at 16:20 Central Daylight Time (CDT) on June 17, 2003 while operating at 100% power. The HPSC pump breaker is adjacent to the SWP-P2C breaker on the same switchgear. This action rendered the High Pressure Core Spray system (HPCS) inoperable and unable to fulfill the HPCS safety function to mitigate the consequences of an accident. This inadvertent action was immediately recognized by the control room operating team and immediate actions were taken to restore the system to operable. The pump breaker was promptly restored and functional testing of the HPCS pump was completed at 16:36 CDT on June 17, 2003. The High Pressure Core Spray system was restored to full operable status within 16 minutes. All other divisional Emergency Core Cooling Systems (ECCS) were operable. The Reactor Core Isolation Cooling System (RCIC) was also operable during this time period. Investigation into the removal of the HPCS pump breaker is in progress." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-06-17
39946 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-06-17 15:57 | 2003-06-17 18:47 | 2003-06-17 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO EQUIPMENT FAILURE "At 15:57 on 6/17/03, the network link used to activate all Emergency Sirens was inoperable. As a result of the failed link, a total of 154 sirens in Westchester, Orange, Putnam and Rockland Counties in New York were inoperable. The network link was restored at 16:44 on 6/17/03; all Emergency Sirens are currently operable. "Parties Notified: Westchester, Orange, Putnam and Rockland Counties, New York State and the IPEC NRC Resident Inspector were notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-17
39945 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-06-16 13:30 | 2003-06-16 20:36 | 2003-06-16 | UNEXPECTED ISOLATION SIGNAL DURING TESTING WHICH RESULTED IN A MOMENTARY LOSS OF SHUTDOWN COOLING "This event notification is being made to report an event that could have prevented the fulfillment of the safety function to remove residual heat. On June 16, 2003, the plant was shutdown in Mode 4 with reactor vessel level being maintained between 60-120 inches. Operators were performing surveillance testing on the manual pushbutton isolation logic to the Nuclear Steam Supply Shutoff System when an unexpected general outboard isolation signal was received. This resulted in the closure of RHR-V-8 (RHR shutdown cooling outboard containment isolation valve) and the interruption of shutdown cooling. Reactor Recirculation Pump B remained in service providing forced flow through the reactor core. Operators restored from the surveillance, reset the isolation signal, and reopened RHR-V-8. Shutdown cooling was restored 12 minutes after RHR-V-8 went closed. Reactor vessel level and temperature remained stable during the period shutdown cooling was not in service." The licensee's incident and review board determined that the procedure was deficient in that it did not alert operators to the isolation signal which functioned as required. The licensee will inform the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2003-06-16
39944 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-06-16 14:00 | 2003-06-16 19:45 | 2003-06-16 | 4-HOUR REPORTABLE INCIDENT FOR WHICH A PRESS RELEASE WAS MADE "A fluorine gas release occurred in the C-410K facility while operators were charging the gas system. The released gas caused a reaction which consumed a small section of the gas system piping. No detectable quantities of the gas were measured outside the affected facility. The Emergency Action Level classification criteria for fluorine releases was not met. The release was isolated by facility operators. The media requested information from the plant concerning the release and the plant provided a verbal statement. This statement constituted a 'media/press release' which required a 4 hour notification to the NRC as required by plant procedure UE2-RA-RE1030, 'Nuclear Regulatory Event Reporting'. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-06-16
39943 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-06-16 08:01 | 2003-06-16 13:03 | 2003-06-16 | INABILITY TO ACTIVATE EMERGENCY SIRENS DUE TO EQUIPMENT FAILURE "It was discovered on 6/16/03 at 0755 that the plant sirens (Prompt Alert Notification System) were out of service since Sunday 6/15/03 at 0757 [the cause appears to be a continuous signal being transmitted by a siren]. The system was restored to service at 0830 on 6/16/03." The licensee notified local authorities, the State and the NRC Resident Inspector. Similar incidents involving emergency sirens have been reported on 6/10/03 (See EN #39912) and on 6/11/03 (See EN # 39918). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-16
39942 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2003-06-16 07:43 | 2003-06-16 09:34 | 2003-06-16 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM FOR GREATER THAN 8 HOURS "At 0743 CDT on June 16, 2003, the Safety Parameter Display System (SPDS) was out of service for greater than eight hours due to the loss of the Nuclear Steam Supply (NSS) Computer, which provides the computer points for SPDS. "10CFR50.72(b)(3)(xiii), which states 'the licensee shall notify the NRC as soon as practical and in all cases within 8 hours of the occurrence of any event that results in the major loss of emergency assessment capability.' "The loss of SPDS is considered a major or loss of safety assessment capability. The site defines a 'major loss' of SPDS, 'when the SPDS function is not available in the control room for greater than eight hours.' This is consistent with NUREG-1022, EVENT REPORTING GUIDELINES 10CFR 50.72 and 50.73 section 3.2.13, Loss of Emergency Preparedness Capabilities. The NSS Computer went down at 2343 on June 15, 2003 (CDT). The eight-hour unavailability of SPDS expired at 0743 on June 16, 2003 (CDT). Repair efforts have been underway continuously to restore the NSS Computer and return SPDS to service. The expected return to service for SPDS is on June 16, 2003. All other plant conditions are normal." The licensee has notified the NRC Resident Inspector. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-16
39941 | 0 | GUTHRIE HEALTH CARE |  |  |  |  | 2003-06-12 | 2003-06-16 09:20 | 2003-09-05 | DISCOVERY THAT PART OF THE IMPLANTED SEEDS WERE NOT IN THE PROPER SITE A patient was referred for treatment, due to reoccurring prostate cancer, to the hospital where he had previously had treatment. Seeds were implanted around May 2001. A scan of the previous treatment of implanted seeds determined that many of the seeds were not located in the prostate, but in adjacent tissue where they would have been ineffective in treatment. Also, a review of the records indicated a scan was performed in early 2002, but was not followed up on. The patient and referring physician have been informed. The hospital is conducting an investigation into the event and also developing a plan to provide appropriate treatment for the patient. * * * UPDATE ON 07/18/03 AT 1638 FROM JOON PARK TO ARLON COSTA * * * Post-op dosimetry on one patient was determined to be a misadministration. The dose that covered the prostate was more than 20 percent different from the prescription as well as the penile bulb dose being close to 50 percent of the prescription dose. Efforts are being made to contact the affected patient. The licensee will continue efforts to obtain post-op dosimetry on the rest of the patients related to this incident so that evaluations for misadministration can be performed. Notified R1DO (Della Greca) and NMSS EO (Pierson). * * * UPDATE ON 07/25/03 AT 0921 EDT FROM JOON PARK TO JOHN MACKINNON * * * Post-op dosimetry for two patients were determined to be a misadministration. The patients had their prostates treated some time in the year 2001. The iodine-125 seeds were placed 2 to 3 centimeters below the area where they were supposed to be located. The improper location of the iodine-125 seeds caused more than 50% of the prescribed dose to be delivered to an un-intended organ. The patients will be notified. Notified R1DO (Dan Holody) and NMSS EO (Trish Holahan). * * * UPDATE ON 07/30/03 AT 0911 EDT FROM JOON PARK TO ARLON COSTA * * * Two additional patients of a group of seven were identified as having received a misadministration of iodine-125 to an unintended organ. The patients will be notified of this misadministration. The licensee is in the process of clarifying and document the issues related to this incident. Notified R1DO (James Moorman) and NMSS EO (Tom Essig). * * * UPDATE ON 08/07/03 AT 1535 EDT FROM CHARLES LEE TO NATHAN SANFILIPPO * * * Another patient has been identified who received a misadministration of iodine-125 to the prostate. The prescribed dose was 144 Gy, and it was delivered using 76 seeds and 27 needles as planned prior to the implant date. After reviewing the CT, which was done on Feb. 27, 2001, the V100 of the prostate received 29% of the prescribed dose. The penile bulb at 72 Gy received 44.8%. The licensee indicated that they have looked into 8 patients who may have been misadministered, of which, one was not declared a misadministration. The other seven appear in this notification. There are 23 total patients that the licensee intends to review. Notified R1DO (Clifford Anderson) and NMSS EO (Fred Brown). * * * UPDATE ON 08/14/03 AT 1150 EDT BY CHARLES LEE TO JOHN MACKINNON * * * Twelve more patients have been added to the number of patients. Patients are identified by a six digit number. Patient# [deleted]- On this date, March 21, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 77 seeds and 26 needles as planned prior to the implant, The V 100 of the prostate received 39% of the prescribed dose and the V50 of the penile bulb received 88%. Patient# [deleted]- On this date, May 23, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed close was delivered using 53 seeds and 18 needles as planned prior to the implant. The V100 of the prostate received 62% of the prescribed dose and the V50 of the penile bulb received 57%, Patient# [deleted]- On this date, December. 13, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 86 seeds and 21 needles as planned prior to the implant. The V 100 of the prostate received 70% of the prescribed dose and the V50 of the penile bulb received 99%. Patient# [deleted]- On this date, February 22, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 77 seeds and 25 needles as planned prior to the implant. The V100 of the prostate received 52.5% of the prescribed dose and the V50 of the penile bulb received 80%. Patient# [deleted]- On this date, March 15, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 67 seeds and 27 needles as planned prior to the implant. The V 100 of the prostate received 59% of the prescribed dose and the V50 of the penile bulb received 86.5%. Patient# [deleted]- On this date, July 5, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 62 seeds and 21 needles as planned prior to the implant. The VI 00 of the prostate received 49% of the prescribed dose. Patient# [deleted]- On this date, February 8, 2001, the former physician, prescribed a dose of 144-Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 45 seeds and 18 needles as planned prior to the implant. The V 100 of the prostate received 68% of the prescribed dose. Patient# [deleted]- On this date, September 5, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 58 seeds and 20 needles as planned prior to the implant. The V100 of the prostate received 59.5% of the prescribed dose. Patient# [deleted]- On this date, May 31, 2001, the former physician, prescribed a dose of 14-4Gy to the prostate using 1-125 seeds. The prescribed dose was delivered using 60 seeds and 17 needles as planned prior to the implant. The V1 00 of the prostate received 68% of the prescribed. Dose. Patient# [deleted]- On this date, January 22, 2001, the former physician, prescribed a dose of 144Gy to the prostate using I-125 seeds. The prescribed dose was delivered using 54 seeds and 3, 8 needles as planned prior to the implant. The V100 of the prostate received 73% of the prescribed dose, Patient# [deleted]- On this date, January 10, 2001, the former physician, prescribed a dose of 144Gy to the prostate using I-125 seeds. The prescribed dose was delivered using 58 seeds and 19 needles as planned prior to the implant. The VI 00 of the prostate received 54% of the prescribed dose. Patient# [deleted]- On this date, June 21, 2001, the former physician, prescribed a dose of 144Gy to the prostate using 1-125 seeds, The prescribed dose was delivered using 82 seeds 28 needles as planned prior to the implant, The V 100 of the prostate received 73% of the prescribed dose. Notified R1DO (Glenn Meyer) & NMSS EO (Linda Psyk). * * * UPDATE AT 1124 EDT ON 9/5/2003 FROM C. LEE TO ERIC THOMAS * * * Patient # [deleted] - On 10/3/2001, the former physician prescribed a dose of 144 Gy to the prostate using I-125 seeds. The dose was delivered using 67 seeds and 23 needles as planned prior to the implant. The V100 of the prostate received 72.5% of the prescribed dose. Patient # [deleted] - On 10/4/2001, the former physician prescribed a dose of 144 Gy to the prostate using I-125 seeds. The dose was delivered using 74 seeds and 30 needles as planned prior to the implant. The V100 of the prostate received 66.7% of the prescribed dose. Notified R1DO (Pam Henderson) and NMSS EO (Tom Essig) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | DOSE TO OTHER SITE > SPECIFIED LIMITS | [8 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) | 35.3045(a)(3) |  |  | 0 | 2003-06-16
39940 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-06-16 05:15 | 2003-06-16 08:38 | 2003-06-16 | VALID FEEDWATER ISOLATION SYSTEM SIGNAL GENERATED A valid feedwater isolation signal (FWIS) was generated while controlling steam generator water level near 82% wide range during heat-up activities to take the plant from Mode 4 to Mode 3. The set point for FWIS is 67% narrow range, which is relatively close to the 82% wide range the plant was being controlled. Level was allowed to get slightly higher which activated the FWIS. No isolation occurred as the valves were already closed and level was being maintained with auxiliary feedwater. Level has been restored to less than the set point. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-06-16
39939 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-06-15 09:28 | 2003-06-15 14:45 | 2003-06-15 | AUTOMATIC ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM WHILE IN HOT STANDBY "At 0928, on 6/15/03, with the reactor shut down in Mode 3, a feedwater isolation signal and an automatic start of both Motor-Driven Auxiliary Feedwater Pumps (AFW) occurred due to the trip of the last running Main Feedwater Pump. The event occurred as the plant operators closed the reactor trip breakers per plant procedure OP-104 in preparation for a reactor startup. The Main Feedwater Regulating Valves (MFRVs) were in automatic and the MFRV block valves were open. With reactor coolant system average temperature at less than 564°F and the reactor trip breakers open, a MFRV close signal is established via the P-4 permissive. Closing the reactor trip breakers removed the permissive P-4 block signal that was maintaining the MFRVs closed. This allowed the MFRVs to open to the full open demand position. With the MFRVs feeding the steam generators and no load conditions on the secondary plant, steam generator level exceeded the HI-HI level setpoint of 78%. This generated a turbine trip signal, a Main Feedwater isolation signal, and a trip of the Main Feedwater Pumps. The trip of the last running Main Feedwater Pump generated the automatic AFW actuation. This condition is being reported as actuation of Auxiliary Feedwater System in accordance with 1O CFR 50.72(b)(3)(iv)(A). "A reactor trip signal was not generated during this event and no control Rods had been withdrawn from the reactor core at the time of the event. "The NRC Resident Inspector was notified." The plant is stable in mode 3 and the AFW system is running to maintain steam generator levels. All systems functioned as required. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-06-15
39938 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-06-14 10:53 | 2003-06-14 14:32 | 2003-06-14 | REACTOR MANUALLY TRIPPED DUE TO MAIN FEEDWATER PUMP TRIP At 1053 ,on 6/14/03, the reactor was manually tripped from 100% in response to a trip of the "B" main feedwater pump (MFP). Both motor-driven auxiliary feedwater pumps and the turbine driven auxiliary feedwater pump auto started due to the lo-lo steam generator level. Operations personnel responded to the event in accordance with applicable plant procedures and the plant was stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip. The cause of the MFP trip is still under investigation. All rods fully inserted no ECCS actuation occurred and the PORV lifted and fully reseated. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-06-14
39937 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-06-13 20:21 | 2003-06-14 02:05 | 2003-06-14 | LOSS OF BOTH OFFSITE POWER SOURCES TO TECHNICAL SUPPORT CENTER "During severe thunderstorms in the area power was lost to the onsite Technical Support Center (TSC) for approximately 90 minutes. These storms caused both offsite power sources to the TSC to de-energize at 2021. Grid operators began restoration activities immediately and power was restored to the facility at approximately 2200. Investigation is in progress for the cause of the line tripping." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  |  | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-14
39936 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-06-12 16:20 | 2003-06-13 15:55 | 2003-06-13 | ARIZONA LICENSEE, UNITED DAIRYMEN OF AZ, DISCOVERED A DAMAGED HYDROGEN 3 EXIT SIGN At approximately 4:20 PM MST June 12, 2003, the Agency was informed by the General Licensee that they had discovered an EXIT sign containing Tritium was damaged. The sign contained 11.5 Curies of Tritium when installed. The General Licensee had no idea when the sign was damaged, in fact, he was surprised to learn that it contained radioactive material. The sign was a Safety Light Model XT. When the Agency arrived on scene, it was determined that the light tubes were all missing for this sign. One individual had used a ladder to attempt to replace the "light" bulbs since they were "burned" out. Wet wipes taken of the remains of the sign did not detect hydrogen 3. No one could tell the Agency of the condition of the glow tubes or where they are now located. The sign was located in a 30,000 square foot warehouse storing powdered milk. Evaporative coolers circulate cool air into the warehouse. The Agency continues to investigate this incident. The NRC and FBI will be notified of this event | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-06-18
39935 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-06-11 | 2003-06-13 15:14 | 2003-06-13 | SIX VIOLATIONS FOUND DURING RECENT INSPECTION AT A TEXAS LICENSED FACILITY On June 11, 2003 the Texas Department of Health, Bureau of Radiation Control conducted a follow up inspection of licensed activities at the Humana Hospital Day Surgery Center DBA The Surgical Center (TSC), Bryan, Texas. The inspection findings were discussed with Dr. Alikhan, Radiation Safety Officer and his staff In a preliminary exit briefing at close of inspection. Based on the results of his inspection., the Inspector has determined that at least 6 violations of the Agency requirements occurred. In addition, the violations were identified by this Agency rather than through the Licensee conducting Radiation Protection Program (RPP) audits. The Inspector reviewed five (5) total patients affected, since the last inspection by this Agency conducted on January 18, 2001. Utilization logs indicate that this number could increase given a review of the patients treated prior to January 18, 2001, with the use of the stroutium-90 eye applicator. Therefore, as discussed with the RSO during the exit briefing, additional information may be required of TSC before the Agency can make a determination to conclude this issue. The Inspector informed the Licensee that the number and characterization of apparent violations could change as a review Is conducted. Inspection Findings: Items of Noncompliance 1. Violation of 25 TAC §289.256(ee)(1)(a)(i): The Licensee failed to report and notify this Agency of a dose that differs from the prescribed dose by more than 5 rem (0.05 Sv) effective dose equivalent, 50 rem (0.5 Sv) to an organ or tissue, or 50 rem (0.5 Sv) shallow dose equivalent to the skin and either: a. the total dose delivered differs from the prescribed dose by 20% or more. 2. Violation of 25 TAC §289.202(e)(1): The Licensee failed to conduct a Radiation Protection Program (RPP), sufficient to ensure compliance with the provisions of §289.202. The RPP was not developed, documented, and implemented. 3. Violation of 25 TAC §289.201(g)(1)(b): The Licensee exceeded the six-month leak test interval for a sealed source of radioactive material for a 100mCi Sr-90 source, S/N 0214, during the time period from January 18, 2001 until June 4, 2003. 4. Violation of 25 TAC §289.256(p)(1)&(2): At the time of the inspection, the Licensee had failed to generate written directives signed and dated by an authorized user prior to administration of Sr-90 Brachytherapy. (i) prior to implantation: the treatment site, the radionuclide, number of sealed sources and dose; and (ii) after implantation but prior to completion of the procedure: the radionuclide, treatment site, number of sealed sources, total sealed source strength and exposure time or, equivalently, the total dose. 5. Violation of 25 TAC§289.256(bb)(6)(A)(B)(C)&(D): The Licensee failed to determine the calibration measurements of Brachytherapy sealed sources. 6. Violation of 25 T,AC §289.256(i)(2)(A)&(B): The Licensee's Radiation Safety Committee has not been composed of the required personnel. By evidence of the January 30, 2003 Radiation Safety Committee minutes that identifies representatives to attendance, the Radiation Safety Officer and an authorized user of type of use permitted (surgery) by the license, were not present. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-06-18
39934 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-06-13 | 2003-06-13 14:47 | 2003-06-13 | WRONG DOSAGE ADMINISTERED TO A PATIENT DUE TO HUMAN ERROR Discovery of right patient/ right radiopharmaceutical but wrong dosage. Patient returned after 48 hours for a scan. Doctor asked the tech for the prescription that was issued. The tech had ordered the wrong dose for the prescribed procedure. A thyroid scan was conducted with 2.3 millicuries of Iodine -131 vs. the required 300 microcuries of I-131. As corrective action any I-131 dose will require concurrence of the physician prior to ordering the dose. The cause was due to human error since the radiopharmacy sent the dose as ordered by the Tech. Both the referring physician and the patient have been informed of the error. The physician has stated that the dose error has caused no injury to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-06-18
39933 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-06-10 08:00 | 2003-06-13 13:00 | 2003-06-13 | ARIZONA LICENSEE, QUALITY TESTING, REPORTED A MISSING TROXLER MOISTURE DENSITY GAUGE "At approximately 8:00 AM MST June 10, 2003, Arizona was informed by the Licensee Radiation Safety Officer that they believe a Troxler Model 3411 B SN 4647 moisture-density gauge was missing and had been since 5:00 AM. At approximately 8:30 MST the Agency was informed that gauge fell off of the truck and had been recovered by JSW Concrete Contractor. The gauge was recovered from Price Road under the Fry Road Overpass. The Department of Public Safety and the Chandler Police were notified prior to recovery. The Licensee took possession of the gauge at approximately 9:00AM. There were no indications the gauge had been opened. Inspection by the State Agency revealed several possible violations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-06-18
39932 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-06-13 05:36 | 2003-06-13 08:51 | 2003-06-13 | MANUALLY REACTOR TRIP DUE TO INDICATION OF MISALIGNED ROD "While inserting Shutdown Bank "B" during the Rod Swap portion of physics testing, Rod J-7 indicated a rapid drop from approximately 100 steps to 47 steps on the CERPI (Computer Enhanced Rod Position Indication) panel. The reactor operator stopped insertion of "B" shutdown bank and the CERPI indication for rod J-7 remained at 47 steps. The remaining CERPIs in "B" shutdown bank varied from 96 to 100 steps "I&C and Engineering investigated and found no problems with the CERPI indication. Physics testing was terminated and the reactor was manually tripped and 1-E-0 initiated. All systems functioned as required on the trip. Rod Drop time data from the CERPI program shows all rods in Shutdown Bank "B" had a drop time 1.24 to 1.27 seconds with the exception of J-7, which had a drop time of 1.04 seconds. "An investigation is ongoing as to the cause of rod J-7 indication." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-06-13
39931 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-06-13 00:30 | 2003-06-13 02:44 | 2003-06-13 | EMERGENCY SIREN ACUTATED "Grand Gulf Control Room was notified by the Louisiana Office of Emergency Preparedness that an Emergency Siren was initiated. There is no reason for this siren to have actuated. The siren has been secured and deenergized. This event is being reported due to the local media broadcasting a no emergency message. The total number of emergency sirens remains above 75%(precent)." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-13
39930 | 0 | US AIR FORCE |  |  |  |  | 2003-06-10 | 2003-06-12 16:42 | 2003-06-12 | LOST EXIT SIGN The US air Force reported that one tritium exit sign was determined missing after an inventory check on 06/10/03 at Cannon AFB, NM. Prior to January - February contractor work the sign was accounted for. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-06-12
39929 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-06-11 | 2003-06-12 15:59 | 2003-06-12 | INCORRECT TREATMENT AREA DISCOVERED DURING A BREAST CANCER TREATMENT At the beginning of the 6th treatment the physicist discovered a geographic location error on the placement of a 3 curie +/- Iridium-192 source in the patient for treatment of breast cancer. Discovered an input error on the five previous treatments. Measurements should have been input to the Gamma Med Plus (HDR device) in millimeters were mistakenly entered in centimeters. Steps for the 20 millimeter source should have been in 1 millimeter increments. Therefore, the source was actually never in the patient's body. The physicist has estimated 70 Gray superficial dose to the skin at a depth of up to 1 centimeter. Deep dose (beyond 1 centimeter) is estimated at 30 Gray. The patient has developed a small red spot which is being monitored by the hospital for potential blistering. The patient and the hospital have agreed to re-start this patient's treatments. Corrective actions to prevent a re-occurrence of this event will follow with the Licensee's 15 day written report of the incident. Dose to original treatment site is in excess of 20% of the intended dose. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-06-17
39928 | 0 | US AIR FORCE |  |  |  |  | 2003-06-11 | 2003-06-12 15:53 | 2003-06-12 | AMERESIUM SOURCE LOST FOLLOWING F-16 CRASH The Air Force reported that a F-16 fighter jet crashed in Arizona near Luke AFB yesterday with a 8 microcurie Americium - 241 source. The source could not be found. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AZ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-06-12
39927 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-04-28 20:58 | 2003-06-12 14:43 | 2003-06-12 | INVALID ACTUATION OF A CONTAINMENT VENT ISOLATION VALVE The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73 (a)(2)(iv)(A) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of the WBN Train B Containment Vent Isolation signal. NUREG1022, Revision 2 identifies the information that needs to be reported as discussed below. (a) The specific train(s) and systems(s) that were actuated. On April 28, 2003, at 2058 EST, a Train B Containment Vent Isolation (CVI) signal was received when the hand switch for the containment purge radiation monitor was placed in off, unblocking the monitor. The high radiation alarm was still locked in following maintenance on the monitor and was not cleared before unblocking. The containment radiation monitor was inoperable and was removed from service at the time the signal was received. The CVI was not responding to an actual plant condition. (b) Whether each train actuation was complete or partial. The actuation was considered complete. The CVI signal for Train B automatically isolated the containment vent system. The containment radiation monitor was considered inoperable due to the maintenance. (c) Whether or not the system started and functioned successfully. Train B Containment Vent Isolation signal automatically actuated and functioned successfully. The CVI signal was not in response to an actual plant condition. The containment radiation monitors were returned to service and the containment vent air cleanup unit was also returned to service. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-06-12
39926 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-06-12 11:20 | 2003-06-12 12:09 | 2003-06-12 | NOTIFICATION AUTOMATICALLY MADE TO THE OFFSITE FIRE DEPARTMENT The well water booster pump catastrophically failed setting off the smoke detector which sent a signal to the fire protection panel resulting in an automatic notification to the fire department. The fire department responded, but there was no fire. The smoke detector was probably set off from smoke when the pump motor failed. The NRC was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-12
39925 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-06-11 23:45 | 2003-06-12 00:34 | 2003-06-12 | GREATER THAN 30% OF THE OFFSITE NOTIFICATION SIRENS OUT OF SERVICE DUE TO STORM Greater than 30% of the offsite prompt notification system sirens are out of service due to storm related loss of power. Repairs are presently in progress to restore power to the affected sirens (34 of 99). State and Local agencies have been notified to implement compensatory measures if required. The NRC Resident Inspector will be notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-12
39924 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2003-06-11 15:05 | 2003-06-11 18:30 | 2003-06-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE CHILLERS "At 1409 on 6/11/03, both Control Complex Chillers were declared inoperable. The inoperability resulted in an entry into ITS 3.0.3 due to the inability to comply with ITS 3.7.18. At 1505 CR-3 [Crystal River Unit 3] began a power decrease in compliance with the actions of ITS 3.0.3. This is a 4-hour reportable event as required by 10 CFR 50.72(b)(2)(i). "At 1618 on 6/11/03 the operating Control Complex Chiller was declared Operable and the actions of ITS 3.0.3 were exited. The plant has been returned to full power operation. "The safety significance of this event was small. The Control Complex cooling safety function was available through the use of existing procedures and available alternate cooling methods. At 1456, an available Control Complex Chiller was manually loaded and is currently providing all required cooling to the control complex in automatic mode." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-06-11
39923 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-06-11 14:53 | 2003-06-11 17:18 | 2003-06-11 | REACTOR PROTECTION SYSTEM ACTUATION DUE TO MAIN TRANSFORMER LOCKOUT RELAY TURBINE TRIP "At 1453 EDT on 6/11/03, Unit 1 experience a reactor trip due to a main transformer lockout relay turbine trip. All equipment operated as designed. 10 CFR 50.72(b)(2)(iv)(B). Main transformer 'C' appears to have an internal fault, [and] may need to be replaced. All control rods inserted fully. "A valid actuation of the Auxiliary Feedwater System resulted, due to the reactor trip. 10 CFR 50.72(b)(3)(iv)(A). The unit is stable, using main feedwater and condenser steam dump [as a means of heat removal]. All safety-related systems are available except for Unit 1 Emergency Diesel Generator which is out of service for maintenance. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-06-11
39922 | 0 | CONSOLE ENERGY INC |  |  |  |  | 2003-06-04 | 2003-06-11 15:12 | 2003-06-26 | MISSING OR LOST GAUGE CONTAINING A RADIOACTIVE SOURCE A Texas Nuclear Product pipe mounted fixed gauge device, model 5202, Series SG, serial number B174 containing a Cesium 137 (Cs-137), 500 millicuries source (assay date of November 1984) could not be located in storage. The gauge was removed from a pipe on the evening of 1/28/03 by an independent contractor who placed the gauge in a temporary storage on the morning of 1/29/03 at the Buchanan Mine Preparation Plant located in Mavisdale, Virginia. The gauge was closed and pad locked before it was placed in the small building storage room. The independent contractor and the plant foreman looked for the gauge on 6/2/03 and could not locate it. They continued looking for the gauge until 6/4/02 when they declared that it was missing. The licensee has no reason to believe that the gauge left the property, is retracing the steps of the gauge movement and is interviewing their employees in an attempt to locate the gauge. * * * UPDATE AT 0951 EDT ON 06/26/03 FROM REGION II IAT (BOLAND) to NRC HOC (GOTT) * * * The following was emailed from Region II: "The licensee searched their site for the gauge and interviewed employees who had access to the floc [floculant] building with negative results. "There are two waste streams in which the gauge may have left the plant: "The first is in scrap metal. Scrap metal waste goes to Mansbauch Metal in Ashland, Virginia. Incoming waste at Mansbauch must pass through an Exploranium portal monitor. The alarm set point for this type of monitor is normally set at twice background so they are very sensitive. The scrap metal is then put on a conveyor for further processing. Three Ludlum detectors monitor the loose scrap on the conveyor. The processed scrap must then pass through the portal monitor leaving the facility. The smelter accepting the scrap will also have a portal monitor. There were no alarms in the time period under consideration and there is no backlog of scrap at the facility. This does not seem to be a credible scenario for the loss of the gauge. "The second waste stream is for normal industrial waste. The local sanitary landfill is not used and, according to the licensee, all waste other than scrap metal is supposed to be sent to the industrial waste stream. The waste is transferred by H&K Trucking Co. to the Cumberland Plateau Regional Waste Management Authority in Lebanon, Virginia for waste consolidation prior to being sent to the BFI Carter Valley Landfill in Hawkins Co. Tennessee. Waste coming into the Cumberland facility is dumped on the floor and then loaded into a larger container for shipment to the landfill. Periodically, individuals at this facility remove metal such as soft drink cans for further sale to a scrap dealer. The BFI Landfill has a portal monitor and was sensitive enough to recently detect in a large waste shipment, a facial tissue used by an individual that had been administered Tc-99m. "On June 17, NRC inspectors discussed the issue with licensee representatives and surveyed areas of the site where the gauge might logically have been moved. The radiation detection instruments the inspectors used were sensitive enough to detect the gauge radiation unless it was significantly shielded above and beyond the shielding inherent in the gauge. The inspectors demonstrated that their survey instruments could easily detect the radiation from a similar gauge that was in place at the facility. The inspectors also traveled to the BFI landfill and discussed the issue with landfill operators. "The operators of the Cumberland Plateau facility issued a memorandum to staff describing the gauge and stating the importance of its recovery. The Buchanan facility management was to also issue a similar memorandum and claims to still be looking for the gauge." Notified NMSS (Broaddus), R2DO (Ogle), NRC IAT (Hahn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-06-11
39921 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-05-22 08:02 | 2003-06-11 14:49 | 2003-06-11 | INVALID ACTUATION AND VARIOUS SYSTEM ISOLATIONS DUE TO A FAILED RELAY "On May 22, 2003, at 0802 central time, while operating at 100 percent power, Grand Gulf Nuclear Station experienced an invalid actuation of the 'B' Containment, Drywell, and Auxiliary Building Isolation System. A failed relay caused a fuse to blow which resulted in actuation of the isolation logic for the 'B' Containment, Drywell, and Auxiliary Building Isolation System. This event resulted in isolation of the Plant Service Water (PSW), Plant Chilled Water (PCW), Drywell Chilled Water (DWCW), and Instrument Air (IA) to the Auxiliary Building. The PSW isolation caused loss of Component Cooling Water (CCW) in the Auxiliary Building and loss of Turbine Building Cooling Water. Reactor power was reduced to approximately 50 percent as a result of the loss of PSW." The licensee informed the NRC resident inspector. | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-06-11
39920 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-06-11 12:45 | 2003-06-11 14:42 | 2003-06-11 | SECURITY REPORT INVOLVING A PLANT SECURITY OFFICER Discovery of criminal act involving individual granted access to the site. Immediate compensatory measures taken upon discovery. The licensee informed local law enforcement and the NRC resident inspector. Contact the Headquarters Operations Officer for additional details. *** UPDATE ON 6/11/03 AT 2029 FROM D. POPP TO A. COSTA *** The non-licensed employee was determined to be under the influence of alcohol during a "for cause" test. The individual's access to all NMC facilities has been revoked. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | FITNESS FOR DUTY |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) | 26.73 |  |  | 0 | 2003-06-11
39919 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-06-11 12:17 | 2003-06-11 14:07 | 2003-06-11 | CONTROLLED PLANT TS SHUTDOWN DUE TO LOSS OF HVAC SYSTEM "On 6/11/03 at 12:17, the 'A' Control Structure Chiller tripped. The 'B' Control Structure Chiller was already inoperable for maintenance on the 'B' Chiller Fans. With the loss of Control Structure HVAC System the ability to maintain temperatures in various spaces including Relay rooms, Control Room Floor Cooling and Emergency Switchgear rooms was lost. Units 1 and 2 entered [Technical Specifications] TS 3.0.3 and a controlled shutdown of both units were commenced at 13:15. The 'A' Chiller was restarted at 12:47 and cooling was reestablished to the required areas, however the 'A' chiller is not considered operable at this time. The 'B' Chiller was placed in service and was declared operable at 13:20 [and the controlled shutdown of both units were terminated]." "This constitutes a Tech Spec required shutdown and requires a 4-hr ENS notification in accordance with 10 CFR 50.72(b)(2)(i). The failure also requires an 8-hr ENS notification in accordance with 10 CFR 50.72(b)(3)(v)(A-D) due to the loss of a safety function." The licensee notified the NRC Resident Inspector. | 100 | 98 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2003-06-11
39918 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-06-11 08:10 | 2003-06-11 13:46 | 2003-06-11 | INABILITY TO ACTIVATE EMERGENCY SIRENS DUE TO EQUIPMENT FAILURE "On June 11, 2003 at 0810 hours, the control room was notified that all Prompt Alert and Notification System (PANS) sirens were inoperable. All necessary notifications to local towns and MEMA (Massachusetts Emergency Management Agency) have been made. A backup plan (route altering) is in place in the event of an emergency at Pilgrim station. It was determined that one of the sirens was transmitting a continuous radio signal to the remaining sirens, preventing actuation. The faulty siren was isolated from the system at 1125 hours." The licensee informed both state and local agencies and the NRC resident inspector. This condition involving a different siren in the system occurred on 6/10/03. See EN #39912. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-11
39917 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2003-06-11 01:30 | 2003-06-11 02:26 | 2003-06-11 | AUTOMATIC TURBINE TRIP/REACTOR TRIP DUE TO HIGH HIGH STEAM GENERATOR WATER LEVEL "On 06/11/03, Unit 2 Reactor tripped via Turbine Trip due to high-high Steam Generator level. All Control Rods fully inserted. Unit stable in Mode 3 (Hot Standby). Auxiliary Feedwater system was manually started and currently maintaining steam generator levels. Investigation is in progress to determine initial cause for loss of feed to the 2A Steam Generator from its associated low power feedwater regulating valve." Coming out of a refueling outage reactor power was at 30% when it was noticed that main feedwater regulating valves were oscillating. Reactor power was reduced to 20% and the low power feedwater regulating valves were placed in service so testing of the main feedwater regulating valves could be performed. During testing of the main feedwater regulating valves at approximately 22% reactor power low power feedwater flow to the 2A Steam Generator ceased. The dual indications for the low power feedwater regulating valve indicated that the valve was open but Steam Generator 2A water level was decreasing. Since main feedwater regulating valve was being tested the 100% bypass low power feedwater regulating valve was opened. Steam Generator water level began to increase rapidly so the valve was closed. 2A Steam Generator level began to decrease so the 100% bypass low power feedwater regulating valve was reopened. This time 2A Steam Generator water level increase above 88% narrow range which caused an automatic turbine trip. Since reactor power was greater than 15% the reactor automatically tripped due to the turbine trip. All rods fully inserted into the core. Since the reactor core had very little decay heat the main steam isolation valves were closed and both motor driven auxiliary feedwater pumps were manually started. Motor Driven Auxiliary Feedwater Pumps and Steam Generator PORVs operation is maintaining the plant in a Hot Standby condition. All emergency core cooling systems are fully operable and the emergency diesel generators are fully operable if needed. The electrical grid is stable. The licensee believes that the stem of the low power feedwater regulating valve separated from the valve which in turn caused the valve to close while still having dual indication that the low power feedwater valve was open. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-06-11
39916 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-06-10 17:20 | 2003-06-10 22:28 | 2003-06-10 | LOSS OF OFFSITE EMERGENCY RESPONSE CAPABILITY DUE TO DAMAGED POWER LINE Power to the Emergency Operations Facility (EOF) was unavailable for approximately two and a half hours due to a severe thunderstorm and a downed power line feeding the facility. An Emergency Diesel Generator (EDG) is running, supplying power to the EOF. The licensee notified the NRC Resident Inspector. *** UPDATE AT 2311 EDT ON 6/10/03 FROM J.R. WEEKLEY TO A. COSTA *** The downed power line to the EOF has been repaired and electricity to the facility has been restored. The licensee terminated use of the EDG. The NRC Resident Inspector will be notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-10
39915 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-06-10 12:11 | 2003-06-10 17:50 | 2003-08-01 | INADEQUATE I & C CABLE SEPARATION DISCOVERED DURING APPENDIX "R" REVIEW "McGuire has identified that Unit 1 and Unit 2 electrical cables associated with redundant safe shutdown trains do not meet the separation criteria of Appendix R. Specifically, cables for all four channels of a Unit's Reactor Protection System (RPS) are routed together through the respective Unit's ETA Switchgear Room. This room has no fire detection or suppression capabilities in the area containing the cables. Consequently, in the event of a postulated Appendix R fire in the ETA Switchgear Room, all four channels of the respective Unit's RPS could be susceptible to fire damage. Upon discovery of this condition, a fire watch was established in the Unit 1 and Unit 2 ETA Switchgear Rooms. "McGuire has not yet determined whether this condition would result in the loss of a safety function significantly degrading plant safety. However, since this condition is similar to an example provided in NUREG 1022 Section 3.2.4, McGuire is conservatively reporting this as an unanalyzed condition significantly degrading plant safety." The licensee informed the NRC resident inspector. * * *Retraction on 08/01/03 at 1034 EDT by Tom Arlow taken by MacKinnon * * * "Subsequent evaluation has concluded that the condition identified in the event report 39915 does not significantly degrade plant safety since the affected Unit would remain capable of proceeding to a safe shutdown condition should the subject RPS trains experience fire damage. In addition, probabilistic risk assessment of this condition determined it has low safety significance. Therefore, McGuire is retracting Event Report 39915." R2DO (Jim Moorman). The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-06-10
39914 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2003-06-10 08:40 | 2003-06-10 15:17 | 2003-06-10 | AGREEMENT STATE REPORT - REFINERY FIRE INVOLVING POTENTIAL DAMAGE TO NUCLEAR GAUGE The following agreement state report was received at the Operations Center via fax: "Radiation source involved in fire [at 500 West St Bernard Hwy, Chalmette, LA]. The gauge was closed and had normal readings of 0.25 mR/hr. Area barricaded and restricted. A leak test was being performed. The gauge was being overnighted to Ohmart for analysis. The gauge contained 1600 mCi [millicuries] of Cs-137." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-06-13
39913 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-04-16 | 2003-06-10 15:40 | 2003-06-10 | AGREEMENT STATE REPORT - PATIENT OVEREXPOSURE DUE TO MISADMINISTRATION The following agreement state report was received by the NRC Operations Center via email: "This is notification of an event in Washington State as reported to the Washington Department of Health, Division of Radiation Protection. "STATUS: new and closed "Licensee: Swedish Hospital and Medical Center "City and State: Seattle, Washington "License Number: WN-M008-1 "Type of license: Broad B (medium broad) "Date of event: 16 April 2002 (the department was notified on 16 May 2003 after the licensee performed a standard QA case review. The licensee submitted a full report of the incident, dated 29 May 2003). "Location of Event: 747 Summit Avenue, Seattle, Washington "ABSTRACT: An error occurred due to incorrect determination of treatment time. Treatments are planned by use of a graph. This treatment called for a 3.0 mm vessel. When the graph was used to determine treatment time, a time for using a larger vessel was incorrectly selected. This resulted in an extended treatment causing a 25% overexposure to the patient. "When licensee staff discovered the error, the treatment protocol was changed to require two qualified people to independently verify that the treatment/dwell time has been correctly established. This changed was made as a result of their case review procedure. "There was no media coverage. A Departmental investigation was not performed due to the length of time between incident and notification, and that the licensee had performed a self-imposed corrective action. The department will follow-up during routine visits to ensure that the licensee is operating per the new protocol. "What is the notification or reporting criteria involved? Misadministration "Activity and Isotope(s) involved: 53.5 mCi (maximum), Strontium-90/Yttrium-90 as sealed sources. "Overexposures? The patient was the only person overexposed. There was no overexposure to any member of the treatment team, staff, or general public. "Lost, Stolen or Damaged? Not Applicable "Disposition/recovery: Treatment procedures were amended to require written review of the intended treatment by both Radiation Oncologist and Radiological Physicist. "Leak test: 21 February 2002, by the manufacturer. "Vehicle: Not Applicable "Release of activity? None "Activity intended: Not Applicable "Misadministered activity received: Not Applicable "Device: Novoste Beta-Cath, source train # 484/00. "Exposure: (intended/actual); 18.4 Gy/23 Gy "Consequences: Licensee now uses protocol that requires two people who independently verify the correct vessel size, dwell time, and intended dose. The excess exposure is not expected to produce any undesirable effects. "Was patient or responsible relative notified? Yes "Was written report provided? Yes "Was referring physician notified? Yes "Consultant used? No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-06-13
39912 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-06-10 09:30 | 2003-06-10 12:36 | 2003-06-10 | INABILITY TO ACTIVATE EMERGENCY SIRENS DUE TO EQUIPMENT FAILURE "On June 10, 2003 at 0930 hours, the control room was notified that all 112 Prompt Alert and Notification System (PANS) sirens were inoperable by maintenance personnel. All necessary notifications to local towns and MEMA (Massachusetts Emergency Management Agency) have been made. A backup plan (route altering) is in place in the event of an emergency at Pilgrim station. It was determined that one of the 112 sirens was transmitting a continuous radio signal to the remaining sirens, preventing actuation. The faulty siren was isolated from the system at 1040 [hours], and the remaining 111 sirens are now operational." The licensee informed both state and local agencies and the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-10
39911 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2003-06-05 19:49 | 2003-06-10 11:31 | 2003-06-10 | FAILURE IN RADIOACTIVE GAS RELEASE MONITORING EQUIPMENT DEGRADES ACCIDENT MITIGATION SYSTEM The following information was received from the licensee via facsimile: "At approximately 19:49 hours [EDT] on June 5, 2003, during a source check of containment radiation monitor R-11 with containment pressure relief in progress, the containment pressure relief isolation valves, V12-10 and V12-11, would not close automatically. The valves were closed by use of the control switch in the control room to stop the pressure relief of the containment at the time of the source check failure. The source check should have caused the valves to close automatically by the initiation of a containment ventilation isolation signal. The penetration was isolated at 20:47 hours by the use of closed and de-activated automatic isolation valve; specifically valve V12-10 was closed and de-activated, in accordance with Technical Specifications Limiting Conditions for Operation (LCO) 3.6.3, Containment Isolation Valves, Required Action B.1. Subsequent evaluation, during review of the condition report for this failure, has determined that the failure, which was caused by a faulty control switch, would have prevented the automatic closure of these valves as required for a containment isolation or a containment high radiation signal. Therefore, this event is being reported as a condition that alone could have prevented the fulfillment of a safety function of a structure, system, or component that is needed to control the release of radioactivity or mitigate the consequences of accident, in accordance with 10 CFR 50.72(b)(3)(v)(C) and (D). The control switch was repaired at approximately 14:13 hours on June 6, 2003, and the system was restored to operable status at that time. A planned and monitored gaseous release from the containment was in progress at the time of this event using the containment pressure relief system. No release limits were exceeded. If plant conditions had required isolation of the penetration, alarms and indications in the Control Room would have alerted the operators to the condition and the applicable operating procedures direct the operators to manually isolate the penetration. "(The following information is system description information for the Containment Pressure and Vacuum Relief System copied from the H. B. Robinson Steam Electric Plant, Unit No. 2, Updated Final Safety Analysis Report): "Normal power operation is conducted with the closed containment building at essentially atmospheric pressure. The Containment Pressure and Vacuum Relief System is provided to control variations in containment pressure with respect to atmospheric pressure. These variations are due to changes in atmospheric pressure and leakage from the Instrument Air and Penetration Pressurization Systems. The containment pressure and vacuum relief system includes separate 6 inch lines penetrating the containment, each equipped with two quick-closing, tight-seating, 125 psi air operated butterfly valves, one inside and one outside containment. These valves are designed to fail closed on loss of control signal or control air, and are closed during normal plant operation, except as required for pressure control. "The butterfly valves are protected by debris screens, located inside containment and attached to the inboard pressure and vacuum relief valves, which will ensure that airborne debris will not interfere with their tight closure. The pressure relief line discharges to the plant vent through a HEPA filter and charcoal filters. These filters are provided for removal of particulate and halogen radioactivity from the vented air. Operation of the pressure and vacuum relief lines is manually controlled by the plant operator. A narrow range pressure transmitter continuously indicates containment pressure in the Control Room. Separate high and low pressure alarms are actuated by this transmitter to alert the operator to overpressure and vacuum conditions. These alarms are tentatively set for actuation at plus and minus 0.3 psig. Vacuum relief can be accomplished without regard to atmospheric conditions. In the event of pressure buildup, the operator will be guided by atmospheric conditions, and by the containment particulate and radiogas monitor in relieving the overpressure. Manual operation of both these lines is overridden by automatic containment isolation and containment high radioactivity signals." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-06-10
39910 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-05-21 11:55 | 2003-06-09 21:18 | 2003-06-09 | TEMPORARY LOSS OF RESIDUAL HEAT REMOVAL PUMP USED FOR SHUTDOWN COOLING "This event notification is being made to report an event that could have prevented the fulfillment or the safety function to remove residual heat. On May 21, 2003, the plant was shutdown in Mode 5, with reactor pressure vessel (RPV) level being maintained greater than 22 feet above the RPV flange. Technicians were performing routine maintenance and removed an electrical lead from the wrong relay. As a result of removing the wrong lead, Residual Heat Removal (RHR) valve RHR-V-9 closed after receiving a close signal. RHR-V-9 is one of two primary containment isolation valves in the common suction piping to both RHR shutdown cooling loops. The valve closure caused pump RHR-P-2A to trip resulting in a loss of RHR shutdown cooling, and a loss of forced flow through the reactor core. Natural circulation was verified. RHR shutdown cooling could have been promptly restored if desired, but the plant remained in natural circulation to support other maintenance activities. The RHR-V-9 isolation logic was reset 31 minutes after the isolation occurred, at which time RHR-A was declared operable. This event was originally deemed to be not reportable by Columbia. This 8 hour report is being made 19 days after the event date." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2003-06-09
39909 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2003-06-09 16:50 | 2003-06-09 17:15 | 2003-06-09 | OFFSITE NOTIFICATION DUE TO UNSCHEDULED RELEASES "At 1650 the Maine Emergency Management Agency and Department of Human Services were notified of unscheduled releases that occurred on Friday 6/6/03 and Saturday 6/7/03 [at Maine Yankee]. Both releases were from vacuum drying of fuel canisters. "On Friday 6/6/03 Maine Yankee released 0.258 Curies of gas; 0.158 Curies of this release exceeded the value projected for this period and is therefore classified as unscheduled. The total gas release resulted in an exposure of approximately 0.001 millirem and occurred from 1930 to 2400. "On Saturday 6/7/03, Maine Yankee released 0.308 Curies of gas; 0.208 Curies of this release exceeded the value projected for this period and is therefore classifieds as unscheduled. The total gas release resulted in an exposure value of approximately 0.001 millirem, and occurred for the 24 hour period of 6/7/03." The licensee will place this information in their public information tape as a means of press release. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-09
39908 | 0 | US ARMY |  |  |  |  | 2003-06-03 | 2003-06-09 13:28 | 2003-06-09 | CHEMICAL AGENT ALARM DETECTOR POTENTIALLY LOST FROM MAINTENANCE SHOP A chemical agent alarm detector, model M22, containing a 30 millicuries Ni-63 (nickel) source was turned in to the Michigan Army National Guard owning unit maintenance shop in Lansing, Michigan for calibration in February 2003. On June 3, 2003 the owning unit reported to the Radiation Protection office of the US Army Soldier Biological Command, Aberdeen, MD, via email that the maintenance shop could not locate the detector. This incident is currently under investigation and a preliminary report will be written within 21 days followed by a final report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-06-09
39907 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2003-06-05 16:47 | 2003-06-05 17:25 | 2003-06-05 | OFFSITE NOTIFICATION TO STATE AGENCIES INVOLVING UNSCHEDULED RELEASE The following information was provided by the licensee via fax: "Notified Maine Emergency Management Agency of unscheduled release that occurred on Monday June 2, 2003. Notified Department of Human Services of same. "Maine Yankee released 3E-8 curies of liquid. 3E-8 curies of this release exceeded the value projected for this period and is, therefore, classified as unscheduled. The total liquid release resulted in an exposure value of 1E-8 millirem. "This unscheduled release resulted from low levels of Cs-137 exiting the restricted area via a storm drain, and occurred throughout the 24-hr time period from 6-2-3." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-06-05
39906 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-06-03 | 2003-06-05 16:50 | 2003-06-05 | TWO TROXLER MOISTURE DENSITY GAUGES DISCOVERED ABANDONED On 6/3/03 during a special inspection for non-payment of license fees, state inspectors found the Abiotic Enterprises facility located at 2320 South Portland in Oklahoma City closed and, by all appearances, defunct. The landlord who is located in the same structure said that his tenant, i.e., Abiotic Enterprises, was five (5) months in arrears on rent and that he had not seen any activity for more than a month. The state inspectors entered the business with the assistance of the landlord and found two (2) Troxler Moisture Density Gauges, a model 3430 S/N 29405 and a model 3440 S/N 29452, inside an unlocked caged area. The cases containing the gauges and the source rods were also found unlocked. Oklahoma has revoked Abiotic Enterprises license subject to administrative appeal. On 6/4/03, both Troxlers were impounded by the state and are currently in storage within the OK rad program vault. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2003-06-10
39905 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-06-05 15:45 | 2003-06-05 16:44 | 2003-06-05 | LOSS OF 2 OFFSITE EMERGENCY NOTIFICATION SIRENS AT INDIAN POINT On 06/05/03 at 1644 EDT the licensee reported that 2 of 16 emergency notification sirens located in Orange County failed on 06/05/03 at 1545 EDT due to a loss of power. An investigation is underway to determine the cause and restore power to the affected sirens. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-05
39904 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2003-06-05 | 2003-06-05 13:15 | 2003-06-07 | AGREEMENT STATE REPORT INVOLVING A MISSING WELL LOGGING SOURCE SHIPMENT On 6/5/03, the NM Rad Control Program Office was notified by SpectraTek that one of four boxes in a shipment of well logging sources sent from SpectraTek in Albuquerque via FEDEX on 6/2/03, airbill #791397943907, to Elite Air Freight in Houston, TX was missing. The missing box contains a 40 millicurie Scandium-46 source. The shipment which is enroute to Nigeria is currently being held in Houston pending resolution of the missing source issue. Elite Air Freight contacted FEDEX who believes that the package has been located in the Houston area. NM State Report #NM-03-04. * * * UPDATE 1342EDT 6/6/03 FROM MIKE BREWER (SPECTRATEK) TO S. SANDIN The missing box containing the 40 millicurie Scandium-46 source was located and delivered to Elite Air Freight in Houston, TX the morning of 6/6/03. Notified R4DO(Loveless), NMSS(Broaddus), DOE(Bailey), and EPA RegionVI(Hammack). * * * UPDATE 1540EDT 6/6/03 FROM PAUL PATRICK (FEDEX) TO S. SANDIN Due to an administrative oversight, the wrong airbill was updated showing delivery. FEDEX is still investigating and attempting to locate this shipment. Notified R4DO(Loveless), NMSS(Broaddus), DOE(Bailey), and EPA RegionVI(Hammack). * * * UPDATE 1730EDT 6/7/03 FROM MARVIN SUDDUTH TO GERRY WAIG * * * The missing package was located at approximately 1645EDT at the Houston-Hobby Satellite facility in the Dangerous Goods area with no indication of damage or tampering. A FEDEX security specialist is currently escorting the package to the main FEDEX facility for safe storage over the weekend. FEDEX will make arrangements to have a management representive deliver the package to the receipt on Monday morning and will inform SpectraTek. Notified R4(Loveless, Maier ), R2(Landis), NMSS(Holahan, Broaddus, Miller), EDO(Kane), OSTP(Lothaus), DOE(Turner), EPA RegionVI(Hammack), and DHS(Svenningsen). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2003-06-10
39903 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-06-04 11:15 | 2003-06-04 19:03 | 2003-06-05 | APPENDIX R ISSUE During an Appendix R design basis review, an Engineer noted that cables associated with normal operation of components used for one train (Primary Isolation Valves) of Appendix R mitigation were routed through an adjacent fire zone associated with the other train of Appendix R mitigation. During an Appendix R event, control of the affected components is transferred to the Standby Shutdown Facility, which electrically isolates the subject cables. However, the area containing the subject cables does not have fire detection equipment. The Engineer noted that if a fire occurred and damaged the cables, it would be theoretically possible for a "smart short" to result in damage to equipment before action could be taken to transfer control to the Standby Shutdown Facility. Initial Safety Significance: This condition is similar to an example given in NUREG 1022, Section 3.2.4 (fire barrier missing such that the required degree of separation for redundant safe shutdown trains is lacking). In order to result in a loss of safety function, the postulated fire would have to damage the cable, result in a smart spurious actuation of a component, damage that component such that it became inoperable (such as by burning out the motor of a valve), then also spread within the fire zone to damage the redundant component (for example by burning the power cable or motor control center). The Oconee license basis is no spurious circuit operations for 10 minutes. Cable testing sponsored by the NRC, NEI, and EPRI for fire exposure has demonstrated that armored type cable construction used in this application is more rugged than other designs and that internal cable failure times usually extend beyond 30 minutes. The area containing the cables is a high traffic area for both personnel and material - including low quantities of transient combustibles, but has no appreciable fixed fire loads. Thus the probability of a fire of sufficient energy to damage the cable is low. Pending a PRA analysis, it appears reasonable to credit prompt discovery of a fire and initiation of action to suppress the fire and/or transfer of control to the Standby Shutdown Facility prior to cable damage. Therefore the overall risk impact of this event is currently considered low. Corrective Action: The SSF has been declared inoperable pending establishment of a fire watch. The NRC Resident Inspector will be informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-06-05
39902 | 0 | ST. BARNABAS MEDICAL CENTER |  |  |  |  | 2003-06-03 09:30 | 2003-06-03 15:13 | 2003-06-03 | SOURCES IN PATIENT FOUND TO HAVE MIGRATED DURING TREATMENT After 17 hours of irradiation with a cesium-137 source, it was discovered that the source was capable of migrating along a tube that was 16 centimeters long. While the Doctors thought the sources (left and right tubes) were at the 0 centimeter position in the tube they were probably at various locations in the tube during the patient's treatment. Spacers were not placed in the tubes to prevent the cesium-137 sources from moving. During the 17 hours the sources were in the patient the patient laid flat on his/her back but the patient was allowed to move his/her legs and move back and forth. The movements of the patient caused the sources (one cesium-137 source in each tube) to move up and down the tubes. At the end of 17 hours it was found that one of the sources was at the far end of the tube instead of being at the other end of the tube (0 centimeter position). Doctor of the patient was informed of this incident. Patient was not harmed by this error. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2003-06-03
39901 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-06-01 06:14 | 2003-06-03 13:44 | 2003-06-03 | STATE OF NEW YORK AND ORANGE COUNTY NOTIFIED On June 3, 2003 at approximately 1006 hours, a review of siren data from June 1, 2003 revealed that four (4) of a total of 16 sirens in Orange County experienced a power failure. The power failure lasted from approximately 0614 until restoration at 0819 hours. The two (2) hour power failure was caused by damage sustained to a power pole in Orange and Rockland utility system. Route alerting was available during the loss of sirens. The NRC Resident Inspectors, State and Orange county were notified of this event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-06-03
39900 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2003-06-02 14:00 | 2003-06-02 15:28 | 2003-06-02 | WEEKLY SILENT EMERGENCY SIREN TEST FAILED The weekly silent testing of St Marys county failed to transmit the test signal resulting in 17 out of 17 emergency siren test failures. St Marys county will have to perform route alerting until the emergency sirens have been restored to service. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2003-06-02
39899 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2003-06-02 09:00 | 2003-06-02 11:50 | 2003-06-02 | LINE BREAK IN FIRE PROTECTION SYSTEM While adding a new component, Hydrogen Fluoride Mitigation Tower (sprays water on an HF release), to their fire protection system when an underground line break to the fire protection system occurred between the Fluorine Plant and the Feeds Material Building. The fire protection system line break was isolated via valves and the water leak was stopped. Proper Fire Protection System pressure has been restored. All Safety system are covered by the Fire Protection System. NRC Residents Inspectors at Paducah were notified of this event by Honeywell International. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2003-06-02
39898 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-06-01 08:50 | 2003-06-01 11:00 | 2003-06-01 | REACTOR SCRAM FROM 98% POWER DUE TO LOAD REJECTION "At 0850 EST [6/1/03] Pilgrim Station received a full reactor scram from 98.5% power from the Main Generator lockout relay tripping. The Main Generator lockout relay caused both 345 KV output breakers to open and caused a load reject scram. "All systems operated as designed. Received expected alarms and isolations [as follows]: Group 2 C PCIS, Primary Containment Isolations, Reactor Building isolation, Group 6 (Reactor Water clean up isolation). Isolations [were] due to normal post scram level shrink to +2 inches. Isolations occur at +12. "Preliminary indications are a fault on Unit Aux. Transformer." All control rods fully inserted. There was no ECCS actuation and the lifted Safety Relief valves seated properly. The unit is currently stable in the hot standby mode of operation. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-06-01
39897 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2003-05-28 16:30 | 2003-05-31 13:40 | 2003-05-31 | NRC BULLETIN 91-01, 4 HOUR REPORT The following is taken from a facsimile report from the licensee to the NRC Operations Center. "Short Description/Event Title: Enriched uranium rods mixed with Maine Yankee boron carbide poison rods. "Consequences - details: This material was always within our control. The identification and tracking of the material was deficient. Additionally, the necessary controlled parameters to assure nuclear safety were not established or maintained for the specific location and configuration in which the rods were stored. "Immediate action taken: Rod downloading personnel were instructed to obtain the pin-stamped number from each rod that is determined to contain uranium, which will aid subsequent investigation. The remaining rods in the storage box were evaluated for extent of condition, and the potentially containing uranium have been segregated to an approved location to further ensure their favorable configuration. Key personnel at Hematite and Columbia were also informed of the issue. "Full Description: Three uranium-bearing fuel rods were identified at approximately 1630 hours on May 28, 2003 as part of a zircaloy scrap recovery project. The scrap recovery effort is being conducted inside the rod loading room of Building 230, and involves tubing from a Maine Yankee fuel fabrication campaign conducted by the previous owner, ABB, in 1997. The fuel was never shipped to Maine Yankee due to that plant's subsequent shutdown. The fuel rods were opened by ABB, and the enriched uranium pellets were recovered during the first quarter of 1998. The boron carbide (B4C) poison rods were not opened at that time. The B4C rods are now being downloaded by a Westinghouse sub-contractor for recovery of the zircaloy cladding. When opened, three rods from the last box to be downloaded were found to contain uranium pellets rather than B4C, Because of the potential of finding at least some pellets, all operations were being conducted under appropriate radiological controls. An additional 21 rods from that last box that have been identified as suspect due to their weight difference. They have been put aside at an approved location, but not yet opened for verification. "Additionally, a separate box of rods containing what appears to be depleted uranium were also identified about two weeks ago. The preliminary determination of the contents being depleted uranium is based on their physical characteristics and markings. These rods are still under investigation to confirm that they contain depleted uranium. During the period of storage, this material was stored in the warehouse portion of Building 230, which is located within the fenced and protected area of the site. This material was always within our control, but the identification and tracking of the material was deficient. In response to this issue the following actions have been taken: "A review of the reporting requirements of 10 CFR Parts 70.50, 74.11, 73.71 and Appendix G of Part 73 established that this issue does not meet the requirements for formal reporting. Nevertheless, a courtesy call was placed this afternoon to the D&D Project Manager at NRC Region III. A high level CAPS item, has been established for tracking of all actions taken regarding this matter. A Root Cause Analysis will also be conducted. Consideration was given to whether this issue should be treated as an extension of the Kardex issue that was the subject of a separate report, but it appears that it would be appropriate to treat this matter separately due to the differing circumstances. Arrangements have been made to have an independent review conducted at the site to determine if additional measures should be taken in locating material. This is expected to occur next week. "Plant management initially assessed this situation as unreportable to the NRC for material control aspects as noted above. It was also assessed as not reportable under NRC Bulletin 91-01, Supplement 1, 'Reporting Loss of Criticality Safety Controls,' because of the following criticality safety aspects: "The as-found condition was bounded by existing analysis for rod channel boxes formerly used in the manufacture of fuel rods; The as-found condition was safe due to the extensive amount of absorber, in the form of B4C rods, surrounding the uranium rods; The as-found condition was safe due to the inability for introducing moderator because a lid was secured on the storage box. The box was stored on a cantilever rack that further precluded the possibility of flooding. "Nevertheless, a courtesy call was placed within 24-hours of discovery to the facility's Project Manager at NRC Region III. Further review has determined that the as-found condition was not bounded by the rod channel box analysis, but is bounded by fuel assembly analyses. Additionally, the situation is now assessed as reportable under Bulletin 91-01 because the necessary controlled parameters to assure nuclear safety were not established or maintained for the specific location and configuration in which the rods were stored. A formal 91-01 report, Number 39897, has therefore been made to the facility's NRC Project Manager and the NRC Operations Center." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | MO | FUE | [5 empty] | 0 | 2003-05-31
39896 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2003-05-30 22:00 | 2003-05-31 01:07 | 2003-05-31 | LOSS OF COMMUNICATION DUE TO UNAVAILABILITY OF SIRENS "At about 2200 [CDT] on 5/30/03, greater than 25% of the CPS [Clinton Power Station] notification sirens became unavailable due to a loss of AC power. Fourteen sirens are unavailable at this time [due to inclement weather], eleven constitutes 25% lost for greater than one hour." The licensee has notified the State Police, will notify the NRC Resident Inspector and is in the process of restoring availability of the inoperable sirens. *** UPDATE AT 0555 EDT ON 5/31/03 FROM KEN LEFFEL TO ARLON COSTA *** Availability was restored to all sirens, except four. The licensee will notify the NRC Resident Inspector. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-31
39895 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-05-30 18:55 | 2003-05-30 22:36 | 2003-05-30 | LOSS OF OFF-SITE EMERGENCY NOTIFICATION SIRENS AT WOLF CREEK "At 1755 CST 5/30/2003 power was lost to the Otter Creek and Jacobs Creek Emergency Notification sirens. Lake Siren #2 has been out of service since 5/28/2003 due to lightning damage. Station procedures consider the loss of three or more Emergency Notification Sirens for greater than one hour a major loss of emergency assessment capability reportable under 50.72(b)(3)(xiii). "At 2108 CST station monitoring equipment indicated that power had been restored to the Otter Creek and Jacobs Creek Sirens." The licensee has notified the NRC Resident Inspector and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-30
39894 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2003-05-30 08:30 | 2003-05-30 16:54 | 2003-06-05 | SECURITY GUARD POSTED WITHOUT PROPER EQUIPMENT A plant security officer was stationed at a security post without all equipment required to properly man that post. Immediate compensatory measures were taken upon discovery. The licensee notified the NRC Resident Inspector. Refer to the Headquarters Operations Officer Log for additional details. * * * UPDATE AT 1220EDT ON 6/5/03 FROM ANDREW WISNIEWSKI TO S. SANDIN The licensee upon further review concluded that the incident was logable and is, therefore, retracting this report. The licensee informed the NRC Resident Inspector. Notified R1DO(Linville). Contact the Headquarters Operations Officer for details. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-05-30
39893 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-05-30 13:30 | 2003-05-30 15:21 | 2003-05-30 | RECEIPT OF CONTAMINATED MATERIAL IN EXCESSOF 10 CFR 71.87 LIMITS "On May 30, 2003 at 1330 CDT Duane Arnold Energy Center (DAEC) confirmed receipt of a material shipment with removable surface contamination that exceeded the limits of 10 CFR 71.87 (20.1906 d.1) of 22,000 dpm/100 square cm. The shipment, a transfer cask intended for future dry storage, had 23,496 dpm/100 square cm of non-fixed external contamination. The contamination was found upon receipt of the cask during routine receipt surveys. This shipment was a surface contaminated object (SCO), with less than type A quantity of radioactive material." The licensee has notified the NRC Resident Inspector. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW | [5 empty] | 0 | 2003-05-30
39892 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-05-27 | 2003-05-29 17:19 | 2003-05-30 | AGREEMENT STATE REPORT - ARIZONA The following information was obtained from the Arizona Radiation Regulatory Agency via facsimile: "On May 27, 2003, a patient was administered 27 mCi of Iodine-131 (Iodide) instead of the prescribed dose of 5 mCi. Initial investigation indicates that Medi-Physics Inc. had mistakenly sent a 27 mCi dose designated for AMI to Phoenix Baptist Hospital and the 5 mCi dose for Phoenix Baptist Hospital to AMI. It appears that the 27 mCi dose had been accurately assayed by the Technician, had been noted to differ from the requested 5 mCi, but had been administered to the patient anyway. It should also be noted that the patient had a thyroid ablation procedure conducted previously. Medi-Physics Inc. and Phoenix Baptist Hospital are investigating the situation and a report from each will be forthcoming. "The Agency and licensees will continue to investigate this occurrence and report further." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-06-03
39891 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-05-29 21:18 | 2003-05-30 00:43 | 2003-05-30 | 161 KV WAS DECLARED INOPERABLE DUE TO THE PREDICTED POST TRIP VOLTAGE BELOW SETPOINT The following information was obtained from the licensee via facsimile: " [Abnormal Operating Procedure] AOP-31 '161KV GRID MALFUNCTIONS' was entered due to the predicted post trip 161 KV voltage dropping to 160.6 KV on the PCMMINT [Personal Computer Monitoring of Missouri, Iowa and Nebraska Transmission] computer monitoring program. 161 KV was declared inoperable due to the predicted post trip voltage being below the 160.7 KV setpoint. Tech Spec 2.7(2)C, 72 hour LCO was entered. Both emergency diesel generators are operable. "Main generator VARS [Volt-Amperes Reactive] were raised from 100 to 150 MVARS lagging in an attempt to raise predicted post trip voltage. Predicted voltage rose above 161 KV for approx. 5 minutes and then lowered below 161 KV again to 160.8 KV and is now fluctuating. System Operations was notified and stated that 161 KV actual voltage remained at approx. 164 KV and that the electrical grid was stable. "Design Engineering was notified and hypothesizes that MAPP [Mid-America Power Pool] values into PCMMINT program may not be valid and that they will attempt to validate the inputs." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2003-05-30
39890 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-05-28 07:30 | 2003-05-29 12:40 | 2003-05-29 | DISCOVERY OF A CONTROLLED SUBSTANCE WITHIN THE KEWAUNEE PLANT PROTECTED AREA "On 5/28/03 at approximately 0730 CDT on-site testing of a substance proved positive for a controlled substance. The substance was found by a member of plant staff on the plant grounds within the protected area. The plant staff member took possession of the substance and immediately contacted Security staff personnel for assistance. There were no personnel noted in the area of the substance [at the time of discovery]. After confirming the substance, it was turned over to Kewaunee County Sheriff's Department." Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2003-05-29
39889 | 0 | UNIVERSITY OF PENNSYLVANIA |  |  |  |  | 2003-05-29 | 2003-05-29 08:54 | 2003-05-29 | LOSS OF RADIOACTIVE SOURCE "On Tuesday April 29, 2003, a laboratory supervisor at the Hospital of the University of Pennsylvania (HUP) notified Environmental Health and Radiation Safety that a package of 250 [microcurie] of P-32 was not received by her lab as expected on April 25, 2003. The package was shipped as an excepted package not subject to external labeling. "The package was delivered by materials management staff and left in the hallway near the laboratory with other supplies instead of being delivered directly to the lab as required. "The radiation safety investigation determined that housekeeping staff removed the package unopened from the hallway and disposed of it in the regular trash. Based on the activity and exposure rate, this package did not present an exposure to any employee or member of the general public. "Corrective actions have been initiated with laboratory, materials management and housekeeping staff to prevent reoccurrence." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-05-29
39888 | -1 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-05-29 02:39 | 2003-05-29 05:43 | 2003-07-25 | DEGRADED ACCIDENT MITIGATION FEATURE The following information was obtained from the licensee via facsimile: "On 05/29/2003 at 0239 [CDT], during performance of 3-SR-3.5.1.7, HPCI [High Pressure Coolant Injection] Main and Booster Pump Developed Head and Flowrate Test at Rated Reactor Pressure, following release of the HPCI Trip Push button, the HPCI Turbine Stop Valve, 3-FCV-73-18, did not return to the OPEN position as required by the surveillance. The SR [Surveillance Requirement] was stopped. "This is reportable as an 8 hour report in accordance with 10CFR50.72(b)(3)(v)[(D) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.' "This is also reportable as a 60 day written report in accordance with 10CFR50.73(a)(2)(vii) as 'Any event where a single cause or condition caused at least one independent train or channel to become inoperable in a single system designed to: (D) Mitigate the consequence of an accident.'" The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 07/25/03 @ 1456 BY NACOSTE TO GOULD * * * RETRACTION This report is being retracted. Upon further evaluation, it was determined that failure of the HPCI stop valve to re-open, (after successful performance of the HPCI flow test) did not result in a condition that could have prevented the fulfillment of the safety function. The HPCI stop valve did not re-open due to failure of the overspeed trip device to reset. This overspeed trip device only actuates during a HPCI turbine overspeed condition or it can be manually actuated to test the stop valve trip and reset function. In this case, since no overspeed condition occurred, the actuation was most likely the result of testing activities. HPCI reset following an overspeed trip is not a safety function of HPCI, and is not credited in the accident analysis for HPCI. Therefore, the failure of the HPCI stop valve to reset and reopen is not a condition that could have prevented the fulfillment of the safety function of HPCI, and this event is not reportable. The NRC Resident Inspector was notified. Notified Reg 2 RDO (Anne Boland) | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-05-29
39887 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-28 11:00 | 2003-05-28 23:00 | 2003-05-28 | BULLETIN 91-01 24-HOUR REPORT At 1100 [CDT] on 5/28/03, approximately 1/8 inch layer of water was discovered in the bottom of NAM [Negative Air Machine] 2000-4 in the C-310 truck alley in violation of NCSA GEN-09. GEN-09 prohibits the use of NAMs on spraying/wet operations where intake could contain droplets of moisture. This control prevents uranium from being washed off the filters into an unsafe configuration in the bottom of the NAM. The NRC Resident Inspector has been notified of this event. PGDP Assessment and Tracking Report No. ATR 03-1592, PGDP Event Report No. PAD-2003-012. SAFETY SIGNIFICANCE OF EVENTS: The amount of fissile material accumulated in the bottom of the NAM, does not exceed residual quantities. This indicates, with high confidence, that less than a safe mass is present. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) In order for a criticality to be possible, greater than a critical mass of uranium must be accumulated then become moderated. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC) Double contingency is maintained by implementing two controls on mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Less than an always safe mass of uranium. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The first leg of double contingency is based on mass. NCSA GEN-09 requires that D/P measurements be performed for each NAM filter section each time the machine is placed in service and immediately prior to taking the machine out of service. This control provides a means for detecting material that has been removed from the filter into an unsafe geometry in the bottom of the NAM. These checks were performed; therefore, this control was not violated. The second leg of double contingency is based on mass. NCSA GEN-09 prohibits the use of NAMs on spraying/wet operations where intake could contain droplets of moisture. This control prevents uranium from being washed off the filters and into an unsafe configuration in the bottom of the NAM. The control was violated since a water spray is used at the burp station to cool the cylinder. However, since only a residual amount of uranium (less than an always safe mass) was washed off the filter, the parameter has been maintained. Since double contingency is based on two controls on one parameter, and a control was violated, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Change filters according to CP4-GP-BG2108. 2. Decon the residual amount of uranium at the bottom of the NAM according to CP4-CU-CH2103. 3. While investigating this incident, a concern was identified as to whether or not the system configuration has been adequately analyzed for NCS purposes. The NAM shall remain out of service until the system configuration issue has been resolved, at which time the exclusion zone and postings may be removed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-05-28
39886 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2003-05-24 12:00 | 2003-05-28 18:44 | 2003-05-28 | OFFSITE NOTIFICATION On 5/24/03, Maine Yankee left an inaccurate message on their answering service that provides the public with information regarding the daily release of radioactivity from the site. Due to the vacuum drying of spent fuel that was being transferred from the fuel pool to dry storage casks, the daily gaseous release from the site on 5/24/03 was 0.1 Curies, which disagreed with the level of 0.01 Curies that was left on an information telephone recording that the public can access. On 5/28/03, the licensee discovered this administrative error and informed the Maine Emergency Management Agency and the Maine Department of Health and Human Services. The Region 1 Duty Officer was informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-28
39885 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2003-05-28 11:34 | 2003-05-28 12:38 | 2003-05-28 | RPS ACTUATION At 1134 EDT on 5/28/03, Calvert Cliffs Unit 2 experienced an automatic reactor trip. The cause of the trip appears to be loss of load caused by a main turbine trip on either reverse power or overspeed. The turbine trip may have been caused by planned troubleshooting on the turbine governor valve controls. All control rods inserted normally on the trip. One or both pressurizer power operated relief valves lifted and immediately re-seated following the trip. The steam generator atmospheric valves opened and immediately closed following the trip. All Emergency Diesel Generators and ECCS systems are operable, and the licensee plans to conduct a quick trip recovery. The licensee notified the NRC Resident Inspector, and the Calvert County Control Center of this event. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-05-28
39884 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2003-05-23 16:30 | 2003-05-27 12:49 | 2003-05-27 | AGREEMENT STATE REPORT On 5/22/2003, the licensee sent a shipment of radioactive material to Elite Airfreight in Houston, TX. On 5/23/2003 at approximately 1630 MDT, Elite Airfreight contacted the licensee to inform them that only 2 of the 3 boxes of radioactive material in the shipment had arrived in Houston. The licensee contacted Federal Express, who tracked the missing package to the Fedex facility in Memphis, TN. Fedex planned to send the missing package to Houston on 5/24/2003. As of 5/27/2003, the package still had not arrived in Houston. The licensee contacted Fedex again, and was told the package was still in Memphis, and would be shipped to Houston today (5/27/2003). The missing package is a 12X12X12 inch fiberboard box containing 40 millicuries of Antimony-124, and has a Transportation Index of 4. This event is state of New Mexico event number NM03-02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2003-05-30
39883 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-05-23 15:50 | 2003-05-27 10:17 | 2003-05-27 | MALFUNCTION OF A HIGH DOSE RATE AFTERLOADER During a heart procedure at the Union Memorial Hospital in Maryland with a Galileo III (HDR - High dose rate afterloader) device using a Phosphorus - 32 source wire, of up to 600 millicuries, a malfunction occurred with the active wire in place in the patient's heart. When the source was to be retracted the source would not retract. The physician utilized the machine interrupt to try to get the source to move to the shielded position and it failed. The physician then pushed the system STOP button to get the source to retract and it also failed to perform the retraction. The physician then moved to the hand-wheel to retract the source, but this function also malfunctioned. At this point the physician pulled the entire catheter and dropped it to the Operating Room floor. The power cord was then removed from the wall receptacle depriving the machine of power and then the source retracted to the fully shielded position. The licensee was informed that this would constitute a Therapy Event within the State of Texas and the state would need a complete report and an emergency read of all badged personnel in the OR during the procedure. The Licensee responded that the machine was not within the State of Texas. A report to the state of Texas is still required by License Condition # 16 due to failure of the drive mechanism of the GALILEO III to retract the source to safe storage until the fourth emergency procedure was performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-05-30
39882 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2003-05-26 22:15 | 2003-05-27 05:32 | 2003-06-17 | REACTOR COOLANT SYSTEM PRESSURE/TEMPERATURE TS LIMITS WERE EXCEEDED At 2215 on 5/26/03 it was noted that Reactor Coolant System (RCS) Pressure/Temperature Limits for Non-Nuclear Heatup or Cooldown Following Nuclear Shutdown, Figure 3.4.9-1 of Technical Specifications, had been exceeded. This condition occurred due to Bottom Head Temperature being low due to a loss of forced circulation when Reactor Recirculation Pumps tripped during the manual scram reported in notification 39881. Reactor pressure was lowered and compliance with the curves has been reestablished. An analysis of this condition is required to be conducted in accordance with Technical Specification Required Action 3.4.9 A.2 to determine RCS acceptability for continued operation. The Reactor is required, as per LCO action statement, to be placed in Mode 4 by 1045 on 5/28/03. The NRC Resident Inspector was notified. * * * UPDATE 1614EDT ON 6/17/03 FROM ED McCUTCHEN TO S. SANDIN * * * The licensee is retracting this event based on the following: "Retraction of Event Notification 39882: "On May 27, 2003, Cooper Nuclear Station reported that Reactor Coolant System (RCS) Pressure/Temperature (P/T) Limits for Non-Nuclear Heatup or Cooldown Following Nuclear Shutdown, Figure 3.4.9-1 of Technical Specifications, had been exceeded (Reference Event 39882). This condition occurred when Reactor Recirculation Pumps tripped during the manual scram reported in Event 39881. With the loss of forced circulation, stratification of the reactor coolant occurred and the resultant bottom head (Lower Plenum) temperatures were below the Technical Specification limit. "The condition was reported in accordance with 10 CFR 50.72(b)(3)(ii)(A) as an event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. "CNS was in Mode 3 (Hot Shutdown) when the P/T Limits were exceeded. Reactor pressure was lowered and compliance with the curve was reestablished. Per Limiting Condition for Operation (LCO) 3.4.9, Condition B, required Action B.2, the reactor was required to be in Mode 4 (Cold Shutdown) by 1045 on May 28, 2003. The reactor was placed in Mode 4 at 0844 on May 27, 2003. "The Technical Specification required evaluation to determine that the RCS is acceptable for operation prior to entering Mode 2 (Startup) or Mode 3 has been completed. The evaluation determined that pressure and temperature data recorded during the condition demonstrate that the P/T Limits were maintained for the Upper Vessel/Steam Dome and Beltline Regions for the duration of the event. "The recorded data for the Lower Plenum exceeded TS Figure 3.4.9-1 which is a composite curve established by superimposing limits derived from stress analyses of those portions of the reactor vessel and head that are the most restrictive. The analysis developed a bottom head (Lower Plenum) specific P/T curve using bottom head specific stresses and material properties. Considering this bottom head P/T curve, the evaluation results demonstrate that region specific P/T Limits for the Lower Plenum region of the vessel were maintained for the duration of the event. "This event is bounded by the existing fatigue analysis for a loss of Feedwater Pumps. The transient has been captured in the fatigue monitoring program. The vessel usage factor of 1.0 has not been exceeded. Consequently, the reactor vessel maintains adequate structural integrity for continued operation. "CNS is retracting this event based on the evaluation which demonstrates that the plant safety barrier (RCS) was not degraded." The licensee informed the NRC resident inspector. Notified R4DO(Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-05-27
39881 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-05-26 17:27 | 2003-05-26 21:47 | 2003-05-26 | MANUAL REACTOR SCRAM This report is being made in accordance with 10CFR50.72 section (b)(2)(iv)(A), (b)(2)(iv)(B), and (b)(3)(iv)(A). At 1727 on 5/26/03 a manual Reactor Scram was inserted from approximately 90 percent power due to high vibration on the main turbine. This action was taken in accordance with station procedures. The subsequent shrink caused reactor water level to lower to approximately -42 inches below instrument zero on the wide range level instruments. This level was low enough to cause the actuation of: Primary Containment Group Isolations 2, 3, and 6, High Pressure Coolant Injection (HPCI) system, Reactor Core Isolation Cooling (RCIC) system, and the Alternate Rod Insertion (ARI) system. The HPCI and RCIC systems injected for less than one minute. After Reactor water level recovered HPCI and Reactor Feed Pumps (RFP) were tripped prior to receiving the high water level trip of these pumps. The RCIC turbine tripped automatically on high reactor water level. A single RFP has been restarted and is currently providing feed water to the Reactor. On the Scram all rods inserted and all systems appear to have functioned as designed. The Nebraska Public Power Load Dispatcher reports that the electrical grid is stable. The plant is currently in Mode 3 and is being cooled down to Mode 4. When operators first noted the high turbine vibration, reactor power was lowered from 100 percent to 90 percent. The maximum specification for turbine vibration is 14 mils, and the operators noted a maximum indication of 12.5 mils prior to the scram. The cause of the excessive vibration is believed to be the number 5 bearing on the low pressure turbine. All Emergency Core Cooling Systems and Emergency Diesel Generators are operable. The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-05-26
39880 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2003-05-25 21:45 | 2003-05-25 23:12 | 2003-05-25 | INADVERTENT ACTUATION OF EMERGENCY SIREN # 38 IN DORCHESTER COUNTY, MARYLAND Emergency Siren # 38 inadvertently actuated in Dorchester County, Maryland at 1610 EDT. Dorchester County Emergency Response Center drove out to the Emergency Siren and verified that the Emergency Siren had actuated. Dorchester County Emergency Response Center notified Calvert Cliffs Nuclear Power Plant at 2145 EDT that Emergency Siren # 38 had actuated. Some kind of atmospheric anomaly caused the Emergency Siren to actuate. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-25
39879 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2003-05-15 12:00 | 2003-05-23 14:58 | 2003-05-23 | MISSING/LOST STATIC ELIMINATOR POLONIUM-210 SOURCE. On May 22, 2003, the MA Radiation Control Program received a letter, dated May 16, 2003, from Sipex, Corporation, a general license holder, notifying them that Sipex Corp. was missing one Static Eliminator source. The Static Eliminator was manufactured by NRD and it contained four Po-210 sources. The Po-210 sources are located in the fitting of an air line. On May 15, 2003 the air line was relocated to a different location. After the air line had been relocated it was discovered that one of its four Po-210 sources was missing. Sipex Corp. believes that the source is still in the facility or it ended up in the trash. The calculated Po-210 source strength as of May 23, 2003 is 1.6 millicuries. The State of MA tracking number for this event is 05 4172. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2003-05-28
39878 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2003-05-22 12:00 | 2003-05-22 15:45 | 2003-05-22 | LOST NDC GAUGE "During an inspection of a general licensee in Dothan, AL, the Agency has discovered that an NDC Model 103 gauge (S/N 2112), containing one 150 millicurie Americium 241 source is unaccounted for. The device was purchased by Ludlow Coated Products in Dothan, AL. That plant closed and the three GL gauges were supposedly transferred to another Ludlow plant in Mississippi in 2000. The plant was then acquired by Twitchell Corporation (another GL licensee of this Agency's). During our inspection of Twitchell, questions arose regarding the whereabouts of the 3 GL gauges from the site once registered to Ludlow. Investigations by Twitchell representatives resulted in documentation of the transfer of 2 of the devices, but no information regarding the NDC device. The investigation and search for the lost device is continuing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2003-05-27
39877 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-05-13 12:00 | 2003-05-22 14:10 | 2003-05-22 | RADIATION TREATMENT TO WRONG AREA The Ohio Department of Health Bureau of Radiation Protection received a report of misadministration from University Hospitals of Cleveland on May 20, 2003. The report involved a Brachytherapy prostrate therapy with Iodine-125 seeds. The total amount of activity administered was 20.0 millicuries. Preliminary indication is a treatment to the wrong target area. A written report will be sent to the Ohio Department of Health within 15 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-05-27
39876 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-05-22 12:00 | 2003-05-22 12:32 | 2003-05-22 | WORK STOPPAGE BY IBEW LOCAL 1289 UNION. IBEW Local 1289 Union personnel implemented a work stoppage and started exiting the site at 1200 hours this date (05/22/03). Required watch stations are being relieved by management personnel. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-22
39875 | 0 | TERRACON CORPORATION |  |  |  |  | 2003-05-21 | 2003-05-21 18:08 | 2003-05-21 | DAMAGED MOISTURE DENSITY GUAGE A moisture density gauge owned by the licensee was damaged when it was run over at a construction site in Raymore, Missouri (Hwy. 58 at Lauris Dr.). The gauge is a Campbell Pacific model CPN1DR containing a 10 millicurie Cs-137 source and a 50 millicurie Am-241:Be source. The gauge has been isolated and it has been determined that the sources appear intact. The licensee is the process of retrieving the gauge for return to the manufacturer. Notified R3DO (A. Stone), R4DO (T. Pruett), R4 (Mark Shaffer), NMSS EO (L. Camper) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2003-05-21
39874 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-05-21 13:55 | 2003-05-21 17:32 | 2003-05-21 | LOSS COMMUNICATION DUE TO MORE THAN 10% AVAILABILITY OF SIRENS "On May 21, 2003 at 1355 hours, during on site monitoring of the offsite emergency notification system, three (3) sirens out of a total of 10 in Putnam County indicated a communications failure. The cause for the failure was subsequently determined, based on information obtained by the crew, to have been attributed to communication failure due to fuse failure at the sirens. Communication was fully restored to the affected sirens at approximately 1549 hours on May 21, 2003. Route alerting was available during the loss of sirens. "The NRC resident inspectors, State and Putnam county were notified of this event." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-21
39873 | 0 | S.K. GEOTECHNICAL CORPORATION |  |  |  |  | 2003-05-21 07:00 | 2003-05-21 13:06 | 2005-02-09 | STOLEN MOISTURE DENSITY GAUGE A Campbell Pacific Nuclear portable moisture density gauge Model MC-3, Serial Number MC 39058846 was stolen from the licensee's storage trailer. The gauge contains a cesium-americium-beryllium radioactive source (10 millicuries Cs-137 and 50 millicuries Am-241/Be). The licensee's trailer containing the stolen gauge was located at a Home Depot construction site, 1801 Custer Ave, Helena, MT 59601. Helena City police is investigating this and other thefts that occurred overnight at several trailers located at this same site. The licensee contacted Region IV (M. Shaffer) and will contact the Montana Department of Health. * * * UPDATE ON 02/09/05 @ 1819 BY GREG STAFFILENO TO CHAUNCEY GOULD * * * The licensee was contacted by another company which also uses moisture density gauges to inform them they had in their possession the stolen gauge. The individual that had the device spotted it for sale on the street in Los Angeles CA for $20 and bought it. The devise appeared to be in good shape but has been taken to a local gauge service company where it will be checked out before it is returned to the original licensee. Notified Reg 4 RDO (Whitten) and NMSS EO(Reamer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-05-21
39872 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-05-21 04:18 | 2003-05-21 11:31 | 2003-05-21 | ACCIDENT MITIGATION DEGRADED DUE TO PRESSURE SWITCHES OUTSIDE TECHNICAL SPECIFICATION ALLOWANCES "During calibration of Dresden Unit 2 Electromatic Relief Valve/Target Rock Valve Pressure Switches, two of the five pressure switches were found outside the Technical Specification (TS) Allowable Range and outside the Analytical Limit (1.5 psig above the TS Allowable). Setpoints for the B and C Electromatic Relief Valves (ERVs) were found at 3.1 and 2.4 psig above the TS allowable respectively. The TS Bases state that four ERVs are required to accomplish the safety function for pressure mitigation. This event is reportable because two of five ERV pressure switches were outside TS allowables, which could have prevented fulfillment of the safety function for pressure mitigation (10 CFR 50.73(a)(2)(v)]. The pressure switch setpoints have been subsequently calibrated and returned to within TS allowable values." The licensee notified NRC Resident Inspector. | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-05-21
39871 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2003-05-21 02:20 | 2003-05-21 09:15 | 2003-05-21 | FAILURE OF THE SECURITY FORCES HAND HELD RADIOS Security at the site had a partial loss of their radio system. Their Bay station and telephone communications systems were up, but the hand held radios could not transmit out. These radios, however could receive. This problem has occurred in the past. Their communications people were able to reboot the system and go back to the secondary and returned the radios back to service. There was no evidence that equipment had been tampered with. The NRC Resident will be notified. | 98 | 98 | 98 | 98 | 98 | 98 | -1 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW | [5 empty] | 0 | 2003-05-21
39870 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-20 19:15 | 2003-05-21 00:08 | 2003-05-21 | CRITICALITY CONTROL 24-HOUR REPORT (BULLETIN 91-01) The following information was received from the regulatee via facsimile : "At 1915 on 5/20/03, the Plant Shift Superintendent (PSS) was notified that some removed process gas equipment item groups in C-720 have not received proper independent mass verification in violation of NCSA GEN-010. The group mass is required to be independently verified to be within always safe mass limits. This is done by independently verifying the equipment item mass is correctly copied onto the grouping sheet. An entry was discovered on the grouping sheet in which the mass on the equipment was 0 [zero] pounds, however the GEN-010 tag on the equipment item indicated a mass of 284 pounds of uranium at 1.38% enrichment. Additionally, several equipment items were tagged with GEN-010 tags that had information lined out and corrected, appearing to violate the independent verification of the equipment item mass, on the tag. This information was then subsequently used for grouping purposes on the equipment grouping sheet. This is a legacy issue, as the dates on the tags are from the 97-98 timeframe. "SAFETY SIGNIFICANCE OF EVENTS: "Double contingency was not maintained because the independent verification of mass has not been performed. However, the policy for the shop is to only allow items which have been fully decontaminated into the shop, which gives high confidence that less than a safe mass is present. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "In order for a criticality to be possible, greater than a critical mass of uranium must be accumulated [and] then become moderated. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Double contingency is maintained by implementing two controls on mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "Less than an always safe mass of uranium. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The first leg of double contingency is based on mass. NCSA GEN-010 requires that the total uranium mass of grouped items be verified less than the UH [Uncomplicated Handling] mass limit and documented. The mass of an equipment item was incorrectly copied onto the grouping sheet. However, the listed mass for the item is UH at the listed enrichment. In addition, other items in the group have tags, which indicate no visible contamination but have been updated and only have one signature. This mass was then used in the grouping. The control was violated, however the parameter has been maintained. "The second leg of double contingency is based on mass. NCSA GEN-010 requires that the total uranium mass of grouped items be independently verified less than the UH mass limit and documented in accordance with CP2-PO-FO1031 [a facility procedure]. The independent verification was incorrectly performed; therefore, this control was violated. Since there are two controls on one parameter, double contingency was not maintained. "Since double contingency is based on two controls on one parameter, and a control was violated, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Ensure each item in the group is properly tagged according to CP2-CO-CN2030 [a facility procedure]. Properly group and document each equipment item according to CP2-CO-CN2030. Upon completion of the above corrective actions, the exclusion zone and postings may be removed." The regulatee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-05-21
39869 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-20 09:30 | 2003-05-20 23:46 | 2003-05-21 | SAFETY EQUIPMENT FAILURE The following information was obtained from the regulatee via facsimile: "05/20/03 at 0930 hrs. following the investigation into circumstances surrounding NRC Event #39853 (PTS-2003-011 update #1), the Plant Shift Superintendent's (PSS) office was notified that the air supply line to the parent cylinder safety valves had been disconnected during applicable TSR mode III (Cylinder/Pigtail Operations) on multiple occasions in both the X-343 and X-344 facilities. Discussions with facility management and operating personnel indicate the air supply line was disconnected in preparation for sampling operations. This condition is reportable under 76.120 (c)(2)(ii) and 76.120 (d)(2). The equipment is required by Technical Safety Requirements (TSR) to be available and operable and either should have been operating or have operated on demand. "The PSS directed an extent of condition be performed for cylinder operations in X-342, X-343, X-344 and X-326 withdrawal station. The result of the extent of condition placed the X-343 sample autoclaves in mode VII (shutdown) and removed from service until affected procedures can be changed, the X-344 autoclaves remain operable, the X-342 autoclaves remains inoperable, and the X-326 withdrawal station remains operable." The regulatee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2003-05-21
39868 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-05-05 | 2003-05-20 19:13 | 2003-05-20 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The licensee reported a medical misadministration involving High Dose Rate brachytherapy MammoSite treatment to a 70-year old female. Upon administering the first of ten planned fractions it was noticed that the Ir-192 source did not reach the center of the balloon but was near the periphery 30 millimeters from the center. The patient dose was reassessed and it was determined that the dose to the target area was less than planned (56% of the planned dose). The patient and the patient's physician were notified. It has been determined that there were no adverse effects to the patient. Corrective actions will address four factors contributing to the misadministration: wrong orientation of the patient during a CT scan; delays in issuing the treatment plan due to a computer network failure; mis-communications regarding the specified treatment plan; and similarities between CT-based and radiographic-based printouts. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2003-05-23
39867 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2003-05-20 10:52 | 2003-05-20 11:39 | 2003-05-20 | EMERGENCY RESPONSE DATA SYSTEM UNABLE TO SUPPLY DATA TO NRC OPERATIONS CENTER "The Emergency Response Data System (ERDS) was discovered at 1022 [Et] to be unable to supply ERDS data to the NRCOC. At 1052, a loss of the ability to supply ERDS for greater than 30 minutes occurred. This constitutes a reportable event based upon 10CFR50.72(b)(3)(xiii). "At the time the failure was discovered, the Turkey Point Unit 3 was in the process of responding to a Technical Specifications required shutdown due to a failure in the rod control system (reported separately). The anticipated unit condition will be Mode 3 until the rod control system is repaired." The licensee will notify the NRC Resident Inspector. Notified R2DO (R. Haag) | 83 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-20
39866 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2003-05-20 09:16 | 2003-05-20 11:39 | 2003-05-20 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO ROD CONTROL SYSTEM ERROR "Shutdown Bank 'B' group step counter for group (1) did not indicate outward rod motion during rod exercising surveillance. Shutdown Bank 'B' group (2) step counter indicated normal outward rod motion. Urgent failure for rod control system annunciator received. Tech Specs required initiation of Nuclear Plant Shutdown." At the time of this notification, the plant is in Mode 1 at 80% power with a controlled plant shutdown in progress. The licensee has notified the NRC Resident Inspector. Notified R2DO (R. Haag) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-05-20
39865 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-05-20 06:50 | 2003-05-20 08:51 | 2003-05-20 | OFFSITE NOTIFICATION TO NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION At 0650 EDT on 5/20/03, the licensee notified the State of New Jersey Department of Environmental Protection due to an impending planned scram. Additionally, they notified the same agency that Oyster Creek will have a potential non-compliance based on the plant canal temperature recorder losing power (see event #39862). This is a potential violation of the plant's New Jersey Pollution Discharge Elimination System permit. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1100 EDT ON 5/20/03 FROM DOSTAL TO CROUCH * * * The licensee will be issuing a press release based on loss of 4160 VAC bus and resulting plant shutdown. | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-20
39864 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-05-20 04:53 | 2003-05-20 08:27 | 2003-05-20 | MANUAL REACTOR TRIP DUE TO LOSS OF OPERATING MAIN FEED PUMP The following information was obtained from the licensee via facsimile: "At 0453 on 05/20/03 with the reactor at approximately 20 percent power in MODE 1, the reactor was manually tripped in response to an automatic trip of the operating Main Feed Pump (MFP). Both motor-driven Auxiliary Feedwater (AFW) pumps started due to the trip of the MFP. Safety systems functioned as required. The operations crew responded to the event in accordance with applicable plant procedures. The plant was stabilized at normal operating no-load Reactor Coolant System temperature and pressure following the reactor trip. The cause of the MFP trip is still under investigation. This condition is being reported as actuations of the reactor protection system and AFW in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." According to the licensee, the MFP tripped after loss of the "A" condensate booster pump. After the manual trip, all control rods inserted into the core. There were no primary relief valves actuated during the resulting transient. Main Steam Isolation Valves were closed during the trip therefore decay heat is being removed via AFW and the steam generator power operated relief valves. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-05-20
39863 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2003-05-20 03:25 | 2003-05-20 07:30 | 2003-05-20 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO REACTOR COOLANT BOUNDARY LEAKAGE The following information was received from the licensee via facsimile: "At 0325 hours CDT on 5/20/2003, the Unit One Reactor Coolant System was determined to have Pressure Boundary Leakage. The Unit was in the process of shutting down for a maintenance outage, and subcritical at the time. The leakage was found during a Drywell inspection as part of the shutdown. The leak was located upstream of the isolation valves on the reactor head vent line. The Technical Specification Required Action for this Condition (Technical Specification 3.4.4, Condition C) is for the Unit to be in Mode 3 in 12 hours and be in Mode 4 in 36 hours. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(i)." The licensee is unable to quantify the leak at this time and is unable to determine if the this was a long-term leak. Unit 1 entered Mode 3 (Hot Shutdown) at 0607 CDT. The NRC Resident Inspector was notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-05-20
39862 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-05-20 00:30 | 2003-05-20 02:47 | 2003-05-20 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS The plant experienced a trip of the "C" 4160 V electrical bus. This condition required entry into multiple technical specifications the most limiting being 3.3.D.5.B due to the loss of the capability to determine the rate of identified containment leakage. This required the reactor to be placed in a shutdown condition within the next 12 hours. The licensee believes that the cause of the "C" bus trip is a fault on the bus that is indicated as a lockout, however, the specific fault is unknown at this time and is under investigation. Due to the faulted bus, the station's emergency diesel generator did not start and will not be able to power any equipment on the "C" bus until the fault is repaired. Significant safety equipment lost due to loss of the bus is as follows: Emergency Service Water pump and Containment spray system #1 Service Water pump #1 Reactor Building Closed Cooling pump #1 Standby Gas Treatment system #1 Core spray and Core spray booster pumps "A" & "D" (4 pumps total) Standby Liquid Control pump #1 Control Rod Drive pump #1 The plant is commencing the required shutdown and expect to be at 60% reactor power by 0430 EDT. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE AT 1040 EDT ON 5/20/03 FROM PEZZELLA TO CROUCH * * * As a result of the loss of 4160 VAC, the safeguards system became degraded. Immediate compensatory measures were taken upon discovery. Contact the Headquarters Operations Officer for details. * * * UPDATE AT 1245 EDT ON 5/20/03 FROM PIETRUSKI TO THOMAS * * * The plant initiated an unplanned reactor manual scram from 60 percent power at 0945 ET. This event was reported per 10 CFR 50.72(b)(2)(iv)(B): 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. The licensee had planned to scram the plant from 30 percent power, but because of the loss of "C" 4160V electrical bus, they were unable to remove the second stage reheaters and feedwater heaters from service, and were thus limited by procedure from lowering power to the desired level prior to inserting a scram. The licensee notified the NRC Resident Inspector. Notified NRR EO (T. Reis, R. Dennig), DIRO (M. Evans), R1DO (A. Dimitriadis) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2003-05-20
39861 | 0 | ILLINOIS DEPARTMENT OF NUC. SAFETY |  |  |  |  | 2003-05-17 18:45 | 2003-05-19 16:30 | 2003-05-19 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE "On Saturday, May 17, at approximately 1845 hrs a Troxler moisture/density gauge Model # 3440, serial no. 21948, was stolen from a licensee's locked truck while it was parked in a parking lot at 105 N. Des Plaines, in Chicago. The licensee's technician stopped on his way home from work at this location and noticed, upon returning to his vehicle, that the rear hard cover, locked hatch had been broken into. Upon further inspection, the technician noticed that the locked and chained nuclear gauge had been taken. Immediately following this discovery, the Chicago Police Department was notified along with the licensee's Radiation Safety Officer/President, Scott R. Nelson. Scott Nelson mobilized to the crime scene. En route he notified the Illinois Department of Nuclear Safety's Radiological Duty Officer, Larry Haskell. Upon arrival at the scene, Mr. Nelson informed the police of the gauges operations, potential health issues and completed filing a police report. It apparently was evident that the truck was broken into. The police report number is HJ-369907. The station is Area 4." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | MAT | [5 empty] | 0 | 2003-05-19
39860 | 0 | GIBRALTAR PLASTIC CORPORATION |  |  |  |  | 2003-05-19 09:30 | 2003-05-19 12:58 | 2003-05-19 | SURFACE CONTAMINATION LEVELS ON SOURCE IS GREATER THAN LIMITS The licensee was packaging eleven cesium sources for shipment to Adco Services Incorporated. Upon surveying the sources, the contractor found that one Cs-137 source, Model No.S-4, Serial No.485 indicated field testing contaminations above 0.005 microcuries (exposure rate greater than 0.5 mR/h). The source activity is believed to be approximately 10.2 millicuries. This contaminated source will be packaged as dry waste in certified type A containers and will be shipped for disposal . The cabinet where the source was stored was contaminated and will also be packed and shipped for disposal. The licensee contacted Region 1 (D. White). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2003-05-19
39859 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-05-19 09:05 | 2003-05-19 10:32 | 2003-05-19 | MANATEE TRAPPED IN THE INTAKE CANAL The following information was received from the licensee via facsimile: "Notification being made due to a State Notification (Florida Fish and Wildlife Commission - Bureau of Protected Species) at 0905 [EDT]. (10 CFR 50.72 (b)(2)). "State notification made due to a Manatee trapped in the Intake Canal. The animal appears to be in good condition and State personnel are [en route] to assist in removal and release. "This notification includes requirements per St. Lucie Environmental Protection Plan Technical Specifications, Appendix B, section 4.1. This is a 72-hr notification for unusual occurrence of any species protected by the Endangered Species Act of 1973." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OTHER UNSPEC REQMNT |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-19
39858 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-05-19 05:18 | 2003-05-19 09:43 | 2003-05-19 | PLANT COMMENCED TECH SPEC REQUIRED SHUTDOWN The following information was received from the licensee via facsimile: "At 0323 [CDT] on May 19th an Individual Rod Position Indication (IRPI) of control bank D exceeded 12 steps from its bank demand position. At 0418 an additional IRPI of control bank D exceeded 12 steps from its bank demand position, at which time the two IRPI indications were declared inoperable. At 0518 the plant initiated a Standard Shutdown Sequence as required by the plant's Technical Specifications (TS 3.10.f.2) since two IRPI's in a group were out of service. At 0530 the two IRPI were within 12 steps of the bank demand position and therefore the shutdown sequence was exited. Power is being held at 97% to investigate. "This is a 4-hour. Notification made in accordance with 10CFR50.72(b)(2)(i)." Initially, rod G-3 indication was greater than 12 steps from the bank demand position. Then rod G-11 indication drifted greater than 12 steps from the bank demand position. Currently, power in stable at 97% with G-3 indicating 198 steps and G-11 indicating 204 steps and bank demand position at 202 steps. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1540 EDT ON 5/19/03 FROM JONATHAN ROBB TO E.THOMAS * * * Mr. Robb called back to clarify that IRPI indication deviated gradually from bank rod position as the bank was withdrawn, and as power and Tavg were increased. | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-05-19
39857 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-05-19 04:24 | 2003-05-19 05:39 | 2003-05-19 | AUTOMATIC REACTOR SCRAM RESULTING IN PRIMARY CONTAINMENT AND REACTOR BUILDING ISOLATIONS At 0424 EDT, during startup operations, the Main Turbine Bypass valves unexpectedly opened and depressurized the reactor vessel. After depressurization, the reactor level increased due to swell and caused an automatic reactor scram. Additionally, there was a Reactor Building Isolation Signal and Group I, II, and VI Primary Containment Isolation Signal generated. Immediately after the automatic scram, five control rods failed to insert into the core. Plant operations personnel performed actions in accordance with their Emergency Operating Procedures to drive the control rods into the core. According to the licensee, adequate shutdown margin was always maintained. The plant electrical system is stable with plant equipment being powered from offsite and the startup transformer. Reactor pressure and level are being maintained via steam line drains to the main condenser. Troubleshooting of the Main Turbine Bypass valves/control system is in progress. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE ON 5/19/03 @ 0934 EDT FROM ERIC OLSON TO CROUCH * * * The following clarification of the above information was received from the licensee via facsimile: "At 04:24 EDT, during startup operations, the Main Turbine Bypass Valves failed open. At the beginning of the event reactor pressure was approximately 880 psig. When the Main Turbine Bypass Valves opened, reactor pressure lowered to approximately 820 psi and reactor water level swelled (due to voiding) from 28 inches to approximately 55 inches. This resulted in a Group I PCIS [Primary Containment Isolation Signal] being generated as designed and automatically closing the MSIV's [Main Steam Isolation Valves]. MSIV closure terminated the depressurization, however initiated an automatic RPS [Reactor Protection System] signal as designed. Termination of depressurization resulted in reactor level lowering to approximately 7 inches which in turn initiated a Group II (Containment Isolation) and Group VI (Reactor Water Cleanup Isolation) PCIS signals. All rods inserted during the scram, however five control rods went beyond full in. Actions were taken in accordance with EOP's [Emergency Operating Procedures] and plant operating procedures to verify the five control rods were beyond full in. This is an indication issue with control rods that can occur when a scram signal is present and the Control Rod Drive System charging water flow drives the control rods beyond the [zero] and full in reed switches. "The plant electrical system is stable with plant equipment being powered from offsite power via the startup transformer. Reactor pressure is being maintained by steam line drains to the main condenser. Reactor water level is being maintained with normal feed and condensate system. "Troubleshooting of the Main Turbine Bypass Valve/Control system is in progress. "The [NRC] Resident Inspector has been notified." | 0 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-05-19
39856 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-05-18 18:07 | 2003-05-18 21:58 | 2003-05-18 | RPS ACTUATION WHILE CRITICAL "On 5/18/03 with the reactor at 28 percent power in MODE 1, an unplanned actuation of the reactor protection system occurred. At 1807 the reactor was automatically tripped from a turbine trip - reactor trip signal. All systems functioned as required and no other safety systems were actuated. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load Reactor Coolant System temperature and pressure following the reactor trip. The cause of the turbine trip is under investigation. "This condition is being reported as an unplanned reactor protection system actuation in accordance with 10 CFR 50.72(b)(2)(IV)(B) and 10 CFR 50.72(b)(3)(iv)(A)." All rods fully inserted and decay heat is being removed via the PORV's. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-05-18
39855 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-05-17 22:05 | 2003-05-18 04:27 | 2003-06-10 | DEGRADED CONDITION DUE TO CRACK INDICATIONS ON VESSEL HEAD "At 18:00 on 5/15/03, craze cracking indications were found on a Reactor Pressure Vessel Head Penetration. At 22:05 on 5/17/03, it was determined that this condition was reportable as a prompt eight-hour report under 10 CFR 50.72(b)(3)(ii)(A). "During the Unit 2 reactor head inspection, five small, shallow indications were found on the inside diameter of penetration #74. The indications are closely spaced and are approximately 3/8 inch below the J-groove weld region. Initial calculations showed a crack depth of 0.117 inches. All of the indications are bounded within an area that is one inch wide by 2.6 inches high. There was no through-wall leakage and the reactor coolant pressure boundary remains intact. "These indications were previously identified during the last refueling outage in February 2002. They were evaluated as acceptable to leave in service for a full cycle at that time, and they have not shown any significant growth since then. "The industry guidance on projected flaw growth rates has been revised since these indications were discovered in 2002. As a result, the new projections for these indications result in less than a full fuel cycle before reaching the limit for remaining in service. Therefore, repairs will be needed. Current plans are to perform an excavation of the affected area, under existing code guidance." The NRC Resident Inspector has been notified. * * * UPDATE AT 0811 EDT ON 6/10/03 FROM HACKMAN TO CROUCH * * * The following information was obtained from the licensee via facsimile: "Following evaluation of the condition reported in EN# 39855, it has been determined that the craze cracking indications in penetration 74 of the Unit 2 Reactor Pressure Vessel Head do not represent a seriously degraded principal safety barrier of the nuclear power plant. "As stated in the initial ENS report, the flaw was on the inside diameter of the penetration approximately 3/8 inch below the J-groove weld. The flaw evaluation concluded that no growth occurred from the last inspection and at least one effective full power year of operation would pass prior to the crack growing to an unacceptable depth (75 percent through wall). Accordingly, Cook Nuclear Plant withdraws EN# 39855. "Additionally, as part of the withdrawal, a correction to the information contained in EN# 39855 is being made. EN# 39855 stated that repairs were required this refueling outage due to changes in the industry guidance on projected flaw growth rates. The flaw evaluation performed for the 2002 refueling outage was based on growth charts in the flaw evaluation handbook (WCAP 14118, Rev 5) using the depth of the cracking without considering the length. The flaw evaluation for this outage was conservatively calculated considering both depth and length, which resulted in less than a cycle of operation prior to growing 75 percent through wall. The decision to repair the penetration allows Unit 2 to operate for a full fuel cycle. There was no change in industry guidance that compelled a repair for this outage." The crack was repaired during the current refueling outage. The longest crack length identified was 2.1 inches with a depth of .117 inches in the penetration inside diameter of 2.75 inches. Wall thickness of penetration is nominally 0.625 inches. The NRC Resident Inspector was notified of the retraction by the licensee. Notified R3DO (Hills) and NRR EO (Reis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling Shutdown; FMode2: Refueling Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-05-18
39854 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-05-16 04:56 | 2003-05-16 12:53 | 2003-07-15 | SPECIFIED SYSTEM ACTUATION "On 5/16/03 with the reactor shutdown in MODE 3, an unplanned actuation of Auxiliary Feedwater (AFW) system occurred during testing of the 'B' Main Feed Pump (MFP). A trip of an uncoupled MFP generated a signal to start both motor-driven AFW pumps during testing following maintenance. The 'A' motor-driven AFW pump was already in service, so the 'B' AFW pump started on receipt of the signal. Feed to the steam generators was always available, even without the additional actuation of the AFW system. The purpose of the actuation of AFW following a trip of the main feed system is to ensure adequate flow to the steam generator. In this case, the main feed pump was being tested and was not being used to provide flow to the steam generator. Therefore the actuation was not required to provide any safety function. The 'B' motor-driven AFW pump was secured within approximately two minutes because the additional flow was not required. This condition is being reported as an unplanned system actuation in accordance with 10 CFR 50.72(b)(3)(iv)(A). "10 CFR 50.72 requires an 8-hour report for, 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' In this case, the AFW pump start signal due to trip of the last running MFP is only applicable in MODES 1 and 2, and is not required in the current MODE of plant operation (MODE 3). "The NRC Resident Inspector was notified." * * * UPDATE ON 7/15/03 @ 1044 BY YADUSKY TO LAURA * * * RETRACTION Upon further evaluation, it has been determined that the reported event did not meet the definition of a valid signal. Therefore, the reporting criterion contained in 10 CFR 50.72(b)(3)(iv)(A) was not applicable. Per NUREG 1022, Revision 2 (Event Reporting Guidelines 10 CFR 50.72 and 50.73), "Valid actuations are those actuations that result from `valid signals' . . . That are initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system." Because the AFW actuation signal was not initiated in response to an actual loss of the last running MFP (the motor was disconnected from the pump and no MFP was in operation), the actuation was not valid; therefore, the event is not reportable per 10 CFR 50.72(b)(3)(iv). In addition, because the invalid signal was received after the safety function had already been completed (the alternate train of AFW was operating at the time of the uncoupled motor trip), the event is not reportable per 10 CFR 50.73(a)(2)(iv)(A)(2)(ii). The NRC Resident Inspector was notified. NRC notified REG 2 RDO. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-05-16
39853 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-15 14:00 | 2003-05-16 10:04 | 2003-05-21 | SAFETY SYSTEM ACTUATION On 5/15/03 @1400 during pigtail disconnect, a small amount of particulate fell from the pigtail. This particulate began to smoke resulting in a see and flee. During the see and flee the gas release alarm was activated. The alarm resulted in the actuation of a "Q" Safety system while in applicable mode (mode III). The PSS Responded to the see and flee. The affected cylinder was made inoperable. No spread of contamination outside already posted area. Air sampling results are less than MDA. The NRC Resident Inspector was notified. * * * UPDATE AT 23:46 EDT ON 5/20/03 FROM McCLEERY TO CROUCH * * * The following update was received from the regulatee via facsimile: "5/20/05: As requested, this is additional information to clarify some questions in the initial report of PTS-2003-011. Mode III (Cylinder/Pigtail Operations) includes but is not limited to pigtail connection/disconnections, roll/tilt and valve clarity checks; steam valves closed, cylinder valve or safety valve may or may not be closed. MDA is minimum detectable activity. The initial report should have been marked as Other Non-CFR Requirements in place of (c)(2) safety equipment failure. Additionally, during the investigation of the event it was determined the cylinder safety valve air supply was removed prior to the see and flee. This condition is reportable under 76.120 (c)(2)(ii) [and] 76.120 (d)(2). The equipment is required by Technical Safety Requirements (TSR) to be available and operable to perform the required safety function, while the autoclave is operating in mode III (cylinder/ pigtail operations). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIP DISABLED/FAIL | OTHER UNSPEC REQMNT | [8 empty] | NON EMERGENCY | 3 | OH | FUE |  | 72.75(c)(2) |  |  |  | 0 | 2003-05-16
39852 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-05-15 13:15 | 2003-05-15 17:17 | 2003-05-15 | SAFEGUARDS EVENT The licensee reported a vulnerability in a safeguard system that could allow unauthorized or undetected access to a protected area and vital area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-05-15
39851 | 0 | NATIONAL RESPONSE CENTER |  |  |  |  | 2003-05-14 18:00 | 2003-05-15 13:45 | 2003-05-16 | TRANSPORTATION INCIDENT The National Response Center sent a fax to the Operations Center regarding the following transportation incident: A tractor trailer carrying the reactor vessel head from North Anna power plant to EnviroCare in Clive, UT was sideswiped by a pickup truck being driven by a drunk driver near Kingman, KS on Route 42. The pickup truck passed the tractor trailer at approximately 80 mph, and proceeded down the road, where it was involved in a traffic accident. The incidental impact between the pickup and the tractor trailer caused a minor tear in the protective tarp and plastic container containing the vessel head, along with depositing some paint on the head itself. There was no apparent structural damage to the vessel head, and no apparent radioactive release into the atmosphere. The truck driver stopped his vehicle in Greensburg, Kansas to assess the condition of the vessel head. The shipper is sending a representative to inspect the packing material integrity. The state of Kansas will also be sending a representative out to the scene to assist. *****UPDATE ON 5/16/03 AT 13:50 EST FROM CONNELLY TO LAURA***** Three independent radiological surveys conducted by the State of Kansas and North Anna determined there was no spread of contamination and only minor damage occurred to the shipping packaging for the vessel head. The minor damage was repaired and the truck was released. Notified R4DO (W. Johnson), DIRO (McGinty) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | KS | OTH | GEN |  |  |  |  | 0 | 2003-05-15
39850 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-05-14 18:48 | 2003-05-15 12:18 | 2003-05-16 | AGREEMENT STATE REPORT The licensee reported a potential overexposure to a radiographer who was x-raying some pipes at a worksite. After completing a section of piping, the radiographer should have cranked his source back in, but was interrupted by another technician and left his work area. When he returned, the radiographer changed out his film, and moved the guide tube to another section of piping to begin more x-rays. At this point, he realized that his survey meter had pegged high, and remembered that he had not cranked the source back in prior to moving it. He proceeded to immediately crank the source back to its fully shielded position. The exact time and distance from the source for the radiographer's exposure is unknown, and the licensee is attempting to re-create the scenario. The source was 26 Curies of Iridium 192, model number INC-32. The serial number is unknown at this time. A preliminary investigation by the licensee estimates the radiographer's exposure to 800-900 millirem whole body. There is currently no exposure estimate for his hands/extremities. The radiographer's badge was sent off for processing. Results will be reported on 5/16/03 to the NRC. The Texas Department of Health is sending an additional inspector to the site to investigate. * * * UPDATE ON 5/16/03 @ 1120 BY WATKINS TO GOULD * * * Blazer Industrial Radiography brought in a consultant to perform preliminary dose calculations for the whole body and the right hand of the radiographer. The results were 1.3R for the whole body and 37.1R for the right hand, neither of which exceeds the annual regulatory limit. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-05-20
39849 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-05-15 02:52 | 2003-05-15 05:27 | 2003-05-16 | REACTOR TRIP FROM 100% POWER ON BOTH UNITS DUE TO TURBINE TRIP ON BOTH UNITS The licensee reported that a loss of power on the 345KV grid caused a turbine trip on both units which resulted in a reactor trip from 100% on both units. All rods fully inserted and no ECCS was actuated. Both units are currently at Mode 3 in natural circulation and stable. The auxiliary feed water systems started on both units to maintain steam generator levels. The reactor coolant temperature is being controlled by using the steam generator atmospheric relief valves. Since the safety systems were powered by an alternate offsite power supply, the 4 emergency diesels did not auto start, but they are operable. The licensee is investigating why they lost the 345KV grid. The NRC Resident Inspector was notified. *****UPDATE ON 5/16/03 AT 1500 EST FROM D. BUTLER TO R. LAURA***** "Status as of 10:30, 05/16/03 - Sequence of Events 1. Parker line experiences a `B' phase to ground fault at 02:52. 2. CPSES [Comanche Peak Steam Electric Station] Parker feeder breaker 8040 fails to trip as required. Primary and backup ground relaying do not actuate. No trip signal is sent to the Parker breaker. Should normal tripping have occurred, fault would likely have cleared and event ended. East Bus backup timers are not initiated due to lack of Parker Breaker 8040 trip signal. Operation of the backup timers would have isolated the East bus. CPSES impact would likely have been lowering one unit to 50% power while operating the other unit at 100% power. 3. Parker line remains faulted with fault current being supplied from the East bus, West bus and CPSES generation. 4. Approximately 30 cycles into the fault, 345 Kv offsite feeds began to trip via their own protective schemes. 5. At approximately 1.3 seconds, Unit 1 and 2 Main Generator breakers trip on generator backup Main transformer neutral ground relaying. 6. Unit 1 and 2 Main Generator lockout relays actuate on Load Rejection protection. 7. Unit 1 and Unit 2 Normal 6.9KV busses trip on Generator lockout signals. 8. Unit 1 Normal busses slow transfer to Station Transformer 1 ST at approximately 5 seconds. Unit 2 two normal bus alternate feed 2ST has been de-energized from the 8080 breaker blocking slow transfer operation. 9. Station Transformer 1 ST `C' phase time over current relaying operates generating a 1 ST lockout signal. 10. Unit 1 normal 6.9Kv bus alternate feeder breakers are tripped via the 1 ST lockout signal. Unit 1 and Unit 2 normal 6.9Kv busses are now de-energized. 11. East and West busses are inspected by ONCOR and CPSES Maintenance. Switchyard West bus is re- energized from the Wolf Hollow Line. 12. Station transformers 1ST and 2ST are re-energized and power restored to Unit 1 and 2 Normal 6.9KV busses. "Troubleshooting "Primary Fault detection relay is tested and is found failed. The Fault detector serves as a Supervisory relay during line faults. It serves as a trip permissive, placing the trip circuits of the ground detection relaying in service. Failure of the Fault Detector is the obvious cause of the Primary relay protection scheme failure to operate. Backup Fault detection relay is tested and is found to operate correctly. Failure of the backup protection scheme is likely caused by the inconsistent operation of the backup ground relay and failure of the CA unit of the Zone 1 relay." Notified R4DO (Johnson) | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-05-15
39848 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-05-14 09:45 | 2003-05-14 18:44 | 2003-05-14 | FITNESS FOR DUTY A licensed employee was determined to be under the influence of alcohol during a random drug test given at the Limerick Generating Station. Employee was dual-licensed at both Limerick and Peach Bottom. (Refer to Event Notification #39847). The employee's access to the plant has been removed. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2003-05-14
39847 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-05-14 09:45 | 2003-05-14 17:22 | 2003-05-14 | FITNESS FOR DUTY A licensed employee was determined to be under the influence of alcohol during a random drug test. The employee's access to the plant has been removed. Contact the HOO for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2003-05-14
39846 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-05-14 | 2003-05-14 15:46 | 2003-05-14 | LOSS OF SIRENS "Indian Point Energy Center (IPEC) Units 2 and 3 are making an eight-hour non-emergency notification in accordance with 10CFR50.72(b)(3)(xiii). "On May 14, 2003 at 1035 [EDT], Rockland County notified Emergency Planning (EP) that while attempting to perform a 'Cancel Test' of the counties sirens a communication failure was recorded on all Rockland County sirens. EP performed a review of the status of the system and determined that a communication loss was experienced that prevented transmittal of instructions to all sirens in the four counties. Communication between the Indian Point Energy Center Emergency Operations Facility (EOF) and the 154 sirens was re-established as of 1251 [EDT]. Personnel will continuously man the EOF to initiate sirens if needed, until control can be re-established from the affected counties. Route alerting was available during the loss of sirens. "The NRC resident inspector, County and State were notified of this event." | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-14
39845 | 0 | UNIVERSITY WISCONSIN-MADISON |  |  |  |  | 2003-05-13 14:00 | 2003-05-14 12:35 | 2003-05-14 | MEDICAL EVENT AT UNIVERSITY WISCONSIN-MADISON A significant under-exposure occurred on a patient undergoing therapy for liver cancer. The source was an SIR-SPHERE using .058 curies of Y-90 isotope. The Y-90 isotope was in semi-liquid form. The prescribed dose was 58 milli-curies and the patient was delivered only 2 milli-curies. The vendor of the machine has been contacted and will repair the equipment. The hospital speculated that the delivery tube may have had air leaks resulting in the source not being fully inserted. The patient has been rescheduled for the therapy on May 28, 2003. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-05-14
39844 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2003-05-14 04:10 | 2003-05-14 11:43 | 2003-05-14 | APPENDIX "R" ISSUE AT PEACH BOTTOM 3 "On May 14, 2003, at approximately 0410, the shift supervisor determined that the Alternate Shutdown Panel on Unit 3 was not operable following discovery of a de-energized power supply. The panel provides the capability to maintain a safe shutdown path for a fire in the cable spreading room, main control room or main control room fan room. Therefore, operators would have been prevented from implementing required actions for a fire in those areas. The apparent cause of the loss of power was a broken wire, which was discovered during routine testing of the panel. "Power was restored to the Alternate Shutdown Panel at approximately 1030 on May 14, 2003 and further investigation is in progress to determine the cause of the broken wire and full extent and effect of the de-energization of the panel." The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-05-14
39843 | 0 | NUCOR STEEL |  |  |  |  | 2003-05-12 15:00 | 2003-05-13 13:14 | 2003-05-13 | METAL THICKNESS GAUGE SHUTTER ASSEMBLY DAMAGED On 5/12/03 at 1500 CST, the shutter assembly on an IMS model TIAS-04 metal thickness gauge became stuck and resulted in shutter assembly bolts shearing. The gauge contains 50 curies of Cs-137. The licensee safed the gauge by isolating air to the air-operated gauge. The manufacturer was contacted and is currently on-site repairing the gauge. Additionally, during the incident, the assistant RSO walked below the gauge without having his radiation detection meter. Ion chambers mounted in the gauge area were reading zero at the time. Area monitors mounted in the area were not in alarm. The RSO has sent the assistant RSO's film badge out for processing. The licensee has contacted Region 3 personnel (Sandy Frazier and Debbie Piskura). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2003-05-13
39842 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-12 09:00 | 2003-05-12 23:08 | 2003-05-12 | LOSS OF ONE OF TWO CONTROLS ON MODERATION NRC BULLETIN 91-01 24 HOUR NOTIFICATION The following information was received from the licensee via facsimile: "At 0900 on 5/12/03, the Plant Shift Superintendent (PSS) was notified that differential pressure transmitter inputs for three Freezer/Sublimers, U/2(Unit # 2) C/B (Cell B), U3 C/B and U/4 C/B located in C-337, were installed incorrectly. The transmitter (PDT-338) measures the differential pressure between the R-114 (freon) and the Recirculating Cooling Water (RCW). NCSA CAS-001 requires that the pressure differential between the R-114 and RCW pressures be such that the R-114 pressure is at least 2.0 psia above the RCW pressure. This would preclude the introduction of a moderator (RCW) into the process side of the system. The correct configuration of these inputs has the pressure tap on the inlet line to the condenser/reboiler. For Freezer/Sublimers U/2 C/B, U/3 C/B and U/4 C/B the pressure tap is located on the outlet line from the condenser/reboiler. As installed, the low differential pressure-alarm may not come in until after the R-114 pressure and RCW pressure at the inlet of the Condenser/Reboiler have exceeded the NCS limit. At 1040 on 5/12/03, the PSS was notified by Nuclear Criticality Safety that one of the two controls on moderation had been lost. The System Engineer identified four additional Freezer/Sublimers, two in C-331 and two in C-335, with the same problem. These Freezer/Sublimer units were out-of-service and the RCW had been drained prior to the walk-down. , SAFETY SIGNIFICANCS OF EVENTS: Although high side Condenser/Reboiler pressure readings could not be taken due to incorrect installation of an AQ-NCS pressure instrument, the integrity of the F/S tubes has been maintained. All of the Condenser/Reboilers had the RCW drained by 1345 hours on 5-12-03. thus re-establishing double contingency. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(s) OF HOW CRITICALITY COULD OCCUR) In order for a criticality to be possible, an unsafe mass of uranium would have to be present within the Freezer/Sublimer unit and a moderator would have to enter through the Freezer/Sublimer and Condenser/Reboiler tubes. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION,ETC.) Double contingency is maintained by implementing two controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): For the 20 MW Freezer/Sublimers, less than a safe mass of uranium, at less than or equal to (LEU) U235. For the 10 MW Freezer/Sublimers, less than a safe mass of uranium, at less than or equal to (LEU) U235 NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIFNCIES The first leg of double contingency relies on Freezer/Sublimer and Condenser/Reboiler tube integrity. Since high UF6 pressure alarms or other operational indicators, caused by leaking R-114 into the Freezer/Sublimer, have not been received on the Freezer/Sublimer units, the integrity of the Freezer/Sublimer tubes has been maintained. Therefore, this leg of double contingency was maintained. The second leg of double contingency relies on the differential pressure between the R-114 and RCW, controlling the differential pressure such that the R-114 is maintained at least 2.0 psi above the RCW precludes the introduction of RCW to the process side of the unit. Monitoring the RCW pressure on the outlet to the Condenser/Reboiler, instead of the inlet, does not give correct differential pressure readings. Therefore. This leg of double contingency was not maintained. Even though the moderation parameter was maintained through integrity of the Freezer/Sublimer and Condenser/Reboiler tubes, double contingency Is based on two controls on moderation. Thus, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLFMENTED: 1. Drain Condenser/Reboiler RCW for the affected Freezer/Sublimer units. Completed at 1345 on 5-12-03. 2. Correct the installation of the pressure taps In accordance with the approved Engineering drawings. Complete prior to returning Freezer/Sublimors to service The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-05-12
39841 | 0 | TRIPLER ARMY MEDICAL CENTER |  |  |  |  | 2003-05-12 11:00 | 2003-05-12 17:32 | 2003-05-12 | NUCLEAR MATERIAL MISSING DURING SHIPMENT The following information was received from the licensee via facsimile: "An order for 150 milli-curies (mCi) of iodine-131 was placed with Mallinckrodt on May 9, 2003. The package was received by the Nuclear Pharmacist,[DELETED], on May 12, 2003 and indicated that the package had 154.10 mCi of iodine-131 but was measured to contain only 54.0 mCi of iodine-131. "At 11:00 [HST] the Nuclear Pharmacist paged me and I immediately went to the Nuclear Pharmacy laboratory. I verified that the dose calibrator was set on I-131and inquired about the package receipt procedures. The Nuclear Pharmacist indicated that the package was in excellent condition with no sign of physical damage. The package was received in a timely manner, metered and swiped without incident. The package contained two vials supposedly containing 140.00 mCi and 14.10 mCi of iodine-131 for a total of 154.10 mCi. The contents of the package appeared to be intact. The Nuclear Pharmacist combined the two vials and assayed the dose in the dose calibrator for an iodine ablation therapy but measured only 54.0 mCi of I-131. "At 11:20 I notified Mallinckrodt of the discrepancy, and then at 11:30 I notified the NRC Operations Center to report the missing licensed material in accordance with 10 CFR Part 20.2201(a)(1)(i). I will also contact the shipper, MMS Courier, and the Army Medical Command as well as any local or state notifications that are required." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-05-12
39840 | 0 | STATE OF MISSOURI |  |  |  |  | 2003-05-10 18:00 | 2003-05-12 14:57 | 2003-05-12 | LOST AND THEN RECOVERED TROXLER ASPHALT CONTENT GAUGE The following information was obtained from the licensee via facsimile: "On Saturday evening, May 10, 2003, at approximately 6:00 pm [CDT], a tornado wiped out a trailer at an asphalt plant that contained an asphalt nuclear gauge 3241 [Troxler]. The gauge was in its gray shipping container that was locked inside a metal case, which was bolted to the floor. The gauge was found about 100 feet from the trailer site out of the metal box, but the gray shipping case was still intact. It did not appear to be damaged. The contractor, Chester Bross Construction Company, found the gauge and stored it in their plant shack with their gauge. Their Safety Director, [DELETED], also came up on Sunday morning and took readings. Neither gauge appeared to be leaking." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-05-12
39839 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-05-10 19:00 | 2003-05-12 14:27 | 2003-05-12 | LOSS OF CRITICALITY MONITORING SYSTEM DETECTORS DUE TO LIGHTNING STRIKE The following information was obtained from the licensee via facsimile: "On Saturday, May 10, 2003 at approximately 17:30 [EDT], a 'storm watch' was initiated due to an electrical storm in the vicinity of the site. The 'storm watch' is an action whereby individuals are stationed throughout the facility with monitors to compensate for loss of detection or inadvertent howler sounding due to a potential lightning strike during a severe thunderstorm. The 'storm watch' was effectively implemented per procedure. A lightning strike occurred during 'storm watch' at approximately 19:00 resulting in several high level alarms and one low level alarm (hazardous waste building). The detector and monitor at the hazardous waste building (low level alarm) was damaged by lightning and was replaced by a Rad Con Technician (RCT). All high alarms immediately reset and the system was thought to be functional. 'Storm watch' was terminated. "On Sunday, May 11, 2003 around 21:00 Security notified Radiation Control that another detector was in a low alarm. Another RCT responded and in addition to testing the detector in low alarm, he tested the entire system and found two other areas impaired, indicating high, but no alarm. The two areas are (1) a vault and (2) the hazardous waste/laundry/super compactor areas. Radiation Protection Management was notified at approximately 23:00. The affected detectors are as follows: Three detectors in the vault Three detectors in the hazardous waste/laundry/super compactor area "These detectors are six of eighteen in Zone 5. There are six 'zones' in the criticality monitoring system. These six detectors are believed to have been impaired since the May 10 lightning event. No work was in progress in the area of the impairment through the course of this problem. Although conservative calculations indicate the area detectors in Zone 5 may not have initiated activation of the howlers during this period; the functional detector in the hazardous waste building would have given a high alarm alerting security to notify Radiation Control. "All detectors and monitors were repaired and functional by 03:20 on May 12, 2003. "An investigation team was assigned to do a root cause analysis. "Apparent cause: On May 10, 2003, the technician failed to execute a complete system test as required by procedure after the lightning strike." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 70.50(b)(2) |  |  |  | 1 | 2003-05-12
39838 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-05-12 01:02 | 2003-05-12 03:28 | 2003-05-12 | AUTOMATIC TURBINE TRIP/REACTOR TRIP DUE TO MAIN GENERATOR OUTPUT BREAKER OPENING Main Generator output breaker opened after receiving Main Generator voltage regulator # 1 (core 1) & # 2 (core 2) alarms causing an automatic turbine trip followed by an automatic reactor trip (first out annunciator was over temperature differential temperature). All rods fully inserted into the core. Both motor driven auxiliary feedwater pumps were manually started to maintain reactor coolant temperature and proper steam generator water levels. Steam is being dumped to the main condenser. Emergency Operating procedure 1.0 entered and then Emergency Operating procedure 1.1, Reactor Recovery Procedure was entered. All emergency core cooling systems and the emergency diesel generators are fully operable if needed. The licensee believes that the main generator exciter breaker opened before the main generator output breaker opened. No work was going on in the area of the main generator when the output breaker opened. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-05-12
39837 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-05-10 15:09 | 2003-05-10 20:54 | 2003-05-10 | MANUAL RPS ACTUATION DUE TO FAILED OVERRIDE FEATURE "At 1509 [CDT], during the performance of the Division One (1) LOOP / LOCA Test, the instrument air to Control Rods was lost due to a failure of the supply isolation valve to re-open during the test. It was planned that the Scram Air Header isolation valve would close during the test but the LOCA Override feature failed to work and prevented the valve from being re-opened. A manual Rx Scram was inserted before Scram Air Header pressure dropped to the point that it would have caused a Rx Scram. "The Control Rods were already inserted into the Core and no Rod motion occurred. The valve was manually re-opened and air was restored to the Scram Air Header. The Scram was reset at 1546 [hrs.]. The Plant is currently in a Refueling Outage. Troubleshooting will be occurring to determine the failure of the override feature to function:" Normal Scram Air Header pressure is 120 psig. At a pressure of 38 psig, the Scram Air Header valves will start to fail close due to low air pressure and result in a Scram. The licensee initiated the manual Rx Scram when pressure reached 60 psig decreasing. The air header depressurized completely until the air supply valve was manually re-opened after operators were unable to open the valve from the control room. During this outage, there was some work performed on the Scram Air Supply Isolation valve but none that would have affected the LOCA Override feature. The Isolation valve override will be repaired during this refueling outage. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-05-10
39836 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-05-10 15:06 | 2003-05-10 17:25 | 2003-05-10 | OFFSITE NOTIFICATION TO STATE OF WISCONSIN The following information was obtained from the licensee via facsimile: "On 5/10/03, while performing a reactor plant startup, the 'B' AFW [Auxiliary Feed Water] pump Safeguards Alley trench overflowed. Recent procedural changes have been made to N-FW-05B which do[es] not allow throttling of the lube oil coolers discharge valves to prevent flooding. To address the condition, a sump pump was used to pump water from the trench directly to the turbine building standpipe because the normal flowpath ( Turbine Building Sump ) capacity had been exceeded. This water is believed to be free from radiological, chemical, or petroleum products as it is processed as pure DI [de-ionized] water. This has effectively created a previously unrecognized and consequently unauthorized discharge flowpath. This notification is being made due to the expected report to the Wisconsin DNR [Department of Natural Resources] on the same incident." To mitigate this condition, the licensee has temporarily changed the revised procedure to allow throttling of lube oil coolers discharge valves (original procedural guidance) until the revised procedure can be re-evaluated. The discharge did not exceed any reportable quantities. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-10
39835 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2003-05-10 10:28 | 2003-05-10 13:37 | 2003-05-10 | PLANT MAY HAVE EXCEEDED RATED THERMAL POWER DURING PREVIOUS OPERATING CYCLE The following information was obtained from the licensee via facsimile: "On May 10, 2003, plant personnel determined that River Bend Station [RBS] may have operated above the licensed thermal power limit of 3039 MWt [megawatts thermal] during the last operating cycle due to a non-conservative error in feedwater flow measurement. RBS installed a new feedwater ultrasonic flow meter during the last refueling outage. Data analyzed following initial testing of the new flow meter resulted in the identification of discrepancies between feedwater flow measurements from the new ultrasonic flow meter, the previously installed external ultrasonic flow meter and the venturi nozzle flow meter. Feedwater flow measurement directly impacts the calculation of thermal power during plant operation. The plant normally operates at 100% thermal power. Thus, any non conservative error in feedwater measurement results in thermal power greater than 100%. "Initial review of feedwater flow data indicates that the licensed thermal power limit may have been exceeded. Further analysis is ongoing to determine the magnitude of the condition. This condition was primarily caused by error in the flow measurement using the previously installed external ultrasonic flow meter. As this device is no longer installed in the plant, the reported condition has no impact on current plant operation. This report is being made as required by RBS Operating License [OL] Condition 2.E as a violation of OL Condition 2.C(1)." The licensee has notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2003-05-10
39834 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-05-08 19:30 | 2003-05-08 21:53 | 2003-05-08 | LOSS OF FIVE EMERGENCY SIRENS DUE TO POWER OUTAGE The following information was obtained from the licensee via facsimile: "On 05/08/2003 at 1840 CDT, the National Weather Service in Topeka, KS declared a Tornado Warning for the area around Wolf Creek Generating Station. The Tornado Warning was in effect until 1930 CDT. The storm cell moved through Burlington, KS, approximately 6 miles southwest of the facility, causing power to be lost to the city of Burlington. Plant Security notified the Control Room that the loss of power to Burlington had caused power to be lost to five (5) E-Plan Sirens and an intrusion alarm on one additional E-Plan Siren. This information was relayed to Security via the installed telemetric monitoring system. At this time, Burlington is without power and the sirens remain without power." There is no ETA for power restoration. The licensee has informed the NRC Resident Inspector and the local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-08
39833 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2003-05-08 04:00 | 2003-05-08 16:16 | 2003-05-08 | SAFETY EQUIPMENT FAILURE DUE TO SEVERE THUNDERSTORM CONDITIONS The following information was received from the licensee via facsimile: "At approximately 4:00 a.m. [EDT] on May 8, 2003, the Criticality Warning System (CWS) coverage was temporarily lost due to severe thunderstorm conditions. The two Data Acquisition Modules (DAMS) providing redundant criticality detector coverage of the Dry Conversion Process (DCP) plant area were simultaneously lost. Additional isolated DAM failures occurred at other locations, but CWS coverage was maintained for the remainder of the facility. "In DCP, operations were suspended, and all movement of fissile material was halted. Personnel were restricted from affected plant areas. Maintenance instrumentation personnel diagnosed and successfully restored CWS coverage for the DCP plant area at approximately 7:00 a.m. Normal plant operations were resumed at approximately 9:30 a.m. Restoration of remaining redundant CWS coverage for all areas was completed at 11:45 a.m. "This condition is reported pursuant to 10CFR70.50(B)(2) as an event in which equipment is disabled or fails to function as designed when required by license or regulation to be available to mitigate the consequences of an accident. Incident investigation and evaluation of additional corrective actions pending." Licensee will be notifying New Hanover County Emergency Management, North Carolina Department of Radiation Protection, NRC Region 2 and NRC Headquarters Global Nuclear Fuels Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2003-05-08
39832 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-05-08 08:00 | 2003-05-08 10:40 | 2003-05-08 | EMERGENCY SIREN ACCIDENTLY INITIATED. The Claiborne County Civil Defense department inadvertently initiated an emergency siren. The siren has been secured, and a "No Emergency" message has been issued to the local media. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-08
39831 | 0 | WASHINGTON HOSPITAL CTR |  |  |  |  | 2003-05-06 | 2003-05-07 14:57 | 2003-05-07 | MEDICAL EVENT - BRACHYTHERAPY RADIATION THERAPY NOT ADMINISTERED TO INTENDED SITE A patient at Washington Hospital Center, being administered brachytherapy treatment, received the treatment to a non- intended site. Based on preliminary information, this occurred due to the Strontium 90 source being placed in the wrong place during treatment. The patient received the intended 23 gray dose. The patient has been notified and the licensee is investigating the cause of the event. The licensee has notified the Hospital Chief Medical Physicist, Oncologist, and will also notify the Hospital Cardiologist. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2003-05-07
39830 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-05 19:05 | 2003-05-06 15:46 | 2003-05-06 | AUTOCLAVE "O" RING FAILURE On 5/5/03 at approximately 1905 hours, X-344 Operations Personnel identified visible/audible steam out leakage on Autoclave #2. Autoclave #2 was operating in Operational Mode 2 (heating) at the time of discovery. The out leakage was determined to be due to a failure of the "Q" Safety System Component "O"-Ring which seals the cylinder within the autoclave. The Autoclave Steam Supply was immediately valved off and the autoclave was opened for inspection. This inspection identified a 9/16" gap in the "O"-Ring Seal which would have degraded the seal to the point that it could not perform its designed safety function as required during Operational Mode 2 Evolutions. This incident is being reported as a Safety Equipment Failure while operating in an Applicable Mode. Immediate Radiation / Air Monitoring indicates no release of Radioactive Material occurred as a result of this incident. The Autoclave was declared inoperable by the Plant Shift Superintendent. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2003-05-06
39829 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-05-06 11:30 | 2003-05-06 15:12 | 2003-05-06 | OVERFLOW OF PLANT WASTE WATER INTO THE JAMES RIVER At 1130 hours on 5/06/03, wastewater overflowed from a holding tank, which resulted in a discharge of sewage into state waters through the plants storm drain system. This discharge was a result of a failure of a transfer pump, which pumps the wastewater from the holding tank to another portion of the stations water treatment system. It is estimated that approximately 150 gallons of wastewater entered the plants discharge canal which enters state waters before it was isolated. Cleanup efforts are in progress. This event is being reported in accordance with 10CFR50.72(b)(2)(xi) due to the fact that the Virginia Department of Environmental Quality was notified at 1424 hours of the discharge into state waters. The State was notified and the NRC resident Inspector will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-06
39828 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-05-06 08:57 | 2003-05-06 14:08 | 2003-05-06 | NOAA WEATHER RADIO PROMPT NOTIFICATION SYSTEM OUT OF SERVICE FOR PLANNED OUTAGE NOAA Weather Radio Prompt Notification System was taken out of service by the National Weather Service for a planned outage. This results in a Major Loss of Offsite Notification capability. The State of Georgia (GEMA) and the 4 EPZ counties were notified of the NOAA Weather Radio Prompt Notification System outage. NOAA Weather Radio Prompt Notification System was returned to service at 1338 EDT. The State of Georgia (GEMA) and the 4 EPZ counties were notified that the NOAA Weather Radio Prompt Notification System is back in service. The state and local agencies were notified and the NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-06
39827 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-05-06 | 2003-05-06 10:24 | 2003-05-06 | SAFETY EQUIPMENT FAILURE "Operations Personnel were performing a cylinder disconnect in Autoclave #2. The cylinder was rolled from the 6 O'Clock cylinder valve position, to the 12 O'Clock cylinder valve position to complete disconnecting the cylinder safety valve and pigtail from the cylinder. At approximately 2006 hours UF6 was observed smoking from the mechanical connection for the cylinder safety valve and the cylinder valve. Additionally, smoke appeared to be coming from the top of the cylinder valve. The Operator seeing the smoke alerted personnel in the area, actuated the Emergency Shell Closure and the Gas Release Alarm placing the Autoclave in containment. Emergency Response Personnel Responded and performed Air Samples for HF and Uranium. All samples were less than Minimum Detectable." The licensee notified the NRC Resident Inspector, and will notify the Department of Energy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIP DISABLED/FAIL | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 72.75(c)(2) |  |  |  | 0 | 2003-05-06
39826 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2003-05-05 20:41 | 2003-05-05 23:48 | 2003-05-05 | LOST ERDS DUE TO COMPUTER MALFUNCTION "Loss of ERDS communication Link from 20:41 [EDT] until 22:26 [EDT] 5/5/03. Computer displayed hard disk error. Rebooted machine; error corrected. Re-established ERDS Link." The NRC Resident Inspector will be notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-06
39825 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-05-05 14:45 | 2003-05-05 17:44 | 2003-05-05 | OFF SITE NOTIFICATION DUE TO LOSS OF 35 POUNDS OF FREON R-22. The licensee discovered that approximately 35 lbs of freon R-22 was missing from a plant refrigeration system. The State of New York requires the licensee to notify the National Response Center, New York State Department of Environmental Conservation and Oswego County Emergency Management Office of R-22 leaks to air >1 lb in any 24 hour period. The system currently tested tight, however an investigation is showing there was probably an acute release >1 lb during recent maintenance activities. The licensee notified the NRC Resident Inspector, the State, local agencies and other Government Agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-05
39824 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2003-05-05 11:30 | 2003-05-05 16:25 | 2003-05-05 | MALFUNCTIONING IRRADIATOR CARRIER DOOR HINGE PIN ASSEMBLY Steris-Isomedix Services reported to the state that they had an incident where the hinge pin assembly on the carrier door of an irradiator malfunctioned. This resulted in the door opening and jamming at the source rack which in turn left the source in a fully unshielded position. The operator then went to the hoist cables for the source rack, which is in a shielded area, moved the cables around a bit and unjammed the source rack returning the source to the fully shielded position. The amount of time taken to return the source to the fully shielded position was approximately 20-30 minutes. The licensee is shutting down all irradiators to check the hinge pin assemblies. There were no exposures. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0 | 2003-05-08
39823 | 0 | FOX CHASE CANCER CENTER |  |  |  |  | 2003-05-02 10:48 | 2003-05-05 12:50 | 2003-05-05 | MISSING FEDEX SHIPMENT OF PHOSPHORUS-32 The licensee, Fox Chase Cancer Center reported not receiving a shipment of 351 micro curies of liquid P-32 from Amersham's Arlington, Illinois facility. The material, which is used in the licensee's research lab, was shipped via FEDEX on 4/11/03 and was to be received on 4/14/03. The material was scanned when loaded on the FEDEX truck, but not scanned when the delivery was made at the licensee's facilities. The licensee has no record of receiving the package and has filed a claim with FEDEX. FEDEX is still investigating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-05-05
39822 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-05-02 23:40 | 2003-05-03 06:27 | 2003-05-03 | LOSS OF ERDS SYSTEM At 2340 CDT on 5/2/03, the licensee discovered that Dresden Station's Emergency Response Data System (ERDS) computer was not functioning. Technicians performed troubleshooting and the ERDS computer was restored at 0440 CDT on 5/3/03. The licensee will notify the NRC Resident Inspector | 0 | 100 | 56 | 0 | 100 | 56 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-03
39821 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-05-02 16:45 | 2003-05-02 19:57 | 2003-05-02 | DEGRADED CONDITION DUE TO POSSIBLE THROUGH WALL LEAKAGE ON CRDM PENETRATIONS "During a walkdown of the Unit 3 reactor vessel [RV] head and CRDM [Control Rod Drive Mechanism] nozzle penetrations prior to RV head retirement, evidence of possible through wall leakage was observed on two CRDM penetrations. The locations are nozzle 4 and nozzle 7. Nozzle 7 had been previously repaired. Review of past outage video tape could not disposition as either new or old leakage. Several additional nozzle to head penetrations were masked by chromated water leakage deposits. "Initial Safety Significance: Any RCS [Reactor Coolant System] leakage from these penetrations would have been below the threshold of measurability by the reactor coolant system leakage measurement process. "The Reactor Vessel Head is scheduled for replacement during the present refueling outage. Therefore, there are no plans at this time to perform additional inspections or repairs on the current head." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-05-02
39820 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2003-03-24 | 2003-05-02 16:32 | 2003-05-02 | AGREEMENT STATE REPORT - RADIOACTIVE SHIPMENT EXCEEDED LIMITS On 3/24/03 Troxler Electronic Laboratories of Research Triangle Park, NC received a shipment of two boxes from AEA Technology, Inc. of Burlington, MA. Each box contained fifty 40 millicurie Am-241:Be sources. Following return of a survey meter from calibration, the RSO at Troxler performed a survey of the boxes on 3/31/03 and determined that the radiation levels exceeded limits for the shipment. Each box measured 315 millirem/hr neutron and gamma at the surface (limit of 200 millirem/hr). Additionally, the bill of lading and DOT sticker on each box listed the Transportation Index (TI) at 1.6 which is the limit, however the measured TI was 3.1 (3.0 millirem/hr neutron and 0.1 millirem/hr gamma at 1 meter). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2003-05-07
39819 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-05-02 06:10 | 2003-05-02 09:37 | 2003-05-02 | MAIN FEEDWATER PUMP "B" MANUALLY TRIPPED CAUSEING AUXILIARY FEEDWATER PUMP ACTUATION. "The 1A and 1B Motor Driven Aux Feed Water Pumps auto started due to trip of the 1B Steam Generator Feed Pump (SGFP). "The pump was providing feed water to the steam generators and a local watch was established to trip the pump should an overspeed condition be observed. The watch was established due to the overspeed test not having yet been done on the SGFP. The watch observed speed increasing on the SGFP and tripped the pump locally when speed was observed to be 5000 rpm and rising. The pump had previously been running at a stable 3600 rpm. "Control room staff entered AOP-13, Los of Feed, reduced nuclear power to 2% and stabilized the plant. (1A & 1B Motor Driven Aux Feedwater pumps can only handle 3% thermal rated power) "Plans are to investigate and correct the cause of the 1B SGFP speed increase. "The trip of SGFP occurred during plant startup from refueling with 1A SGFP Out of Service" The NRC Resident Inspector was notified of this event by the licensee. | 2 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-05-02
39818 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-05-02 06:32 | 2003-05-02 08:45 | 2003-05-02 | OFFSITE NOTIFICATION At 0632 CDT on 5/2/03, there was a small fire in Control Room Alarm Panel C-8-C. The fire was immediately extinguished with a hand held halon extinguisher. Two alarmed (tagged) cards were found to be damaged. The cause of the fire is under investigation, and there was no effect on plant operations. The licensee notified the NRC Resident Inspector. *** RETRACTION ON 5/2/03 AT 1549 FROM R. SCHREIFELS TO A. COSTA *** "NMC [Nuclear Management Company] is retracting the notification made at 0745 on 5/2/03 based on the small fire not being related to or affecting the health and safety of the public or site personnel. The alarm functions affected by the circuit board fire were confined to those associated with power supplies to non-safety bus which was previously de-energized. Plant operations was not otherwise affected." The Licensee notified the NRC Resident Inspection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-05-02
39817 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-05-02 02:14 | 2003-05-02 02:40 | 2003-05-02 | TECH SPEC REQUIRED SHUTDOWN DUE TO BOTH HYDROGEN IGNITER TRAINS DECLARED INOPERABLE. "A" and "B" Hydrogen igniter trains are inoperable requiring a plant down power per Tech Spec 3.0.3. Tech Spec 3.0.3 requires the plant to be in Hot Standby in 7 hours (clock started at 0115 EDT). "B" Train was inoperable to repair a cable and a cable was mistakenly cut on "A" Train. All Emergency Core Cooling Systems are operable, electrical grid is stable, and the Emergency Diesel Generators are fully operable as needed. The NRC Resident Inspector was notified of this event by the licensee. **** UPDATE on 05/02/03 at 0809 EDT by L. Brown taken by MacKinnon **** Train "A" Hydrogen igniters declared operable and Tech Spec 3.0.3 exited at 0741 EDT after its cable was repaired. NRC R2DO (Joel Munday) notified. The NRC Resident Inspector was notified of this update by the licensee. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-05-02
39816 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-05-01 14:30 | 2003-05-01 18:26 | 2003-05-01 | LOSS OF RADIATION LEVEL INDICATIONS IN THE AUXILIARY BUILDING AND CONTAINMENT VENT STACKS "On May 1, 2003 at 1430 [EDT], it was determined that the Containment and Auxiliary Building SPING units were not functioning properly and could not be relied upon to determine Emergency Classifications based on Emergency Action Level Chart A(2). Alternate Radiation Monitors remain available to provide indication of radiation levels in the Auxiliary Building and Containment Vent stacks; however, their use is not currently proceduralized. The use of the alternate Radiation Monitors to determine the Emergency Classification could impair the plant's ability to declare an emergency in a timely manner. Therefore, this is being conservatively reported as a major loss of emergency assessment capability under 10 CFR 50.72(b)(3)(xiii). "Safety equipment not operational for routine outage maintenance: 'A' Diesel Generator." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-05-01
39815 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-04-30 16:30 | 2003-05-01 12:46 | 2003-05-01 | AGREEMENT STATE REPORT: LOST AND FOUND RADIOACTIVE MATERIAL "An Amersham 660 radiography exposure device containing 26.7 curies of iridium-192 was lost from the back of a truck on 4/30/03 and recovered on 5/1/03. A radiography crew completed work for the day at a temporary job site. After traveling for about 15 miles from the site, the radiographers could not recall whether the device had been secured in the hut on the back of the truck. Upon checking, the crew found the truck's tailgate was open and the camera was not in the hut. Retracing their route did not locate the device nor was anyone still at the job site who may have found the device. The crew notified the RSO, obtained a scintillation radiation detector from another site, performed a more extensive search of the route with no success in locating the device. An Agency inspector joined the Licensee's search on 5/1/03. During the morning an individual notified the Licensee that he found the device. The Licensee is taking possession of the device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | MAT | [5 empty] | 0 | 2003-05-01
39814 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-04-27 12:00 | 2003-05-01 09:54 | 2003-05-01 | STUCK IRRADIATOR SOURCE The State of Nebraska was notified by Becton Dickinson Consumer Products located in Holdrege, Nebraska, that on 04/27/03 a source got stuck in the Becton Dickinson Pool Irradiator. The stuck source was moved to a shielded position. Nordion repaired the stuck source on 04/27/03. Nobody was exposed to the stuck source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2003-05-06
39813 | 0 | SIOUX VALLEY HOSPITAL |  |  |  |  | 2003-04-01 12:00 | 2003-04-30 18:41 | 2003-04-30 | POTENTIAL OVEREXPOSURE AS RECORDED IN PERSONAL DOSIMETER This is a preliminary report of a potential reportable event under 10 CFR 20.2203(2)(i). Nuclear Technologist dosimeter readings values for the month of February 2003 were reported by the NVLAP-accredited dosimeter company at 7877 mrem DDE. The Hospital does not have any other technologists, physicists or physicians with dosimeter readings above ALARA-1 levels for the month of February 200. The Licensee reported that there has been no unusual sources or amounts of activity present within their facility which could explain only one individual receiving 100 times their "normal" range occupational exposure in a single month. The Licensee is making preparations to conduct experiments in conjunction with the dosimeter company to duplicate the unusual exposure pattern and will complete and file a final report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | SD | HOS | [5 empty] | 0 | 2003-04-30
39812 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2003-04-30 14:20 | 2003-04-30 21:52 | 2003-05-05 | DEGRADED CONDITION DUE TO DEFECT IN REACTOR VESSEL HEAD PENETRATION "On April 30, 2003, at 1420 hours, with St. Lucie Unit 2 in a refueling outage, FPL discovered a defect in reactor vessel head penetration 72. This flaw was found during the ongoing reactor vessel head inspection being performed in accordance with the requirements of NRC Order EA-03-009. The defect is OD surface connected, extends into the nozzle and penetrates into the J-groove weld between the nozzle and reactor vessel head. The defect is described as an axial flaw, 0.28 inches deep X 0.96 inches long, on the downhill side of the penetration. Per the inspection guidance, surface flaws located in the attachment weld area are not acceptable. "There had been no indication of RCS leakage during the previous cycle's operation. This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A)." The Licensee notified the NRC Resident Inspector. *** UPDATE ON 5/2/03 AT 1337 EDT FROM R.WELLER TO A. COSTA *** "This report is a supplement to original event report #39812 dated April 30, 2003. On May 2, 2003 at 1240 hours, with St. Lucie Unit 2 in a refueling outage, FPL discovered a defect in reactor vessel head penetration #18. This is the second flaw found during the current ongoing reactor vessel head inspection being performed in accordance with the requirements of NRC Order EA-03-009. The defect is OD surface connected, extends into the nozzle and through the J-groove weld between the nozzle and reactor vessel head. The defect is described as an axial flaw, 0.39 inches deep X 2.98 inches long, on the downhill side of the penetration. Per the inspection guidance, surface flaws located in the attachment weld area are not acceptable. There had been no indication of RCS pressure boundary leakage during the previous cycles operation. This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A)." The Licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/05/03 @ 1503 BY HESSLING TO GOULD * * * This report is a correction to the supplement to original event report #39812 dated April 30, 2003. On May 2, 2003 at 1240 hours, with St. Lucie Unit 2 in a refueling outage, FPL discovered a defect in reactor vessel head penetration #18. The second flaw was incorrectly identified to be 0.39 inches in depth, and 2.98 inches in length, located on the down-hill side of the penetration. The correct depth was 0.26 inches in depth, length was 2.98 inches. The location of this flaw was on the side of the penetration, vice on the down-hill side. This flaw was found during the current ongoing reactor vessel head inspection being performed in accordance with the requirements of NRC Order RA-03-009. The defect is OD surface connected, extends into the nozzle and through the J-groove weld between the nozzle and reactor vessel head. The defect is described as an axial flaw. Per the inspection guidance, surface flaws located in the attachment weld area are not acceptable. There had been no indication of RCS pressure boundary leakage during the previous cycle's operation. The NRC Resident Inspector was notified. The Reg 2 RDO (Munday) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-04-30
39811 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-04-28 07:00 | 2003-04-30 13:18 | 2003-04-30 | TEXAS AGREEMENT STATE REPORT ON DISABLED GAUGE FOR OIL CRACKING PLANT "Licensee immediately suspended operations in the affected "reactor" (oil cracking plant) due to loss of measurement caused by loss of level/density measurements from an Ohmart Corporation (OC) Model SH-F2, source holder, containing 1 curie of Cs-137, Serial # 68526, located on the exterior surface of the SAS Sodium reactor, vessel # R-7202. Operators noted a loss of measurement at approximately 7:00 a.m. When investigating the outside of the reactor vessel, on-site personnel noted that the fixed gauge had broken free of its mounting bracket and fallen, face-down, approximately 10 feet to the ground. Plant personnel immediately notified Techstar, a subsidiary of Ohmart/Vega Corporation, for field service. A service technician arrived on scene, surveyed the gauge for radiation leakage, checked for contamination, and checked the functional operation of the gauge. The shutter was closed and locked by service personnel, until damage could be assessed. No damage was sustained by the gauge. The mechanism was fully functional and has been reinstalled on the reactor vessel. A set screw (a 3/4 to 1 inch bolt) had failed on the mounting bracket, due to suspected structural fatigue and vibration over 11 years since the gauge was installed (December 1992). The gauge was reinstalled in a bracket modified to fit on the welded beam (2-inch pipe), that will not allow the gauge to fall if the set screw fails in the future. All other gauges on site were checked by service personnel for security and possible deterioration on mounting hardware. This gauge was unique in this plant due to it's mounting which has now been upgraded to allow for fail-safe operation without loss of function should the bracket fail. Problem has been corrected by the service company. Modification to the mounting bracket and replacement of the set screw has rectified the cause of this incident and returned the reactor to operation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-05-05
39810 | 0 | SUSTAINABLE RESOURCES CENTER |  |  |  |  | 2003-04-25 19:30 | 2003-04-29 16:04 | 2003-04-29 | STOLEN X-RAY FLORESCENCE DEVICE Sustainable Resources Center reported that their cleaning people let an individual into the building on 4/25/2003 at approximately 1930 and believe that he stole the X-Ray Florescence ( XRF) device. The unit was a Niton model XL300 serial # U2830NR2200 containing 14 millicuries of cadmium-109 and was inside a case resembling a camera case. This device is used to analyze lead base paint and was on lease to Sustainable Resources Center. The Minneapolis Police Department will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-04-29
39809 | 0 | US ARMY |  |  |  |  | 2003-03-12 10:00 | 2003-04-29 13:37 | 2003-04-29 | LICENSEE REPORTED TWO LOSS/STOLEN TRITIUM EXIT SIGNS The licensee reported that two tritium exit signs stored in boxes in a storage building in the hazmat center turned up missing. Each sign had 15 curies of tritium for a total of 30 curies. Last inventory made on these signs was 09/00. They have searched for them with no success. They are continuing further investigation to determine if the signs had been installed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | KY | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-04-29
39808 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-04-29 03:13 | 2003-04-29 06:01 | 2003-04-29 | MANUAL REACTOR TRIP DUE TO FIRE IN THE HIGH PRESSURE TURBINE The following information was received from the licensee via facsimile: "Class B fire south end of turbine resulted in manual trip of the Rx and Turbine. The fire was out in 47 minutes. There were no ESF actuations - all systems responded as expected except let down isolated on a low pressurizer level. Due to the fire being greater than 15 minutes a [Notice of Unusual Event] was entered at 0313 [EDT] and exited at 0520 [see event notification 39807]. The plant is currently in Mode 3 Hot Standby." During the reactor trip, all rods inserted. The electrical bus is stable and supplying required plant loads. The other unit on the site was already shutdown and unaffected by the fire or reactor trip. Core decay heat is being removed using the steam dump to condenser system and the auxiliary feedwater system. The extent of damage to the turbine is under investigation by the licensee. The NRC Resident Inspector has been notified by the licensee. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-04-29
39807 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-04-29 | 2003-04-29 04:52 | 2003-04-29 | UNUSUAL EVENT DECLARED DUE TO FIRE IN THE TURBINE The following information was obtained from the licensee via facsimile: "Class B fire south end of Main High Pressure Turbine located 53 foot elevation of turbine building. Reactor and turbine were manually tripped. Fire brigade was dispatched. Fire was out in 47 minutes. There were no ESF actuations or other anomalies during trip with one exception - letdown isolated on low pressurizer [level] and was subsequently restore[d]. No injuries." The NRC Resident Inspector was notified by the licensee. * * * UPDATE ON 4/29/03 @ 0527 EDT FROM MIKE DONEGAN TO HOWIE CROUCH * * * The licensee has terminated the NOUE at 0520 EDTon the basis that the fire is out and the plant is stable. Notified R1DO (Jackson), NRR EO (Lyons), DIRO (Evans), DENVER and FEMA (Sullivan). | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-04-29
39806 | 0 | GE NUCLEAR ENERGY |  |  |  |  | 2003-04-28 | 2003-04-28 21:37 | 2003-04-30 | INTERIM SURVEILLANCE PROGRAM FOR FUEL CHANNEL BOW MONITORING (PART 21) The control rod-fuel channel interference evaluation has been completed. It determined that BWR/6 and BWR/4 & 5 C-lattice plants with GNF thick/thin channels potentially have increased channel bow that can impact fuel bundle lift, loads on reactor internals, and control rod operability. An interim surveillance program has been developed to augment the surveillance requirements in the plant Technical Specifications until other actions, which mitigate or limit the potential for control rod-channel interference due to channel bow can be identified and implemented. The recommendations address the extent and frequency of surveillance actions, and the plants to which they should be applied. This surveillance program provides early indication of potentially degraded operational performance and assurance that action is taken before reaching excessive levels of control rod friction. This surveillance plan is limited to BWR/6 and BWR/4 &5 C-lattice plants with GNF thick/thin channels and GE control rods. There have been no indications of operational or scram problems on BWR/2, 3 and 4 D-lattice plants, and as a result, they are excluded from the interim surveillance program. Plants Recommended for Surveillance Program Clinton Hope Creek Nine Mile Point 2 Fermi 2 Grand Gulf River Bend LaSalle 1 LaSalle 2 Limerick 1 Limerick 2 Perry 1 Susquehanna 1 Susquehanna 2 *** UPDATE ON 4/30/03 AT 1841 FROM J.S. POST TO A. COSTA *** GE Nuclear Energy has submitted correspondence to the USNRC to exclude the following plants from the surveillance program: Hope Creek, LaSalle1, LaSalle2, Susquehanna 1 and Susquehanna 2. Notified R1DO(Jackson), R3DO(Gardner), R4DO(Pick) and NRR EO(Gillespie). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-04-28
39805 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2003-04-28 18:35 | 2003-04-28 19:57 | 2003-04-28 | REDUCED REACTOR POWER FROM 100% TO HOT STANDBY DUE TO INOPERABLE ISOLATION VALVE Unit 3 commenced a load reduction at 1835 to comply with T.S. 3.6.4, Containment Isolation Valve. The letdown isolation valve CV-3-200B was declared inoperable at 1600 due to indications there may be through valve leakage. Letdown is still currently in service. The intent is to isolate the letdown penetration once the unit is in mode 3, and affect troubleshooting and repairs. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-04-28
39804 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2003-04-28 16:45 | 2003-04-28 19:27 | 2003-04-28 | REACTOR TRIP FROM 100% POWER DUE TO A TURBINE TRIP The licensee reported they had a turbine trip possibly due to the loss of output breakers which resulted in turbine overspeed causing the trip. The reactor trip from 100% was caused by the turbine trip. All rods fully inserted and there was no ECCS actuation, however one PORV lifted and reseated. All three emergency diesel generators auto started and loaded. The 4 reactor coolant pumps lost power, so the reactor was in natural circulation from 1645 to 1823 when they restored one coolant pump. The plant had lost power restored at 1904. They also had their aux. feedwater to auto start as expected due to a low steam generator level. The plant is currently stable and they are investigating the cause of the turbine trip. The NRC Resident Inspector was notified along with the New York Public Service Commission | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-04-28
39803 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2003-04-28 09:00 | 2003-04-28 14:25 | 2003-04-28 | FAILURE TO TAKE FITNESS FOR DUTY TEST A contract supervisor refused to take a required fitness for duty test this morning. This action resulted in him being permanently denied access. His work history was reviewed and no discrepancy was found. The individual has turned in his resignation. The NRC Resident inspector will be informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 26.73 |  |  |  | 0 | 2003-04-28
39802 | 0 | DELTA CONSULTING ENGINEER |  |  |  |  | 2003-04-28 10:00 | 2003-04-28 12:03 | 2003-04-29 | STOLEN TROXLER GAUGE Licensee reported that a Troxler Gauge Model 3430 serial number #029673 containing approximately 90 millicuries of Cs-137 and 44 millicuries of Am-241 was stolen from a construction site trailer in Guaynabo, Puerto Rico. Sometime between the evening of 4/25/03 and 10:00 on 4/28/03. The licensee has notified the local law enforcement. Note From HOO: Troxler model 3430 normally has 8 millicuries of Cs-137. * * * UPDATE ON 04/29/03 @ 1515 BY SOUSA TO GOULD * * * The Troxler gauge was returned on 04/29/03 @ 1400 to the licensee. There appeared to be no damage to the gauge, but they will be performing a leak test on it. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | PR | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-04-28
39801 | 0 | HOSPITAL OF ST. RAPHAEL |  |  |  |  | 2003-04-28 | 2003-04-28 11:37 | 2003-04-28 | PROVISIONAL REPORT OF MEDICAL MISADMINISTRATION On 4/22/03, Nuclear Medical Technicians at St. Raphael Hospital received 2 vials ( 75 millicurie each) of I-131 that was to be administered to a patient later that afternoon. The vials were placed in their normal storage location. When the patient arrived, a nuclear technician administered only one vial of the I-131 which only gave the patient half of the prescribed dose. On 4/23/03, while preparing nuclear medicine for a different patient, a technician discovered the second vial of I-131 that was to be administered to the patient from the previous day. Upon discovery, the patient and the prescribing physician was notified of the error. The physician determined that the 27 hour span between doses would have no deleterious effects on the patient so the second dose was administered in the afternoon of 4/23/03. The intended dosage was 150 millicuries and the received dose was 142.4 millicuries. The RSO was notified at 0800 hrs. EDT on 4/24/03 and contacted NRC Inspector Richard McKinley who advised the licensee to make this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | HOS | [5 empty] | 0 | 2003-04-28
39800 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-04-26 22:06 | 2003-04-27 18:05 | 2003-04-27 | PLANT HAD A SAFETY EQUIPMENT FAILURE At 2208 CST, on 4-26-03 the Plant Shift Superintendent (PSS) was notified that a UF6 Release Detection System smoke detector for the No. 3 Normetex Pump in C-315 had fired. Operators responded and found no indications of a UF6 release. The No. 3 Normetex Pump was in TSR 2.3.1 Mode 4, "Not In Use" at the time the smoke detector alarmed. Operators then attempted to reset the smoke detector and a system trouble alarm was received. The trouble alarm would not reset and attempts to test fire the smoke detectors for the Normetex Pumps was unsuccessful. At the time of this incident, the C-315 No.1 and No. 2 Normetex Pumps were in an operational mode in which the UF6 Release Detection System was required to be operable, TSR 2.3.4.3 Mode 2, "Withdrawal". The PSS declared the system inoperable and TSR LCO 2.3.4.3 actions were implemented to establish a smoke watch and place the Normetex pumps in Mode 3, "Standby". The failed smoke detector was replaced, post maintenance testing completed and the system was declared operable at 0053 CST on 4-27-03. The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(l); "An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident." The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. The NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2003-04-27
39799 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2003-04-26 17:46 | 2003-04-26 18:23 | 2003-04-26 | NOUE DECLARED DUE TO FIRE IN THE OWNER PROTECTED AREA LASTING MORE THAN 10 MINS. The licensee declared a NOUE at 1803 due to a fire in the owner protected area on the motor of the "B" circulating water pump at the intake that lasted for more than 10 minutes. There are a total of three pumps and two are now operable. The smoking fire (no flames) was extinguished at 1823 with no assistance from offsite. There were no injuries or damage to the plant. The licensee will not issue a press release. The licensee notified the State of South Carolina, Darling , Lee, and Chesterfield counties. The NRC Resident Inspector was notified. *****UPDATE ON 4/26/03 AT 19:30 FROM EAYRES TO LAURA***** The NOUE was terminated at 19:23. The electrical fire is out and there was no impact on continued plant operation. Notified R2DO (ERNSTES), DIRO (EVANS), NRR (LYONS), NRC ALTERNATE SITE, FEMA (EACHES) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-04-26
39798 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2003-04-25 | 2003-04-25 10:26 | 2003-04-25 | AGREEMENT STATE REPORT - KENTUCKY "This letter is notification of a stuck radiography source event that occurred on March 28, 2003 at Marathon Petroleum in Louisville Kentucky. The licensee involved was Hayes Testing Laboratory, Inc., Radioactive Material License Number 201-168-05. The radiography source was 92.7 [curies] of Ir-192, housed in a 660 B Camera, S/N 1175. "On March 28, 2003, during performance of radiography with the source extended, a magnet stand fell approximately 10 feet onto the source tube. This resulted in a crimp in the source tube, and the radiography source could not be retracted into the camera. The area had been initially roped off and posted off at the 2 mrem/hr boundaries, but once the radiography source could not be retrieved, personnel followed licensed emergency procedures and secured the entire area. "The radiographer and the radiographer's supervisor attempted to use all safe means to retrieve the radiography source without success. The Radiation Safety Officer (RSO) was contacted immediately, and was able to determine source location, and shielded the exposed source with four (4) 25 lb. bags of lead shot. The RSO using extended handle channel locks, was able to un-crimp the source tube and retrieve the radiography source back into the camera. The estimated time to un-crimp the source tube and retrieve the source was approximately 2.5 minutes. "The radiographer, radiographer's assistant, radiographer's supervisor and RSO's dosimetry were immediately sent to ICN [a film processing lab] for processing. The exposure results were highest in all aspects for the RSO at 111 mrem deep dose, 107 mrem eye dose, and 103 shallow dose. "The response to this event was considered appropriate and met licensing conditions. The Commonwealth of Kentucky considers this event closed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | KY | OTH | AGR |  |  |  |  | 0 | 2003-04-30
39797 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-03-29 01:14 | 2003-04-25 10:24 | 2003-04-25 | 60-DAY OPTIONAL REPORT FOR INVALID SPECIFIED SYSTEM ACTUATION The following information was obtained from the licensee via facsimile: "THIS IS BEING REPORTED PER 10 CFR 50.73(a)(2)(iv)(A). "The following systems inadvertently actuated: "Core Spray A "Core Spray B "#2 Diesel Generator started and came to speed "Core Spray A and B were complete actuations. "#2 Diesel Generator was a partial actuation since it did not load. There was no loss of offsite power or requirement to load. "Affected equipment started and functioned successfully." The cause of the actuation was human error when the operator performing a Reactor Protection System surveillance test mechanically actuated the wrong relay. The reactor was in refueling and flooded-up at the time of the core spray actuation. There was a minor change in skimmer surge tank level before Operations personnel were able to manually isolate core spray. The licensee still has a Significant Condition Report (SCR) open that should address ways to minimize re-occurrence. The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-04-25
39796 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-24 14:17 | 2003-04-25 09:58 | 2003-04-25 | FITNESS FOR DUTY A contract employee was determined to be under the influence of marijuana during a monitor result drug test. The employee's access to the plant has been permanently terminated. Contact the HOO for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Shutdown | Hot Shutdown |  | Hot Shutdown | Hot Shutdown |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2003-04-25
39795 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-04-03 | 2003-04-24 15:59 | 2003-04-24 | REPORT OF EXPOSURE OF LICENSEE EMPLOYEES WAS MADE TO THE STATE The licensee reported the exposure of licensee employees to radiation from a TN Technologies model 5174 (serial # B103) fixed gauge containing a 2 curie Cs-137 sealed source. The gauge fell approximately 6 feet from its location on a coke hopper on approximately 04/03/03. The welds which attached the gauge anchoring bolts appear to have failed. The gauge had been in place since 1992. The gauge fell with the shutter open onto the first landing of the skip pit area. The gauge went un-noticed for a week until April 11 @ 1300 when maintenance workers were called to move what was thought to be a motor (all labels and markings on the gauge were unreadable). The workers spent approximately 1.5 hours rigging and moving the gauge before an individual recognized the gauge and secured the area. A contractor, Radiometrics, was then called in to secure the gauge. The Ohio department of Health was called concerning the incident on April 17 @1400. An on-site investigation was done and a dose assessment of affected personnel is in progress. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-04-29
39794 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-04-24 14:06 | 2003-04-24 15:01 | 2003-04-24 | OFFSITE NOTIFICATION DUE TO HYDRAULIC OIL SPILL The licensee notified the state that they had approximately one tablespoon of hydraulic oil spill from a manlift to the soil in the south RCA yard near the rad waste reduction facility. The NRC RDO(Gray) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-24
39793 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-04-24 09:47 | 2003-04-24 15:33 | 2003-04-24 | GRAND GULF AUTOMATIC SCRAM AND ECCS INJECTION DUE TO PARTIAL LOOP "At 09:47 (CDT), Grand Gulf Nuclear Station (GGNS) auto scrammed due to complications following a partial loss of offsite power. At the time of the scram there was a severe thunderstorm in the vicinity of GGNS. It is believed that high winds caused damage in the GGNS switchyard which in turn led to the partial LOOP. The following items actuated/initiated during this event: "1. RPS automatic actuation, exact cause unknown. "2. HPCS and RCIC initiated on reactor water level 2 and injected into the vessel to restore water level. "3. Division 2 and 3 EDGs started on a loss of power to the 16 and 17 buses. Division 2 and 3 EDG energized the 16 and 17 buses respectively. "4. Some time after the initial event the 15 bus lost power and was re-energized by the Division 1 EDG. "5. All MSIVs isolated on loss of power. "6. Containment isolation occurred on power loss and on reactor water level 2. "At present reactor water level is being maintained with RCIC and reactor pressure is being maintained with SRVs. A review of plant data is underway to confirm proper response of plant equipment." The NRC Resident Inspector was notified by the licensee. *****UPDATE ON 4/24/03 AT 19:20 FROM BRINMAN TO LAURA***** "It should be noted that offsite power was always available to the GGNS from the ESF transformer #12 during/following the scram at 09:47 hours (CDT) on 4/24/03. Also, there was no structural damage to the GGNS switchyard. There was only minor damage to a locking collar on a disconnect in the GGNS switchyard. The wind blew the disconnect closed breaking it's locking collar and grounding the switchyard through a grounding strap. The grounding strap disintegrated and a lockout occurred on service transformer #21 and the west bus of the GGNS switchyard. Power has been restored to all busses and all diesel generators have been secured." Notified R4DO (C. Cain) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-04-24
39792 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-04-24 11:00 | 2003-04-24 12:07 | 2003-04-24 | ALERT AT PERRY DUE TO EVENT IN FUEL HANDLING BUILDING "At 11:00 the control room received a High alarm on the FHB Gas and Alert on FHB Iodine. ONI ZZZ-7 was entered along with ONI J11-2 and ONI D17. Fuel movement was stopped after all fuel was placed in a safe condition. The FHB, Drywell, and Containment were evacuated and the Containment and FHB closure plans were carried out. At 11:30 the control room received a report that the fuel bundle being inspected in the FHB had a bubble float to the top of the pool. At 11:27 the alarms in the FHB reset. The entry into an Alert was recognized at 11:50 and initial notifications were completed. The Technical Support center has been staffed to develop a recovery plan." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | ALERT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-04-24
39791 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-04-24 | 2003-04-24 05:42 | 2003-04-24 | CRITICALITY CONTROL 24-HOUR REPORT (RESPONSE BULLETIN 91-01) The following information was obtained from the regulatee via facsimile: "At 1320 [CDT] on 4/23/03, the Plant Shift Superintendent (PSS) was notified that the trap media replacement activities for C-337 #4 Seal Exhaust (SX) trap were performed on 4/6/03 through 4/8/03 and the trap media and the bottom screen were replaced. Contrary to the requirements of NCSA CAS-007, 'independent verification of no trap media below the bottom screen' was not performed prior to the bottom flange being removed. This requirement ensures that an unanalyzed volume of media does not spill from the trap. "The NRC Resident Inspector has been notified of the event. "PDGP Assessment and Tracking Report No. ATR 03-1199 PGDP Event Report No. PAD-2003-008 NRC Event Worksheet [39791]. "Responsible Division: Maintenance "SAFETY SIGNIFICANCE OF EVENTS: "Although the trap was not independently verified to be essentially empty of accumulated trap mix, prior to in-place maintenance, no media was found when the bottom flange was removed. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(s) OF HOW CRITICALITY COULD OCCUR): "In order for a criticality to be possible, a critical volume of trap mix would have to be accumulated in an unsafe geometry. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION. ETC): "Double contingency is maintained by implementing two controls on volume. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "There was no media found when the bottom flange was removed. "NUCLEAR CRITICALITY SAFETY CONTROL (S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The first leg of double contingency relies on controlling the volume of trap mix available to be spilled from the, trap after removal of media above the bottom screen. NCSA CAS-007 requires the trap to be verified emptied of trap media prior to in-place maintenance, thus ensuring that the trap does not contain any accumulated trap mix in excess of a 5.5-gal drum. Verification of the trap mix accumulated in the trap was not done, thus, this control was violated. "The second leg of double contingency relies on controlling the volume of trap mix available to be spilled from the trap after removal of media above the bottom screen. NCSA CAS-007 requires the trap to be independently verified emptied of trap media prior to in-place maintenance. Independent verification of the trap mix accumulated in the trap was not performed, therefore, this control was violated. Neither of the controls (verification and independent verification) of the single parameter (volume) were performed and double contingency was not maintained. "No trap media was spilled from the trap, thus maintaining the volume parameter. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "None." Operations notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-04-24
39790 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-24 03:48 | 2003-04-24 04:40 | 2003-04-25 | ALERT DECLARED At 0348 EDT on 4/24/03, the plant experienced an influx of fish on the intake screens for the circwater and essential service water (ESW) systems. This resulted in a loss of vacuum to Units 1 and 2 main turbines, which led operators to manually trip both reactors. Following the trip, operators noted that ESW flow to all 4 emergency diesel generators (EDGs) was severely degraded. This resulted in the licensee declaring all 4 EDG's inoperable. An alert was declared at 0348 EDT, and the NRC entered Monitoring Mode at 0506 EDT. * * * UPDATE AT 0600 ON 4/24/03 FROM LICENSEE TO H. CROUCH * * * All EDG's have adequate flow to be used in an emergency, but remain inoperable. The licensee is assessing damage to intake screens and strainers in the ESW system, and manually backwashing ESW screens. * * * UPDATE AT 0718 ON 4/24/03 FROM DEAN BRUCK TO E. THOMAS * * * The licensee made a 4-hour ENS notification under 10 CFR 50.72(b)(2)(iv)(B) to inform the NRC of the manual reactor trips inserted on Units 1 and 2 at 0328 and 0329 on 4/24/03 for the reasons listed above. Post-trip response of the plant was normal. Main Steam Isolation Valves were manually closed on both units due to lowering Reactor Coolant System temperature and lowering vacuum. Both units remain in Mode 3. * * * UPDATE AT 1020 ON 4/24/03 FROM TODD CASPER TO E. THOMAS * * * The licensee made an 8-hour ENS notification under 10 CFR 50.72(b)(3)(iv)(A) to inform the NRC of the Auxiliary Feedwater System (AFW) actuations in Units 1 and 2 following the reactor trips. The heat removal path for both units is via AFW to the steam generator pressure operated relief valves. * * * UPDATE AT 0532 ON 4/25/03 FROM R3 IRC TO E. THOMAS * * * The licensee terminated the Alert at 0521 EDT. The Alert was terminated based on having one train of ESW and one EDG declared OPERABLE for each Unit. The NRC exited the Monitoring Mode of normal operations at 0532 EDT. | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | M/R | M/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-04-24
39789 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2003-04-23 19:23 | 2003-04-24 01:25 | 2003-04-24 | ACCIDENT MITIGATION "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. On 04/23/03, at 18:15 CDST, the 1A Diesel Generator was made inoperable for a scheduled surveillance. Concurrent with this inoperability, the 0 Diesel Generator received a spurious CO2 actuation signal. This spurious CO2 partial logic actuation did not result in an actual CO2 injection into the 0 Diesel Generator Room. The CO2 system partial actuation however resulted in several ventilation dampers failing closed as designed. With these dampers closed, the ventilation support system for the 0 Diesel Generator became inoperable, the 0 Diesel Generator was declared inoperable at 1923 hours 04/23/03. This condition resulted in both the 1A and 0 Diesel Generators concurrently being inoperable. Actions were taken to terminate the 1A Diesel surveillance and restore the 1A Diesel Generator to an operable status. This was accomplished at 1952 hours 04/23/03. The 1A and 0 Diesel Generators were simultaneously inoperable for 29 minutes. Due to the concurrent Diesel Generator inoperabilities which affect redundant trains required to mitigate the consequences of an accident, it has been determined that this event is reportable as an 8 hour ENS notification. "Corrective actions have been initiated to address the 0 Diesel Generator CO2 system and restore the ventilation dampers to an operable status. The spurious actuation of the 0 Diesel Generator CO2 system was determined to be due to a Non-Licensed Operator opening the fire detection panel for inspection." The licensee notified the NRC Resident Inspector. | 67 | 0 | 0 | 67 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-04-24
39788 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2003-04-23 19:55 | 2003-04-23 23:44 | 2003-04-23 | LOST OF EMERGENCY ASSESSMENT CAPABILITY "This report is being made pursuant to 10CFR50.72(b)(3)(xiii) Major loss of emergency assessment capability. During the performance of routine surveillance LOS-VG-M1 Standby Gas Treatment System Operability Test and Inservice Test of 1VG001 and 1VG003, it was reported that the installed preplanned monitoring system sample pump tripped. At 19:55 CDST on April 23rd it was confirmed that the sample pump had tripped for the Preplanned Alternate sampling system. This Preplanned Alternate sampling system had been connected to comply with the Technical Requirements Manual (TRM) from the inoperability of the installed Standby Gas Treatment Stack monitoring system (Standby Gas Treatment system Wide Range Gas Monitoring system -SBGT WRGM). Troubleshooting is in progress to restore the Preplanned Alternate sample pump. The Standby Gas Treatment Train has been secured and placed in standby configuration. The plant is stable and no abnormal or elevated release occurred during this event." The licensee notified the NRC Resident Inspector. | 67 | 100 | 0 | 67 | 10 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-23
39787 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-12 12:54 | 2003-04-23 12:46 | 2003-04-23 | INVALID START OF THE FOUR EMERGENCY DIESEL GENERATORS. On 04/12/03 at 1254 an invalid start of the four emergency diesel generators occurred. The actuation was caused by a loss of DC power to the 1BB emergency diesel start circuit and a auto start signal to the remaining 3 emergency diesel generators. Power loss was caused by poor terminal lug contact on a space breaker during testing of a Vital Battery breaker. The specific train actuated were both Train "A" and "B" for both Units 1 and 2. The system actuated was emergency AC electrical power (emergency diesel generators). Complete train actuation occurred. The Emergency Diesel Generator start was successful. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-04-23
39786 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-08 12:11 | 2003-04-23 12:43 | 2003-04-23 | INVALID UNIT 2 TRAIN "B" CONTAINMENT VENT ISOLATION (CVI) . On 04/08/03 at 1211 an invalid Unit 2, Train "B", Containment Vent Isolation (CVI) occurred. The actuation was caused by increased sensitivity of radiation monitor 2-RM-90-131 as a result of small perforations in the aluminum foil cover of the detector. The specific train actuated was Train "B", and the system which received the isolation signal were Containment Ventilation Purge and EXHAUST (already closed) and Radiation Monitoring isolation valves (went closed). Complete train actuation occurred. The Containment Ventilation Isolation function was successful. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-04-23
39785 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-03-21 12:19 | 2003-04-23 10:23 | 2003-04-23 | INVALID SPECIFIED SYSTEM ACTUATION "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73(a)(iv)(A) to describe an unplanned, invalid actuation of a specified system, specifically the E-2 Emergency Diesel Generator (EDG). "On March 21, 2003, a momentary short was created during the installation of test jacks, which resulted in an invalid start signal to the E-2 EDG. The E-2 EDG started, however, the associated emergency buses remained energized from their normal power supplies. "The affected emergency diesel generator responded as expected for the given conditions and was subsequently returned to a normal configuration per plant procedures. No deficiencies or abnormalities were noted during the event. "This event has been entered into the site-specific corrective action program for resolution. "The NRC resident has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-04-23
39784 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-04-23 02:07 | 2003-04-23 05:29 | 2003-04-23 | RPS ACTUATION WHILE CRITICAL "At 0207 EDT on April 23, 2003, a loss of feedwater occurred on Unit 1. Operators initiated a manual reactor scram at 15 [inches] RPV level (auto scram signal = 12.5 [inches]). The high pressure coolant injection (HPCI) and reactor core isolation coolant (RCIC) systems initiated as designed at -38 [inches], and injected into the RPV. RPV level was restored to the normal band, HPCI and RCIC secured, and a reactor feed pump was returned to service. The following isolation signals were received; Groups IB, IIA, IIC, III, VIB, VIC, VIIB, VIIIB, and HVAC. RPV and containment parameters are normal with an RPV cooldown in progress. "The loss of feed resulted from sequential trips of all 3 reactor feed pumps on low suction pressure due to an apparent isolation of the condensate deep bed demineralizers. The cause is under investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-04-23
39783 | 0 | US ARMY ROCK ISLAND |  |  |  |  | 2003-04-22 12:00 | 2003-04-22 16:14 | 2003-04-22 | M1A1 COLLIMATOR TRITIUM FILLED TUBE FOUND BROKEN. This event probably occurred the weekend of April 19-20, 2003 at the Ohio National Guard facility located in Newton Falls, Ohio. Ohio National Guard were unpacking an M109 Howitzer issue box at the receiving dock. The guardsmen were placing the unpacked packing material in a dumpster. As they were unpacking the box they noticed broken glass inside the plastic bag containing a collimator, which contains a 10 curie source. The National Guard contacted the on site Radiation Safety Officer (RSO). The RSO wipe tested the collimator and its case, then double bagged it and placed it into the radiation storage shed located outside of the shop. They then wiped tested and double bagged all packing materials associated with the crate and retrieved the packing materials from the dumpster. Wipe tests of all affected areas were also taken and submitted to Radiological Engineering Laboratory for analysis. Analysis results indicated significant contamination within the storage area. The Ohio Army National Guard RSO is being provided with the analysis results and decontamination procedures. They have also been advised to place those individuals closely involved with the significant contamination, on tritium bioassay program until it can be determined whether tritium exposure occurred or until tritium levels are eliminated. Decontamination procedures will be performed and contamination radiation surveys of all affected areas accomplished until contamination levels are reduced to acceptable levels or eliminated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2003-04-22
39782 | 0 | HARTFORD HOSPITAL |  |  |  |  | 2003-04-18 16:00 | 2003-04-22 15:12 | 2003-04-22 | SOURCES INCORRECTLY POSITIONED IN A PATIENT. The following is submitted as a medical event record for Hartford Hospital, Hartford, CT. This occurred late Friday, April 18, 2003 and it involved the use of the 3.5 French, 40 mm Novoste Beta-Cath unit with a Beta-Rail catheter. Novoste had a representative onsite to provide training to the interventional cardiologist. The radiation oncologist and the medical physics staff were experienced in the handling of the 3.5 French Beta-Cath unit. The Novoste representative was not in the cath lab operatory at the time of the insertion of the Beta-Rail catheter, or, of the sources. He was observing from the adjacent control area and he thought the interventional cardiologist understood the markings on the new style catheter. The interventional cardiologist imaged the patient (using fluoroscopy) and determined that the sources were incorrectly positioned. At approximately 60 seconds into the treatment, the sources were withdrawn. The catheter was correctly positioned and the sources were reinserted for the accurate treatment of the cardiac vessel. No adverse effects were seen to occur to the patient, and, none are expected to occur. A written report will be submitted to the Region I offices within 15 days as required. Notified R1DO Harold Gray and NMSS EO John Greeves. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [10 empty] | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-04-22
39781 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-04-22 14:51 | 2003-04-22 15:10 | 2003-04-22 | OFFSITE NOTIFICATION TO THE OHIO EMERGENCY PROTECTION AGENCY "On 04/22/03 at 1341 hours, while taking # 3 boiler off line, the average opacity reading was above 20% on two occasions within a one-hour period. This requires a verbal notification to the Ohio Environmental Protection Agency (OEPA). "At 1451 hours, the Plant Shift Superintendent notified OEPA of the X-600 Steam Plant opacity exceedance. UE-RA-RE1030, App. D, section P, requires a 4 hour NRC event when other government agencies are notified." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-04-22
39780 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2003-04-22 | 2003-04-22 11:05 | 2003-04-22 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The licensee reported that upon arriving at their work site in Bethesda, MD early in the morning of 04/22/03 they discovered that their construction trailer was broken into and a moisture density gauge stolen. The gauge is a CPN Model # MC1DR, S/N MD00305503 containing 10 millicuries Cs-137 and 50 millicuries Am-241:Be. The licensee notified the Montgomery County Police (Case # B03089862). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2003-04-25
39779 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-04-21 21:17 | 2003-04-21 22:26 | 2003-04-21 | ELECTROMATIC RELIEF VALVE FAILED TO OPEN DURING POWER ASCENSION TESTING. While performing Technical Specification required surveillance testing during power ascension per NI-ST-C2, Solenoid-Activated Pressure Relief Valves Operability and Flow Verification Test, 111 Electromatic Relief Valve (ERV) failed to open as required. 111 ERV has been declared inoperable and Technical Specification 3.1.5. (b) has been entered. This Limiting Condition of Operation requires reactor coolant dome pressure be reduced to 110 psig or less within 10 hours (start time is 2117 EDT). The cause for the failure of 111 ERV is under investigation. The other 5 ERV's (used also as ADV valves) tested satisfactorily. Plant preparations are in progress. The electrical grid is stable and their Emergency Diesel Generators are fully operable if needed. All Emergency Core Cooling systems (including the Isolation Condenser) are fully except for 111 ERV. The licensee notified the New York Service Commission of this event. The NRC Resident Inspector was notified of this event by the licensee. | 23 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-04-21
39778 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-04-21 07:30 | 2003-04-21 15:32 | 2003-04-21 | EMERGENCY RESPONSE SIREN ACTUATED. At approximately 1430 hours EDT, control room personnel received notification that one emergency response siren may have inadvertently actuated. At approximately 1400 hours EDT control room personnel were notified that local press and media outlets were informed of the siren malfunction. Currently 94 of 96 sirens are operable. The NRC Resident Inspector will notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-21
39777 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-04-21 11:40 | 2003-04-21 12:35 | 2003-04-24 | DISCOVERY OF SAFEGUARDS INFORMATION. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THIS EVENT BY THE LICENSEE. CONTACT THE HOO FOR FURTHER DETAILS. * * * * UPDATE ON 04/24/03 AT 1410 BY HALLIDAY TO GOULD * * * * RETRACTION The Security Manager, with personnel from Security and Regulatory Compliance reviewed the incident using the guidance in USNRC Regulatory guide 5.62, Reporting of Safeguards Events, and USNRC Generic Letter 91-03, Reporting of Safeguards events. It was determined that although the document contained some low level safeguards information, the document could not have significantly aided an adversary in defeating a security barrier or in carrying out an act of radiological sabotage as the key piece of safeguards information, an encryption table, was not filled out. Based on that determination JAF is withdrawing the one-hour telephone notification (EN-39777). The event remains a loggable event per 10 CFR 95.57(b). It was entered into the Security Log at the time of notification. The event has also been entered into the licensee's corrective action program for apparent cause determination. The NRC Resident inspector was notified and the state will be notified. Notified the Reg 1 RDO(Gray) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-04-21
39776 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-04-20 12:35 | 2003-04-20 17:21 | 2003-04-20 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM (SPDS) FOR GREATER THAN 1 HOUR "At 1235 hours EDT on 04/20/03, the Safety Parameter Display System (SPDS) portion of the Emergency Response Facility Computer System (ERFCS) was noted to be inoperable due to all outputs being displayed in 'magenta' color. At the time of the failure, the ERFCS computer was being re-initiated by Instrumentation & Controls personnel and failed to restart following the re-initiation sequence. "As of 1335 hours EDT on 4/20/03, SPDS has been out of service for greater then 1 hour. which is considered a major loss of emergency assessment capability. "Troubleshooting of the ERFCS by Instrumentation & Controls personnel identified a software problem. At 1600 hours EDT on 04/20/03, Instrumentation & Controls personnel were able to restore the 'A' train ERFCS and at 1630 hours EDT on 04/20/03 the ERFCS and SPDS were declared operable [efforts to restore the 'B' train are ongoing]. "This report is being made in accordance with I0CFR50.72(b)(3)(xiii)." The Licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-20
39775 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-04-20 15:13 | 2003-04-20 16:28 | 2003-04-20 | LEAK DISCOVERED ON HIGH PRESSURE CORE INJECTION PIPING DURING SURVEILLANCE TESTING "During the performance of STP [Surveillance Test Procedure] 3.5.1-09, HPCI [High Pressure Core Injection] System Post-Startup Operability Test, on 4/20/03, a small leak was detected on a ¾ inch pipe nipple on the seal water line on the main HPCI pump. Engineers determined that the leak is from a small crack at a threaded connection. This piping is ASME class 2 piping. This leak constitutes a loss of structural integrity of a Class 2 component as required by section 3.7.3 of the Technical Requirements Manual [TRM]. "At 1337 CDT, on 4/20/03, entered T[TRM] LCO [Limiting Condition of Operation] T3.7.3 condition A, Structural Integrity of Class 1 or Class 2 components not maintained in MODES 1, 2 and 3. "At 1513 CDT on 4/20/03, the HPCI system was isolated and declared Inoperable. Entered [Technical Specification] LCO 3.5.1 Condition F, HPCI System Inoperable, 14 days to restore HPCI. This unplanned HPCI System inoperability is reportable under 10CFR50.72(b)(3)(v)(d) as a single train failure that could have prevented the fulfillment of a safety function of structures or systems designed to mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. | 18 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-04-20
39774 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2003-04-20 | 2003-04-20 05:40 | 2003-04-20 | PALO VERDE SPURIOUS ACTUATION OF OFFSITE EMERGENCY NOTIFICATION SIREN "At 0000 MST on April 20, 2003, the Palo Verde Unit 1 Control Room was notified of a spurious actuation of an emergency warning siren in the vicinity of 348th avenue and Buckeye Road. While not confirmed at this time, the siren is believed to be siren #17 which is approximately five miles to the Northeast of Palo Verde. At approximately 0035 MST, the Unit 1 Control Room was informed [that] the siren was no longer actuating. This siren provides emergency notification to approximately 89 members of the public. "No press release is planned at this time, however, the event is being reported due to the inquiry of a citizen to the Energy Control Center (ECC) and a subsequent notification to the Maricopa County Sheriff's Office. "There is no event in progress and no risk to the health and safety of the public. Members of the public within audible range of the siren may have a concern for their radiological health and safety. "Unit 1 is at approximately 98% power in Mode 1 at normal operating temperature and pressure. "Unit 2 is at approximately 98% power in Mode 1 at normal operating temperature and pressure. "Unit 3 is at 0% [power] in a refueling outage. "The NRC Sr. Resident Inspector has been informed of the siren actuation and [of] this ENS notification. "Note: The checkbox below for 'OTHER GOV AGENCIES' is referring to the Maricopa County Sheriff's Office." | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-20
39773 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-04-19 20:08 | 2003-04-19 23:23 | 2003-04-19 | MANUAL REACTOR TRIP WITH A SUBSEQUENT AUXILIARY FEEDWATER ACTUATION The following information was received from the licensee via facsimile: "A 4 hr. report due to a manual reactor trip (RPS actuation) due to an oil leak on the main turbine. "An 8 hr. report due to Aux[iliary] Feedwater System initiation due to the reactor trip (expected response)." The manual reactor trip was due to a lube oil leak through the diaphragm on the EHC (Electro-Hydraulic Control) interface valve. The leak caused the interface valve to close therefore isolating EHC hydraulic fluid to the turbine control system. During the trip, all rods inserted into the core. As a result of the transient, a pressurizer power-operated relief valve lifted and indications show that it subsequently re-seated. There are no indications that the blow-out plug on the pressurizer relief tank was damaged. Pressurizer relief tank pressure has been reduced to normal. Additionally, a secondary tube side relief lifted and was re-seated after the second running feedwater pump was secured. Decay heat is being removed via the steam dump to condenser system operating in automatic. The electrical grid is stable and supplying plant loads. There was no affect on the other operating unit. As expected, the Auxiliary Feedwater System initiated. The system has been returned to normal, standby configuration and steam generator level is being controlled by the main feedwater system operating in manual control. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-04-19
39772 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2003-04-19 15:30 | 2003-04-19 19:33 | 2003-04-19 | REACTOR PROTECTION SYSTEM ACTUATION The following information was received from the licensee via facsimile: "While performing STP [Surveillance Test Procedure] M-200-2, the RPS [Reactor Protection System] S/G [Steam Generator] Low Press[ure] Trip Units were bypassed using the S/G Low Press[ure] Bypass key. The bypass was automatically removed early before the S/G Low Press[ure] trips were clear[ed]. This resulted in the RPS calling for the TCBs [Trip Circuit Breakers] to open. The CEAs [control rods] were already in the core. This is an 8 hr. report[able] per [10 CFR] 50.72(b)(3)(iv)(A). S/G Press[ures] were [approximately] 700 psi." The surveillance test procedure was to allow time response testing on the trip circuit breakers by the Electrical department (which requires the TCBs to be closed). The plant was also performing a plant heatup in preparation for plant startup. During normal operations, the S/G Low Pressure Trip setpoint is 700 psi. The surveillance test procedure allowed the S/G Low Pressure Trip to be bypassed via the bypass key. If the S/G Low Pressure Trip is keyed to bypass and the S/G pressure increases to greater than 785 psi, then the 700 psi trip setpoint is automatically re-instated regardless of bypass key position. The licensee is investigating the reason that the S/G Low Pressure Trip was automatically re-instated with S/G pressure at approximately 700 psi. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-04-19
39771 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-04-18 23:15 | 2003-04-19 00:45 | 2003-04-19 | OFFSITE NOTIFICATION TO OHIO EPA OF OPACITY EXCEEDANCE "On 4/18/03 at 2315 hours, the high pressure blower overload tripped on X-600 [Steam Plant] #3 boiler. This equipment failure caused two opacity readings (six minute average) to be above 20%. This requires a verbal notification to the Ohio Environmental Protection Agency (OEPA). "At 2350 hours, the Plant Shift Superintendent notified OEPA of the X-600 Steam Plant opacity exceedance. UE-RA-RE1030, App. D, section P, requires a 4 hour NRC event [notification] when other government agencies are notified." The high pressure blower overload breaker was reset and the #3 boiler is currently operational. The Licensee is investigating the cause of the blower overload trip. The Licensee informed both the NRC Resident Inspector and the DOE Site Representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-04-19
39770 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-18 14:08 | 2003-04-18 16:59 | 2003-04-18 | NON- WORK RELATED FATALITY TO CONTRACT EMPLOYEE PROMPTS OFFSITE NOTIFICATION The following information was received from the licensee via facsimile: "At approximately 1408 EDT on April 18, 2003, a non-work related medical emergency occurred at the Sequoyah Nuclear Plant (SNP). Specifically, a contract laborer went into cardiac arrest. The individual was attended to by SNP Emergency Medical Technicians (EMTs). The individual was transported off-site in a TVA ambulance and was subsequently transferred to a Hamilton County ambulance. The individual was pronounced dead on arrival at the hospital. The fatality was not related to the health and safety of the public or on-site personnel. "The individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved. "A notification was made to the Occupational Safety and Health Administration at 1555 EDT this date. This ENS notification is in response to a notification to a other government agency in accordance with 10 CFR 50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-18
39769 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-04-18 | 2003-04-18 09:31 | 2003-04-18 | THEFT AND RECOVERY OF MOISTURE DENSITY GAUGE The following information was received via facsimile from the Ohio Department of Health: The licensee reported the theft and recovery of a Humboldt Scientific moisture/density gauge (model 5001, serial #750) containing a 44 millicurie Am-Be source and a 11 millicurie Cs-137 source. The gauge was stolen during the early hours of April 18, 2003 from the back of a truck parked at an employee's residence in Brooklyn Heights, Ohio. The truck and gauge case was broken into. The licensee notified police and the Ohio Department of Health. At 8:45 AM on April 18, the employee discovered the gauge on the side of the road a short distance from his residence where the theft occurred. The gauge did not appear to be damaged. Notified R3DO (T. Kozak), NMSS (F. Brown), NSIR IAT (M. Kormann) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-04-23
39768 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-04-17 14:35 | 2003-04-17 17:34 | 2003-04-22 | LOSS OF 9 OUT OF 16 EMERGENCY SIRENS IN ORANGE COUNTY The following information was obtained from the Licensee via facsimile: "On April 17, 2003, at 1435 hours, it was determined that 9 out of 16 emergency sirens in Orange County were out of service due to a transmission line failure. Unit 2 was at 100% power and Unit 3 was shutdown. This results in a degraded emergency siren notification system in one of the four counties covered by the emergency plan which is reportable under 10 CFR 50.72(b)(3)(xiii). The emergency plan had route alerting and public radio announcements available as necessary to notify the public in-lieu of the non-operational sirens. Restoration of the sirens occurred at 1709 hours. The county was notified." The transmission line failure caused a loss of two substations which powered the affected sirens. The NRC Resident Inspector will be notified by the Licensee. ***UPDATE ON 04/22/03 AT 1626 HOURS BY G. KELLER TAKEN BY MACKINNON*** At 1230 hours on April 22, 2003, during the review of the computer records for the loss of sirens previously reported on Thursday, April 17, 2003, it was determined that, at 1636 hours, two additional sirens in Putnam county could not be sounded. The loss of signal was not immediately evident and was due to the loss of power to repeater R-257 in Rockland county. This resulted in Putnam county having less than 90% of the sirens available. At the time of the event this resulted in a degraded emergency siren notification system of an additional county covered by the emergency plan which is also reportable under 10 CFR 50.72(b)(3)(xiii). The emergency plan had route alerting and public radio announcements available as necessary to notify the public in lieu of the non-operational sirens. Restoration of the sirens occurred at 1659 hours. The State of New York and the county were notified. NRC R1DO (H. Gray) notified. The NRC Resident Inspector was notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-17
39767 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-04-17 | 2003-04-17 18:37 | 2003-04-17 | FITNESS FOR DUTY A contract supervisor refused to provide a fitness-for-duty specimen after being randomly chosen for testing. The employee's access has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2003-04-17
39766 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-04-17 12:10 | 2003-04-17 13:21 | 2003-04-17 | SAFEGUARDS INFORMATION NOT PROPERLY CONTROLLED Immediate compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for further details. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-04-17
39765 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2003-04-16 13:59 | 2003-04-16 15:46 | 2003-04-16 | ALERT DECLARED "At 1359 CDT, Quad Cities declared and ALERT condition on Unit 2. This ALERT was declared due to a stuck open [power operated] relief valve (3B PORV). A manual scram was initiated [at 1337 CDT]. Priorities include actions to close the 3B relief valve and to maximize Torus cooling. Note that the ALERT was declared due to condition FA1 (relief valve stuck open and Torus temperature." The reactor was scrammed due to a 95 deg F Torus temperature. All rods fully inserted on the scram. The Torus temperature peaked at 118 degrees F, and then started to decrease due to Torus cooling. The tech spec limit on Torus temperature is 110 deg F. Cooldown rate exceeded 100 deg F per hour, and all MSIVs were closed to limit the cooldown rate. The NRC Region III Incident response center was fully staffed at 1415 CDT. The NRC entered Monitoring mode at 1435 CDT, with Region III in the lead. * * * SUMMARY AT 1600 CDT ON 4/16/03 FROM DAVID WASNIACK (EXELON) TO NRC STAFF * * * Torus temperature now <110 deg F. Expect to be in Mode IV by 1900 CDT. In order to de-inert the Torus, must have Torus temperature <95 deg F, and have shutdown cooling supplied to the core. Anticipate 15-16 hours before the drywell can be accessed to attempt to manually shut the valve. The licensee has attempted to close the PORV from the control room via several means (switch and pulling control power fuses) and been unsuccessful. * * * SUMMARY AT 1715 CDT ON 4/16/03 FROM DAVID WASNIACK TO NRC STAFF * * * The licensee is continuing plant and Torus cooldown, and anticipates terminating the ALERT when the plant is in Mode 4, at approximately 1900 CDT. Suspected cause of the PORV lifting is a failed pilot. * * * SUMMARY AT 2130 CDT ON 4/16/03 FROM DAVID WASNIACK TO NRC STAFF * * * Shutdown cooling was established at 2104 CDT. Current temperature 275 deg F, cooldown rate is 80 degrees per hour. At 2237 CDT, the licensee declared that Unit 2 was in Mode 4. * * * SUMMARY AT 2245 CDT ON 4/16/03 FROM DAVID WASNIACK TO NRC STAFF * * * The NRC exited Monitoring mode at 2255 CDT. * * * SUMMARY AT 2340 CDT ON 4/16/03 FROM RALPH BASSETT TO NRC STAFF * * * The licensee terminated the alert at 2251 CDT. The plant is in Cold Shutdown Mode 4 with the RCS depressurized and less than 212 deg F. Notified DHS (Stucky), FEMA (Saunder), DOE (Rick) , USDA (L. Thomas), HHS (M. Miller), EPA (Flach), NRR EO (S. Black), HQ PAO (W. Beecher), R3 (S. Reynolds). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-04-16
39764 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-04-16 11:45 | 2003-04-16 14:14 | 2003-04-16 | FITNESS FOR DUTY "Event: At 11:45 on April 16, 2003, the Oconee Medical Review Officer notified the affected individual of a confirmed positive test result following a random Fitness For Duty (FFD) screening test. The confirmed positive was for alcohol. The individual being tested is a Supervisor in the Radiation Protection Section. "Initial Safety Significance: None: There is no reason to believe there has been any adverse consequences from this event. The employee had been in meetings all morning until he reported for the random screening test. This event is not considered to have impacted operation of the plant in any way. "Corrective Action(s): The immediate action was to place the individual's security badge on FFD hold, which will deny access to the protected area. Also, the individual was referred for immediate assessment by the Employee Assistance Program counselor, who will determine the extent of additional actions." The licensee notified the NRC Resident Inspector. | 100 | 100 | 82 | 100 | 100 | 82 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.73 |  |  |  | 0 | 2003-04-16
39763 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2003-04-15 | 2003-04-16 10:07 | 2003-04-16 | MASSACHUSETTS AGREEMENT STATE REPORT ON SHIPPING PACKAGE RADIOLOGICAL ISSUE "On April 15, 2003, a Yellow-III Package containing 30 millicuries (1.1 Gbq) of Co-60 measured 400 millirem/hr on the surface. The Shipper was AEA Technology QSA GMBH, Giesilweg 1, D-38110 Braunschweig, Germany. The carriers included Federal Express Freight and Ground Control. Immediate reporting requirements means investigation is not complete at the time of report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2003-04-21
39762 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-04-15 09:45 | 2003-04-16 06:32 | 2003-04-16 | BULLETIN 91-01 24 HOUR REPORT FOR CRITICALITY CONTROL "At 0945 on 4/15/03, the Plant Shift Superintendent (PSS) was notified that SX/WA (Seal Exhaust/Wet Air) pump components were discovered outside the C-337 SX/WA FCA (Fissile Control Area) not properly tagged and spaced, as required by NCSA CAS-007. Tagging of items removed from the SX/WA FCA ensure proper identification of potential fissile components requiring spacing controls. Components include used oil solenoid valve, 3 inch elbow, oil mist filter crushing tool, 3 gas ballast pipes and valves, oil level sight glass, oil or water flow sight glass and copper tubing. The NRC Resident Inspector has been notified of this event." SAFETY SIGNIFICANCE OF EVENTS: While an approved analysis does exist for subcriticality of this upset condition, a control relied upon for double contingency was violated. POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for a criticality to be possible, a second independent and unlikely event would need to occur concurrently with the loss of spacing accident. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): Double contingency is maintained by implementing controls on interaction and an independent failure. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: Less than the safe mass of uranium at plant maximum assay of 5.5 wt. % U235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on interaction. Components removed from a SX/WA FCA shall be spaced a minimum 2 feet, edge-to-edge from other potentially fissile material or components, the SX/WA components were spaced less than the required 2 foot spacing. Therefore, the control on interaction was violated and the parameter was lost. The second leg of double contingency is based on the subcriticality of the loss of spacing. The improperly spaced components are of small size and limited uranium loading which are in a configuration that is bounded by calculations performed for the SX/WA station. Therefore, this leg of double contingency is maintained. Since the interaction parameter was lost; therefore, the double contingency principle was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: See remediation guide. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-04-16
39760 | 0 | LACROSSE | 1 |  |  | [1] AC (ALLIS CHAMBERS) | 2003-04-15 11:58 | 2003-04-15 13:30 | 2003-04-15 | UNUSUAL EVENT At approximately 1158 CDT, the CO2 system discharged in the 1B Emergency Diesel Generator (EDG) building. The licensee declared a UE at 1215 CDT because they had to call an offsite fire department for assistance in re-entering the building. The fire department arrived on site at 1233 CDT and promptly entered the 1B EDG building. The cause of the CO2 discharge was high temperature in the building (140 degrees F) caused by a malfunctioning space heater. The licensee exited the UE at 1252 CDT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-04-15
39759 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-02-25 21:39 | 2003-04-15 13:03 | 2003-04-15 | INVALID SPECIFIED SYSTEM ACTUATION "60-Day Optional 10 CFR 50.73(a)(1) Report - Invalid Actuation of Primary Containment Isolation System (PCIS) and Secondary Containment Isolation Dampers (SCIDs). "In accordance with 10 CFR 50.73(a)(2)(iv)(A), the following is a report of an invalid actuation of the PCIS and SCIDs for Units 1 and 2. This notification is provided in lieu of submitting a written LER. "On February 25, 2003, at approximately 2139 hours, failure of the main stack radiation monitor resulted in a PCIS Group 6 isolation and SCIDs. PCIS Group 6 valves include isolation valves from the Containment Atmosphere Control, Containment Atmosphere Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems. Due to the shared configuration of the main stack radiation monitoring system, these isolations occurred on both Unit 1 and Unit 2. In addition the Standby Gas Treatment system initiated on both Units, as expected for the given plant conditions. The actuations of PCIS Group 6 valves and SCIDs were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open at the time of the event closed). The main stack radiation monitor was subsequently returned to service and the other affected systems returned to their normal operating lineup. No deficiencies or abnormalities were noted during this event. The NRC Resident Inspector was notified of this 60-Day report. Discussion of the cause and corrective actions associated with this event are documented in the site corrective action program (i.e., AR 85815)." | 94 | 98 | 0 | 94 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-04-15
39758 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-04-15 02:30 | 2003-04-15 09:18 | 2003-04-15 | UNPLANNED LOSS OF SPDS/ERDS FOR GREATER THAN 8 HOURS AT SUSQUEHANNA "On 4/15/03 the Main Control Room received alarms indicating failure of the power supplies to the Safety Parameter Display System (SPDS). At the time the 2 uninterruptible power supplies were crosstied due to maintenance. Investigation into the cause of the failure is ongoing with repairs expected to take longer than 8 hours. "Currently, Unit 2 is in a refueling outage in Cold Shutdown. Control room indication and the plant computer system is still available with the exception of those points supplied by the SPDS power supply. "Due to the failure of the SPDS UPS, 12 of approximately 300 inputs to the ERDS system will be displayed as invalid data until the SPDS power is restored. "Since the Unit 2 SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and therefore reportable under 10CFR50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-15
39756 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2003-04-10 17:30 | 2003-04-14 13:05 | 2003-04-15 | LOST MOISTURE DENSITY GAUGE A Campbell Pacific Nuclear Model MC-DR1P s/n MD20200680 moisture/density gauge was lost out of a transport vehicle on 4/10/03. The gauge contains 10 millicuries of Cs-137 and 50 millicuries of Am-241:Be. The gauge was not properly secured in the transport vehicle prior to transportation. Licensee's corrective actions included a meeting with all gauge users on 4/14/03, and issuing an orange cone to be put in the back of each transport vehicle to remind users to secure gauges before transport. Local law enforcement was notified of this event. The licensee may issue a violation letter for failure to follow procedures. Notified R4 DO (C. Johnson) and NMSS EO (F. Brown) *****UPDATE ON 4/15/03 AT 10:40 FROM MARSHALL TO LAURA***** The licensee called at 6:15 pm PDT to advise the gauge had been found on April 14 in the middle of the street in vicinity of where it had been lost. It had taken the finder some time to track down the owner of the gauge. The gauge case was missing but the gauge was reported to be undamaged. Notified the R4DO (Johnson) and NMSS (ESSIG). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2003-04-17
39755 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-04-11 14:00 | 2003-04-14 11:34 | 2003-04-14 | TEXAS AGREEMENT STATE REPORT FOR FIRE DAMAGED THREE SOURCE HOLDERS "Fire detectors activated in the multi-Product Unit 1 on Friday afternoon, insulation and sheeting on the unit were damaged by the fire. Three Ohmart SH-F1 source holders were installed on the unit. Each source holder contains a Cesium-137 source with an estimated activity of 120 millicuries each. The on-site fire department was notified and extinguished the fire. It was suspect that the gauges had been engulfed in the fire. However, after notification to Techstar, an on-site visit for inspection and verification determined that none of the gauges were burned in the fire but had been affected by the heat of the fire. It has been explained that the detectors were damaged. The Techstar firm confirms that all labels are intact and legible. A leak test was performed on each unit for gross contamination and a radiation survey and occupancy evaluation was performed. No contamination was detected. The ion chamber detectors will have to be replaced, as the greater part of the fire was on the detector side of the vessels. Techstar placed the three units shutters in the closed position until repairs to the facility can be made. Estimated time to repair the facility is approximately 10 working days. After repair the ion detectors will be replaced and the gauges will be tested by Techstar." Notified NMSS EO (F. Brown) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-04-17
39754 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-04-13 16:56 | 2003-04-13 19:06 | 2003-05-21 | REACTOR VESSEL BOTTOM HEAD DEGRADED CONDITION "On 4/12/2003, during the Unit 1 11th (1RE11) refueling outage, an inspection was performed of the vessel bottom head. This bare metal inspection identified a potential leak indication at the head to penetration interface for Bottom Mounted Instrumentation (BMI) penetrations 1 and 46. There was a small amount of residue around the outer circumference of the BMI penetrations. No wastage was observed. Samples of the residue were taken and the area was cleaned with demineralized water. Chemical sample results available as of 1300 on 4/13/2003 are not conclusive; however, they have confirmed that the residue found at the Penetration 46 contains boron, indicating that this could be an RCS leak. The residue removed from Penetration 1 was characterized as 'gummy' and its composition is still under investigation. Additional exams are planned to confirm the likely origin of the residue and to determine the scope of any repairs. There has been no indication of RCS leakage observed at the BMI penetrations during previous operational cycles. This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A)." Unit 1 will remain in mode 5 until appropriate corrective actions are identified. The licensee informed the NRC resident inspector. * * * * UPDATE 1151 EDT 04/18/03 FROM WAYNE HARRISON TO MIKE RIPLEY * * * "STP Nuclear Operating Co. will be making a press release [at 12:00 pm 04/18/03] concerning the indications found on the Bottom Mounted Instrumentation penetrations on Unit 1. The release is being coordinated with NRC Region IV. "STP has notified or will be notifying various federal, state and local agencies, including FEMA, the governors office, Matagorda County, Bay City. City of Palacios, state representatives and state senators, US representatives and US Senators." The licensee notified the NRC Resident Inspector. Notified R4DO (C. Johnson), HQ PAO (W. Beecher) *** UPDATE AT 1745 EDT ON 05/21/03 FROM WAYNE HARRISON TO ARLON COSTA *** "STP Nuclear Operating Co. expects to make a press release on 5/22/2003 concerning the indications found on the Bottom Mounted Instrumentation penetrations on Unit 1. NRC Region IV has been advised of the planned press release. STPNOC will also be sharing the press release with various local and state government agencies. "The draft release is attached. "NRC was notified of the leakage per 10CFR50.72 on 4/13/2003 (EN# 39754). "NRC was notified of a press release describing the leakage on 4/18/2003 (EN#39754 update)." The licensee notified the NRC Resident Inspector. Notified HQ PAO (W. Beecher) and R4DO(T. Pruett). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-04-13
39753 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-12 22:21 | 2003-04-12 23:50 | 2003-04-13 | TURBINE TRIP CAUSES REACTOR TRIP AT SEQOUYAH UNIT 2 "While resetting a turbine trip supervisory module, the unit 2 turbine tripped from "Turbine High Vibration Turbine Trip" at 22:21. The reactor tripped as a result of the turbine trip. Investigation is pending concerning the turbine vibration equipment. "Auxiliary feed water system initiated as designed. All secondary plant equipment performed as expected. "The plant is being maintained in Mode 3 at NOT/NOP, 547 degrees F and 2235 psig, with auxiliary feed water supplying the Steam Generators and steam dumps removing the decay heat." All control rods inserted into the core with no problems. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-04-13
39752 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2003-04-12 18:47 | 2003-04-12 20:55 | 2003-04-12 | AUTOMATIC REACTOR SCRAM- ALL RODS FULLY INSERTED At 1847 hours on 04/12/03 the Peach Bottom Atomic Power Station Unit 2 experienced an automatic reactor scram and shutdown following an air line failure which resulted in the closure of the "D" outboard main steam line isolation valve. The closure of this valve resulted in a Reactor High Pressure Automatic Scram Signal. This caused a actuation of the Alternate Rod Insertion system on reactor high pressure of 1106 psi. All rods fully inserted. Additionally reactor vessel water level lowered to approximately negative 10 inches which resulted in a RPS and PCIS Group 2 & 3 isolations. All systems activated as required. The outage control center is currently staffed and repair/planning and restart preparation activities are in progress. Peach Bottom Atomic Power Station Unit 2 plant conditions are currently stable. A copper air line going to the solenoid valve which operated the "D" outboard main steam isolation valve failed. Cause of the line failure is unknown at this time. The offsite electrical grid is stable and all emergency core cooling systems are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-04-12
39751 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-04-11 18:30 | 2003-04-12 17:02 | 2003-04-12 | LOSS OF DOUBLE CONTINGENCY PROTECTION NRC BULLETIN 91-01 24 HOUR NOTIFICATION Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt. % U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107. Time and Date of Event: 18:30 hours, April 11, 2003. Reason for Notification: On March 19, 2003, six UF6 cylinders were placed on hold because Westinghouse questioned if the cylinders were properly tested following repair. The ANSI N14.1 nameplate had been removed from supporting "feet" and-welded directly onto the pressure vessel dome. The "U" Stamp had been replaced with an "R" Stamp and documentation from the shipper indicated that the fillet weld on the dome had undergone dye-penetrant testing. The UF6 cylinder pressure vessel, however, had not undergone hydrostatic testing. The "hold" consisted of a flag in the UF6 cylinder tracking computer database, which was inserted as a manual edit. The hold flag should have prevented the cylinders from being transferred into work in process (WIP) to allow processing. On March 31, 2003 one of the six cylinders was allowed by the tracking database to be processed. A second cylinder with the hold flag was allowed to be processed on April 1, 2003. Unaware of the failure of the hold flags, the safety analysis proceeded. On April 10, 2003 NCS and process engineering completed the safety review begun on March 19, 2003 of the nameplate welding using applicable pressure vessel standards including an on-site interview with a certified boiler code inspector. The conclusion of the safety review was that the "R" Stamp cylinders met the ANSI N 14.1 requirements and were acceptable for processing. On April 11, 2003, NCS began a review of the sequence of events leading to the processing of the two hold tagged cylinders. At approximately 18:30 hours April 11, 2003 NCS completed its final interview. Shortly thereafter, it was determined that there had been a loss of previously documented double contingency protection. NCS immediately informed the EH&S manager of the event. Double Contingency Protection: The parameters that directly affect neutron multiplication for the vaporizers are mass (density) and geometry (level control). A criticality could be possible in a vaporizer under the following conditions: Sufficient material is discharged from the cylinder into the vaporizer in order to form a critical UO2F2 H2O density (optimum moderation), and water slab height increases to a critical height. Cylinder integrity maintains mass control. The U235 mass control depends upon maintaining the structural integrity of the cylinder to ensure that no material is released due to a sudden uncontrollable rupture. The geometry control consists of ensuring that condensate drains properly from the vaporizer, and detecting water accumulation should it occur. It has been determined that less than previously documented double contingency protection remained for the system and that greater than a safe mass was involved. Double Contingency protection was restored within 4 hours. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criterion for a 24-hour notification. As Found Condition: See "Reason for Notification." As detailed above, the Investigation found that the cylinders were safe to process. In fact, there never was an actual safety issue. The event did point out a weakness in our control of UF6 cylinders that will be addressed. Summary of Activity: 1) The four remaining cylinders were physically tagged out. 2) A complete inventory and inspection of all cylinders on-site was performed. 3) It was verified that no movement of UF6 cylinders onto the site or into processing will occur for the next week. Conclusions: 1) Loss of double contingency protection occurred. Greater than a safe mass was involved. 2) At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. 3)The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. 4) Notification was the result of an event, not a deficient NCS analysis. 5) A causal analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-04-12
39750 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2003-04-11 17:00 | 2003-04-11 17:17 | 2003-04-11 | UNANALYZED CONDITION COULD CAUSE HIGH PRESSURE INJECTION PUMP DAMAGE "As a result of an in-depth design and performance capability review, a non-conforming condition was identified whereby, utilizing only safety grade equipment, long term cyclic repressurizations of the reactor coolant system (RCS) may occur following a subset of postulated very small Loss of Coolant Accidents (LOCAs) with effective break sizes in a range between 0.0021 ft2 to 0.0045 ft2. The repressurization cycles were not previously analyzed, but are predicted by a new application of the license basis 10 CFR 50.46 Evaluation Model. Although non-safety grade equipment would be available to prevent repressurizatons, if only safety grade LOCA mitigating equipment is credited, these repressurizazion cycles could be postulated to damage both High Pressure Injection (HPI) pumps. This could occur due to pump deadheading after HPI recirculation flow back to the borated water storage tank is procedurally isolated upon tank low level and pump suction has been manually transferred to the containment emergency sump at minimum of approximately 20 hours into the postulated event. Minimum recirculation flow back to the borated water storage tank initially provided protection against deadheading the pump and previously assumed reactor coolant system pressures would have allowed continued HPI pump flow. During part of the newly predicted repressurization cycle, RCS pressure would exceed the shutoff head of the HPI pumps. Without minimum flow, the pumps would be damaged. "This issue is currently evaluated by Condition Report 02-06702. Davis-Besse has determined this condition is reportable under § 50.72(b)(3)(ii)(B) 'Any event or condition that results in ..'The nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' Although the plant is currently in cold shutdown and the HPI pumps are not required to be operable per the Technical Specifications, this issue represents a historical condition that existed within the last three years." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-04-11
39749 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2003-04-11 01:45 | 2003-04-11 06:23 | 2003-04-11 | MANUAL REACTOR TRIP DUE TO VIBRATIONS ON THE MAIN TURBINE "A manual scram was initiated at 0145 on April 11, 2003, due to vibrations on the Main Turbine trending up to the trip setpoint. A scheduled plant shutdown was in progress for a maintenance outage [of the 'B' recirculation flow control valve sensor]. All plant systems operated normally on the scram. The plant is shutdown at 0% power in Mode 3. The turbine vibrations returned to normal values after the turbine tripped." All rods inserted normally. All safety and electrical systems operated as designed during and after the reactor trip. The plant is stable and using normal feedwater. There was nothing unusual or not understood. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-04-11
39748 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-04-10 10:32 | 2003-04-10 15:49 | 2003-04-10 | A NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL DURING A RANDOM TEST. ACCESS HAS BEEN PULLED. HIS WORK WAS REVIEWED AND NO IMPACT FOR SAFETY RELATED WORK WAS FOUND. NO FURTHER DETAILS. NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS EVENT BY THE LICENSEE. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2003-04-10
39747 | 0 | OJOS HOSPITAL |  |  |  |  | 2003-04-09 | 2003-04-10 14:22 | 2003-04-10 | MEDICAL EVENT INVOLVING SR-90 EYE APPLICATOR EXCEEDING THE PRESCRIBED DOSE BY 32% The Ojos Hospital located in San Juan, PR sent a New England Nuclear Model NB-1, S/N 0433, to the University of WI for calibration in October of 2002. The unit was returned with the calibration source, however, technicians at the hospital failed incorporate the results into the respective documents at the hospital. This resulted in approximately 36 patients receiving a dose 32% higher than the prescribed dose. Typical doses administered during treatment are 1000, 1500 or 2000 rads. In the case of a 2000 rad prescribed dose, the actual dose delivered is 2646 rads. The consultant who performs semi-annual leak tests discovered the discrepancy and notified hospital management who ceased at treatment with this device on 4/9/03. The affected patents have not been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | DOSE > SPECIFIED EFF LIMITS | [8 empty] | NON EMERGENCY | 2 | PR | HOS |  | 35.3045(a)(1) | 35.3045(a)(2) |  |  | 0 | 2003-04-10
39746 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-04-10 07:30 | 2003-04-10 12:54 | 2003-04-10 | 10 OF 16 SIRENS OUT OF SERVICE On April 10, 2003 at 0730 hrs 10 of 16 sirens in Orange county were reported out of service because of a loss of power to the Harriman repeater site. The repeater site power was restored and the sirens were returned to service at 1025 hrs. Route alerting was available during the loss of the sirens. The NRC Resident Inspector, County and State were notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-10
39745 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2003-04-09 19:43 | 2003-04-09 23:42 | 2003-05-02 | UNATTENDED SECURITY HANDGUN FOUND IN THE PROTECTED AREA Immediate compensatory measures taken upon discovery. The Licensee has notified the NRC Resident Inspector. *** RETRACTION FROM D. MARKS TO A. COSTA AT 1858 ON 5/2/03 *** Upon further review of 10 CFR 73, Appendix G, Paragraph 1(a)(3), the Licensee is retracting this event notification. Contact the NRC Headquarters Operations Officer for additional details. The Licensee notified the NRC resident inspector. Notified the R4DO (Pick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-04-09
39744 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-09 12:00 | 2003-04-09 13:14 | 2003-04-09 | OFFSITE NOTIFICATION DUE TO LETHAL SHORT- NOSE STURGEON TAKE The following information was received from the Licensee via facsimile: "A sturgeon was recovered from the Circulating Water intake during normal trash raking. Environmental Licensing was notified to determine the species of sturgeon. It was determined to be a shortnose sturgeon (Endangered). Initially the sturgeon was alive and injured. Following recovery, the sturgeon died. The National Fisheries and the New Jersey D.E.P. [Department of Environmental Protection] was notified." Additionally, the Licensee notified Lower Alloway Township. The Licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-09
39743 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-08 14:53 | 2003-04-08 19:36 | 2003-04-08 | AUXILIARY FEEDWATER ACTUATION DUE TO LOW STEAM GENERATOR WATER LEVEL The following information was received from the Licensee via facsimile: "On April 8, 2003 with Unit 2 in Mode 5 (Cold Shutdown), the auxiliary feedwater (AFW) system automatically actuated on a valid signal when the solid state protection system (SSPS) was placed in service while the steam generator level was below the AFW actuation set point. The actuation was unplanned. "S/G [Steam Generator] 2-1 level had been lowered to below the feed ring for work on an AFW system check valve. Operations was performing testing on the AFW system using AFW Pump 2-2, and was going to restore S/G level to normal (approximately 33% narrow range level) during the test. In conjunction with the AFW system testing, SSPS was being placed in service in preparation for an expected Mode 4 transition later in the watch after the AFW system testing was complete. When SSPS was placed in service, the low level in S/G 2-1 made up the coincidence for starting the motor driven AFW pumps. AFW Pump 2-2 was in operation, but AFW Pump 2-3 started in response to the low S/G level. AFW Pump 2-3 was aligned for recirculation flow, and did not feed forward on the automatic start. Operations then restored S/G 2-1 level above the low level trip point and secured AFW Pump 2-3. "The start of AFW Pump 2-3 on a valid low level signal from S/G 2-1 is reportable as an 8 [hr.] non-emergency report." In addition to the AFW actuation, the Licensees did receive a S/G blowdown isolation signal but S/G blowdown was not in service at the time. The Licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-04-08
39742 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-04-07 14:10 | 2003-04-08 15:10 | 2003-04-08 | INFORMATION CALL "Unfounded Suspicious Call concerning demonstrations at the Callaway Nuclear Plant. "On 04/07/03 at approximately 1400 hours, the Assistant Superintendent of Security at the Callaway Plant received a call from Callaway County Sheriff. The sheriff stated that on 04/04/03 at 2036 hours the county dispatcher received an anonymous call stating that a demonstration would take place at the Callaway Plant on Wednesday April 9, 2003. The caller did not offer any additional information even when questioned other than he would get hurt if he stated anything else. "[Neither] Ameren Corporate Security, Callaway Plant Security, Callaway County Sheriff's Department nor [DELETED] with the FBI office in Jefferson City have received or come in contact with any information concerning any type of possible demonstration. "The Callaway Plant EDO, Protective Services Superintendent and Vice President were notified of this call. The Sheriff's Department plans on conducting extra patrols of the area on 04/09/03 as well as an increased awareness by Security." Notified IAT (J. Davidson) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW | [5 empty] | 0 | 2003-04-08
39741 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2003-04-07 22:19 | 2003-04-07 22:36 | 2003-04-09 | UNUSUAL EVENT At 2201, a fire started in the pressurizer doghouse. Welding operations were ongoing in the upper part of the space, and a slag catchment device lower in the space caught fire. The fire brigade responded to the scene. At 2219, the licensee declared an Unusual Event because of an ongoing fire in the vital area for greater than 15 minutes. At 2234, the fire was put out by pouring water down onto the fire from above, and a reflash watch was set. There was no damage noted to plant equipment, and no injuries to personnel. The licensee notified the NRC Resident Inspector and the surrounding counties. * * * UPDATE AT 2309 ON 4/7/03 FROM DAVE SEPANICH TO ERIC THOMAS * * * At 2300, the licensee secured from the Unusual Event. There was no damage noted to plant components, and scaffolding will be erected to conduct further inspections. The licensee notified the NRC Resident Inspector and the surrounding counties. * * * UPDATE AT 0008 ON 4/8/03 FROM MIKE KORSNICK TO ERIC THOMAS * * * The cause of the fire was slag from welding operations that fell through some fire blankets and ignited the herculite underneath. A fire brigade member will be sent back into the space this morning to conduct further damage assessment. * * * UPDATE 1502 EST ON 4/9/03 FROM MARK GECKLE TO S.SANDIN * * * The licensee provided the following information as an update to this report: "During the three-minute time period 2231 to 2234 on 4/7/03, the criterion for upgrade to Alert was met. However, the fire was reported out prior to Alert declaration (i.e., Alert criterion no longer applicable). Note: This update is being made in accordance with administrative requirements." The licensee explained that the Alert declaration would have been required in accordance with NUMARC guidelines NUMARC/NESP-007 Revision 2. However, these guidelines allow 15 minutes to recognize that the Alert criterion was satisfied and it was during this period when the fire was reported out. The licensee informed the NRC resident inspector. Notified R1DO(Trapp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Refueling; FMode2: Refueling | UNUSUAL EVENT | 1 | MD | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-04-07
39740 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2003-04-07 17:00 | 2003-04-07 17:30 | 2003-04-07 | UNANALYZED CONDITION "During the System Health Readiness Review at Davis-Besse Nuclear Power Plant, a potential issue was discovered concerning operability of the HPI Pumps. When the HPI Pumps are taking suction from the emergency sump (i.e., under post LOCA condition after the initial HPI injection has occurred and BWST has been depleted), it could receive particle size that could damage or render the HPI pumps inoperable due to sump debris. A review of pump design and rotor dynamic analysis have determined that [the] pumps are unsuitable to take suction from a source that contains debris in the water, such as the post LOCA debris (i.e., fibrous material from insulation) in the containment emergency sump. "The above issue is documented in Condition Report 03-01738 and is currently being further investigated. Davis-Besse has determined that the above condition will be reportable under 10 CFR 50.73(a)(b)(v), Event or Condition that could have prevented fulfillment of a safety function, and 10 CFR 50.73(a)(2)(ii), Degraded or Unanalyzed Condition. Although this condition was discovered during plant shutdown where HPI pumps are not required to be operable per TS 3.5.2, a subsequent review of immediate notification requirements found this condition may require an 8 hour notification via 10 CFR 50.72(b)(3)(ii), i.e., that is to report a historical condition where [a] degraded/unanalyzed condition existed within 3 years. The Statements of Consideration for this reporting criterion implies such conditions if it existed within 3 years should be reported via 10 CFR 50.72(b)(3)(ii)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-04-07
39739 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2003-04-07 | 2003-04-07 14:49 | 2005-02-08 | AGREEMENT STATE REPORT - TRANSPORTATION INCIDENT INVOLVING TWO TROXLER DENSITY GAUGES The following information was obtained from State of Florida Bureau of Radiation Control via e-mail: On 4/05/03, a truck transporting a load of hazardous chemicals and two Troxler moisture density gauges was involved in an early morning accident. As a result of the accident, the truck caught fire and burned up. It was not known until 4/07/03, when a copy of the bill of lading was obtained, that the truck was carrying radioactive material. The Troxler gauges were being returned to the licensees from Troxler, Inc. after being calibrated. The gauges have not yet been located. Florida is investigating. * * * UPDATE ON 02/08/05 @ 1226 FROM CHARLES ADAMS(fax) TO CHAUNCEY GOULD * * * On 4-5-03 a truck fire destroyed two Troxler gauges (FL03-058, PNO-II-03-005). Only one was found. Today the other has been located. The trucking company which carried the gauges apparently took the remains of the truck to their location in Lakeland Florida after the accident in 03. They just tried to send that metal to a scrap dealer and it set off the radiation alarm. Investigation by a hired consultant found the burned out remnants of the gauge. Swipes show no leakage. The licensee will take possession and arrange with Troxler for disposal. Notified Reg 2 RDO (Widman), NMSS EO (Essig) and Reg 1 RDO (Cobey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2003-04-10
39738 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-04-06 05:30 | 2003-04-06 09:42 | 2003-04-06 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "At 2050 4/05/03 it was identified that the requirements of LCO 3.1.6 Control Bank Insertion Limits was not met for Unit 2. Control rod bank overlap between control bank C and control bank D was at 126 steps instead of the required 125 steps. Entered TSAC 3.1.6.B.1.1 to verify SDM to be within the limits provided in the COLR within 1 hour and entered TSAC 3.1.6.B.2 to restore control bank sequence and overlap to within limits within 2 hours. "TSAC 3.1.6.B.1.1 was met at 2124 when SDM was verified to be within the limits provided in the COLR. "At 2250 TSAC 3.1.6.B.2 required action was declared not met. Entered TSAC 3.1.6.C.1 to be in MODE 2 with Keff < 1.0 within 6 hours. "Unit 2 entered MODE 3 at 0530 4/06/03 in accordance with TSAC 3.1.6.C.1." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2222 EDT ON 4/6/03 FROM F. FLENTJE TO E. THOMAS * * * "A news release on the Unit 2 shutdown was issued by Nuclear Management Company, LLC (NMC) at 1845 hours CDT on April 6, 2003. The NRC Resident Inspector was notified at 2041 hours CDT on April 6, 2003, that the news release had been issued. Event investigation and equipment repairs continue. Current estimated restart date is April 8, 2003." Notified B. Clayton (R3DO) | 0 | 0 | 0 | 0 | 55 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-04-06
39737 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-04-05 07:45 | 2003-04-05 09:45 | 2003-04-10 | LOSS OF METEOROLOGICAL INSTRUMENTATION DUE TO ADVERSE WEATHER "This notification is being made per 10CFR50.72.(b)3(xiii): Eight hour Reports - Any event that results in a major loss of emergency assessment capability, offsite response or offsite communications capability. "The following events have occurred: Due to freezing rain and icing conditions a Loss of on-site (Main Tower and JAF Tower) meteorological instrumentation for wind speed, wind direction and delta T or sigma theta has occurred. This is considered to be a major loss of emergency assessment capability and is reportable under 10CFR50.72. "Back up Meteorological information remains available." The licensee has notified the NRC Resident Inspector and county agencies and will be notifying State agencies. *** UPDATE ON 4/10/03 AT 0809 EST FROM R. MATTESON TO A. COSTA *** Licensee notified that only two sirens are now out of service and that the remaining sirens are operational. Notified the Region 1 Duty Officer (Trapp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-05
39736 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-04-05 02:07 | 2003-04-05 03:58 | 2003-04-05 | NOTIFICATIONS MADE TO OTHER GOVERNMENT AGENCIES "On 4/4/03 at 2113 hrs the Plant Shift Superintendent's office was notified that approximately 25,000 gallons of trichloroethene (TCE) contaminated ground water was discharged onto the ground. During a routine shift turnover an operator observed that the check valve on well B-10 stuck open allowing water to backflow into the well casing and over flow onto the ground. This requires a verbal notification to the Ohio Environmental Protection Agency (OEPA) and to the National Response Center. "At 0207 hours, the Plant Shift Superintendent completed notifications to the Ohio Environmental Protection Agency (OEPA) and to the National Response Center. UE2-RA-RE1030 App. D, section P requires a 4 hour NRC event when other government agencies are notified." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-04-05
39735 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-04-04 18:24 | 2003-04-04 23:41 | 2003-04-05 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "On April 4, 2003, at 1824 PST, with Unit 2 at approximately 54 percent power, operators commenced a shutdown to mode 5 in accordance with technical specification 3.7.5 C. 1, 'Auxiliary Feedwater (AFW) System,' due to two AFW trains determined to be inoperable. "While trouble-shooting leaking AFW check valves, AFW discharge check valve (FW-2-377) to steam generator (SG) 2-1 was determined to be inoperable due to incorrect installation. Based on radiography, the check valve appears to be installed incorrectly such that it may not allow sufficient AFW flow to SG 2-1. This condition renders two trains of AFW inoperable. "The two motor-driven and one turbine-driven AFW pumps and their flow paths to the other three SGs remain operable. The system is designed such that design basis decay heat can be removed by a single AFW pump delivering flow to at least two SGs. "Unit 2 had ended the recent refueling outage on March 25 and had yet to reach full power when this problem was discovered. Check Valve FW-2-377 had been disassembled during this refueling outage." The licensee has notified the NRC Resident Inspector. | 0 | 20 | 0 | 0 | 54 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2003-04-05
39734 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-04-04 15:26 | 2003-04-04 18:26 | 2003-04-04 | OFFSITE NOTIFICATION OF POTENTIAL FUEL OIL SPILL "Operations was notified by site chemistry management that a report of a potential fuel oil spill was being made to the North Carolina Department of Environmental Health and Natural Resources, Regional Division of Water Quality. Diesel fuel oil has been identified seeping onto the floor of the Augmented Off-Gas (AOG) building. A diesel fuel oil transfer line from the off-load station to a fuel oil storage tank runs underground in the vicinity of the AOG building and is suspected as the source of the leak. The quantity of the leakage is not known at this time. A follow-up discussion with the Division of Water Quality personnel is scheduled for Monday, April 7, 2003, when more information will be available. "Initial safety significance of this event is zero because this does not affect operation of the Units." The licensee notified the NRC Resident Inspector. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-04
39733 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-04-04 13:54 | 2003-04-04 16:35 | 2003-04-04 | AUTOMATIC REACTOR SCRAM AT BRUNSWICK DURING START-UP FROM REFUELING OUTAGE "On April 4, 2003, during a Unit 2 reactor start up, primary containment group 1 isolation was received which resulted in a reactor scram. Following the scram, reactor water level lowered to approximately 150 inches. This is below the Reactor Water Low Level One set point of 166 inches. As a result of the low water level, primary containment group 2, 6, & 8 isolation signals were received. All required isolations occurred as a result of the Reactor Water Low Level One isolation signal. All control rods fully inserted on the scram. Reactor Core Isolation Cooling was manually started and Reactor water level was restored to the normal band. Reactor Core Isolation Cooling was shutdown after Reactor water level was restored. "It is believed that the cause of the group 1 isolation signal (Main Steam Isolation Valve closure Scram signal) was an Electro-hydraulic Control (EHC) malfunction that caused the Main Turbine Bypass valves to open. This resulted in the Main Steam Line pressure dropping below the group 1 set point of 850 psig. Investigation is ongoing to determine the exact cause of the EHC malfunction." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-04-04
39732 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-04-04 10:30 | 2003-04-04 12:58 | 2003-04-04 | LOSS OF GREATER THAN 50% OF EMERGENCY SIRENS "At 1030 on April 4, 2003 it was reported to the Control Room that greater than 50% siren population coverage was lost. The percent siren coverage population lost is 55.06%. The lost siren coverage is due to weather related power outages. Crews have been dispatched and are working to restore power to the affected sirens. "This is being reported under 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (loss of greater than 50% of emergency sirens). It is also being reported under 10 CFR 50.72(b)(2)(xi) as any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. The NRC Resident Inspector was notified." *** UPDATE FROM RYAN RODE TO ERIC THOMAS AT 1930 EST ON 4/4/03 *** "At 1432 on 4/4/03, EP Manager informed control room staff that Two Rivers Utilities completed repairs to various sirens. Total loss of coverage has been reduced to 20.23%. NRC Resident, state and local agencies have been notified." R3DO (B. Clayton) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2003-04-04
39731 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-04-04 09:13 | 2003-04-04 11:18 | 2003-04-04 | LOSS OF 27 OUT OF A TOTAL OF 37 EMERGENCY NOTIFICATION SIRENS DUE TO ICE STORM "This notification is being made per 10CFR50.72.(b)3 (xiii): Eight hour reports - Any event that results in a major loss of emergency assessment capability, offsite response capability or offsite communications capability. "The following sequence of events have occurred: - On 4/3/03, a severe Winter ice storm. Affecting Oswego County, NY began. - On 4/4/03, Time: 0603, a report from the Oswego Warning Point informed NMP1 Control Room that 14 Emergency Notification Sirens were inoperable. - On 4/4/03, Time: 0913, a report from the Oswego County Emergency Operations Center informed NMP 1 Control Room that 27 Emergency Notification Sirens were inoperable." The NRC Resident Inspector and State and local government agencies have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-04
39730 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-04-04 09:17 | 2003-04-04 11:17 | 2003-04-10 | PLANT HAS MORE THAN 50% OF THEIR EMERGENCY SIRENS OUT OF SERVICE DUE TO ICE STORMS The licensee received a call from the Oswego county EOC that 25 out of a total of 37 emergency sirens are out of service due to ice storms. The NRC Resident Inspector was notified. ***UPDATE on 04/10/03 at 1422 hours by T. Page taken by MacKinnon*** "As of April 10, 2003 at 0830, all but 2 of the sirens (out of a total of 37) have been restored to operational status. Efforts are continuing to restore electrical power to the remaining 2 sirens. "As a result, the conditions under the initial notification was made no longer exist (10CFR50.72(b)(3)(xiii) .. Major loss of offsite response capability - due to loss of multiple sirens). This informational notification is provided to update the NRC as to the current conditions." NRC Region 1 Duty Officer ( James Trapp) notified. The NRC Resident Inspector was notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-04
39729 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-04-04 07:16 | 2003-04-04 09:43 | 2003-04-08 | LOSS OF MORE THAN 50% OF THE EMERGENCY SIRENS The plant has 59 of the 96 offsite notification system sirens out of service due to loss of power caused by ice storms damage to the electrical power supplies. They do not know how soon the sirens will be returned to service. The NRC Resident Inspector and local government were notified and the state will be informed. * * * UPDATE AT 1436 EDT ON 4/8/03 FROM DOUG PETERSON TO ERIC THOMAS * * * 82 of the 96 offsite notification system sirens are back in service. 13.5% of the sirens remain inoperable. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-04
39728 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-04-03 22:05 | 2003-04-04 00:18 | 2003-04-04 | FALSE ACTIVATION OF PUBLIC ALERT SYSTEM The plant had a false activation of the Public Alert Notification System (PANS) by the Sherbune County Sheriff's Department. Sherbune County personnel stated that they had accidentally triggered the system that resulted in the sirens in both Sherbune and Wright counties to sound. Both counties performed a signal cancellation and the sirens were silenced within 5 - 10 minutes. The NRC Resident Inspector was notified along with the state and local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-04
39727 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-04-03 16:05 | 2003-04-03 18:16 | 2003-04-04 | UNPLANNED SIREN OUTAGE DUE TO ADVERSE WEATHER AND OFFSITE NOTIFICATION AT KEWAUNEE "At 1605 on April 3, 2003 it was reported to the Control Room that greater than 50% siren population coverage was lost. The percent siren coverage population lost is 50.03%. The lost siren coverage is due to weather related power outages. Crews have been dispatched and are working to restore power to the affected sirens. "Additionally, substation Line Y-51 is out-of-service due to the weather conditions. Three of the four off-site power lines remain available. "The plant is currently in the process of reducing power for a refueling outage. "This is being reported under 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (loss of greater than 50% of emergency sirens). It is also being reported under 10 CFR 50.72(b)(2)(xi) as any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." The NRC Inspector was notified. *** UPDATE FROM JAMES BAPTIST TO ERIC THOMAS AT 1701 EST ON 4/4/03 *** Power has been reduced to 42 percent due to coastdown to refueling outage. Substation line Y-51 is back in service, rendering four or four off-site power lines available. There are now 9 sirens out of service, which equals 61.97% of all available sirens. The licensee has notified the NRC Resident Inspector, along with the local sheriff's department and state officials. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2003-04-03
39726 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-04-03 14:56 | 2003-04-03 18:05 | 2003-04-04 | PARTIAL LOSS OF COMMUNICATIONS "On 4/3/03 at 1456, due to adverse weather conditions, power was lost to the Site Boundary Control Center. This resulted in a loss of ENS FTS 2000 Communication System in the TSC and Control Room. This event is reportable per Duty and Call Superintendent Handbook DOS 2.1.1 Section 4.7, Clarification of NUREG-1022 Section 3.2.13, Loss of EP Capabilities. Commercial phone lines are fully functional." The licensee informed the NRC Resident Inspector, as well as state and local authorities. * * * UPDATE ON 4/4/03 @ 0145 BY RAASCH TO GOULD * * * At 2309 on 4/3/03, the EP Manager reported from the EOF that all phones are lost in the EOF. This event is reportable per Duty and Call Superintendent Handbook DCS 2.1.1 section 4.7, clarification of NUREG - 1022, section 3.2.13 loss of EP capabilities. At 2315 on 4/3/03, power was restored to the EOF. Communication capabilities from the EOF, TSC and Control Room ENS phones are restored. The Resident Inspector will be notified. Region 3 RDO(Clayton) was notified. * * * UPDATE FROM RYAN RODE TO ERIC THOMAS AT 1930 ON 4/4/03 * * * "Upon review of event notification 39726 at 1805 EST on 4/3/03, and the update to that notification at 0148 EST on 4/4/03, two corrections should be noted: 1) The original notification states that commercial phone lines were fully functional. This was correct for the control room and TSC. The commercial phones were not functional in the EOF located in the Site Boundary Control Center (SBCC), 2) The update at 0148 EST, which reported that all phones were lost in the EOF, occurred when the power was lost to the SBCC, which occurred at about 1456 CST on 3 April 2003." The NRC Resident Inspector was notified. R3DO (B. Clayton) was notified. | 97 | 97 | 0 | 97 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-04-03
39725 | 0 | DEACONESS HOSPITAL |  |  |  |  | 2003-03-28 11:00 | 2003-04-03 16:35 | 2003-04-03 | MEDICAL EVENT AT DEACONESS HOSPITAL IN INDIANA A medical event occurred on 3/28/03 at 11:00 CST when a 9 year old patient received an actual dose of 400 microcuries of I-131, for a thyroid scan and uptake, instead of a planned dose of 4 microcuries of I-131. The error occurred when the patient couldn't swallow the capsule and the hospital ordered a liquid form of the radioisotope. The wrong dosage was ordered from the radiopharmacy. The error was not discovered until after the dosage had been administered. The hospital indicated they did not expect any significant adverse health effect. The hospital was performing some more detailed calculations involving this event. A review was initiated to clearly identify the cause and initiate corrective actions to prevent recurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-04-03
39724 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-04-03 10:55 | 2003-04-03 12:30 | 2003-04-03 | OFFSITE NOTIFICATION During a safety walkdown at the old Emergency Operating Facility, a small amount (approximately 1 quart) of oil was discovered in the soil around an energized transformer. The leakage probably occurred over a long period of time, as there was no current leakage noted. The soil that contained the oil was remediated, and a sample was sent off for PCB testing. The licensee stuck a container under the transformer to gather any more leakage that might occur. The licensee was unsure whether the transformer belonged to them or to the local utility. This event was reported to the NRC because the licensee notified the state of Connecticut. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-04-03
39723 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-03-31 22:00 | 2003-04-03 12:21 | 2003-04-03 | ATTEMPTED THEFT OF A TROXLER GAUGE The Texas Department of Health reported the attempted theft of a Troxler Model 3430, (serial # unknown), on the night of 3/31/03 from a secure storage trailer at a Texas Department of Transportation construction site in Abilene, TX. Site personnel discovered the gauge in an open case on the floor of a construction trailer with its lock cut. The trailer and its storage closet had been broken into. The sealed source contains 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be. Gauge is currently secured in a different area awaiting results of leak and serviceability tests. An investigation is in process to determine whether other items were stolen, or whether this gauge was the only target of the attempted theft. This event is technically not reportable, but was entered as an attempted theft due to three other similar incidents that did result in stolen gauges in the Dallas-Fort Worth area under similar circumstances. The Texas Department of Transportation notified all other licensee's possessing portable nuclear gauges in the Abiline and Dallas-Fort Worth regions, along with local police and the Dallas FBI office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-04-08
39722 | 0 | UNIVERSITY OF MICHIGAN |  |  |  |  | 2003-04-01 16:00 | 2003-04-02 11:46 | 2003-04-02 | MEDICAL EVENT INVOLVING ADMINISTRATION OF LESS THAN PRESCRIBED DOSE A physician prescribed a dose for an outpatient therapy at 25 millicuries of Iodine 131. After completion of the treatment it was determined that the patient actually received an exposure of 18.1 or 27.6% less than the prescribed dose. The empty vials of Iodine 131 were re-assayed and 6.4 millicuries of Iodine 131 apparently remained adhered to the glass vial. The adherence of Iodine to the vial is being assessed by the Licensee and NRC Region 3. The patient was notified of this incident by the attending physician and the patient will return for administration of the remaining dose. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-04-02
39721 | 0 | MEDICAL CENTER OF BEAVER, PA |  |  |  |  | 2003-03-31 14:00 | 2003-04-02 08:51 | 2003-04-02 | PATIENT RECEIVED A DOSAGE TO AN UNINTENDED TISSUE AREA The patient had a HDR (High Dose Rate) treatment using 4-9 curies of Ir-192 when the tube was inserted into the treatment area it was 6 cms short of going to the planned area to be treated. This was caused by the wrong numbers being entered. It is estimated that the patient received between 500 and 1,000 Rads to the wrong area. The patient and prescribing physician were informed. There apparently was no adverse affects to the patient from this error. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2003-04-02
39720 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2003-04-01 16:03 | 2003-04-01 19:46 | 2003-04-01 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM "At 1603 EST, PSL [Plant Saint Lucie] Unit 2 was manually tripped due to increasing condenser backpressure (loss of vacuum). The manual trip is considered an RPS [Reactor Protection System] actuation. The plant was stabilized in Mode 3. Auxiliary Feedwater actuation occurred due to reduced steam generator level, as expected. The 2A and 2B AFW [Auxiliary Feedwater] pumps started and supplied feedwater to the 2A and 2B S/Gs [steam generators]. The 2C (steam driven AFW pump tripped. This was not expected. The 2C AFW pump has been reset for operation, but was not tested." The reactor was shutdown with all control rods fully inserted, the unit is currently stable in mode 3 with the main feedwater pumps supplying cooling to the steam generators. With the exception of the 2C steam driven AFW pump, all other electrical power sources and decay heat removal systems functioned as required. This incident had no impact on Unit 1 which remains at full power. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-04-01
39719 | 0 | YORK HOSPITAL |  |  |  |  | 2001-03-30 | 2003-04-01 16:45 | 2003-04-01 | LICENSEE TRANSFERRED RADIOACTIVE MATERIAL TO NON-LICENSED ENTITY On March 30, 2001, the Licensee transferred a Varian 6/100 linear accelerator containing depleted uranium source for disposal to a recipient who was not authorized to possess depleted uranium. The linear accelerator was eventually sold and transferred to a clinic in Reynosa, Mexico. On October 14, 2002 the Licensee submitted a written report on this incident to Region 1. The NRC has issued Office of Investigation Report No. 1-2002-036, Inspection Report No. 03003085/2002001 and the Licensee has responded to these two reports via correspondence with Region 1, dated March 27, 2003. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-04-01
39718 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-04-01 10:50 | 2003-04-01 13:53 | 2003-04-03 | VULNERABILITY DISCOVERED IN A SAFEGUARD SYSTEM AT COLUMBIA GENERATING STATION Immediate compensatory measures taken upon discovery. Licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. *** EVENT RETRACTED AT 1723 EST ON 4/3/03 BY CHESTER GREEN TO ERIC THOMAS *** A review revealed that the vulnerability mentioned in the original report does not exist. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-04-01
39717 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-03-31 20:00 | 2003-04-01 12:49 | 2003-04-01 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the Texas Department of Health, Bureau of Radiation Control via facsimile: "The gauge operator was working a night assignment. After completion he took his company vehicle to the company office to complete paperwork at approximately 11:20 p.m. After completion of the paperwork he returned to his vehicle at approximately 11:40 p.m. and discovered that his assigned CPN nuclear density gauge (Model MC1-DR, Serial No. MD0129983) with two sealed radiation sources: a 10 millicurie Amersham, Model CPN 131, cesium-137 capsule, Serial No. 2870, that is engraved on the source rod as "CS9983" (source type plus the last four digits of the gauge Serial No.); and a 50 millicurie Amersham, Model CPN131, americium-241/beryllium, Serial No. 0992, that is engraved on the gauge's internal source pedestal as "AM9983" (source type plus the last four digits of the gauge Serial No.), was missing from the truck. The Licensee's security chain had been cut and was left in the vehicle. The 'red' transport case had been locked but the Licensee reports finding a piece of it's lock, also cut, in the bed of the truck. However, the transport case was also missing. In addition, the gauge's rod handle was also locked within the case before the gauge was stolen. The Licensee also reported that nothing except the gauge and it's case were removed from the truck. This Agency has searched Agency Open Records requests back through January 2002, with no suspicious request noted." There is no media attention at this time. The Licensee is considering whether or not to post a reward for return of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-04-04
39716 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-03-31 16:25 | 2003-03-31 18:03 | 2003-03-31 | LOST/MISSING SAFEGUARDS INFORMATION Compensatory measures not required at this time. The licensee will be informing the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-03-31
39715 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-03-31 12:59 | 2003-03-31 15:40 | 2003-03-31 | AUTOMATIC REACTOR TRIP DUE TO A MAIN FEEDWATER REGULATING VALVE FAILING CLOSED "While Unit 2 was operation at 100% power steady state, 'C' MFRV [Main Feedwater Regulating Valve] failed closed due to a failed driver card at 1259 [EST]. The reactor automatically tripped 13 [thirteen] seconds later due to steam flow greater than feed flow coincident with a low SG [Steam Generator] level in the 'C' SG as expected. This is a 4 [four] hour notification. "All 3 [three] AFW [Auxiliary Feedwater] pumps auto started due to a low-low SG level in 'C' SG as expected. This is an 8 [eight] hour notification. "The unit is stable in Mode 3. Expect to re-start after repairs are made to 'C' MFRV circuitry." All rods inserted normally. All safety and electrical systems operated as designed during and after the reactor trip. There was nothing unusual or not understood. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-03-31
39714 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2003-03-29 04:00 | 2003-03-29 13:41 | 2003-03-29 | DEGRADED CONDITION DUE TO LEAKAGE AT SMALL BORE INCONEL 600 PENETRATIONS The following information was received from the licensee via facsimile: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 29, 2003, at approximately 04:00 Mountain Standard Time (MST) engineering personnel performing preplanned visual examinations of reactor coolant System (RCS) piping in accordance with procedure requirements discovered boric acid residue on three RCS small bore Inconel 600 penetrations. One location was the RCS hot leg in-service thermowell 3JRCBTW0112HB. The visual observation was characterized as a small white trail of boron residue running down the hot leg approximately 2 inches. There were no signs of dripping, spraying, puddles of liquid, or liquid running down the nozzle or hot leg. The residue appeared dry. The other two were on pressurizer heater sleeves (nozzles) A-4 and A-18. The visual observation at these two locations was characterized as a small white buildup of boron residue around the heater sleeve as the sleeve enters the pressurizer bottom head. There does not appear to be residue running down the outside of the sleeves. There were no signs of dripping, spraying, puddles of liquid, or liquid running down the nozzle or [pressurizer]. The residue appeared dry. "Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.14 permits no reactor coolant system (RCS) pressure boundary leakage and therefore, the discovery of leakage (presumed boric acid residue) from the hot leg thermowell and the pressurizer heater sleeves was a degradation of a principal safety barrier. Therefore, the ENS notification of this event is in accordance with 10CFR50.72(b)(3)(ii). The control room personnel entered LCO 3.4.14 Condition B and are continuing to place the plant in Mode 5. The RCS was being cooled down in preparation for Unit 3's tenth refueling outage. At the time of discovery, the RCS was at approximately 520 degrees F and 2218 psia. "An investigation of this event will be conducted in accordance with the PVNGS [Palo Verde Nuclear Generating Station] corrective action program. The cracking of Alloy 600 components both at Palo Verde and industry-wide has been attributed to axially oriented, primary water stress corrosion cracking (PWSCC). PWSCC is not considered a significant threat to the structural integrity of the RCS boundary, thermowell, or heater sleeves as this type of cracking typically results only in small leaks. "The bases for this conclusion is that if PWSCC occurred at Palo Verde, the cracks would be predominately axial in orientation. As in this case, the cracks would result in visibly detectable leakage that would be apparent during visual examinations, performed as part of walkdown inspections, before significant damage to the reactor coolant boundary occurred. "Palo Verde has a program for replacing the Alloy 600 hot leg thermowells. This thermowell was scheduled for replacement during this refueling outage. The plans to replace the thermowell remain unchanged. "A mechanical nozzle sleeve assembly (MNSA) will be installed on each of the pressurizer heater sleeves. "No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-03-29
39713 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-29 04:42 | 2003-03-29 07:15 | 2003-03-29 | MANUAL REACTOR TRIP DUE TO LOSS OF SECONDARY CIRCULATING WATER PUMPS "Salem Unit 2 was manually tripped in response to loss of circulating water pumps. Loss of circulators was caused by heavy grass intrusion from the Delaware River. At time of trip, a load reduction was in progress and power level was approximately 80%. All safety systems operated as designed during and after the reactor trip. Unit 2 is currently stable in Mode 3 at normal operating temperature and pressure. All reactor cooling pumps are in service and core cooling is being supported by auxiliary feedwater pumps and main steam dumps to the condenser. No safety systems or equipment was out of service at the time of the trip. Salem Unit 1 was also affected by the heavy river grass conditions and is currently in Mode 1 and stable at 55% reactor power." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-03-29
39712 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-29 02:55 | 2003-03-29 04:44 | 2003-03-29 | HPCI TURBINE FAILS TO COME TO SPEED DURING SURVEILLANCE TEST "While starting up Unit Two reactor from a planned refueling/maintenance outage, the HPCI system would not pass the required tech spec surveillance when tested at 160 psig reactor pressure. The HPCI turbine failed to come up to speed due to its turbine steam control valve did not open after the turbine stop valve was opened per system operability surveillance. The system engineer and maintenance are investigating the speed control circuit at this time." The licensee has notified the NRC Resident Inspector. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-03-29
39711 | 0 | FOX CHASE CANCER CENTER |  |  |  |  | 2000-04-16 | 2003-03-28 14:30 | 2003-03-28 | NRC LICENSEE TRANSFERRED RADIOACTIVE MATERIAL TO UNLICENSED ENTITY On April 16, 2000, the licensee transferred a Varian 6/100 linear accelerator, with a 41 millicurie depleted uranium source, to Centura X-Ray, Cleveland, Ohio, an unlicensed entity. The transfer was part of an equipment upgrade made between the licensee and Siemens Medical Systems Inc. Siemens sold the Varian 6/100 to Linac Systems, Lakewood, New Jersey who in turn sold the equipment to eRad Therapy, Inc. of Bothell, Washington. eRad Therapy transported the device to the therapy division of Centura X-ray. The depleted uranium is currently in the possession of a licensed low level waste storage facility awaiting burial at an appropriate waste disposal facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-03-28
39710 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-03-26 07:30 | 2003-03-28 12:15 | 2003-03-28 | AGREEMENT STATE REPORT - INJURED AND CONTAMINATED EMPLOYEE TRANSFERRED OFFSITE The following information was obtained from Texas Department of Health, Bureau of Radiation Control via facsimile: "The Agency was notified that at 7:30 AM [CST] [on] 3/26/03, a neutron tube blew apart inside the pulse neutron facility located at 2001 Rankin Road, Houston, TX 77073-5114. The employee that was involved received superficial lacerations. EMT's were notified at this time. Immediately after the accident H-3 [tritium] contamination was found around the wound area. The contamination was found in a swipe that was analyzed by the licensee using their laboratory located on the premises. The swipe was found to have 19 [nanocuries] of H-3 contamination. The employee was transferred by ambulance to a local hospital. We believe at this time it was Memorial Hospital. The EMT's and the hospital were made aware of the radiological contamination and all precautions were taken. The licensee requested that all materials removed or used at the hospital, and in the ambulance be returned to the licensee. [Urinalysis] was [performed] on the employee and found to be at baseline levels. Contamination was contained in the building where the accident happened and contamination on the floor was decontaminated to background levels. The licensee is following up with the hospital concerning the contaminated clothing, and debris associated with the incident. The licensee will submit a report within thirty days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-04-02
39709 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2003-03-28 00:45 | 2003-03-28 02:28 | 2003-03-28 | POTENTIAL MEDIA INTEREST DUE TO STATE POLICE SEARCH OF THE OWNER CONTROLLED AREA The Calvert Control Center in Prince Frederick County received an anonymous call through the 911 operator which prompted the Maryland State Police to furnish additional officers to the site for a search of the woodline area of the owner controlled property. The licensee will inform their media group due to the potential media interest and has informed both state/local agencies and the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-28
39708 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2003-03-27 | 2003-03-27 15:18 | 2003-03-27 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE/DENSITY GAUGE The following information was received from Alabama Office of Radiation Control via facsimile: "The Agency has been notified by Thompson Engineering and Testing, Inc. that a Troxler Model 3440 Gauge (serial #32128) containing a maximum of 9 millicuries of cesium 137 and 44 millicuries of americium 241/beryllium is missing. They have conducted a search of many of their Alabama offices, and have been unable to locate it. Since their records do not show this device being used in some time, it had been in storage, and was not detected as lost until the six month leak test was due. They are continuing to search for the gauge, and will notify this office of their findings." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2003-04-01
39707 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2003-03-27 | 2003-03-27 17:40 | 2003-03-27 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following information was received from the New York State Department of Health, Bureau of Environmental Radiation Protection: "This notice is in regard to a medical misadministration involving a Novoste Beta-Cath IVB 3.5F system, Model A1767 with AEAT Model SIC W.2 source train. The event occurred on March 25, 2003. "Two attempts to advance the source train into the delivery catheter were unsuccessful. A third (and final) attempt resulted in the source train becoming stuck in the patient's femoral artery, somewhere in the lower groin area. The sources could not be returned to the base unit. The treatment team then removed the catheter, with the source extended, and placed these items into the emergency bailout box. "The licensee estimated that the patient received an exposure of 250 Rads to an area of the femoral artery in the lower groin area. The oncologist and cardiologist decided not to proceed with IVB treatment of this patient. Hospital staff concluded that the misdirected radiation exposure would not have a significant health effect on the patient. "This event meets the reporting requirements in 10 NYCRR 16. The facility will investigate the circumstances, procedures, training, history of use, etc., and will submit a written report within 7 days. The device, including catheter and hydraulic attachment (syringe) will be sent to the vendor for evaluation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2003-04-01
39706 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2003-03-26 15:00 | 2003-03-27 16:22 | 2003-03-27 | AGREEMENT STATE REPORT - LOST OR STOLEN IODINE SOURCES The following information was received via e-mail from the Illinois Department of Nuclear Safety: "[DELETED], RSO of SourceTech Medical [(DELETED)] in Carol Stream, IL called at 1500 hours on March 26, 2003, to report that he had received a shipment of returned I-125 seeds. The dose rate on the surface of the package was 9 [millirem/hr] instead of the expected dose rate of less than 0.5 [millirem/hr]. Upon opening the box, 2 loose sources were found on top of the packing material. 7 sources were noted in the shipping papers. An additional source was found in a partially loaded Mick applicator but there were no sources in the second Mick applicator. A total of only 3 sources were found after looking through the other two lead containers in the package. "Based on assay of the three seeds, the 4 missing seeds are 425 [microcurie] I-125 each for a total of 1.7 [millicurie]. The contents of the package (Fed Ex tracking no., [DELETED]) were obviously not prepared in accordance with instructions provided by Source Tech in that the lids to the containers were not secured nor were the vials used in the lead containers as the instructions call for. The carrier, Federal Express had been contacted by [DELETED] and the delivery truck surveyed. No sources were located during the survey. According to tracking information, the package had gone from St. Augustine through Jacksonville FL, Atlanta GA, Memphis TN, Chicago, IL and the Schaumburg IL sorting facility prior to delivery in Carol Stream. An inspector was dispatched to the Schaumburg facility at 15:45 to attempt a search of the Schaumburg facility. "The sources were shipped from Slagley Hospital (Florida [DELETED]) in St. Augustine Florida on Monday 3/24/2003. [DELETED] tried contacting the site RSO, [DELETED], this afternoon but was unsuccessful. The department contacted Mr. [DELETED] of the Florida program in their Orlando office and relayed the information available at the time (see above). He indicated that he would attempt a call as well but suspected the hospital staff would be gone given the time of day (16:30) in Fla. On 3/27/03, [DELETED] notified the department that he contacted the Florida licensee and the St. Augustine hospital claimed that they counted twice the seven seeds not used in a patient, placed them in a 'screwed sealed cartridge' then put them in a shipping box for FedEx. The department also informed [DELETED], Ph.D., health physics consultant for FedEx, that there are apparently 4 iodine-125 seeds in FedEx facilities or vehicles somewhere as indicated by the routing in the message below. Jim Lynch of the NRC was also advised of the situation. On 03/26/03, a departmental inspector arrived at the Federal Express Depot located at 1270 Wilkening Road in Schaumburg; [DELETED] and explained the purpose of the visit. The inspector was provided access to the package/truck staging area. Based on the FedEx tracking number, the author was told that the bay used by the vehicle was the same one used in a previous, recent incident involving I-125 seeds. Surveys were performed by the inspector using an Eberline Model PRM-6 ratemeter, serial number 1470, last calibrated on May 16, 2002, with an Eberline Model LEG-1 probe. Background readings were [approximately] 250 - 350 CPM. Areas surveyed included the conveyor belt system, particularly junctions between belts, walkways, and the concrete pad where vehicles park for loading/unloading. Particular attention was paid to the area where the truck was unloaded and the seeds had been found in the previous incident. No seeds were located by the inspector. The department is reviewing the packaging used by SourceTech and the instructions to see if there they can be improved to prevent recurrences. The event was reported to the NRC Operations Center at 1622 hours EST on 3/27/03 and assigned Event No. 39706. A copy of this report was electronically forwarded to the Ops Center as well as the states of FL, GA, TN and NRC Region III." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-04-01
39705 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2003-03-27 09:43 | 2003-03-27 13:51 | 2003-03-27 | MANUAL REACTOR TRIP DUE TO CONDENSER TUBE RUPTURE The following information was received from the licensee via facsimile: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 27, 2003, at approximately 09:43 MST Palo Verde Unit 1 experienced a manual reactor trip from approximately 98% rated thermal power due to a condenser tube rupture. Unit 1 was at normal operating temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. There was no loss of normal heat removal capabilities, or loss of any safety functions associated with this event. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. There is no estimated time and date for the Unit 1 restart at the time this call is being made." Palo Verde Units 2 and 3 were unaffected by the Unit 1 trip. There were no lifts of primary or secondary power-operated or manual relief valves. Decay heat removal is being provided via condenser clean-up long path recirc and normal cooldown via the unaffected condenser. Prior to the trip, chloride levels in the steam generators were measured at 25 ppm and rising. Plant abnormal operating procedures require a manual reactor trip at 35 ppm chloride. There is no indications of primary-to-secondary leakage. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-03-27
39704 | -1 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-03-26 10:12 | 2003-03-26 11:16 | 2003-04-04 | REACTOR VESSEL HEAD DEGRADED CONDITION "During the unit 1 cycle 12 refueling and steam generator replacement outage, an inspection was performed of the vessel head in accordance with NRC Order EA-03-009. This bare metal inspection identified a potential leak indication at the head to penetration interface for CRDM (Control Rod Drive Mechanism) penetration #3. On March 26, 2003, at approximately 1012 hours EST, it was decided that the chemical samples have confirmed that the residue found at this interface contains boron, iron, and zinc, indicating that this was an RCS leak. This leak is most likely from a through wall crack in the RCS pressure boundary at the CRDM interface. Volumetric exams are planned to confirm the crack and to determine the scope of any repairs. In accordance with the Order, a 100% volumetric inspection is being prepared for this outage. Prior to this identification, this unit was rated as a 'low susceptibility category.' There had been no indication of RCS leakage during the previous cycle's operation. This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A)." The licensee has notified the NRC Resident Inspector. *****UPDATE ON 4/4/03 AT 1355 FROM LEAHY TO LAURA***** "The purpose of this notification is to update event #39704 concerning a potential pressure boundary leak at CRDM #3. TVA has completed both UT and PT examinations of CRDM #3. The results of these exams do not provide any indication of a crack in the RCS pressure boundary. Investigations are continuing as to the source of the residue found at the penetration. Based on the results of the vessel head examination, this investigation is focusing on determining whether the residue was a result of a prior leak from a non-RCS pressure boundary location." Notified R2DO (A. Boland) *****RETRACTED ON 4/4/03 AT 1702 EST FROM LEAHY TO LAURA***** "The purpose of this notification is to retract the original 10 CFR 50.72 notification described in event notification #39704. TVA's previous update to this notification stated that we had no indication of a pressure boundary crack and that we were continuing to investigate the source of the residue found near CRDM penetration #3. Isotopic analysis (Cesium isotopes) of the boron residue from the head now confirmed that the residue was over 10 years old and likely the result of a conoseal leak that occurred in that period. As such, TVA is retracting the original notification." Notified R2DO (A. Boland) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-03-26
39703 | 0 | DOYLESTOWN HOSPITAL |  |  |  |  | 2003-03-25 09:00 | 2003-03-26 11:10 | 2003-03-26 | MEDICAL EVENT WHICH INVOLVED EXCEEDING THE PRESCRIBED DOSE TO A PATIENT During a procedure using a Galileo 3 IVB made by Guidant, the company trainer was demonstrating how to conduct the procedure. A "hot" (wire containing approximately 100 millicuries of P-32) wire was to be inserted into the patient's coronary vessel, but prior to this a dummy wire was to be inserted. The dummy wire was inserted but not all the way. It was removed and then the "hot" wire was inserted to the same position and then removed. It was then realized that it was not fully inserted, so they reinserted it to the full position realizing that the patient would get more that the prescribed dose of 2,000 rads (actual dose received was 2,833 rads or 41% more than the prescribed dose), but the treatment was needed by the patient. There would be no adverse affects to the patient and both the patient and prescribing physician were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-03-26
39702 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-03-26 02:45 | 2003-03-26 06:04 | 2003-03-26 | SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "On 3/26/03 at 02:45 [CST], Unit 2 experienced a trip of the 2B Recirculation system variable frequency drive (VFD). The 2A VFD had tripped earlier in the shift. This resulted in entry into Technical Specification 3.4.1.B, which requires the plant to be placed in Mode 3 within 12 hours. The unit was manually scrammed at this time in accordance with plant procedures. "This event is reportable within 4 hours per 10CFR 50.72 (b)(2)(i) as 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications'. It is also reportable per 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.73(a)(2)(i)(A) and (iv)(B)." The cause of the Recirculation System VFD is being investigated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 61 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-03-26
39701 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-25 23:58 | 2003-03-26 00:30 | 2003-03-26 | OFFSITE NOTIFICATION OF MEDICAL CONDITION "On 3/25/03 at 23:45 [EST] the Main Control Room was notified that an individual with a medical condition (believed to be a kidney stone) needed to be transported to the hospital by ambulance. An ambulance was dispatched to the site. The individual was not contaminated. The individual was transported to a local hospital for treatment. "The Pennsylvania Emergency Management Agency was notified at 23:58 [EST]. Due to notification to another government agency, this event is reportable under 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-26
39700 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-03-25 12:00 | 2003-03-25 12:42 | 2003-03-25 | DISCOVERY OF CRIMINAL ACT INVOLVING FALSIFICATION OF INFORMATION PERTAINING TO ACCESS SCREENING Compensatory measures taken by Licensee upon discovery. The NRC Resident Inspector will be notified. Contact HOO for additional information. SEE EVENTS #39697 AND 39698. | 100 | 100 | 99 | 100 | 100 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-03-25
39699 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-03-25 11:21 | 2003-03-25 11:42 | 2003-03-27 | ALERT DECLARED DUE TO LOSS OF SHUTDOWN COOLING The reactor is shutdown for a refueling outage since 3/17/03. An alert declaration was made on 3/25/03 at 1121 EST due to loss of shutdown cooling. Time to boil is estimated to be less than fifty five (55) minutes. Plant status is degrading. There are no radioactivity releases in progress. The current wind direction is from 270 to 90 degrees. The wind speed is eight (8) miles per hour, class B stability with no precipitation. Mitigating responses by the Licensee are in progress. The U.S. NRC entered the Monitoring Phase of Normal Mode at 1159 at EST. *** UPDATE ON 3/25/03 AT 1233 EST FROM JONATHAN SEGUNDO TO HQ OPERATIONS CENTER*** The Alert condition was terminated and the Station entered an Unusual Event at 12:31 EST due to loss of offsite power. Shutdown cooling was restored at 11:41 EST. Plant systems are being powered by the Emergency Diesel Generators. Reactor Coolant System temperature is at 104 degrees Fahrenheit. There are no radioactivity releases in progress. *** UPDATE ON 3/25/03 AT 1824 EST FROM AMY HAZELHOFF TO ARLON COSTA*** "Nuclear Management Company is providing additional information related to event notification 39699, which was reported at 1121 [1142] EST on March 25, 2003. This information is provided for completeness of reportability requirements. The event reported earlier is also reportable under the following criteria: 10CFR50.72(b)(3)(iv)(A), due to actuation of the emergency diesel generators and 10CFR50.72(b)(3)(v)(B), due to loss of shutdown cooling. "Additionally, a press release has been issued. Therefore, a report is required per 10CFR50.72(b)(2)(xi) for notification to offsite agencies. Palisades remains in an Unusual Event until a qualified offsite circuit is supplying a vital bus. The plant is currently stable. The root cause [of this incident] is not yet known." Notifications of this update were made by the Licensee to the NRC Resident Inspector, the state, local and other government agencies, and a press release was issued on this incident. * * * UPDATE ON 3/27/03 AT 1742 EST FROM PAUL ZWISSLER TO HOWIE CROUCH * * * Palisades Nuclear Power Plant has terminated the Unusual Event declared on 3/25/03. Plant vital busses are being powered by offsite power source and the emergency diesel generators have been secured and returned to standby status. There were no security implications associated with this event. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | POT RHR INOP | OFFSITE NOTIFICATION | IMode1: Refueling; FMode1: Refueling | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(2)(xi) | 0 | 2003-03-25
39698 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-25 12:00 | 2003-03-25 12:57 | 2003-03-25 | DISCOVERY OF CRIMANAL ACT INVOLVING FALSIFICATION OF INFORMATION PERTAINING TO ACCESS SCREENING Compensatory measures taken by Licensee upon discovery. The NRC Resident Inspector will be notified. Contact HOO for additional information. SEE EVENTS # 39697 AND 39700 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-03-25
39697 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-25 | 2003-03-25 12:41 | 2003-03-25 | DISCOVERY OF CRIMANAL ACT INVOLVING FALSIFICATION OF INFORMATION PERTAINING TO ACCESS SCREENING Compensatory measures taken by Licensee upon discovery. The NRC Resident Inspector was notified. Contact HOO for additional information. SEE EVENTS # 39698 AND 39700 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-03-25
39696 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-03-24 00:30 | 2003-03-25 01:15 | 2003-03-31 | BULLETIN 91-01 24 HOUR REPORT FOR CRITICALITY CONTROL At 0030 on 3-24-03, the Plant Shift Superintendent (PSS) was notified that nine (9) pallets of process equipment containing less than a safe uranium mass and spaced 2 feet edge to edge were discovered in C-335. NCSA GEN-010 requires that the total uranium mass of an equipment group be independently verified and documented to be less than or equal to a safe mass based on the highest assay according to CP2-PO-FO1031. No documentation exists to support that the total uranium mass was verified or independently verified according to CP2-PO-FO1031 in violation of NCSA GEN-010. The NRC Senior Resident Inspector has been notified of this event. PGDP Assessment and Tracking Report No. ATR 03-0876; PGDP Event Report No. PAD-2003-006, NRC Event Worksheet [EN 39696]. Responsible Division: Operations SAFETY SIGNIFICANCE OF EVENTS: Although the total mass of the grouped items was not independently verified to be less than a safe mass, no single pallet contains greater than 35 pounds of uranium. The highest enrichment of any item was 2.0 wt. % 235U. The safe mass for uranium at 2.0 wt. % 235U is approximately 250 pounds. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR In order for a criticality to be possible, greater than a safe mass of uranium must be accumulated and then become moderated. CONTROLLED PARAMETERS MASS. MODERATION, GEOMETRY, CONCENTRATION, ETC Double contingency is maintained by implementation of two controls (verification and independent verification) of mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS); No single pallet has greater than 35 pounds of uranium and the highest assay of any Item is 2.0 wt. % 235U. The safe mass for this assay is 250 pounds. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The first leg of double contingency is based on mass. NCSA GEN-010 requires that the total uranium mass of grouped items be verified less than the UH [Uncomplicated Handling] mass limit and documented. No documentation exists that substantiates that this verification was performed; therefore, this control was violated. However, since none of the groups contain greater than a safe mass this parameter was not exceeded. The second leg of double contingency is based on mass. NCSA GEN-010 requires that the total uranium mass of grouped items be independently verified less than the UH mass limit and documented in accordance with CP2-PO-FO1031. No documentation exists that substantiates that this independent verification was performed; therefore, this control was violated. Even though the mass parameter was maintained, double contingency is based on two controls on mass. Since neither control was maintained, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Properly group and document each pallet according to CP2-CO-CN2030. 2. Upon completion of corrective action 1 for each of the 9 pallets, the exclusion zone and postings may be removed. *** UPDATE ON 3/31/03 AT 2137 EST FROM T. WHITE TO A. COSTA *** "As a result of further investigation, four additional palettes of process equipment containing less than a safe mass were discovered in C-335 at Col W-26 to W-27 (the original event was in C-335 Col D-2 to D-3). These additional pallets exist in the same state as the original nine. No documentation exists to support that the total uranium mass was verified or independently verified according to CP2-PO-FO1031 in violation of NCSA GEN-010. "The NRC Resident Inspector has been notified of this update. "PGDP Assessment and Tracking Report No. ATR 03-0943." Notified R3DO (Clayton), NMSS EO (Frant) and DIRO (Jolicoeur). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-03-25
39695 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-24 16:52 | 2003-03-24 17:26 | 2003-03-24 | UNUSUAL EVENT DUE TO CONTAMINATED INDIVIDUAL BEING TRANSPORTED OFFSITE "At 4:52 PM EST PPL Susquehanna, LLC, declared an Unusual Event for a contaminated individual transported offsite. The EAL entered was 5.1. The individual had fallen while working in the Unit 2 Drywell of the Primary Containment. Unit 2 is presently in a refuel outage. First Aid personnel were dispatched and treated her injuries. The individual's injuries prevented the removal of all of the protective clothing. Based on the inability to remove the clothing and completely frisk the individual, the individual is being considered contaminated. At 16:57 a local ambulance transported the person offsite en route to a local hospital. "This Emergency Plan entry is reportable under 10CFR50.72(a)1. "According to station guidelines, the Pennsylvania Emergency Management Agency (PEMA) was also notified of the incident. Due to notification to a government agency and possible public interest, this event is also [reportable under ] 10CFR50.72(b)(2)(xi)." The Licensee notified the NRC Resident Inspector, local authorities, the state and will issue a press release of this incident. *** UPDATE ON 3/24/03 AT 1948 EST FROM JERRY RINEHART TO ARLON COSTA *** "At 19:15 EST the Unusual Event was terminated. The individual's PCs [protective clothing] were contaminated to 600 ccpm [corrected counts per minute]. The PCs were removed at the hospital and no other contamination was found. The ambulance and the treatment room at the hospital were also frisked and no contamination was found. The contaminated PCs will be secured by the hospital's Radiation Protection staff and returned to the site tomorrow. "The individual suffered a broken wrist [and was treated for other minor injuries]." "All state and local agencies have been advised. A press release will be made." The Licensee notified the UE termination to the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2003-03-24
39694 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-24 14:55 | 2003-03-24 15:55 | 2003-03-24 | OFFSITE NOTIFICATION DUE TO BRUSH FIRE ON COMPANY PROPERTY "On 3/24/03 at 1455 [EST] the Main Control Room was notified of a brush fire on company property, outside the protected area. County Emergency communications were notified to dispatch a local fire company to extinguish the fire. The fire was not endangering the protected area surrounding the plant and therefore the onsite fire brigade was not activated. No other equipment or company structures were threatened. It was reported that the fire was extinguished at 1526 hours. "According to station guidelines, the Pennsylvania Emergency Management Agency (PEMA) was notified of the incident at 1512 hours. Due to notification to a government agency and possible public interest, this event was determined to be reportable under 10CFR50.72(b)(2)(xi)." The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-24
39693 | 0 | MONCRIF ARMY COMMUNITY HOSPITAL |  |  |  |  | 2003-03-24 11:20 | 2003-03-24 15:30 | 2003-03-24 | EXTERIOR SURVEY OF PACKAGE CONTAINING TECHNETIUM 99M RESULTED IN A COUNT LEVEL OF 21000 DPM A package containing technetium - 99m delivered by Syncore (Cardinal Health) of Columbia SC, to Moncrif Army Community Hospital was found to have surface contamination levels of 21,000 dpm on its exterior. The package was opened and it was verified that the metal container was not internally contaminated. The ammo box was placed in a store room to decay. The five (5) capsules containing technetium - 99m were used by the Hospital. The RSO called the vendor and informed them of the surface contamination found on the outside of the package. The RSO will survey the path traveled through the Hospital by the vendor carrying the package to ensure the absence of loose contamination. The RSO will contact the vendor to verify if they had contamination issues with other shipments. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | SC | HOS |  | 30.50(b)(1) |  |  |  | 0 | 2003-03-24
39692 | 0 | FRAMATOME ANP |  |  |  |  | 2003-03-24 07:30 | 2003-03-24 09:55 | 2003-03-24 | RAD SHIPMENT EXTERNAL LEVELS > LIMITS While receiving a rad shipment of CRDMs (control rod drive mechanisms) from Arkansas Nuclear One, the receipt survey of the bottom of the package was 380 mrem/hr (millirem/hour) on contact. The remaining five sides of the package each measured less than 200 mrem/hr on contact. Smear surveys of the package were within limits for surface contamination. 2 meter surveys along the outer surface of the vehicle all indicated less than 5 mrem/hr. Surveys behind the cab of the truck were 1 mrem/hr. The package was placed in a secure, isolated location at the facility. The licensee has contacted Arkansas Nuclear and TAG Transport, Inc, to discuss how to proceed with this issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2003-03-24
39691 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-03-23 10:44 | 2003-03-24 09:53 | 2003-03-24 | POWER SUPPLY FAILURE RESULTED IN THE UF6 RELEASE DETECTION SYSTEM BEING INOPERABLE At 1044 CST, on 3-23-03 the Plant Shift Superintendent (PSS) was notified that the control power for C-337A Autoclaves 1 East and 1 West was interrupted due to a fuse smoking in the distribution panel. The power supply for the local autoclave area audible and visual alarms for the UF6 Release Detection System are fed from the #1 Autoclave control power. Due to the loss of control power to the #1 Autoclaves, the UF6 Release Detection System was rendered inoperable. At the time of this incident, the C-337A facility was in an operational mode in which the UF6 Release Detection System was required to be operable. The system was declared inoperable and Limiting Conditions for Operation (LCO) required actions were put in place until power could be restored. Power was restored and the UF6 Release Detection System was declared operable at 1206 on 3-23-03. The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(1): "An event in which equipment is disabled or fails to function as designed when the equipment is required by TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident." The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2003-03-24
39690 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-03-22 16:33 | 2003-03-22 20:20 | 2003-03-22 | BABY SEA OTTER TRAPPED AT PLANT INLET "A baby Sea Otter, an endangered animal is trapped at the Auxiliary Salt water pump inlet between the bar racks and screens. The mother Otter is outside of the bar racks. We have contacted a diver to assist the [baby] Otter to safety. We have also secured the screen such that it will not start until we have moved the [baby] Otter to safety. This is being reported as an endangered sea animal taken on-site, alive, and state agencies may be notified. We are coordinating the rescue with the Marine Mammal Rescue Center." The Licensee will notify the NRC Resident Inspector, the State and other Government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-22
39689 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2003-03-22 09:30 | 2003-03-22 18:44 | 2003-03-22 | AGREEMENT STATE REPORT: STOLEN MOISTURE DENSITY GAUGE "At 11:12 a.m. on Saturday March 22, 2003 James L. McNees of the Office of Radiation Control was contacted at his home by Mr. Tad Nelson of Gallet and Associates, (Alabama Radioactive Material License No. 991) and notified that at approximately 10:00 a.m. this morning that a Campbell Pacific model MC-3 moisture density gauge had been stolen from the back of a company pickup truck at an employee's home. Nelson stated that the Homewood (Alabama) Police Department was currently at the location investigating. The device contains approximately 10 mCi [millicuries] of Cs-137 and 40 mCi [millicuries] of Am-241. Nelson further stated that the shipping container housing the device was locked, as was the control mechanism on the device, and that the thief(s) reportedly obtained the device by cutting the chain by which the shipping container was locked to the bed of the truck. "Alabama Emergency Management Agency was notified at 11:28 a.m., who [in turn] alerted other civil authorities in the Jefferson County area. The principal concern being that once the thief discovers that the stolen device has little value at sale, and is hazardous, that it will be abandoned. "Mr. Nelson agreed that if the device was not recovered by this afternoon that a press release should be made. At 5:00 p.m. today, March 22, 2003, the writer was informed by Mr. Nelson that the device had not been recovered. Both agreed that Gallet and Associates should forward the attached press release to local Jefferson County media outlets. The Licensee, Gullet & Associates, issued the following Press Release on March 22, 2003: "Around or before 9:30 on March 22, 2003, a moisture-density gauge containing sealed sources of radioactive material was stolen from its case locked to a truck owned by Gallet & Associates, Inc. of Birmingham, Alabama. The truck was parked at a home in the Edgewood community of Homewood, Alabama near the Palisades Shopping Center. The Homewood Police Department was notified and is continuing their investigation. "The Attached is a sketch of the gauge stolen. Labels indicating the device is radioactive should be visible on the gauge itself. Normally the radioactive sealed source is locked in a safe position. The device does not pose a health hazard as long as it is not tampered with or handled by untrained individuals. Please notify the Homewood Police Department at (205) 877-8637, Gallet & Associates, Inc. at (205) 942-1289, the Alabama Division of Radiation Control at 1-800-582-1866, or your local police department if found. "Since the device and sale of such is regulated it therefore has no resale value and can only be used to determine the moisture content and density of soils by licensed, qualified personnel. "A reward is offered for the recovery or information leading to the recovery of the device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2003-03-26
39688 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-22 16:45 | 2003-03-22 17:40 | 2003-03-22 | NOTIFICATION TO PEMA OF CONTRACTOR TRANSPORTED OFFSITE FOR TREATMENT "On 3/22/03 at 1645 the Main Control Room was notified of an individual (Contractor) experiencing symptoms of a Heart Condition. An ambulance was dispatched to the site. The individual was in an office space at the time of the occurrence and was not contaminated. Site EMTs responded and the individual was found to be conscious and stable. The Pennsylvania Emergency Management Agency [PEMA] was notified at 1655. The individual was transported to a local hospital for treatment. The ambulance left site at 1725. Due to notification to another government agency, this event is reportable under 10CFR50.72(b)(2)(xi)." The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-22
39687 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-03-21 22:07 | 2003-03-22 08:30 | 2003-03-23 | LOSS OF COMMUNICATIONS WITH SAFETY PARAMETERS DISPLAY "On 3/21/2003 at 22:07, the Wolf Creek Generating Station experienced an unexpected loss of the Nuclear Plant Information System (NPIS) Computer. This computer supplies data for the Safety Parameter Display System (SPDS). Trouble shooting efforts have been unsuccessful, thus far, in restoring the system. Because SPDS has been lost for longer than a short period of time, Wolf Creek Nuclear Operating Corporation is making this notification pursuant to 10 CFR50.72(b)(3)(xiii). There is no other loss of emergency assessment capability concurrent with this on going loss of the SPDS. Plant personnel entered the applicable Off Normal procedures and are taking local readings of equipment normally monitored by the NPIS Computer." The Licensee notified the NRC Resident Inspector. *** UPDATE ON 3/23/03 AT 1645 CST FROM DAVE DEES TO ARLON COSTA *** "At 1320 CST 3/23/2003 the NPIS Computer was returned to service and declared operable. The return of the NPIS Computer to an operable condition restored the SPDS assessment capability function." The Licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-03-22
39686 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-03-21 20:53 | 2003-03-21 21:21 | 2003-03-22 | UNUSUAL EVENT DECLARED DUE TO POTENTIAL INTRUDER INSIDE THE PA The licensee provided the following information during their initial call: "We declared a UE (Unusual Event) [at 2053 EST] based on 18A. Security declared code Red. We have an intruder in the PA (Protected Area). We have no indications of off normal plant conditions and we have no specific threat indicated." The licensee initially reported that their CAS (Central Alarm Station) received an alarm from the security fence around the PA. Some security force members reported seeing some sort of object come over the fence simultaneous with the alarm. Site security immediately responded to the situation, along with the Seabrook Emergency Response Team (SERT), and the FBI. Region I developed a timeline for this event, contact the HOO for details. An ongoing conference bridge was established with NSIR management (Holonich, Zimmerman), headquarters and regional IAT members (Warren, Smith, Whitney), Region I management (Miller, Wiggins, Blough, McDermott, Frechette), the NRC Resident Inspector (Dentel), and the FBI. The NRC went to Monitoring Mode for this event at 2230 EST on 3/22/03. *** UPDATE AT 0720 EST ON 3/22/03 BY ERIC THOMAS *** The FBI is conducting interviews with 4 site security personnel. The FBI has completed two of four interviews with security personnel. One, who was in the CAS, says he saw a square-looking object cross his screen that monitors the protected area boundary. The second interviewee was patrolling outside the protected area in his vehicle and saw a large bird (probably a wild turkey) with approximately a four-foot wing span fly across the road in front of him. This coincides with the location and time at which the CAS operator saw the image on his screen. The licensee is planning to perform walkdowns of all vital systems, and the SERT teams are performing additional sweeps of the protected area this morning. Additionally, licensee personnel in the Seabrook TSC are updating Region I NRC personnel on the situation every 30 minutes. *** UPDATE AT 1030 EST ON 3/22/03 BY ERIC THOMAS *** Security personnel completed second sweep of the protected area at 0955 with negative results. Interviews with 4 security personnel by the FBI revealed the following likely scenario: - Approximately 2030 on 3/21/03 - PA fence alarm coincides with CAS security officer seeing a dark mass coming over the fence on his monitor. CAS personnel then saw this featureless mass disappear behind a building inside the PA. - Approximately 2100 - CAS security officer notices dark mass on the monitor fly from a building downward over the PA security fence. Shortly thereafter, a security officer on patrol outside the PA sees a wild turkey with approx. 4-foot wing span fly across the road about 20 feet in front of his vehicle. Searches of the fence line in the area of the intrusion revealed no footprints or damage to the fence. Conclusion by site operations and security personnel, as well as FBI, is that the fence alarm was caused by intrusion of some sort of wild animal, possibly a turkey, and that there was no human intrusion onto the site. *** UPDATE AT 1102 EST ON 3/22/03 BY LICENSEE TO ERIC THOMAS *** The licensee terminated the Unusual Event at 1052 EST on 3/22/03. *** UPDATE AT 1235 EST ON 3/22/03 BY ERIC THOMAS *** The NRC exited Monitoring Mode at 1205 EST. A Commissioners' Assistants' brief was held at 1230 EST. See HOO log for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-03-21
39685 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-03-21 03:40 | 2003-03-21 11:58 | 2003-03-21 | AGREEMENT STATE REPORT: STOLEN TROXLER MOISTURE DENSITY GAUGE "Gauge operator was working the swing shift supporting operations of construction of the Dallas Area Rapid Transit (DART) in Dallas, Texas. Enroute to company office, he stopped by his residence from 3:00 a.m. to 3:40 a.m. for breakfast. Before departing for the storage location, 2200 Gravel Drive, Fort Worth, he noted that the gauge and chain were missing from his company [Law Engineering & Environmental Services, Inc.] truck (Black Ford, F-150). The stolen gauge is a Troxler 3411 B, Serial No. 10732, with two sealed sources: Cs-137, 8 millicuries, Serial No. 40-8208 and AM-241/Be, 40 millicuries, Serial No. 46-2134. A report of the theft was made to the White Settlement Police Department and to his supervisor, [DELETED]. The gauge, chain, and lock are completely missing from the vehicle. "Licensee notified White Settlement Police Department, and Texas Department of Health/Bureau of Radiation Control, TDH/BRC will notify NRC, INEEL, Troxler Electronic Labs, and the states of Arizona, Arkansas, Louisiana, New Mexico, and Oklahoma, as well as, the country of Mexico. "Media attention: None at this time. Licensee is debating notifications to local media and possibly offering a reward for return of the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-03-26
39684 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2003-03-20 16:37 | 2003-03-20 17:37 | 2003-03-20 | MISSING RADIOGRAPHY CAMERA CONTAINING AN IRIDIUM-192 RADIOACTIVE SOURCE "A Department inspector in the W. Chicago Regional Office, took a call ago from the RSO of Conam Inspection Inc. (lL-01225-22) in Glendale Heights, IL. The RSO reported that a radiography camera [Model 660-B, S/N B2872] containing 86 Ci [Curies] of Ir-192 [Iridium-192], as of March 20, 2003, destined for the Sequoyah Power Plant in Soddy Daisy, Tennessee had failed to arrive as of the expected delivery date 3/17/2003. He further stated that the carrier has been contacted daily since 3/18/03 for information as to the package's whereabouts with no success. As of 1515 hrs. on 3/20/03, the carrier indicated to him that the package may have been misrouted and can only confirm the package leaving a sorting facility in Lisle, Illinois with potential stops in South Bend, Indiana and the carrier's hazmat center in Wilmington, Ohio. The RSO was advised that a thorough search was being conducted by the carrier's personnel. "The RSO is sensitive to the current security issues and wanted to ensure the situation was promptly reported and to indicate some extent of frustration with the carrier although he hoped that the carrier would indeed locate the package. The package is in a black AEA Technology [Model 424-9, Sealed Source] overpack box marked with S/N 853 and labeled as a 'Yellow II.' The RSO provided a copy of the shipping paper that included the specific information concerning the radiography camera, the package tracking number, and a contact number at the carrier. The department used this information and made direct contact with the carrier. Carrier confirmed the above information and is continuing their search. In fact, the carrier reported this event to the NRC Operations Center as did NRC Region II." * * * UPDATE ON 3/21/03 AT 1544 EST VIA EMAIL FROM JOE KLINGER TO ARLON COSTA * * * "A Department inspector in the W. Chicago Regional Office, took a call ago from the RSO of Conam Inspection Inc. (IL-01225-22) in Glendale Heights, IL. The RSO reported that a radiography camera containing 86 Ci of Ir-192, as of March 20, 2003, destined for the Sequoya Power Plant in Soddy Daisy, Tennessee, had failed to arrive as of the expected delivery date 3/17/2003. He further stated that the carrier has been contacted daily since 3/18/03 for information as to the package's whereabouts with no success. As of 1515 hrs. on 3/20/03, the carrier indicated to him that the package may have been misrouted and can only confirm the package leaving a sorting facility in Lisle, Illinois with potential stops in South Bend, Indiana and the carrier's hazmat center in Wilmington, Ohio. The RSO was advised that a thorough search was being conducted by the carrier's personnel. "The RSO is sensitive to the current security issues and wanted to ensure the situation was promptly reported and to indicate some extent of frustration with the carrier although he hoped that the carrier would indeed locate the package. The package is in a black AEA Technology overpack box marked with S/N 853 and labeled as a 'Yellow II'. The RSO has been asked for a copy of the shipping paper that includes the specific information of the radiography camera, the package tracking number, and a contact number at the carrier so that the Department may make direct inquiries with the company. "On 21 March departmental inspectors proceeded to the Lisle, Illinois Airborne Express distribution facility to survey the area to try and locate the device. At approximately 0930 on 21 March [DELETED], Conam, notified the department that the camera was located by Airborne Express at one of their facilities in Springdale, South Carolina. The camera will be transported to its original destination at Soddy Daisy, TN. Upon learning this information, the departmental inspectors immediately terminated their survey of the Lisle Airborne Express facility. The problem appeared to be a failure to follow the appropriate procedure by Airborne Express for their hazmat packages. The Airborne Express procedures are adequate and are routinely used effectively but for this package they made an error that resulted in the hazmat package being sent to their standard package processing facility in Atlanta and subsequently inadvertently sent to Springdale, SC. Airborne Express is reviewing possible actions to prevent recurrence. NRC was notified by phone and email that the camera had been located. The event was assigned event number 39684." Notified NMSS EO (Camper), R3DO (Creed), R2DO (Julian) and via fax DOE, EPA, USDA, HHS, FEMA and DHS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-03-25
39683 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2003-03-20 08:30 | 2003-03-20 13:13 | 2003-03-20 | MEDIA COVERAGE OF TERRORIST TARGET "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This ENS notification is to inform the agency of an issue within the NRC's purview that may affect or raise a concern about the public health and safety. "It has been reported in two news articles that the Palo Verde Nuclear Generating Station has been identified as a terrorist target. These two articles have been copied from the internet [www.cnn.com/2003/US/Southwest/03/20/nuclear.plant.threat/index.html and www.washtimes.com/national/20030320-43174000.htm] and attached to this notification. We have also been informed of television coverage on the same subject on CNN and local networks. "The Palo Verde Nuclear Generating Station is prepared to respond to media questions, but has no plans to issue a press release. "The NRC Resident Inspector has been notified of this ENS call." | 97 | 98 | 99 | 97 | 98 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-20
39682 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-20 00:15 | 2003-03-20 04:39 | 2003-04-10 | INOPERABLE SECONDARY CONTAINMENT "On 3/20/03 at 0015 hours during performance of Secondary Containment drawdown testing, it was determined that the Technical Specification maximum allowed combined flowrate of 2885 SCFM for Zone 1 and Zone 3 was exceeded. The average flow for the two zones was approximately 3000 SCFM. The condition required the Station to declare both zones inoperable, and placed Unit 1 in a 4 hour LCO to restore Secondary Containment. Unit 2 is already in Mode 5, however the condition would have prevented all additional fuel moves. The Standby Gas Treatment System was capable of maintaining the DP requirement of 0.25 " vac. water gauge during the test. By 0330 investigation had reduced flow from the two zones to approximately 2600 SCFM, and the LCO was exited. The inoperability of Secondary Containment is a loss of an entire Safety Function that is needed to control the release of radioactive material, and is reportable under 10CFR50.72(b)(3)(v)(c)." The licensee notified the NRC Resident Inspector. ***RETRACTION by Grant J. Fernsler on 04/10/03 at 1303 ET taken by MacKinnon *** "A subsequent evaluation performed by Station Engineering determined that although inleakage had exceeded the required Technical Specification limit, secondary containment and the supporting equipment would have been fully capable of performing its designed safety function. Specifically, engineering calculations for secondary inleakage greater than what was experienced on 03/20/03 demonstrated that the dose consequences of a postulated event would not exceeded 50% of the 10CFR100 limits. Based on the fact that the safety function of the Secondary Containment to adequately contain the release of radioactive materials was still maintained, this ENS notification is being retracted." NRC Region 1 Duty Officer (James Trapp) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2003-03-20
39681 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-03-19 21:30 | 2003-03-19 23:15 | 2003-03-20 | SINK HOLE IN SITE STABILIZATION POND "The site stabilization pond has developed a sink hole which has created a partial bypass of the normal treatment system from an unauthorized release point. The stabilization pond receives water pumped from a Storm Drain Basin which collects storm drainage from various areas around the site. This release from an unauthorized discharge point requires notification to the State of North Carolina in accordance with our NPDES permit. This report initiated per [50.72(b)(2)(xi)] due to State of North Carolina notification." The licensee has notified the NRC Resident Inspector. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-20
39680 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-03-19 11:04 | 2003-03-19 18:16 | 2003-05-19 | HATCH MODIFICATION COULD HAVE IMPACTED COMPLETION OF A CONTROL ROOM EVACUATION "At 1104, 3/19/03, while operating at 100% power, Callaway Plant discovered that a modification performed on an equipment hatch impacted the ability to complete a Control Room evacuation in the event of a fire. The modification had installed a hatch in a floor penetration between elevations that had a latching mechanism installed on the bottom side of the hatch but the associated T-handle was not initially installed on top of the hatch. The latch mechanism could still be operated from the top via a large opening in the hatch where a ladder passed through the hatch. This modification could have resulted in the inability to access the area and valves below the hatch that would require manipulation during a Control Room evacuation. When this problem was identified, a T-handle was installed on top of the hatch for operating the latching mechanism and resolved the situation. "This event affects our commitment for the Control Room Fire Safe Shutdown analysis and is being reported as an unanalyzed condition per 10CFR50.72(b)(3)(ii)(B)." The licensee has notified the NRC Resident Inspector. Notified R4DO (C. Johnson) * * * RETRACTION ON 5/19/03 AT 1451 EDT FROM TIM HOLLAND TO E. THOMAS * * * "This event is being retracted. Upon further Engineering evaluation, it was determined that there was sufficient time to allow using an alternate route to access and operate the valve located on the elevation below the equipment hatch. Thus this event did not represent an unanalyzed condition and is not reportable." Notified R4DO (T. Pruett) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-03-19
39679 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-03-18 14:15 | 2003-03-19 14:11 | 2003-03-19 | AGREEMENT STATE REPORT - PACKAGE RECEIVED IN EXCESS OF SURFACE CONTAMINATION LIMITS The following information was extracted from the licensee's report to the Texas Department of Health: Package arrived and was unloaded with forklift at about 2:15 PM. Wet wipe when it came in the door and found 2,500 cpm/290 cm2 above background (8,620 dpm/100 cm2). Second wet wipe found 250 cpm/25 cm2 above background (9,600 dpm/100 cm2). Dry wipe of the wooden pallet found 450 cpm/300 cm2 above background (1,500 dpm/100 cm2) The cask was moved into the east Hot Cell, which has HEPA ventilation. Wet wipes of forks of fork lift were clean; wet wipes of forks of pallet jack were clean. The Truck was called back to check for contamination at 2:30 PM. The truck was frisked at about 3:00 PM and it was found that the truck was clean; the driver's hands were clean; the truck's pallet jack and dolly were clean; and the plywood boards on and by the cask were clean. Dry wipes were begun on the entire surface of the cask and pallet. Wipes on top of cask and pallet had loose contamination ranging from 0 - 3,000 cpm/300 cm2 above background (0 to 10,000 dpm/100 cm2). The sides of cask and pallet had no loose contamination. Isotope was determined to be Sc-46 by gamma spec. It has a 83.8 day half life. Talked to HP at Texas A&M, at about 3:15 PM and she described a Sc-46 airborne measurement, that the cask had been cleaned with Fantastic, and that release wipes showed very low contamination (below 75 dpm/100 cm2 contamination). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | MAT | [5 empty] | 0 | 2003-03-19
39678 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-03-18 20:47 | 2003-03-18 21:05 | 2003-03-18 | ALERT DECLARED DUE TO FIRE IN CABLE SPREADING ROOM The licensee declared an alert at 2047 EST due to a fire in the cable spreading room which started at 2037 EST. The fire was declared out by 2130 EST in response to deenergizing 480 volt AC load center # 12. Preliminarily, the fire appears to have occurred within the breaker compartment on load center #12 supplying Charging Pump 55A . Plant conditions remains stable with shutdown cooling continuing in service. There were no releases or other offsite consequences. The licensee notified the NRC Resident Inspector. * * * * UPDATE RECEIVED FROM J. MIKSA BY M. RIPLEY AT 2326 EST 03/18/03 * * * * The licensee terminated the alert at 2326 EST on 03/18/03. Notified R3DO (J. Creed), NRR EO (S. Richards), DIRO (N. Mamish), FEMA (Watch Officer), DHS (S. Tull) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-03-18
39677 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2003-03-18 10:00 | 2003-03-18 15:15 | 2003-03-18 | OFFSITE NOTIFICATION The Governor's Office of the State of Arizona issued a press release regarding National Guard deployment at the Palo Verde Nuclear Generating Station (PVNGS). The press release was issued at approximately 10:00 MST 03/18/03. The Palo Verde Nuclear Generating Station has no plans to issue a press release at this time. The licensee notified the NRC Resident Inspector. Notified R4DO (C. Johnson) | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-18
39676 | 0 | DEFENSE DISTRIBUTION DEPOT |  |  |  |  | 2003-02-24 | 2003-03-18 08:06 | 2003-03-19 | LOST AMERICIUM-241 SEALED SOURCES On 3/18/2003, NRC Headquarters was informed by the master materials licensee (located in New Cumberland, PA) that on 3/17/2003, it was discovered by the licensee that two Americium-241 sealed sources were unaccounted for. The sources were tracked to a shipment facility at Warner Robbins Air Force Base on 2/24/03, but there is no record that the sources were shipped out of the facility or where they might be stored. The sources are contained in a laser transmitter/receiver and contain 4 microcuries of Americium-241. * * * * UPDATE FROM D. MACK TO M. RIPLEY 1336 EST ON 03/19/03 * * * On 03/18/03, NRC Headquarters was informed that the laser transmitter/receiver (S/N 10425) containing both Americium-241 sources was located at Laken Heath Air Force Base in England on 03/18/03. Further investigation continues. Notified R1DO (P. Eselgroth) and NMSS EO. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-03-18
39675 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-17 08:18 | 2003-03-17 16:48 | 2003-03-17 | REACTOR WAS MANUALLY TRIPPED WHILE IN MODE 3 DUE TO ONE ROD REMAINING AT 0 STEPS WHILE THE BANK OF RODS WAS BEING WITHDRAWN "On 3/17/2003 at 0818, Unit 2 was in its 11th refueling outage in MODE 3 (hot standby). Post-maintenance testing of digital rod position indication (DRPI) was in progress in accordance with Surveillance Test Procedure (STP) R-1C. Rod control bank B was being withdrawn. As the bank of rods was withdrawn, rod F2 DRPI indication remained at 0 steps. When the bank demand position indication exceeded rod F2's DRPI indication by greater than 12 steps, the reactor trip breakers were opened by manual reactor trip initiation. This action was taken to comply with the STP precautions to positively place the control rods in a known position, i.e. fully inserted. All systems actuated as required rods fully inserted, the main turbine automatically tripped. "Manual initiation of a reactor trip where the actuation is not part of a pre-planned evolution is reportable under 10CFR50.72. (b) (3) (iv) (A) and 50.72(b) (3) (iv) (B) (1). While the reactor trip was initiated in accordance with the STPs precautions, the manual actuation was not an expected outcome of the STP. "Subsequently, it was determined that rod F2 was indeed on the bottom as indicated by DRPI. A moveable gripper fuse was blown preventing that rod from being withdrawn. The blown fuse was replaced and testing continued in accordance with the outage schedule." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-03-17
39674 | 0 | ELMBROOK MEMORIAL HOSPITAL |  |  |  |  | 2003-03-07 13:00 | 2003-03-17 14:29 | 2003-03-17 | MISSING IODINE-125 SEED On March 3, 2003 120 Iodine-125 seeds, each with an activity of 0.31millicuries, were implanted in a patient. Four of the seeds were recovered from the bladder and placed in a lead pig. On March 7, 2003 an inventory was taken of the lead pig before shipping the seeds back to the manufacturer. During the inventory check it was discovered that the lead pig only contained 3 Iodine-125 seeds instead of 4. A radiation surveys were taken of the areas where the seeds had been removed and the missing seed was not found. Notified NMSS EO (F. Brown) and R3DO (K. O'Brien, J. Creed). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-03-17
39673 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-03-16 21:49 | 2003-03-17 01:25 | 2003-03-17 | MANUAL REACTOR TRIP AND AUXILIARY FEEDWATER ACTUATION DUE TO CONDENSATE PUMP TRIP The following information was obtained from the licensee via facsimile: "Unit 1 manual reactor trip (RPS actuation) was initiated at 2149 [CST] due to a loss of main feedwater. The event was initiated by a trip of Condensate Pump 1-01 which resulted in a trip of Main Feedwater Pump 'B' and Main Feedwater Pump 'A' due to inadequate suction pressure. "An automatic initiation of Auxiliary Feedwater (ESF actuation) occurred when both Main Feedwater Pumps tripped. "Unit 1 is currently in Hot Standby (Mode 3) with decay heat removal via Auxiliary Feedwater and Steam Dump to the Main Condenser. All safety systems responded appropriately. The cause of the Condensate Pump 1-01 trip is currently under investigation." All control rods fully inserted. There are no indications of any primary-to-secondary leakage. There were no primary or secondary power operated relief or manual relief valves lifted. The electrical grid is stable. The licensee did receive low steam generator level alarms (as expected) but levels were recovered and are being maintained via the Auxiliary Feedwater system. Unit 2 is stable and was not affected by the Unit 1 trip. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-03-17
39672 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-03-16 05:25 | 2003-03-16 10:58 | 2003-03-16 | ACCIDENT MITIGATION SYSTEM INADVERTENT ISOLATION The following information was obtained from the licensee via facsimile: "ON 03/16/2003 AT APPROXIMATELY 0525 CST, HPCI ISOLATED AND TRIPPED DURING PERFORMANCE OF 2-SR-3.5.1.7, HPCI MAIN & BOOSTER PUMP SET DEVELOPED HEAD & FLOW RATE TEST. INITIAL INDICATIONS [ARE] HPCI ISOLATED ON A HIGH STEAM FLOW SIGNAL. THERE IS NO INDICATION OF A STEAM LINE BREAK. INVESTIGATION IS ON-GOING. "THIS IS REPORTABLE AS A 8-HOUR NON-EMERGENCY EVENT 10CFR50.72(b)(3)(v), AND A 60 DAY WRITTEN REPORT 10CFR50.73(a)(2)(vii), AS "ANY EVENT OR CONDITION THAT AT THE TIME OF DISCOVERY COULD HAVE PREVENTED THE [FULFILLMENT] OF THE SAFETY FUNCTION OF STRUCTURES OR SYSTEMS THAT ARE NEEDED TO: (A) SHUTDOWN THE REACTOR AND MAINTAIN IT IN A SAFE SHUTDOWN CONDITION (B) REMOVE RESIDUAL HEAT (C) CONTROL THE RELEASE OF RADIOACTIVE MATERIAL; OR (D) MITIGATE THE CONSEQUENCES OF AN ACCIDENT." The licensee will notify the NRC Resident Inspector. | 0 | 31 | 0 | 0 | 31 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-03-16
39671 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2003-03-14 | 2003-03-14 17:13 | 2003-03-14 | ILLINOIS AGREEMENT STATE REPORT ON LOST SOURCE "On March 13, 2003 the RSO of Cook County Hospital called the Illinois Northern Regional office to report that an Sr-90 eye applicator source was missing from its storage location along with some exempt quantity calibration and reference sources and some associated records. A thorough survey of the facility had been conducted the previous two days with no success. This hospital is going through the process of relocating to new facilities immediately adjacent to the existing site. At first it was thought that these sources had been moved with other brachytherapy sources and had been merely overlooked in the transition. Further inspection showed that was not the case. Apparently the source has been mistakenly removed during efforts to clean and prepare the area for occupancy by another hospital department. This probably occurred at the end of January 2003 based on interviews with several associated individuals. The room where the source cabinet had been stored had been cleaned and its contents sent for disposal or relocation to the new oncology department on January 30 and 31. The Department sent an inspector to the facility the next morning, 14 March, to conduct interviews, perform monitoring, verify the extent of the search efforts undertaken to this point and make an independent evaluation of the reported fate of the device. Surveys of several areas with a variety of appropriate rate meters and probes including old and new storage locations, oncology departments, shipping and receiving docks, waste handling locations and nuclear medicine departments were unsuccessful in recovery of the applicator. Interviews with the RSO, facility medical director, radiation oncologist, supervisory radiation technician and individuals who performed the clean out work do not provide any additional information as to the fate of the source as all state that they did not remove the source from its storage cabinet. The source was initially 35 milliCuries in 1955 and has since decayed to approximately 11 millicuries to date. The source does not appear in the NRC SSDR due to its age. The manufacturer is listed as TRAUSLAT with model number RA-1 and a serial number of 183. Given the situational circumstances, the existing presence of nearby brachytherapy sources of Cs-137 and a teletherapy source in the area, the limited access to the room, control of keys, and the disappearance of records along with check sources leads the RSO as well as the Department inspector to believe that the eye applicator and exempt quantity reference sources were inadvertently disposed as waste back in late January 2003. There is a slight potential that the material may be discovered in the hospital as the various departments continue their relocation to new facilities. The licensee will file the required report and the department will take appropriate action based on additional information received. Event reported to NRC Operations Center on at 1713 ET 14 March 2003 and assigned event number 39671." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-03-19
39670 | 0 | WESTINGHOUSE |  |  |  |  | 2003-03-14 | 2003-03-14 15:47 | 2003-12-25 | 10 CFR PART 21 REPORT REGARDING FAILURES OF ABB CIRCUIT BREAKERS Circuit breakers manufactured by ABB Inc. and used for Class 1E applications by Westinghouse were shipped to the Calvert Cliffs Plant with model 5 operating mechanisms installed. Recently, Westinghouse had retrofitted the breakers with model 7 operating mechanisms manufactured by ABB Inc. Westinghouse validated that the original breaker qualifications (for Class 1E applications) are still applicable with the model 7 operating mechanism installed. Two of these breakers failed to close and latch during testing at Calvert Cliffs. The first breaker failed to close and latch during acceptance testing on January 18, 2003. The second breaker failed to close and latch during its installation acceptance test in the breaker cubicle on January 27, 2001. * * * UPDATE VIA FAX ON 12/24/03 AT 15:25 CST BY ABB INC * * * Summary: The issue reported in the notification above is limited in scope and there is no indication that the failure mode will exist in a K-Line breaker. ABB does concur that dimensional non-conformities were present in the breakers that exhibited the fail to close of the primary and secondary trip latches. ABB also concurs that this out-of-tolerance situation is contributory to the failure exhibited in the 5VHKR250 1200A breaker but is not in and of itself the root cause of failure. Notified R1DO (R. Lorson), R2DO (M. Ernstes), R3DO P. Louden), R4DO (L. Smith), NRR (Jack Foster) via email | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-03-14
39669 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-03-13 14:30 | 2003-03-13 18:35 | 2003-03-13 | DEGRADED APPENDIX "R" BARRIER AT MONTICELLO "During inspection of penetration FZ-4900 in the upper 4KV room it was discovered there was a portion of the penetration seal that was degraded which caused the upper and lower 4KV rooms to communicate with each other. Penetration seal FZ-4900 is a gypsum wall board assembly approximately 18 inches wide 4 foot high and 24 foot long. The degraded part of the penetration is approximately 1 inch by 4 inch hole. The upper and lower 4 KV areas are required to be separated in accordance with 10CFR50 Appendix R requirements." The licensee indicated they established a fire watch as a compensatory measure. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-03-13
39668 | -1 | REGIONS HOSPITAL |  |  |  |  | 2003-03-07 09:00 | 2003-03-13 17:27 | 2003-03-19 | SURFACE CONTAMINATION ON AMMO BOX GREATER THAN ACCEPTABLE LIMITS On March 7 @ 0900 an ammo box was received from Syncor that measured 0.3mr/hr at the surface and had a wipe of approximately 9707 DPM (2200 DPM is acceptable). Syncor was notified of the contamination on the box. The box was put into the hospital's storage area until March 11 when the measurements taken were at background. The box was than returned to Syncor. * * * RETRACTION RECEIVED FROM R. SOGARD BY M. RIPLEY 1505 EST ON 03/19/03 * * * After review of applicable reportability criteria and discussions with NRC Region 3, the licensee is retracting this notification. Because the surface contamination criteria for items received is actually 22,000 DPM (vice 2,200 DPM for items being shipped), the box contamination is not reportable by this licensee. Notified R3DO (J. Creed) and NMSS (F. Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MN | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2003-03-13
39667 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-03-13 08:00 | 2003-03-13 16:32 | 2003-03-13 | ERROR IN THE CURRENT SAFETY ANALYSIS FOR A STEAM GENERATOR TUBE RUPTURE "On March 13, 2003 while operating at 100% power, Callaway Plant determined a problem existed in the current safety analysis for a steam generator tube rupture accident accompanied by an overfill condition of the ruptured steam generator. This problem was discovered while reviewing a future plant modification package. The current FSAR analysis concluded that an overfill condition would not occur during a tube rupture accident. "Through investigations instigated during the modification review process, it was determined that for current plant conditions, an overfill condition could result if an auxiliary feedwater control valve supplying the ruptured steam generator were to fail open. In this case, it was concluded that the ruptured steam generator would overfill and water would be released through the steam generator safety valves, resulting in a radioactive release to the environment greater than allowed by regulatory guidance. Since this accident was not adequately incorporated in the FSAR, specific procedural time limits for operator actions had not been developed. This lack of credited operator time limits coupled with past plant modifications result in a potential to exist for the ruptured steam generator overfill scenario. "Current Technical Specifications allow a reactor coolant system Dose Equivalent Iodine (DEI) value of 1.0 microcurie per gram. To assure compliance with existing regulatory guidance, plant procedures have been changed to administratively reduce the steady state DEI limit to 0.3 microcurie per gram, a value that has not been exceeded in the last three years. Current steady state DEI concentration in the reactor coolant system is 0.001769 microcurie per gram. The new lower DEI limit will ensure that if an overfill condition were to occur during a steam generator tube rupture, post accident radiological consequences would not exceed the limits imposed by the FSAR and the Standard Review Plan." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-03-13
39666 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2003-03-03 | 2003-03-13 15:00 | 2003-03-19 | NEW MEXICO AGREEMENT STATE REPORT ON LOST SOURCE "On March 3, 2003, Cardinal Health in Albuquerque shipped out an ammo-can, via Federal Express Overnight, containing 1.251 Giga-Becquerel of I-131 in an inorganic salt, solid state to the Cardinal Health facility in Amarillo, TX. for delivery on 03/04/03. The Amarillo facility called on Tuesday, 03/04/03, to state they never received it. [DELETED ] placed a call with Federal Express immediately to trace the package. She continued to place calls with Federal Express on 03/05/03 and 03/06/03 to check on the status of the package. On each occasion, Federal Express stated they had yet to locate the package. On Friday 03/07/03 I called [DELETED ] at our Quality and Regulatory Dept. to notify them of the missing package. He, in turn, placed a call with the New Mexico Environment Dept. On Monday, 03/10/03, I called Federal Express and spoke with [DELETED ] of the Amarillo office. She stated that they had done a thorough search of the Amarillo office and could not find the package. She also stated that there was to be a search of the Memphis location and that they would hopefully know something by Tuesday 03/11/03. I notified [DELETED ] of my conversation with Federal Express. We did not hear anything from FedEx on Tuesday. On Wednesday 03/12/03, I called FedEx again and spoke with a representative by the name of [DELETED]. She confirmed that the package had still not been located. I then contacted [DELETED ] again to report the information. I also left a message with the New Mexico Environment Dept. regarding the current state of the matter. We will continue to monitor the situation. The tracking number for the package is [DELETED]." * * * UPDATE RECEIVED VIA EMAIL FROM W. FLOYD TO M. RIPLEY AT 1454 EST 03/19/03 * * * The missing I-131 package was delivered to the licensee's pharmacy in Amarillo, TX on 03/18/03. The package was in good condition and had not been opened. The licensee continues to discuss the issue with FedEx to reduce recurrence of such events. Notified R4DO (C. Johnson) and NMSS EO (F. Brown) . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2003-03-18
39665 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-03-13 06:15 | 2003-03-13 13:38 | 2003-03-13 | MAJOR LOSS OF EMERGENCY PREPAREDNESS CAPABILITIES The licensee was notified by Ocean County that their alarm panel indicated the radio power to the prompt notification sirens had failed with unknown affect on the sirens operation. The Licensee Technicians were dispatched and had to reboot a computer to clear the alarm. Sirens would not operate until the computer was rebooted. Sirens tested satisfactory @ 0930 hours. This notification was made because it can not be determined if the Ocean County siren activation technicians possess the knowledge and skills to reboot this computer if siren activation would have been required. If it is later determined that the technicians did possess the required knowledge and skills, this notification may be retracted. The NRC Resident Inspector was notified along with local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-03-13
39664 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2003-02-27 09:28 | 2003-03-13 11:14 | 2003-03-13 | INVALID SPECIFIED SYSTEM ACTUATION 60 DAY REPORT "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 17, 2003, at approximately 0928 Mountain Standard Time, Palo Verde Nuclear Generating Station Unit 2 experienced an invalid actuation (start) of the 'A' Emergency Diesel Generator (EDG). EDG 'A' inadvertently started when an Instrument and Control technician, performing the ESFAS train 'A' subgroup relay functional and response time surveillance test, completed a step in the test procedure out of sequence. The technician verified the status of [actuated] an ESFAS relay contact, which generates an EDG start signal, before the 'A' EDG control mode switch was placed in the OFF position. "This report is not considered an LER. "EDG 'A' was the specific System and train that actuated. "EDG 'A' started in the Emergency Mode. The train actuation was complete. "EDG 'A' started and came up to rated speed and voltage as designed. "This report is being made under 10 CFR 50.73 (a) (2) (iv) (A)." The licensee has notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-03-13
39663 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-03-05 20:00 | 2003-03-12 11:11 | 2003-07-25 | WA AGREEMENT STATE REPORT ON POSSIBLE OVEREXPOSURE INCIDENT "Licensee: PM TESTING LABORATORY "Licensee number: WN-11R047-1 "Type of licensee: Industrial Radiography "Date of event: March 5, 2003 "Location of event: Port of Tacoma, WA. German cargo ship 'Big Lift' "ABSTRACT: (as reported by licensee's representative) A radiographer and Assistant Radiographer were performing radiography at the Port of Tacoma, on a German cargo ship 'Big Lift' on March 5, 2003, at approximately 10 PM [PST]. The work required the radiographers to use a cherry-picker type lifting vehicle to access the work area since the area was about 100 feet above deck level. The Radiographer and Assistant were both in the lift bucket, 2 feet apart, at the time of the incident. The industrial radiographic device (Amersham Corporation Model 660B, containing approximately 70 curies of iridium 192) with connected guide tube, collimator and control cables had been lifted into position and secured in the area of the intended exposure. The exposure device had been made ready for the exposure. The operation required the Radiographer and Assistant to move the lift as far from the exposure area as possible while extending the control cable. "As the lift was being positioned away from the work area it swayed, this startled the radiographer who dropped the control cable. The sway also caused the lift's engine to stall. The action of dropping the control cable to the extent of its length and resulting sudden stop at the end of the drop caused the source to become unshielded. Their survey meter immediately went off scale on the highest scale and their alarm-rate meters were alarming. "It took the radiographers, by their estimate, about 30 seconds to restart the [lift] vehicle, move the bucket so they could recapture the control cable and secure the source. When they were able to check their pocket ion-chambers, they found them off scale. Work was stopped for the day and both film badges were sent for processing. "Results from film badge processing and analysis indicated the Radiographer received a whole body exposure of 1600 millirem. This coincided with the calculations made by the Radiographer after the incident. The film badge for the Assistant indicated an exposure of 1,423,000 millirem. When the badge processor was contacted and asked to reanalyze the film they stated they got the same exposure. "Since both radiographers were within 2 feet of each other in the lift basket and calculations confirmed that the Radiographer's exposure was 1600 milliRem, it appears the exposure to the Assistant was incorrectly determined. In addition, the Assistant is not exhibiting any signs of an excessive exposure. The company is submitting a report of the incident. The Division is performing an investigation. Media, at present, are not involved. "What is the notification or reporting criteria involved? WAC 246-221-260, Reports of overexposures and excessive levels and concentrations. "Activity and Isotope(s) involved? 70 curies of Iridium 192. "Overexposure? Until the investigation indicates otherwise, the process report of the Assistant's film badge indicates a whole body exposure of about 1,423,000 milliRem. The over exposure is apparently not real since calculations using exposure time, distance and source activity and a second film badge, worn by another individual closely associated with the first all indicate exposure is unusual but much lower. Staff will investigate." * * * UPDATE 1326 EDT on 7/25/03 FROM A. SCROGGS VIA EMAIL TO THE OPS CENTER * * * The following is a portion of an email received from the Dept. of Health, Rad Materials Section: "The initial report indicated that an Assistant Radiographer appeared to have received an overexposure. The Department's investigation determined this not to be true. "As a result of the department's investigation of the event and review of the radiography company's assumptions and calculations, the Assistant's exposure was determined to be 1600 millirem. Although this is a significant and unusual exposure, given the circumstances of the event, the department considers that any health effects would be minimal. "The event is considered to be closed." Notified R4DO (Pruett) and NMSS (Greeves). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-03-17
39662 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-03-12 00:25 | 2003-03-12 02:13 | 2003-03-12 | FUEL OIL SPILL "At 0025 [on] 3/12/03, notification was made to offsite government agencies, the U.S. Coast Guard National Response Center and the Alabama Department of Environment Management. The notification was required because approximately 50 gallons of fuel oil were spilled on site reaching on site waters. Control measures were implemented to prevent oil from reaching navigable waters. Plant operations were unaffected." The source of the spill was the fuel oil storage tank for 2 "C" Emergency Diesel Generator. While in the process of filling the tank, the worker became distracted and did not secure at 96 percent full per procedure. This was not a 'reportable quantity'. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-12
39661 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2003-03-11 21:15 | 2003-03-11 21:48 | 2003-03-11 | CONTRACT EMPLOYEE INAPPROPRIATELY GRANTED UNESCORTED PLANT ACCESS Unescorted access was inappropriately granted to a contract employee. Immediate compensatory measures were taken upon discovery. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-03-11
39660 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2003-03-11 | 2003-03-11 11:59 | 2003-03-11 | AGREEMENT STATE REPORT: MISSING BRACHYTHERAPY IRIDIUM-192 SEED. Dr. Sinnott called to report the loss of an Ir-192 brachytherapy seed with a current activity of 6 millicuries. The source was last visually inventoried in December 2002. The loss was noted yesterday, March 9, 2003, while the physicist was packaging sources for return to the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2003-03-14
39659 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2003-03-10 22:38 | 2003-03-11 05:23 | 2003-04-28 | POTENTIAL RAD GROUND RELEASE PATH DISCOVERED DUE TO LOSS OF SECONDARY CONTAINMENT "This notification is being made pursuant to NRC regulation 10CFR50.72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "On March 10, 2003 at 22:38, it was determined that the secondary containment was inoperable due to a leak in the Z sump manway gasket. The plant was in Mode 5, shutdown, performing fuel shuffle when secondary containment was declared inoperable. LCO 3.6.4.1 was entered. The fuel shuffle was secured at 22:40 after the completion of the fuel move that was in progress. No additional Core Alterations or OPDRVs [Operations Potentially Draining the Reactor Vessel] were in progress. Upon investigation into the secondary containment operability, it was determined that a non-Tech Spec surveillance performed on dayshift also rendered secondary containment inoperable due to additional leakage pathway via the Z sump. A principal safety function of Secondary Containment is to limit the ground level release to the environs of airborne radioactive materials resulting from a fuel handling accident. "As a result of the alignment of the Z sump the potential existed that if a radioactive release were to occur due to a fuel handling accident, part of the filtered release via Standby Gas Treatment System could be a ground level release vice a release through the Elevated Release Point. The surveillance has been completed and the additional leakage paths that were opened due to the surveillance have been sealed. The leaking manway gasket was determined to be due to not adequately torquing the gasket bolts. The bolts have been retorqued. Secondary containment was reestablished, and was declared OPERABLE at 02:55, 3-11-03. "The NRC Senior Resident has been notified." * * * RETRACTION TAKEN ON 04/28/03 AT 1123 EDT FROM JIM SUMPTER TO GERRY WAIG * * * "THIS IS A RETRACTION OF EVENT #39659. "On 3/10/2003 at 2238 CST, Cooper Nuclear Station made an 8 hour 50.72 non-emergency notification to the NRC per 50.72 (b)(3)(v)(D). It was determined that the secondary containment was inoperable due to a leak in the Z sump manway gasket. The plant was performing fuel shuffle at the time. LCO 3.6.4.1 was entered. The fuel shuffle was secured at 22:40 after completion of the fuel move that was in progress. Investigation determined that a non-Tech Spec surveillance performed on dayshift also rendered secondary containment inoperable due to an additional leakage pathway via the Z sump. As a result of the alignment of the Z sump, the potential existed that if a radioactive release were to occur due to a filet handling accident, part of the filtered release via the Standby Gas Treatment System could be a ground level release. This would potentially result in unacceptable dose levels since DBA calculations assulne an elevated release point for this accident. Thus, the secondary containment would be unable to fulfill its accident mitigation safety function to limit the release to the environs of radioactive materials from postulated design basis accidents (DBA) to control room occupants and off-site. "Further evaluation demonstrated that if a fuel handing accident had occurred at the time of discovery of the condition, the thyroid doses to control room personnel (which are the limiting doses for this accident) would have been less than DBA values. Other doses would remain a small fraction of 10CFR100 and General Design Criteria 19 limits. This is because the plant had been shutdown for 14 days reducing considerably the fuel handling accident source term. In addition, the estimated ground level release flow rate was a small percentage of the elevated release point flow rate. Finally, most of the radiation dose from this accident occurs in the first 90 seconds of the event via the unfiltered Reactor Building exhaust. Therefore, the secondary containment, which includes the Standby Gas Treatment system and the elevated release point, would have performed its accident mitigation safety function and was operable." The licensee will notifiy the NRC Resident Inspector NRC R4DO (Greg Pick) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-03-11
39658 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2003-03-10 11:37 | 2003-03-10 18:24 | 2003-03-10 | PRIMARY CONTAINMENT AIRLOCK SEALS DEFLATED. At 1137 CST on 03/10/03, with the plant at 87% power, the Main Control Room team received indications that the seals were deflated on both doors of primary containment airlock JRB-DRA1. Personnel were exiting containment through the airlock at this time. Personnel were dispatched and airlock integrity was restored at 1208 CST. The cause of the condition appears to be related to the mechanical interlock. This interlock did not function as required to prevent deflation of the seals on both doors concurrently. This condition is being evaluated. This condition could have resulted in a loss of function of the Primary Containment to confine a postulated release of radioactive material to within limits. The Senior Resident Inspector was notified of this event by the licensee. | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2003-03-10
39657 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-10 07:31 | 2003-03-10 17:32 | 2003-03-10 | REACTOR COOLANT SYSTEM LOW TEMPERATURE OVERPRESSURE PROTECTION (LTOP) NOT ENABLED During the eleventh refueling outage on Unit 2 (2R11) the reactor coolant system low temperature overpressure (LTOP) protection was inoperable due to the individual power operated relief valves (PORV's) control switches being selected to the "closed" position. LTOP was unable to perform its required automatic function from 0829 PT on 03/09/03 until the discovery time of 0731 PT on 03/10/03. This discrepancy was discovered by the operator during the beginning of shift board walkdown, at which time the PORV selector switches were returned to "auto" and LTOP protection was enabled. At no time were any of the LTOP setpoints challenged. Residual Heat Removal (RHR) pump suction relief valves (setpoint is 450 psi) were also available during this time frame to provide overpressure protection. Reactor Coolant temperature was 109 degrees F. LTOP setpoint was for 435 psi. The LTOP PORV's control switches were closed during the vacuum degas procedure. Licensee is still investigating this event. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-03-10
39656 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2003-03-10 03:00 | 2003-03-10 15:24 | 2003-03-10 | BULLETIN 91-01 24-HOUR REPORT DUE TO FAILED IN-LINE CONCENTRATION MONITOR During a routine check of the in-line monitor in a low-level waste solution stream, the monitor was observed to be "refreshing" but appeared to have an unusual background reading. Discharge to waste tanks WD01 and WD02 was suspended, however, approximately 11 liters of solution with a U-235 concentration of approximately 0.02 grams U-235/liter was discharged to the waste tanks. Approximately 4.0 grams U-235 was calculated to be in the waste tank based on sample and non-destructive assay scan of the tank being filled. The samples obtained from the tank were analyzed and matched the concentration of the liquid waste being discharged to the tank. There were no releases, contamination, or personnel exposures associated with the incident. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 1 | 2003-03-10
39655 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-03-08 12:45 | 2003-03-10 14:54 | 2003-03-10 | AGREEMENT STATE REPORT: STOLEN TROXLER MOISTURE DENSITY GAUGE "A Troxler model #3430 (serial number 27095), portable moisture/density gauge was reported stolen from the Texas Medical Center construction project site located at 2450 Holcomb, Houston, Texas between 12:45 p.m. and 1:30 p.m. CT on Saturday, March 8, 2003. This device is bright yellow, approximately 11" long x 8" wide x 5" tall with two metal posts approximately 18" tall protruding from the top of the device and a locked handle at the top. The device contains two sealed sources (isotopes) double-encapsulated in stainless steel, and is licensed by the Texas Department of Health. When not in use, the device emits low-level energy equivalent to a single chest x-ray, which poses no threat unless the device is tampered with. "A police report has been filed with the Houston Police Department. "The company is offering a $500.00 reward for the return of the device on the 'no-questions-asked' bases. If found, please do not move the device and contact the Houston Police Department and refer to police report no. 032141303E. If anyone has any information regarding the theft of the device please [call PSI]." The State of Texas believes the Troxler moisture density gauge contains 10 millicuries of Cesium-137 and 40 millicuries of Am/Be-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-03-13
39654 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-07 17:00 | 2003-03-10 14:26 | 2003-03-10 | FITNESS FOR DUTY FOR ALCOHOL On 03/07/03 at 1700 hours CT a contract employee was asked to take a for cause test for alcohol. He refused to take the test and he then resigned from his position. At 1731 hours his unescorted access was terminated. The licensee escorted the individual offsite and to his residence. His work record was reviewed and nothing unusual was found. The NRC Resident Inspector will be informed by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.73 |  |  |  | 0 | 2003-03-10
39653 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-10 09:18 | 2003-03-10 12:12 | 2003-03-10 | MANUAL REACTOR TRIP Unit 2 Manual Reactor Trip at 0918 ET on 03/10/03 due to the following sequence events: At 0903 Hotwell Pump "B" tripped on neutral overcurrent. At 0911 Both # 7 Heater Drain Tank Pumps tripped. Per AOP-S.04 started decreasing unit power. At 0918 Main Feedwater Pump "A" tripped initiating Unit Runback Balance of Plant (BOP). At 0918 Manual Reactor Trip. Due to both Main Feedwater Pump's rupture discs blown plant is using Steam Generator Atmospheric Relief Valves to cool the plant and maintain a Hot Standby condition. No leaking steam generator tubes. The electrical grid is stable and the emergency diesel generators are fully operable if needed. Sequoyah Unit 1 is in coastdown. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-03-10
39652 | 0 | OAKWOOD HOSPITAL |  |  |  |  | 2003-03-10 10:00 | 2003-03-10 11:43 | 2003-03-10 | MEDICAL EVENT TO AN UNINTENDED SITE At 1000 EST on 03/10/03 it was discovered that a patient at Oakwood Hospital located in Dearborn, MI had implanted 42 Iodine-125 seeds into his bulb of urethra instead of his prostrate. The urologist had misinterpreted the ultrasound scan. The total activity of the Iodine-125 seeds was 14.2 millicuries, each seed was 0.338 millicuries. The patient and his Medical Doctor have been notified of the error. No side affects to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2003-03-10
39651 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-03-10 00:12 | 2003-03-10 03:45 | 2003-03-10 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON GENERATOR DIFFERENTIAL RELAY ACTUATION "At 0012 EST on March 10, 2003, with Watts Bar Unit 1 in Mode 1 at 100% power, the reactor tripped due to an automatic signal. All plant safety systems were in service at the time to the trip, except for the 2B-B diesel generator which was out of service for scheduled maintenance, and all [safety systems] responded as designed. All control rods inserted as required and the Auxiliary Feedwater System [AFW] initiated as expected. "The reactor trip resulted from a turbine trip signal that was generated as a result of a main generator/transformer differential electrical relay actuation. The plant is currently stable in Mode 3 and will remain in this Mode until completion of the investigation." AFW was removed from operation and the main feed pumps have resumed normal feed to the Steam Generators. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-03-10
39650 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-03-09 20:47 | 2003-03-10 00:46 | 2003-03-10 | SAFETY INJECTION SYSTEM ACTUATION AND CAUSE UNDER INVESTIGATION "At 20:47 on 3/9/03, Unit 2 experienced a Safety Injection while the plant was stable at NOP(2235 psig)/NOT (567 degrees) in Mode 3. All systems actuated as designed. An operator was operating the 'B' S/G PORV shortly before the event occurred. All MSIVs were closed for ongoing work on the main turbine. The Sequence of events report showed all 3 channels of steam pressure spiking low on the 'B' Steam Generator as the cause of the event. Initial look at trends on the integrated computer system showed [that] steam pressure channels did not lower to a point to cause the safety injection. An Event Review Team is being formed to investigate this event. "A Reactor Coolant System PORV opened due to high pressure when the Spray valves closed due to the Instrument Air isolation (due to phase 'A') with the Pressurizer Heaters in manual. The Pressurizer heaters were secured and Reactor coolant System pressure stabilized. All ESF systems actuated as designed. The following systems actuated: Auxiliary Feedwater, Safety Injection, Phase 'A', Control Room Envelope and Fuel Handling Building HVAC systems, Essential Cooling Water, Component Cooling Water, Emergency Diesel Generators and ESF sequencers." There was no safety injection since pressure was maintained above 2199 psi during the transient (Hi Head is 1700 psi). Heat removal is being performed through S/G PORVs and Unit 2 is currently stable at Mode 3. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-03-10
39649 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-08 22:18 | 2003-03-09 12:08 | 2003-03-09 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY FOR GREATER THAN 8 HOURS "On 3/9/03 the Main Control Room was notified that the Unit 2 SPDS [Safety Parameter Display System] computer was not updating properly. A review into the history identified that the SPDS computer had stopped updating at 22:18 on 3/8/03. The computer group attempted to reset the SPDS computer to correct the condition. The reset was successful and all indication returned to normal. "Since the Unit 2 SPDS computer system was unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and therefore reportable under 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-03-09
39648 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-09 03:12 | 2003-03-09 04:08 | 2003-03-09 | OFFSITE NOTIFICATION "On 3/9/03 at 0140 the Main Control Room was notified that an ambulance was requested at the site. A contract pipe fitter working in Primary Containment on unit 2 experienced heat stress. Site EMT's stabilized the individual and he was transported to a local hospital for treatment. The individual was not contaminated. The ambulance left site at 0216, and the Pennsylvania Emergency Management Agency was notified at 0312. Due to notification to another government agency, this event is reportable under 10CFR50.72(b)(2)(xi)." The Licensee notified the State of Pennsylvania and will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-09
39647 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-07 23:55 | 2003-03-08 01:58 | 2003-04-15 | AUTOMATIC DIESEL ACTUATION CAUSED BY LOSS OF GENERATION EXCITATION TRIP "During planned Unit Two manual scram in preparation for refueling outage, all four Emergency Diesel Generators received an auto start signal. Auto start signal was generated from a Primary Generator Lockout caused by a Loss of Generator ExcitatIon Trip. A 1/2 Group 1 signal was also received during the shutdown due to a steam flow trip unit failure, which has been repaired. All other systems operated as designed, scram actions completed, plant stable. The Loss of Excitation Trip should have been blocked by main generator PCB openings. Investigation currently underway to determine cause of Loss of Excitation Trip malfunction." There was no loss of power. The busses were not loaded after all four diesels started. The diesels operated normally and have been returned to a standby lineup. All other systems operated as required. The Licensee notified the NRC Resident Inspector. ****RETRACTION on 04/15/03 at 1320 EDT by Charles Elberfeld taken by MacKinnon**** Upon further evaluation, it has been determined that the signal that started the EDGs did not meet the definition of a valid signal and so the reporting criterion contained in 10 CFR 50.72 (b)(3)(iv)(A) is not applicable to the condition reported on March 8, 2003 (Event Number 39647). Valid actuations of the EDGs are the result of loss of coolant accident signals (from either Unit 1 or 2) or as the result of emergency bus degraded voltage or undervoltage signals. Therefore, the actuation of the EDGs reported as a valid actuation in accordance with 10 CFR 50.72 (b)(3)(iv)(A) is retracted and is being reported, as allowed by 10 CFR 50.73 (a), in this telephone notification in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as an invalid actuation. EDGs 1, 2, 3, and 4 automatically started and functioned successfully. Because electrical power was never lost to the emergency busses and none of the EDGs loaded to their respective emergency busses, the actuations were considered to be partial. Safety significance is considered to be minimal. Emergency Diesel Generators started and operated normally. Electrical power was never lost to the emergency busses. Power Circuit Breaker trip operating mechanism assembly was replaced. NRC R2DO (Tom Decker) notified. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-03-08
39646 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2003-03-07 13:31 | 2003-03-07 22:06 | 2003-03-07 | OPEN AUXILIARY BUILDING DOOR COULD HAVE CAUSED A LOSS OF SECONDARY CONTAINMENT FUNCTION "At 1622 CST on 3/7/03, a Condition Report was written to identify that Auxiliary Building door PW-95-02 was open because a door assist device malfunction prevented closure of the door. This condition existed from 1331 until 1449 on 3/7/03. "This condition could have resulted in a loss of function of the Secondary Containment since Standby Gas Treatment system may not have been able to draw down pressure in the Auxiliary Building to the required vacuum." The licensee notified the NRC Resident Inspector. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2003-03-07
39645 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2003-03-07 20:49 | 2003-03-07 21:32 | 2003-03-31 | UNUSUAL EVENT DECLARED DUE TO INABILITY TO REACH HOT SHUTDOWN WITHIN TECH SPEC ACTION STATEMENT TIME LIMIT The licensee declared an unusual event at 2049 EST due to the inability to reach Mode 4 within the Technical Specification action statement time limit of 2049 EST for charging pumps inoperable. The charging pumps were declared inoperable as a result of system complications associated with the reactor trip and charging system leakage occurring at 1439 EST 3/7/03 (see Event # 39644). The licensee notified the NRC Resident Inspector. * * * UPDATE 0420EST ON 3/8/03 FROM ROBERT MALONEY TO S.SANDIN * * * The licensee terminated the Unusual Event at 0146EST after Unit 2 entered mode 4. The licensee informed state/local agencies and the NRC resident inspector. Notified R1DO(Shanbaky), EO(Grimes) and FEMA(Stinedurf). * * * UPDATE 0944EST ON 3/31/03 FROM STEPHEN BAKER TO S. SANDIN * * * The following information was submitted as an update: "On March 7, 2003, Millstone Unit No. 2 made a 1-hour report of an Unusual Event declared due to an inability to reach hot shutdown within Tech Spec action statement time limit (Event no. 39645). This notification was made because the required Mode was not reached within the required Tech Spec action time. Three charging pumps were declared inoperable resulting in an entry into TS 3.0.3. The appropriate Mode could not be reached within the time prescribed by the TS due to the inability of the charging system to supply adequate makeup to the RCS through the normal flow path. An alternate alignment was established via HPSI, The limited rate of makeup via this alternate path prevented the plant from reaching Mode 4 within the allowed outage time. "The criteria for deviation from plant Tech Specs was inappropriately checked off as it was interpreted to mean a violation of plant Tech Specs. Criterion 10CFR50.72(b)(1) 'deviation from the plant's Tech Specs pursuant to § 50.54(x)' did not apply. "Additionally, criterion 10CFR50.72(b)(3)(v)(A), loss of safety function, did apply and this event should have been reported under this criterion since three charging pumps were declared inoperable." The licensee will inform the NRC resident inspector. Notified R1DO (Bellamy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) |  | 0 | 2003-03-07
39644 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2003-03-07 14:39 | 2003-03-07 15:46 | 2003-03-07 | PLANT DECLARED UNUSUAL EVENT DUE TO REACTOR TRIP WITH LEAKAGE FROM CHARGING SYSTEM A reactor automatic trip was received at 1439 EST. The cause of the trip is unknown and investigation continues, although reactor protection system testing was in progress at the time of the trip. All systems responded normally with the exception of the charging system. The licensee declared an unusual event at 1516 EST due to charging pump discharge relief valves lifting thereby creating leakage into the auxiliary building. Preliminarily, the cause of the relief valve discharge was blockage in the normal charging line downstream. Charging flow was reestablished via the alternate flowpath. A minimal radioactive release from the auxiliary building ventilation resulted from the charging system leakage. The NRC Resident Inspector was notified. State and local officials were notified and the licensee issued a press release. * * * UPDATE 0420EST ON 3/8/03 FROM ROBERT MALONEY TO S.SANDIN * * * The licensee terminated the Unusual Event at 0146EST after Unit 2 entered mode 4. The licensee informed state/local agencies and the NRC resident inspector. Notified R1DO(Shanbaky), EO(Grimes) and FEMA(Stinedurf). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-03-07
39643 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2003-03-07 14:40 | 2003-03-07 19:17 | 2003-03-10 | 1- HOUR SAFEGUARD REPORT Discovery of criminal act involving individual granted access to the site. Immediate compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. **** RETRACTION ON 03/10/03 AT 1555 ET BY TOM VEITCH TAKEN BY MACKINNON **** After additional review, it was determined that drugs do not fall into the classification of contraband and thus need not be reported under this criterion. R3DO (Ken O'Brien) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 83 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-03-07
39642 | 0 | LOUISIANA DEPT ENV QUALITY |  |  |  |  | 2003-02-14 | 2003-03-06 15:31 | 2003-03-06 | IRRETRIEVABLE SEALED SOURCE "An NWA tool with a 2 Ci [Curie] source of Cs-137 and a 4 Ci source of Am241Be were lost down [a] hole at 11540 feet on February 14, 2003. Attempts were made until February 20, 2003 to retrieve the tool, but they were unsuccessful. The well was back filled with 500 ft of cement to a depth of 10881 ft. DEQ is currently waiting for the written report for additional information." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-03-11
39641 | 0 | LOUISIANA DEPT ENV QUALITY |  |  |  |  | 2003-02-17 | 2003-03-06 15:30 | 2003-03-06 | IRRETRIEVABLE SEALED SOURCE "A 3 Ci [Curie] sealed source of AmBe 241 was lost down [a] hole on February 17, 2003 at a depth of 6600 ft. Attempts were made to retrieve the source but they were unsuccessful. A vented bridge plug was set at 5335 ft and low permeability cement was dumped until 5300 ft. Additional information will be sent at a later date." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-03-11
39640 | 0 | LOUISIANA DEPT ENV QUALITY |  |  |  |  | 2003-03-05 | 2003-03-06 15:29 | 2003-03-06 | IRRETRIEVABLE SEALED SOURCE "Computalog was performing analysis of the amount of petroleum in the Strategic Petroleum Reserve salt dome in Hackberry, LA. The tool hung up on the casing near the top and fell to the bottom. The source was a 172 mCi [millicurie] source of Cs- 137 and it fell to a depth of 4000 ft. Attempts were not made to retrieve the tool because the dome is so wide at the bottom. DEQ is waiting on the written report for additional information." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-03-11
39639 | 0 | HOLTEC INTERNATIONAL |  |  |  |  | 2003-01-03 | 2003-03-06 14:10 | 2003-03-06 | PART 21 NOTIFICATION - AALBORG FLOW METERS Holtec International reports a potential defect in Aalborg model GFM671S mass flow rate meters. The instruments are used to verify the correct amount of helium is backfilled into dry spent fuel storage canisters. These instruments were never used on a Holtec cask system containing spent nuclear fuel because the problem was discovered during the preparatory phase before fuel loading. Four meters were purchased for use at the Trojan nuclear plant to measure the amount of helium gas injected into a loaded Holtec dry spent fuel Multipurpose Canister (MPC). It was determined that erroneous data was coming from the flow rate meters. It was determined by Aalborg that the published correction factors for helium/nitrogen were incorrect for this model flow meter. At the time the discrepant condition was identified, none of the flow meters had been used on an MPC loaded with spent fuel and they were subsequently removed from service until they could be correctly calibrated. Four flow rate meters were procured and delivered to the Trojan nuclear power plant. Three were not used in actual fuel loading activities due to the discovery of the mis-calibration during dry run activities. The fourth flow rate meter has been removed from the site. Aalborg is developing new helium correction factors. In the interim, they have committed to using helium to calibrate all flow meters destined for use in measuring helium. Trojan plant was the first plant where flow rate meters and flow totalizers were to be used to confirm adequate helium backfill in Holtec MPCs loaded with spent fuel. Therefore, no other Holtec client is affected for past loading operations. For future MPC loading operations, Holtec users, as well as other purchasers and licensees are being notified via this report that Aalborg flow meters procured for use in important-to-safety activities may not be calibrated correctly and that certain catalogue correction factors have been determined to be incorrect. The calibration of Aalborg flow meters should be confirmed prior to use in important-to-safety activities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2003-03-06
39638 | 0 | STATE OF WV RAD HEALTH PROGRAM |  |  |  |  | 2003-03-06 01:15 | 2003-03-06 01:24 | 2003-03-06 | AUTOMOBILE ACCIDENT INVOLVING RADIOGRAPHY SOURCE At 0124 EST on 3/06/2003, NRC Headquarters was contacted by State of WV Radiation Health Program that an automobile/truck accident had occurred in Parkersburg, West Virginia that involved a Iridium-192 radiography source. Local HazMat responders do not have radiation monitoring equipment. Currently, LLEA is in contact with Camden-Clark Hospital to obtain proper radiation monitoring equipment to determine if packaging is intact. (It was determined that Camden-Clark is unable to respond). Vehicle is located in local towing impound yard. West Virginia will be responding in the morning to perform surveys. Notified NMSS EO (Reamer), R2DO (Evans), DIRO Mgr. (Holonich), NRC Transportation (Osgood), DOT (LT. (jg) Johnson) and DOE (Gibson). * * * * UPDATE FROM D. HILL TO M. RIPLEY AT 1250 EST 3/6/03 * * * The State of WV Radiation Health Program completed an inspection and radiation survey. The Iridium-192 radiography source was found intact. Radiation levels were normal and there was no spread of radioactivity. The radiography equipment was released to the licensee for transport back to the work site where it was being used. Notified NMSS EO (Reamer), R2DO (Evans & Pelchat), DIRO Mgr. (Holonich), DOT-NRC Watch Officer, DOT (LT. Higgins), DOE Watch Officer, NTSB (Belchius), USCG (LT. Gross), EPA R3 (Minnick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | WV | TRA | [5 empty] | 0 | 2003-03-06
39637 | 0 | 3M CORPORATION |  |  |  |  | 2003-03-04 | 2003-03-04 14:50 | 2003-03-04 | LOST OR STOLEN, ANTI-STATIC, POLONIUM 210 SOURCE A 0.3 millicurie, Polonium 210 source, nuclear static eliminator, model P2001, serial number A2BG425 was reported as not received being by the recipient. The source is used in a laboratory balance application to eliminate static charge and is about 2 inches long. The original source strength was 4.5 millicuries (8/2002) and 0.3 millicuries as of 3/2003. The shipment was made on January 6, 2003 from 3M Corporation, St Paul, MN to the manufacturer of the static eliminator, NRD, Grand Island, NY. This shipment consisted of 42 sources, in a common box, of which the recipient reported receipt of only 41 sources. A extensive search has been conducted for the missing source by the sender and recipient with negative results. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-03-04
39636 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2003-03-04 03:11 | 2003-03-04 12:02 | 2003-03-04 | AUTOMATIC START OF THE DIV 1 DIESEL GENERATOR COOLING WATER PUMP "ON MARCH 3rd, 2003, AT 0311 HOURS, WITH UNIT 2 IN MODE 1 (RUN), THE DIVISION 1, DIESEL GENERATOR COOLING WATER PUMP (DGCWP), WHICH PROVIDES THE EMERGENCY SERVICE WATER TO THE RESIDUAL HEAT REMOVAL (RHR) ROOM COOLERS (VY), AUTOMATICALLY STARTED DURING THE PERFORMANCE OF A MAINTENANCE ACTIVITY ASSOCIATED WITH THE UNIT 2 RESIDUAL HEAT REMOVAL (RHR) CORNER ROOM FAN (VY) BREAKER INSPECTION. THE APPARENT CAUSE OF THE AUTO START WAS THE ACTUATION OF THE AUXILIARY CONTACTS IN THE FAN BREAKER CUBICLE BY THE TECHNICIAN AS PART OF THE MAINTENANCE ACTIVITY. THE APPARENT CAUSE WAS THE RESULT OF AN INADEQUATE REVIEW OF THE ELECTRICAL RELAY LOGIC DURING DEVELOPMENT OF THE INSTRUCTION FOR THE MAINTENANCE ACTIVITY. THIS ACTUATION OF THE AUXILIARY CONTACTS PROVIDED AN INVALID SIGNAL THAT CAUSED THE DIVISION 1 DIESEL GENERATOR COOLING WATER PUMP TO LOGICALLY BELIEVE THE 2A RHR PUMP ROOM COOLING FAN WAS RUNNING, THEREBY GENERATING AN AUTO START SIGNAL. THIS INVALID BREAKER CONTACT CLOSURE RESULTED IN THE AUTOMATIC ACTUATION OF THE DIVISION 1 DGCWP. THIS SYSTEM ACTUATION IS REPORTABLE UNDER 10CFR50.73 (a) (2) (iv) (A). "THE DIVISION 1 DIESEL GENERATOR COOLING WATER PUMP RESPONDED SATISFACTORILY. "THIS REPORT IS BEING MADE IN ACCORDANCE WITH 10CFR50.73 (a) (1), WHICH STATES THAT IN THE CASE OF AN INVALID ACTUATION REPORTED UNDER 10CFR50 .73 (a) (2) (iv), OTHER THAN AN ACTUATION OF THE REACTOR PROTECTION SYSTEM (RPS) WHEN THE REACTOR IS CRITICAL, THE LICENSEE MAY PROVIDE A TELEPHONE NOTIFICATION TO THE NRC OPERATIONS CENTER WITHIN 60 DAYS AFTER DISCOVERY OF THE EVENT INSTEAD OF SUBMITTING A WRITTEN LICENSEE EVENT REPORT (LER)." The licensee has notified NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-03-04
39635 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-03-04 08:54 | 2003-03-04 10:33 | 2003-03-04 | THROUGH WALL LEAKAGE IDENTIFIED ON VESSEL HEAD PENETRATION A through wall leak was noted during a VT-2 inspection of reactor vessel head penetration "50". This condition has been assessed as a degradation of a principle safety barrier. Unit 1 is in a maintenance and refueling outage and is replacing the reactor vessel head during this outage. The old head was visually inspected at penetration "50" to followup on inspection results from a previous outage in 2001. The NRC Licensee was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-03-04
39634 | 0 | GENERAL ELECTRIC |  |  |  |  | 2003-03-03 | 2003-03-03 20:51 | 2003-06-06 | PART 21 NOTIFICATION - FUEL CHANNEL BOW GE Nuclear reports a new phenomenon that causes fuel channel bow. "Shadow Corrosion" is the hydrogen-induced growth of the channel wall closest to the control blade when the fuel channel is in a highly controlled location during its initial fuel cycle. The hydrogen-induced growth leads to channel bowing toward the control blade late in life. This condition is believed to be most significant for BWR/6 plants. There are two effects of the new phenomenon: 1. It is not accounted for by thermal limit calculations 2. The bias towards the control blade can lead to control rod-fuel channel interference. To mitigate the impact on thermal limits, an interim penalty of .02 has been applied to the Operating Limit Minimum Critical Power Ratio for all BWR/6's. In the long-term, updated channel bow data will be used in the approved fuel licensing models and this data will be incorporated into future reload licensing analyses. Recommended actions for non-BWR/6 plants are expected by June 6, 2003. Concerns related to the control rod-fuel channel interference include: 1) friction that could cause fuel bundle lift, 2) transfer of forces to reactor internals causing higher stresses, and 3) slower scram speeds. There have been no interim actions designated to mitigate these effects, but recommendation for a surveillance to help detect control rod-fuel channel interference is expected by April 28, 2003. Affected plants at present are all BWR/6's. Potentially affected plants are all BWR's, with the exception of Columbia Generating Station. * * * UPDATE ON 6/6/03 AT 1821EDT FROM JASON POST TO GERRY WAIG * * * "The NRC was previously notified of a Reportable Condition for fuel thermal limits calculations on BWR/6 plants. Subsequent analysis has shown that it is not a reportable condition on BWR/2-5 plants. This completes the commitment made in the reference letter to evaluate the impact on BWR/2-5 thermal limits calculations by June 6, 2003." Notified (via email) R1DO (James Linville), R2DO ( Kerry Landis), R3DO (Ken O'Brien), R4DO (Dave Loveless), NRR (David Matthews). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-03-03
39633 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-03 | 2003-03-03 20:38 | 2003-03-03 | OFFSITE NOTIFICATION OF 2 CONTRACT EMPLOYEES REPORTING TO THE SITE WITH RADIOACTIVE CONTAMINATION "Two contract General Electric employees reported to the plant from a foreign nuclear power plant with levels of radioactive contamination which alarmed the plant's portal monitors while exiting the protected area. The radionuclides identified were Co-60 and Mn-54. These 2 personnel had not entered the RCA at Susquehanna. Additional follow-up radiological surveys are in progress. "The Resident NRC Inspector and Pennsylvania Department of Environmental Protection have been notified. "A press release is planned once the additional surveys are complete." | 100 | 85 | 0 | 100 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-03
39632 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-03-03 | 2003-03-03 14:44 | 2003-03-03 | RPS ACTUATION WHILE CRITICAL "Unit 2 Reactor SCRAM occurred during scheduled down power associated with 2R07 activities. The Reactor SCRAM occurred as a result of an RPS actuation following a manual turbine trip due to elevated vibration levels. All systems actuated as designed. This report is being made pursuant to 50. 72(b)(2)(iv)(B) due to the actuation of the Reactor Protection System (RPS). Scheduled 2R07 activities continue." All rods inserted normally. All systems functioned as designed. There was nothing unusual or not understood. Decay heat removal method will be to the main condenser followed by establishing shutdown cooling with the RHR system. | 0 | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-03-03
39631 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-03-02 14:30 | 2003-03-02 16:00 | 2003-12-31 | OFFSITE NOTIFICATION TO STATE AGENCY OF EXPIRED GREEN SEA TURTLE FOUND AT BARRIER NET "NRC notification [is] being made due to state notification to [the] Florida Wildlife Commission regarding a Green Sea Turtle found dead at barrier net pursuant to 10 CFR 50.72(b)(2)(xi)." The turtle was found on the surface at the barrier net with no injuries or abnormalities except for fresh cuts common for turtles coming through pipes. The cause of death is unknown at this time. A necropsy is planned. The NRC Resident Inspector will be notified by the licensee. * * * UPDATE ON 3/15/03 @ 1033 EST FROM TEREZAKIS TO CROUCH * * * "On 3-15-03, a green sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 0920 EST. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC." The NRC Resident Inspector will be notified by the licensee. * * * UPDATE ON 3/19/03 AT 1222 EST FROM E. SUMNER TO RIPLEY * * * "On 03/19/03 @ 1105 hrs., one loggerhead turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injury to the turtle is not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1115 EST." The NRC Resident Inspector was notified. * * * UPDATED ON 3/31/03 AT 1159 EST FROM W.L. PARK TO A. COSTA * * * "On 3-31-03 [1105 EST], a loggerhead sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1105 EST. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC." The NRC Resident Inspector will be notified. * * * UPDATE 1235EST ON 4/9/03 FROM ANDY TEREZAKIS TO S.SANDIN * * * "On 4-9-03, a loggerhead sea turtle was retrieved from the plant's Intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1100 EST. This non-emergency notification is being made pursuant to 10CFR50.72(b)(2)(xi) due to the notification of FWCC." The licensee informed the NRC resident inspector. Notified R2DO(Landis). *** UPDATE ON 5/2/03 AT 1826 FROM S. OEHRLE TO A. COSTA *** "On 5/2/03, a green sea turtle was retrieved from the intake canal. The turtle required rehabilitation. The injuries were not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission was notified at 1445 EDT. This non-emergency notification is being made pursuant to 10 CFR 50.72 (b)(2)(xi) due to offsite notification." The Licensee will notify the NRC Resident Inspector. Notified R2DO (Munday). **** update on 05/24/03 at 1417 EDT FROM JOE HESSLING TO JOHN MACKINNON **** "On 5-24-03, a loggerhead sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The turtle was very underweight and lethargic, no injuries or anomalies noted. Turtle's condition is not causal to plant operation. Per the plant's turtle permit the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1345 EDT. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC. NRC R2DO (TOM DECKER) notified. The NRC Resident Inspector was by notified of this event by the licensee. ****UPDATE ON 5/27/03 AT 10:49 FROM HESSLING TO LAURA**** "On 5-27-03, a loggerhead sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The turtle was underweight, and missing lower posterior marginals on left side. Turtle's injuries are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 0850 EDT. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC." Notified R2DO (T. Decker) * * * UPDATE ON 06/17/03 AT 12:45 EDT FROM CALVIN WARD TO ARLON COSTA * * * "At approximately 12:45 p.m. on 6/17/03 a loggerhead turtle was rescued from the St. Lucie Plant intake canal. The turtle was injured and will be transported to the State authorized sea turtle rehabilitation facility. The Florida Dept. of Environmental Protection (FDEP) was notified at 1:09 p.m. as required by the St. Lucie Plant Sea Turtle Permit - see the attached sea turtle stranding report (1 page). "Notification to the state government agency requires a four (4) Hr. Non-Emergency Notification to the NRC per 10 CFR 50.72(b)(2)(xi). There were no unusual plant evolutions in progress which may have contributed to this event." The licensee notified the NRC Resident Inspector. Notified R2DO (L. Wert). * * * UPDATE 0605 EDT ON 6/26/03 FROM STEVE MERRILL TO S. SANDIN * * * The licensee was informed by the FWCC that the green sea turtle requiring rehabilitation which was retrieved from the plant's intake canal on 3/15/03 had expired within 10 days of removal. Consequently, the licensee is updating their 3/15/03 report to include this additional information. The licensee will inform the NRC Resident Inspector. Notified R2DO(C. Ogle). * * * UPDATE 1506 EDT ON 07/01/03 FROM CALVIN WARD TO GOTT * * * On 04/02/03, a green sea turtle was retrieved from the intake canal. The turtle required rehabilitation. The injuries were not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission was notified. This non-emergency notification is being made pursuant to 10 CFR 50.72 (b)(2)(xi) due to offsite notification. On 07/01/03 licensee QA discovered that the injury had occurred and that the NRC had not been notified within the 4 hours. The failure to report the event within the regulatory time is being investigated and has been entered into the stations corrective action program. The licensee notified the NRC Resident Inspector. Notified R2DO (Munday) * * * UPDATE 1750 EDT ON 07/07/03 FROM JOE HESSLING TO MACKINNON * * * On 07/07/03, a Loggerhead sea turtle was retrieved from the plants' intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's Turtle permit, the Florida Fish and Wildlife Conversation Commission (FWCC) was notified at 1715 EDT. This non-emergency is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC. The licensee notified the NRC Resident Inspector. Notified R2DO (Munday). * * * UPDATE ON 07/25/03 @ 1510 BY CALVIN WORD TO STEVE SANDIN * * * On 7/25/03, a sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC. The licensee notified the NRC Resident Inspector and other Government Agencies Reg 2 RDO(Anne Boland) was informed * * * UPDATE ON 08/06/03 AT 1611 BY ALAN HALL TO ARLON COSTA * * * "On 08/06/03 [at 1410], a sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC. Stranding Report copy attached." The licensee will notify the NRC Resident Inspector. Notified R2DO (Stephen Cahill). * * * UPDATE ON 08/19/03 AT 1328 EDT BY JOHN BRADY TO JOHN MACKINNON * * * On 08/19/03 at 1218 EDT, a Loggerhead sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's permit, the Florida Wildlife Conservation Commission (FWCC) was notified. NRC Resident Inspector was notified. R2DO (Ernstes) notified. *****UPDATE ON 10/07/03 AT 0910 FROM MOTHENA TO LAURA***** "On 10/7/03, at 08:30, a Dead Green sea turtle was retrieved from the plant's intake canal. There were no abnormalities or injuries found. The death does not appear to be causal to plant operation. The turtle will be sent to veterinarian for necropsy. Per the plant's Turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 0849 EDT. This non-emergency notification is being made pursuant to 10CFR 50.72(b)(2)(xi) due to the notification of FWCC." Notified R2DO (K. Landis) and the licensee notified the NRC Resident Inspector. * * * UPDATE ON 12/31/03 BY CHRISTIANSEN TO MACKINNON * * * "On 12/31/03, a sea turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified. This non-emergency notification is being made pursuant to 10 CFR 50,72(b)(2)(xi) due to the notification of FWCC." The NRC Resident Inspector will be informed. Notified Reg 2 RDO(Bonser) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-03-02
39630 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2003-03-02 03:35 | 2003-03-02 10:43 | 2003-03-07 | PRIMARY CONTAINMENT MEASURED LEAKAGE EXCEEDS THE ALLOWED LEAKAGE. During routine scheduled LLRT (Local Leak Rate Testing) of Penetration X-214, HPCI (High Pressure Coolant Injection) Exhaust Discharge to the Torus, leakage was unable to be quantified. Additionally, of the two isolation check valves in the line, the licensee could not determine which one was leaking. As such, Primary Containment Allowed Leakage (La) is unable to be verified to be less than allowed. The plant was in Mode 4 (Cold S/D) for a scheduled refueling outage with temperature being maintained between 130 and 145 degrees Fahrenheit and Primary Containment not required at the time of discovery. The plant will remain in cold shutdown until repairs are completed. The NRC Resident Inspector was notified. * * * * RETRACTION RECEIVED AT 1326 EST ON 03/07/03 BY BLAIR TO RIPLEY * * * * "On 3/2/03 at 0943 CST, Cooper Nuclear Station made an 8 hour 50.72 non-emergency notification to the NRC. This was done due to the failure of Local Leak Rate Testing (LLRT) involving the High Pressure Coolant Injection (HPCI) exhaust discharge to the Suppression Chamber. Leakage was unable to be quantified. Additionally, of the two isolation check valves in the line, testing was unable to determine which one was leaking. "Based on indications of leakage during the LLRT, maintenance activities were started on one of the valves (HPCI-15CV). Upon removal of the HPCI-15CV bonnet it was noticed that the valve was not properly seated. Engineering is continuing to evaluate this condition. To facilitate continuing troubleshooting HPCI-15CV was manually closed by pushing the disk into the valve seat. The bonnet was re-installed and the LLRT was repeated. The other check valve in this line (HPCI-44) was not touched or manipulated during the period of time between successive LLRT's. "The results of the repeat LLRT were well within acceptance criteria limits demonstrating that HPCI-44 was properly performing its containment isolation function. Since HPCI-44 was working properly, the conditions that required an 8 hour 50.72 notification no longer apply. The penetration was always capable of performing the containment isolation function. "The NRC Resident Inspector was notified." Notified R4 DO (D. Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-03-02
39629 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-03-01 01:54 | 2003-03-01 05:39 | 2003-03-01 | REACTOR MANUALLY TRIPPED FROM 100% POWER The Operators manually trip the reactor from 100% power following a loss of condensate flow in the secondary system. The cause is unknown and being investigated. All rods fully inserted and no relief valves lifted. However, the auxiliary feedwater and feedwater actuations were received following the trip as expected. The reactor is in hot standby. The NRC resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-03-01
39628 | 0 | THOMAS JEFFERSON UNIV HOSPITAL |  |  |  |  | 2003-01-28 13:00 | 2003-02-28 15:52 | 2003-02-28 | 1.3 MILLICURIES SULPHUR-35 SOURCE INADVERTENTLY DISCARDED AS REFUSE On 1/20/03 a package was delivered from PerkinElmer Lifesciences located in Boston, MA to the Thomas Jefferson University Hospital. The package included two (2) medical isotopes used in research; 1.3 millicuries Sulphur-35 (Half-life 87.4 days) and 250 microcuries Tritiated Thymidine. The package was shipped as excepted quantity not subject to external labeling. A lab worker sometime between 1/23 and 1/24 discarded the package containing the two sources as trash which was collected on 1/27 at approximately 0500 hours and taken to the landfill. The licensee conducted interviews emphasizing prompt handling, good communication and individual responsibility to prevent recurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-02-28
39627 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-02-28 08:57 | 2003-02-28 14:10 | 2003-02-28 | LESS THAN THE REQUIRED NUMBER OF OPERABLE EMERGENCY DIESEL GENERATORS "While the plant was in cold shutdown, the division number 2 onsite emergency power (diesel generator) was made inoperable when it was discovered that the time delay relay, which energizes to cause the associated room cooling system to start when the diesel generator automatically initiates or the temperature in the room reaches 104 degrees F, was not replaced before exceeding it's analyzed service life. The division number 1 onsite emergency power (diesel generator) was already inoperable when the fuel oil transfer pump flow was found to be less than required while performing a technical specification surveillance test. "Technical Specification Limiting Condition of Operation (LCO) [3.8.2] for AC Sources during shutdown was entered. This LCO is required to be entered when one diesel generator is not capable of supplying one division of the onsite Class 1E AC electrical power distribution subsystem(s) to support equipment required to be operable. The following actions were immediately taken in accordance with this LCO and will remain in place until the LCO can be met: 1. Core alterations are not allowed. 2. Movement of irradiated fuel assemblies in secondary containment is not allowed. 3. Operations with the potential to drain the reactor vessel are not allowed. 4. Replacement of the subject relay was initiated. "No fuel movement, core alterations or operations with the potential to drain the reactor vessel were in progress. "All offsite power sources are available and operable. No maintenance will be conducted which could potentially affect the availability of these offsite sources or the associated distribution systems." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-02-28
39626 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2003-02-05 15:00 | 2003-02-28 13:46 | 2003-02-28 | AGREEMENT STATE REPORT- RECEIPT OF CONTAMINATED PACKAGES The following is taken from an email received from the MA Dept. of Public Health, Radiation Control Program: "On Wednesday, February 5, 2003, it was discovered that a routine wipe of an incoming 20 millicurie (0.740 GBq) Iron-55 source ordered from AEA Technology QSA, Inc. was contaminated. The wipe was sent off for analysis. On Friday, February 14, the wipe was reported to contain 213.7 nanocuries (7.91kBq) of Iron-55 contamination. The distributor, AEA Technology QSA, Inc., was notified of the leaking source as was the Radiation Control Program of the Massachusetts Department of Public Health. "In the interim, on Monday, February 24, 2003, another incoming Iron-55 leaking source from the same lot number was discovered by Niton Corporation at approximately 5:00 p.m. The wipe has been sent to an authorized consultant for further analysis. The level of contamination of the second source has not been reported to the Agency at the time of this report. Again, the manufacturer/distributor, AEA Technology QSA, Inc., was notified of the leaking source as was the Radiation Control Program. "An investigation into these leaking source events has been initiated by the Radiation Control Program." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2003-03-05
39625 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-02-27 19:45 | 2003-02-27 23:37 | 2003-02-27 | UNIT COMMENCED TECH SPEC REQUIRED SHUTDOWN DUE TO INOPERABLE EDG "This ENS notification is made to report initiation of a plant shutdown required by the Columbia Generating Station Technical Specifications (TS's) pursuant to 10CFR 50.72(b)(2)(i). This plant shutdown was initiated due to the inability to restore the Division I Emergency Diesel Generator (DG-1) to operable status prior to exceeding the expiration of the Completion Time of TS LCO 3.8.1, Condition B.4. Columbia Generating Station was granted enforcement discretion (NOED 03-4-001) from compliance with the completion time requirements of TS 3.8.1, Condition B.4, for an eleven-day period beginning on February 16, 2003 and ending February 27, 2003 at 9 p.m. (PST). The enforcement discretion was granted to allow the replacement of a degraded DG-1 generator bearing. Both generator bearings were replaced. However, during post maintenance tests to validate operability of DG-1, vibration levels for the new bearings showed evidence of an increasing trend. Based on this, DG-1 is currently considered inoperable. Even though the current vibration levels are very low, the plant has decided further testing and diagnosis is necessary to support a decision on DG-1 operability. Although the Completion Time of TS 3.8.1, Required Action B.4 expires at 9 p.m., plant shutdown commenced at approximately 7:45 p.m. (PST), on February 27, 2003." The licensee informed the NRC resident inspector. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-02-27
39624 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2003-02-27 17:31 | 2003-02-27 19:50 | 2003-02-27 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "On 02/27/03 at 1731[CST] hours, Point Beach Unit 1 commenced an orderly reactor shutdown in response to TS [Technical Specifications] Action Statement 3.6.3.D.1, which requires the unit to be taken to Mode 3 in 6 hours when two containment isolation valves are inoperable for greater than 1 hour. Valves 1SC-953 and 1SC-966B, pressurizer liquid space sampling containment isolation valves, were declared inoperable when leakage was evident past the shut valves. At 1748 hours, the pressurizer liquid space penetration flow path was verified as being isolated by shutting manual valve 1SC-952. The shutdown was terminated at 1751[CST] hours. "Earlier in the afternoon, it had been reported to the Control Room that the reactor coolant primary sampling containment isolation valves (1SC-955 and 1SC-966C) were leaking through. The penetration flow path for these valves was isolated via shutting valve 1SC-954B. Further investigation revealed that leakage was still present. The leakage was isolated by shutting 1SC-952. "The 1D Pressurizer Heater Bank tripped during attempt to manually energize pressurizer heaters. Minimum required pressurizer heater capacity is maintained. Investigation is in progress." The licensee has notified the NRC Resident Inspector. | 92 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-02-27
39623 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-02-27 13:01 | 2003-02-27 17:15 | 2003-02-27 | AUTOMATIC ACTUATION OF THE #2 EMERGENCY DIESEL GENERATOR "This provides notification of an automatic actuation of the No. 2 Emergency Diesel Generator (EDG) at Beaver Valley Power Station (BVPS) Unit No. 1 "On 2/27/2003 at 1301 hours, BVPS Unit No. 1 was at 58 % power following a startup from a recent forced outage. The 'B' Main Feedwater Pump (MFP) tripped on overcurrent shortly after it was started. Concurrent with the MFP trip, the breaker which feeds the non-safety related 'D' bus from the offsite power source also tripped, de-energizing the 'D' bus. [The 'D' bus supplies power to the 'B' MFP.] The loss of the 'D' bus caused the loss of power to the safety related Emergency 'DF' bus, which caused the No. 2 EDG to start and re-energize the Emergency 'DF' bus with all equipment properly loaded. "Control Room personnel entered Abnormal Operating Procedure 1.36.2, 'Loss of 4KV Emergency Bus.' Reactor Power was manually ramped back to 43 % power in response to this transient. Actions are being taken to re-energize the non-safety related 'D' bus from its offsite source. The EDG remains in operation with no abnormalities. The cause of the 'B' MFP trip is being investigated. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(iv)(A) as an actuation of an emergency diesel generator which is part of the onsite emergency AC electrical power system. The NRC resident has been notified." | 43 | 0 | 0 | 58 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-02-27
39622 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-02-25 17:05 | 2003-02-26 12:12 | 2003-02-26 | OFFSITE NOTIFICATION DUE TO SPILL OF BIOCIDE TREATED FIRE PROTECTION WATER The following information was obtained from the licensee via facsimile: "On 02/25/2003, we received a fire panel alarm for X-04 fire pump run with water flow. The source of leakage was identified as a broken sprinkler (40A1) in the MMO building which is located outside our protected area. The leak was isolated and the [fire protection] system was placed back in standby at 1922 [hrs] that same day. The initial alarm was received at 1705. "On 02/26/2003 at 0915, we notified our contact person (Shannon Kennedy) at the TCEQ [Texas Commission on Environmental Quality] by voice mail. The following release information: "'Based on the level change of our fire protection tank, CPSES [Comanche Peak Steam and Electric Station] released approx[imately] 11,500 gallons of [fire protection] water to the environment. Of that, approx[imately] 8000 - 9000 gallons were discharged to our lake (Squaw Creek Res[ervoir]). The [fire protection] water contained 50 ppm of biocide and had a pH of 8.5. Based on day light visual inspection of our lake, there was no indication of stressed or dead fish. There was no observed environmental impact.'" The NRC Resident Inspector was notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-26
39621 | 0 | US ARMY |  |  |  |  | 2002-12-12 | 2003-02-26 09:54 | 2003-02-26 | CHEMICAL AGENT DETECTOR DISCOVERED MISSING DURING INVENTORY A Chemical Agent Detector, serial #Z03-D-04277 containing 300 microcuries of Americium-241 was discovered missing during a inventory that took place at the US Army Soldiers and Biological/Chemical Command in December 2002. The National Guard initiated an investigation to determine location and cause of the loss of the missing chemical agent detector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | GA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-02-26
39620 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-02-26 00:17 | 2003-02-26 02:05 | 2003-02-26 | PLANT ENTERED A NOUE DUE TO BOTH EMERGENCY DIESEL GENERATORS BEING DECLARED INOPERABLE The licensee declared an unusual event at 0026 CST due to both Emergency Diesel Generators being inoperable resulting in the loss of on-site power capability. At 0017 the "B" Diesel Generator failed to start during an attempt to verify operability as required by TS 3.7.b.2 since the "A" Diesel Generator was out of service for maintenance. They are investigating the cause for the no start of the "B" Diesel Generator. The plant has 6 hrs to be in hot standby and the following 6 hrs to hot shutdown. The NRC Resident Inspector will be notified. State and local agencies were notified and there may be a press release. * * * UPDATE AT 0804 EST ON 2/26/03 FROM JERRY RISTE TO ARLON COSTA * * * "Unusual Event Termination "At 0624 the B emergency diesel generator was returned to service. This exited the condition in EPIP-AD-02, Emergency Class Determination," requiring declaration of an Unusual Event. At 0656 the Unusual Event was terminated." The licensee replaced a faulty speed sensing relay at the "B" EDG relay panel and was subsequently able to re-start the diesel from the control room. The unit is currently stable, holding power at 9.3% and all systems are functioning as required. The licensee notified the NRC Resident Inspector, the State and local authorities. A media/press release was issued by the licensee. Notified R3DO(Kozak), NRR EO (Johnson), DIRO (Hiland) and FEMA (Caldwell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) |  |  | 0 | 2003-02-26
39619 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-02-25 07:50 | 2003-02-25 15:28 | 2003-02-25 | LOSS OF ALL EMERGENCY SIRENS The following information was obtained from the licensee via facsimile: "Indian Point Energy Center (IPEC) Units 2 and 3 is making an eight-hour non-emergency notification in accordance with 10CFR50.72(b)(3)(xiii). "On February 25, 2003, at 0752 hrs [EST] an investigation revealed that the siren control system had apparently become inoperable at approximately 0650 hrs. This condition affected the ability to sound all of the 154 sirens in the four counties of Orange, Putman, Rockland and Westchester for a period of 3 hours and 17 minutes. The siren system was successfully corrected, tested and returned to service at 1016 hrs. "The NRC Resident Inspector was notified of this event." No state, local, or other government agencies were notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-02-25
39618 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-02-25 14:10 | 2003-02-25 15:11 | 2003-02-25 | PHYSICAL SECURITY EVENT Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. Licensee notified NRC Resident Inspector. Refer to HOO log for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-02-25
39617 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2003-02-25 06:15 | 2003-02-25 06:56 | 2003-02-25 | DEGRADED PLANT ACCESS DUE TO CAR ACCIDENT ON SITE ACCESS ROAD "One car accident on access road to plant, however offsite. Degraded emergency responder access." The licensee will notify the NRC Resident Inspector. * * * * RETRACTION RECEIVED AT 1059 EST ON 2/25/03 FROM MCILNAY TO RIPLEY * * * "Upon further review and in accordance with the guidance provided by NUREG-1022, Rev. 2, Section 3.2.13, Loss of Emergency Preparedness Capabilities, Turkey Point is retracting the NRC notification made under 10CFR 50.72(b)(3)(xiii) 0656 on February 25, 2003. As discussed in NUREG-1022, Loss of Offsite Response Capability considerations, NRC notification is required when a major loss of offsite response capability occurs. A major loss of offsite response capability is considered to include loss of plant access for other than a short time for events that causes the access road to be impassible. The Turkey Point access road was limited to one lane (out of a normal two lane access) for 79 minutes, but at all times was accessible." Notified R2 DO (C. Ogle). | 60 | 100 | 0 | 60 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-02-25
39616 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-02-24 15:48 | 2003-02-24 17:02 | 2003-02-25 | UNUSUAL EVENT DUE TO MAIN STEAM LINE ISOLATION WITH SAFETY INJECTION The following information was received from the licensee via facsimile: "At 1548 [EST], on 2/24/03, Beaver Valley Unit 1 experienced an automatic reactor trip and safety injection on low steam line pressure. An automatic main steam line isolation also occurred and all three main steam line isolation valves shut. After the automatic actions occurred, operators noted that all three steam generator pressures appeared normal. Operators were dispatched to investigate in the field and found no indications of a steam leak. "Emergency procedure E-0, Response to Reactor Trip and Safety Injection, was entered at 1548. At 1600, the Shift Manager declared an unusual event. Initial notifications to state and local agencies were complete at 1609. Per procedure E-0, after meeting Safety Injection termination criteria, the Boron Injection Tank was isolated at 1603 and Safety Injection was terminated. "Initial review of computer information revealed that closure of the 'C' main steam isolation valve is the probable cause of the reactor trip, safety injection and main steam isolation. "The gaseous release occurred due to tritium in the secondary and the fact that the turbine driven auxiliary feed pump is in service. No protective action recommendations were made. "All systems and equipment functioned as designed." Technical Support Center is staffed but not activated. All control rods inserted into the core. The electrical grid is stable. Unit 1 is stable. Core cooling is being accomplished via auxiliary feedwater and steam generator atmospheric dump valves. There is previously identified steam generator "B" tube leakage of less than 0.1 gallons per day. The NRC Resident Inspector has been notified. * * * UPDATE AT 1735 EST ON 2/24/03 BY HOWIE CROUCH * * * The licensee has terminated the Unusual Event. They have re-established a pressurizer steam bubble. The plant and electrical grid is stable. Decay heat removal is via auxiliary feedwater and the steam generator atmospheric steam dumps. Notified FEMA, EPA, R1DO (Kinneman), DIRO (Mamish) and NRR EO (Reis). * * * UPDATE AT 0300 EST ON 2/25/03 TO MIKE RIPLEY FROM P. SENA * * * The licensee updated the event classification 10 CFR sections and current plant status. "At 1735 [2/24/03], the Unusual Event was terminated. This was based upon termination of the safety injection, completion of emergency operating procedure actions, and stabilization of plant conditions. This was previously communicated to the NRC Operations Center at 1740. "As of 0245, on 2/25/03, Unit 1 remains in mode 3. Heat removal is via the steam generator atmospheric steam release valves. All main steam isolation valves remain shut as the event investigation continues. The preliminary initiator of the event remains the inadvertent closure of 'C' Main Steam Isolation Valve. The offsite release (due to tritium activity in the secondary) has been calculated and determined to be of minimal/no effect on the public. The projected whole body dose was 5.12E-7 mrem [millirem]. This is equivalent to 3.41 E-6 percent of the yearly Offsite Dose Calculation Manual Limit." Notified FEMA, EPA, R1DO (Kinneman), DIRO (Mamish) and NRR EO (Reis) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 0 | 2003-02-24
39615 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-02-24 14:00 | 2003-02-24 16:46 | 2003-02-24 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was obtained from the Texas Department of Health via facsimile: "Leaking source was discovered during routine servicing of an ASOMA Model 200 analytical instrument, Serial No 4668. The instrument contained a sealed Amersham 13 millicurie, Cm-244 source, Serial No 2695LM, Amersham Model No. CLCL. Last assay date was 08/15/95. Leakage detected was from a routine wipe test which resulted in 0.0077 microcuries of removable contamination. The source is being prepared for return to the manufacturer for evaluation and disposal. All other interior components and exterior surfaces of the instrument were wipe tested and found to have no contamination above the Licensee's minimum detection limit of 360 picocuries." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-02-27
39614 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-02-24 11:17 | 2003-02-24 15:36 | 2003-02-24 | AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL The following information was received from the licensee via facsimile: "At 1117 [CST] on 02/24/2003 with Unit 2 in MODE 3 (Control Rods fully inserted), a full reactor scram signal (RPS) [Reactor Protection System] was received due to low reactor water level. The lowest level observed was 1.6 [inches] with a scram set point of 2 [inches]. All expected PCIS [Primary Containment Isolation Systems] Isolations, GROUP 2 (RHR S/D cooling) [Residual Heat Removal], GROUP 3 (RWCU) [Reactor Water Clean-Up), GROUP 6 (Ventilation) & GROUP 8 (TIP) [Transverse Incore Probes] were received along with the auto start of 'B' CREVS [Control Room Emergency Ventilation System] and the three SBGT [Standby Gas Treatment] Trains. This low water level event is believed to be a result of manual closure of 2C RFP [Reactor Feed Pump] Discharge valve (2-FCV-3-5) and the slow response of the RFP BYPASS valve (2-FCV-3-53) "This event is reportable per 10CFR50.72 (b)(3)(iv)(A) as 'Any event or condition that results in valid actuation of RPS & PCIS as described in (1) & (2) below'." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-02-24
39613 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-02-13 | 2003-02-24 12:06 | 2003-02-24 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was obtained from the Texas Department of Health via facsimile: "During routine service of an ASOMA (SPECTRO) Model 200, Serial No 4390, a wipe test was performed on a 20 millicurie Am-241 source, Serial No 13730W. Contamination of 0.035 microcuries was detected on the wipe. The source is an AEA Technology (Amersham) Model AMC.D2 with a source product code AMCK2175. It is encapsulated in an X10/2 capsule. The source was removed and is being returned to the manufacturer for evaluation. All other interior components and exterior surfaces of the instrument were wipe tested and found to have no contamination above the Licensee's minimum detection limit of 360 picocuries. Agency was notified by telephone of the leaking source on February 13, 2003. A written report was sent to this Agency that same date. This incident was closed February 24, 2003. No violations have been cited. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [10 empty] | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-02-27
39612 | 0 | FAIRFAX HOSPITAL |  |  |  |  | 2003-02-21 12:15 | 2003-02-24 07:45 | 2003-02-24 | LOST RADIOPHARMACEUTICAL DEVICE CONTAINING TECHNETIUM-99 On 2/21/03 at approximately 1030 EST, the radio-pharmacy in the Nuclear Medicine Department of the Fairfax Hospital received a shipment of radio pharmaceuticals. As they were preparing to administer a dose to a patient, they discovered that one syringe containing 10 millicuries of Technetium-99M Mag-3 was missing. The licensee stated that the dose was listed on the in-processing documents as received. The licensee's current assumption is that either the dose was not actually shipped or that it was misplaced within the laboratory. The licensee plans on continuing to investigate the whereabouts of the device. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | VA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-02-24
39611 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2003-02-22 01:23 | 2003-02-22 05:30 | 2003-02-22 | MANUAL REACTOR TRIP DUE TO MAIN TURBINE ELECTRO-HYDRAULIC OIL LEAK "At 0123 [CST] a manual scram was inserted with the unit at 91% power in coastdown. Main Electro Hydraulic Control sump level low alarm was received. Cavitation of Main Electro Hydraulic control pumps and report of a leak around the main turbine front standard were received from the field. Manual scram was inserted. A previous condition existed on Feed regulating valve C with the valve not able to close more than 80% open. A level 8 signal was received tripping reactor feed pumps. At 0136 Reactor Core Isolation Cooling was initiated. A reactor level 3 signal was received isolating Suppression Pool Cleanup isolation valves. Reactor feed pump was restarted [and] received a level 8 second time due to leak by of feed regulation valves. A second level 3 was received after the second level 8. Reactor level is being controlled 10 to 51 inches with Reactor core isolation cooling. Outboard main steam isolation valves were closed for pressure control. Pressure control is on main steam line drains." "Upon further review of plant data, it has been determined a 3rd reactor water level 8 trip was received prior to RCIC stabilizing level." All control rods fully inserted and the electrical system responded normally. The licensee notified the NRC Resident Inspector. *****UPDATE ON 2/22/03 at 18:00 FROM WILLIAMSON TO LAURA***** The RCIC system has been shutdown and the normal feed water system placed back into service to maintain reactor veesel water level. | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-02-22
39610 | 0 | U.S. DEPT OF VETERANS AFFAIRS |  |  |  |  | 2003-02-21 09:00 | 2003-02-21 17:27 | 2003-02-21 | POSSIBLE MEDICAL EVENT During an intravascular brachiotherapy procedure, several Strontium-90 sources (approx. 60 millicuries) were used. The sources were deployed from the transfer device and were not seen at the desired treatment on the patient. The sources were withdrawn back into the transfer device. The physician does not believe that the sources entered the patient on this initial attempt, but there was a possible dose at a location other than the treatment site in excess of the limits in 10 CFR 30.3045(a)(iii). After retraction, the sources were successfully deployed into the patient and verified by the physician via a fluoroscope. Adverse effects on the patient are not expected. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 4 | CO | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2003-02-21
39609 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-02-21 04:24 | 2003-02-21 08:10 | 2003-02-21 | REACTOR WAS MANUALLY SCRAMMED FROM 27% POWER On 2/21/03 @ 0424 PNPS was making preparations to scram using an approved Shut Down procedure and experienced a Recirc Pump Runback of the only Recirc MG set in service. Computer generated Core Flow indicated approximately 17 Mlbm/Hr and 25% Reactor Power. The Operator at the Controls calculated Reactor Power and Flow using the PNPS Power to Flow (P/F) Map. Indications on the P/F Map showed a value in the OPERATION PROHIBITED REGION (17% Reactor Power and 14 Mlbm/Hr Flow). Per PNPS procedures, intentional operation in this area is prohibited and you must immediately restore to within the analyzed operation area. This area is not part of the Reactor Instability Region. These discrepancies were noted by the Shift Manager who directed the Reactor to be Scrammed. All other safety and nonsafety plant equipment functioned normally after the Reactor Scram. All rods fully inserted, no ECCS actuated and no relief valves lifted. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-02-21
39608 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-02-21 00:25 | 2003-02-21 02:30 | 2003-02-21 | REACTOR IS BEING SHUT DOWN DUE TO ONE RECIRCULATION LOOP BEING INOPERABLE "On 2/20/03 @ 0525 PNPS experienced a trip/lockout of 1 of their 2 Recirc MG sets. This caused Reactor Power to decrease to 70% of rated. All other safety and nonsafety plant equipment functioned normally after the Recirc MG trip. Due to our Facility Operating Licenses PNPS entered an Active LCO for One Recirculation Loop Inoperable. The License states, 'The Reactor shall not be operated with one recirculation loop out of service for more than 24 hours. With the reactor operating, the plant shall be placed in a hot shutdown condition within 24 hours unless the loop is sooner returned to service.' "After extensive trouble shooting activities PNPS decided that the loop will not be returned to service in the required time frame and has commenced a normal shutdown to hot shutdown condition on 2/21/03 @ 0025. Reactor Power at the time of commencement of shutdown was 37%." The licensee believes the cause was due to a field lead breaking off the slip rings. Estimated down time is 5 to 8 days. The NRC Resident Inspector was notified and the licensee may notify the media. | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-02-21
39607 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-02-20 | 2003-02-20 15:00 | 2003-02-20 | CALIFORNIA AGREEMENT STATE REPORT FOR MEDICAL EVENT AT ALTA BATES MEDICAL CENTER "Received a call today at about 1430 hours from [ ] who is one of Alta Bate's medical physicists (therapy department), to report a therapeutic misadministration involving I-125. The regular RSO is on leave. The patient was prescribed 0.35 millicuries I-125 for a brachytherapy procedure (prostate implant; involving 80+ seeds) on 2/19/03, but received 0.52 millicuries, or an estimated 50% overdosage, because the calculation [was] done incorrectly." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-02-25
39606 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-02-20 13:49 | 2003-02-20 19:12 | 2003-02-20 | CALIFORNIA AGREEMENT STATE REPORT FOR MEDICAL EVENT AT UNIVERSITY OF CALIFORNIA "I took a call on a therapeutic misadministration from the RSO for UCIMC (LN 0278-30). The incident involved the administration (via injection) of Y-90 microspheres (25 microns) for the treatment of unresectable hepatic carcinoma. The intended dosage was 96.2 millicuries, and the administered dosage was approximately 38.48 millicuries (i.e., an underdose of 60%). "The delivery system consists of an injection system, connected to the vial containing the microspheres, which has one line leading to a receiving vial, and another to the patient. The direction of the flow is determined by position of the valve connecting these two lines. Just beyond the vial containing the microspheres there are also two mounted detectors (like small pocket chambers), which give a visual indication when the microspheres begin moving out of the vial. "The physicist was priming the system prior to a scheduled treatment. When the priming reaches the point that the microspheres begin to exit the vial, the valve is turned to direct the flow from the "receiving vial" to the patient. In this case, the physicist accidentally over-primed the system and about 60% of the activity washed in the receiving vial. The physician, an authorized user, was also present during the treatment. They completed this treatment, and the physician is still reviewing whether it is necessary to perform another treatment to reach the prescribed dosage, or whether this treatment will be adequate as it stands. "The licensee is awaiting a report from the physician and physicist as to what might have caused this to occur. At the present time, they think it may simply be that the physicist did not respond quickly enough to the indication on the detectors that activity was passing out of the isotope vial. That is, it may simply be a slow reflex problem. The manufacturer happened to be on site at the time of the incident, and indicated there had been two similar previous events (one allegedly at a hospital in PA), but no further details on the events were obtained by the licensee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-02-25
39605 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-02-20 15:30 | 2003-02-20 17:59 | 2003-02-20 | NON-WORK RELATED DEATH OF PLANT EMPLOYEE "On 2-20-03 at 1530 hours, the Occupational safety and Health Administration (OSHA) was notified of a non-occupational related employee death. The reporting requirement, 29 CFR 1904.39(b)(5), specifically requires employers to notify OSHA when an employee death occurs within thirty (30) days of a heart attack which occurred on plant premises. This is not classified as a work related event. "This is being reported in accordance with UE2-RA-RE1030 'Nuclear Regulatory Event Reporting,' notification made to another government agency." This worker had two previous heart attacks. He complained to co-workers of chest pains during a break on 2/17/03. On his way to the site medical facility, he began to feel chest pains and was taken to the local hospital. He died on the morning of 2/20/03 of heart failure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-02-20
39604 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-02-20 18:00 | 2003-02-20 17:38 | 2003-02-20 | ERDS OUT OF SERVICE FOR PLANNED OUTAGE AT FERMI 2 "The safety parameter display system (SPDS) is being removed from service to perform planned upgrades to the system. The removal of the SPDS affects the transmission of data for the emergency response data system (ERDS). The SPDS will be deactivated at approximately 1800 hours on February 20, 2003, and will not be returned to service until the end of April 2003. During this period, the primary plant indicators that supply the SPDS, in conjunction with the other indication and communication systems available to the plant operations staff will be used for emergency response if needed. This condition is reportable in accordance with 10CFR50.72(b)(3)(xiii). The Senior Resident Inspector, appropriate Region III and NRR Staff members, have been briefed on this modification." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-02-20
39603 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2003-02-18 10:16 | 2003-02-20 17:32 | 2003-02-20 | INVALID SPECIFIED SYSTEM ACTUATION "On February 18, 2003, at 1016 hours, with Unit 2 in Mode 5 (refuel), the 2B Emergency Diesel Generator (DG), automatically started during the restoration from the reactor vessel hydrostatic leakage test. The apparent cause was a spurious pressure spike sensed at instrument rack 2H22-P004 while opening the reactor vessel head vent valves. This pressure spike caused the associated reactor vessel water level transmitters to sense a low level condition. This invalid low level signal resulted in the automatic actuation of the 2B DG (Div. III) which is the emergency power supply to the Unit 2 High Pressure Core Spray (HPCS) system. The Unit 2 HPCS pump control switch had been placed in the pull to lock position as part of the procedure controls for the hydrostatic leakage test and therefore did not actuate. This system actuation is reportable under 10 CFR 50.73 (a)(2)(iv)(A). "The 2B DG responded normally and reached normal speed and voltage. It was run both loaded and unloaded successfully, and was secured at 1042 on February 18, 2003. "This report is being made in accordance with 10 CFR 50.73 (a)(1), which states that in the case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv), other than an actuation of the RPS when the reactor is critical, the licensee may provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-02-20
39602 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2003-02-20 06:30 | 2003-02-20 15:04 | 2003-02-20 | LOW LEVEL RADWASTE INCINERATOR FIRE EVENT AT FRAMATOME "At approximately 0630 hrs. a cardboard waste box, containing about 9.75 grams of U-235, was being fed into the low level rad waste incinerator. The box entered into the feed box area of the incinerator and the outer door closed, however the inner door, separating the feed box from the incinerator, only partially opened and prevented the waste box from being fed into the incinerator. The waste box caught fire in the feed box area which resulted in damage to the primary HEPA filter and associated pre-filter for the feed box and incinerator shroud (located just above and directly downstream of the feed box area). The final HEPA filters remained undamaged. The ventilation duct upstream of the final HEPA filters is equipped with a fire deluge system, which remained unactivated indicating the temperature seen by the final filters was below the deluge system activation temperature (less than 180 degrees F). The fire self-extinguished when the inner door was fully closed and the waste box and contents were consumed. There was no unusual release of radioactive material from the facility as demonstrated by stack air sample results and samples taken from the roof and surroundings. The two employees in the facility were checked and no detectable contamination, and only minimal (less than .1 DAC hrs.) exposure occurred. An Incident Investigation Board (IIB) has been convened. The equipment is currently shutdown and will remain down until the IIB report is complete and appropriate corrective actions are completed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 4 | WA | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2003-02-20
39601 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-01-08 12:00 | 2003-02-20 15:32 | 2003-02-20 | ABNORMAL RADIOGRAPHY SOURCE RETRIEVAL The following information was received by fax from the Ohio Department of Health: "The licensee reported [an] abnormal radiography source retrieval due to a crimped guide tube. A test piece fell on the guide tube during radiography operations in the licensee's radiography vault. The licensee's source retrieval procedure was implemented and the source was successfully retrieved. A total of 3 [millirem] was received by 2 individuals during this operation." The source was Ir-192, 83 Curies, manufactured by AEA Technologies, model number 424-9, serial number 07686B. The radiography camera is a Model 880 manufactured by AEA Technologies, serial number D1163. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-02-25
39600 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-02-19 | 2003-02-20 15:31 | 2003-02-20 | LOST AIR IONIZER The following report was received by fax from the Ohio Department of Health: "The Bureau received a report of a lost generally licensed air ionizer [static eliminator]. The device was [an] NRD, LLC model P-2021-8101, serial # A2BP733. The device contained a Po-210 source with an activity of 1.25 [millicuries] on 2/20/03." The loss was attributed to inadequate training. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-02-25
39599 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2003-02-19 | 2003-02-19 17:44 | 2003-02-19 | AGREEMENT STATE REPORT - RADIOGRAPHER RECEIVED GREATER THAN 5 REM ANNUAL LIMIT FOR 2002 During QA audit of licensee by Oregon Department of Human Services, Radiation Protection Services, it was determined that one radiographer employed by the licensee had exceeded his 2002 annual dose limit by approximately 800 millirem. This discrepancy was evident by the difference between pocket ion dosimeter and TLD readings. Oregon Radiation Protection Services continues to investigate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2003-02-24
39598 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-02-19 08:45 | 2003-02-19 16:56 | 2003-02-19 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE "The gauge was in use on February 18, 2003. At close of business, the operator locked the gauge handle, placed it in its transportation case, and locked the case with chain and lock to a projection inside a Conex container. The Conex was then padlocked closed for the evening. When the operator arrived on-site the following morning, (February 19, 2003), he discovered that all contractor Conexes had been broken into and basically all Conexes on the site had been 'cleaned out.' The Houston Police Department was notified, arrived on site, and took statements from all personnel suffering a loss. The stolen gauge was a Troxler Model 3430, Serial No.: 20385, containing two sources: a 1.48GBq/40 milicuries (+/- 10%) Am-241:Be source, Serial No.: 47-15863, and a 0.30 GBq/8 millicuries (+/- 10%) Cs-137 source, Serial No.: 75-1733. The site is believed to be located in Harris County. The gauge and sources were last leak tested on August 5. 2002, with negative leakage results." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-02-24
39597 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-02-19 10:30 | 2003-02-19 16:39 | 2003-02-19 | OFFSITE NOTIFICATION DUE TO LEAK OF HAZARDOUS MATERIAL (NON-NUCLEAR) TO THE ENVIRONMENT The following information was obtained from the licensee via facsimile: "1. Event Description "On Wednesday morning, 2/19/03, at approximately 10:30 AM, a leak was discovered in the line originating from the LLR [Low-Level Radioactive] equalization tank south of the Internal Outfall 401 Sump. This was a low volume leak (approximately 500 gallons) in an uncontrolled area that was inaccessible and low lying. Considering the inclement weather conditions at the time, there was significant standing water in the area underneath the leak and it could not be determined whether this was from the leak or from snow melt. The area surrounding the leak was roped off, the line was isolated, and the standing water pumped back into the equalization tank system. This liquid is hazardous waste due to the pH (1.1) "2. Evaluation of the Event "QWI 14,1.10, Appendix 1 states that the General Manager has to be notified of the event within 24 hours and the NRC within 24 hours if the following condition is met: "An unplanned contamination event that: "(1) Requires access to the contamination area by workers or the public to be restricted for more than 24 hours by imposing additional radiological controls or by prohibiting entry into the area; and (2) Involves a quantity of material greater than 5 times the lowest Annual Limit on Intake specified in SNM-42 (ICRP-68), for the material. "A 10 [milliliter] sample of the standing water was analyzed on a low background alpha/beta proportional system. This sample had an activity of 20 [nanocuries per liter] alpha and 48 [nanocuries per liter] beta. Assuming 1,893 liters was involved in the release (per Waste Treatment's estimate of 500 gal. maximum), the total alpha and beta activity released was 37.9 [microcuries] alpha and 87.1 [microcuries] beta. Convention for the initial analysis of liquid waste is to assign all alpha activity to U-234 and all beta activity to Sr-90. Sr-90 has the most conservative ALl [Annual Limit on Intake] among the beta/gamma emitters seen in LTC [Lynchburg Technical Center] effluents. It should be noted that the proportional counter used for this analysis was beta calibrated with Tc-99 which has a lower beta energy than Sr-90, the beta emitter of concern at LTC. This causes an overstatement (conservative estimate) of the Sr-90 beta activity in the sample. "Five times the ALl for Uranium is 135 microcuries (since the material is in liquid form, the ICRP-68 ingestion ALl of 27 microcuries was used as the ALI for comparison). The estimated amount of U-234 involved is 37.9 microcuries. "Five times the ALl for Sr-90 is 240 microcuries (since the material is in liquid form, the ICRP-68 ingestion ALl of 48 microcuries was used as the ALl for comparison). The estimated amount of Sr-90 involved is 871 microcuries. "The leaking pipe/flange was replaced and the impacted area cleaned to the extent practical and clean gravel placed in the impacted area. This is not reportable as a radiological event since the quantity of material does not exceed 5 times the ALl." The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (2) |  |  |  | 1 | 2003-02-19
39596 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-02-13 09:54 | 2003-02-19 15:43 | 2003-02-19 | OFFSITE NOTIFICATION DUE TO SERIOUS PHYSICAL INJURY AT AMEREN UE CALLAWAY PLANT The following information was obtained from the licensee via facsimile: "At 0954 [CST] on February 13, 2003, the Control Room was notified of a personnel injury in the Turbine building. After examination by the site doctor, the individual was transported off site for treatment. Subsequently, on February 18, 2003, the individual was admitted to the hospital for further treatment. Preliminary investigation indicates that the individual was struck in the face with a flying object. The individual was using a filter change out tool and attempting to disconnect a 2" Camflex plug. The line was apparently pressurized resulting in ejection of the plug toward the individual's face when it was disconnected. The Missouri Public Service Commission was notified at 2:02 pm CST on February 19,2003 of the serious injury. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-19
39595 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-02-18 12:00 | 2003-02-18 12:40 | 2003-02-18 | 1- HOUR SAFEGUARDS REPORT Unescorted access granted to contract employee inappropriately. Immediate compensatory measures taken upon discovery. Contact Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-02-18
39594 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2003-02-17 | 2003-02-18 09:36 | 2003-02-18 | AGREEMENT STATE - RADIATION WORKER EXCEEDED TEDE DOSE LIMIT "Description of Incident: On the afternoon of February 14, 2003, DRH received a call from Sonny Mallette with Southern Inspection Services, concerning a radiographer receiving a TEDE for calendar year 2002 exceeding 5 rem. Mr. Mallette stated that the employee had received 4722 mrem [millirem] by the end of the 11th report for 2002, and they had watched his dosimeter readings closely, but when they received the end of year report he had gone over the 5 rem limit [5,066 millirem]. He stated that the dose was received in work situations where shielding and distance are at a minimum. One setup involved shooting up in a oil drilling rig derrick where no shielding is available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0 | 2003-02-21
39593 | 0 | CARBOLINE COMPANY |  |  |  |  | 2003-02-17 | 2003-02-17 16:44 | 2003-02-17 | 10 CFR PART 21 NOTIFICATION - CARBOLINE COMPANY The following information was obtained from the vendor via facsimile: "This letter serves to notify the Commission of a potential safety related noncompliance deviation in a basic component as defined in 10CFR Part 21. The noncompliance involves hard settling of Carboguard 890 Part B; the affected batches are 2A9266L, 2A9275L, and 2H9352L "The hard settling of Carboguard 890 Part B would result in a mixed product that would have lower pigment volume concentration (PVC) than standard material that has been uniformly dispersed. Potential deficiencies would be a lack of film build during application as a result of a lower initial viscosity and the fact that some particles from the hard settling may have been dispersed into the mixed product. These particles could result in the clogging of spray gun tips or having particles embedded into the applied coating, which are aesthetically unpleasing. Overall the lack of pigment in the coating film affects the application and aesthetic properties of the coating and not the performance properties. The primary criteria for the epoxy coating's performance are that the stoichiometry of epoxy resin to amine curing agent are not changed by more than 10%. Based upon a prior non-nuclear occurrence we know that the hard settling does not alter the stoichiometry of the coating and the cure of the product will be within the parameters designed by the formulating chemist. Based upon prior testing of numerous coatings for use in nuclear power plants we have not seen any detrimental performance when lower PVC coatings were evaluated. Resin rich coatings are typically gloss coatings and they aid in radiation decontamination and chemical resistance. As such, Carboline does not feel that the performance of the coating will be adversely affected. "A database has been created documenting all shipments of the affected batches made within the 2002 calendar year to present; approximately 30 utilities/customers are affected. All customers who our records indicate have been shipped batches 2A9266L, 2A9275L, and 2H9352L shall be notified promptly. We are requesting that customers review their stock of Carboguard 890 Part B and return the affected batches for replacement. "In summary, Carboline has taken appropriate corrective action, notified the NRC, and shall notify all customers promptly." The affected parties are as follows: Consumers Energy - Palisades Generating Plant Energy Steel & Supply - 2715 Padan Street, Auburn Hills, MI Florida Power & Light - 9760 SW 344th St., Florida City, FL Hutchinson & Gunter - 715 Grpve Street, Greensburg, PA Imaging & Sensing Technology - IST Conax Nuclear, Inc., Buffalo, NY Newbury Sandblasting - PO Box 378, Newbury, OH Nullifire Ltd. - Torrington Avenue, Coventry, UK Point Beach Nuclear - 6610 Nuclear Road, Two Rivers, WI Prairie Island - Welch, MN Ameren/UE-CIPS - Callaway Plant Duke Energy Corp - Nuclear Assessment Division, SC Ellis & Watts - 4325 Slick Lane, Bativa, OH FirstEnergy, Davis-Besse Oak Harbor, OH Howden Buffalo - New Philadelphia, OH Omaha Public Power - Fort Calhoun Nuclear Station Palmer Industrial Coatings - Williamsport, PA Rotork Controls - Rochester, NY TXU Electric - Glen Rose, TX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MO | OTH | PAR | 21.21 |  |  |  | 0 | 2003-02-17
39592 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2003-02-17 14:13 | 2003-02-17 15:29 | 2003-02-17 | 8-HOUR NON-EMERGENCY NOTIFICATION DUE AUTOMATIC START AND LOAD OF THE 1B EMERGENCY DIESEL GENERATOR The following information was obtained from the licensee via facsimile: "While performing maintenance activities to replace a failed undervoltage relay on 1B3 4160 VAC bus, the undervoltage protection triggered a load shed on the 1B3 4160 VAC bus causing a loss of power to the bus and automatic start and load of the 1B Emergency Diesel Generator. Although the potential for this event was previously briefed for the relay replacement, this event is being reported under 10CFR50.72(b)(3)(iv)(A)." The load shed caused a loss of the 1B motor-generator (MG) set but both MG sets are 100% capacity sets. There were no adverse consequences due to the trip of the 1B MG set. The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-02-17
39591 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-02-17 08:30 | 2003-02-17 13:57 | 2003-02-17 | UNANALYZED CONDITION FOR ISOLATION CAPABILITY OF MANUAL VALVES IN THE COMPONENT COOLING WATER SYSTEM "During the eleventh refueling outage on Unit 2 (2R11), component cooling water (CCW) system manual valve CCW-2-18 was found to have a damaged liner. The subject valve is used to separate the two vital normally cross-tied CCW trains in case of a CCW leak either as an independent event or as a passive failure following a loss of coolant accident. Valve CCW-2-18 would not have performed its licensing/design function of providing CCW train isolation. "The licensing/design bases for this CCW System, as discussed in table 9.2-7 of the FSAR and in SSER 16, is for a maximum 200 gpm leak to occur. Leakage would be detected by falling level in the CCW surge tank. Because of the remaining 4000 gallons in the CCW surge tank after receipt of the low-level alarm, there would be at least 20 minutes for the operator to isolate the leak before the surge tank is empty. The period is extended if the automatically operated, Design Class II, normal makeup path functions as designed and adds makeup water to the system. PG&E's abnormal operating procedure, OP AP-11, has provision for aligning a 250 gpm Class I supply of water to the CCW surge tank. "The design/licensing basis of a 200 gpm leak being isolated in 20 minutes assumes that manual valves used during the isolation operation hold and terminate the leak. There is no evidence that PG&E nor the NRC have considered that a leak would not be isolated upon completion of actions to separate the trains. The identified condition, though not believed to represent a safety concern, is different than that discussed in SSER 16. Therefore, the condition is considered to be outside the design basis for the plant." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-02-17
39590 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-02-17 10:58 | 2003-02-17 13:34 | 2003-02-17 | OFFSITE NOTIFICATION OF SEPTIC SYSTEM OVERFLOW "On 2/17/03 at 1058, Xcel Energy Environmental Services completed notification to the Minnesota Pollution Control Agency (MPCA) concerning an approximately 300 gallon septic system overflow event. The distribution system appears to be frozen due to cold weather and lack of snow cover, causing the pump discharge to flow out to grade. Spill has been contained and cleanup completed." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-17
39589 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-02-16 02:53 | 2003-02-16 03:10 | 2003-02-19 | NOUE DECLARED DUE TO REDUCED PLANT SERVICE WATER FLOW Licensee reported that service water pump intake bay level decreased requiring the shutdown of one dilution water pump to increase bay level to normal. Flow was reduced on the operating dilution water pump by throttling the discharge flow to maintain bay level at the normal operating level. The cause of the reduced service water bay level is being investigated. The licensee has notified the State of Michigan and VanBuren county. The licensee will contact the NRC Resident Inspector. Notified FEMA of this event * * * UPDATE AT 0418 EST ON 2/16/03 BY GERRY WAIG * * * NRC entered monitoring phase of normal mode for this event at 0418 EST on 2/16/03 after decision maker brief (Jim Dyer, Geoffrey Grant, Tony Vegel, Pat Hiland, and John Zwolinski). * * * UPDATE AT 0825 EST ON 2/16/03 BY GERRY WAIG * * * NRC exited monitoring phase of normal mode for this event at 0825 EST on 2/16/03 after briefing (J. Dyer/ R3 IRC members, S. Collins, J. Zwolinski, R. Zimmerman, D. Wessman, W. Kane, & P. Hiland). * * * UPDATE AT 1600 EST ON 2/16/03 BY HOWIE CROUCH * * * Divers are at Palisades and preparing to inspect (most likely tomorrow). The plant is stable and the bay level is stable. The plant continues in the Unusual Event. Exit criteria will be root cause discovery. It was noted that South Haven municipal water (near Palisades) was experiencing like symptoms. * * * UPDATE AT 1301 EST ON 2/19/03 BY HOWIE CROUCH * * * The licensee has terminated the NOUE declared on 2/16/03. The licensee has restored full capability to provide make-up water to the plant's service water intake (ultimate heat sink). The NRC Resident Inspector has been notified by the licensee. Headquarters Operations Officer notified R3DO (Miller), NRR EO (Zwolinski), FEMA and DIRO (Hiland). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-02-16
39588 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-02-14 19:00 | 2003-02-15 16:15 | 2003-02-15 | CRITICALITY CONTROL 24-HOUR (BULLETIN 91-01) REPORT The following information was obtained from the regulatee via facsimile: "At 1900 on 2-14-03, the Plant Shift Superintendent (PSS) was notified that the C-333 "E" Surge Drum, 0-25 psia pressure recorder was not working and the 0-2 pressure recorder was off-scale. The 0-25 psia pressure recorder had failed violating the requirements of a Safety Related Item (SRI) credited in NCSE [Nuclear Criticality Safety Evaluation] 016. As a result, the shiftly pressure checks could not be performed. Instead of installing a sample buggy to measure pressure, the drum pressure was reduced in order to read the pressure on the 0-2 [psia] pressure chart recorder. The purpose of the pressure check is to identify if wet air in-leakage has begun on the surge drum bank. "Double contingency has been restored since the ability to read pressure in the surge drum bank using a properly operating AQ-NCS [Augmented Quality - Nuclear Criticality Safety] pressure instrument has been restored. "The NRC Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: "Although pressure readings could not be taken due to a failed AQ-NCS pressure instrument, there are several important mitigating factors. First, the integrity of the drum bank has been maintained. Second, the uranium has been maintained in the gas phase. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) "These drums are used to store gasses. Therefore, in order for a criticality to be possible, wet air would have to react with any UF6 in the drum. The leak would have to occur over a long period, in order to create a large mass of U02F2 and then sufficiently moderate the material. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.) "Double contingency is maintained by implementation of two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL(INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS); "The material in the Surge Drum is in a gaseous state. System NCS limit is 1.7 wt.% U235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "The first leg of double contingency is based on maintaining the integrity of the surge drum system against wet air in leakage. This integrity is assured by a SRI for the unlikely breach of the surge drum system. Structural integrity of the drum is intact, therefore this SRI is maintained. "The second leg of double contingency is based on the performance of shiftly pressure checks using an AQ-NCS instrument as an indication of wet air in-leakage. The required checks could not be performed due to a failed instrument, resulting in a loss of this control. Instead of installing a sample buggy to measure pressure, the drum pressure was reduced in order to read the pressure on the 0-2 pressure chart recorder. Since there are two controls on one parameter, double contingency was not maintained. "Even though moderation control was maintained, double contingency is based on two controls on moderation. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: None." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-02-15
39587 | 0 | STATE OF CALIFORNIA |  |  |  |  | 2003-02-13 07:30 | 2003-02-14 16:55 | 2003-02-14 | AGREEMENT STATE REPORT- UNIVERSITY OF CALIFORNIA AT SAN DIEGO SAFETY EQUIPMENT FAILS TO FUNCTION The following information was obtained via e-mail from California Department of Health Services, Radiological Health Branch: "At approximately 7:30 am [PST], February 13, 2003, the University of California at San Diego (California Radioactive Materials No. 1339-37) was performing one of the monthly Quality Assurance (QA) tests on their High Dose Rate Afterloader (HDRA). They had a treatment scheduled for later that morning, and the guide tubes and extenders were already attached in preparation for the treatment. During the typical monthly check, the licensee disconnects two of the guide tubes, and attaches the QA catheter, placing one end in the well chamber to measure the source strength, and that is what occurred this time. However, when the channel was set to run the QA test, the operator inadvertently set the wrong channel, and the source was extended into one of the guide tubes, rather than through the QA catheter and into the well chamber. When the operator tried to retract the source, it would not retract. "The operator used a survey meter at the door of the treatment room to verify the source was still out, and re-confirmed that with the indication on the room monitor. After several attempts to retract the source from the console, the operator entered the room, and placed all the guide tubes into the emergency source pig, and closed the lid. The operator states the dose-rate in the room, with the source in the pig was reduced to approximately 3 milliR/hr at one foot from the pig. He estimates he was within one meter of the unshielded source for no more than 5 seconds, and that his hand was within one foot of the source for approximately 3 seconds. Currently, the licensee estimates the dose to the operator as under 100 millirem whole body. They have sent his dosimeter for emergency processing. It is unknown at this time if he was wearing an extremity dosimeter. "After placing the guide tubes with the source in the pig, the operator left the room, locked it, and contacted Nucletron Corporation to service the device. The licensee contacted the State of California with this information at approximately 10:30 am PST on February 14, 2003. The State of California is investigating this event, and will provide updated information as needed. This event would be reportable to the NRC pursuant to 10 CFR 30.50(b)(2), and to the State of California under the comparable California regulation (17 CCR 30295)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-02-19
39586 | -1 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2003-02-03 | 2003-02-14 14:32 | 2006-02-03 | POSSIBLE MEDICAL EVENT AT PHILADELPHIA VETERANS ADMINISTRATION MEDICAL CENTER Informed by a representative of the Department of Veteran's Affairs National Health Physics Program (NHPP) that a possible medical event may have occurred at the Philadelphia Veterans Administration Medical Center. The event took place on February 3, 2003 but was not determined until it was discussed on February 13, 2003. The procedure being performed at the time of the event was a permanent prostate seed implant brachytherapy. The nuclide involved is I-125. A fraction of the seeds intended to be implanted into the prostate were recovered from the bladder. The medical authorized user (the physician prescribing and performing the procedure) rewrote the written directive in the operating room to reflect the number of seeds that were successfully implanted into the prostate. Calculations are presently being made to determine the exposure to the bladder. Preliminary calculations indicate that there are no deterministic effects to the patient as a result of the event. All the seeds are presently accounted for. There was no patient intervention. The NHPP is currently investigating the event. * * * RETRACTION AT 14:05 EST ON 2/3/2006 FROM GARY WILLIAMS TO ABRAMOVITZ * * * "Based on our discussions with NRC Region III, the circumstances for event do not meet the definition in 10CFR35.3045 as a medical event." Contacted the R1DO (Meyer), R3DO (Riemer), and NMSS EO (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2003-02-14
39585 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2003-02-06 | 2003-02-14 11:22 | 2003-02-14 | AGREEMENT STATE REPORT - MEDICAL EVENT The Iowa Department of Public Health provided the following via fax: "Here is a summary of the event that occurred a week ago: "The University of Iowa (Iowa Radioactive Materials License No. 0037-1 -52-AAB) provided a 700 Rad (7 Gy [Gray]) dose to an unintended site using a Varian-TEM Ltd. Model VariSource HDR Remote Afterloader. The planned area of treatment was a tumor in the bronchial area. "The licensee measured and tested a catheter using the dummy source. After the test, the catheter was placed in a box and sent for sterilization. On February 6, 2003. the licensee used what they thought was the correct catheter during one fraction. "When the patient returned on February 13, 2002, for the second fraction, a medical physicist discovered that the catheter was 30 centimeters too short. "The dose was delivered to the skin in the nasal passages rather than the bronchial area. The attending physician was present at the time the error was discovered and has been informed. The patient has been advised of the error and given the option of discontinuing treatment. The patient has elected to undergo treatment for the correct site. "The cause of the error is currently under investigation and the licensee's report, which is due to IDPH by February 28, 2003, will address corrective actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2003-02-19
39584 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-02-13 10:00 | 2003-02-13 19:45 | 2003-02-13 | SIGNIFICANT INSERVICE INSPECTION FINDINGS FOR UNIT 2 STEAM GENERATOR TUBES The following information was obtained from the Licensee via facsimile: "On February 13, 2003, during the Unit 2 eleventh refueling outage (2R11), eddy current data on SG [Steam Generator] 2-4 indicated that greater than one percent of the total tubes inspected were defective. Most of the pluggable indications are due to outside diameter stress corrosion cracking (ODSCC) at the tube support plate intersections. Eddy current examination of these tubes indicated that the ODSCC crack growth rate at the tube support plate exceeded the program predicted growth rates. Preliminary calculations indicated the TS 5.6.10.d.5 limit for probability of burst (POB) was exceeded. "An additional defective tube in SG 2-4 row 5 tube bend has been identified that will be subject to additional insitu testing. PG&E has expanded the SG inspection scope and identified a team to prepare a root cause determination. "An NRC teleconference in accordance with TS 5.6.10.d.5 was held on February 13, 2003, at 1000 PST, to provide initial notification of significant findings. Additional teleconferences have been scheduled to provide additional inservice inspection results as they become available. "The NRC Resident Inspector and an additional onsite Region IV inspector were part of the teleconference presentation cited above." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-02-13
39583 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-02-12 17:04 | 2003-02-12 21:21 | 2003-04-04 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE DURING TESTING During a test of HPCI, the flow controller failed as the controller was being transferred from manual to balance. The system was manually tripped and remains inoperable. The system impacted is the High Pressure Coolant Injection and the cause is being investigated. The plant is also in a LCO action statement. Corrective action is being implemented to correct this single train system failure. The NRC Resident Inspector was notified. State and local agencies will be notified. *** EVENT RETRACTION BY TIM WITSCHEN TO ERIC THOMAS AT 1600 EST ON 4/4/03 *** "Event report 39583 was determined not to be reportable. The HPCI system would have been able to perform its safety function of automatically delivering 2700 gpm to the reactor within 45 seconds of initiation signal in the event of a loss of coolant accident, and to mitigate the consequences of a high energy line break. [Therefore], this event is being retracted." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-02-12
39582 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-02-12 09:45 | 2003-02-12 16:41 | 2003-02-12 | SUPERVISOR TESTED POSITIVE FOR ALCOHOL IN RANDOM TEST COMPENSATORY MEASURES PUT IN PLACE WHEN DISCOVERED. NRC RESIDENT INSPECTOR WAS NOTIFIED CONTACT HOO FOR ADDITIONAL INFORMATION | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.73 |  |  |  | 0 | 2003-02-12
39581 | -1 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2003-02-07 17:20 | 2003-02-12 16:13 | 2003-04-01 | LEAKAGE DISCOVERED FROM HIGH PRESSURE SAFETY INJECTION SYSTEM OUTSIDE CONTAINMENT "On February 7, 2003, at approximately 17:20 Mountain Standard Time (MST), Palo Verde Unit 2 discovered leakage from the high pressure safety injection system outside containment that could contain highly radioactive fluids during a serious transient or accident exceeded the safety analysis leakrate limit. The drain valve that was the source of the leakage was promptly tightened to return to within the analysis limit and subsequently repaired to further reduce leakage to a level as low as practicable. There was no release of radioactivity to the environment as a result of this event. There were no adverse safety consequences resulting from the event. The "loss of safety function" reporting requirement would be triggered by the described condition because the post-LOCA dose calculations assume no more than 1500 ml/hour leakage outside of containment in the 10 CFR 100 siting analysis. At the time of discovery, the leakage was 1715 ml/min (102900 ml/hr). Therefore the safety function to control the release of radioactive material such that the dose to a member of the public would not exceed 10 CFR 100 limits during a potential LOCA was not fulfilled. At the time of the discovery the condition was promptly corrected so no ENS report was thought to be required, however on further review it was noted that the reporting requirement states "Any event or condition that at the time of discovery could have prevented.." and therefore remains immediately reportable even if the condition no longer exists." The NRC Resident Inspector was notified. *** RETRACTED ON 4/1/03 AT 1605 EST FROM D. STRAKA TO A. COSTA *** "This notification is a RETRACTION of the February 7, 2003, ENS #39581 which reported a Palo Verde Nuclear Generating Station Unit 2 loss of safety function to control the release of radioactive materials due to leakage from the high pressure safety injection system outside containment that could contain highly radioactive fluids during a serious transient or accident arid exceed the safety analysis Ieakrate limit. "At the time of discovery, the leakage was assumed to exceed the 10 CFR 100 limits for dose to a member of the public during a potential LOCA [Loss of Coolant Accident]. Therefore the safety function to control the release of radioactive material would not be fulfilled. "PVNGS [Palo Verde Nuclear Generating Station] System Engineering re-evaluated the condition and has concluded that the identified leakage was well within the limiting large break loss of coolant accident analysis and that the 10 CFR 100 limits would not have been exceeded. Therefore, the loss of a safety function DID NOT exist and the condition is not reportable. "The NRC Resident Inspector has been notified." | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2003-02-12
39580 | 0 | ABC LABORATORIES |  |  |  |  | 2003-02-08 | 2003-02-12 15:19 | 2003-02-12 | MISSING NICKEL-63 FOIL SOURCE The licensee, ABC Laboratories of Columbia, Mo., reported they had lost a <15 millicurie Ni-63 foil source (serial # F2288) that had been removed from a Gas Chromatograph Chemical Detector and placed in storage. They think it may be in a dryer at the lab. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-02-12
39579 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-02-12 09:45 | 2003-02-12 13:46 | 2003-02-12 | LOSS OF SAFETY FUNCTION ON BOTH UNITS DUE TO TWO EMERGENCY D/G's BEING DECLARED INOPERABLE Emergency Diesel Generator "2A" was removed from service for pre-planned maintenance. This condition renders the "2A" Nuclear service Water pump inoperable. They had a vital i/c inverter "2EID" to fail, rendering the "2B" Emergency Diesel Generator inoperable due to its fuel oil fill valve failing closed. By the "2B" Diesel Generator being inoperable it rendered the "2B" Nuclear Service Water pump inoperable. The Nuclear Service Water is shared between both units. A loss of safety function occurred on Unit 2 due to two Diesel Generators being inoperable and no Nuclear Service Water train being operable. Since the Nuclear Service Water system is a shared with Unit 1, it also experienced a loss of a safety function. The system was returned to service within 9 minutes after re-opening the fuel oil fill bypass valve which rendered Diesel Generator "2B" operable again. The NRC Resident Inspector was notified. State and Local agencies will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-02-12
39578 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2003-02-11 09:40 | 2003-02-11 11:08 | 2003-02-11 | OFFSITE NOTIFICATION "Notification from Land Utilization that a 'Endangered Species' crocodile will need to be transported offsite to Miami Metro Zoo for rehabilitation of injury to left rear leg. "Land Utilization notified the Florida Fresh Water and the Wildlife Conservation Commission at 09:40 EST." The licensee will notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-11
39577 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-02-10 16:20 | 2003-02-11 06:16 | 2003-04-03 | STEAM VALVE SHUTDOWN DUE TO HIGH CONDENSATE LEVEL "At 1620 hrs, Autoclave (AC) #2 in the X-344 Facility experienced a Steam Shutdown due to high condensate level alarms (A) and (B) actuating. The AC was in applicable TSR MODE IV 'Feeding, Transfer or Sampling' when the actuation occurred. This is considered a valid actuation of a 'Q' Safety System. The autoclave was placed in MODE VII 'Shutdown' and declared inoperable by the Plant Shift Superintendent (PSS). An investigation is underway to determine the cause of the actuation. No release of radioactive material occurred as a result of the incident. This event is being reported in accordance with UE2-RA-RE1030 Appendix D. J. 2. Safety Equipment Actuations." The Autoclave (AC) lost one of four trains. This event was caused by operator error. A root cause investigation is planned by the licensee. The licensee notified the NRC resident inspector. *** EVENT RETRACTED ON 4/3/2003 AT 1521 EST BY STEVE MAY TO ERIC THOMAS *** "Nuclear Regulatory Affairs (NRA) reviewed the basis for the above event notification and determined that the notification can be retracted. The high condensate level alarms actuated in mode VIII (containment), which is not an applicable mode." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-02-11
39576 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-02-10 18:00 | 2003-02-10 18:46 | 2003-02-10 | INFORMATION CALL WITH POTENTIAL MEDIA ATTENTION "On February 10, 2003 the parents of an eight-year-old boy diagnosed with cancer filed a federal lawsuit against Florida Power and Light Company. The lawsuit alleges that the cause of the cancer was attributable to the child living in close proximity to the St. Lucie Nuclear Power Plant. "This event has created significant attention from both the local and national media FPL does not currently plan to make a formal press release. This informational notification is being made to alert the NRC of the situation and potential media inquiries." The NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2003-02-10
39575 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-07-18 | 2003-02-10 14:29 | 2003-03-07 | POTENTIALLY MISSING PHOSPHORUS-32 SHIPPING PACKAGES Single packages containing P-32 (~14 day half-life) were destined for four different out-of-state locations (in CA, KS, NY and TX). Intended shipping dates were July 18, August 5 and August 6, 2002. Carrier reported packages potentially missing within 2-3 days after intended shipping dates. The per-package activities ranged from 250 microcuries to 1 millicurie. All subject radioactive material contents are presently well past ten half-lives. After several months of shipper-carrier joint investigation, the cause(s) remain undetermined. Actions have been taken by shipper and carrier to prevent recurrence. * * * * UPDATE RECEIVED BY RIPLEY FROM CARPENITO 1448 EST ON 03/07/03 VIA FAX "Five additional single-package shipments (four P-32 and one I-125), destined for five different locations, shipped August 27, October 17, November 4 and 26, and December 13, 2002, were reported to MARCP as missing on 2/14/03. The per-package activities ranged from 250 to 500 microcuries of P-32 and 50 microcuries I-125. All subject packages were shipped before the shipper and carrier corrective actions had been implemented in late December 2002. No packages shipped since the corrective actions have been implemented have been reported to MARCP as missing." Notified NMSS EO (Reamer) and R1 DO (Shanbaky) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2003-02-13
39574 | 0 | INDIANA DEPARTMENT OF TRANSPORTATIO |  |  |  |  | 2003-02-09 04:20 | 2003-02-09 07:10 | 2003-02-09 | DAMAGED TROXLER GAUGE AT CONSTRUCTION SITE The RSO from the Indiana Department of Transportation reported a damaged Troxler gauge at a new construction site located approximately 1 mile west of the Indianapolis Airport. A bulldozer drove over the Troxler gauge. The gauge belongs to the State of Indiana. The gauge was a model number 3440 and had the serial number 19699. The gauge contained approximately 8 millicuries Cs-137 and 40 millicuries of Am-241/Be. The operating rod handle on the top of the gauge was bent over such that the plate on the bottom was stuck open. The RSO performed a radiological survey. The gauge casing was intact and no leakage was found. No personnel contaminations or radiation overexposures were observed. The RSO roped off the area. The RSO planned to transport the gauge back to the facilities shielded room. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | IN | MAT | [5 empty] | 0 | 2003-02-09
39573 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-02-07 14:08 | 2003-02-07 15:54 | 2003-02-07 | UNANALYZED CONDITION RELATED TO A POTENTIAL DISCHARGE OF THE C02 FIRE SUPPRESSION SYSTEM "On 2/7/2003 at 1408 hours, the Beaver Valley Power Station control room was notified by Engineering that a potential pressure transient from a discharge of the C02 total flooding fire suppression system in the East and West Cable Vaults at Beaver Valley Unit 1 (BV-1) could result in an unanalyzed condition. This pressure transient could cause the fire barriers within the subject areas to be structurally challenged, resulting in the potential for a postulated fire in one fire area to spread to an adjacent fire area. This condition could invalidate the assumptions made in the BV-1 fire protection safe shutdown analysis per 10 CFR 50 Appendix R. This condition was discovered following engineering's evaluation of a Condition Report initiated on 2/5/03 concerning the potential for a C02 discharge in the above areas that could have resulted in a breach of the fire barriers between adjacent fire areas. The automatic C02 suppression system in the East and West Cable Vaults was defeated on 2/5/03 at 2150 hours in response to the initial identified concern and a fire watch was established in the affected areas. These compensatory measures eliminate the potential for C02 overpressure transient condition in the affected areas. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition that significantly degrades plant safety since a potential discharge of the C02 fire suppression system in response to a postulated fire could have invalidated the assumptions made in the BV-1 fire protection safe shutdown analysis per 10 CFR 50 Appendix R. The NRC resident has been notified of the degraded condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-02-07
39572 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-02-06 17:39 | 2003-02-06 22:39 | 2003-02-06 | AGREEMENT STATE NOTIFICATION OF RADIATION OVER - EXPOSURE "Abstract: On January 31, 2003, the Radiation Safety Officer from the University contacted our office to notify us that a physician, who works in the Radiation Oncology Department at the University's Medical Center-Hillcrest, received a whole body dose of 5700 mrem for CY 2002, exceeding the occupational worker limit of 5000 mrem/year. The 5700 mrem was all received during the dosimeter wear period of October to December 2002. "The RSO states that this exposure appears to be real and therefore qualifies as an overexposure. The matter is being investigated by UCSD's Environmental, Health and Safety office with a formal report to be submitted within 30 days. "The physician has been interviewed by UCSD and feels the dose may have occurred during Cs-137 seed implants. UCSD is currently in the process of researching how many seed implants this doctor was involved in during this time period (they think the doctor was involved with at least 2-3 seed implants between October 1 through December 31, 2002). "In the years 2000, 2001 and for the first three quarters of 2002, this individual's reported dose was 0 DDE, LDE, SDE (note: This individual lost the ring badges for the first three quarters of 2002 and there are no ring badge records available for 2002). UCSD is having a special session of the Radiation Safety Committee next week to discuss this overexposure and will do their own investigation. They will also ask the doctor what happened to the ring badges. "Summary: At approximately 0900, the Brea office received a call from John Zummo, RSO and John Olson, ARSO from The Regents of the University of California, San Diego, 9500 Gilman Drive, La Jolla, CA 92093-0920, RAML# 1339-37, (858) 534-1069 to give notice that dosimetery readings indicate an overexposure to a staff physician. The physician works in the Radiation Oncology Department of Hillcrest Medical Center, San Diego, and received a dose of 5700 mrem whole-body for CY 2002, exceeding the occupational worker limit of 5000 mrem/year. The 5700 mrem was all received during the dosimeter wear period of October to December 2002. "A preliminary report was e-mailed to the office (sent 0912, on 1-31-03). That report relays that, based on the information known so far, the 5700 mrem appears to be real and therefore qualifies as an overexposure. The matter is being investigated by UCSD's Environmental, Health and Safety office with a formal report to be submitted within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-02-11
39571 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2003-02-06 12:11 | 2003-02-06 19:04 | 2003-02-12 | UNANALYZED CONDITION FOR CABLE SEPARATION CRITERIA AT INDIAN POINT 2 "At 1600 hours on February 6, 2003, IP determined that CR IP-2002.00765, issued to identify that the routing of charging pump power supply and control cables does not meet the cable separation criteria specified in 10CFR50 App R section III.G.1, was reportable as a potentially unanalyzed condition. This condition was discovered during the re-baseline of the 10CFR50 Appendix R analysis. A fire in Fire Area F could potentially disable all 3 charging pumps as a result of the loss of the 23 charging pump alternate power feed transfer switch; loss of the 23 charging pump 'alternate' power feed cable, and the alternate/normal power feed cable between the transfer switch and the pump; loss of 22CHP power feed cable; loss of local/remote control cable, PL2, disabling remote operation for all 3 charging pump breakers; and loss of Control cables and pneumatics 22 and 23 charging pumps. Fire protection impairment actions were implemented per Procedure SAO-703. This condition was determined to be reportable using the guidance of NUREG-1022 which cites the absence of adequate separation between redundant shutdown trains to be reportable as a significant degradation of plant safety. Although it is possible that this condition was previously identified and dispositioned, an analysis is not readily available." The NRC Resident Inspector has been notified. * * * UPDATE ON 2/12/03 @ 1757 BY DURR TO GOULD * * * Event notification 39571 made on February 6, 2003 identified an unanalyzed cable separation issue discovered during the re-baseline of the 10 CFR 50, Appendix R, analysis. As part of the on-going re-baseline, CR-IP-2003-867 was written at 1353 hours on February 12, 2003 to identify the potential failure of normal power supply cables for the six service water pumps to meet the separation criteria of 10 CFR 50, Appendix R, Section III,G. 1. The cables are potentially vulnerable to the effects of a single postulated fire in fire area J. The specific location of this common vulnerability is Manhole 23, located on the 15 foot elevation of the turbine building adjacent to the northwest corner of the 6.9 kV switchgear cabinets. Manhole 23 is covered by a checkered plate that is open to the 15 foot elevation and has not been credited as a fire barrier. The normal power supply cables are credited for a fire in Fire Area J to supply power to at least one service water pump. The normal power supplies for the six service water pumps are routed from the 480 V Switchgear Room through manhole 23. Fire protection impairment actions are taken per Procedure SAO-703. Although it is possible this condition was also previously identified and dispositioned, the analysis is not readily available for assessment as part of the re-baseline. The licensee notified the NRC Resident Inspector. Notified R1 DO (Meyer) and NRR EO (Zwolinski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-02-06
39570 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-02-06 15:00 | 2003-02-06 17:17 | 2003-02-06 | AGREEMENT STATE REPORT INVOLVING MISSING 62 MILLICURIE STRONTIUM-90 SOURCE The following information was received from the Arizona Radiation Regulatory Agency: "Date: February 6, 2003 "Time: 3:00 PM (MST) "First Notice: 03-04 "Arizona Location "Tucson FEDEX "Phoenix, AZ 85040 "License No. Transportation to "AZ 10-44 "At approximately 2:00 PM the Agency was informed by the University of Arizona that on 1/23/2003 they shipped a 90-Sr sealed source [62 mCi] to Novoste at Norcross, GA. At approximately 11:30 MST the University was contacted by Novoste and informed that a package with the University waybill did not have the 90-Sr sources but contained airplane parts. FEDEX reported to the University that the shipment left Tucson, AZ 6:44 PM on 1/23/03 arriving in Memphis TN around 1:07 AM 1/24/03. The log indicates 'Missing Paperwork.' Subsequently the package went to Atlanta and the Decatur Station. The package was back in Memphis on 1/26/03, then back the Atlanta and Decatur on 1/27/03. At approximately 9:07 AM, 1/27/03 the package was delivered to Novoste. The shipping package was a 12 by 13 inch metal pail weighing 35 pounds. It was shipped standard overnight on waybill # 838483848672. "The Agency and the University continue to look for the source. "The states of GA, and TN and U.S. NRC and FBI are being notified of this event." Call the Headquarters Operations Officer for contact information. *** UPDATE ON 2/7/03 1500 EST FROM ROD HARRELL TO ARLON COSTA *** The Sr-90 source was held by FEDEX at Memphis pending completion of paperwork and was subsequently sent to Novoste at Norcross, GA. The source was delivered to Novoste on 01/27/03 at 0930 EST. Notified NMSS EO (Leach), TAS (Hann), R4DO (Johnson), R4 IAT (Boland) and FEMA, DOE, USDA, HHS, EPA, DOT(NRC) via fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-02-11
39569 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-02-06 15:00 | 2003-02-06 17:28 | 2003-02-06 | AGREEMENT STATE REPORT INVOLVING FIVE MISSING I-125 SEEDS The following information was received from the Arizona Radiation Regulatory Agency: "Date: February 6, 2003 "Time: 3:00 PM (MST) "First Notice: 03-03 "Arizona Licensee: "Scottsdale Memorial Health Services, Co., Inc. "9003 E. Shea Blvd. "Scottsdale, AZ 85260 "License. No. 07-265 "On January 29, 2003, a Bracytherapy procedure using Iodine-125 seeds (3M, Model 6500 Series) was conducted at the above named hospital. On February 6, 2003, it was discovered that five seeds containing approximately 0.39 mCi each could not be accounted for. A survey of the source storage area, source use area, linens, and waste was conducted and could not account for the missing sources. "The Agency and licensee will continue to investigate this occurrence and report further. "The U.S. NRC and the U.S.FBI are being notified of this event." Call the Headquarters Operations Officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-02-11
39568 | 0 | BRIGHAM YOUNG UNIVERSITY |  |  |  |  | 2003-02-03 | 2003-02-06 14:51 | 2003-02-06 | GENERAL LICENSED TRITIUM EXIT SIGNS DESTROYED BY FIRE On 2/3/03 the Chemical Management Facility at the Brigham Young University Campus in Laie, HI caught on fire. The facility was storing 28 Tritium signs and the Safety Officer (SO) at the University believes that they were vaporized with the intense fire and no residues of the Tritium signs were found by the Environmentalist Contractor in charge of the building clean up. Based on other self-powered exit signs the SO feels the missing signs contained 10 Curie tritium sources each and were manufactured by SRB Technologies, Inc. located in Winston-Salem, NC between 1992 and 1993. A written report will be submitted for the loss of this general licensed material in accordance with NUREG-1556. Call the Headquarters Operations Officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-02-11
39567 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-02-05 16:34 | 2003-02-06 13:23 | 2003-02-06 | LOSS OF TWO EMERGENCY SIRENS IN ORANGE COUNTY DUE TO POWER OUTAGE "Indian Point Energy Center (IPEC) Units 2 and 3 is making an eight-hour non-emergency notification in accordance with 10CFR50.72(b)(3)(xiii). "On February 4, 2003, during a scheduled quarterly test of the offsite emergency notification system, two (2) sirens out of a total of 16 in Orange County failed to respond. These two sirens are located in Harriman State Park. The cause for the failure was subsequently determined, based on information provided by park rangers, to have been attributed to a loss of power in the area serving the sirens. Power was fully restored to the affected sirens at approximately 0500 hours on February 5, 2003 and had been unavailable for approximately 17 hours. "The NRC resident inspector was notified of this event." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-02-06
39566 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-02-06 09:45 | 2003-02-06 13:03 | 2003-07-25 | OFFSITE NOTIFICATION TO STATE AND LOCAL AGENCIES REGARDING TRITIUM SPILL "Notification was made to the state of New Jersey to report a spill of radioactive material, specifically, tritium at a concentration of 6.92 E-5 microcuries/ml. The material is presently contained on the property of Salem Generating Station and was discovered at 0945 on February 6, 2003. "Soil samples obtained at a depth of 20 feet from 2 monitoring wells indicates the presence of tritium. The monitoring wells are adjacent to Salem Unit 1 and within the protected area. We recently sampled all domestic water supplies and the results were negative. There is no indication of any offsite release, there is no threat to the public or company employees. We cannot determine at this time if this is an existing or historic condition. We are continuing with additional analysis to determine the source and extent of the condition." The licensee informed state agencies and the NRC resident inspector and will inform the local agency of LAC. * * * UPDATE ON 07/25/03 @ 1553 BY RUDOLPH CHAN TO CHAUNCEY GOULD * * * On July 25, 2003, PSEG made an update notification to the New Jersey Department of Environmental Protection on the results of PSEG's ongoing remediation work investigation plan for the previously reported tritium spill. The update stated that additional samples from test wells have identified presence of tritium at levels above background. Specifically, sample results obtained from a new well placed as part of the ongoing investigation indicated a tritium concentration of 3.5 E-3 microcuries/milliliter. Additionally, a sample from an existing well indicated a result of 1.25 E-4 microcuries/milliliter, which was higher than previously observed at this location although from a different type of well. Gamma scans of samples from both locations detected no other radionuclides. There is no indication of any offsite release and there is no threat to the public or company employees. We cannot determine at this time if this is an existing or historic condition. We are reviewing the situation with our expert panel to determine the proper location for additional test wells to determine the source and extent of the condition. The NRC resident and regional inspectors have been made aware of the test results. The NRC REG1 RDO (Daniel Holody) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-06
39565 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2003-02-05 | 2003-02-06 12:39 | 2003-02-06 | AGREEMENT STATE REPORT - LOST /RECOVERED TROXLER MOISTURE DENSITY GAUGE Received fax from Nevada Health Division Radiological Health Section on 2/6/03 reporting the following: On 2/5/03, a Licensee Technician left a Troxler gauge (3411B No.T13081) locked but not secured in the vehicle. He left for a brief tour of the construction site and when he returned to the truck the gauge was missing. The gauge case reportedly showed evidence of minor abrasions as if it had fallen out of the bed of a pickup. The gauge was found by local police and returned to the licensee. When the gauge was recovered, the source rod was reportedly in the safe, shielded position. The gauge index rod was slightly bent but the source rod is not prevented from full retraction into the shielded position. The licensee reports that when the gauge was refurbished by Troxler approximately one month ago, the trigger lock to lock the source rod in the shielded position was removed. The licensee intends to have a training session with all gauge users later this week. They also intend to implement a field audit process. Call the Headquarters Operations Officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2003-02-11
39564 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-02-05 20:58 | 2003-02-06 00:12 | 2003-02-06 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "In accordance with 10 CFR 50.72(b)(2)(iv)(B) 'Any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation', DC Cook Unit 2 is making a 4 hour non-emergency report. "On 2-5-03, at 2058, Cook Unit 2 tripped due to a failed 24 VDC control group #3 power supply. This caused the feedwater regulating valve for Steam Generator #3 to fail closed and the reactor tripped on Feed-flow/Steam-flow mismatch coincident with low level on loop 3. All control rods inserted, the turbine tripped and auxiliary feedwater pumps started as designed. The Main Steam Stop Valves were manually closed during the implementation of the Emergency Procedures to stop the RCS cooldown. There were no other notable occurrences as a result of the trip. "The RCS is currently stable in Mode 3 at normal operating pressure and temperature. Activities are in progress to determine the cause of the power supply failure and the extent of condition." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-02-06
39563 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-02-05 12:25 | 2003-02-05 15:50 | 2003-02-05 | OFFSITE NOTIFICATION "On February 5, 2003 at 1225 hours, reports were made to the National Spill Response Center, the EPA Regional Response Center, the Michigan State Police Operations Center and the State of Michigan Dept of Environmental Quality concerning a leak (approximately 500 pounds) of ethylene glycol, which is used in the cooling tower de-icing system, to the environment. Media interest may be expected." The licensee will not issue a press release unless media interest is generated. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-05
39562 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-02-05 08:45 | 2003-02-05 12:00 | 2003-02-05 | NOTIFICATION TO STATE OF RADIOACTIVE MATERIAL FOUND IN SCRAPYARD "At 0845, Florida Power and Light Company (FPL) notified the Florida Bureau of Radiation Control of an item found at a scrap yard facility in Coral Springs, FL. The item was an Eberline model RD-A2A radiation detector, serial number 2555, with the label indicating a sealed source with 50 nanoCuries of Am-241 (exempt quantity). The detector was removed from the facility, surveys were performed by FPL personnel and no other radioactive material was found. An investigation is in progress to determine the origin of the material." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-05
39561 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-02-04 22:40 | 2003-02-05 00:12 | 2003-02-05 | LOSS OF METEOROLOGICAL DATA AT SALEM AND HOPE CREEK STATIONS "THIS 8-HOUR NOTIFICATION IS BEING MADE TO REPORT THAT THE SALEM AND HOPE CREEK SITE LOST ALL METEOROLOGICAL DATA FOR WIND SPEED, DIRECTION AND TEMPERATURE AT 1440 ON 2/04/03. ALL THREE UNITS ARE OPERATING AT 100% POWER. NO ACTUATIONS HAVE TAKEN PLACE RELATED TO THIS EVENT. THE CAUSE OF THIS LOSS IS BEING INVESTIGATED. PROCEDURAL GUIDANCE IS AVAILABLE TO OBTAIN THE NECESSARY DATA FROM THE NATIONAL WEATHER SERVICE SHOULD THIS DATA BE NECESSARY." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-02-05
39560 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-02-04 14:34 | 2003-02-04 16:05 | 2003-02-04 | FITNESS FOR DUTY "A licensed operator tested positive for a controlled substance as a result of a random test. The employee's access to the protected area has been terminated. The employee has requested split sample testing. The NRC Resident Inspector has been notified." | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2003-02-04
39559 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-02-04 09:58 | 2003-02-04 11:24 | 2003-02-04 | REACTOR TRIP CAUSE BY A HI-HI LEVEL CONDITION IN STEAM GENERATOR "While replacing a feedwater transmitter, digital feedwater control for CFPT (condensate feedwater pump turbines) and all 4 S/G (steam generators) went to manual. The corresponding feedwater swing caused a Hi-Hi level condition in 1B S/G which resulted in a turbine trip, subsequent reactor trip and auxiliary feedwater auto start. All systems functioned normally." All rods fully inserted and auxiliary feedwater pumps operated properly. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-02-04
39558 | -1 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2003-02-03 17:45 | 2003-02-03 19:51 | 2003-03-27 | CONTROL ROOM VENTILATION FILTER TRAIN INOPERABLE "Plant identified a condition which could render the Unit 1 Control Room Ventilation Filter Train inoperable. This filter train is designed to mitigate radiological conditions within the occupied Control Room during an accident. A distorted cover was identified on ventilation ductwork which failed to provide an adequate seal. The ductwork is under repair and investigation is in progress." The licensee notified the NRC resident inspector. *** RETRACTION ON 3/27/03 AT 0940 EST RECEIVED FROM DAVID FIELDS TO ARLON COSTA *** "FPL is retracting this notification based on a subsequent Generic Letter 91-18 operability analysis of the observed condition. The operability assessment determined that the postulated in-leakage from the distorted ductwork cover plate was bounded by the maximum allowable alternate source term methodology unfiltered in-leakage. The analysis concluded that the control room envelope continued to meet its required safety function with respect to dose. Therefore the condition does not meet 10 CFR 50.72 or 50.73 reporting requirements." The licensee notified the NRC resident inspector. Notified R2DO (Bernhard). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-02-03
39557 | 0 | JANX |  |  |  |  | 2002-12-31 | 2003-02-03 16:35 | 2003-02-03 | PERSONNEL OVEREXPOSURE The Assistant RSO for JANX, Inc. reported that a radiographer working for JANX had, as of the end of 2002, received greater than 5 Rem occupational exposure for the year. The total exposure was 5.81 Rem based on film badge up to December 2002 and pocket dosimetry for December 2002. The employee began work for JANX in October 2002 but at that time no exposure information for previous employment was available. Film badge data of exposures received during employment with two other employers indicated an earlier 2002 exposure of 2.43 Rem. This data was received by JANX on 1/31/03 at which time the overexposure was recognized. The employee has been unemployed since mid-December 2002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2003-02-03
39555 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-02-03 09:40 | 2003-02-03 11:36 | 2003-02-03 | OFFSITE NOTIFICATION DUE TO EXCEEDING DISCHARGE PERMIT LIMITS "Notification made to other government agency, the EPA. "A telephone call was made at 09:40 am EST on 02/03/03 to the Ohio EPA North East District Office to verify permit requirements for the 'Other Requirements' section, an independent section of the permit. Copper outfall of 44ug/l [micrograms/liter] exceeded limit of 38 ug/l [micrograms/liter]. The following information was extracted from the licensee's facsimile report: "The copper sample for the plant outfall was above the Preliminary Effluent Limit (PEL) of the National Pollutant Discharge Elimination System Permit. This sample is taken as part of the 'Other Requirements' section of the permit. This new sample requirement and PEL were added in July to gather data to determine if copper sampling will be added to future permits. The data would also be used to determine the actual effluent limit. PNPP does not add any copper additive to the plant. It is believed that the copper increase from intake to outfall is from heat exchanger tubing using 'Admiral T Brass' which contains copper. This high reading on outfall copper was due to an increase of lake water copper from the lake freezing." The licensee notified the NRC resident inspector. | 74 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-02-03
39554 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2003-02-01 01:45 | 2003-02-01 09:41 | 2003-03-13 | LOSS OF A SAFETY FUNCTION DUE TO ALL FOUR EMERGENCY DIESEL GENERATORS BEING DECLARED INOPERABLE The following information was received from the Licensee via facsimile: "At 0145 hours [EST] on 2/1/2003, all four Emergency Diesel Generators (EDGs) were declared inoperable following discovery of a Fuel Oil leakage drain path change that was installed to prevent Fuel Oil leakage from reaching the ground water. "This change involved the installation of plastic sleeves on the fuel oil drains for all four EDGs to reroute the fuel oil drains to a catch basin. The normal drain path is through the RHR [Residual Heat Removal] Complex (which houses the EDGs) drain system to the chemical pond. This change was installed after a crack was discovered in a 21 inch concrete line in the drain path from the RHR Complex Drain Sump to the Chemical Pond. This change was installed on 01/17/03. "While running EDG 11 for post maintenance testing following a scheduled maintenance outage, fuel oil in a drain sleeve backed up and spilled out of a vent on the fuel oil drain header. This spillage resulted in a small lagging fire. EDG 11 was immediately shutdown and the fire was extinguished within a few minutes. No significant damage to EDG 11 was caused by the fire. Since all four EDGs had a similar fuel oil drain configuration, they were declared inoperable at 0145 hours and Technical Specification 3.8.1, Condition B was entered, which requires restoration of one division of the EDGs within 2 hours. "At 0329 hours, the normal fuel oil drain configuration was restored for EDG 13 and EDG 14 (Division 2) and Technical Specification 3.8.1, Condition B was exited. At 0345 hours, the normal fuel oil drain configuration was restored for EDG 12 (Division 1). EDG 11 remains inoperable until the completion of post maintenance testing. "This notification is being made in accordance with 10CFR50.72(b)(3)(v)[(D)] due to all four EDGs being inoperable causing the loss of a safety function." The fire was extinguished without offsite assistance and there were no injuries due to the fire. The Licensee has notified the NRC Resident Inspector. *** RETRACTION AT 1118 EST ON 3/13/03 FROM PATRICK FALLON TO ERIC THOMAS *** "While running EDG (Emergency Diesel Generator) 11 for post maintenance testing following a scheduled maintenance outage on February 1, 2003, fuel oil in a drain sleeve backed up and spilled out of a vent on the fuel oil drain header. This spillage resulted in a small fire. The fire caused no damage to EDG 11. Since all four EDGs had a similar temporary fuel oil drain configuration, they were declared inoperable. The normal fuel oil drain configuration was restored within the Completion Time of Technical Specification 3.8.1, Condition B. Notification was made in accordance with 10 CFR 50.72(b)(3)(v) due to all four EDGs being declared inoperable causing the loss of a safety function. "The cause of the fire is believed to be excessive fuel oil leaking from the EDG 11 fuel injector compartment onto the exhaust manifold. (The cause was initially reported as normal fuel injector leakage backing up into the fuel oil drain header due to the temporary drain configuration). The injectors allowed an abnormally high rate of fuel oil leakage into the fuel oil drain header for EDG 11 only. The fuel oil drain rates for EDGs 12, 13, and 14 were observed to be normal during subsequent surveillance testing, and within the capability of the temporary fuel oil drain configuration. "Therefore, EDGs 12, 13, and 14 were capable of performing their safety function and there was no common mode failure, as a result of the temporary drain configuration. This condition is therefore not reportable under 10 CFR 50.72(b)(3)(v). The original notification, Event Number 39554, is retracted." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-02-01
39553 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2003-02-01 03:10 | 2003-02-01 09:25 | 2003-02-01 | MAIN GENERATOR LOSS OF EXCITATION CAUSES A TURBINE TRIP THEN A REACTOR TRIP A loss of main generator excitation caused a turbine trip and, subsequent to that, a reactor trip. During the trip sequence, a non-1E electrical bus experienced low voltage and automatically transferred to an auxiliary bus. During the transfer, both Main Feedwater Pump (MFP) oil pumps tripped causing a trip of both MFPs. The loss of Main Feedwater caused low steam generator levels which initiated the Emergency Feedwater Actuation System (EFAS). EFAS restored steam generator levels to normal. All control rods inserted into the core. No power-operated relief valves, relief valves or code safeties lifted during the trip. The plant is removing decay heat via the steam dump to condenser system. The electrical grid is stable. The other at the site was not affected. The cause of the loss of generator excitation is under investigation. The NRC Resident Inspector was notified of the event by the Licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-02-01
39552 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-02-01 02:33 | 2003-02-01 04:35 | 2003-02-01 | MANUAL REACTOR SCRAM DUE TO CONDENSER TUBE LEAK "Inserted a manual reactor scram due to a condenser tube leak resulting in high condenser, feedwater and reactor water conductivity. " All control rods inserted into the core. There were no openings of power-operated relief valves, relief valves, code safeties, or dump valves. Cooldown is being accomplished via the Reactor cleanup to condenser system. All safety systems operated as expected. The switchyard is in a stable condition. The NRC Resident Inspector was notified by the Licensee. *** UPDATE ON 2/2/03 AT 0044 EST FROM MARK GILBERT TO HOWIE CROUCH VIA FACSIMILE *** "DAEC [Duane Arnold Energy Center] is making an addendum to EN [Event Number] #39552 made on 2/1/2003 at 0233. EN #39552 reported the insertion of a manual scram due to a condenser tube leak which was reportable under 10 CFR 50.72(b)(2)(iv)(B) for an RPS actuation. Following the insertion of the reactor scram, reactor water level dropped below 170 [inches] and PCIS [Primary Containment Isolation Signal] groups 2,3, and 4 were received. All isolations went to completion. The reactor water level drop is normal following a reactor scram due to the void collapse in the reactor vessel. Reactor water level was restored. Currently the plant is stable in Mode 4 and maintaining a normal reactor water level band. DAEC is currently making plans to determine the source of the condenser tube leak. "This addendum report is being made under [10 CFR] 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any systems listed in paragraph (b)(3)(iv)(B) of this section.' as a result of the PCIS groups 2 (Radwaste and TIP [Tranverse Incore Probe] system) and 3 (Containment atmosphere control system)." The NRC Resident Inspector was notified of the addendum by the licensee. | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-02-01
39551 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-01-30 13:00 | 2003-01-31 19:55 | 2003-01-31 | PLANT IN UNANALYZED CONDITION DUE TO INCORRECT INSTALLATION OF DRAIN SYSTEM CLEANOUT PLUG "At 13:00 EST on 1/31/2003, a system manager discovered a dirty radwaste floor drain system cleanout plug installed incorrectly in the Unit 1 A/C RHR room. The threads on cleanout plug were found not engaged. The plug was immediately installed terminating the condition. No check valves are installed in this cleanout line and therefore significant back leakage could occur into the RHR room. "This event resulted in a condition that could have rendered all trains of the RHR system inoperable during a flooding event by bypassing the normal floor drain system. "The time that this condition began is not currently known, pending investigation. A walk down of similar drains on both units is being conducted." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-01-31
39550 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-30 | 2003-01-31 14:00 | 2003-01-31 | TEXAS AGREEMENT STATE REPORT FOR LEAKING SOURCE "The University of Texas ordered a Sodium 22 (Na-22) positron source for research use. The Type A package arrived during the evening of January 30, 2003, and was unpackaged. During un-packaging it was noted that the Source was either leaking or contaminated. Attempts to decontaminate the source only resulted in higher reading. Leakage was measured at 30,000 DPM, therefore, over the 0.0005 uCi [microcurie] leakage limit. "The source arrived from the manufacturer: National Accelerator Center, Somerset West, South Africa. The report was made IAW 25 TAC 289.202 (bbb). A follow-up written report will follow by facsimile within 5 days. Chemical form of the source is solid sodium bicarbonate sealed in a titanium body. Source was leak tested due to the lack of a leak test certificate with the shipment. The inner packaging of the Type A container is also contaminated. No Model # or Serial # is readily apparent." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-02-05
39548 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-01-30 10:54 | 2003-01-30 14:42 | 2003-01-30 | MANUAL REACTOR SCRAM ON DECREASING REACTOR VESSEL LEVEL "At 10:54 CDT Grand Gulf Nuclear Station inserted a manual scram on decreasing vessel level as a result of the loss of all 3 condensate booster pumps. Loss of the booster pumps resulted in loss of normal feedwater to the vessel. Vessel level decreased to the auto initiation set point for High Pressure Core Spray (HPCS), Reactor Isolation Cooling System (RCIC), and Containment Isolation System. HPCS and RCIC started and injected to the vessel and the containment isolated. The HPCS initiation also included an auto start of the HPCS Diesel as expected. Reactor level was restored by injection of HPCS and RCIC. Vessel pressure was maintained by the turbine bypass valves. At present vessel level has been restored to normal. Systems affected by the containment isolation have been restored as needed. The cause of the condensate booster trips is under investigation. A review of plant data is underway to confirm proper response by equipment." There was an ECCS injection for 5 - 10 minutes. All control rods inserted and no relief valves lifted. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-01-30
39547 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2003-01-30 11:30 | 2003-01-30 14:23 | 2003-01-30 | INFORMATION CALL CONCERNING PRESS RELEASE ON SAFEGUARDS EVENT Press release regarding a safeguards event involving a flyover at Palo Verde. The press release was made by a local radio station, KTAR. The NRC resident inspector was notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW | [5 empty] | 0 | 2003-01-30
39546 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-01-29 20:32 | 2003-01-29 20:57 | 2003-01-30 | NOUE DECLARED AT SUSQUEHANNA DUE TO NON-ROUTINE RADIOACTIVE GAS RELEASE "At 8:32 pm EST PPL Susquehanna , LLC, declared an Unusual Event for an Airborne Release. The EAL entered was 15.1.a A.2, I-131 > 2.08E+2 microcuries/minute. Chemistry sample did not indicate any Iodine in the release steam, however Cs-138 was detected in the sample which may have affected the vent stack monitor. Investigation continues. The release is being monitored by the plant Vent Stack monitoring system. The source of the release is unknown at this time. Plant procedures are being implemented to determine and isolate the source. Offsite monitors have been activated to monitor offsite dose rates. Activation of the Emergency plan and Offsite releases are reportable under 10CFR50.72(a)(1) and 10CFR50.73(a)(2)(viii)." The licensee has notified state and local officials and will notify the NRC Resident Inspector. A media/press release is planned. *** UPDATE at 0132 ET on 01/30/03 by Dave Flyte/ Phil Brady taken by MacKinnon **** Unusual Event was terminated at 0125 ET on 01/30/03. Investigation found that the release was from the off gas system via a drain trap which entered the ventilation system which then exited out the vent stack. According to licensee's records, the release was greater than 2 times their Technical Specification limit (208 microcuries per minute) from 1940 hours until 2111 hours. Max level detected was 600 microcuries per minute. No iodine was released just noble gases. NRC R1DO (Brad Fewell), FEMA (Nora Heyman), NRC/DOT (Petty Officer Baumgartner), Office of Homeland Security (Damon Edwards), and NRR EO (Bill Ruland) notified. The NRC Resident Inspector was notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-01-29
39545 | 0 | WHITING CORPORATION |  |  |  |  | 2003-01-29 | 2003-01-29 14:47 | 2003-02-12 | 10 CFR 21 NOTIFICATION - WHITING CORPORATION "This notice is being sent within the two day period to inform you of a safety concern related to Whiting cranes sold to utility companies prior to 1980. The problem was identified through engineering analysis. We are not aware of any failures. "The concern is specific to the Whiting #25 Hoist Unit (Gear Case). One or possibly two internal support bolts in this assembly may be significantly over-stressed. "The exact extent of the over-stressed condition can only be determined by individual analysis of each hoist in question; however, based on findings, a 50% reduction in rated hoist capacity of the effected cranes will allow for continued use of the cranes without compromising design safety factors. This limitation should be enforced until the over-stressed bolts have been replaced or analysis shows that an over-stressed condition does not exist. "Crane owners should contact us at Whiting-Nuclear@WhitingCorp.com and provide the following information; customer name, contact person, email address, telephone number, crane serial number and date of next scheduled outage. "I trust you find that the notification provided is satisfactory and in compliance with 10 CFR 21 reporting requirements. If you have any questions, please do not hesitate to contact me at fteggelaar@whitingcorp. com." * * * UPDATE ON 2/12/03 @ 1617 BY TEGGELAAR (fax) TO GOULD * * * "This is a follow up notice related to our previously reported 10 CFR 21 dated 1/29/2003. As a result of the ongoing investigation and resolution of the previous notice, we have identified 5 cranes that utilize a hoist configuration that does not match the description contained in the previous notice." These cranes are at the following facilities: Indian Point (thought to be Unit 1) Cooper Nuclear Station WPPSS-Hanford #2 [Columbia Generating] Vermont Yankee Millstone (Believed to be Unit 1) "We have or are attempting to contact these customers directly to notify them of this circumstance. These are the only additionally impacted customers we have identified. These were special hoist arrangements using a # 10 hoist unit (gearcase) as opposed to the previously identified #25 hoist unit. "The hoist units identified above are to be limited to 20% of rated capacity to prevent compromising design factors, until such time as the Units can be upgraded." Notified R1 DO (Meyer), R2 DO (Lesser), R3 DO (Burgess), R4 DO (Marschall), NRR (Foster), NRR (Zwolinski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 21.21 |  |  |  | 0 | 2003-01-29
39544 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-01-28 15:30 | 2003-01-28 22:57 | 2003-01-28 | NRC BULLETIN 91-01 24 HOUR NOTIFICATION - PADUCAH GDP "At 1530 On 1-28-03, the Plant Shift Superintendent (PSS) was notified that the condenser pressure on Unit 4 Cell 9 in C-335 was not monitored at the require[d] frequency. When the condenser return valve will be closed and the supply spool piece will remain in place, the condenser supply pressure must be maintained at 20 psig or less to ensure that less than 10Kg of water can enter the process gas system. In order to ensure the pressure Is maintained below the maximum allowable pressures a gauge is installed arid monitored at a frequency of once every 8 hours for Unit 4 Cell 9 in C-335. The gauge was installed and first read at 2245 on 1-27-03. The next reading was taken at 0950 on 1-28-03. This period exceeded the 8 hours allowed. The NRC Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: "The pressure reading frequency was violated, however, the RCW [Recirc Cooling Water] pressure limit was not exceeded. Although a control relied upon for double contingency was violated. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR "In order for criticality to be possible, there must be a large condenser leak at the same time as a high RCW pressure. In addition, the high RCW pressure condition would have to go unnoticed and uncorrected beyond the specified time limits. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC "Double contingency is maintained by implementation of two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND WORST CASE CRITICAL MASS): "No known mass of licensed material exists in the condenser. System NCS limit is [deleted] wt.% U235. "NUCLEAR CRITICALITY SAFETY CONTROLS) OR CONTROL SYSTEMS(S) AND DESCRIPTION OF THE FAILURES OR DEFICITS "The first leg of double contingency is based on the ability to identify a pressure exceedance of the RCW condenser pressure limit within 8 hours. RCW pressure readings are monitored at a frequency at 1/2 the time it would take for an unsafe mass of moderator to leak into the process gas side. The RCW condenser pressure reading was obtained after the 8 hour time limit. Therefore, this leg of double contingency was lost. "The second leg of double contingency is based on the ability to check the pressure reading within 16 hours and to take corrective actions within 23 hours. The pressure was checked within 16 hours and was not In excess of the limit. Since the pressure limit was not exceeded, this leg of double contingency was maintained. "Since the first leg was lost, the double contingency principle was violated. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "At the time of discovery, the appropriate frequency of monitoring was identified and initiated." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-01-28
39543 | 0 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2003-01-28 10:30 | 2003-01-28 17:27 | 2003-01-28 | MEDICAL MISADMINISTRATION - RADIATION DOSE EXCEEDED PLANNED DOSE The following is taken from a facsimile sent from the licensee: A patient with and injury in the right coronary artery was to be treated with Novoste Sr-90 40 mm [millimeter] 3.5 Fr [French] device for 4 minutes 31 seconds each for a pullback procedure. The radiation oncologist had difficulty with the device and had to perform an emergency bail-out. We later confirmed that the sources were stuck either inside or just slightly outside the device, so there was no dose to the patient. The decision was made to proceed with the treatment with the Novoste Sr-90 40 mm 5 Fr device. The radiation oncologist scrubbed and primed the catheter with the dummy device. The change in the treatment device and new treatment time of 3 minutes 41 seconds was noted on the QM form. The revised treatment time, however, was not entered into the stopwatch. Only the physicist verified the time on the stopwatch and because of the similarities in the timing units (4 m 31 s versus 3 m 41 s),did not catch the error in time on the stopwatch. At the end of the treatment the physicist noted that the timer had not been reset for the 5 Fr device. During the 50 extra seconds of treatment time the patient received a dose of 28.2 Gy [Gray] rather than the prescribed dose of 23 Gy (22.6% more than the prescribed dose). The patient was informed of the error by the radiation oncologist and cardiologist later the same day. No adverse effect is expected for the patient "Some of the corrective actions under review include: 1. Improve the double-checking process prior to the start of the treatment. Usually the radiation oncologist double checks the treatment time, but in this case he was scrubbed and could not fully confirm the change in the treatment time on the QM form. Also the clinical coordinator who double checks the time programmed into the stopwatch and handles the back-up timer, was not available during this case, 2. The emergency bail out procedure disrupted the normal flow of the treatment. The team needs to be very aware of the greater vulnerability to error whenever emergency procedures are involved. 3. Scheduling issues may need to be addressed. 4. Additional training issues may need to be addressed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-01-28
39542 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-01-28 09:30 | 2003-01-28 11:39 | 2003-01-29 | PRE-ACCESS CONTRACT SUPERVISOR ACCESS TERMINATED DUE TO A CONFIRMED POSITIVE TEST FOR A CONTROLLED SUBSTANCE. At 09:30 on 01/28/03, a contract supervisor for the turbine upgrade project had a confirmed positive for a controlled substance during a pre-access fitness for duty test. The supervisor's access to the station has been suspended in accordance with the station's fitness for duty program. The NRC Resident Inspector was notified of this event by the licensee. * * * UDATE ON 01/29/03 AT 1414 EST FROM DON ROLAND TO GERRY WAIG * * * "Please note the following correction: "The contract supervisor had a confirmed positive test for a controlled substance during a random FFD test, not a pre-access test as previously reported. The error was a result of misinformation provided by the site testing facility to the Control Room. The individual remains suspended and his access to vital areas & work performance while employed at Susquehanna LLC is presently under review. The NRC residents have been notified." Notified R1DO (Dan Holody) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2003-01-28
39541 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-01-28 09:20 | 2003-01-28 10:05 | 2003-01-28 | OFFSITE NOTIFICATION "A fake news article was created on the internet. This fake article appears to be a CNN report that claimed Seabrook is under intense FBI investigation for dumping several radioactive uranium cores. "The [NRC] resident inspector was notified at 09:20, and the shift manager was notified shortly after. NRC would like to be notified if a press release will be [issued by Seabrook]. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-01-28
39540 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2003-01-22 21:51 | 2003-01-27 17:40 | 2003-01-27 | INVALID AUTOMATIC START OF EMERGENCY DIESEL GENERATOR DURING TESTING "On January 22, 2003, at 2045 hours, with Unit 2 in Mode 5 (refuel), the 2B Emergency Diesel Generator (DG) automatically started during the performance of a Unit 2 High Pressure Excess Flow Check Valve Operability Test. The apparent cause was an improper manipulation of instrument isolation valves during the test, which caused the associated Reactor Vessel Water Level Transmitters to sense a low level condition. This invalid low level signal resulted in the automatic actuation of the 2B DG (Div. III) which is the emergency power supply to the Unit 2 High Pressure Core Spray (HPCS) System. The Unit 2 HPCS pump had been properly removed from service prior to the event and therefore did not actuate. This system actuation is reportable under 10CFR50.73 (a) (2) (iv) (A). "The 2B DG responded normally and reached normal speed and voltage. It was run both loaded and unloaded successfully, and was secured at 0238 on January 23, 2003. "This report is being made in accordance with 10CFR50.73 (a) (1), which states that in the case of an invalid actuation reported under 10CFR50.73(a)2)(iv), other than an actuation of the RPS when the reactor is critical, the licensee may provide a telephone notification to the NRC operations center within 60 days after discovery of the event Instead of submitting a written LER." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-01-27
39539 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-01-23 16:30 | 2003-01-27 15:16 | 2003-02-26 | AGREEMENT STATE REPORT - CONTAMINATED PACKAGE The following is taken from a facsimile from the State of California: "On 1/24/03 the RSO [Radiation Safety Officer] @ IPL [Isotope Products Laboratories] reported their receipt of a contaminated package. The package had been picked up from LAX & delivered to IPL on 1/23 @ 2:25 pm by Kamino Int'l Transport, 2580 Santa Fe, Redondo Beach, contact person [DELETED]. The package was wiped upon receipt, and received the results approximately 4:30 pm. The RSO was notified the next morning. The contamination appears to be H-3, although the licensee needs to perform an energy calibration on their liquid scintillation counter to verify both this and their quantification of the package wipes. It appears that all sides of the package were contaminated, at up to approximately 100,000 dpm/wipe. The latest wipes measured up to approximately 40,000 dpm/wipe. "The package came from a company in Switzerland called RC Tritec AG, who is a distributor for a Russian company (unknown name at this time). IPL believes that the box was trans-shipped, & was never actually at Tritec, but they're still trying to get Lufthansa's paperwork. IPL is also trying to get info on the Russian company. "IPL had the delivery truck return to IPL, & they found a small area of contamination, about 12 X 10 inches, on the carpet, where the package was located, of about 800 dpm/wipe. After vacuuming, they got nothing. About 11 other wipes in the truck were negative. They checked the driver's gloves- there's no removable contamination. All wipes @ IPL's Shipping Dept were negative. They think there was at least one other package on the truck that was destined for an electronics company, but they're still trying to get info on that. There was at least one other package for IPL on the truck that was not contaminated (they're checking to see if it had come from the same Russian company). "Note: Assuming that the contamination is H-3, the dose consequences of 100,000 dpm/wipe are approximately equivalent to the dose consequences of 2.5 dpm/wipe of Cs-137." * * * RETRACTION ON 02/26/03 BY GREGER TO CROUCH * * * This retraction was e-mailed to the Headquarters Operations Officer on 1/29/03 but not posted until 02/26/03 due to administrative oversight: "This package was not contaminated with H-3 as initially thought. The substance causing the liquid scintillation counts was a non-radioactive phosphorescent material that got on the package at the shippers facility. This was confirmed by holding the wipes overnight in a dark environment before counting them. THIS REPORT IS BEING RETRACTED." Notified Fred Brown (NMSS), Eric Leeds (NMSS) and David Graves (R4DO) via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-01-30
39538 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2003-01-27 08:44 | 2003-01-27 10:05 | 2003-01-27 | UNIT 3 MANUALLY TRIPPED DUE TO LOW STEAM GENERATOR LEVELS The following information was submitted via facsimile: "Manual reactor trip on Unit 3 due to low steam generator levels caused by a loss of instrument air pressure. Instrument air pressure has been restored." Operators manually tripped Unit 3 following the loss of instrument air (IA) pressure which resulted in closing of the main feedwater regulating valves. IA can be supplied from one of four compressors; two motor driven and two diesel driven. When the operating motor driven air compressor breaker tripped, both diesel driven compressors received a start signal (the other motor driven compressor had been previously removed from service). One of the diesel driven compressors failed to start while the other started and tripped. IA pressure was restored by manually starting one of the diesel units. The licensee has the cause of the IA loss under investigation. Following the manual reactor trip, all three turbine driven auxiliary feedwater pumps started as expected. The licensee is in the process of restoring normal feedwater and returning the auxiliary feedwater pumps to standby. The atmospheric steam dumps are currently in service to remove decay heat (no known primary-secondary leakage). All control rods fully inserted. The licensee will notify the resident inspector and does not plan a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-01-27
39537 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-26 00:17 | 2003-01-26 02:21 | 2003-01-26 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "Cook Nuclear Plant Unit 2 Technical Specification 3.8.1.1.b requires two separate and independent diesel generators to be operable. Action b specifies [that] if one diesel is inoperable, then 'restore diesel generators to OPERABLE status within 72 hours or be in at least HOT STANDBY within the next 6 hours and in COLD SHUTDOWN within the following 30 hours.' Unit 2 diesel generator 2-OME-150-CD (Unit 2 CD diesel generator) has been inoperable since 04:00 on January 23, 2003 for scheduled maintenance. During post-maintenance testing, diesel load fluctuations occurred which continued to render the diesel inoperable. Diagnostic testing continues on the Unit 2 CD diesel generator. When it became evident operability of the Unit 2 CD diesel generator would not occur by the expiration of the 72 hour Limiting Condition of Operation at 04:00 on January 26, Cook Unit 2 began a power reduction from 100% reactor thermal power. The power reduction began at 00:17 on January 26 at a rate of approximately 20% per hour with a plan to manually trip the reactor to enter Mode 3 (Hot Standby) at 17% reactor thermal power at approximately 05:00. A cooldown to Mode 5 (Cold Shutdown) is expected within 30 hours of the entry to Mode 3 (Hot Standby) in accordance with Technical Specification 3.8.1.1, action b. "This Four Hour Report is being made in accordance with 10 CFR 50.72(b)(2)(i) for the initiation of a nuclear plant shutdown required by a plant's Technical Specifications. "There were no emergency plan or radiological release issues with this Unit 2 event. Unit 1 remains in Mode 5 with a main transformer replacement in progress." The Licensee notified the NRC Resident Inspector. * * * * UPDATE FROM CHARLES ARCHEY TAKEN BY MIKE RIPLEY AT 2310 EST ON 1/26/03 * * * * The licensee provided the following revised wording to reflect a re-evaluation of the Technical Specification requirements for the transition to Mode 5 if the Unit 2 CD diesel generator remains inoperable: "Cook Nuclear Plant Unit 2 Technical Specification 3.8. 1. 1 .b requires two separate and independent diesel generators to be operable. Action b specifies if one diesel is inoperable, then 'restore diesel generators to OPERABLE status within 72 hours or be in at least HOT STANDBY within the next 6 hours and in COLD SHUTDOWN within the following 30 hours.' Unit 2 diesel generator 2-OME-150-CD ('Unit 2 CD diesel generator') has been inoperable since 04:00 on January 23, 2003 for scheduled maintenance. During post-maintenance testing, diesel load fluctuations occurred which continued to render the diesel inoperable. Diagnostic testing continues on the Unit 2 CD diesel generator. When it became evident operability of the Unit 2 CD diesel generator would not occur by the expiration of the 72 hour Limiting Condition of Operation at 04:00 on January 26, Cook Unit 2 began a power reduction from 100% reactor thermal power. The power reduction began at 00:17 on January 26 at a rate of approximately 20% per hour with a plan to manually trip the reactor to enter Mode 3 (Hot Standby) at 17% reactor thermal power at approximately 05:00. "Transition to Mode 3 is expected after the 72 hour time limit is exceeded (04:00 on January 26) and before 10:00 on January 26 (6 hours following expiration of the 72 hour time limit). Transition to Mode 5 is expected before 16:00 on January 27 (within the following 30 hours) if the Unit 2 CD diesel generator remains inoperable. "This Four Hour Report is being made in accordance with 10 CFR 50.72(b)(2)(i) for the initiation of a nuclear plant shutdown required by a plant's Technical Specifications. "There were no emergency plan or radiological release issues with this Unit 2 event. Unit 1 remains in Mode 5 (Cold Shutdown) with a main transformer replacement in progress." R3DO (Christine Lipa) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 55 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-01-26
39536 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-01-25 14:14 | 2003-01-25 17:35 | 2003-01-25 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO A MAIN GENERATOR TRIP "At 1414 hours, with Surry Power Station Unit 2 at 100% reactor power an automatic reactor trip was generated due to a main generator trip. The main generator tripped due to a differential lockout. "Individual rod position indications (IRPI) for three control rods indicated between 11 and 20 steps following the trip. An emergency boration was initiated followed by a normal boration in accordance with station procedures to ensure adequate shutdown margin. The shutdown margin for Unit 2 was determined to be satisfactory. All other control rod indications fully inserted into the core as designed. The three IRPIs that initially did not indicate fully inserted slowly drifted to less that 10 steps. "All three auxiliary feedwater pumps automatically initiated as designed on low low steam generator level following the trip. Currently RCS temperature is stable at 547 degrees and being controlled by condenser steam dump valves. No primary or secondary safety or power operated relief valves were actuated during the event. No indications of primary to secondary leakage exist. "All electrical busses transferred properly following the trip and all emergency diesel generators are operable. At the time of the Unit 2 reactor trip, Surry Unit 1 was off-line due to a previous trip. Load shed occurred on the station service busses as designed. As a result of the load shed signal, the Surry Unit 1 "B" Main Feed Pump tripped. The Unit 1 "A" Main Feed Pump had previously been shut down. This resulted in a loss of both Main Feed Pumps on Unit 1 and restarted the Unit 1 Motor Driven Auxiliary Feedwater Pumps. "There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. The cause of the Unit 2 trip is being investigated. "Unit 2 is currently at Hot Shutdown with RCS temperature being maintained at approximately 547 degrees. Unit 1 is also at Hot Shutdown with RCS temperature being maintained at approximately 547 degrees. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv)." The licensee is investigating the cause of the main generator trip. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-01-25
39535 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-01-25 07:00 | 2003-01-25 09:25 | 2003-01-25 | UNIT 1 EXPERIENCED AN AUTOMATIC REACTOR TRIP ON LO-LO STEAM GENERATOR WATER LEVEL "At 0700 hours, with Surry Power Station Unit 1 at 25% reactor power during power ascension, an automatic reactor trip was generated due to 2/3 channels on 'B' S/G Lo-Lo Level. "All control rods fully inserted into the core as designed. Borated as necessary to ensure adequate shutdown margin. The shutdown margin for Unit 1 was determined to be satisfactory. 'A' and 'B' motor driven auxiliary feedwater pumps automatically initiated as designed on low low steam generator level following the trip. The turbine driven auxiliary feedwater pump tripped. All three Main Steam Trip Valves were manually closed due to the primary RCS cooldown. Primary RCS temperature decreased to approximately 526 degrees. Currently RCS temperature is stable at 547 degrees on the Secondary Power Operated Relief Valves. "No primary safety or power operated relief valves were actuated during the event. No indication of primary to secondary leakage exists, therefore no adverse radiological consequences resulted from this event. "All electrical busses remained energized following the trip and all emergency diesel generators are operable. There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. The cause of the event is being investigated. "Unit 1 is currently at Hot Shutdown with RCS temperature being maintained at approximately 547 degrees. 'Unit 2 was not affected by this event and remains stable at 100% power operations. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv)." Operators were in the process of transitioning between manual and automatic S/G water level control when the automatic trip occurred. The licensee will investigate the cause of the automatic turbine driven auxiliary feedwater pump trip. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-01-25
39534 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-11-25 | 2003-01-24 17:53 | 2003-01-24 | AGREEMENT STATE REPORT - DOSIMETRY LEFT IN RADIOGRAPHY AREA The following information was received from the Texas Department of Health, Bureau of Radiation Control (Texas incident I-7972): "During the monitoring period 11/25/2002 through 12/24/2002, radiographer [deleted] left his badge in an area where it was exposed by a radiography crew performing concrete rebar radiography with long exposure times. [deleted] phoned the licensee's corporate offices on January 23, 2003 to report a badge overexposure. At the current time it is thought that the radiographer reported the incident to his supervisor [deleted] RSO in the Clute [TX] Office. The date and time of that report is currently unknown. His badge exposure was measured at 8.266 Rem. A final report has not been received from the badge processor by the Licensee's corporate office, only a Fax transmittal. The corporate office indicated the incident was not previously reported to the corporate office or they would have had the badge submitted for emergency reading." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-01-29
39533 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-23 | 2003-01-24 14:50 | 2003-01-24 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the Texas Department of Health, Bureau of Radiation Control (Texas incident I-7973): "The nuclear gauge was stolen last night. (January 23-24, 2003). It was stolen from an Econoline van parked overnight at an apartment complex. The gauge was locked inside its case and was inside a storage compartment in the cargo area of the locked van. Access was gained by breaking out the windows of the van. "The gauge operator [DELETED] is uncertain of the exact time of the theft. He went out to dinner in his private vehicle and did not notice any problem with the van when he returned home at approximately 8 o'clock in the evening. However, when he stepped outside at 4:30 am to warm up his wife's car, he noticed the Duncanville [Texas] police were on the scene. Three vans parked within about 150 feet of each other, including his, had been burglarized in a similar fashion. One van belonged to an air conditioning company. "The thief took many other items from the van including concrete testing equipment, a coat, measuring tape and a couple of buckets of tools. The gauge and its case were taken. The case is clearly labeled with the company's name and phone number. Inside the case is a full set of paperwork identifying the gauge, a current leak test, and other documents containing the company's letterhead. The police report number is 03000589. The RSO notified Troxler in Arlington [Texas] of the theft." The gauge is a Troxler Model # 3430, Serial # 031693, 40 millicuries Am-241/Be, 8 millicuries Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-01-29
39532 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-01-24 | 2003-01-24 11:23 | 2003-01-24 | LOSS ENS AND OFFSITE COMMUNICATION "A major telephone line between Plant Hatch and Uvalda [GA] was damaged (cut) causing a major loss of communication system. "The ENS was inoperable, but the NRC could be notified by commercial line. The Prompt Notification (NOAA radios) was inoperable. Approximately one half of the ability to call offsite was lost (one half of the lines). "Note: The Prompt Notification System (NOAA radios) were returned to service at 1115 [EST]. Total out of service time was 45 minutes." The licensee notified the NRC resident inspector. * * * * UPDATE RECEIVED VIA FAX AT 1601 EST ON 1/24/03 FROM BARRY COLEMAN TO MIKE RIPLEY * * * * "We have a new update from Bell South. The line that was cut was not between the plant and Uvalda [GA]. They're repairing the cable now and expect all circuits to be restored by 4:00 PM. Apparently, some land clearing crews were working near the buried fiber between the plant and Baxley [GA] and severed BellSouth's fiber. "NOAA Problem - NOAA was already running on the secondary transmitter fed from Baxley. When the Baxley feed was cut this morning, the whole system shut down because the primary transmitter (fed from Brunswick) was already in error mode, for reasons unknown to us. We powered the entire system down and it started transmitting on the primary Brunswick feed as it should have been." The licensee notified the NRC resident inspector. Notified R2 DO (K. Barr). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-01-24
39531 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-01-24 00:45 | 2003-01-24 08:32 | 2003-01-24 | FAILURE OF ALL REFUELING WATER STORAGE TANK LEVEL INDICATORS "Event or condition that at time of discovery could have prevented the fulfillment of the safety function (FWST [Refueling Water Storage Tank] Auto Swap over). "Refueling Water Tank Level indication for all three channels failed high due to failure of automatic heat tracing which resulted in instrument lines freezing. Exited condition at 0342 hours on 1/24/03." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-01-24
39530 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-01-23 05:00 | 2003-01-23 08:09 | 2003-01-23 | INADVERTENT INITIATION OF ONE EMERGENCY SIREN "Inadvertent initiation of one emergency siren in Claiborne County. The Claiborne County Civil Defense Director has issued a 'No Emergency Message' to four local radio stations. This call-in is made to the NRC because of possible interest by the public. No additional actions are anticipated." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-01-23
39529 | 0 | UNIVERSITY OF IDAHO |  |  |  |  | 2003-01-22 | 2003-01-22 13:53 | 2003-01-23 | LOST EXIT SIGN CONTAINING TRITIUM The licensee reported that an exit sign containing upwards of 21 curies of tritium was missing. The sign had been installed in the Administration Building auditorium in the back stage area. The manufacturer of the sign was SRB. The licensee did not have the model or serial number of the sign at the time of the report. The licensee further indicated that no malevolent intent was suspected. The administration building had been undergoing renovation during the recent past. * * * * UPDATE FROM VICKY SCHUR TAKEN BY MIKE RIPLEY 1/23/03 AT 1632 EST * * * * The exit sign was manufactured by SRB, Inc. The sign is a model B100 Luminexit sign, serial number: 597374. The sign contained 9.75 curies of tritium as of 10/30/95 which was the shipment date from the manufacturer. The licensee stated that the manufacturer has confirmed that the sign has not been returned to them for disposal. The licensee continues to investigate the loss of the sign. Notified R4 DO (G. Pick) and NMSS (J. Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-01-22
39528 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-20 16:30 | 2003-01-21 12:10 | 2003-01-21 | AGREEMENT STATE REPORT - LOST AND SUBSEQUENTLY FOUND TROXLER MOISTURE DENSITY GAUGE The following information was received from the Texas Department of Health, Bureau of Radiation Control, Incident Investigation Group via facsimile: "Driver/Operator was at construction site on north side of San Antonio. Reported that he placed the gauge, without transport case, on the tailgate of his company pickup and completed his paperwork in the cab. When [he] completed [the paperwork], he forgot the gauge was still sitting on the tailgate and drove off from the site. Approximately 300 feet down the access road to Loop 1604, he realized that he had not put his gauge away. To return to the site, he had to loop around several access roads to get back to the area. When he arrived back at the construction site, he could not locate the gauge. He called his company for assistance. The company sent other employees to search the entire area without result and then reported the gauge missing to both the Hollywood Park and San Antonio Police Departments. In a call to the Agency [Texas Department of Health] at approximately 7:30 a.m. on January 21, 2003, it was reported that they believe the gauge was found by another contractor who was also departing the site the night before. It is believed that the gauge was put into the back of [the other contractor's] truck. The gauge is a Troxler 3440, Serial Number 30433, with two sealed sources: Cs-137, 8 millicuries, Serial Number 750-4901: and Am-241/Be, 40 millicuries, Serial Number 47-27488. The Radiation Safety Officer called at 10:53 a.m. on January 21, 2003, saying the gauge was recovered at the construction site at 7:30 a.m. this morning (01/21/2003) from another contractor who had found it onsite. The construction superintendent, when notified at home on the evening on January 20, 2003, had located the contractor who found the gauge, and arranged for the pickup this morning. The RSO did not have full details but has the gauge back in his possession. The gauge was visually inspected for damage and no apparent damage was noted. Radiation levels were normal for the gauge. However, a leak test was performed on the gauge. Results are pending. Both Police Departments have been notified of the recovery. It is not known if the helicopter flight was performed during the hours of darkness. [Hollywood Park Police notified the FBI and arranged for a helicopter to search for the gauge with infrared equipment.]" The vehicle was a company pick-up truck. (No description given or known by reporting official.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-01-24
39527 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-01-19 16:00 | 2003-01-20 16:25 | 2003-01-20 | CA AGREEMENT STATE REPORT FOR STOLEN COMPACTION GAUGE "California received a report on 1/19 at approximately 1600 PST of a stolen Campbell Pacific Nuclear (CPN) MC3 moisture density gauge (serial number N310800424) containing nominally 10 millicuries of Cs-137 and 40 millicuries of Am-241. The gauge was reported stolen overnight 1/18-19/03 from a vehicle parked at a private residence in San Francisco, CA. The gauge was inside a car, covered with a blanket. A car window was broken to gain entry, and the gauge and it's transportation case were stolen. The transportation case, minus the gauge, was found by police in the street approximately one mile away from the scene of the theft. The licensee involved is CA licensee Consolidated Engineering. CA staff are investigating. Local police have been notified. A reward will be offered for return of the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-01-23
39526 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-01-20 14:30 | 2003-01-20 20:13 | 2003-03-07 | SERVICE WATER SYSTEM VALVE PIT PIPING PENETRATION SEAL "On 1/20/2003 at 1430 hours, the Beaver Valley Power Station control room was notified by Engineering that a penetration seal previously installed in a wall which separates two service water system valve pits may have not been adequate. A review of the supporting analysis shows that this penetration seal may not be qualified to withstand the hydraulic pressure which could result from a postulated internal flooding event occurring due to a service water system pipe failure filling the valve pit and its above compartment prior to operator intervention. A failure of this seal during a postulated internal flooding event may result in the loss of motor operated valve movement in both trains of the service water system that would be needed following a design basis accident (DBA). "This design basis calculation and the penetration seal capability are continuing to be evaluated. However, this seal could potentially have prevented the service water system from meeting single failure criterion during a postulated service water system pipe failure. Therefore, Technical Specification (TS) 3.7.4.1 was entered due to less than two trains of service water system being operable as a conservative decision based upon the limited information immediately available to show acceptable seal integrity at the postulated conditions. The TS Action requires restoration of two independent service water system trains within 72 hours. Actions are in progress to install a qualified seal which will prevent the unacceptable flooding conditions from being able to occur. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition that significantly degraded plant safety since this seal has been installed for five months and may have invalidated the independence between the two service water system trains. The NRC resident has been notified of the degraded condition." * * * RETRACTION RECEIVED AT 1002 EST ON 3/07/2003 BY WITTER TO CROUCH * * * "Beaver Valley Power Station (BVPS) Unit No. 2 retracts the notification made on 01/20/2003 at 20:13 hrs [EST] regarding the event reported under 10 CFR 50.72(b)(3)(ii)(B) [ENS #39526]. The previous notification identified a potential issue with a seal penetration which may have invalidated the independence between two Service Water System trains. "Subsequent analysis of the event identified that the installed penetration seal between the two Service Water System valve pits would have been capable of performing its intended safety function. Therefore, the separation and independence between the two Service Water System trains, as required by Technical Specification 3.7.4.1, would have been satisfied. "Given that both trains of the Service Water System were able to perform their safety functions, this was not a condition that significantly degraded plant safety." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-01-20
39525 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-20 10:40 | 2003-01-20 14:40 | 2003-01-20 | RANDOM FITNESS FOR DUTY TEST FAILURE "A non-licensed contract supervisor tested positive during a random test. The employee's access to the plant has been restricted." Contact the HOO for additional details. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2003-01-20
39523 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-19 12:55 | 2003-01-19 21:25 | 2003-01-19 | VARIOUS SYSTEM ACTUATIONS AS A RESULT OF THE LOSS OF OFFSITE POWER The following information was received via facsimile: "At 1255 hrs on January 19, 2003, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 3 with Trains A and D reactor coolant pumps (RCP) running. While placing a surge reactor in the switchyard in service the Unit 1 standby transformer received a lockout and total loss of the North bus. "Unit 1 experienced a loss of offsite power (LOOP) to ESF Trains B & C. Both the Train B & Train C emergency diesel generators (EDG) started as expected. The Train C sequencer operated as expected and the Train C components automatically loaded, However, the Train B sequencer failed resulting in the manual loading of the Train B components in accordance with station off-normal procedures. This resulted in TS 3.0.3 entry in Unit 1 due to the loss of two (2) offsite power sources and the B train EDG (due to the failure of the B Train sequencer). There was a loss of letdown in Unit 1 when Train C isolated. Letdown was restored at 1313 hrs. At 1345 Unit 1 exited TS 3.0.3 when offsite power was restored to B Train. At 1406, offsite power was restored to C Train. The cause of the fault in the switchyard and failed Train B sequencer are under Investigation. "In Unit 2, Train A was aligned to the Unit 1 Standby transformer therefore, Unit 2 experienced a LOOP to ESF Train A. Train A emergency diesel generator automatically started and loaded as expected. As a result of the LOOP, Unit 2 experienced a loss of circulating water and loss of condenser vacuum. The Steam Generators (SGs) were already being supplied by the Auxiliary Feedwater system therefore no interruption to SG cooling. In addition, both Train A and Train D reactor coolant pumps tripped resulting in entry into TS 3.4.1.2, action B & C (boron control limitations and ensure Rx trip breakers open). There was a loss of charging due to the LOOP resulting in a Loss of RCP seal injection, however, component cooling water flow to the thermal barrier maintained seal cooling. Charging has been restored to supply seal injection. At 1840, when starting RCP 2A, pressurizer PORV 655A opened and reseated due to a pressure spike. Unit 1 remains at 100% power and Unit 2 remains in Mode 3." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-01-19
39522 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-01-19 12:52 | 2003-01-19 14:59 | 2003-01-19 | CONTAMINATED, INJURED WORKER TRANSPORTED TO LOCAL MEDICAL FACILITY The following is taken from a facsimile from the licensee: "At 1252 today, a worker in a Contaminated Area in Unit 2 Containment became overheated and required medical attention. The first aid team responded and required that the individual be transported while he was still contaminated. The individual has 100K [100,000] dpm by direct frisk on his skin in the area of his face and 10K [10,000] dpm by direct frisk on his clothing he was wearing. He was transported by local Rescue Squad. While in the ambulance he was decontaminated by HP [Health Physics] personnel that were assisting. Medical College of Virginia (MCV) was notified of a potentially contaminated person that was enroute. The individual is still being transported to MCV where he will receive medical treatment. The individual and ambulance are now clean and all contaminated material will be transported back to NAPS [North Anna Power Station]" The contaminated, injured worker was working on the installation of the blind flange on the fuel transfer tube. The North Anna Unit 2 reactor is refueled. The licensee will notify the NRC Resident Inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2003-01-19
39521 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-01-19 10:11 | 2003-01-19 12:19 | 2003-01-19 | SUSQUEHANNA UNIT 1 SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS The following is taken from a facsimile sent by the licensee: "At 10:11 hrs on 1/19/2003 Susquehanna Unit 1 began a shut down required by Technical Specifications. "At 13:06 hrs on 1/16/2003 the 'B' diesel generator was being returned to service following maintenance. This placed Unit 1 and Unit 2 into a 72 hour LCO (3.8.1 Cond. B). During its operability run, the governor exhibited erratic operation and the diesel was shut down. The 'E' diesel generator was re-substituted for the 'B' and an operability run was initiated. During the run, the 'E' diesel generator tripped on reverse power. Station personnel continue to troubleshoot the unrelated problems with the diesel generators. Initial engineering analysis has determined that there is no common mode failure with these 2 problems or with the remaining 3 operable diesel generators. "The 72 hour LCO for inoperability of 1 Diesel Generator (3.8.1 Cond. B) will expire at 13:06 hrs today. This will require both Unit 1 and Unit 2 to enter LCO 3.8.1 Cond. F, which requires both units to be in Hot Shutdown within 12 hours and Cold Shutdown within 36 hours. "An additional ENS report will be made when power reduction begins on Unit 2." The licensee has notified the NRC Resident Inspector of this event and plans to make a press release. * * * UPDATE 1600EST ON 1/19/03 FROM DAVID WALSH TO S. SANDIN * * * "At 15:38 hrs on 1/19/2003 the 'E' diesel generator was declared operable. This returned the station to 4 operable diesel generators and allowed exiting the LCO 3.8.1 Cond. B and Cond. F. Power reduction on Unit 1 was halted at approximately 50%. Unit 2 remained at 100% power. Current plans are to return Unit 1 to 100% power." The licensee is reviewing whether a press release will be made. Also, the licensee informed the NRC resident inspector of this update. Notified R1DO(Barkley) and NRR EO(Marsh). | 50 | 0 | 0 | 77 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-01-19
39520 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-01-17 14:43 | 2003-01-17 16:28 | 2003-01-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO FAILED SURVEILLANCE ON REACTOR TRIP BREAKER The following information was obtained from the licensee via facsimile: "At 11:40 [EST] on January 17, 2003, during surveillance testing of the 'B' train Reactor Trip Breaker (RTB), the breaker spuriously opened. This caused the RTB to fail its surveillance test and be declared inoperable. The facility Technical Specifications (TS), LCO 3.3.1 (Reactor Trip System Instrumentation), Action 8 of Table 3.3-1 requires 6 hours to Mode 3, Hot Standby. Rework activities were begun but the station commenced a power decrease at 14:43 [EST] to comply with the requirements of the TS. "At 15:10 [EST] on January 17, 2003, the activities, including retesting were completed and the breaker was declared operable at which time the plant exited from the TS Limiting Condition for Operability Action. At this time the power decrease was stopped. Power was held stable at 95% awaiting completion of all paperwork associated with this surveillance test. Power ascension commenced at 15:55 [EST]." Determined from the Licensee that the Reactor Trip Breaker spuriously opened after it was closed during the test. The breaker was replaced with another breaker and the surveillance test was performed on the new breaker successfully. The Licensee has informed the NRC Resident Inspector. | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-01-17
39519 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-01-17 11:30 | 2003-01-17 14:35 | 2003-01-17 | OFFSITE NOTIFICATION DUE TO VIOLATION OF DISCHARGE PERMIT The following information was obtained from a facsimile from the Licensee: "On 1/17/2003 at 1130 hours, the Beaver Valley Power Station received notification that an operator found raw sewage running from the Unit 2 Sewage Treatment Plant through a slightly open connection and immediately closed the isolation valve, stopping the flow. "Assessment by the Beaver Valley response determined that a sewage removal vendor had previously attempted to pump sludge from a plant sewage system, but nothing came out. He then apparently only partially closed the isolation valve and left the site. Subsequently, sewage began to flow out. Approximately 750 gallons of sewage was released down a storm sewer [drain]. An unknown quantity of sewage entered the Ohio River via Peggs Run. Approximately 50 gallons of sewage remaining on the surface at the local location is being cleaned up. "Pennsylvania Department of Environmental Protection (DEP) has been notified. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(xi) as a situation related to the protection of the environment for which notification to other government agencies have been made. The NRC resident has been notified." The notification to the Pennsylvania DEP was made due to a violation of the plant's discharge permit. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-01-17
39518 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-16 16:45 | 2003-01-17 12:18 | 2003-01-17 | TEXAS AGREEMENT STATE REPORT FOR STOLEN MOISTURE DENSITY GAUGE "Event location: Near intersection of Milam and 700 block of Clay Road, Houston, Texas (Downtown) "Event type: RAM Stolen (Stolen Moisture-Density Gauge) "Notifications: TDH Medical Duty Officer, TDH/BRC, City of Houston Police Department "Event description: Driver/operator returned to his vehicle at completion of the work day (construction site for a Houston Metro Station) and discovered the nuclear moisture density gauge and case are missing from his truck. The chain and lock were still attached to the truck. The company believes the gauge handle and latch were pried from the case. The gauge and case are missing. The missing gauge is a Troxler Model 3411B, Serial No. 20098, with two sealed sources: 8 millicuries of Cs-137, Serial No. 751355; and 40 millicuries of Am-241/Be, Serial No. 4715582". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-01-22
39517 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-01-16 17:00 | 2003-01-17 09:44 | 2003-02-11 | LEAKING PROMETHIUM - 147 SOURCE The licensee informed the Ohio Department of Health on 1/16/03 of a leaking Pm-147 source possibly caused by a defective or failed material. The source had been received by ABB from a customer in Japan (Yokagawa Electric). The source was contained and no spread of contamination was detected. ABB will inform the facility in Japan and properly dispose of the source. The leaking source was a 70 millicurie Pm-147, ABB model S-11. *****UPDATE BY FAX ON 2/11/03 AT 11:30 FROM MIKE SNEE TO RICH LAURA***** The leaking source was an ABB model S-20 instead of the earlier reported model S-11. Notified NMSS (F. Brown) and R3DO (S. Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-01-22
39516 | 0 | SCIENTECH |  |  |  |  | 2003-01-15 | 2003-01-16 21:52 | 2003-01-16 | 10 CFR 21.21 POTENTIAL DEFECTIVE COMPONENTS The following is taken from a facsimile received from Scientech, Inc.: "SCIENTECH, Inc.'s subsidiary, NUS Instruments, Inc. (NUSI) has determined that Basic Components, supplied in two CMM 900 Modules to Entergy-Fitzpatrick (P.O. #4500510231) and one CMM900 module to Constellation-Nine Mile Point (P.O. #00-31440) contain a defect that is reportable under 10CFR21. Additionally, NUSI has determined that other clients (see attached list) have been supplied assemblies containing components that may contain similar defects. NUSI is currently in the process of determining all affected model numbers and serial numbers. "NUSI determined that this potential defect was reportable on January 9, 2003 and the SCIENTECH, Inc. President was informed January 15, 2003. All potentially affected clients are being notified concurrently with this notification. "The defective component, OPA2111KP, was manufactured by Burr-Brown (aka TI or Texas Instruments-Tucson) and installed by NUSI in assemblies shipped to one or more of the clients identified in the attached client list. At this time only assemblies containing the OPA2111KP component have failed, as reported by Entergy-Fitzpatrick and Constellation-Nine Mile Point. NUSI has opened a 10CFR21 file concerning these components and has numbered it as 21-03-01. "TI has identified three additional part numbers (OPA111, 0PA404, and 3656) that NUSI currently uses that were manufactured by Tl utilizing the same process that was used for the manufacture of the defective OPA2111KP component; these other part numbers will require further evaluation. "A formal written report will be provided within 30 days of this notification." Potentially affected plants include: Region 1: Nine Mile Point, Millstone, Fitzpatrick, IP2 &3, Beaver Valley, Salem/Hope Creek (PSE&G), Ginna, Pilgrim. Region 2: Brunswick, Robinson, Harris, Crystal River 3. Region 3: Kewaunee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | ID | OTH | GEN | 21.21 |  |  |  | 0 | 2003-01-16
39515 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2003-01-16 16:40 | 2003-01-16 17:13 | 2003-01-16 | UNANALYZED CONDITION AT MILLSTONE 3 "This report is being submitted to report an unanalyzed condition that could significantly degrade plant safety in accordance with 10CFR50.72(b)(3)(ii)(B). As the result of an engineering analysis, it was determined that the fire safe shutdown strategy may not be adequate to ensure that the plant can achieve and maintain safe shutdown for certain fire scenarios. "On January 16, 2003, with Millstone Unit 3 in Mode 1 at 100% power, and as a result of transient analysis of certain fire shutdown scenarios, it was determined that postulated extended loss of all seal cooling events have the potential for over-pressurization of the Reactor Coolant Pump (RCP) No.1 seal leak-off line. The RCP No. 1 seal return line is designed to recover low pressure and temperature leak-off volume and return it to the volume control tank or charging pump suction. In response to a Cable Spreading Area, Control Room, or Instrument Rack Room fire, operation could be impacted because Emergency Operating Procedures (EOPs) may not adequately mitigate the scenario where a loss of all RCP seal cooling results in increased RCP seal leakage. This increased seal leakage assumption causes above normal pressure and temperature fluid conditions within the No. 1 seal return line. The over-pressurization that may occur could challenge the seal leak-off line structural integrity and a pressure boundary failure is considered possible. Per BTP 9.5-1, the credited injection pathway needs to be sufficient to preclude draining of the pressurizer below the indicating range. Because this condition would significantly complicate shutdown in the event of fire in these areas, this condition is being reported as an unanalyzed condition that significantly degrades plant safety, pursuant to 10 CFR 50.72 (b)(3)(ii)(B). "This condition assumes a fire of sufficient magnitude to cause a loss of all AC power which results in an extended loss of all seal cooling. This is considered to be a low probability event. "Compensatory measures are in place and include continuous fire watches in the Cable Spreading Area and the Instrument Rack Room. The continuous fire watch in the Control Room is satisfied by the presence of the Control Room staff. Additional fire extinguishers in impacted areas are in place. Administrative control requiring prior Shift Manager approval have been implemented to set limits on ignition source permits, use of transient combustibles, and use of flammable liquids within the impacted areas. Compensatory measures will remain until needed EOP revisions, plant modifications, or further analysis are made to address this condition. This condition remains under evaluation in accordance with the Millstone Corrective Action Program." The Licensee has informed the NRC Resident of this event. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-01-16
39514 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-01-15 21:15 | 2003-01-15 22:12 | 2003-01-15 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO STEAM GENERATOR CHANNELS DECLARED INOPERABLE "On January 15, 2003 at 2115 hours a Technical Specification required shutdown was initiated in accordance with the Technical Specification 3.0.3. Technical Specification 3.0.3 had been entered due to all four steam generator low-level channels in each steam generator being declared inoperable when the low-level trip setpoints were determined to be set below the allowable value specified in Technical Specification 3.3.1, 'Reactor Protection System Instrumentation', and Technical Specification 3.3.3. ' Engineered Safety Features Instrumentation'." NRC Resident Inspector has been informed. | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-01-15
39513 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-01-15 20:10 | 2003-01-15 21:01 | 2003-01-15 | UNUSUAL EVENT DECLARED DUE TO FIRE IN THE MAIN TRANSFORMER >15 MIN. Unusual event declared at 2025 EST due to fire in the Unit 1 main transformer caused main turbine trip, resulting in a reactor trip. All control rods fully inserted, all reactor coolant pumps are running with offsite power available. Cause of fire is unknown at this time. Fire was out at 2045 EST. Off-site fire assistance was called but fire was out prior to their arrival. One person transported off-site for minor injury due to fall. Environmental issues due to transformer oil and fire suppression. Environmental personnel are on-site. Clean-up is in progress. NRC Resident Inspector has been informed. ***Update 1/15/03 2238 Dan Malone to Howie Crouch*** Unusual Event terminated at 2220 EST. NRC Resident Inspector has been notified. Notified R3DO (Hill), NRREO (Marsh) and FEMA. ***Update 1/15/03 2339 EST Brian Bates to Howie Crouch*** "At 2010 on 1/5/03, a fault occurred in the Unit 1 Main Transformer, resulting in a fire. The fault caused an automatic main generator trip and an immediate turbine trip and reactor trip. The fire was originally extinguished at 2035, with one minor reflash that was promptly controlled by the fire brigade. The Emergency Plan was activated at the Unusual Event level due to a fire within the protected area not being extinguished within fifteen minutes. All applicable notifications were made for the Emergency Plan declaration, including a one-hour report to the NRC at 2100 (event notification # 39513). There was one minor personnel injury involved which required off-site medical attention, due to an individual suffering a fall and smoke inhalation. Offsite notifications were made to the National Response Center, Michigan Emergency Alert System, and the Local Emergency Planning Commission regarding the spilled transformer oil, which is currently being cleaned up. The auxiliary feedwater system actuated due to low steam generator levels after the reactor trip, as expected. There were no significant complications in the plant response to the reactor trip, and the unit is stable in Mode 3. The Unusual Event was exited at 2220." The Licensee notified the NRC Resident Inspector of this update. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2003-01-15
39512 | 0 | ROCKBESTOS-SUPRENANT CABLE CORP. |  |  |  |  | 2003-01-14 | 2003-01-15 16:42 | 2003-02-21 | INITIAL NOTIFICATION OF 10 CFR PART 21 DEFECT/FAILURE TO COMPLY "The following information is supplied in accordance with the requirements of 10 CFR 21. "I. Name and address of individual informing the Commission: [Deleted] "II. Identification of the basic component supplied which fails to comply or contains a defect: "The KXL 760D insulation system (chemically crosslinked only) provided in some of the Firewall III cables manufactured from January 1992 thru June 1995 may include an alternate resin which was not part of the baseline qualification testing. "III. Identification of the firm supplying the basic component which fails to comply or contains a defect: "The Rockbestos-Surprenant Cable Corp., East Granby, CT facility. "IV. Nature of the defect or failure to comply and the safety hazard which is created: "Nature of Defect: An alternate resin material may have been substituted in the insulation system for Firewall III cables (chemically crosslinked cables only). Potential Hazard: The chemically cured insulation system utilizing KXL 760D for cables manufactured from January 1992 thru June 1995 may not be enveloped by qualification report QR5804. "V. The date on which the information of such defect or failure to comply was obtained: "On the basis of our evaluation it was determined on January 14, 2003 that a defect or failure to comply as defined by 10 CFR 21 existed. "VI. The number and location of all basic components which contain a defect or falls to comply: "The number and location of all basic components which may contain a defect or fail to comply is yet to be determined. "VII. The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: "Based on testing and analysis, both resin suppliers indicated that both resins were quite similar and they were not able to distinguish or identify one resin from the other. Documented evidence of their conclusion has been requested. Rockbestos-Surprenant has instituted a similarity analysis program on both resins that is expected to be completed by March 14, 2003. Preliminary test results indicate that the two resins are indistinguishable. A full report will be available upon completion of the similarity analysis program. " VIII. Any advice related to the defect or failure to comply about the basic component that has been, is being, or will be given to purchasers: "Purchasers will be advised not to install any Firewall III cables that employ the chemically cured insulation material that were manufactured from January 1992 thru June 1995 until the results of the similarity program are known. Further advice will be provided at that time." * * * * WRITTEN NOTIFICATION UPDATE RECEIVED BY LETTER ON 2/21/03 BY MIKE RIPLEY * * * The following changes to Sections VII and VIII were provided in the written notification: "VII. The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: "Rockbestos-Surprenant has implemented a two step process to evaluate the potential effect on baseline qualification arising from use of the alternate resin. "Step 1: "Because the two resins are so similar, locating finished cable for testing was not immediately feasible. In order to completely explore this avenue, samples containing both the qualified and alternate resins were sent by Rockbestos-Surprenant to both resin manufacturers to use whatever methods available to differentiate their resin in the finished material. If an analytical method could be found to identify the resin used, Rockbestos-Surprenant would look to the utilities to find inventory containing the alternate resin. Based on the cable available, an appropriate test program could be established to document qualification. Both suppliers have indicated, however, that they were not able to identify their resin in the sample provided. "Step 2 "Based on the limited availability of the alternate resin (discontinued in 1995) a similarity analysis program has been established by Rockbestos-Surprenant which is running in parallel with Step 1 that will compare the two resins. The program has been designed to address electrical performance, dielectric strength, physical properties, heat aging to end of life condition, irradiation with 200 Mrad exposure, and moisture absorption. FTIR scans will be generated for both finished samples including the starting resins for comparison. Testing is scheduled to be completed by March 14, 2003. Preliminary test results indicate that the two resins are indistinguishable. A frill report will be available upon completion of the test comparison program. "Additionally, third party testing consideration is being given regarding a proposed test program designed for analysis and identification of the resins. The submitted test program is currently being evaluated by Rockbestos-Surprenant. " VIII. Any advice related to the defect or failure to comply about the basic component that has been, is being, or will be given to purchasers: "Purchasers are being advised not to install Firewall III cables that employ the chemically cured insulation material that was manufactured from January 1992 thru June 1995 until the results of the test comparison program are known. Further advice will be provided at that time." Notified R1 DO (C. Anderson), R2 DO (C. Ogle), R4 DO (J. Madera), R4 DO (K. Kennedy), NRR (J. Foster), NMSS (R. Torres) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN | 21.21 |  |  |  | 0 | 2003-01-15
39511 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-01-02 | 2003-01-15 16:12 | 2003-01-15 | OFFSITE NOTIFICATION TO OSHA OF EMPLOYEE'S DEATH On January 2, 2003, an employee was burned by steam and scalding water released from a tank. There was no radioactivity involved in this release. The employee was treated at an emergency room and then later transferred to the University of Virginia hospital. The employee passed away on 01/15/03. The licensee will be making a notification to OSHA and issuing a press release. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (2) |  |  |  | 1 | 2003-01-15
39510 | 0 | PENNSYLVANIA HOSPITAL |  |  |  |  | 2003-01-13 12:00 | 2003-01-15 13:49 | 2003-01-16 | DAMAGED IODINE-125 SEED RESULTS IN DOSE THAT DIFFERS FROM PRESCRIBED DOSE BY >20 % "On Monday January 13, 2003 a prostate implant was performed on [DELETED]. The seeds that were used were Amersham's Echoseed. Each seed had an activity of 0.472 [millicurie] apparent activity (NIST 1999) on the day of the implant. The actual activity is 1.78 times the apparent activity which results in an actual activity of 0.84 [millicurie]. "During the implant there was difficulty in removing a cartridge. Once the cartridge was removed, there was some activity that registered in the Mick gun. A blood clot that registered radioactivity was expelled from the gun and was isolated and the implant proceeded. This involved the last seed in a Mick disposable cartridge. "Once the implant was completed, the blood clot was examined and was found to contain a fragment of a seed. The entire operating room was checked carefully to see if the other portion of the seed was anywhere on the operating room. There was no contamination found in any of the instruments or in any of the used cartridges with the GM probe. No seeds or any activity was discovered during cystography or in any of the trash in the operating room. The feet of all the individuals involved in the procedure were checked in case a seed adhered to a shoe covering. It was assumed that the remainder of the seed was placed in the patient's prostate. The radiation oncologist ordered that the patient be given a blocking dose of iodine in the form of Lugol's solution. The radiation oncologist informed the patient that he was being placed on this medication because of the possibility that a leaking seed was implanted." The prescribing physician has informed the patient. * * * UPDATE ON 1/16/03 AT 1123 BY SHABASONS TO GOULD * * * The licensee originally reported this event under 10 CFR 35.3045(a)(1) and called to change it to 10 CFR 35.3045(a)(2). The licensee estimates that the thyroid dose is <5 Rem. The NRC Headquarters Operations Officer notified the R1DO (Richard Barkley) of this update. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2003-01-15
39509 | 0 | ALLEGHENY GENERAL HOSPITAL |  |  |  |  | 2003-01-14 15:00 | 2003-01-15 13:08 | 2003-01-15 | ESTIMATED OVEREXPOSURE TO SKIN OR EXTREMITIES > 50 REM An employee at the hospital was found to have an estimated 6 microcuries of I-131 contamination on his right index finger. It is suspected that he received the contamination while working in the hot lab. Decontamination efforts are in progress at this time. There is no spread of contamination in the hot lab and an investigation is in progress. The estimated exposure to the finger is > 50 Rem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2202(b)(1) |  |  |  | 0 | 2003-01-15
39508 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-01-13 19:30 | 2003-01-14 15:02 | 2003-01-15 | AGREEMENT STATE REPORT INVOLVING LOST SOURCES The Licensee reported the loss of five 0.355 microcurie, I-125 brachytherapy seeds. The seeds were model # IAI-125A and they were inventoried upon receipt from the manufacturer, Iso-Aid. The seeds were being washed prior to sterilization (this is a deviation from procedure) and the licensee believes they were washed down the drain to the public sewer system. The Licensee reports that surveys do not indicate that they are in the sink or trap. ***UPDATE 01/15/03 1202 EST MIKE BRODERICK TO MIKE NORRIS*** The seeds are actually 0.355 millicurie sources. Notified NMSS (Brown) and R4DO (Sanborn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2003-01-17
39507 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-01-14 01:37 | 2003-01-14 04:18 | 2003-01-14 | MANUAL REACTOR TRIP DUE TO HIGH REACTOR COOLANT PUMP SHAFT VIBRATION "At 0137 hours, with Surry Power Station Unit 1 at 100% reactor power, a manual reactor trip was initiated due to elevated shaft vibrations (alert and danger) on 'C' Reactor Coolant Pump. "IRPI indication for one control rod indicated 25 steps following the trip. Borated as necessary to ensure adequate shutdown margin. All other control rods fully inserted into the core as designed. The IRPI indication for this rod is trending down at this time. The shutdown margin for Unit 1 was determined to be satisfactory. Auxiliary feedwater automatically initiated as designed on low low steam generator level following the trip. Primary RCS temperature decreased to approximately 541 degrees following the reactor trip and was stabilized at 547 degrees. "No primary safety or power operated relief valves were actuated during the event. As a result of the loss of turbine load, the secondary power operated relief valves actuated during the transient. No indication of primary to secondary leakage exists, therefore no adverse radiological consequences resulted from this event. "All electrical busses transferred properly following the trip. #1 EDG was T/O [tagged out] prior to unit trip. All other emergency diesel generators are operable. There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. The cause of the event is being investigated. "Unit 1 is currently at Hot Shutdown with RCS temperature being maintained at approximately 547 degrees. Unit 2 was not affected by this event and remains stable at 100% power operations. This event is being reported in accordance with 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv)." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-01-14
39506 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-01-13 06:18 | 2003-01-13 08:47 | 2003-01-13 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER CIRCULATING WATER PUMP At 0618 EST the #35 Circulating Water Pump tripped. The other circulating water pump supplying the same condenser section was out of service for maintenance. The resulting loss of all circulating water to one condenser section produced a high differential pressure between sections. The reactor was manually tripped in accordance with plant procedures. All controlled rods fully inserted. The Auxiliary Feedwater Pump automatically started as expected. During the transient, the #32 Reactor Coolant Pump tripped due to an unknown cause and is being investigated. Additionally, the # R14 Plant Vent Gas radiation monitor went into alarm and then immediately returned to normal, however the redundant monitor did not show any increase in radiation. Additionally, the #32 Source Range Detector did not come on scale on the reactor trip, however the redundant detector functioned normally. The electrical system responded normally. There were no releases associated with this event. The cause of the circulating water pump trip is under investigation. The licensee has notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-01-13
39505 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-01-12 23:04 | 2003-01-13 02:48 | 2003-01-13 | OPEN DUCTWORK ACCESS PANEL PREVENTED MAINTAINING CONTROL ROOM POSITIVE PRESSURE "On January 12, 2003 at 2304, control room pressure was observed to be negative. At the time the "A" Control Room Emergency Filtration (CREF) system was tagged out for scheduled maintenance. The event was initiated when technicians opened an access panel on the "A" CREF control room air supply duct within the control room boundary to repair a gasket. This resulted in both "A" and "B" trains of CREF unable to perform its design safety function: specifically, maintaining the control room at a 1/8 inch water gauge positive pressure relative to adjacent areas. Without assurance of CREF system providing positive pressure in the control room, mitigating the consequences of an accident could have been prevented. Upon discovering the cause, technicians were ordered to close the access panel. Control room pressure promptly returned to a normal, positive value. Total time at negative pressure was ten minutes. No unexpected response was experienced. In addition to the "A" CREF train, the "A" Hydrogen/Oxygen analyzer was inoperable at the time of the event." The licensee has notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-01-13
39504 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-01-12 15:53 | 2003-01-12 18:40 | 2003-01-12 | AUTOMATIC SCRAM ON LOWERING REACTOR VESSEL WATER LEVEL DUE TO FEED PUMP TRIP "Unit 1 was operating at 94 percent power (presently max power) when 1B Reactor Feed Pump (RFP) low oil pressure annunciator was received coincident with 1B RFP trip at 1552. Reactor water level lowered and initiated an automatic SCRAM as the Reactor Operator was inserting a manual SCRAM at 1553. All systems initiated and isolated as required. A group 6 [containment atmospheric and sampling] and Group 2 [drywell floor equipment drain isolation valves] isolation was received on low Reactor water level and verified. The Emergency Diesel Generators started as expected due to a reverse power lockout of the main generator. After the SCRAM the 1A RFP tripped on high water level. Prior to restarting a RFP a second SCRAM signal was received on low level. The Reactor Core Isolation Cooling (RCIC) system was manually started to restore level while the reactor feed pump was being restarted. The preliminary investigation indicates that the running lube oil pump on the 1B RFP tripped. The standby lube oil pump started however, apparently, did not recover lube oil pressure in time to prevent a trip of 1B RFP." All control rods properly inserted into the reactor core. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-01-12
39503 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-12 13:10 | 2003-01-12 18:14 | 2003-01-12 | LOSS OF MET TOWER DATA "Event: On January 7, 2003 the Primary Meteorological (Met) Tower was removed from service to repair the 76-meter wind direction function. Removing the primary tower from service results in all functions (i.e. wind speed, wind direction, and air temperature) being declared INOPERABLE. On January 12, 2003 at 1310, the 60-meter air temperature for the Back-up Meteorological Tower was declared INOPERABLE due to faulty readings. "Effects on Plant: This has resulted in a loss of the capability to determine differential temperature for emergency assessment (plume}. "Cause: The cause of the faulty Back-up Met Tower 60-meter temperature indication is under investigation. The Primary Met tower is INOPERABLE because it is disabled to correct the 76- meter wind direction function. "Actions Taken or Planned: 1) The portable meteorological monitoring system is being placed in-service per Diablo Canyon Power Plant (DCPP) Equipment Control Guideline (ECG) 40.l-B.1. This restores differential temperature monitoring capability. 2) DCPP maintenance personnel have been dispatched to repair either the primary or back-up tower. The plant will remain in a 7 day ECG until either towers air temperature monitoring function has been restored to OPERABLE status." The NRC Resident Inspector. has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-01-12
39502 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-11 21:45 | 2003-01-11 23:45 | 2003-01-12 | OFFSITE NOTIFICATION TO FBI AND LOCAL LAW ENFORCEMENT At 2345 EST on 1/11/03, the licensee reported that they had contacted the Charlotte, NC FBI and the Charlotte-Mecklenburg, NC police department concerning a report they received at 2145 EST on 1/11/03 from the Mt. Gilead, NC Volunteer Fire Department concerning a plastic traffic cone that was set on fire on Highway 73 approximately one-eighth mile east of the main entrance road to the McGuire Station and approximately one-half mile from the owner-controlled area checkpoint on the entrance road. The licensee will be informing the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-01-12
39501 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-10 23:20 | 2003-01-11 07:15 | 2003-01-11 | LOSS OF ALL METEOROLOGICAL DATA FOR WIND SPEED, DIRECTION, AND TEMPERATURE This report is from the Salem/Hope Creek site. Both Salem units and the Hope Creek unit are in power operation. "This 8-hour notification is being made to report that the Salem and Hope Creek site lost all meteorological data for wind speed, direction and temperature at 1520 [EST] on 1/10/03. All three units are operating at 100% power. No actuations have taken place related to this event. The cause of this loss is being investigated. Procedural guidance is available to obtain the necessary data from the national weather service should this data be necessary." The NRC resident inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-01-11
39500 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2003-01-10 11:56 | 2003-01-10 16:05 | 2003-01-10 | MANUAL SCRAM DUE TO LOWERING REACTOR VESSEL WATER LEVEL "This report is being made pursuant to 10CFR50.72(b)(2)(iv)(B), RPS Actuation (scram). At 11:56 CDST on January 10,2003, during normal operation, unit 2 was manually scrammed due to lowering vessel water level. The lowering water level was from the loss of the 2B Condensate pump and the 2A & 2C Heater Drain pumps which resulted in a loss of both Turbine Driven Feed Pumps. ECCS equipment responded as expected (no automatic injection or starts). Hot Standby Mode of Operation was achieved with out difficulties and residual heat is being rejected to the condenser. No Safety Relief Valves actuated. "Initial investigation revealed that the 2B condensate pump motor failed and may have resulted in an electrical fluctuation on electrical buses resulting in tripping some non-essential components. Further investigation, including troubleshooting is in progress for activities related to the condensate and heater drain pump loss." All rods properly inserted into the core. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-01-10
39498 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-01-10 09:00 | 2003-01-10 12:47 | 2003-01-10 | OFFSITE NOTIFICATION TO LOCAL COUNTY EMERGENCY AGENCIES "At 0905, an injury occurred to a worker when the individual received 2nd degree burns to his forearms. The worker was treated by the Company First Aid Team and released to Radiation Protection Personnel for deconning the individual. The burn area had some contamination of 100 to 400 counts above background. The individual was deconned by our Radiation Protection Personnel and our Company Medical Personnel and is no longer contaminated. The individual was released back to work. The local County Emergency Management Agencies were notified of the potential for transportation of the individual to a local hospital, but transportation will not be required. The individual has requested no medical treatment from the local hospital. The local County Emergency Management Agencies were re-notified that the individual would not be transported." The State of Ohio and local Counties were informed of this event. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-01-10
39497 | -1 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-01-03 10:00 | 2003-01-09 13:55 | 2003-02-10 | UNCOMPENSATED SECURITY GUARD DEGRADATION FOR 1 HOUR Immediate compensatory measures were taken upon discovery. The licensee notified the resident inspector. Refer to the HOO log for additional details. * * * UPDATE ON 2/10/03 @ 1208 BY LYON TO GOULD * * * RETRACTION The licensee is retracting this event The NRC Resident Inspector was notified. Notified Reis(EO) and Meyer(Reg 1 RDO) Contact the HOO for further information. * * * UPDATE ON 2/26/03 @ 1254 EST BY PRUSSMAN TO CROUCH * * * Licensee corrected statements made during retraction. Contact the HOO for further information. Notified Dennig (NRR EO) and Kinneman (R1DO). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-01-09
39496 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2003-01-09 05:40 | 2003-01-09 12:47 | 2003-01-09 | RHR VALVE AUTOMATICALLY WENT CLOSED INSTEAD OF OPEN DURING TESTING "At 0540 hours CST on 1/9/03 during the performance of QCOS 1000-09 (RHR Power Operated Valve Test), the RHR Injection Valve 2-1001-29A automatically closed upon achieving the full open position. Group II isolation relays for both the 2-1001-29A and 2-1001-29B valves were discovered energized, which would cause these injection valves to close thereby prohibiting the low pressure injection function for both RHR subsystems (note that no Group II isolation signal was present). As such, Technical Specifications 3.5.1 Condition D was entered. The isolation logic relays were reset (deenergized) at 0625 CST and the 2-1001-29A and 2-1001-29B valves were satisfactorily cycled. Technical Specifications 3.5.1 Condition D has been exited. A prompt investigation is in progress. "The notification is being made in accordance with 10CFR50.72(b)(3)(V)." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-01-09
39495 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-08 04:00 | 2003-01-08 11:23 | 2003-01-08 | LOSS OF ENS AND OFFSITE COMMUNICATION "At 04:00 on 01/08/03, normal offsite communications were lost. This included normal telephone lines, ring down lines to State and County officials, and the ENS line to the Nuclear Regulatory Commission. Communications were still available with the STP Coordinator via the ring down line and the 800 MHz radio. Also had communications established with offsite personnel via a satellite phone and cellular phones. Communications with Emergency Response Organization personnel was still available through backup notification instructions. "Normal communications were restored at 07:10 on 01/08/03. "This is being reported under 10 CFR 50.72(b)(3)(xiii). "The cause of this event was due to the tripping of a breaker that supplies power to our offsite communications equipment. This equipment has a battery backup and the battery supplied power to the communications equipment until it lost it's energy." NRC Resident inspector notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-01-08
39494 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-01-07 16:24 | 2003-01-07 18:32 | 2003-01-07 | AGREEMENT STATE REPORT ON LEAKING SOURCES Texas Department of Health received a telephone notification from Spectro Instruments that two 50 microcurie Fe-55 sources were leaking. Sources S/N 5069LG and S/N 6172LG were leak tested 0.4 microcuries and 0.13 microcuries respectively. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-01-10
39493 | 0 | MIDMICHIGAN MEDICAL CENTER |  |  |  |  | 2003-01-06 16:45 | 2003-01-07 12:33 | 2003-01-07 | MEDICAL EVENT < 50 % OF PRESCRIBED DOSE At 0830 on 1/7/03, it was discovered that a patient receiving braqchytherapy to the right lung using a high dose remote afterloader, received an actual dose less than the prescribed dose. The source was a 5.2 curie Ir-192 and the prescribed dose was 2000 cGy, which was to be administered in four 500 cGy increments. The computer was programmed for the four increments, but the total prescribed dose was set for 500 cGy, resulting in an actual dose delivered of 125 cGy. The patient was informed that the dose received was lower than intended and they would be receiving the total prescribed dose in the remaining three increments. The attending Physician will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-01-07
39492 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-11-22 09:43 | 2003-01-07 11:00 | 2003-01-07 | 60 - DAY OPTIONAL 10 CFR 50.73 REPORT - INVALID ACTUATION OF THE RPS SYSTEM "The following notification is provided by [Entergy Nuclear Operations] ENO regarding Indian Point Unit 2 pursuant to 10 CFR 50.73(a)(2)(iv)(A) as 'Any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS) including: reactor scram or reactor trip.' This notification is provided in lieu of submitting a written LER for a RPS actuation that was invalid and occurred while the reactor was subcritical. "On November 22, 2002, at approximately 0943 hours, a reactor trip signal occurred and the reactor trip breakers opened. The plant was in Hot Shutdown Condition following the completion of 2R15 refueling activities with the reactor subcritical (100 cps), and the Reactor Coolant System (RCS) temperature and pressure at 548 F and 2195 psig, respectively. Control rod testing was in progress with Control Rod Shutdown Bank 'A' withdrawn at two steps. All other control rods were at zero steps. "An invalid RPS actuation was initiated while in this condition due to ongoing work. At approximately 0930 hours, in preparation for control rod drop testing the reactor trip breakers were closed. At approximately the same time, technicians were in the process of re-terminating previously de-termed RCS narrow range [Resistance Temperature Detector] RTD's. At approximately 0940 hours, Control Rod Shutdown Bank 'A' was withdrawn at two steps to support control rod drop testing. At approximately 0943 hours, technicians landed a lead on loop 1 cold leg RTD, generating an Over Temperature Delta Temperature (OTDT) signal. This resulted in a reactor trip due to a 2/4 channel OTDT trip logic. OTDT channel 2 was previously placed in trip due to nuclear flux power range channel N-42 connected to the reactivity computer in support of low power physics testing. The reactor trip breakers opened, inserting Shutdown Bank 'A' rods. All other rods were already fully inserted. Plant response was as expected. This trip did not cause a primary or secondary transient. Plant recovery was achieved in accordance with existing operating procedures." Licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-01-07
39491 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-01-07 03:20 | 2003-01-07 06:05 | 2003-01-07 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM (SPDS) "At 0220 hours on 01/07/03, the Safety Parameter Display System (SPDS) portion of the Emergency Response Facility Computer System (ERFCS) was noted to be inoperable, due to all outputs being displayed in 'magenta' color. "Troubleshooting of the ERFCS determined that the 'B' train of the ERFCS had failed and prevented the 'A' train from booting as required. This resulted in the failure of both trains of ERFCS and SPDS. Instrumentation & Controls personnel were able to restore the 'A' train ERFCS and at 0450 hours on 01/07/03 the ERFCS and SPDS were returned to service. "SPDS was out of service for greater than 1 hour, which is considered a major loss of emergency assessment capability. "This report is being made in accordance with 10CFR50.72(b)(3)(xiii). "NRC, Mr. Crouch notified. Faxed to NRC # 301-816-5161 at 0618 hours." The NRC Resident Inspector was notified of this event by the Licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-01-07
39490 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-01-06 16:00 | 2003-01-06 16:58 | 2003-01-06 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "At approximately 7:30 AM, January 6, 2003, the Agency [Arizona Radiation Regulatory Agency] received a voice mail message advising that a Troxler Model 3440 device, Serial Number 30391, was missing from 4440 West Mountain View Road, Glendale, AZ. The device contains 8 millicuries of Cesium-137 and 40 millicuries of Americium-241:Berylium. The information supplied indicated that there is [evidence] that the device was stolen. LICENSEE believes the source disappeared between 2:00 AM and 6:00 AM January 3, 2003. Agency investigation indicates [that] the lock was cut and the device removed from the shipping case. Glendale Police Department is also investigating this event, report number 03-972. "The LICENSEE and the Agency continue to investigate this event. "The States of CA, CO, NV, NM, and UT and U.S. NRC and the U.S. FBI are being notified of this event. Mexico is also being informed of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-01-09
39489 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-06 11:00 | 2003-01-06 15:18 | 2003-01-06 | FITNESS FOR DUTY A non-licensed Supervisor tested positive for controlled substance during a random test. The employee's access to the protected area has been terminated. The NRC Resident Inspector has been notified. Contact the HOO for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2003-01-06
39488 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2003-01-04 01:13 | 2003-01-04 07:47 | 2003-03-04 | LOW PRESSURE COOLANT INJECTION DECLARED INOPERABLE "At 0113 hours CST on 1/4/2003, SR 3.5.1.1 [Surveillance Requirement] (monthly fill and vent surveillance) was initiated on U-2 B RHR loop. When the high point vents were opened, no flow was observed within the established venting criteria required by the surveillance. Based on this, neither LPCI [Low Pressure Coolant Injection] subsystem could be ensured filled to the injection valves. Both LPCI subsystems were declared inoperable and TS 3.5.1 [Technical Specification] Condition D [was] entered. At 0204 hours CST, when full flow was observed from the 2B RHR loop, TS 3.5.1 Condition D was exited. At 0210 hours CST, 2A RHR loop was subsequently vented and full flow was observed immediately. "This notification is being made in accordance with 10CFR50.72(b)(3)(v)[(D)]." Licensee has informed the NRC Resident Inspector. *** EVENT RETRACTED ON 3/4/03 1157 EST BY MIKE SWEGLE TO ERIC THOMAS *** "ENS Retraction - Low Pressure Coolant Injection Declared Inoperable "The purpose of this notification is to retract the ENS report made on 1/04/2003 at 0747 EST (Event #39488). The initial report was made when it appeared the established venting criteria for Low Pressure Coolant Injection (LPCI) was not met during the monthly fill and vent surveillance. A subsequent investigation has determined that the LPCI system was properly filled and vented at the time. A review of plant parameters (including alarm data, system piping configuration, and Reactor Building Equipment Drain Tank flow indications) confirmed that the RHR piping was properly filled. "The original event is attributed to difficulty in interpreting the sight glass indications during the venting process. The sight glass indicator used to visually verify that flow is established during the venting surveillance was not properly drained. "For these reasons, Quad Cities Station has determined that the LPCI system was fully operable at the time of the event." The licensee has informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-01-04
39487 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-01-03 11:01 | 2003-01-03 15:14 | 2003-01-03 | AUTOMATIC REACTOR TRIP DUE TO POWER RANGE NEUTRON FLUX - HIGH NEGATIVE RATE TRIP "On January 3, 2003, Wolf Creek Generating Station Unit 1 was operating at 100% reactor power when an automatic reactor trip occurred at 11:01 a.m. CST. Scheduled preventative maintenance had been completed on the control rod drive motor generator set, and the system was being placed back into service when an automatic reactor trip was received due to a Power Range Neutron Flux - High Negative Rate trip on all four power range channels. "An Auxiliary Feedwater Actuation Signal was received and initiated the Auxiliary Feedwater System as expected. Plant equipment performed as expected. "Investigation into the cause of the reactor trip is in progress. The plant is currently in MODE 3, Hot Standby. This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The Licensee has notified the NRC Resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-01-03
39486 | 0 | METAL MANAGEMENT AEROSPACE, INC |  |  |  |  | 2002-12-17 | 2003-01-02 14:59 | 2003-01-02 | LEAKING SOURCES DISCOVERED DURING SEMI-ANNUAL LEAK CHECK The Licensee reported that the semi-annual leak check of two Cd-109 sources indicated removable surface contamination. The two 20 millicurie sources, serial numbers A2-235 and A3-236, indicated .04 microcuries/swipe and .041 microcuries/swipe, respectively. The equipment housing the sources has been removed from service pending decontamination activities by a vendor. The Licensee reported no spread of contamination outside the source housings. The Licensee has contacted NRC Region 1 (Steve Courtemanche). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2003-01-02
39485 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-01-01 06:26 | 2003-01-01 10:09 | 2003-01-01 | REACTOR TRIP AND AUXILIARY FEEDWATER ACTUATION START SIGNALS RECEIVED DURING DRAINING OF THE LOOP # 2 STEAM GENERATOR. "At 0626 EDT on 01/01/03, Sequoyah Unit 2 received reactor trip and Auxiliary Feedwater (AFW) start signals while draining the loop 2 Steam Generator (S/G). The low-low level trip inputs to the RPS (reactor protection system) were blocked in accordance with the procedure. However, the EAM/TTD [environmental adverse monitor/trip time delay] low-low level trip inputs were not blocked prior to commencing the drain down [the procedural step had been N/A'd]. The setpoint for the trip is 15% on 2/3 Level Transmitters with an increasing time delay based on core delta T [with reactor power less than 50%]. "Unit 2 was in Mode 5 [cold shutdown] prior the actuation with all rods inserted. The reactor coolant system was at 115 [degrees] F and 5 psig. The AFW pumps were in pull-to-lock and did not start as a result of the signal. No other equipment started or repositioned as a result of the low-low level signal. "The first out annunciation cleared at 0939 EDT after blocking the EAM/TTD low-low level inputs." The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-01-01
39484 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-01-01 05:57 | 2003-01-01 09:05 | 2003-01-06 | LOSS OF ENS PHONES "At 0557 CST it was discovered that the ENS Phones in both the Control Room and TSC were not functioning. Minimum required backup communications systems were verified operable. Repairs have been initiated." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 1/6/03 BY ARLON COSTA * * * NUREG-1022, Rev. 2, page 77 states that "Loss of either ENS or HPN does not generate an event report." Event 39484 was generated due to an administrative oversight. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-01-01
39483 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2002-12-31 19:30 | 2002-12-31 22:37 | 2002-12-31 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF SIRENS "At 19:30 [CST] on December 31, 2002, ANO Security received an offsite call from the Pope County Emergency Services Office regarding actuation of emergency sirens in the Russellville area. The sirens silenced automatically approximately 3 minutes later after they timed out. Information provided by Pope County Emergency Services indicated the cause of the actuation of the sirens was attributed to a damaged transformer in the vicinity of the siren stations as reported by one caller. At 20:02 Channel 11 News in Little Rock called security inquiring about this event." The Licensee reported that the sirens are currently operable. The NRC Resident Inspector was notified and State Agencies will be notified of this incident. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-31
39482 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-12-31 20:13 | 2002-12-31 21:13 | 2003-01-06 | LOSS OF COMMUNICATION VIA ENS "At 1535 CST [12/31/02] it was discovered that the ENS Phones in both the Control Room and TSC were not functioning. Minimum required backup communication systems were verified operable. Repairs were initiated and the phone systems were restored to an operable status at 2000 CST. The Licensee notified the NRC Resident Inspector. * * * UPDATE ON 1/6/03 BY ARLON COSTA * * * NUREG-1022, Rev. 2, page 77 states that "Loss of either ENS or HPN does not generate an event report." Event 39482 was generated due to an administrative oversight. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-31
39481 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2002-12-26 05:18 | 2002-12-31 11:15 | 2003-01-03 | PALO VERDE 2 OFFSITE NOTIFICATION ON COOLING TOWER WATER SPILL "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On Tuesday, December 31, 2002, the Palo Verde Nuclear Generating Station Unit 2 will provide a voluntary written report to the Arizona Department of Environmental Quality (ADEQ) of an event related to the protection of the environment. Specifically, the report will detail an unintentional release of an estimated 72,000 gallons of cooling tower water to the unlined ditch that carries storm water from the gunite lined storm water collection system to Sedimentation Basin #1. The release began at approximately 05:18 Mountain Standard Time (MST) on December 26, 2002 and was stopped at approximately 05:50 MST on December 28, 2002 following discovery. No news release is anticipated." The NRC Resident Inspector was notified. ***UPDATE 01/03/03 1551 EST DAN MARKS TO JASON FLEMMING*** "It has been brought to Palo Verde's attention that this ENS event report 39481 has been posted on the NRC website with an error. The release stopped at approximately 05:50 MST on December 26, 2002. The webpage incorrectly states December 28, 2002." The NRC resident inspector has been notified. | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-31
39480 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2002-12-30 20:10 | 2002-12-31 01:34 | 2003-01-27 | MONTICELLO INITIATED TS REQUIRED PLANT SHUTDOWN DUE TO INOPERABILITY OF BOTH EDGs "With #12 EDG inoperable due to a maintenance issue [on 12/29/02 at 2330 CST] , it is required to test #11 EDG within 24 hours. Testing causes #11 EDG to be inoperable, therefore both EDGs are inoperable requiring [the initiation of] a plant shutdown per T.S. 3.9.B.3.a.2 and a non-emergency notification per 10 CFR 50.72/8 hour. #11 EDG subequently tested operable and the plant exited T.S. shutdown requirement at 2300 on 12/30/02." The licensee stated that the period of time both EDGs were inoperable was from 2010 to 2300 on 12/30/02. The inoperablity of the #12 EDG was due to an equipment problem with the DC fuel oil pump. After fixing the DC fuel oil pump on the #12 EDG, the EDG was restarted and the "failure-to-start" alarm lit and the "cranking" alarm lit and stayed in for 5 minutes. The licensee is currently evaluating these problems. The #12 EDG remains in a 7 day limiting LCO action statement. The #11 EDG started and tested satisfactorily with no problems. The inoperability of the #11 EDG was due to some of the set up conditions for testing when the EDG is considered to be inoperable per procedure. The NRC Resident Inspector was notified. * * * RETRACTED ON 1/27/03 AT 1714 EST BY DAVID BARNETT TO GERRY WAIG * * * "On 12/29/02 at 2330 CST, the Monticello nuclear power plant notified the NRC operations center of the #12 EDG being declared inoperable when personnel noted an equipment problem during surveillance testing. In addition, the #11 EDG was declared inoperable due to station Technical Specification required surveillance testing to prove operability of the #11 EDG while the #12 EDG was inoperable. The report was made pursuant to 10CFR50.72(b)(3)(v) under Event Notification number 39480. "Upon further review, Monticello is retracting the event reported based on the information in NUREG-1022, Rev. 2, page 56, which states, 'The following types of events or conditions generally are not reportable under these conditions. Sub-item 3 states: removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function).' "The station condition reported in Event Report #39480 was determined not to be reportable based on the following: 1) #11 EDG was inoperable due to the performance of a surveillance test in accordance with the station's Technical Specifications and an approved procedure; and 2) #11 EDG successfully passed the surveillance test to prove operability. Additionally, the required TS LCO action statement requiring plant shutdown was entered. The appropriate procedure was entered. However the station was not required to reduce power or initiate shutdown by inserting negative reactivity and additionally the shutdown was not imminent, since the #11 EDG was confirmed to be operable." The licensee has notified the NRC Resident Inspector, State of Minnesota, and Local Government of this retraction. Notified R3DO (Mark Ring) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | POT UNABLE TO SAFE SD | POT UNCNTRL RAD REL |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(C) |  | 0 | 2002-12-31
39479 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-12-30 10:47 | 2002-12-30 13:47 | 2002-12-30 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Humbolt moisture density gauge , Model # HSI5001P, Serial # 838, was stolen from the back of a truck sometime between 12/28/02 and 12/30/02 in Redlands, CA. The gauge contained 10 millicuries of Cs-137 and 40 millicuries Am-241:Be. On Saturday, December 28, 2002, an employee took the gauge back to his residence after performing a job. The gauge was chained and locked in the back of his truck. On Monday morning at approximately 0645 PST the employee noticed that the gauge, chains and lock were missing from the back of his truck. He reported the theft to the Radiation Safety Officer (RSO). The RSO reported the theft to the State of California. The theft was also reported to the local police and the licensee is posting a notice with a reward in local newspapers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-01-02
39478 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-30 14:15 | 2002-12-30 15:51 | 2002-12-31 | LOSS OF OFFSITE EMERGENCY SIRENS DUE TO LIGHTNING STRIKES All emergency sirens (66 of 66) serving Hood and Somervell Counties, TX are out of service due to lightning strikes on communications repeater equipment. The licensee has notified the Hood and Somervell County Sheriff Departments and will be notifying the NRC resident inspector. Repair crews are responding and expect to make repairs within about 4 hours. ***UPDATE on 12/31/02 at 0113ET by Don Cerny taken by MacKinnon**** All sirens were returned to service December 31, 2002 at midnight. NRC R4DO (Bill Johnson) notified. The NRC Resident Inspector will be contacted by the licensee of this update. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-30
39477 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-12-28 15:20 | 2002-12-29 13:27 | 2002-12-29 | SAFETY EQUIPMENT FAILURE "At 1515 CST, on 12-28-02 the Plant Shift Superintendent (PSS) was notified that the power for C-746Q1 facility was being returned to the normal supply. The C-746Q1 CAAS system power was being supplied via a portable generator to maintain CAAS operability. As part of this evolution, the CAAS system power was to be transferred back to normal as well by repositioning a knife switch and disconnecting the portable generator. When the knife switch was repositioned, C-746Q1 CAAS Cluster AD Trouble alarm was received (expected alarm) but did not immediately clear (unexpected response). When the building was entered, the building area lights were illuminated, the UPS POWER ON light was extinguished and the HORN POWER ON light was illuminated. The CAAS UPS had the Battery Status light flashing and the Load Status light illuminated. At 1520, the UPS ON/Standby switch was manipulated in an attempt to reenergize the UPS since the assumption was that there was power to the UPS. This inappropriate action de-energized the UPS, extinguished the HORN POWER ON light and the CAAS horn power was lost. This caused a loss of CAAS Audibility for C-746Q1 end TSR LCO 2.6.4.1b was immediately entered. There were no fissile material operations in progress and all of the personnel in the affected area had a radio in constant communication with the Central Control Facility satisfying the required actions of TSR 2.6.4.1b. Upon further investigation it was determined that the knife switch had not been fully engaged in the normal power position and no power was available to the UPS as indicated by the extinguished UPS POWER ON light. At 1530 the knife switch was exercised and fully engaged in the normal power position. The UPS POWER ON light illuminated, the UPS was reenergized and CAAS Horn light illuminated reestablishing CAAS audibility and TSR 2.6.4.1b was exited. "The events reportable as a 24 hour event, as required by 10 CFR76.120(c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2002-12-29
39476 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-12-29 00:10 | 2002-12-29 02:56 | 2002-12-29 | MANUAL SCRAM AT FERMI 2 DUE TO INABILITY TO DRIVE CONTROL RODS "The reactor was being shut down from 100% due to a low output voltage condition from Master Power Unit (MPU) 3. Power was lowered using core flow to 75%. The low MPU 3 voltage allowed selection of control rods but would not allow control rods to be inserted. On Sunday, December 29, 2002 at 0010 hours, the reactor [was manually] scrammed from 75% power. "Reactor level is stable in the normal band (197 inches). Reactor Level 3 (173 inches) was reached and level was restored to normal. "No ECCS systems actuated. No safety/relief valves opened. All systems functioned normally. Reactor level is being maintained using feed water through the startup level control valve. Cool down is through the main turbine bypass valves to the main condenser. The following Level 3 isolations occurred as expected: Group 4 - RHR Shutdown Cooling and Head Spray Group 13 - Drywell Sumps Group 15 - Traversing Incore Probe Systems "NRC Senior Resident Inspector has been notified. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Any event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The licensee also indicated that all control rods properly scrammed into the core. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-12-29
39475 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-12-28 12:28 | 2002-12-28 14:38 | 2002-12-28 | LOSS OF COMMUNICATION WITH OFFSITE EMERGENCY RESPONSE FACILITY Lost power to Emergency Operations Facility (EOF) at approximately 1228 CST on 12/28/02. The power outage is likely caused by a car/pole accident at Hwy 42 and Nuclear Rd. Repairs to the pole are expected to be complete by 1500 CST today (12/28/02). The Licensee has phone cell communications capability with the EOF if needed. The NRC Resident Inspector has been notified. *** UPDATE FROM DEAN RAASCH TO ARLON COSTA ON 12/28/02 AT 1649 EST *** "Subsequent to the first notification it was discovered that the ENS phone lines from both the Control Room and TSC were also lost. "Power was restored to the EOF at 1515 CST. ENS phones are also restored at this time." The Licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-28
39474 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-12-26 08:30 | 2002-12-26 11:35 | 2002-12-26 | AGREEMENT STATE NOTIFICATION OF IRRETRIEVABLE WELL-LOGGING SOURCE Timothy Bonzer of the Colorado Radiation Services notified the NRC Operations Center via fax on 12/26/02 at 1135 EST on an incident involving an abandoned well-logging source assembly at a gas well near Rifle, Colorado by Schlumberger Technologies Corp. The sources (Cs and AmBe) were lost at approximately the 8,000 ft level and efforts to retrieve the sources were unsuccessful. They had taken the necessary measures to deflect any future attempt to drill in the same location and will place a stainless steel warning placard at the surface. They intended to abandon the sources and are still planning to use the well for the production of natural gas. The Colorado Emergency Management organization is cognizant of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-12-31
39473 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-26 16:20 | 2002-12-26 17:47 | 2002-12-26 | RPS ACTUATION FOLLOWED BY AUTOMATIC REACTOR TRIP "At 16:20 EST, Unit 2 #3 Reactor Coolant Pump Tripped due to actuation of its 6.9 KV Circuit Breaker's Toroidal Ground Relay (Device 50G). The trip of the RCP resulted in an automatic reactor trip from 100% rated thermal power. "All support equipment operated as designed. No primary or secondary safety valves opened. The Unit is stable. Mode 3 conditions are being maintained." The reactor was shutdown with all control rods fully inserted. The remaining 3 RCPs are in operation and transferring decay heat to the steam generators. The NRC Resident Inspector was notified. * * * UPDATE FROM MITCH TAGGART TO ARLON COSTA ON 12/26/02 AT 21:43 * * * Actuation of RPS System (Reactor Trip) and Auxiliary Feedwater as expected from reactor trip in accordance with 10CFR50.72(b)(3)(iv)(A)(1) RPS and (6) Auxiliary Feedwater. The Licensee will notify the NRC Resident Inspector. The Headquarters Operations Officer notified NRC R2DO (Stephen Cahill) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-12-26
39472 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-12-25 16:03 | 2002-12-25 20:09 | 2002-12-25 | SAFETY PARAMETER DISPLAY SYSTEM OUT OF SERVICE FOR GREATER THAN 1 HOUR "At 1603 hours on 12/25/02, the Safety Parameter Display System (SPDS) portion of the Emergency Response Facility Computer System (ERFCS) was noted to be inoperable, due to all outputs being displayed in magenta color. "Troubleshooting of the ERFCS determined that the Central Emergency Operations Facility (CEOF) input into the ERFCS was causing the system to fail. The CEOF input into the "A" ERFCS was defeated and at 1714 hours on 12/25/02 the ERFCS and SPDS were returned to service, "SPDS was out of service for greater then 1 hour, which is considered a major loss of emergency assessment capability. "This report is being made in accordance with 10CFR50.72(b)(3)(xiii). "The NRC resident inspector was informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-25
39471 | 0 | COLORADO DEPT OF PUBLIC HEALTH |  |  |  |  | 2002-12-12 | 2002-12-24 17:57 | 2002-12-24 | AGREEMENT STATE REPORT - DELIVERY DRIVER CONTAMINATED WHEN HANDLING SHIPMENT PACKAGES On 12/12/02 a Mallinckrodt, Inc. delivery driver was contaminated with Iodine-131 due to handling three packages picked up from University Hospital in Denver, CO. The contamination was discovered upon the driver's return to the Mallinckrodt facility. The driver's hands were successfully decontaminated and subsequent bioassays indicated no readings above action levels. The three contaminated packages and the driver's lab coat were bagged and isolated. No further contamination was found. Upon investigation, it was determined that a nuclear medicine technologist at University Hospital had contaminated her gloves while handling an I-131 capsule and then handled the shipping boxes without changing her gloves. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | HOS | [5 empty] | 0 | 2002-12-24
39470 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2002-10-22 | 2002-12-23 16:04 | 2003-02-12 | NICKEL-63 SOURCES INADVERTENTLY DISPOSED OF AS SCRAP A gas chromatograph, Model HP 5880GLC, with two Ni-63 sources was inadvertently disposed of with other excess property as scrap metal from the Veterans Administration's Puget Sound Health Care System on 10/22/02 without notifying the RSO. The loss was discovered on 11/25/02 during a routine inventory. The two sealed sources were contained in an electron capture detector within the gas chromatograph. The two sources consist of 13.1 millicuries of Ni-63 each (as of 11/25/02). The source serial numbers are 89665 and 89474. The RSO and the Veterans Administration National Health Physics Program are investigating and will file a written report within 30 days. * * * UPDATE ON 2/12/03 @ 1510 BY SIMMONS TO GOULD * * * The licensee reported that the Ni-63 sources were licensed under a general license and should have been reported under 31.5.c.viii. Notified R4 DO (Marschall) and NMSS EO (Holahan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | WA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-12-23
39469 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2002-12-12 | 2002-12-23 15:07 | 2003-06-06 | STOLEN TROXLER DENSITY MOISTURE GAUGE P & M Construction, Inc. notified the state on 12/12/02 that a Troxler model 3411B (serial # 12073) density moisture gauge was stolen from their shop in Ponderosa, New Mexico sometime in September or October of this year. The gauge contained a 9 millicurie Cs-137 source (serial # 409584) and a 50 millicurie Am-241: Be source (serial # 477368). The gauge was locked in its transport container with a locked chain securing the container. This chain was cut and the locked container was removed from the shop. A police report was made. * * * UPDATE ON 6/5/03 FROM BILL FLOYD TO NRC OFFICE OF PUBLIC AFFAIRS * * * A local man found the stolen gauge in the Albuquerque West Mesa area on 5/24/03. He had knowledge of this type of instrument and was able to trace it to the proper owner by the paperwork accompanying the gauge. The gauge is in good condition, but will remain secured and out of service until results of a leak test are received. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2002-12-26
39468 | -1 | PALISADES | 1 |  |  | [1] CE | 2002-12-23 13:00 | 2002-12-23 15:02 | 2003-02-20 | CONTAINMENT HYDROGEN MONITOR CHANNEL OUT OF SERVICE At 1300 on 12/23/02, it was determined that two vent caps were found removed from the supply and return headers on the right channel of the containment hydrogen monitor, EC-162, which constituted a reportable condition under 10 CFR 50.72(b)(3)(v)(C) and (D), 8-hour report. This is based on a release path available such that if the hydrogen monitor was placed in service, post-accident, the site release limits could be exceeded. Also, with the openings in the supply and return lines, a valid hydrogen concentration could not be obtained. As a result, operator action to place the hydrogen recombiner in service could have been missed. There are no indications that these caps were removed maliciously or as an act of sabotage. It should be noted that the other (left channel) hydrogen monitor is the preferred monitor to be placed in service due to input to the Emergency Response Data System. Both the 3/8 inch vent caps were re-installed upon discovery. The licensee stated that no recent maintenance in the area. The last time the vent caps were known to be removed were in May, 2001 for testing. The caps were documented as being re-installed after the test was complete. The licensee notified the NRC resident inspector. * * * UPDATE ON 2/20/03 @ 1041 BY MALONE TO GOULD * * * RETRACTION THE LICENSEE IS RETRACTING THIS EVENT An analysis has since determined that the potential release from the uninstalled pipe caps and the potential delay in placing a hydrogen recombiner in service are bounded by their respective analyses of record, considering reasonable assumptions of recognition of the condition from available indications. Consequently, there was no condition which could have prevented the fulfillment of a safety function needed to control the release of radioactive material or mitigate the consequences of an accident. The NRC Resident Inspector was notified. Region 3 RDO(Madera) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2002-12-23
39467 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-12-23 01:59 | 2002-12-23 02:53 | 2002-12-23 | AUTOMATIC REACTOR TRIP CAUSED BY MAIN GENERATOR TRIP Automatic reactor trip caused by main generator backup relay protection trip. The plant currently is stable in mode 3 with Auxiliary Feedwater in service for decay heat removal. All control rods fully inserted, no primary relief valves lifted and no ECCS actuation occurred. The Licensee reports that the electrical grid is stable and all emergency diesels are available. The Licensee has notified the NRC Resident Inspector. * * * UPDATE 0913 EST 12/23/02 BRUCE PARRISH TO MIKE NORRIS * * * The Licensee reported an automatic initiation of Auxiliary Feedwater due to steam generator Lo Lo level (setpoint 27%) during the trip, which is an 8 hour non-emergency notification of 10 CFR 50.72 (b)(3)(iv)(A), Specified System Actuation. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-12-23
39466 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2002-12-21 20:35 | 2002-12-22 00:18 | 2002-12-22 | AUTOMATIC REACTOR SCRAM AFTER EHC FAILURE At 2035, an EHC failure occurred that caused multiple bypass valves to open. Reactor pressure dropped resulting in a Group 1 isolation (closure of MSIV's) which caused a reactor scram. Lowest pressure was approximately 850#. Level dropped through Lo Level (1"), resulting in Group 2/3 PCIS isolation. Level continued to Lo Lo Level (-48"), resulting in ECCS actuation and injection (HPCI & RCIC). ARI also initiated resulting in trip of both Recirculation pumps. Plant is stabilized and preceding to cold shutdown. The Licensee has notified the NRC Resident Inspector. The plant currently has MSIV's shut due to 3 Bypass valves open and are maintaining pressure control with HPCI & RCIC. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2002-12-22
39465 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-12-20 19:15 | 2002-12-20 20:04 | 2002-12-20 | UNANALYZED CONDITION "Inspection of the Harris Nuclear Plant (HNP) Safe Shutdown Analysis (SSA) in Case of Fire identified that for postulated fires in three fire areas, the design and compensatory actions assumed by the Safe Shutdown Analysis would not ensure a protected train of equipment would remain available. This condition constitutes noncompliance with the HNP FSAR and is reportable as an unanalyzed condition as described in 10CFR50.72. "The inspection identified that postulated fires could cause spurious actuation of components potentially resulting in loss of the Charging/Safety Injection Pump (CSIP) assumed to be protected by the Safe Shutdown Analysis. The fires were postulated to cause spurious closure of valves in the suction and/or discharge flowpaths for the protected CSIP prior to implementation of the preplanned actions designed to preserve these flowpaths. The protected CSIP could be lost if it was in service at the time of the postulated fire. "The plant is instituting several interim compensatory measures to minimize the impact of the postulated fires. These measures include aligning the Charging System and de-energizing certain valves to minimize susceptibility to mal-operation of components, and posting a fire watch in fire areas of concern." The three areas of concern for the postulated fires are in the 261 RAB elevation north-south hallway. The cable spreaders in this area constitute the susceptible equipment. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-12-20
39464 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-12-19 | 2002-12-19 22:09 | 2002-12-19 | 8-HOUR NOTIFICATION FOR UNANALYZED CONDITION "During a review of the Fort Calhoun Station fire protection program, it was discovered that for a potential fire in two fire areas in the plant the protected train of reactor inventory control would not be free of fire damage. During a postulated fire in either one of two fire areas the charging pump credited for maintaining hot shutdown reactor coolant inventory may be affected by a fire in one of the areas. This represents a technical noncompliance with 10CFR50 Appendix R section III.G.2 and does not affect current plant operation. As a compensatory measure, the plant is instituting hourly fire watches in the affected fire areas." The licensee notified the Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-12-19
39463 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-12-19 14:30 | 2002-12-19 17:49 | 2002-12-19 | REACTOR CORE ISOLATION COOLING(RCIC) SYSTEM OPERATION FROM THE REMOTE S/D PANEL MAY NOT BE AVAILABLE FOR SAFE SHUTDOWN OF THE UNIT. On December 19, 2002, during an engineering review of the impact of electrical faults on the ability of systems required to safely shutdown the facility in the event of a fire, it was determined that Reactor Core Isolation Cooling (RCIC) system operation from the remote shutdown panel (RSDP) may not be available for safe shutdown of the unit. A postulated fire that results in an electrical short of the Division 2 125/250 VDC distribution system to ground may cause a voltage control device to fail integral to a RSDP instrument power supply inverter. If the inverter fails as a result of the ground, no power supply would be available for automatic or manual control of the RCIC turbine at the RSDP. In addition, loss of the same inverter would also result in the loss of reactor, drywell and suppression pool monitoring instruments at the remote shutdown panel. The current fire safe shutdown analysis credits only the RCIC system for post-fire inventory control during a worst case main control room fire. This analysis requires RCIC to be operational from the RSDP. With this postulated loss of RCIC RSDP capability during a main control room fire, this event is reportable under 10CFR50.72(b)(3)(ii). There were no actual safety consequences associated with this reportable event since there was no fire in the control room. The design basis fire in the control room assumes an all encompassing fire which is unlikely and would more likely be limited to a single panel. An Alternate Safe Shutdown impairment has been established in accordance with station requirements. Compensatory measures consist of calibrating a spare inverter for installation and expediting installation of a plant modification to remove the postulated failure mechanism. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-12-19
39462 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2002-12-19 12:00 | 2002-12-19 16:20 | 2002-12-19 | AGREEMENT STATE REPORT INVOLVING A LOST EXIT SIGN Lost tritium source (exit sign). Purchased in 1987, 15 Curies at time of purchase. Lost at Holdrege, NE Country Club following a renovation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2002-12-24
39461 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2002-12-17 10:00 | 2002-12-19 10:38 | 2002-12-19 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE At 1038 EST on 12/19/02, Oklahoma Department of Environmental Quality notified us that on 12/17/02 at 1000 CST, an Oklahoma Department of Transportation (ODOT) Troxler Moisture Density gauge was damaged in an accident. The accident occurred when a subcontractor's water tank truck backed over an ODOT pickup truck and the gauge that was resting on the Standard Block. The gauge was damaged, but the sealed sources were contained in shielding and were not ruptured. The gauge, S/N 27829, contains an 8 millicurie Cs-137 source and a 40 millicurie Am-241/Be source. The gauge will be shipped to Troxler for repair or disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | MAT | [5 empty] | 0 | 2002-12-19
39460 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2002-12-19 03:59 | 2002-12-19 05:42 | 2002-12-19 | AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE GENERATOR TRIP "Main Turbine Generator and Reactor trip from 100% power. All control rods inserted. Plant is stable in Mode 3, Hot Standby. No release in progress." The Licensee has notified the NRC Resident Inspector and the State of Arkansas. The Licensee indicated that no ECCS actuation occurred, the electrical grid is stable with all Emergency Diesel Generators available, and that there is no primary to secondary Steam Generator leakage. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-12-19
39459 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2002-12-18 14:30 | 2002-12-18 15:22 | 2003-10-14 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY An unauthorized entry into the protected area occurred by a contract employee. Immediate compensatory measures were taken upon discovery. The licensee has notified the NRC Resident Inspector. Contact the HOO for additional details. * * * UPDATE ON 10/14/03 @ 1650 BY REIMERS TO GOULD * * * After further review of this event the Licensee has concluded that this event is not reportable and therefore it should be retracted. The NRC Resident Inspector will be informed. Notified Reg 2 RDO(Ogle) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-14
39458 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-12-18 07:28 | 2002-12-18 08:19 | 2002-12-23 | UNAUTHORIZED ACCESS TO VITAL AREA Nuclear Facilities Group personnel tailgated into a vital area. Immediate compensatory measures taken upon discovery. Licensee notified NRC Resident Inspector and will be notifying Pennsylvania Emergency Management Agency. Refer to HOO Log for details. * * * * UPDATE TAKEN FROM DON ROLAND BY MIKE RIPLEY AT 1544 EST ON 12/23/02 * * * * Further review of this event by the licensee has determined that the entry into the vital area is not reportable per the guidance in NUREG-1304 item 2.4.11.a and Generic Letter 91-03 enclosure 1. Entry into the vital area was not made with malevolent intent and the individual had a level of security screening that would have qualified him for access to the area. The licensee notified the NRC Resident Inspector. Notified R1 DO (B. McDermott). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  |  | 50.72(b)(2)(xi) |  |  | 0 | 2002-12-18
39457 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-12-15 | 2002-12-17 18:00 | 2002-12-17 | PACKAGE AT DALLAS FORT WORTH (DFW) AIRPORT EXCEEDS RADIATION LIMITS BASED ON LABELING "The package exceeded the package limits based on the labeling and the container. Radiation readings were about 17 mR/hr. at one meter. The limit was 10 mR/hr. at one meter. A yellow Ill and Yellow II label provided inconsistent radiation information. The package was held at a cargo bay by US Customs. The TDH/BRC responded to a call for assistance to survey the package and help determine its contents. The inspector responded on site performed a survey and notified the Licensee's RSO. The Licensee planned to send a representative to repackage and relabel the package prior to the package being released for shipment to Houston, TX. The information provided is preliminary and based on telephone conversations with involved parties." The package was air cargo on an international flight being shipped from Schumberger in Singapore to Schlumberger in Houston, TX. The Texas Department of Health, Bureau of Radiation Control has notified NRC R4, US Customs, DFW, and the licensee. The Texas Department of Health, Bureau of Radiation Control incident number is I-7962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-12-20
39456 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-12-17 12:40 | 2002-12-17 15:12 | 2002-12-17 | OFFSITE NOTIFICATION TO STATE OF PLANT OUTAGE EXCEEDING 3 DAYS At 1240, 12/17/02, Callaway Plant notified the Missouri Public Service Commission (MPSC) of a forced outage lasting longer than three days. This notification was performed in accordance with 4CSR240-20.080(3)(B) and included the following information: On Saturday, December 14, 2002, at 0420 the Callaway Plant shutdown while preparing to secure a condensate pump located in the non-radioactive secondary system. While shutdown, problems were discovered with a steam driven auxiliary feedwater pump and these problems had to be corrected prior to returning the plant to service. Repairs to the steam driven auxiliary feedwater pump have been completed and it is anticipated that the Callaway Plant will return to service on December 17, 2002. This ENS notification is being made in accordance with I0CFR50.72(b)(2)(xi) for notification to another government agency. The licensee has notified the NRC Resident Inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-17
39455 | 0 | STEEL OF WEST VIRGINIA |  |  |  |  | 2002-12-16 13:00 | 2002-12-17 13:45 | 2002-12-17 | DAMAGED SOURCE HOLDER ON STEEL LEVEL GAUGE At 1345 EST on 12/17/02, the licensee reported that at approximately 1300 EST on 12/16/02, a radioactive source holder on a molten steel level gauge was damaged from molten metal at the Steel of West Virginia facility in Huntington, WV. The gauge is a Kay-Ray, Model # 7060SD, Serial # S93K0407. The gauge contains 500 millicuries of cesium-137. The molten metal penetrated the outer casing on the holder and melted the lead shielding. The holder was placed in a shielded container and moved to a secure location. The licensee is making arrangements for disposal. A radiation survey of the area was conducted and no contamination or abnormal readings were detected. The licensee notified NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-12-17
39454 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-10-29 09:17 | 2002-12-17 12:24 | 2002-12-17 | 60 - DAY OPTIONAL 10 CFR 50.73 REPORT - INVALID ACTUATION OF THE AFW SYSTEM "60 DAY REPORT - INVALID ACTUATION OF SPECIFIED SYSTEM - This 60-day optional report as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73 (a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Auxiliary Feedwater (AFW) system. On October 29, 2002, at 0917, with Unit 1 in MODE 1 at 100% power, an invalid signal was generated on Train A of the AFW system during auxiliary safeguards testing. During the performance of resistance checks, technicians reported hearing relay chattering inside the # 1 AFW pump turbine control panel. Following the autostart of the 1A motor driven AFW pump, increased AFW flow was noted for steam generators 1A and 1B. This was indicative that valves in Train A of the AFW system had automatically repositioned, in addition to the 1A motor driven pump automatically starting. The pump was subsequently secured and the AFW system was returned to standby readiness. This was considered a partial system/train actuation. During this event, the AFW system performed as expected. This event was entered into the site specific corrective action program for resolution." The NRC Resident Inspector will be notified of the event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-12-17
39453 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-12-17 06:55 | 2002-12-17 10:59 | 2002-12-17 | SEABROOK EMERGENCY OFF-SITE SIRENS INOPERABLE "There was a simultaneous inoperability of Mass. Emerg. Mgt. Agency Framingham and Tewksbury Region 1 siren activation equipment for [greater than] 1 hour. This is reportable per 10 CFR 50.72 (b)(3)xiii. This condition has been corrected (~0900 today). Both systems relied on a single uninterruptable power supply which had failed. This single failure vulnerability was previously identified and is scheduled to be modified in Jan. 2003." The licensee notified the NRC Resident Inspector of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-17
39452 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-12-17 | 2002-12-17 10:52 | 2002-12-18 | AGREEMENT STATE REPORT DUE TO LOST TROXLER DENSITY GAUGE "At about 4:45 PM [CST] our time last evening (12/16/02) we received a call from PSI Corporate in Illinois. Their Colorado license number is 928-02 for the Wheat Ridge Office. They reported a lost moisture-density gauge which apparently fell out of the back of a truck on a highway construction project located on Hwy 85, between Hwy 7 & 136th earlier in the day. According to the RSO [Radiation Safety Officer], the technician admitted that the device was not secured in the back of the truck during movement. It is not clear yet whether the tailgate was down or not. PSI reported the gauge loss to CSP [Colorado State Police] and Adam's County [Sheriff's Office]. They have also issued a reward for the return of the device. Visual Inspection of the shoulder and median failed to find the device, which was reported to be in the case. RSO claims that the case is clearly marked with PSI's phone number and address, and is properly labeled according to regulatory requirements. "It is a Troxler 3411-B, SN 12179." * * * UPDATE FROM PHIL EGIDI TO HOWIE CROUCH ON 12/18/02 AT 1136 EST * * * The Troxler Density Gauge has been found intact with the gauge still locked in the storage case. External swipes showed no contamination. Unit is being taken to Troxler repair center in Dallas for complete inspection. Headquarters Operations Officer notified NMSS (Fred Brown) and R4DO (Linda Howell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | MAT | [5 empty] | 0 | 2002-12-17
39451 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2002-12-17 06:50 | 2002-12-17 09:57 | 2002-12-17 | OFFSITE NOTIFICATION DUE TO DUCK HUNTERS NEAR PLANT SITE Notified by the licensee that they made offsite notifications to the FBI, Maine Game Warden, and the Lincoln County, Maine Sheriff's Office due to duck hunters shooting in the direction of the plant from an island 50-100 feet away from plant property. There were no injuries to plant personnel and no damage to plant property. The hunters were approached by plant security personnel and subsequently found another place to hunt. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-17
39450 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-12-16 15:47 | 2002-12-16 18:17 | 2002-12-16 | NINE MILE POINT UNIT 2 REACTOR SCRAM ON HIGH REACTOR PRESSURE "Failure of main generator stator water cooling temperature control valve resulted in loss of generator stator water cooling and main generator runback signal. Reactor power reduction was initiated with reactor recirculation flow and continued with insertion of control rods. Turbine bypass valves opened as result of main generator runback signal. Reactor protection system auto actuated on high reactor pressure [1052 psig] at 1547 [EST], 12/16/02. [The maximum reactor pressure observed during the transient was 1055 psig.] All control rods fully inserted . No safety relief valves opened. No ECCS systems actuated. Reactor water level being controlled by reactor core isolation cooling and condensate/ feedwater. Reactor pressure [is] being controlled by turbine bypass valves." The licensee has notified the NRC Resident Inspector of this event. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-12-16
39449 | 0 | GEORGIA DEPT. OF NATURAL RESOURCES |  |  |  |  | 2002-12-16 | 2002-12-16 11:03 | 2002-12-16 | AGREEMENT STATE REPORT INVOLVING STOLEN GAUGE Georgia Department of Natural Resources reported to the NRC Operations Center via fax on 12/16/02 at 10:37 a.m. that a Niton XL-309 gauge was stolen on 12/9/02 during overnight hours from the trunk of an automobile while in a hotel parking lot. The gauge contained seven millicuries of Cd-109. The Licensee was instructed to notify the FBI and was given the telephone number for the Miami Beach FBI Office. The Georgia Department of Natural Resources also notified the Florida Radiation Control Program and NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | GA | MAT | [5 empty] | 0 | 2002-12-16
39448 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-15 18:08 | 2002-12-15 21:18 | 2002-12-15 | MANUAL REACTOR TRIP DUE TO HIGH MAIN TURBINE VIBRATIONS "At 18:08 on 12/15/02, the reactor was manually tripped due to high vibrations on the Main Turbine. Investigation into the cause of the Main Turbine high vibrations is in progress. "This is being reported under 10CFR50.72(b)(2)(iv)(b). "During the reactor trip, all control rods fully inserted. Auxiliary Feedwater System automatically actuated as expected on low-low steam generator water level, Main Condenser Vacuum was secured to reduce Main Turbine speed quicker, Main Steam isolation was manually actuated, and the Steam Generator Power Operated Relief Valves automatically opened to maintain primary system temperature. "Primary System temperature and pressure is being maintained at 573 degrees/2235 psig. "Technical Specification 3.7.1.3 was entered at 18:11 due to Auxiliary Feedwater Storage Tank level less than the minimum required level of 485,000 gallons. This requires the level to be restored to above required limit within 4 hours or be in Hot Standby within the next 6 hours. Currently makeup to the storage tank is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-12-15
39447 | 0 | SYNCOR INTERNATIONAL CORP. |  |  |  |  | 2002-12-15 05:00 | 2002-12-15 08:40 | 2002-12-16 | Tc-99m CANISTERS UNDAMAGED DURING TRANSPORTATION ACCIDENT The NRC Operations Center was notified by the Connecticut Department of Environmental Protection (CT DEP) that an vehicle accident involving a Syncor delivery to local hospitals and pharmacies had occurred. A follow-up discussion with the Radiation Safety Officer (RSO) for Syncor International Corporation located at 628 Hebron Avenue, Bldg.4, Glastonbury, CT 06033, provided detailed information related to the incident. The company vehicle (pickup truck) accidentally rolled over after encountering a patch of black ice. Eight canisters (ammo box style) were ejected from the vehicle bed during the accident at Route 6 and State Road 384 in Coventry, Connecticut. The company driver was in the process of picking up and delivering the canisters which house Tc-99m syringes (unit dose) that are enclosed in lead pigs. Both the local police and fire departments and the CT DEP responded to the accident which happened at approximately 0500 EST on 12/15/02. The driver was taken to a local hospital for routine x-rays and treatment. The initial assessment of the incident was that the canisters were not breached. No contamination was detected by the first responders. Syncor will follow up with measurements of the swipes using Multi-Channel Analyzer methodology. * * * UPDATE AT 10:18 ON 12/15/02 FROM MATT SVEJK TO ARLON COSTA * * * The test results of the wiped canisters using a Multi-Channel Analyzer did not indicate any counts above background. The total Tc-99m activity of the five active canisters (the other three were return canisters) was approximately 1,137 millicuries (assay estimate as of 0500 EST on 12/15/02). Notified R1DO(Lew) and NMSS(Essig). UPDATE AT 1433 EST ON 12/16/02 FROM KORY KODIMER TO GERRY WAIG Mr. Kodimer, Health Physics Program Manager, Syncor International Corp., Woodland Hills, CA, called to report that NRC Region 1 and 4 have been contacted by the Syncor corporate office. Additionally, Mr. Kodimer reported that all 8 canisters have been returned to the licensee's (Syncor International Corp.) Glastonbury, CT facility. Notified R4DO (Tom Andrews) and NMSS (Charles Cox) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | TRA | [5 empty] | 0 | 2002-12-15
39446 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2002-12-15 02:30 | 2002-12-15 06:28 | 2002-12-15 | FITNESS FOR DUTY - LICENSED OPERATOR UNFIT FOR SCHEDULED WORK Licensed employee was determined to be under the influence of alcohol during a 'for cause' test, did not assume any shift duties and his plant access has been terminated. Contact HOO for additional details. Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 26.73 |  |  |  | 0 | 2002-12-15
39445 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-12-14 04:20 | 2002-12-14 09:11 | 2002-12-14 | AUTOMATIC REACTOR TRIP ON OTDT DURING DOWNPOWER "At 0420 on 12/14/02, a valid actuation signal was generated that caused an Overtemperature Delta T (OTDT) Reactor Trip. The cause of the OTDT trip was a downpower at 1% per minute due to an oil leak on the 'C' Condensate Pump. A valid actuation signal was generated for the Auxiliary Feedwater Actuation System (AFAS), the Feedwater Isolation System (FWIS) and the Steam Generator Blowdown System Isolation System (SGBSIS) due to Steam Generator Low Levels. After the Turbine Driven Auxiliary Feedwater Actuation Signal (AFAS) was reset, a second AFAS was received and the Turbine Driven Auxiliary Pump failed to start. All other systems functioned as expected. "An Event Review Team (ERT) has been assembled to determine the cause of the event. Additional corrective action to be taken will be based upon recommendations provided by the ERT. "The Senior NRC Resident Inspector has been notified of the event." Both motor driven Auxiliary Feedwater Pumps are in service currently maintaining SG levels. The Main Condenser is available for removal of decay heat via the Main Steam Dump Bypass. All rods fully inserted. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-12-14
39444 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-12-13 14:50 | 2002-12-13 17:04 | 2002-12-13 | OFFSITE NOTIFICATION DUE TO DIESEL FUEL SPILL "At 1450 EST on 12/13/2002, Susquehanna LLC Main Control Room received a request for additional information from the Pennsylvania Emergency Management Agency (PEMA). PEMA received rumors that a HAZMAT team had been dispatched to Susquehanna in response to a spill associated with a potential sabotage event. "At 1158 EST a delivery truck at the owner controlled entrance gate was identified to have a saddle tank leak which resulted in a spill of approximately 10 gallons. The diesel fuel was contained by site personnel, and is in the process of being cleaned by site personnel. None of the oil reached a waterway, and therefore does not meet the requirements for a reportable spill. The delivery company contacted their contracted spill response team, and they responded to the site. They were subsequently released without performing any of the cleanup activities. The minor spill was not due to sabotage. This information has been provided to PEMA. "This report is being issued due to the involvement of other government agencies, and reportable under 10CFR50.72(b)(2)(xi)." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-13
39443 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-12-13 08:30 | 2002-12-13 10:25 | 2002-12-13 | LOSS OF MORE THAN 25% OF THE STATIONS ALERT SIRENS "Loss of more than 25% of the stations total alert sirens have been disabled for more than one hour (0830-0930) due to a loss of power. This was due to severe weather." The loss of alert sirens affects offsite response/notification. Efforts to restore power to the sirens are in progress at this time. The licensee has notified the NRC Resident Inspector of this event. **** UPDATE on December 13, 2002 at 1500 Hours by Louis Nowell taken by MacKinnon **** Less than 25% of the stations total alert sirens are disabled due to a power loss. NRC R2DO (Mike Ernstes) notified. The NRC Resident Inspector has been notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-13
39442 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2002-12-03 | 2002-12-12 15:57 | 2002-12-12 | AGREEMENT STATE REPORT INVOLVING MEDICAL MISADMINISTRATION "The licensee reported a medical misadministration involving a High Dose Rate Afterloader. The patient treatment plan required 20 steps in a treatment with the stepping distance of 0.5 centimeters. The licensee reported that the stepping distance was actually 1.0 centimeter. (The cause of the deviation has not yet been determined.) The deviation resulted in an unplanned dose to an unintended site. The exposure was to 10 centimeters outside the planned treatment area. The dose has not yet been determined." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2002-12-17
39441 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2002-10-20 10:54 | 2002-12-12 15:57 | 2002-12-12 | "INVALID AFW SYSTEM ACTUATION "EVENT DESCRIPTION "This report is being made in accordance with [10 CFR] 50.73(a)(1), which states, in part, 'In the case of an invalid actuation reported under [10 CFR] 50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' This invalid actuation is being reported under [10 CFR] 50.73(a)(2)(iv)(A). "NUREG-1022, Rev. 2, 'Event Reporting Guidelines 10CFR50.72 and 50.73 provides guidance for determining if an actuation is invalid. The NUREG states, in part, that invalid actuations include actuations that are not the result of valid signals and are not intentional manual actuations. Valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. This report documents an actuation that was not the result of a valid signal and was not an intentional manual actuation. For these reasons, this event constitutes an invalid actuation. "NUREG-1022, Rev. 2, states that the report should provide the following information: - the specific train(s) and system(s) that were actuated, - whether each train actuation was complete or partial, and - whether or not the system started and functioned successfully. "On October 20, 2002 at 1054 CDST, the Turbine Driven Auxiliary Feedwater (TDAFW) pump auto-started as a result of an invalid signal. Investigation into the event has shown that the steam supply valve to the TDAFW pump (MS-102) opened inadvertently, starting the TDAFW Pump. Control room annunciators and computer points alarmed. Steam generator blowdown valves closed, per design, as a result of the TDAFW pump start. The TDAFW pump was placed to pullout after verifying that there were no valid automatic start signals." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-12-12
39440 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2002-12-12 08:20 | 2002-12-12 11:32 | 2002-12-12 | INADVERTENT ACTUATION OF OFFSITE EMERGENCY NOTIFICATION SIRENS "TMI is making a 4 hour report in accordance with 10 CFR 50.72 (b)(2)(xi) of an event that occurred at approximately 8:20 AM on Thursday, December 12, 2002 when the offsite emergency sirens for TMI- 1 located in Dauphin County were activated. The siren activation was not related to any condition or event at TMI- 1. The sirens sounded for only a few minutes (less than 10 minutes). TMI- I has notified Dauphin County, the other risk counties and the Pennsylvania Emergency Management Agency of the inadvertent siren activation. The site NRC resident inspectors office has been informed of the inadvertent activation and that a 4 hour notification is being made. "The cause of the inadvertent activation is not known at this time. This activation of the sirens has been entered into the site corrective action program to determine the cause and the actions necessary to prevent recurrence. "It is our understanding that Dauphin County has issued a press release regarding the activation of the sirens. "There was no impact on TMI-l due to the activation of the offsite sirens located in Dauphin County, Pennsylvania. The TMI- I alert and notification system remained operable for the duration of the event." *** UPDATE ON 12/12/02 AT 1549 BY JOHN SCHORK TO ERIC THOMAS *** "On Thursday, December 12, 2002 at 11:32 am, TMI made a 4 hour report in accordance with 10 CFR 50.72 (b)(2)(xi) of an event that occurred at approximately 8:20 am on Thursday, December 12, 2002 when the offsite emergency sirens for TMI-1 located in Dauphin County were inadvertently activated. This is an update to that notification. "The TMI-1 sirens located in Dauphin County were inadvertently activated at 8:20 am on Thursday, 12/12/2002. The siren activation was not related to any condition or event at TMI-1. The sirens sounded for only a few minutes (less than 10 minutes). TMI-1 notified Dauphin County, the other risk counties and the Pennsylvania Emergency Management Agency of the inadvertent siren activation. The site NRC resident inspector's office was informed of the inadvertent activation and that a 4 hour notification was made. "During the afternoon of December 12, 2002, troubleshooting of the cause of inadvertent actuation that occurred at 8:20 am resulted in a second, momentary re-activation of the Dauphin County sirens at 1:43 pm. The troubleshooting was successful and the cause of the inadvertent actuation, a software error in the access program for activation of the sirens, was identified. The risk counties and the Pennsylvania Emergency Management Agency have been notified of the second activation. In addition the site NRC senior resident inspector has been notified of the second activation and our intent to submit a revised 4 hour report. "The inadvertent activation of the sirens has been entered into the site corrective action program to determine the cause and the actions necessary to prevent recurrence. "Dauphin County has issued a press release regarding the initial activation of the sirens. "There was no impact on TMI-1 due to the initial activation of the offsite sirens at 8:20 am located in Dauphin County, Pennsylvania nor was there any impact on TMI-1 due to the second activation. The TMI-1 alert and notification system remained operable for the duration of both activations." Notified R1DO David Lew. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-12
39439 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2002-12-11 18:13 | 2002-12-12 00:20 | 2003-01-30 | RHR B MINIMUM CONTROL FLOW VALVE INOPERABLE "Scheduled maintenance activities were being performed on RHR B minimum flow valve 1E12-F064B which is a containment isolation valve. When the E12-F064 B power supply was energized the Control Room indication for the valve indicated intermediate. Local indication for the valve indicated the valve was closed. When the valve control switch was taken to closed the valve was observed to move 1/16 of an inch and the control room indication changed to full close. The valve was closed and verified down powered on 12/09/02 to comply with Tech Spec 3.6.1.3 Primary Containment Isolation Valves. Maintenance test equipment was installed however no maintenance had been performed." Licensee informed NRC resident inspector. *** RETRACTION ON 01/30/03 AT 1016 ET BY MR. RUSSELL TAKEN BY MACKINNON *** "Subsequently, an engineering evaluation that utilized the valve as-found test data concluded that the valve stem loading was reduced. This resulted in the intermediate valve position when the valve breaker was re-energized. It was also determined that although the valve stem load was reduced, the valve disc remained tightly seated in the closed position. "The valve provides isolation for a containment penetration that interfaces with a closed system outside containment. Since the valve was determined to have remained closed, and the closed system outside containment had not been breached, there was no loss of the containment accident mitigation function and no loss in the control of radiation release function. Since neither of these two functions was lost, there was no reportable condition, and this Event Notification (EN# 39439) is retracted." R3DO (Mark Ring) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2002-12-12
39438 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-12-11 11:20 | 2002-12-11 11:20 | 2002-12-23 | UNAUTHORIZED ENTRY INTO A VITAL PLANT AREA BY CONTRACT PERSONNEL An unauthorized entry into a vital area occurred by a contract employee. Immediate compensatory measures were taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the HOO for additional details. * * * * UPDATE TAKEN FROM DON ROLAND BY MIKE RIPLEY AT 1544 EST ON 12/23/02 * * * * Further review of this event by the licensee has determined that the entry into the vital area is not reportable per the guidance in NUREG-1304 item 2.4.11.a and Generic Letter 91-03 enclosure 1. Entry into the vital area was not made with malevolent intent and the individual had a level of security screening that would have qualified him for access to the area. The licensee notified the NRC Resident Inspector. Notified R1 DO (B. McDermott). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 0 | 2002-12-11
39437 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-12-11 02:30 | 2002-12-11 02:41 | 2002-12-11 | OFFSITE NOTIFICATION TO FAA Licensee made an offsite notification to FAA due to loss of power to plant stack lighting. FAA assigned notification number MIV-212/061-RG. FAA was again notified at 0230 EST that the stack lights were returned to service, Licensee notified NRC resident. RETRACTION BY FRANK CIGANIK TO ERIC THOMAS ON 12/11/02 AT 1736 "Reason for retraction: As per written guidance in NUREG-1022 (Event Reporting Guidelines) Section 3.2.12, the NRC doesn't need to be informed of problems with plant stack or water tower lighting" Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-11
39436 | 0 | R. M. WESTER ASSOCIATES CONSULTING |  |  |  |  | 2002-12-10 14:30 | 2002-12-10 18:18 | 2002-12-10 | HUMBOLT MOISTURE DENSITY GAUGE DAMAGED At a construction site in Downtown St. Louis, a moisture density gauge was run over by a high lift. The gauge was in the uncovered position, and is currently buried in the soil. Local fire department was notified, and came to the site to measure radiation levels. Levels were 112 mr/hr at a distance of 3 feet. The area has been secured, awaiting arrival of a hazardous material removal team from R.M. Wester Associates (license #24-20091-01). The hazmat team will remove the gauge and any contaminated soil that they find. Humbolt is also dispatching an environmental response team to the site. The moisture density gauge contains 10 mCi of Cs-137 and 40 mCi of Am-241. The R3 PAO was notified. The R3DO (P. Hiland) contacted the state of Missouri. **** UPDATE AT 2030 EST FROM R3DO AND DARREL WIEDEMAN TO MIKE RIPLEY **** Gauge has been recovered. Actual readings were 1.25 mr/hr at 3 feet. Gauge was slightly damaged, but the source was intact. No contamination was found in the area. Humbolt representative was on the scene. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2002-12-10
39435 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2002-12-10 | 2002-12-10 14:41 | 2002-12-10 | POWERPLEX INCORE MONITORING SYSTEM Location of fuel assemblies in BWR/6 reactors with the POWERPLEX incore monitoring system may affect their orifice pressure loss coefficients by as much as 40%. The GE core monitoring system uses average orifice loss coefficient values for all assemblies in the core, and a recent evaluation by GE for current fuel designs indicates that the assumption may be non-conservative by up to .01 in predicted MCPR. Analyses have been performed at Grand Gulf and River Bend, the two BWR/6 reactors in the U.S. which use the POWERPLEX incore monitoring system, to assess the impact of using position dependent orifice loss coefficients. The analyses indicate that for Grand Gulf, MCPR is non-conservatively over predicted by not more that 2%, and that LHGR and MAPLHGR are non-conservatively under predicted by not more than 2%. For River Bend, the analyses indicate that MCPR is non-conservatively over predicted by up to 1.2%, LHGR is non-conservatively under predicted by up to 0.7%, and MAPLHGR is non-conservatively under predicted by up to 0.6%. The affected plants, Grand Gulf and River Bend, have been notified by Framatome. Compensatory measures were recommended to apply an administrative penalty on the allowed values of MCPR, LHGR, and MAPLHGR. The POWERPLEX incore monitoring input decks have been modified to include the correct orifice loss coefficients. The plants are currently operating with correct orifice loss coefficients in the POWERPLEX incore monitoring system. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | FUE |  | 21.21 |  |  |  | 0 | 2002-12-10
39434 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-10 11:20 | 2002-12-10 12:20 | 2002-12-10 | OFFSITE NOTIFICATION DUE TO SUSPICIOUS INDIVIDUAL The licensee is issuing the following press release: "BRACEVILLE, IL - About 11:30 p.m. Monday, a man driving a compact vehicle failed to stop at the Braidwood Nuclear Station's initial security checkpoint in violation of station security policies. The unidentified male, who was in the plant's parking lot briefly, refused to obey the security officers' instructions, drove through the station parking lot and left the site. He did not threaten the safety of the plant. At no time was the health and safety of the public threatened. The man left the site after a few minutes and was detained in a short period of time by officers from the Wilmington Police Department, who had been notified by the Braidwood Police Department. "After the man entered the station property, Braidwood security officers used a direct communications link to immediately contact local authorities, who subsequently notified the FBI. Exelon is working with the FBI's Chicago office and local authorities and has notified the Nuclear Regulatory Commission. "Plant security forces acted promptly and effectively in handling the incident and received outstanding support from local law enforcement. The FBI is handling the investigation." The Licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-12-10
39433 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2002-12-10 08:25 | 2002-12-10 10:39 | 2002-12-10 | MANUAL TRIP FROM 100% POWER DUE TO STEAM GENERATOR LEVELS APPROACHING LOW LEVEL TRIP POINT The unit was manually tripped from 100% power due to steam generator levels approaching the low level trip setpoint. The motor driven auxiliary feedwater pumps auto started as a result of a trip of both main feedwater pumps and the turbine driven auxiliary feedwater pump autostarted due to low steam generator levels. The main feed pumps trip was a result of loss of power to the control systems. An unintentional impact to the power supply for the control systems by plant facilities personnel resulted in the loss of power. All rods fully inserted, no ECCS actuation occurred and no relief valves lifted. The unit is currently in mode 3 and all plant systems responded as designed. The NRC Resident inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-12-10
39432 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-11-26 | 2002-12-10 10:13 | 2002-12-10 | AGREEMENT STATE REPORT ON AN I-131 SPILL AT A TEXAS HOSPITAL "Patient was administered an I-131 capsule for ablation therapy on November 26, 2002. A fragment was dropped on the floor. The fragment was measured to contain 13 millicuries of I-131. A contamination survey of the room determined that an area by the sink and an area by the imaging table revealed contamination. The room was sealed off, contamination by the sink was determined to have contamination in the amount of 2 millirem/hour near the sink and 1.6 millirem /hour near the imaging table. After decontamination the room was re-surveyed with the result of 1.6 millirem/hour near the sink and 0.8 millirem/hour. Wipe tests were sent to the nuclear pharmacy for analysis. Results of the analysis indicated 87,313 dpm near the sink and 1,229 dpm near the imaging table. With readings still above the action limits for contamination the facility closed the room for four (4) weeks. At that time additional wipe tests will be conducted and submitted to the nuclear pharmacy for analysis. Bioassay of personnel performing decontamination were conducted 24-hours after the clean-up with no action required for the clean-up crew. The fragment of the capsule was packaged in a lead container and returned to the nuclear pharmacy for disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | HOS | [5 empty] | 0 | 2002-12-10
39431 | 0 | THRASHER ENGINEERING |  |  |  |  | 2002-12-09 21:00 | 2002-12-09 23:14 | 2002-12-09 | MOISTURE DENSITY GAUGE STOLEN FROM VEHICLE On 12/09/02, between 2100 EST and 2200 EST, a Troxler moisture density gauge, Model # 3430, serial # 23602, belonging to Thrasher Engineering, was stolen from the back of the company's pick-up truck while parked at the Middlebrook Mall in Bridgeport, WV. The chain securing the gauge was cut and the gauge was taken. The gauge contained 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be. The Licensee reported the stolen Troxler gauge to the Bridgeport, WV City Police (Case No. 0267811). Notified R2DO (B. Bonser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-12-09
39430 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-09 10:20 | 2002-12-09 12:42 | 2002-12-10 | LOSS OF ENS AND COMMERCIAL TELEPHONE LINES At 10:20 CST on 12/9/2002, experienced a major loss of offsite communications ability on the ENS, NARS, and commercial telephone systems. Repair personnel have been dispatched to the site by Ameritech. The licensee is continually manning a cell phone until the lines are restored. Internal communications on site are still available, as well as microwave communications to the EOF. A trouble ticket was generated for the FTS lines, ticket number 3612. The licensee notified the State and stated that the NRC Resident Inspector will be notified. * * * * UPDATE FROM ZION TO MIKE RIPLEY AT 2325 EST 12/9/02 * * * Repair crews have pinpointed the telephone line problem and anticipate completing repairs by mid-day Tuesday, 12/10/02. The licensee continues to man a cell phone until the lines are restored. Notified the R3 DO (P. Hiland) ***UPDATE FROM ZION TO HOWIE CROUCH AT 0509 EST ON 12/10/02 *** Licensee reported that all commercial and ENS lines have been repaired and returned to service. Notified the R3 DO (P. Hiland) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-09
39429 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-12-07 06:35 | 2002-12-07 08:51 | 2002-12-07 | PLANT ENTERED TS 3.4.4 DUE TO PCS BOUNDARY LEAKAGE OF APPROXIMATELY 1.5 GPM During a drywell entry to identify the source of increased drywell leakage, they discovered a primary coolant system (PCS) leak on the "3A" reactor recirculation pump discharge loop flow instrument line. This condition required entry into TS 3.4.4 which requires that there is no pressure boundary leakage. Entering this condition requires that the unit be in mode 3 in 12 hours and mode 4 in 36 hours, which is a TS required shutdown. The leakage is estimated to be approximately 1.5 gpm. They will commence repairs when they reach mode 4 (may go to mode 5). The NRC Resident inspector was notified. | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2002-12-07
39428 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2002-12-05 15:45 | 2002-12-06 16:38 | 2002-12-06 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL SPILL IN X-RAY ROOM Tennessee Event Report ID No.: TN-02-170 "[State of Tennessee] DRH [Division of Radiological Health] was notified on 12/6/02 by the Radiation Safety Officer at Vanderbilt University Medical Center of a spill of Yttrium-90 microspheres. The material was being used in an x-ray room for treatment of hepatic tumors. Approximately 4% of the 64 millicurie dose was spilled onto the floor of the room. The room was isolated and is being decontaminated. The Radiology Department was closed after the spill to survey for any possible spread of contamination and was reopened this morning. The room where the spill occurred is still restricted. The State will investigate and will inform the NRC of the results of the investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | HOS | [5 empty] | 0 | 2002-12-06
39427 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2002-12-06 06:32 | 2002-12-06 15:35 | 2002-12-06 | FITNESS FOR DUTY A licensed operator tested positive for alcohol during a random test. The employee's access to the protected area has been terminated pending confirmatory testing. The NRC Resident Inspector has been notified. Contact the HOO for additional details. | 0 | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2002-12-06
39426 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-12-05 | 2002-12-06 13:13 | 2002-12-06 | AGREEMENT STATE REPORT - MEDICAL EVENT, DOSE GREATER THAN 20% LARGER THAN PRESCRIBED "On December 5, 2002, the RSO at Northwest Community Hospital, Arlington Heights IL, notified the department of a 'reportable' (misadministration) event that occurred involving Intravascular Brachytherapy. The treatment was for a 52 mm lesion using 85 mCi [millicuries] of P-32 (GDT source) in a Guidant Corporation Galileo device. The prescribed dose was 20 gray. Using a three step automated system, as the 1st step was completed, the authorized user intervened and repositioned the markers for the system to intentionally deliver an additional dose to this area of the lesion. After completing the treatment. The calculated dose to the lesion was determined to be 24.6 gray. This is greater than 20% over the prescribed dose for this treatment and thus a reportable event. The RSO reported that the clinical range for this treatment is 15-26 gray so no adverse health effects are anticipated with this event. The RSO stated that a written report would be filed with the department within the required 15 day period. "Event Date 12/05/2002 License No: IL-01094-01 Licensee: Northwest Community Hospital City: Arlington Heights State: IL Event Class: MD2 - MEDICAL EVENT Medical Event Information: Patient Number: 1 % Overexposed: 23 Procedure: BRACHY, REMOTE AFTERLOADER, Dose in RAD: 2460 Organ: HEART Study: CARDIOVASCULAR SYSTEM Radionuclide: P-32 Administered By: PHYSICIAN Keywords: INTRAVASCULAR BRACHYTHERAPY" Item Number: IL020074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-12-11
39425 | 0 | LEHEIGH VALLEY HOSPITAL |  |  |  |  | 2002-12-04 17:00 | 2002-12-05 12:10 | 2002-12-05 | MEDICAL EVENT - DOSE TO SKIN OTHER THAN TREATMENT SITE The attending physician, also the Radiation Oncologist, discovered that one of the catheters containing 3 seeds of iridium-192 was out of position. The treatment was a 48 hour dose to the lip area for a carcinoma. The physician had checked the location at 1700 EST on 12/3/02 and when checking at 1700 EST on 12/4/02 discovered the one catheter under the patient under a bed pad. The estimated dose to the skin of the back, conservatively using the entire 24 hours, is 240 rem. The possible result is some erythmea, reddening of the skin. The patient has been informed. The actual treatment site dose is only 4.3 % under the planned so no further treatment is necessary or reportable. The Radiation Safety Officer intends to notify NRC Region 1. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2002-12-05
39424 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-12-05 03:07 | 2002-12-05 08:45 | 2002-12-05 | LOSS OF OFFSITE EMERGENCY SIRENS DUE TO ADVERSE WEATHER "At 0307, greater than 20% of the Off Site Emergency Sirens were inoperable due to loss of power during the current Ice Storm. Currently 59 of 81 sirens are out of service. This requires an 8 hour notification per 10CFR 50.72. Additionally, at 0645, Lee County had gone one hour without any operable sirens. At 0830, Harnett County had gone one hour without any operable sirens. Transmission is aware and are prioritizing repairs." The licensee informed state/local agencies and the NRC resident inspectors. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-05
39423 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-05 01:45 | 2002-12-05 02:00 | 2002-12-05 | LOSS OF OFFSITE EMERGENCY SIRENS DUE TO ADVERSE WEATHER "Any event that results in a major loss of emergency assessment capability, offsite response capability; or offsite communications capability. Currently greater than 16 ENS sirens are inoperable which is greater than 25% of siren capability." The licensee will inform local agencies and the NRC resident inspector. * * * * UPDATE FROM LICENSEE TO MIKE RIPLEY AT 1647 EST 12/5/02 * * * * The licensee stated that crews are continuing to restore all ENS sirens to service and that currently only 13 ENS sirens are inoperable which is less than the 25% of siren capability criteria. Notified R2DO (Robert Haag) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-05
39422 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-12-05 00:43 | 2002-12-05 01:52 | 2002-12-08 | LOSS OF OFFSITE EMERGENCY SIRENS DUE TO ADVERSE WEATHER "Twenty-four (24) emergency sirens out-of-service due to loss of power because of ice storm. These sirens have been out-of-service more than one hour and preparations underway to restore to service." The licensee will inform state/local agencies and the NRC resident inspector. * * * UPDATE ON 12/05/02 @ 1028 BY BRADLEY TO GOULD * * * The site currently has 47 of 89 sirens out of service and has placed their backup route alerting system in service in the affected counties. They also have a reverse 911 callup system in place in the county that the site is located. Present estimates for returning power to the counties and thus to the sirens is approximately one or two days. The Resident Inspector was notified. * * * UPDATE ON 12/08/02 AT 1730 EST BY BRADLEY TO JONES * * * "This report is concerning Catawba Nuclear Station present siren status. There are still 9 out of 89 CNS sirens out of service due to loss of power in the EPZ Counties from the ice storm. "Significant progress has been made on restoring power to the EPZ counties as shown by the following siren status: 2 of 72 in York County, 3 of 6 in Gaston County, and 4 of 11 in Mecklenburg equals 9 out of 89 sirens without power. Route alerting for all counties is still in place and available if needed. Present estimation for the return of these nine sirens [is] one to two more days." The NRC Resident Inspector will be notified. Notified R2DO (B. Bonser) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-12-05
39421 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2002-12-03 13:30 | 2002-12-03 17:13 | 2002-12-26 | HPCI SYSTEM DECLARED INOPERABLE DURING QUARTERLY PERFORMANCE TESTING "During scheduled High Pressure Coolant Injection [HPCI] system quarterly performance testing, the HPCI system was declared inoperable when it was determined that the HPCI turbine steam admission valve (23MOV-14) failed ASME Section XI, Inservice Testing Stroke Time Criteria. During Testing the steam admission valve opened only 35-38% of full stroke. However, with this deficiency the HPCI system met required test acceptance criteria for flow control, injection capacity, and injection time. It was determined that the steam admission valve partially opened due to a broken wiring connection in the valve operator. The broken connection was repaired and HPCI testing was completed satisfactorily. The HPCI system was declared operable at 1630 EST (12/3/02)." The licensee intends to notify NRC Region of this event. * * * EVENT RETRACTION FROM ANDY HALLIDAY TO ARLON COSTA ON 12/26/02 AT 14:56 * * * "Event Notification Retraction "On 12/3/02 at 1330 EST, the James A. Fitzpatrick nuclear power plant notified the NRC operations center of the High Pressure Coolant Injection (HPCI) System being declared inoperable when the HPCI turbine steam admission valve (23MOV-14) failed ASME Section XI lnservice Testing stroke time criteria. During testing, the steam admission valve opened only approximately 39% of full stroke due to a broken wiring connection in the valve operator, The report was made pursuant to 10CFR50.72(b)(3)(v)(D) under Event Notification number 39421. "Based upon further review, it has been determined that, despite the problem noted, HPCI would have performed its safety function, With this deficiency (at 1040 psig reactor pressure), the HPCI system still met the required test acceptance criteria for flow control, injection capacity and injection time, as the HPCI control valve, located in series in the steam flow, compensated for the partial closure of the steam admission valve. An engineering evaluation showed that the HPCI System would have continued to meet its design basis requirements over the full operational pressure range (150 psi to 1195 psig). "The failure of 23M0V-14 to fully open was immediately corrected. The cause of the failure and its applicability to other safety related components will be determined through the JAF corrective action system. "Based upon the ability of the HPCI System to perform its safety function, the above notification, number 39421 is being retracted." The Licensee has notified the NRC Resident Inspector. Notified R1DO (Jenison). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-12-03
39420 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-30 18:57 | 2002-12-03 15:04 | 2002-12-03 | UNOCCUPIED CONTRACTOR VEHICLE ROLLED DOWN EMBANKMENT AND CAUGHT FIRE "The following is an Information Only notification based on the potential for interest and rumor control. "On November 30, 2002, at 1857 PST, an unoccupied vehicle went over an embankment and landed in the surf zone near the plant discharge. The 3/4 ton diesel 4 x 4 pickup truck landed on its wheels with its engine running. Waves were breaking over the hood. Due to safety concerns personnel were not allowed access to the vehicle, and the engine continued to run. There was no evidence of an oil or fuel leak. At 2256 PST, the vehicle caught fire. The plant fire department put the fire out with water. "The National Response Center and [California] Office of Emergency Services were notified of the potential for a release. "On December 1, 2002, the vehicle was pulled out and inspected. The fuel tank and oil pan were still intact." The licensee notified the NRC Resident Inspector of this event. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2002-12-03
39419 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-12-03 08:55 | 2002-12-03 13:35 | 2002-12-03 | FITNESS FOR DUTY - EMPLOYEE FAILED RANDOM DRUG TEST A non-licensed employee tested positive for drugs during a random drug test. The employee's access to the plant has been terminated. Contact the HOO for additional details. The licensee will notify the NRC Resident Inspector of this event. | 0 | 90 | 100 | 0 | 90 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2002-12-03
39418 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2002-12-02 17:46 | 2002-12-02 19:48 | 2002-12-02 | COMMENCEMENT OF TECH SPEC REQUIRED SHUTDOWN "At 16:47 (EST) Unit 1 experienced a loss of Channel 12 Reactor Protection System (RPS). Power to RPS Bus 12 was shifted to its backup power supply. This was coincident with Emergency Diesel Generator 102 (EDG) being inoperable. This condition requires commencement of a Plant Shutdown within 1 hour and be in a Cold Shutdown Condition in ten hours (LCO for TS 3.6.3 - Emergency Power Sources). At 1746 a shutdown was commenced in accordance with N1-OP-43C. At 1900 a successful post maintenance test was completed on EDG 102 and EDG 102 was declared operable. Plant Shutdown actions have been terminated and the 1 and 10 hour shutdown LCO exited. The plant is at 98.6 percent power and remains in a 7 day LCO in accordance with TS 3.6.3 (Emergency Power Sources). "Investigation is underway into the cause of the loss of RPS Bus 12." Also, the loss of one half of the 'Energize to Function' portion of the Automatic Depressurization System. The NRC Resident will be informed of this event. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION | POT RHR INOP |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) | 50.72(b)(3)(v)(B) |  | 0 | 2002-12-02
39417 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-11-29 09:00 | 2002-12-02 17:42 | 2002-12-06 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "This is to report a stolen moisture density gauge in the State of California (California incident number 112902). "The licensee is Geosoils in Van Nuys, California (California license number 4741-19). The gauge was reported stolen via a voice-mail message left Friday morning, November 29, 2002. The State offices were closed that day for the Thanksgiving holiday. "The gauge was stolen some time mid-morning on November 29, 2002, from the back of a pick-up truck, parked at a residence in the city of Gardena. The chain securing the gauge package to the truck was cut. The local police took a report. The licensee will be running an ad offering a reward for the return of the gauge for the next 10 days in the local newspaper. "This is all the information we have at the present time. We are awaiting a report from the licensee, confirming the activity and nuclide(s) in the gauge, as well as the serial number, and other information." * * * * UPDATE FROM ROBERT GREGOR TO MIKE RIPLEY (VIA FAX) AT 1509 EST ON 12/6/02 "On December 5, 2002, GeoSoils left a message on my voicemail stating that the gauge had been recovered, and was intact. "December 6, 2002, telephone call with Ron Allen, RSO. The gauge was founded abandoned on Alabama Street, in South Central Los Angeles. "LAPD and LAFD were notified that there was a suspicious orange package with radiation symbols that was unattended in the street. Both agencies responded, inspected the package, and determined that it was undamaged and so they checked it into evidence at the Lynwood Police Dept. "GeoSoils was notified by LAPD that their property had been found, and they could come retrieve it. "GeoSoils took photographs of the gauge, determined that the sources were still in the gauge, and will send the gauge to Maurer Associates (the local CPN authorized service representative) for a thorough inspection." Notified R4DO (Williams) and NMSS EO (Fred Brown) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-12-05
39416 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-12-02 14:15 | 2002-12-02 17:32 | 2002-12-02 | OFFSITE NOTIFICATION TO THE DOE CONCERNING ACCIDENTAL DISCHARGE OF WEAPON ON SITE Misfired security weapon. No one was hurt during this incident and compensatory measures were taken as appropriate. The Licensee notified the DOE and is in the process of filing a report and indicated that there may be a press release on this incident. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-12-02
39415 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-11-20 | 2002-12-02 15:50 | 2002-12-02 | AGREEMENT STATE REPORT INVOLVING MEDICAL MISADMINISTRATION "A medical misadministration was reported to Arkansas Department of Health Radiation Control and Emergency Management's Radioactive Materials Program by CARTI-UAMS on November 27, 2002 via a voice mail message. Due to the Thanksgiving holiday, the message was not reviewed by the Department until December 2, 2002. "According to the voice mail message and the preliminary telephone interview with the licensee, the misadministration resulted from the incorrect positioning of a treatment tandem within the cervical treatment cylinder. As a result, the treatment was delivered approximately 3 cm inferior to the intended position. The incorrect positioning of the tandem that occurred during first treatment on November 20, 2002 was noted when the medical physics staff was reviewing the position verification film for the second treatment on November 27, 2002. "An onsite investigation will be conducted by the Department on December 2, 2002. An updated report of the medical misadministration will be provided following this investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2002-12-05
39414 | 0 | PALISADES | 1 |  |  | [1] CE | 2002-12-01 21:54 | 2002-12-02 01:43 | 2002-12-02 | AUTOMATIC REACTOR TRIP ON LOSS OF MAIN GENERATOR LOAD "At 2154 hours on December 1, 2002, an automatic reactor trip occurred on loss of main generator load. The loss of load trip occurred when the main generator tripped due to a fault in the plant switchyard. The switchyard fault was caused when the ground wire on the 345 KV transmission tower which is immediately adjacent to the plant switchyard fell and came in contact with switchyard 'R' bus. When the main generator tripped, and with the switchyard 'R' bus de-energized as a result of the fault, the cooling tower pumps, condensate pumps, and primary coolant pumps lost power. The steam driven main feedwater pumps tripped due to loss of suction pressure when the condensate pumps tripped. The reactor trip occurred as expected with all full-length control rods fully inserted. With the loss of the main feedwater pumps the auxiliary feedwater system actuated as expected and is currently providing core heat removal. The plant is currently stable in Mode 3 on natural circulation. "Palisades Switchyard Configuration "The Palisades switchyard is comprised of two 345 KV busses, the 'F' (Front) and 'R' (Rear) busses. The plant's Safeguards transformer is fed from the 'F' bus. The plant's vital AC busses are normally aligned to the Safeguards transformer and remained powered throughout the event. The plant's Startup transformer is fed from the 'R' bus. The plant's non-vital AC busses would normally transfer to the Startup transformer on a reactor trip. However, with the 'R' bus deenergized the Startup transformer was not available and therefore power was lost to the cooling tower pumps, condensate pumps, and primary coolant pumps. "Core Heat Removal "Core heat removal is being provided by the auxiliary feedwater system with steaming to atmosphere via the atmospheric steam dump valves. The auxiliary feedwater system is comprised of three, full capacity, auxiliary feedwater pumps (two motor driven pumps and one steam driven pump). The motor driven pumps are powered from the plant's vital AC busses. All three auxiliary feedwater pumps are operable and one pump is in service providing core heat removal. "Extra precautions have been taken to ensure the operability of the auxiliary feedwater pumps and their power supplies, including the vital AC busses, their associated diesel generators, and the offsite circuit from the Safeguards transformer. "Plant Technical Specifications "The following three Technical Specification LCO Conditions apply as a result of the loss of the switchyard 'R' bus: "Condition 3.8.1A, One offsite circuit inoperable. "Condition 3.4.5A, One required PCS loop inoperable. "Condition 3.4.5C, No PCS loop OPERABLE." The Licensee reports that there is no primary to secondary leakage in the steam generators. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-12-02
39413 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2002-12-01 17:33 | 2002-12-02 00:31 | 2002-12-06 | STATION STARTUP AND EMERGENCY STATION SERVICE TRANSFORMERS DECLARED INOPERABLE "Available plant indicators showed that main generator output exceeded 150 MVARs [million volt-amperes reactive] for approximately 4 minutes due to local grid conditions at 17:33 hours on December 1, 2002. The maximum value noted was 155 MVARs. Recent analysis and procedural guidance requires the two offsite power sources, consisting of the Station Startup Service Transformer and the Emergency Station Service Transformer to be declared inoperable above 150 MVARs. The grid operator was contacted and action was taken to lower local MVARs to below the allowed limit. The offsite power sources were declared operable at 17:37 hours." The Licensee has notified the NRC Resident inspector. * * * * RETRACTION FROM COY BLAIR TO MIKE RIPLEY ON 12/6/02 AT 1358 EST * * * * "EN # 39413 reported declaring both off-site power sources inoperable due to generator MVAR output being above procedural limitations. An updated loadflow analysis was performed to evaluate off-site grid response under the conditions existing at the time of the event. The results of this evaluation demonstrated that procedural MVAR limits were conservative and that off-site power sources remained operable during the period of time that generator MVAR output was above procedural limitations." The licensee notified the NRC Resident Inspector. Notified the R4DO (W. Jones). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-12-02
39412 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-30 16:05 | 2002-11-30 21:30 | 2002-11-30 | OFFSITE NOTIFICATION TO LOCAL LAW ENFORCEMENT AGENCIES Potential trespasser outside of the Protected Area. Immediate compensatory actions taken. Local law enforcement notified. Licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Center for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-30
39411 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-11-28 13:50 | 2002-11-29 18:19 | 2002-11-29 | AGREEMENT STATE REPORT INVOLVING A STOLEN PORTABLE GAUGE "An authorized user reported that a portable gauge (believed to be a Troxler model 3411 containing no more than 10 millicuries of cesium 137 and no more than 50 millicuries of americium 241/beryllium) had been stolen from his pickup truck sometime between 7:30 PM Wednesday, November 27, and 4 AM Thanksgiving morning. The authorized user had brought the gauge to his residence and left the gauge in its locked case chained into the open bed of his pickup truck. During the night an attempt was made to cut the chain. However, it proved to be easier to break off the case handle through which the chain was secured to the vehicle. The damaged but presumably still locked case and locked gauge were then removed. The authorized user notified the police and called the Department of Health's radiation emergency line (206-NUCLEAR). The licensee's RSO was out of town and an alternate licensee official was notified. Department of Health staff advised the licensee official to post a reward and to provide more detail including the serial number of the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-12-04
39410 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2002-11-28 21:05 | 2002-11-28 23:08 | 2002-11-28 | OFFSITE NOTIFICATION TO LOCAL LAW ENFORCEMENT AGENCIES Non-credible bomb threat. Immediate compensatory actions taken. Local law enforcement notified. Contact the Headquarters Operations Center for additional details. Licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-29
39409 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2002-11-22 | 2002-11-27 15:31 | 2002-11-27 | AGREEMENT STATE REPORT INVOLVING A STOLEN/RECOVERED TROXLER GAUGE A Troxler Model 3440, S/N 26331, containing 8 millicuries Cs-137 and 40 millicuries Am-241:Be, was recovered from an abandoned stolen vehicle in Queens, NY at approximately 1300 EST on 11/27/02 after a police cruiser's radiological pager alerted. The vehicle was stolen from a location on 120th Street between 20th and 21st Ave in Queens and reported to the NY City Police Department on 11/22/02. The NY City Health Department Bureau of Rad Health is storing the gauge in their lab currently and will return it to the licensee after confirming proper ownership. The gauge was found intact with normal radiation readings. Materials Testing Lab, Inc. is a NY State DOL licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2002-12-02
39408 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-11-25 12:00 | 2002-11-27 11:25 | 2002-11-27 | STATE LICENSEE REPORTED A STOLEN MOISTURE DENSITY GAUGE Soils and Material Consultants reported to the state that a CPN model MC1DR (serial # MD 80804445) moisture density gauge was stolen from a truck with a locked camper shell while parked on a Wal Mart parking lot in Brighton, Co. The gauge was not chained or locked to the truck bed. It contained 10 millicuries of Cs-137 and 50 millicuries of Am-241:Be. Local law enforcement was notified. No media inquiry or reward has been made at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-12-02
39407 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2002-11-25 14:30 | 2002-11-26 14:02 | 2002-11-26 | AGREEMENT STATE NOTIFICATION - DAMAGE TO TROXLER MOISTURE DENSITY GAUGE "While a back scatter measurement was being taken in a closed lane of Interstate 75 southbound a tractor-trailer swerved to avoid another vehicle, struck the gauge damaging it. Based on field measurements there is no evidence of the sources being breached or leaking, no contamination identified. Source was separated from the source rod. The gauge has been recovered and returned to the [Georgia] DOT [Department of Transportation] headquarters office. This is all that is known about the incident at this time." The gauge contained 10 millicuries of Cs -137 and 40 millicuries of Am-241:Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | GA | OTH | AGR |  |  |  |  | 0 | 2002-11-29
39406 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-11-26 03:42 | 2002-11-26 08:24 | 2002-12-30 | UNIT 2 HPCI SYSTEM DECLARED INOPERABLE Unit 2 HPCI (High Pressure Coolant Injection) system was declared inoperable at 0342 [CST] due to a failed relay for the MGU (Motor Gear Unit) flow control circuit. The relay is normally energized when the MGU is at the High Speed Stop and is utilized to de-energize the motor gear unit when a limit switch is reached to prevent damage to the MGU motor. The resultant failure affects HPCI such that the MGU will not function from a signal generated by the Flow Indicating Controller. HPCI can be operated manually from [the] Control Room. The Resident Inspector was notified of this event. *** EVENT RETRACTION FROM ROBERT BROCH TO ARLON COSTA ON 12/30/02 AT 1326 *** "On November 26, 2002 at 0724 CST, Dresden Station made an ENS Notification (EN 39406) regarding a High Pressure Coolant Injection inoperability due to a failed relay for the Motor Gear Unit (MGU) flow control circuit. It was reported that the failed relay affected HPCI such that the MGU would not function from a signal generated by the Flow Indicating Controller. The MGU was capable of being operated from the Control Switch in the Control Room at all times. The condition was reported, in accordance with 10 CFR 50.72(b)(3)(v)(D), as reduction in accident mitigation capability. "Upon further evaluation of the issue, the following conclusions were reached: In the event that HPCI would have automatically initiated following the failure of the relay, the Motor Speed Changer (MSC) would have run to the High Speed Stop (HSS). When the turbine reached 4000 rpm and flow increased the MGU would have remained at the HSS. Therefore, HPCI would have continued to operate at 4000 rpm and maximum injection flow (>5000 gpm) until the system restored reactor water level to +48" (at which point the turbine trips) or the Control Room Operator took manual control. It is important to note at this point that even if the flow controller circuitry is operational, the system would have responded in the same manner described above. If no operator action was assumed following the relay failure, HPCI would have increased reactor water level to the high water trip for break sizes within its capability. "NUREG 1022 states that the intent of the 10 CFR 50.72 and 50 .73 reporting criteria is to capture events where there would have been a failure of a safety system to properly complete a safety function. In the above described condition, the HPCI system was still capable to perform its intended safety function. The system would have automatically started on an initiation signal, come up to speed (4000 rpm), and provided >5000 gpm to the reactor vessel. Additionally, the restart capability of the system was not affected by the relay failure. Therefore, the system would have operated long enough to complete its intended safety function as defined in the safety analysis report. "Based on the above evaluation, HPCI was capable of performing its functions as specified in the Technical Specifications, the safety analysis report and met all of the operability requirements specified by the plant licensing basis. Based on these conclusions, EN #39406 is being retracted. The NRC Resident Inspector and the R3DO(Lanksbury) were notified. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-11-26
39405 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2002-11-25 16:10 | 2002-11-25 17:08 | 2002-11-25 | OFFSITE NOTIFICATION TO THE STATE OF FLORIDA CONCERNING DISCHARGE OF A WEAPON ONSITE "On November 24, 2002, at 1715 hours, a contract security officer inadvertently discharged his weapon when it was reloaded following routine maintenance. The accidental weapon discharge was attributed to personnel error, and no injuries resulted from this event. In accordance with Chapter 493 of the Florida Statutes, Wackenhut Corporation, the state licensed FPL security contractor, notified the Florida Division of Licensing of this event on November 25, 2002, at 1610 hours. This non-emergency notification is being made pursuant to 10 CFR 5072(b)(2)(xi) due to the notification of Florida Division of Licensing." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-25
39404 | 0 | SPECTRUM TECHNOLOGIES |  |  |  |  | 2002-11-25 | 2002-11-25 16:25 | 2002-11-25 | PART 21 INITIAL NOTIFICATION - CUTLER-HAMMER A200 NEMA SIZE 1 STARTERS "Equipment Identification: Starter, Non-Reversing, Size 1, 600 VAC, 3 Pole, W/125 VDC coil, Westinghouse/Cutler-Hammer P/N A200M1CS, Type B Thermal Overloads, Ambient Compensated, Manual Reset Only "In March 2002, Spectrum Technologies provided 20 Class 1E safety related Cutler-Hammer A200 NEMA Size 1 starters to Rochester Gas & Electric Company - Ginna Station. We had purchased the starters as commercial grade items from Cutler-Hammer, and dedicated them per EPRI NP5652, method 1, Special Tests and Inspections. This dedication successfully verified the following critical characteristics: Markings Dimensions and Configuration Electrical Functional Attributes, Including: Insulation Resistance, Current Carrying Capacity, Minimum Pickup and Drop Out Voltage, [and] Time Current Characteristics of Overload Relay "Ginna Station recently advised us that one of the starters had experienced an open phasing failure. They reported that they noted no current flow on one phase when measured with a clamp-on ammeter, and that current started to flow when the hand pressure was applied to the moving plunger extension that protrudes out the top of the starter. They also noted that the overall travel of the plunger appeared to be less than that noted on a similar older vintage starter. They provided the failed starter and the older vintage starter to us for our investigation. The continuity of all phases was successfully verified, along with the magnetic pull force of the coil, which was comparable to the older vintage starter. We then mounted the failed starter on a vertical plate in a horizontal (worst case) orientation, energized the coil and loaded the main contacts to 27 amps. This condition was maintained until the temperature stabilized with the highest temperature recorded on the terminals (i.e., 59 [degrees] C to 63 [degrees] with ambient at 20.3 [degrees] C). None of this testing performed could duplicate the single phasing condition observed by Ginna Station. We verified that the total stroke of the failed starter was less than that of the earlier vintage starter by as much as 0.059 [inches] by our measurement. "The failed starter and the earlier vintage starter were provided to Cutler-Hammer for an OEM evaluation. The results of the OEM evaluation was e-mailed to our Cutler-Hammer distributor and provided to us on November 21, 2002, a copy is attached. This information has been provided to Ginna Station, and they advised us today (November 25, 2002) that the starters have been installed in 11 safety related locations, as follows: MOV-857A, Residual Heat Removal Pump A Discharge MOV-4616, Service Water Isolation in Auxiliary Building (Open & Close Circuit) MOV-860C, Containment Spray Pump B Discharge MOV-813, Component Cooling Water Isolation to Reactor Support Coolers (Open & Close Circuit) MOV-700, Residual Heat Removal Pump Suction from Loop A Holt Leg MOV-878A, Safety Injection Discharge to Loop B MOV-856, Residual Heat Removal Suction from Refueling Water Storage Tank MOV-4780, Service Water Isolation in Screenhouse (Open & Close Circuit) "We are currently expediting Cutler-Hammer to complete an audit at their manufacturing facility to identify the magnitude of this condition and specify the date codes effected. We are also expediting Cutler-Hammer to obtain acceptable replacements for the starters provided to Ginna Station." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2002-11-25
39403 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-11-25 | 2002-11-25 12:55 | 2002-11-25 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The State of Colorado Radiation Services notified us that on 11/24/02, Goodson & Associates reported a Troxler moisture density gauge, model 3430, serial number 22804, was stolen from the back of a vehicle in Denver, CO. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-11-28
39402 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-11-24 08:14 | 2002-11-24 10:29 | 2002-11-24 | NOTIFICATION OF OFFSITE AUTHORITIES OF FIRE IN ONSITE WAREHOUSE "At approximately 08:14, Sunday, November 24,2002, East Warehouse Sprinkler System Initiated annunciator alarmed. Seconds later, 1P-48 Electric Fire Pump initiated as indicated on panel 1C40. The Second Assistant was dispatched and reported the sprinkler system in operation and a portion of the East Warehouse filled with smoke. The on-site fire brigade was assembled at this time. "The Fire Brigade Leader, after reaching the East Warehouse, reported no open flames and smoke emanating from a popcorn machine located in a breakroom in the warehouse. As a precaution, off-site assistance was requested of the Palo Fire Department. Currently the fire is out and the building is being ventilated. This notification is being made due to notification of offsite fire department and local law enforcement agencies." The licensee notified the NRC Resident Inspector. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-24
39401 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-11-23 03:32 | 2002-11-23 07:37 | 2002-11-23 | AUTOMATIC REACTOR TRIP DUE TO LOW-LOW STEAM GENERATOR LEVEL "At 0332 hours, with Surry Power Station Unit 2 at 85% reactor power, a low low S/G level signal was received which resulted in an automatic reactor trip. Immediately prior to the trip, the Turbine Stop and Governor Valves were being manipulated for a scheduled Governor Valve Freedom Test. While closing Turbine Governor Valve #3 the Turbine Valve Limiter failed to zero closing all four governor valves. This led to the automatic reactor trip. "IRPI indications for six control rods indicated between 11 and 20 steps following the trip. [Unit 2 was] borated as necessary to ensure adequate shutdown margin. All other control rods fully inserted into the core as designed. The shutdown margin for Unit 2 was determined to be satisfactory. Auxiliary feedwater automatically initiated [ESFAS] as designed on low low steam generator level. All three Main Steam Trip Valves were manually closed due to inability to verify full closed indication on #1 Turbine Stop Valve. Primary RCS temperature decreased to approximately 547 degrees following the reactor trip and is currently stable on the Secondary Power Operated Relief Valves. "No primary safety or power operated relief valves were actuated during the event. No indication of primary to secondary leakage exists, therefore no adverse radiological consequences resulted from this event. "All electrical busses transferred properly following the trip and all emergency diesel generators are operable. There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. The cause of the event is being investigated. "Unit 2 is currently at Hot Shutdown with RCS temperature being maintained at approximately 547 degrees. "Unit 1 was not affected by this event and remains stable at 100% power operations. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(b)." The Resident Inspector was notified of this event. | 0 | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-11-23
39400 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-11-22 01:04 | 2002-11-22 22:54 | 2002-11-22 | NON-CONSERVATIVE ANALYSIS OF THE OSCILLATION POWER RANGE MONITOR PERIOD SETPOINT "On November 22, 2002, Nine-Mile Point Unit 2 received confirmation from General Electric of a Non-Conservative Analysis of the OPRM Period Setpoint. "The Non-Conservative Analysis affected the OPRM Reactor Protection System (RPS) scram setpoint. The RPS setpoint could have resulted in violating the Minimum Critical Power Ratio (MCPR) safety limits during a thermal - hydraulic instability. "At the time of the notification Nine-Mile Point Unit 2 was in Mode 4 cold shutdown. Upon notification, the OPRM's were immediately declared inoperable. "On November 22, 2002, the OPRM's were adjusted to satisfy the vendor recommendations and the OPRM's have since been declared operable. "This report is being made in accordance with Nine-Mile Point Unit 2's Operating License 2.C.2 Technical Specification and Environmental Protection Plan. Nine-Mile Point Nuclear Station, LLC shall operate the facility in accordance with Technical Specifications." The NRC Resident Inspector has been notified of this event | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2002-11-22
39399 | -1 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2002-11-22 16:50 | 2002-11-22 21:17 | 2003-08-04 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During inspection of the High Pressure Core Spray (HPCS) 2VY02A area cooler, missing sheet metal screws were discovered. This could have prevented the High Pressure Core Spray System (HPCS), a single train safety system, from performing its design function during a seismic event. This also made the Division 3 Diesel Generator inoperable. This is reportable as an 8 hour ENS notification. "The required actions of Technical Specification (TS) 3.5.1 were entered on 11/22/02 at 1650 when the system was made inoperable. TS 3.8.1 does not require Division 3 Diesel Generator operability if HPCS is declared inoperable. Preparations to replace the missing sheet metal screws are in progress. All other Emergency Core Cooling Systems are operable at this time. An extent of condition review will be performed on all divisions for both units." The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 11/23/02 @ 1333 BY CLARK TO GOULD * * * "Subsequent to ENS notification EN #39399, repairs were affected to the HPCS area cooler (2VY02A) and the system was returned to operable. An extent of condition inspection was performed on the remaining Unit 1 and Unit 2 divisional area coolers. During these inspections it was discovered that the Unit 1, Division 2 area cooler (1VY03A) was also missing several sheet metal screws. The system was removed from service, repaired and returned to operable. No problems were discovered on either of the two remaining Unit 1 divisional area coolers. During inspection on Unit 2, the Division 2 area cooler (2VY03A) was missing all of its sheet metal screws. At the time of discovery of the Division 2 inoperability, the HPCS (Division 3) area cooler had already been repaired and declared operable. It was determined however, that at some point both the HPCS (Division 3) and Division 2 Emergency Core Cooling System (ECCS) injection subsystems were under these conditions simultaneously. Per Technical Specification (TS) 3.5.1 Bases when this combination of ECCS subsystems are inoperable, the plant is in a condition outside of the design basis. Investigation of equipment and maintenance history will be performed to determine if any additional periods existed with multiple divisions under these conditions simultaneously. At this time all divisional area coolers on both Units have been inspected. Those with deficiencies have been repaired and declared operable." The NRC Resident Inspector was notified. Reg 3 RDO (Clayton) was informed. * * * RETRACTION ON 08/10/03 AT 1556 FROM LARRY R. BLUNK TO ARLON COSTA * * * "THIS REPORT CONCERNED THE DISCOVERY THAT THE COOLING COIL MOUNTING SCREWS FOR A NUMBER OF DIVISIONAL AREA COOLERS ON BOTH UNITS 1 AND 2 WERE NOT INSTALLED, WHICH COULD HAVE RENDERED THE ASSOCIATED ECCS SYSTEMS INOPERABLE DURING A SEISMIC EVENT. "STRUCTURAL ANALYSES HAVE BEEN COMPLETED THAT DEMONSTRATE THAT THE SUBJECT DIVISIONAL COOLERS WERE OPERABLE WITH THE COOLING COIL MOUNTING SCREWS NOT INSTALLED. "THIS EVENT IS THEREFORE NOT REPORTABLE UNDER 10 CFR 50.72 (B)(3)(II) 'DEGRADED OR UNANALYZED CONDITION,' OR 10 CFR 50.72 (B)(3)(V)(D), 'EVENT OR CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION NEEDED TO MITIGATE THE CONSEQUENCES OF AN ACCIDENT.' "THE SENIOR RESIDENT INSPECTOR HAS BEEN NOTIFIED." Notified the R3DO (Christine Lipa). | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | UNANALYZED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2002-11-22
39398 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2002-11-22 10:30 | 2002-11-22 16:46 | 2002-11-22 | MISSING 5 MILLICURIE STRONTIUM-90 SOURCE. The Radiation Safety Officer for Brian LGH Medical Center located at 1300 South 16th Street in Lincoln, NE, noticed at 1030 CST on 11/22/02 that a source was missing from a Novoste Beta Cath System source holder. The source holder holds 16 sources of strontium-90, each source is 5 millicuries, and one of the sources was found missing. A search of the device and of the lab did not find the missing source. The RSO contacted the manufacturer. The last time the Novoste Beta Cath System was used was November 13, 2002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2002-11-27
39397 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-11-22 13:28 | 2002-11-22 16:29 | 2002-11-22 | NON-CONSERVATIVE ANALYSIS OF THE OSCILLATION POWER RANGE MONITOR PERIOD SETPOINT "On November 22, 2002, Brunswick Unit 1 received notification from General Electric of a Part 21 Non-Conservative Analysis of the Oscillation Power Range Monitor (OPRM) Period Setpoint. The non-conservative analysis affects the OPRM Reactor Protection System setpoint which may result in inoperability of the OPRM Technical Specification function. Unit 2 does not have the OPRM system installed and is not affected by this condition. Due to the implementation of Technical Specification required compensatory actions, there is minimal safety significance. "All Unit 1 OPRM channels have been declared inoperable. Technical Specification 3.3.1.1 Action I requires an alternate method of detecting and suppressing thermal hydraulic instabilities to be implemented within 12 hours. The alternate methods of detection and suppression are currently in place. Activities are in progress to make the necessary adjustments to return the OPRM channels to an operable status." | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-11-22
39396 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2002-11-22 10:00 | 2002-11-22 16:18 | 2002-11-22 | INADVERTENT START OF "B" EMERGENCY DIESEL GENERATOR "The cause of the inadvertent actuation was human error by an Auxiliary Operator. The Auxiliary Operator mistakenly placed the "A" diesel generator Engineering Safeguards Test Switch in the "Test" position, instead of placing the "B" EDG Engineering Safeguards Test Switch in the "Test" position. During the "B" ESAS [Emergency Safeguards Actuation System] testing, a portion of the test sends a simulated start signal to the "B" EDG. With the "B" EDG Engineering Safeguards test switch in the "Test" position, a light actuates when the simulated ESAS start signal is received, indicating that the ESAS start signal had been received. However, the "B" EDG Engineering Safeguards Test Switch was not in the "Test" position. Therefore the "B" EDG started in accordance with the plant design. "A review of this event has determined that the event is reportable to the NRC in accordance with the guidance in NUREG 1022, Rev. 2. The signal to start the "B" EDG is not considered a "valid" signal because it was not a signal initiated by any actual plant condition or parameter. Therefore, this event is considered to be an inadvertent actuation that was caused by an invalid signal and has been determined to be reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv)(A). "There was no effect on the TMl-1 plant due to the inadvertent start, beyond the "B" Emergency Diesel Generator, The "B" EDG did not initiate block loading or any other sequence of events. The "B" EDG was immediately shutdown and an event investigation was initiated. The "A" EDG remained operable throughout the event. Throughout the event, the "A" EDG was capable of providing emergency alternating current including performing the required "fast start" and block loading in response to an ESAS auto-start signal, an undervoltage condition or loss of offsite power event. "As an immediate action, a test run of the "B" EDG is being performed for approximately 1 hour to confirm that the inadvertent "fast" start did not have any impact on its ability to provide emergency alternating current in the event of an ESAS auto-start signal, an undervoltage condition or loss of offsite power. "As stated above, an event investigation has been initiated. The event will be documented in the site corrective action program. When the cause of the human error is identified, appropriate corrective action will be taken and documented in the applicable corrective action report." The Sr. Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-11-22
39395 | 0 | FRAMATOME ANP |  |  |  |  | 2002-11-22 | 2002-11-22 15:48 | 2002-11-22 | THE "POWERPLEX" MONITORING SOFTWARE CONTAINS AN ERROR "The MCPR calculation using the SPCB correlation in the MICROBURN-B2 and MICROBURN-B codes and associated POWERPLEX monitoring software contains an error. The error is in the determination of the axial adjustment factor for use in the SPCB CPR [Critical Power Ratio] correlation. This can lead to non-conservative CPR calculations when using the SPCB CPR correlation and potentially a violation of the MCPR [Minimum Critical Power Ratio] Technical Specification operating limit since the POWERPLEX incore monitoring code may under predict the MCPR for comparison to the operating limit. This error in MICROBURN-B2 and MICROBURN-B had no impact on the operating limit itself. The POWERPLEX incore monitoring software in use at River Bend, Grand Gulf, and LaSalle Unit 1 is impacted by this error." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-11-22
39394 | 0 | UNITED STATES ARMY -ABERDEEN |  |  |  |  | 2002-10-31 | 2002-11-22 15:31 | 2002-11-22 | MISSING CHEMICAL AGENT DETECTOR CONTAINING 30 MILLICURIES OF NICKEL-63 During a conversation in a training exercise on October 31, 2002, the Radiation Safety Officer at Fort Bragg, NC learned that a Unit had lost a GID-3 Chemical Agent Detector, containing 30 millicuries of Nickel-63, during a training exercise back in Oct/Nov of 2001. The training area was searched and other Units were asked if they had possession of the missing Chemical Agent Detector. The detector was not found and is now it considered missing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-11-22
39393 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2002-11-22 08:56 | 2002-11-22 15:10 | 2002-11-22 | SECURITY REPORT Unattended security weapon, compensatory measures put in place upon discovery. The NRC Resident Inspector was notified Contact HOO for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-11-22
39392 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2002-11-22 | 2002-11-22 13:43 | 2002-11-25 | GENERAL ELECTRIC IDENTIFIED THE STABILITY OPTION III PERIOD BASED DETECTION ALGORITHM Tmin SPECIFICATION HAS A DEFECT "Stability solution Option III is implemented in the Oscillation Power Range Monitor (OPRM). Each OPRM channel contains 18 to 33 OPRM cells (depending upon plant size). Each OPRM cell signal is summed from three to four closely spaced Local Power Range Monitor (LPRM) signals. Each OPRM cell signal is processed through the Option Ill detection algorithms to determine when a trip is required. Trip of one OPRM cell causes its OPRM channel to trip, and when sufficient OPRM channels trip (one-out-of-two taken twice, or two-out-of-four), a reactor scram is initiated to terminate the oscillation. "An OPRM trip is enabled for plant operation within the OPRM Armed Region as defined on the power/flow map. The Armed Region extends from natural circulation to 60% of rated core flow. The licensing basis for the OPRM is to detect all expected oscillations within the OPRM Armed Region, and initiate a reactor trip to suppress the oscillation and provide Minimum Critical Power Limit (MCPR) safety limit protection. "GE LTR NEDO-31960-A, Supplement 1, 'BWR Owners' Group Long - Term Stability Solutions Licensing Methodology (Supplement 1),' November 1995, describes the Option III detection algorithms. The Period Based Detection Algorithm (PBDA) provides licensing basis MCPR safety limit protection. Other algorithms provide defense-in-depth protection. The PBDA includes two parameters called Tmin and Tmax. The PBDA will not evaluate oscillations if the period is less than Tmin or greater than Tmax because these would not be indicative of an expected coupled neutronic/thermal - hydraulic instability. The LTR specifies that 'typical' Tmin values are in the range of 1.0 to 1.4 seconds and 'typical' Tmax values are in the range of 3.0 to 3.5 seconds. "The expected period of a coupled neutronic/thermal-hydraulic instability depends upon the fluid transit time through the core, and therefore depends upon core flow rate. This has been demonstrated in reactor operation and is predicted by GE computer models. At high core flow, the expected oscillation period is shorter. At low core flow rate, the expected oscillation period is longer. The intent of the OPRM is that Tmin and Tmax provide a wide range with adequate margin to the expected oscillation period for operation within the OPRM Armed Region so that all expected coupled neutronic/thermal-hydraulic instabilities will be detected by the PBDA." * * * * POTENTIALLY AFFECTED PLANTS ADDED TO REPORT BY RIPLEY 11/25/02 * * * * The notification identified the following potentially affected plants: Clinton, Brunswick 1, Brunswick 2, Nine Mile Point 2, Fermi 2, Columbia, Dresden 2, Dresden 3, LaSalle 1, LaSalle 2, Limerick 1, Limerick 2, Peach Bottom 2, Peach Bottom 3, Quad Cities 1, Quad Cities 2, Perry 1, Susquehanna 1, Susquehanna 2, Hope Creek, Hatch 1, Hatch 2, Browns Ferry 2, Browns Ferry 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-11-22
39391 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-11-22 10:45 | 2002-11-22 13:34 | 2002-11-22 | OFFSITE NOTIFICATION MADE TO MARYLAND DEPARTMENT OF ENVIRONMENT Hydraulic oil spill from a Sky Lift resulted in 5 gallons of hydraulic fluid deposited on the gravel and pavement below the Sky Lift. The spill was from a separated oil line. No water ways or storm drains were involved. ERPIP 3.0 Hazardous Material Spill and Spill Plan were implemented. Maryland Department of Environment was notified of the hydraulic oil spill (quantity >26 gallons). The event was terminated and the spill was cleaned up at 1300 hours. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-22
39390 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-11-21 09:00 | 2002-11-22 13:03 | 2002-11-22 | STATE LICENSEE REPORTED A CPN MOISTURE DENSITY GAUGE STOLEN State Licensee, Southern California Soil and Testing, Inc. reported that a CPN MC-3, serial # 360203032, moisture/density gauge was stolen from the operator's vehicle in San Diego County. The gauge had been secured to the bed of the truck using a cable and locks. The cable was cut in two places and the gauge was removed. The operator was unsure of the exact location where the theft took place. He made two stops after picking the gauge up from his office, one at his home for 25 mins and one at a 7/11 store at 6:45am. He did not notice the gauge was missing from the back of his truck until an hour later when he checked to see if the gauge had shifted after braking in traffic. The gauge contained 10 millicuries of Cs-137 and 50 millicuries of Am-241:Be. The local law enforcement was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-11-27
39389 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-11-21 21:56 | 2002-11-22 06:27 | 2002-11-22 | VALID SPECIFIED SYSTEM ACTUATION DURING MAINTENANCE "At 2156, 11/21/02, while performing OSP-SB-0002E, a valid actuation signal was generated that caused the 'B' Reactor Trip Breaker to trip open. The cause of the event was the inadvertent mispositioning of a rotary selector switch utilized in the Solid State Protection System (SSPS) circuitry, which enabled the P-10 permissive circuit. Permissive P-10 is normally energized when power increases above 10 percent and this in turn enables a Reactor Trip permissive (P-7) for a low Pressurizer pressure reactor trip which has a setpoint of 1885 psig. Since the plant was in Mode 4 with primary system pressure at 970 psig, a valid Reactor Trip signal was generated and caused the Reactor Trip breaker to open. In addition to tripping the 'B' Reactor Trip breaker, one Source Range detector was de-energized due to energizing the P-10 permissive circuitry. All systems actuated as expected. Performance of OSP-SB-0002B was terminated, the plant was stabilized, a recovery plan was developed, and the procedure was then successfully completed. An Event Review Team (ERT) was assembled to determine the cause of the event. Additional corrective action to be taken will be based upon recommendations provided by the ERT." The Resident Inspector will be notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-11-22
39388 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-11-21 19:53 | 2002-11-22 00:50 | 2002-11-22 | OPRM CHANNELS DECLARED INOPERABLE "On November 21, 2002, Detroit Edison received confirmation from General Electric of a non-conservative analysis of OPRM Period Setpoint. "The non-conservative analysis affected the OPRM [Oscillating Power Range Monitor] Reactor Protection System (RPS) scram setpoint. The RPS setpoint may result in violating the Minimum Critical Power Ratio (MCPR) safety limits during a thermal-hydraulic instability. "All OPRM channels have been declared inoperable. Technical Specifications 3.3.1.1 Action J requires an alternate method of detecting and suppressing thermal-hydraulic instabilities to be implemented within 12 hours. Alternate methods have been established, thus the Technical Specification has been satisfied. "This report is being made in accordance with 10CFR50.72(b)(3)(v), any event or condition that could have prevented the fulfillment of the safety function of a system needed to shut down the reactor and maintain it in a safe shutdown condition. "This report is also being made in accordance with 10CFR50.72(b)(3)(vi). Events covered in paragraph (b)(3)(v) of this section may include one or more procedural errors, equipment failures, and/or discovery of design, analysis, fabrication, construction, and/or procedural inadequacies." The NRC Resident Inspector has been notified of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-11-22
39387 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-11-21 19:55 | 2002-11-22 00:03 | 2002-11-22 | OFFSITE NOTIFICATION TO LAW ENFORCEMENT Notifications were made to the FBI and Linn County Sheriff by the licensee. There was no impact on plant operations. The licensee notified the NRC Resident Inspector. See the HOO Log for additional information. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-22
39386 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-09-27 10:42 | 2002-11-20 11:30 | 2002-11-20 | INVALID SPECIFIED SYSTEM ACTUATION WHILE PERFORMING MAINTENANCE "EVENT DESCRIPTION "This report is being made in accordance with §50.73 (a)(1), which states, in part, 'In the case of an invalid actuation reported under §50.73 (a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' These invalid actuations are being reported under §50.73 (a)(2)(iv)(A). NUREG-1022, Rev. 2, states that the report should provide the following information: "The specific train(s) and system(s) that were actuated "Whether each train actuation was complete or partial "Whether or not the system started and functioned successfully. "On September 27, 2002, at 1042 hours, during the performance of Maintenance Surveillance Test (OMST-RWCU41R), 'RWCU System Isolation Logic System Functional Test,' technician actions to perform positive identification of a logic relay prior to performing visual verification of contacts on that relay as specified within the surveillance procedure instructions, resulted in invalid actuations. The actuations included the Primary Containment Isolation system (PCIS) Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems) and Division A (i.e., inboard) PCIS Group 2 valves (i.e., the Drywell Equipment and Floor Drains). Both Standby Gas Treatment (SBGT) system trains A and B started and the Reactor Building ventilation system isolated. The actuations of PCIS Group 6 and Division A Group 2 valves and Reactor Building ventilation were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). By 1115 hours, the PCIS Group 2 and 6 isolation logic circuits were reset and associated valves reopened as required by plant condition, the Reactor Building ventilation system was returned to service, and both SBGT trains A and B were placed In standby. "Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in AR 72925." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-11-20
39385 | -1 | RESEARCH MEDICAL CENTER |  |  |  |  | 2002-10-11 | 2002-11-19 17:02 | 2002-11-20 | NOTIFICATION OF MEDICAL EVENT INVOLVING DIAGNOSTIC OVERDOSE OF IODINE-131 Research Medical Center reported that they had a diagnostic misadministration that occurred on 10/11/02. The event was reported after it was discovered by an auditor. The patient was administered 3.6 millicuries of I-131 instead of the prescribed dose of 3.0 millicuries. The iodine was being administered for a whole body scan for thyroid carcinoma. The patient and referring physician will be notified by the licensee. * * * RETRACTION ON 11/20/02 AT 1427 EST FROM STEPHEN SLACK TO HOWIE CROUCH * * * Licensee retracted event based on conversation with Region 3 NMSS. Basis for retraction is that patient does not have a thyroid. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2002-11-19
39384 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-11-19 10:30 | 2002-11-19 14:35 | 2002-11-19 | OFFSITE NOTIFICATION TO STATE AND LOCAL AUTHORITIES DUE TO OFFSITE EVENT As a precautionary measure, licensee notified federal, state and local agencies of an event that occurred in the local community. There was no impact on plant operations. Licensee informed NRC Resident Inspector. Refer to the HOO Log for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-19
39383 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-19 08:25 | 2002-11-19 09:57 | 2002-11-19 | OFFSITE NOTIFICATION TO LOCAL LAW ENFORCEMENT Notifications were made to the York County Police and State Wildlife Agency by the Licensee. Refer to the HOO Log for additional information. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-19
39382 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-11-18 09:20 | 2002-11-18 12:05 | 2002-11-18 | FITNESS FOR DUTY - CONTRACT FOREMAN FAILED RANDOM DRUG TEST A non-licensed, contract employee tested positive for drugs during a random drug test. The employee's access to the plant has been terminated. Contact the HOO for additional details. The licensee will notify the NRC Resident Inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2002-11-18
39381 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-11-17 13:06 | 2002-11-17 15:38 | 2002-12-13 | HPCI DECLARED INOPERABLE DURING QUARTERLY SURVEILLANCE TESTING "Unit 1 High Pressure Coolant Injection (HPCI) flow controller indicates 512 GPM with system in standby. Found when aligning system for surveillance. Cannot assure system will achieve rated flow automatically. HPCI is a single train system." HPCI was declared inoperable placing Unit 1 in a 14-day LCO A/S 3.5.1. The licensee intends to troubleshoot the problem including a fill/vent of the applicable flow transmitter. The licensee will inform the NRC resident inspector. * * * RETRACTION ON 12/13/02 AT 0958 EST FROM HARRY RUSSELL TO GERRY WAIG * * * The investigation of the problem noted in Report 39381 reported 11/17/2002 was determined to be setpoint drift of transmitter 1E41N008 and not an inoperable controller. Because this transmitter receives an input of differential pressure and the milliamp output is converted to flow using a square root function the amount of error in the flow rate measurement is not linear throughout the span of the transmitter. The plant has confirmed that the "as found" setpoint drift of this single flow measuring device would still have allowed the affected flow controller to perform its safety function and control flow negligibly lower than the design flowrate (4220 versus 4250 gpm), thereby continuing to allow HPCI to fulfill its safety function. It did not involve a failure of the flow measuring device and would therefore not be indicative of a generic failure problem with similar flow measuring devices on other systems. The HPCI system was operable in its "as found" condition. Based on the guidance in NUREG 1022, Revision 2, this setpoint drift of 1E41N008 is not reportable. Notified R2DO (Mike Ernstes). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-11-17
39380 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-11-16 20:42 | 2002-11-16 22:49 | 2002-11-19 | UNIT 1 EXPERIENCED A MANUAL REACTOR TRIP DUE TO A LOSS OF OPEN LOOP COOLING WATER "The South Texas Project makes the following 4 hour non-emergency report of a manual Reactor Protection System actuation per 10CFR50.72.b.2.ii. "At 20:42 on 11/16/02 Unit 1 reactor was manually tripped due to a loss of open loop cooling water. Reports indicated flooding in the circulating water intake structure due to a problem with circulating water pump #11, which caused the loss of open loop cooling." Operators received a loss of open loop cooling which supplies auxiliary cooling to the main generator. Per procedure, Unit 1 was manually tripped. Upon investigation, a 4-6 inch crack in circulating water pump #11 housing was discovered. A preliminary review indicates that water may have electrically shorted the three operating open loop cooling pumps which are also located in the intake structure. Unit 1 is currently stable in mode 3 with all auxiliary feedwater pumps in service. Vacuum in the main condenser is presently 27 inches with both circulating water pumps 13 and 14 operating. All rods fully inserted. Normal offsite power is available and no electrical buses were lost as a result of the flooding although electrical maintenance is investigating several electrical ground alarms. The licensee reviewed their Emergency Plan and determined that the criteria for declaration of an NOUE was not satisfied. The licensee notified the NRC resident inspector and does not plan on a press release at this time. * * * UPDATE ON 11/19/02 AT 1741 EST FROM GREG JANAK TO HOWIE CROUCH * * * This is a supplemental notification to EVENT # 39380 which was for a 4 hour non-emergency report of a manual Reactor Protection System Actuation. At 20:42 [CST] on 11/16/02 following the Unit 1 manual reactor trip, the Auxiliary Feedwater System actuated as expected on Steam Generator low-low water level. This is being reported under 10CFR50.72(b)(3)(iv)(A). Licensee reported that lowest steam generator water level observed was 17% on one steam generator. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-11-16
39379 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-11-16 09:20 | 2002-11-16 13:18 | 2002-11-16 | OFFSITE NOTIFICATION DUE TO SODIUM HYPOCHLORITE DISCHARGE TO LAKE MICHIGAN "Notification was made on 11/16/02 at 1150 to the National Response Center and at 1205 to the Michigan Dept. of Environmental Quality of a Sodium Hypochlorite discharge to Lake Michigan that exceeded the permitted concentration. On 11/16/02 at 0920, a chemist discovered and isolated a leak from the Hypochlorite facility. Circulating Water discharge Total Residual Chlorine (TRC) was measured at that time to be 0.3ppm. The concentration dropped below the permit limit of 0.038ppm at 0930. A recorded rise in TRC indicated that the leakage started at 0015. The Unit 1 TRC High Alarm did not function. The recorded TRC concentration ranged between 0.26 and 0.4ppm during the 9 hour period. Hypochlorite tank level change indicates that approximately 1080 gallons of 12% sodium hypochlorite solution was discharged from the leak to the forebay and out of the Circulating Water discharge to Lake Michigan. No environmental impact is expected from the discharge based on the chlorine concentration and release duration." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-16
39378 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-11-16 08:40 | 2002-11-16 10:31 | 2002-11-16 | SECURITY REPORT INVOLVING A LOST ACCESS BADGE Immediate compensatory measures taken upon discovery. Licensee notified the NRC resident inspector. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-11-16
39377 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-11-15 03:15 | 2002-11-15 23:44 | 2002-11-16 | 24-HOUR NRC BULLETIN 91-01 CRITICALITY CONTROL ISSUE AT PADUCAH "At 0315 on 11-15-02, the Plant Shift Superintendent (PSS) was notified that the pressure chart recorder for the C-333 'C' surge drum bank had failed, violating an SRI in NCSE.016. As a result of this failure, the shiftly pressure checks performed prior to this discovery were performed using a failed AQ-NCS pressure instrument and therefore were not valid. The purpose of this pressure check is to identify if wet air inleakage has begun on the surge drum bank. Following identification and remediation of failure, pressure checks were performed and it was determined that no wet air inleakage had occurred and double contingency was restored. "The NRC Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE: Although pressure readings were taken using a failed AQ-NCS pressure instrument, there are several important mitigating factors. First the integrity of the drum bank has been maintained. Second, the drum contained non-fissile material. Third, the UF6 has maintained in the gas phase. Because the drum contained non-fissile material, the NCS controls were not necessary to prevent a criticality from occurring. "POTENTIAL CRITICALITY PATHWAYS: These drums are used to store gases. Therefore, in order for a criticality to be possible, the drum would have to contain fissile UF6. Wet air would have to react with any UF6 in the drum. Wet air inleakage would have to occur over a long period of time in order to create a large mass of UO2F2 and then sufficiently moderate the material. "CONTROLLED PARAMETERS: Double contingency is maintained by implementation of two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: Drum bank contains gaseous UF6 enriched to [ ]. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on maintaining the integrity of the surge drum against wet air inleakage. This integrity is insured by an SRI for the unlikely breach of the surge drum system. Structural integrity of the drum is intact, therefore this SRI was maintained. "The second leg of double contingency is based performance of shiftly checks using an AQ-NCS instrument as an indication of wet air inleakage. The required checks were performed using a failed instrument. Since a failed instrument was used, the shiftly checks were invalid resulting in a loss of this control. Since there are two controls on one parameter, double contingency was not maintained. "Even though moderation control was maintained, double contingency is based on two controls on moderation. Therefore double contingency was not maintained. The drum contained a non-fissile material. It should be noted that a second parameter, assay (not controlled in the NCSA), was maintained since the drum bank contained non-fissile material. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS IMPLEMENTATION: Approximately one hour after discovery, AQ-NCS Instrumentation was connected to surge drum manifold and pressure was verified to less than NCS limit. Readings are being obtained from this instrumentation pending calibration of recorder. "DESCRIPTION OF OCCURRENCE: The pressure chart recorder for the C-333 'C' surge drum bank failed, violating an SRI in NCSE.016. As a result of this failure the shiftly pressure checks were performed using a failed AQ-NCS pressure instrument and therefore were not valid. The purpose of the pressure check is to identify if wet air inleakage has begun on the surge drum bank. "It is important to note that an AQ-NCS pressure instrument was subsequently connected to the system and pressure readings have been taken. The pressure readings indicate there has been no wet air inleakage. Double contingency has been restored since the ability to read pressure in the surge drum bank using a properly operating AQ-NCS pressure instrument has been restored "NUCLEAR CRITICALITY SAFETY CONTROLS INVOLVED AND THEIR IMPACT ON DOUBLE CONTINGENCY: Double contingency is maintained by implementing two controls on moderation. "The first leg of double contingency is based on maintaining the integrity of the surge drum system against wet air inleakage. This integrity is assured by an SRI for the unlikely breach of the surge drum system. Structural integrity of the drum is intact, therefore this SRI is maintained. "The second leg of double contingency is based on the performance of shiftly pressure checks using an AQ-NCS instrument as an indication of wet air inleakage. The required checks were performed using a failed instrument. Since a failed instrument was used, the shiftly checks were invalid resulting in a loss of this control. Since there are two controls on one parameter, double contingency was not maintained. "Even though moderation control was maintained; double contingency is based on two controls on moderation. Therefore double contingency was not maintained. The drum contained non-fissile material. It should be noted that a second parameter (not controlled in the NCSA) was maintained since the drum contained non-fissile material. "Potential Critical Pathways: These drums are used to store gases. Therefore, in order for a criticality to be possible, the drum would have to contain fissile UF6. Wet air would have to react with any UF6 in the drum. The leak would have to occur over a long period of time in order to create a large mass of UO2F2 and then sufficiently moderate the material. "Safety Significance: Although pressure readings were taken using a failed AQ-NCS pressure instrument, there are several important mitigating factors. First the integrity of the drum bank has been maintained. Second, the drum contained non-fissile material. Third, the uranium has been maintained in the gas phase. Because the drum contained non-fissile material, the NCS controls were not necessary to prevent a criticality from occurring." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-11-16
39376 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2002-11-15 20:20 | 2002-11-16 00:17 | 2002-11-16 | MANUAL REACTOR TRIP DUE TO HIGH FEEDWATER HEATER LEVEL "While reducing power for a planned refueling outage, at 2020, U1 reactor was manually tripped at 12% power due to Hi Hi Level in 13 'A' Feedwater heater. An existing problem with an extraction bellows in 13 'A' Feedwater heater had been previously identified and contingency plans were in place for monitoring the level during the load decrease. Levels were being monitored locally by Engineering and Operations during the load decrease in anticipation of level control problems. Control Room Operators made the decision as planned, to manually trip the reactor per annunciator response procedures, when it was determined that level in 13 'A' Feedwater heater could not be reduced. During performance of reactor trip recovery procedures, 11 Turbine Driven Auxiliary Feedwater Pump auto started when the running Main Feedwater Pump was secured. 11 Turbine Driven Aux Feedwater Pump was secured and Steam Generator levels are being maintained with 12 Motor Driven Aux Feedwater Pump." Additionally, the Licensee stated that all control rods properly inserted into the core and that all safety systems responded as required. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-16
39375 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2002-11-15 09:57 | 2002-11-15 11:49 | 2002-11-15 | UNIT 3 EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO A GENERATOR LOCKOUT "At 0957 EST, 345 Kv Breaker 3 failed open resulting in breakers 1, 5 and 6 opening. This electrically isolated Unit 3 resulting in the Main Generator primary and backup lockout relays (86P and 86 Bu) tripping. This resulted in an immediate reactor trip. All equipment operated as expected with the following exceptions: 1. 32 Source Range failed to come on scale as required 2. 34 Circulating Water Pump transferred to standby drive when normal drive tripped 3. 36 Circulating Water Pump tripped "The plant is stable in mode 3. Post trip review is in progress and will be completed prior to restart. The Public Service Commission has been notified." There was no maintenance or other activities in progress in the switchyard at the time the 345 Kv Breaker 3 catastrophically failed. Unit 3 is currently removing decay heat via the steam dump bypass to the main condenser. Both motor driven auxiliary feedwater pumps autostarted and are in-service. The steam generator atmospheric dumps may have lifted during the transient. There is no known primary-secondary tube leakage. The licensee notified the NRC resident inspector and plans on issuing a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-15
39374 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-14 | 2002-11-14 18:10 | 2002-11-14 | ELECTRICAL AUXILIARY BUILDING SUPPLY FAN TRIP "The Unit 2 Train C Electrical Auxiliary Building Supply Fan tripped on overload current shortly after starling on Nov 1 2002. The fan then tripped two more times on overload during subsequent troubleshooting. It was determined that the fan overloads for all 3 trains of EAB HVAC in both units were set low such that these fans may trip under reduced grid voltage conditions. All fan overloads were reset at a higher value to protect the motor and allow acceptable performance during the range of design grid voltage conditions. "The design safety function of these fans is to ensure the environmental requirements of vital equipment are satisfied under analyzed conditions including transients and postulated accidents. Since this condition existed prior to correcting the fan overload setpoint value, it was determined to be a condition that could have prevented fulfillment of a safety function. Therefore, this condition is reportable under 10CFR50.72(b)(3)(v). "This condition is susceptible during reduced grid voltage conditions. Further evaluation is in progress and expected to demonstrate that the reduced grid voltage condition occurs during a limited period of time over the operating cycle. Therefore, it is believed that the analysis will conclude that this event is of low safety significance." The NRC Resident Inspector was notified of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-11-14
39373 | 0 | RESEARCH MEDICAL CENTER |  |  |  |  | 2002-11-14 12:00 | 2002-11-14 15:40 | 2002-11-14 | LOST I-125 SOURCE, SLIGHTLY < .5 MILLICURIES, TO BE IMPLANTED IN A PATIENT Following prostate implantation procedure, radiograph showed fewer seeds than believed to have been implanted in the patient (1 seed short). Room, trash, and linens were all surveyed and nothing found. The authorized user believes that the lost seed may have migrated to another location in the patient's body, possibly carried off by one of the surrounding blood vessels. X-ray and CT scans of the immediate area of the implantation did not reveal location of the lost seed. No further scans of the patient are planned. Research Medical Center 2316 E. Meyer Blvd. Kansas City, MO 64132 Notified Bruce Burgess, R3DO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-11-14
39372 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-11-08 | 2002-11-14 15:00 | 2002-11-14 | AGREEMENT STATE REPORT INVOLVING MEDICAL MISADMINISTRATION On November 8, 2002, a patient at the Byrd Regional Hospital located in Leesville, LA, "received a 26 millicurie dose of Tc-99 Sestamibi instead of a 25 millicurie dose of Tc-99 MDP. This occurred [when] the technologist picked up the wrong syringe from the 'hot lab.' The technologist immediately notified the Radiation Safety Officer once he discovered what happened. There appears to be no adverse effects to the patient. The patient did receive the correct dose on November 12, 2002. The technologist will review the facilities procedures to prevent this type of incident from occurring again. The facility notified the doctor, patient, and the Louisiana Department of Environmental Quality (DEQ)." Louisiana event report ID No.: LA020015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-11-19
39371 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-11-13 15:00 | 2002-11-14 08:12 | 2002-11-14 | STOLEN SOIL MOISTURE DENSITY GAUGE The state licensee notified the State of Florida of a soil moisture density gauge that was stolen from the back of a pickup truck located at a temporary worksite. The gauge was last seen between 1500 and 1700 [EST]. The gauge which was a Troxler model 3430 serial # 24277 with activity of 8mCi [millicuries] of Cs-137 and 40 mCi [millicuries] of Am-241/Be had been chained to the truck. A police report was made and a reward is being offered and the state is investigating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-11-19
39370 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2002-11-14 07:45 | 2002-11-14 11:33 | 2002-11-14 | OFFSITE NOTIFICATION DUE TO SIREN MALFUNCTION "At 07:45 [CST] on 11/14/02, ANO Security received offsite calls from an off-duty security officer and the Pope County 911 Office regarding actuation of up to 3 emergency sirens in the Russellville area. The sirens silenced automatically approximately 3 minutes later after they timed out. Information provided by the duty Emergency Planner indicated the cause of the sirens was attributed to a power fluctuation in East Russellville area. The Arkansas Department of Health was contacted and is responding to determine if any corrective maintenance is required. The 911 Office is getting multiple calls from concerned citizens about the sirens. Local radio stations have been made aware of the event and are periodically broadcasting that there is nothing to worry about in an attempt to inform local residents." Licensee notified the NRC Resident Inspector. | 85 | 100 | 0 | 85 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-14
39369 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-11-14 04:19 | 2002-11-14 05:24 | 2002-11-14 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "The Moisture Separator drain tanks each provide a trip signal to the main turbine on a high level on 2 [of] 3 level switches. At 0419 [EST], 2 [of] 3 level switches indicated a high level in the 3A Moisture Separator Drain Tank Level, resulting in a MT [Main Turbine] trip and anticipatory RPS trip. Post-trip response was normal." All rods inserted into the core. No PORV's lifted. No ECCS actuation. The cause of the heater drain system upset is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-14
39368 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2002-11-13 04:58 | 2002-11-13 10:13 | 2002-11-13 | UNIT 1 EMERGENCY DIESEL GENERATOR AUTOSTARTED AND LOADED TO DIVISION 2 BUS. "At 0458 CST on 11/13/02, an undervoltage was detected on 4 KV ESS Div 2 Bus 14-1. The normal feed breaker to the bus auto tripped, the U-1 Emergency Diesel Generator auto started, and loaded to the bus. The preliminary investigation determined that work was being performed in a breaker cubicle adjacent to the bus auxiliary cubicle. Vibration from the work may have caused the bus potential fuse drawer to fall open, actuating the bus undervoltage relay. Normal power to the bus was restored at 0538 hours. A prompt investigation is in progress." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-11-13
39367 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-13 04:07 | 2002-11-13 04:53 | 2002-11-13 | MANUAL REACTOR TRIP FROM 21% POWER "Unit Two Reactor was at 21% power and Main Turbine roll up was in progress to synch to [the] grid after 2R9 refueling outage. Main feedwater was in service to all 4 steam generators. Steam generator #3 water level increased to the Hi-Hi P-14 setpoint which tripped the main turbine and main feedwater. AFW [auxiliary feedwater] actuated as required. The reactor was manually tripped. All rods fully inserted. The cause of the transient is being evaluated at this time. The reactor is stable in Mode 3 [Hot Standby]." Highest steam generator level attained was 88%. Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-13
39366 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2002-10-18 07:30 | 2002-11-12 16:30 | 2002-11-12 | KY AGREEMENT STATE REPORT INVOLVING AN OVER EXPOSURE OF A RADIOGRAPHER "This letter is notification of an overexposure incident that occurred on October 8, 2002 in Ghent, Kentucky. The licensee involved was Huntington Testing & Technology Inc.. Kentucky Radioactive Material License Number 201-551-05. The incident occurred while performing radiography at Kentucky Utilities. The radiography source was 103 Ci [Curies] of Ir-192 [Iridium], housed in a 660 B Camera, S/N B2954. The licensee's interpretation of the reporting criteria resulted in late notification thirty (30) days after the incident. That information was not only delayed, but also incomplete requiring further development before the State of Kentucky could forward this report. "At approximately 7:00 a.m., on October 18, 2002, when reeling in the radiography source after an exposure, it was not fully retracted, nor recognized for approximately three (3) minutes by the radiographer who had entered the area. Upon realization that the source was not fully retracted, the radiographer immediately left the area, extended the source and then retracted it to the housed position. The RSO [Radiation Safety Officer] was contacted and the radiographer removed from any radiological work. "The radiographer's dosimetry was immediately sent to Landauer for processing. The result of his exposure was 4.86 Rem whole body, in addition to his year-to-date exposure of 1.4 Rem, for total yearly whole body exposure of 6.26 Rem. These numbers appear to be close estimates, ending further evaluation of the radiographer's position in relation to the exposed source. Initial reports indicate a survey instrument failure, and failure of the radiographer to monitor the instrumentation and position indicator to ensure retraction of the radiography source. "Further evaluation of the cause of this incident and final dose estimates will be forwarded ending further investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | KY | OTH | AGR |  |  |  |  | 0 | 2002-11-15
39365 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2002-11-12 12:30 | 2002-11-12 16:12 | 2002-11-12 | UNINTENTIONAL RELEASE OF REVERSE OSMOSIS PRODUCT WATER "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On November 12, 2002, APS reported to the Arizona Department of Environmental Quality (ADEQ) the unintentional release of less than 500 gallons of reverse osmosis (RO) product water to sedimentation basin #2 that occurred on October 19, 2002 during a storm. RO product water is make-up water to the site drinking water system and meets all aquifer water quality standards. The Ground Water Quality Protection Permit does not authorize such a release. "This report to the ADEQ is in the form of a letter sent via certified mail. "No news release is anticipated." The licensee notified the resident inspector of this event. | 0 | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Startup | Power Operation | Power Operation | Startup | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-12
39364 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-11-12 09:48 | 2002-11-12 13:01 | 2002-11-12 | MANUAL REACTOR TRIP OF SALEM UNIT 1 DUE TO LOW S/G WATER LEVEL CAUSED BY FEED PUMP RUNBACK "This 4-hour notification is being made to report that Salem Unit 1 reactor was manually tripped at 0948 [EST] (RPS actuation). The trip was initiated due to low steam generator level (~16% narrow range). The low SG level appears to have been caused due to a runback of the 11 steam generator feed pump (SGFP) to idle. The cause of the runback has not been determined at this time. As a result of the runback, the level in steam generators dropped and the operators initiated a main turbine runback and tripped 11 SGFP manually. When operators observed the steam generators approaching the automatic reactor trip setpoint (14%), a manual reactor trip was initiated. "11, 12 & 13 auxiliary feed water pumps auto started after the trip due to valid steam generator low level, as expected on a unit trip. Main feedwater to the steam generators was isolated due to the "feed water interlock" which is expected on a normal trip. Additionally the ATWS mitigation system (AMSAC) did actuate post trip due to low steam generator levels but all auxiliary feed water pumps were already running prior to the actuation. "Salem Unit-1 is currently in MODE 3 [Hot Standby]. Reactor coolant system temperature is 547 [degrees] F with pressure at 2235 PSIG. Unit 1 has no shutdown tech. spec. action statements in effect. Major equipment out of service for planned maintenance includes the 16 service water pump which is expected back later today and Salem Unit-3 which is scheduled to be available on 11/15/02. "There were no personnel injuries or radiological occurrences associated with this event." Additionally, the licensee indicated that while the exact cause of the runback is not known, there was ongoing work on the limit switches for the 11 SGFP at the time of the runback, and there was some arcing in the switches. The licensee notified the resident inspector of this event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-12
39363 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2002-11-11 19:46 | 2002-11-11 22:08 | 2002-11-11 | MANUAL REACTOR TRIP DUE TO TURBINE MOTORING CONDITION ALARM "BVPS Unit 1 was performing a plant shutdown from full power for a scheduled maintenance outage. At 1946 hours [EST], the plant was at 53% power and the 'Turbine Motoring Condition' alarm was received. The condition will cause a Turbine Trip if it exists for thirty seconds. A Turbine Trip will cause an automatic Reactor Trip if greater than 49% reactor power. The Reactor was Manually tripped and the Emergency Operating Procedure E-O was implemented. The Emergency Operating Procedures were exited at 2034 hours [EST]. The Auxiliary Feed Water System actuated as expected. All other systems functioned as required. The cause of the Turbine Motoring alarm is under investigation. The plant is currently stable in Mode 3. Shutdown to Mode 5 will continue for the planned maintenance outage." The Licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 53 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-11
39362 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-11-11 05:15 | 2002-11-11 07:56 | 2002-11-11 | REACTOR SCRAM - RPS ACTUATION ON HIGH REACTOR PRESSURE VESSEL PRESSURE "At 05:15 [EST] all main steam isolation valves isolated unexpectedly. Reactor protection system actuation occurred due to high reactor pressure vessel pressure. All control rods fully inserted. Reactor pressure vessel pressure is being controlled using safety relief valves. Reactor pressure vessel water level is being controlled using reactor core isolation cooling system. Suppression pool temperature is being controlled using residual heat removal system in suppression pool cooling mode. "Cause of the main steam isolation valve isolation is unknown. Plant parameters are stable. [The licensee is] making plans to achieve cold shutdown conditions." The licensee reported that the reactor core isolation cooling system was manually initiated and that reactor vessel level decreased to level 3 during the reactor scram transient. Suppression pool temperature peaked at, and is being maintained steady at, 95 degrees Fahrenheit. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-11
39361 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2002-11-10 22:50 | 2002-11-11 04:28 | 2002-11-11 | AUTOMATIC REACTOR TRIP - RPS ACTUATION FROM LOW DNBR SIGNAL "The following event description is based on information currently available. If through subsequent reviews of this event, additional Information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 2250 Mountain Standard Time (MST) Palo Verde Nuclear Generating Station Unit 1 experienced an automatic reactor trip. The trip is believed to have been caused by a control element assembly deviation that resulted in the generation of a low departure from nucleate boiling (DNBR) trip signal. The cause of the CEA deviation is not known at this time. At the time of the trip the plant was being shutdown in a planned effort to effect repairs on the A train shutdown cooling suction line that had been experiencing high vibration. "All CEAs inserted into the core and safety systems actuated as expected. No other essential safety system actuations occurred and none were required. The plant did experience a loss of letdown flow when nuclear cooling water to the letdown heat exchanger was sensed as being low. Letdown has been restored. "The plant is currently operating in Mode 3, Hot Shutdown. Safety and non-safety related electrical buses remained energized during and following the reactor trip. The offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event." The licensee has notified the NRC Resident Inspector of this event. | 0 | 0 | 0 | 63 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-11
39360 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-08 06:33 | 2002-11-08 16:00 | 2002-11-08 | MANUAL PLANT SHUTDOWN AND MANUAL AFW INITIATION DUE TO LOSS OF CONDENSER VACUUM EVENT "High Ocean Swells and Debris results in a manual shutdown and a Valid Specific System Actuation: Manual Start of Auxiliary Feedwater (AFW) pumps. "On November 8, 2002, at 0633 PST, with Unit 2 operating at 20 percent reactor power, operators manually tripped the turbine due to indications of high differential pressure on the traveling screens at the intake structure. Operators also manually tripped both circulating water pumps resulting in a loss of condenser. In accordance with the abnormal procedure for loss of condenser, operators manually shutdown the reactor and started 2 motor driven AFW pumps. The manual actuation of AFW pumps is being conservatively reported as a specific system actuation per 10 CFR 50.72(b)(3)(iv). "Station loads transferred from auxiliary power to startup power. During the transfer, several systems automatically start standby trains, including 2 containment fan cooler units (CFCUs) and the standby auxiliary saltwater (ASW) pump as designed. No emergency diesel generators started. No PORVs or safety valves lifted. During this event, all safety systems functioned as designed. "On November 7, 2002, operators had ramped Unit 2 power from 100 percent to 20 percent power in anticipation of a significant storm and associated high swells and ocean debris. The possibility of losing the circulating water pumps as a result of the storm was anticipated, and procedures specify maintaining reactor power at 20 percent during these conditions. Unit 2 is currently stable in Mode 3 with heat being removed by AFW and atmospheric steam dumps. "Unit 1 was unaffected by these events due to being in Mode 5 for a generator rotor replacement." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-11-08
39359 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-08 13:10 | 2002-11-08 14:50 | 2002-11-08 | FITNESS FOR DUTY A contract supervisor tested positive for drugs during a random test. The employee's access to the plant has been terminated. Refer to HOO log for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2002-11-12
39358 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2002-11-08 09:05 | 2002-11-08 12:30 | 2002-11-08 | TEAR IN CONTROL ROOM RETURN AIR LINE JOINT AT GINNA "At 0905 on 11/08/02 a tear was discovered in a flexible suction joint to the Control Room Return Air Fan. This tear could allow unisolable outside air to be drawn into the Control Room. A temporary repair was affected at 0945 restoring the integrity of the Control Room ventilation system. An investigation will be conducted to determine the cause of the tear. The NRC inspector was informed." Additionally, the licensee indicated the tear was 6 inches in length. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-11-08
39357 | 0 | POWER RESOURCES |  |  |  |  | 2002-11-07 15:00 | 2002-11-08 11:02 | 2002-11-08 | LICENSEE REPORTED THAT A MONITORING WELL HAS BEEN PLACED ON EXCURSION STATUS. THE LICENSEE REPORTED THAT MONITORING WELL M42 (IN "B" WELL FIELD) FOR AN IN-SITU URANIUM MINE HAS BEEN PLACED IN "EXCURSION STATUS" DUE TO HIGH BICARBONATE AND CONDUCTIVITY MEASUREMENTS. ON 11/07/02 THE WELL WAS SAMPLED WITH THE FOLLOWING RESULTS: CHLORIDES 11 milligram/liter BICARBONATE 375 milligram/liter CONDUCTIVITY 751 micromho/centimeter THE MONITORING LIMITS ARE: CHLORIDES 11 milligram/liter BICARBONATE 281 milligram/liter CONDUCTIVITY 735 micromho/centimeter THE LICENSEE PLANS TO CONTACT THE WYOMING DEPARTMENT OF ENVIRONMENTAL QUALITY, LAND QUALITY DIVISION AND NRC REGION IV REGARDING THIS EVENT. * * * UPDATE AT 1340 ON 11/08/02 BY FUEGEL TO GOULD * * * It was determined that no other agencies should be notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | WY | MAT | [5 empty] | 0 | 2002-11-08
39356 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-11-07 | 2002-11-08 09:41 | 2002-11-08 | AGREEMENT STATE REPORT - LOST OR STOLEN AM-241 SOURCE "Licensee reported at 1530 [EST] that source could not be found during current inventory. Last inventory was performed on 14 February. Licensee is conducting an investigation." The lost or stolen material is a sealed 4 microcurie Am - 241 source used for military sighting application. The State of Florida Bureau of Radiation Control radiological incident number is FL02-172. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-11-13
39355 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-01 17:27 | 2002-11-07 17:16 | 2002-11-07 | INVALID SPECIFIED SYSTEM ACTUATION DUE TO POST MAINTENANCE TESTING "Per 10CFR50.73(a)(1), we make the following report under 10CFR50.73(a)(2)(iv)(A) "At 1727 on 11/01/02, while performing Solid State Protection System Post-Modification Testing (PMT), a fault in Logic Train R resulted in an invalid Train A Safety Injection (SI) actuation signal, Containment Ventilation Isolation (CVI), and Containment Phase A isolation. "We provide the following information: (a) The specific train and systems that were actuated: Train 'A' Safety Injection signal resulted in actuation of ESF Diesel Generator 21, Containment Isolation Phase 'A', Containment Ventilation Isolation and other designated equipment designed to start on a safety injection signal. (b) Whether each train actuation was complete or partial: This actuation signal only affected Train 'A' and was complete. (c) Whether or not the system started and functioned successfully: All affected systems functioned properly." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling Shutdown; FMode2: Refueling Shutdown | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-11-07
39354 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2002-11-07 14:39 | 2002-11-07 16:58 | 2002-11-07 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "Reactor trip believed to be the result of 500KV switchyard maintenance. One Main generator output breaker was open for maintenance prior to the trip, and when the second output breaker opened, the main turbine tripped causing the plant to trip. Emergency Operating Procedure 2, Vital Systems Status Verification has been completed satisfactorily. Emergency Operating Procedure 10, Post Trip Stabilization, has also been completed satisfactorily. The root cause of the trip is unknown at this time." All control rods fully inserted. Steam generator reliefs lifted to relieve steam pressure, and reclosed. No pressure operated relief valve lifted. Licensee notified NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-07
39353 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-11-07 12:47 | 2002-11-07 14:42 | 2002-11-07 | AUTOMATIC REACTOR TRIP ON OVER TEMPERATURE DELTA-TEMPERATURE "Unit 1 automatically tripped on over-temperature delta-temperature reactor trip signal at 1247. All control rods fully inserted. The 1A auxiliary feedwater pump was manually started to supply the steam generator, and the 1B auxiliary feedwater pump started automatically on Low-2 Steam generator level [18%]. The cause of the transient was apparently a turbine malfunction. Pressurizer power operated relief valves opened automatically to lower reactor coolant pressure, and were successfully reclosed. Steam generator relief valves also opened to lower steam pressure, and reclosed. The plant has been stabilized at normal zero power temperature and pressure per emergency procedures." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-11-07
39352 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-11-06 04:30 | 2002-11-07 12:50 | 2002-11-13 | AGREEMENT STATE REPORT INVOLVING STOLEN MOISTURE DENSITY GAUGE The licensee reported at 1115 PST on 7/6/02 that a CPN Model MC3 moisture density gauge was stolen from the back of the licensee's pickup truck on 7/06/02 sometime between 0430 and 0530 PST in the city of Orange, CA . The gauge serial number is not currently available. Gauge contains nominally 10 millicuries Cs-137 and 30 millicuries Am-241/Be. The gauge was chained and locked in the back of the pickup and the chain was found cut. Local law enforcement responded. The licensee plans on issuing a press release and a reward for the return of the gauge. ****UPDATE ON 11/13/02 AT 14:10 FROM LAURA**** The above text listed the incorrect date for the event. The event occurred on 11/6/02 and NOT 7/6/02. Notified DIRO (McGinty) and R4DO (Cain). * UPDATE ON 11/25/02 AT 1216 EST VIA E-MAIL FROM ROBERT GREGER TO HOWIE CROUCH * * * During police investigation by Anaheim Police, the gauge was recovered intact and untampered. Notified NMSS (Tom Essig) and R1DO (Linda Howell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-11-12
39351 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-11-07 09:30 | 2002-11-07 10:22 | 2002-11-07 | POSITIVE INDICATION OF COLIFORM IN WATER SAMPLING Water sampling taken from the office cleaning facility indicated positive on total coliform bacteria. Fecal coliform results were negative. Chlorine residuals established at the time of the sample have been reverified and the licensee believes it was in the sample analysis. Back-up sampling will be taken tomorrow, 11/8/02, and send for sampling verification. The Licensee notified the Maryland Department of the Environment and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-07
39350 | 0 | WAYNE STATE UNIVERSITY |  |  |  |  | 2002-11-06 09:00 | 2002-11-07 08:17 | 2002-11-07 | PHOSPHORUS 32 SOURCES INADVERTENTLY SENT TO LANDFILL WITH TRASH On 11/06/02 at approximately 0600 EDT a Wayne State University custodian mistakenly picked up two shielded 250 microcurie P 32 sources and disposed of them as trash. The trash and sources were subsequently disposed of at a landfill site. The university Office of Environmental Health and Safety contacted the landfill operator to try to locate the sources but was told that the pit in which it would have been placed had been covered over. The sources were used by the university for bio-med research. The licensee plans to notify the State of Michigan of this event. * * * * UPDATE FROM MARY SVOBODA TO MIKE RIPLEY 1533 EST 11/7/02 * * * On 11/07/02 at 1533 EST, the licensee updated the initial information stating that the radioactive material was in the form of two vials of P 32 rather than sealed sources. In addition, the material was placed in the dumpster between 0200 and 0700 EST on 11/06/02, and the landfill site is located in Riverview, MI. The licensee is forwarding a written report to Region 3. Notified NMSS (D. Broaddus) and R3DO (M. Phillips). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-11-07
39349 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2002-11-01 | 2002-11-06 15:50 | 2002-11-06 | AGREEMENT STATE REPORT INVOLVING MEDICAL MISADMINISTRATION "On 11/1 /2002, the Radiation Oncologist was administering a EndoVascular brachytherapy procedure to the patient using a Novoste Beta Cath source. It was noticed on the image monitor by the Radiation Oncologist and the Cardiologist that the distal marker began to move, raising the possibility of source movement despite adequate pressure (as noted by the amber lights). A decision was made by the Radiation Oncologist and the Cardiologist to remove the entire system immediately. The catheter system with its transfer device attached was removed and returned to the 'bailout box'. The patient was surveyed right away and found to have no radioactivity. The transfer device and catheter were surveyed. The sources were found within the system. The sources were successfully returned to the transfer device without any problem. The transfer device was visually checked and surveyed again. The activity remained the same as in the pre-procedure survey. Since the source could not be safely extended again, the treatment was discontinued. 71% of the prescribed dose was delivered. The patient received 29% less dose than prescribed: No increase in complications expected. While one cannot be fully sure of the reduction in control rates, the dose delivered appears to be within the range (800 cGy to 3000 cGy in the Scripps and Gamma 1 trials and 13% less than the WRIST trial) to benefit in preventing restenosis. The patient and the referring physician were informed was informed of this event. "Novoste Model: TDA 0040 transfer device; Ser # 83178 Source strength: Source train Ser # 474/01; Source Strength 1.92 GBq Source length: 40 mm Diagnosis: Coronary artery restenosis Prescribed treatment: 1840 cGy at 2 mm Treatment site and length: RCA; 40 mm Present during procedure: Cardiologist, Radiation Oncologist, Physicist, and Radiation Therapy Physicist ." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2002-11-11
39348 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-11-06 14:40 | 2002-11-06 14:59 | 2002-11-06 | UNUSUAL EVENT DECLARED DUE TO OFF GAS EXPLOSION IN TURBINE BUILDING The Unusual Event was declared based on EAL P2, unanticipated explosion on site, due to an explosion in an Off Gas System line in the Turbine Building. The licensee reports no known damage to systems or equipment, no radiological release, and that the plant remains in stable operation at full power. The cause of the explosion is believed to be from a spark observed in the area of instrumentation attached to the Off Gas System in the Mechanical Vacuum Pump Room within the Turbine Building. The instrumentation was being used to conduct condenser air in-leakage testing at the time of the explosion. The licensee is unsure at this time of the extent of actions which must be completed to terminate the unusual event, however a detail plant walkdown will be conducted. The licensee notified the NJ State Police and the NRC Resident Inspector. ***UPDATE FRANK CIGANIK TO MIKE NORRIS 11/6/02 1859 EST*** "Oyster Creek was in the process of setting up test equipment to be used for the identification of abnormal air leakage into the main condensers. When the test rig was placed in service, a spark was generated which ignited the combustible gas in the off gas exit piping. The off gas system isolated as designed. The test equipment was removed from service, and per the plant abnormal procedure, the isolation was reset. No damage to off gas piping was identified. "Currently the plant is in a stable condition and no emergency action level criteria apply. "Oyster Creek has terminated from the UNUSUAL EVENT as of 1855 hrs." The Licensee as notified the NRC Resident Inspector. Notified R1DO (Doerflein), NRR EO (Ruland), IRO (Wessman) and FEMA (Stiendurf) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-11-06
39347 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2002-11-06 | 2002-11-06 10:39 | 2002-11-06 | OFFSITE NOTIFICATION - UNINTENTIONAL RELEASE OF CIRCULATING WATER TO SEDIMENTATION BASIN "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of I0CFR50.73. "On November 6, 2002, APS reported to the Arizona Department of Environmental Quality (ADEQ) the unintentional release of 4000 gallons of circulating water to sedimentation basin #2 that occurred on October 30, 2002. The Ground Water Quality Protection Permit does not authorize such a release. The five day follow-up written report was made to the State of Arizona. "A courtesy telephone call was made to the ADEQ on the afternoon of November 1, 2002. No news release is anticipated. The licensee has notified the NRC Resident Inspector. | 69 | 100 | 100 | 69 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-11-06
39346 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-09-30 | 2002-11-06 00:25 | 2002-11-06 | TWO SEALED CESIUM SOURCES INADVERTENTLY SHIPPED WITH VEHICLES " SAIC [Science Applications International Corp.] sold two Mobile VACIS trucks to the Department of the Army-SECOM. The Mobile Vehicle and Cargo Inspection System (VACIS) is a truck-mounted gamma-ray imaging system designed to non-intrusively inspect the contents of trucks, containers, cargo and passenger vehicles for explosive devices and/or contraband. "Each Mobile VACIS truck contains one 1.6 Ci Cs-137 sealed source. The trucks were to be shipped first, then the Cs-137 sealed sources were to be shipped later. However on September 30, 2002, the trucks were shipped with the sealed sources inside by mistake without the proper DOT paperwork and marking/labeling. This mistake was not discovered until November 5, 2002, when SAIC prepared to ship the sources. They then discovered that the sources were inside the trucks that had been shipped previously. The trucks were shipped first to Houston by ground and then overseas by ocean carrier. The two shipping companies involved are US Freight and Saudi Arabia Shipping. SAIC has faxed all DOT shipping information to the carrier. The shipment is not due to arrive in port until November 15, 2002. The company plans to have a representative meet the shipment when it arrives at port. "According to SAIC, the sources are in type A containers that are locked. SAIC has the key in their possession- without this key the sources cannot be removed. The highest reading on the truck found during the package survey prior to shipment was 50 microR/hour." The State of California has notified NRC Region 4 (Linda McLean) of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-11-08
39345 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-11-05 11:10 | 2002-11-05 15:19 | 2002-11-11 | DEFECTIVE STEAM GENERATOR TUBES DISCOVERED DURING INSPECTION "During refueling outage RF12, interim results of "A" Steam Generator tube inspections indicate 62 tubes out of 5431 tubes (i.e.,> 1%) have been found to be defective. This steam generator tube inspection result for the "A" Steam Generator is classified as category C-3 in accordance with Technical Specification 5.5.9, Table 5.5.9-2. All defective tubes will be plugged before the steam generator is returned to service. There were no adverse safety consequences or implications as a result of this event. This event did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 11/11/02 @ 1653 BY HENSON TO GOULD * * * "This initial notification was reported under 10CFR50.72(b)(3)(ii)(A) as a Degraded Condition, however, under NUREG 1022, section 3.2.4, discussion (A) 3, the present C-3 classification of the 'A' Steam Generator tubes does not meet the listed criteria for serious steam generator tube degradation. This notification is to amend initial notification, EN #39345, to reflect that this report was made per requirements of Technical Specification 5.5.9, Table 5.5.9-2 only. This C-3 condition does not meet the criteria for serious steam generator tube degradation and thus is not a degraded or unanalyzed condition." The Licensee will notify the NRC Resident Inspector. Notified R4DO (Pruett). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-11-05
39344 | 0 | GRAND VIEW HOSPITAL |  |  |  |  | 2002-11-04 11:00 | 2002-11-05 10:33 | 2002-11-05 | REPORTED LOSS OF I-125 SEED FOLLOWING IMPLANTATION On 11/4/2002 at approximately 1100 hours, following a procedure to implant I-125 seeds into the prostate of a patient, the licensee counted only 57 of planned 58 seeds implanted. Survey of area, surrounding materials, and counting room did not turn up any indications of the lost seed. The unaccounted for seed contains 382 microcuries. Licensee contacted Region I. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-11-05
39343 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2002-11-04 16:44 | 2002-11-04 22:15 | 2002-11-04 | MANUAL REACTOR TRIP DUE TO DECREASING PRIMARY SYSTEM PRESSURE Licensee reported that PZR spray valve ZPV-100A failed to 46.5% open and mechanically bound. Unsuccessful attempts were made to close the valve manually (from controller) and by isolating instrument air to containment. RCS pressure slowly decreased and a manual reactor trip (all rods fully inserted) was performed at 2005 psig . RCS pressure continued to drop to a low of approximately 1840 psig (1740 psig is automatic trip setpoint). Two reactor coolant pumps were secured in accordance with Emergency Operating Instructions and RCS pressure recovered to 2250 psig (NOP) over a 1.5 hour time frame. A containment entry was performed and the spray valve shut while it was being isolated by manually shutting it's associated isolation valves. Decay heat is being removed by dumping steam to condenser and there is no indication of primary to secondary leakage. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-11-04
39342 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-11-04 11:08 | 2002-11-04 11:48 | 2002-11-04 | UNUSUAL EVENT DECLARED DUE TO PRIMARY SYSTEM UNIDENTIFIED LEAKAGE GREATER THAN 10 GPM "Primary system unidentified leakage >10 gpm. Leakage occurred during planned maintenance activity on a NV [Chemical volume and Control System] system demineralizer. The leakage has been isolated at 1108. We are running an NC [primary] system leakage calculation at present prior to terminating the event. All primary system parameters were normal during the event" The leakage was 11 gpm and was indicated by VCT level dropping. The NRC Resident Inspector has been notified. * * * * UPDATE TO MIKE RIPLEY AT 1315 EST 11/04/02 * * * * At 1315 EST 11/04/02 Licensee reported termination of the unusual event at 1302 EST based on recalculation of primary system leakage: Total leakage = 0.094 gpm. Identified leakage = 0.017 gpm. Unidentified leakage = 0.077 gpm. Leakage was caused by leak by through isolation valves onto the floor and down a floor drain in the auxiliary building. Notified NRR EO (Reis), R2DO (Landis), IRO (Wessman), AND FEMA (Zapata). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-11-04
39341 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-11-01 14:45 | 2002-11-02 12:10 | 2002-11-02 | AGREEMENT STATE REPORT INVOLVING UNACCOUNTED FOR Po-210 SOURCE Licensee reported that a 1.5 millicurie Po-210 source is unaccounted for. The source is believed to be at the facility and a search is being performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-11-06
39340 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2002-11-02 03:16 | 2002-11-02 08:38 | 2002-11-02 | UNIT 2 REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL The San Onofre Unit 2 reactor tripped from full power on reactor protection system (RPS) actuation due to low steam generator (SG) 2E089 water level. The low SG water level was caused by the momentary closure of main feedwater regulator valve 2-FV-1111. The momentary valve closure caused the #1 SG water level to drop to the ESFAS/reactor trip setpoint of 21% (NR) resulting in RPS actuation, automatic auxiliary feedwater system initiation, and the trip of both main feedwater pumps. The auxiliary feedwater system was used to restore and maintain SG water levels after the reactor trip. All control rods fully inserted into the reactor and all plant systems responded to the event as expected. The plant is currently stable in hot standby conditions. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2002-11-02
39339 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-11-01 16:41 | 2002-11-01 22:12 | 2002-11-01 | HPCI INOPERABLE DUE TO INDICATED HIGH DIFFERENTIAL PRESSURE ALARM "On November 1, 2002 at 16:41 hours, a High Pressure Coolant Injection (HPCI) Steam Line Break high differential pressure alarm was received, which caused a HPCI Steam Isolation System 'A' signal, closure of the 2-E41-F003, HPCI Steam Supply Outboard Isolation Valve, and a closure signal to the normally closed 2-E41-F041, Torus Suction Valve. Temperature indications, inspection of associated trip instrumentation, and local inspection confirmed that all temperatures for the HPCI system were normal and no steam or line break was present. The high differential pressure alarm cleared at 16:49 hours. "Investigation is currently in progress and drifting of a differential pressure transmitter is suspected. "This event is reportable in accordance with 10CFR50.72(b)(3)(v)(D) since the HPCI system is needed to mitigate the consequences of an accident. "INITIAL SAFETY SIGNIFICANCE EVALUATION "The Reactor Core Isolation Cooling (RCIC) system is operable and Unit 2 has entered the Technical Specification action statement to restore the HPCI system in 14 days. Therefore, this event poses minimal safety significance. "CORRECTIVE ACTIONS "Initial actions were taken to verify no evidence of a steam leak using available indications and an inspection of HPCI steam lines, Further investigation is in progress on the associated differential pressure transmitter." The Licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-11-01
39338 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-11-01 11:58 | 2002-11-01 18:26 | 2002-11-01 | UNANALYZED CONDITION FOR PRESSURIZER LEVEL TRANSMITTER CABLE SEPARATION "During an internal (Self Assessment) Fire Protection Program Review, documentation discrepancies were found related to Pressurizer Level Transmitters LT-101Y and LT-101X (Normal Operating Level Indications) and LT-106 (Cold Calibrated Shutdown Indication). The information did not provide adequate documentation to ensure Appendix R cable separation was met in Containment. A field verification was performed and confirmed that Appendix R cable separation for the above mentioned Pressurizer Level transmitters may not exist. The Plant engineering Department is continuing to evaluate the situation and a Plant Review Committee (PRC) meeting is planned for later this evening to review Engineering's conclusions." "Currently the affected transmitters are operable and this issue relates to Appendix R Licensing Documentation only." The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-11-01
39337 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2002-11-01 15:08 | 2002-11-01 17:52 | 2002-11-01 | DEGRADED PLANT CONDITION DUE TO LOSS OF SAFETY RELATED OFFSITE POWER "This report is being filed per 10CFR50.72.b.3. This is an eight hour notification of a degraded plant condition based on a loss of safety related offsite power. "At 1508 hours, Central New York Power Control notified Nine Mile Point Unit 1 control room staff that a Low Contingency Voltage alarm had been received. Per plant procedures NMP1 entered a 24-hour shutdown Limiting Condition of Operation per Technical Specification 3.6.3. Power Control's Load Flow Computer program that monitors the 115 kV grid for NMP1, determined that there is insufficient voltage (based on the grid loading) to supply NMP1 ECCS loads during a LOCA. "NMP1 has started its DIV 1 emergency diesel generator (EDG). DIV 1 ECCS bus is currently being supplied by the DIV 1 EDG. Plant operators are currently starting the DIV 2 EDG; it will supply DIV 2 ECCS bus. "Power is still available for other non-safety related buses from offsite, however for safety related buses it is considered degraded." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-11-01
39336 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2002-11-01 11:00 | 2002-11-01 16:11 | 2002-11-01 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "A Troxler Electronic Laboratories, Inc. Model 3411B, portable gauging device [serial number 7940, containing approximately 8.0 millicuries of Cs-137 (source serial number CC-571), and approximately 40 millicuries of Am-241/Be (source serial number CAA-4262)] was stolen from the bed of a pickup truck while the licensee's employee went into [ ] Food & Drug to purchase some batteries. The gauging device's source rod was locked in the safe shielded position, the gauging device's transport case was locked, and the transportation case was chained to the licensee's pickup truck. Bolt cutters were used to remove the gauging device from the pickup truck." The Licensee notified the West Valley City Police. The state of Utah has issued a press release. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2002-11-06
39335 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-10-31 | 2002-10-31 16:45 | 2002-11-05 | AGREEMENT STATE REPORT INVOLVING A MEDICAL EVENT "Manufacturer's employee changed the Gamma Knife's printer on 2 Aug 02 and during the process the calibration parameters for the Gamma Knife instrument were reset from 3.52 c/gray (on 6-02) to 3.5 c/gray (on 1-99). Licensee was not aware of the change. Ten patients were treated with this instrument from 26 Aug-30 Oct 02. The area treated was the brain and the overexposure was as much as 60% above the prescribed dose of 12-24 grays. The physicians and patients involved are being notified. The error was discovered during a recalibration on 10-30-02. The instrument has been removed from service. Florida is investigating." The isotope used by the Gamma Knife Model C S/N 4189C is Co-60 (Activity 5.72 Ci). *** UPDATE AT 0800 11/5/2002 FROM CHARLIE ADAMS TO ERIC THOMAS *** The above Co-60 activity was listed incorrectly in the original report. The correct value is 5720 Ci. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-11-05
39334 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-10-30 | 2002-10-31 12:10 | 2002-11-04 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE Licensee reported that a Troxler gauge, was stolen from the open bed of a pickup truck parked in front of a private residence, sometime during the night of 10/30/02. The gauge, model #3440 serial #16911, contained approximately 44 millicuries of Am-241:Be, and approximately 9 millicuries of Cs-137. The gauge was locked and the chain was cut. The licensee will be notifying the Denver police department of the theft. * * * * * UPDATE 1800 EST 11/4/2002 TO MIKE RIPLEY FROM COLORADO DEPARTMENT OF PUBLIC HEALTH AND ENVIRONMENT (received via fax) * * * * "The police recovered a Troxler moisture-density gauge that was reported stolen last week. Kumar and Associates, a Colorado licensee, reported the gauge stolen on 10/31/02 (sec preliminary report 39334). Later that same night, police were called to a Denver location because of a suspicious package that was left by a dumpster. The package was labeled with, a radioactive sticker. The Denver Fire Department's Haz-mat team checked the package and removed it to a safe storage location. Today, 11/4/02, the package was positively identified as the stolen gauge, and returned to the licensee. The licensee reported that the gauge was intact and that the sources appeared undisturbed." Notified R4 DO (C. Marschall) and NMSS EO (P. Holahan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-11-05
39333 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2002-10-31 05:45 | 2002-10-31 11:04 | 2002-10-31 | UNIT 1 MANUALLY TRIPPED DUE TO HIGH SULFATE CONCENTRATIONS IN THE STEAM GENERATORS "On October 31 2002, at approximately 05:45 MST Palo Verde Unit 1 experienced a manual reactor trip from approximately 19% rated thermal power due to high sulfate concentrations in the steam generators. Unit 1 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee stated that the trip was initiated at the recommendation of the Chemistry Manager. The licensee continues to investigate the reason for the high sulfate concentration and an estimated restart date was not given. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-10-31
39332 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-10-30 14:20 | 2002-10-30 17:34 | 2002-10-30 | OFFSITE NOTIFICATION Offsite notification was made to the Pennsylvania Department of Environmental Resources due to approximately 150 gallons of fuel oil spilled on-site. The fuel oil spill was a result of overflow/overfill of 2-2 Emergency Diesel Generator underground storage tank. Fuel oil was contained on site and no oil was discharged to the Ohio River. Cleanup of the fuel is expected to be completed within 24 hours. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-30
39330 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-10-29 10:25 | 2002-10-29 18:11 | 2002-10-29 | AUXILIARY FEEDWATER SYSTEM (AFWS) DECLARED INOPERABLE "At 10:27 CST, the auxiliary feedwater system (AFWS) for Point Beach Nuclear Plant, Units 1 and 2, was declared inoperable due to the potential for fouling of the minimum recirculation orifices for each of the four AFW pumps. The mechanism identified was the potential for foreign materials in the AFW fluid restricting adequate flow through the flow control orifices in the recirculation line. Under such conditions, it is possible that if the discharge valves for the AFW pumps are throttled, adequate flow may be unavailable through the recirculation line and pump damage could occur. "The potential for this common failure mode was realized while conducting an extent-of-condition evaluation for reduced recirculation flow observed during surveillance testing of the P-38A motor driven AFW pump on October 24, 2002. The flow was less than expected but above the minimum required for pump operability. Upon disassembly of the P-38A flow orifice we discovered a build up of corrosion products in the orifice. "Both units entered Tech Spec [Action Condition] 3.7.5.E and required action 3.7.5.E.1 which requires immediate steps to restore an AFWS to operable status. Immediate corrective actions have consisted of briefing the on-shift crew (on-coming crews will also be briefed) of the potential consequences of restricted recirculation flow and directing the operators, in the event of a situation requiring AFW flow, to secure a running AFW pump if the pump discharge falls below minimum flow requirements. In addition, information tags have been attached by the AFW pump flow indicators on the main control boards to convey that information. These action were completed at 1305 CST. At that time, with these administrative controls in place, we declared the AFWS back in service. Longer term corrective actions, including permanent procedure changes, are being evaluated." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-29
39329 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2002-10-28 15:00 | 2002-10-29 15:19 | 2002-10-29 | FOLLOW-UP PATIENT GIVEN INCORRECT PREP DRUG Woodward Regional Hospital was doing an Iodine-131 follow-up scan for residual Thyroid on cancer patient. A nurse injected the patient with the incorrect prep drug, non radioactive drug, prior to the patient being administered 4 millicuries of Iodine-131. The caller believes that the patient was given the incorrect prep drug on October 28, 2002 and today, October 29, 2002, was administered the 4 millicuries of Iodine-131 before given the scan. After the scan was performed it was discovered that the patient was given the incorrect prep drug for the scan. The State of Oklahoma is investigating this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2002-11-01
39328 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-10-28 06:30 | 2002-10-29 13:44 | 2002-10-29 | AGREEMENT STATE REPORT - STOLEN NUCLEAR DENSITY GAUGE "A company technician returned to the office at 6:30 a.m. after an extended job in Brundidge, Alabama. He was in the office to return to operations at the Dallas, office and was beginning to unload his truck and return his equipment to the office. He unlocked his gauge (Troxler Model 3411B, Serial # 6819) and placed it on the tailgate of the truck. He walked into the office to get a chain and lock to secure the gauge in the company storage cabinet. He walked back to the truck to get the gauge and discovered that the gauge and the concrete air meter were missing from the truck. He contacted the dispatcher, who had not yet arrived at the office, to notify the company RSO. Notifications were made to the Bureau of Radiation Control, the Dallas Police Department (Police Report # 823204L - a copy has not been received yet), and three local nuclear gauge repair centers (Richardson & Associated, Component Sales - Houston, and Troxler Labs, Arlington). The gauge has not been located. Source Serial #'s are: Cs-137, 10 millicuries, S/N CC3975, and AmBE-241, 40 millicuries, S/N CCA3132. The BRC is still investigating the incident." "Company truck with Logo, Texas Licensee # 5ND G59" "Texas Incident No.: I-7945" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-11-01
39327 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-10-22 | 2002-10-29 13:04 | 2002-10-29 | AGREEMENT STATE REPORT INVOLVING A MEDICAL EVENT "On 10-22-02 the patient was undergoing the first of six fraction therapy using a HDR source in the cervix. The source was misplaced by approximately 2 centimeters. The dose received was 800 Rem instead of the prescribed dose of 500 Rem. On 10-28-02 the error was discovered during planning for the second fraction, and it was reported the same day. The patient and physician have been notified. No long term health effect is expected and the prescribed treatment is continuing. Licensee will submit a letter of explanation within 15 days. Florida is continuing it's investigation." Florida Incident No. FL02-161 Isotope used was 9.961 Curies Ir-192. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-11-01
39326 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2002-10-28 23:15 | 2002-10-29 03:26 | 2002-11-21 | DAMAGED CONTROL ROOM DOOR SEAL "Declared both trains of Control Room Emergency Recirc inoperable, entered Tech Spec 3.0.3 from Tech Spec 3.7.3 on loss of Control Room boundary. A damaged door seal leading from the Control Complex to the Service building caused the loss of the Control room boundary. Door was closed and temporarily sealed per SOI-M25/26. Exited Tech Spec 3.0.3 at 00:15 on 10/29/02." The NRC Resident Inspector was notified. **** RETRACTION on 11/21/02 at 1717EST by Ken Russell taken by MacKinnon **** Evaluation determined that the door seal leakage was bounded by a calculation for degraded Control Room door seals that determined the maximum leakage allowed by the analysis in the Updated Safety Analysis Report (USAR) would not be exceeded even if the entire seal was removed. Therefore, it has been concluded that the Control Room boundary was not lost and this was not a condition that could have prevented the fulfillment of a safety function. As indicated in the original notification, entry was made into Technical Specification 3.0.3 as a result of the assumed loss of Control Room Emergency Recirculation. However, the condition was corrected within one hour, such that it was not necessary to initiate actions to shutdown and thus this condition was not reported per 10CFR50.73(a)(2)(i)(B), a condition which was prohibited by the plant's Technical Specification. R3DO (Brent Clayton) notified. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-29
39325 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-10-25 14:30 | 2002-10-28 23:33 | 2002-10-28 | AGREEMENT STATE REPORT - MISSING IODINE- 125 SEEDS The Medical Physicist from Little Company of Mary Hospital called to report the loss of 5 Iodine-125 seeds of approximately 0.4 millicuries each. The facility was doing an implant for the treatment of prostate cancer and had cut the strips in half (5 seeds each). After having implanted 9 strips they were unable to locate the tenth piece. They surveyed the room and trash and did not find the missing seeds. The patient was fluoroscoped and x-rayed, the implanted seeds were counted and verified with what had been implanted. A representative from Amersham was present during the procedure and it was not determined if the tube shipped was half empty. The seeds came in steel tubes of 10. It is possible that one steel tube only had 5 when sent. Implant performed at 11:00 on 10/24/02. The tubes were counted, but not opened until the procedure (sterile) was initiated. The licensee kept looking for the missing Iodine-125 seeds and today, October 28, 2002, concluded that the event was reportable and notified the State of CA today at 1458 hours PST. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-10-31
39324 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-09-06 14:38 | 2002-10-28 16:54 | 2002-10-28 | INADVERTENT PRIMARY CONTAINMENT ISOLATION SIGNAL "On September 6, 2002 at 14:38 hours, an inadvertent primary isolation signal was initiated due to a false reactor low level signal. The isolation occurred during the 24-month Reactor Protection System (RPS) surveillance test on Unit 2 Scram Discharge Volume (SDV) level instrument. The affected Group 6C primary containment isolation valves (PCIVs) automatically closed as a result of the isolation signal. Inboard PCIVs on the suppression pool hydrogen and oxygen sampling system closed. In addition, the inboard PCIVs for the primary containment leak detector radiation monitor closed as designed. Inboard and outboard PCIVs for the "2A" containment hydrogen recombiner received an isolation signal but were in a closed position prior to the event. All systems functioned successfully during the event "The cause of the event was mispositioning of the Calibration Select and Command switch on the Rosemount Readout Assembly by the technician performing the test. The test was aborted and the isolation signal was reset. The valves that repositioned were restored to the pre-test configuration and the test was performed successfully. A work group standdown was conducted to review the lessons learned from this event. "This event is reportable per 10 CFR50.73(a)(2)(iv)(A) since PCIVs automatically closed on more than one system "Component data: Manufacturer: Rosemount Nuclear Instruments, Inc. Model number: 710DU Serial number: 66722" The NRC Resident Inspector was notified of this invalid automatic actuation by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-10-28
39323 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-09-20 | 2002-10-28 15:23 | 2002-10-28 | LOUISIANA DEPT OF ENVIRONMENTAL QUALITY AGREEMENT STATE REPORT RE: STOLEN MOISTURE/DENSITY GAUGE "ON SEPTEMBER 20, 2002, A TROXLER 3411-B GAUGE WITH SERIAL NUMBER 4524 WAS STOLEN FROM THE BACK SEAT OF A GMC EXTRA CAB TRUCK. THE GAUGE CONTAINED A 8.0 mCi (MILLICURIE) SOURCE OF CS-137 AND A 40 mCi SOURCE OF AM241:BE. THE GAUGE WAS STOLEN BY BREAKING THE LOCK ON THE SIDE REAR WINDOW OF THE TRUCK. THE GAUGE WAS NOT CHAINED TO THE TRUCK. THE FACILITY HAS CHANGE ITS PROCEDURES TO PREVENT THIS TYPE OF EVENT FROM OCCURRING AGAIN." "CONSTRUCTION TESTING LAB, 3008 5TH STREET, METAIRIE, LA" "STOLEN FROM 1995 GMC EXTRA CAB TRUCK" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-10-31
39322 | 0 | US AIR FORCE |  |  |  |  | 2002-10-24 11:00 | 2002-10-25 09:15 | 2002-10-25 | UNPLANNED CONTAMINATION OF AN INDIVIDUAL AFTER BREAKING A VIAL CONTAINING TRITIUM FROM AN EXIT SIGN. An individual at the Wright Patterson Air Force Base was working in a 40' x 40' rad storage facility when a glass vial from an exit sign(sealed source and device #NY-594-D-102-D) slipped out of its protective plastic cover and broke after hitting the floor. The vial contained approximately 3.226 curies of tritium(calculated activity) which is less than he original activity of 10 curies. The highest reading measured in the room from surveys and swipes was 60,000 cpm. After initial wipe downs with wet rags, contamination was reduced in that area to 800 cpm. They will continue to survey and when contamination is found will continue to decontaminate until acceptable release criteria is obtained. The gentleman that was in the room when the vial broke and release occurred is having a bioassay and an estimate his whole body exposure is between 11-12 mrem. He and a second person are performing the surveys and decontamination of the room. The second individual will also probably get a bioassay upon completion of decon. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2002-10-25
39321 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2002-10-24 20:52 | 2002-10-25 04:43 | 2002-10-25 | CONTAMINATED WORKER TRANSPORTED OFFSITE FOR MEDICAL TREATMENT "While working under the ANO-1 Reactor Vessel Head, an individual bumped his head on a Control Rod Drive Lead Screw. The contact resulted in a 1-inch laceration on the side of the head. The Emergency Medical Response Team was activated and responded to the scene. The Individual was conscious but dazed. An initial survey for contamination was performed and was inconclusive due to background levels at the scene and due to a head brace which was placed on the individual as a precaution to guard against neck injury. An ambulance was called to the site and the individual was transported with a ANO Health Physicist to Saint Mary's Regional Medical Center. Additional surveying of the individual revealed that the individuals head was slightly contaminated at approximately 100 counts per minute above background and the backboard used in transport had approximately 150 counts per minute. The individual was decontaminated by ANO Health Physics personnel dispatched to the hospital. All of the radioactive material was retrieved and returned to the site. The individual is in satisfactory condition and the wound required 3 stitches to close." The licensee will inform the state and has informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2002-10-25
39320 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2002-10-24 12:25 | 2002-10-24 16:10 | 2002-10-24 | OFFSITE NOTIFICATION TO NATIONAL MARINE FISHERIES SERVICE - GREEN SEA TURTLE. A green sea turtle was recovered from Crystal River Unit 3 intake at approximately 01:00 on 10/24. Subsequent to the turtle's recovery it had died. At 12:25, staff biologist in conjunction with Florida Fish and Wildlife Commission, determined that the death was causally related to station operations, and as such, is required to be reported to the National Marine Fisheries Service. This is the first causally related fatality for the current reporting period. The NRC Resident Inspector was notified of the offsite notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-24
39319 | 0 | TESTWELL LABORATORIES, INC. |  |  |  |  | 2002-10-24 06:00 | 2002-10-24 10:21 | 2002-10-24 | TROXLER GAUGE STOLEN FROM VEHICLE A Troxler Gauge Model 3430, serial #20134, belonging to Testwell Laboratories, Inc., was stolen from the inspector's vehicle parked overnight at his residence in Jersey City, NJ. The RSO estimates that the theft occurred between 2200 hours on 10/23 and 0600 hours on 10/24/02. The gauge contains two (2) sources; 8 millicuries of Cs-137 and 40 millicuries of Americium-241:Be. At approximately 0830 hours on 10/24/02, the RSO received a call from the Jersey City Police Department that the stolen gauge was found on the sidewalk at the intersection of Orchard and Crawford street. The RSO arrived on scene and recovered the device at 0930 hours. Due to the number of agencies responding (3-4) to the scene and discussions of the potential for a three (3) block evacuation, the RSO is anticipating media interest. There is no visible damage to the recovered device. The licensee informed NRC Region I (Lodhi). The Jersey City PD file case number is 217013. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-10-24
39318 | 0 | US ARMY |  |  |  |  | 2002-10-24 | 2002-10-24 10:04 | 2002-10-24 | CHEMICAL AGENT DETECTOR DISCOVERED MISSING DURING INSPECTION An M43A1 Chemical Agent Detector, serial #Z03-D-11181, containing 300 microcuries of Americium-241, serial #Z03-C-10528, was discovered missing during a program inspection the week of 14 October, 2002, at the Jackson National Guard Armory in Portland, OR. The National Guard Unit will conduct a complete inventory of detectors the weekend of 1 November, 2002, during their next scheduled drill. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-10-24
39317 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2002-10-24 08:25 | 2002-10-24 09:28 | 2002-10-24 | OFFSITE NOTIFICATION TO STATE AGENCY DUE TO SMALL OIL SPILL ONSITE The Connecticut Department of Environmental Protection, both the Duty office and Oil/Spill Unit, was notified of a minor hydraulic oil spill (approximately 1 gallon) occurring onsite. The spill is contained with cleanup in progress. The licensee will inform the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-24
39316 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2002-10-24 01:22 | 2002-10-24 04:48 | 2002-10-24 | UNIT 1 MANUALLY TRIPPED DUE TO DECREASING STEAM GENERATOR WATER LEVEL "While performing a Plant Startup, following a refueling outage, a manual reactor trip was initiated due to decreasing Steam Generator Level. The trip occurred at 0122 hours. A main feedwater pump was being placed in service just prior to the trip. The auxiliary Feedwater system was placed in service per plant procedures. The cause for decreasing S/G level is being investigated." All rods fully inserted. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-10-24
39315 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-10-23 11:08 | 2002-10-23 20:18 | 2002-10-23 | 91-01 RESPONSE BULLETIN 24 HOUR REPORT- LOSS OF ONE CONTROL (GEOMETRY) "On 10/23/02 @ 1108 hours, The Plant Shift Superintendent (PSS) was notified of a violation of NCSA-0705_035 Control #23 in the X-705 Tunnel Basement Area. Control #23 states in part, 'At no time shall the depth of standing liquid, covering the entire floor area, exceed a depth of 1.7 inches.' Operations Personnel reported that as a result of a failure of the Facility Condensate System, the entire floor was covered by Non-Fissile Liquid greater than 1.7 inches in depth, thus constituting a loss of one Control (Geometry). All other Double Contingency Controls (Concentration, Interaction, and Other Passive Designs) were maintained throughout this event. The Failed System has been isolated and all Uranium Bearing Material Evolutions have been suspended pending repairs to the failed Facility Condensate System. "SAFETY SIGNIFICANCE OF EVENTS: This event has a low safety significance. The majority (99%) of the liquid on the floor area is overflowing steam condensate tank. The only credible way for additional Uranium bearing solution to be added to the liquid on the floor is for a fissile solution storage bank to catastrophically fail. All uranium bearing solution evolutions in this work area have been suspended pending repairs. "POTENTIAL CRITICALLY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): One filled fissile solution storage bank fails while filled with fully enriched saturated U02F2 solution and all of the solution empties onto the floor of the tunnel basement floor mixing with the existing liquid to a minimum depth of 2 inches everywhere on the floor. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The NCSA/NCSE controlled the floor of the tunnel basement area (Geometry), the condition of the floor of the tunnel basement (Geometry), and the depth of standing liquid allowed on the floor of the tunnel basement area. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Less than [. . .] grams of U-235 in the standing liquid on the floor of the tunnel basement area with a maximum enrichment of [. . .] wt% of U-235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The depth of standing liquid, as measured at the deepest location, exceeded the allowed depth of 1.7 inches. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: No Safety System Activation resulted. All uranium bearing solution evolutions were suspended at 1108 hours as a result of this event and will remain as such pending repairs to the Facility Condensate System." The licensee has notified the NRC Resident Inspector and the onsite DOE Representative of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-10-23
39314 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-10-14 | 2002-10-23 17:09 | 2002-10-23 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE North Carolina Incident Report #02-41. Reported to North Carolina Division of Radiation Protection on 10/23/02 that an electron capture device sealed source (20 millicuries of Ni-63, serial #5339) has been determined to be leaking. Smear read 180,000 DPM (0.08 microcuries). Prizm Labs is contacting the manufacturer for disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-10-28
39313 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-10-23 15:00 | 2002-10-23 16:40 | 2002-10-23 | AGREEMENT STATE REPORT - STUCK SOURCE IN BRACHYTHERAPY DELIVERY SYSTEM North Carolina Incident Report #02-40. While performing a QA/QC test of a Gamma Med Brachytherapy system, the source (unknown strength at this time) stuck half way out. Efforts to retrieve the source normally, with the emergency retrieval system, and the manual crank were not successful. The manufacturer has been notified and the area secured. One physicist entered the room during the recovery operation and may have received a dose, survey meter pegged at 2 Rem/hour on entry to room. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-10-28
39312 | 0 | TENET HEALTH SYSTEMS GRADUATE |  |  |  |  | 2002-10-22 10:00 | 2002-10-23 16:38 | 2002-10-23 | MEDICAL MISADMINISTRATION-SOURCE RUPTURE DURING REMOVAL A 830 microcurie Iodine 125 brachytherapy source ruptured while it was being withdrawn from a patient's bladder during a prostate implant. The seed was removed and the patient's bladder was flushed. The flush solution measured 0.2 microcuries. Follow-up actions include evaluation of possible patient thyroid uptake and investigation to determine why the retrieval mechanism ruptured the source. The patient and prescribing physician have been informed of this event. The licensee also notified NRC Region 1 of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0 | 2002-10-23
39311 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2002-10-23 11:13 | 2002-10-23 12:15 | 2002-10-23 | HIGH PRESSURE CORE SPRAY FAILED TO START ON DEMAND The licensee was in the process of conducting normal testing when attempting to start the High Pressure Core Spray Pump, it did not start. The problem is being investigated at this time. This notification is being made per 10 CFR 50.72(b)(3)(v)(D) under accident mitigation. The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-23
39310 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-10-22 12:52 | 2002-10-22 17:34 | 2002-10-22 | LOSS OF HIGH PRESSURE COOLANT INJECTION SYSTEM "At 1252 [CDT] on 10/22/02, during troubleshooting activities, a loss of the Unit 3 Division II ECCS inverter occurred. This resulted in a loss of the High Pressure Coolant Injection system (HPCI) due to a loss of power to the flow indicating controller. This event is reportable within 8 hours per 10CFR 50.72(b)(3)(v) and requires a 60 day written report per 10CFR 50.73(a)(2)(v)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION | POT RHR INOP |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(v)(B) |  |  | 0 | 2002-10-22
39309 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-09-29 09:06 | 2002-10-21 21:15 | 2002-10-21 | 60-DAY REPORT - INVALID ACTIVATION OF STANDBY SERVICE WATER SYSTEM "On September 29, 2002 at 0906 hrs, a pressure transmitter loop channel in the Service Water System was being removed from service as part of an instrument calibration procedure. The transmitter was being electrically disconnected per the procedure, when an inadvertent start of 2SWE-P21A, 'A' Standby Service Water Pump, occurred. The SWE pump started because the technicians inadvertently did not perform a step in the procedure which opens bistables that defeat the actuation of a low pressure signal. The transmitter became deenergized when it's leads were lifted, resulting in an electrical signal which caused the actuation since the signal had not been defeated. Since there was no actual low pressure condition in the system, this was an invalid actuation. Low service water system header pressure is the parameter which would activate this feature and low service water system header pressure was not experienced during this event. A complete actuation of the 'A' train of the Standby Service Water System occurred and the system functioned properly. "This event is reportable pursuant to 10 CFR 50.73(a) (2)(iv) (A) since it involved an automatic actuation of an emergency service water system that does not normally run and that serves as an ultimate heat sink as per 10 CFR 50.73(a)(2)(iv)(B)(9). This actuation was not part of a pre-planned sequence and did not occur with this system properly removed from service. "However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification instead of submitting a written Licensee Event Report since the automatic actuation of the Standby Service Water pump was not generated by a valid actuation." The licensee notified the NRC Resident. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-10-21
39308 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-10-21 16:30 | 2002-10-21 20:22 | 2002-10-21 | FITNESS FOR DUTY REPORT Contractor supervisor tested positive for illegal drugs. The person's unescorted access was revoked. Call the Headquarters Operation Officer for further details. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2002-10-21
39307 | 0 | SOUTHERN INDIANA RADIOLOGICAL ASSOC |  |  |  |  | 2002-10-18 14:00 | 2002-10-21 16:27 | 2002-10-21 | MEDICAL MISADMINISTRATION A radiological laboratory technician inadvertently administered the incorrect dose of Tc-99M to a patient. A bone dose was desired and a lung dose was actually administered. The laboratory stated that the absorbed dose to the patient was insignificant. The cause of the misadministration was a failure by the technician to properly identify the syringe. The corrective action to prevent recurrence was to counsel the technician. The laboratory notified the patient's physician and will file a written report to NRC Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2002-10-21
39306 | -1 | STORA NESO |  |  |  |  | 2002-10-21 | 2002-10-21 16:18 | 2002-10-22 | FAILED LEAK TEST ON STATIC GUN GOING TO DISPOSAL Stora Neso was in the process of disposing of a Chapman Manufacturing (no longer in business) static gun containing 200 millicuries of tritium (when manufactured in September 1965). Stora Neso does not have a requirement to leak test the static gun, which had not been used for a long time. The disposal site requested a leak test. The static gun was wipe tested and the following results were obtained: wet wipe read 0.311409 microcuries and the dry wipe read 0.0556399 microcuries, the action level is 0.005 microcuries. They have taken additional wipes of the gun and container whose results are not available at the time of the report. They have also contacted a testing company to determine what the wipes are actually were measuring. * * * RETRACTION ON 10/22/02 AT 1210 EDT FROM CHUCK CHAPMAN TO GERRY WAIG After discussion between the licensee and NRC Region 3 personnel, the licensee retracted this event on 10/22/02 at 1210 EDT. Notified R3DO (Christine Lipa) and NMSS (Doug Broaddus). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | WI | MAT | [5 empty] | 0 | 2002-10-21
39305 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-10-19 13:47 | 2002-10-19 14:14 | 2002-10-19 | TECH SPEC REQUIRED SHUTDOWN "Millstone U2 Initiation of plant shutdown as required by Technical Specifications 10CFR50(b)(2)(i)" Power supply to the Engineering Safeguards Activation System was replaced and tested satisfactory. Unit will subsequently return back to full power. The licensee notified the NRC Resident Inspector. | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-10-19
39304 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-10-19 10:15 | 2002-10-19 11:55 | 2002-10-19 | LOSS OF ENS AND COMMERCIAL TELECOMMUNICATIONS "At 10:15 on 10/19/02, the ENS and commercial telecommunications capability to dial offsite was found to be non-functioning. Communications to outside agencies have been verified using the microwave lines (RERP lines). The cause of the problem is not yet determined, however, the local telecommunications company is investigating." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-10-19
39303 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2002-10-18 21:30 | 2002-10-19 05:27 | 2002-12-13 | RCIC HIGH STEAM FLOW ISOLATION INSTRUMENTATION INOPERABLE DUE TO BEING OUT OF TOLERANCE "At 2130 hours CDT on 10/18/2002, the U1 RCIC High Steam Flow Isolation Instrumentation was determined to have been inoperable. Both U1 RCIC High Steam Flow switches were found to be outside their Technical Specification Allowable Value during a calibration surveillance. Both U1 RCIC High Steam Flow switches were subsequently recalibrated back to within their Technical Specification Allowable Value. "This notification is being made in accordance with 10CFR50.72(b)(3)." The NRC Resident Inspector has been notified. * * * UPDATE 1145EST ON 12/13/02 FROM RON RUSTICK TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this notification is to retract the ENS report made on 10/19/2002 at 05:27 EDT (Event #39303). The initial report concerned the Reactor Core Isolation Cooling (RCIC) system high steam flow isolation function. On 10/18/2002, both required high steam flow isolation instruments were found to be outside of their Technical Specifications Allowable Value (AV); therefore, a notification was made under 10CFR50.72(b)(3)(V)(D). However, a subsequent review of this event has determined that only one of the two required channels actually exceeded the AV and thus one channel was OPERABLE and capable of initiating the isolation function (i.e., there was no loss of safety function). For this reason, Quad Cities Station has concluded that the RCIC high steam flow isolation function was preserved." The licensee informed the NRC resident inspector. Notified R3DO(Hiland). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-19
39302 | 0 | US ARMY |  |  |  |  | 2002-10-17 | 2002-10-18 09:52 | 2002-10-18 | POSSIBLE LOST/STOLEN CHEMICAL AGENT DETECTOR The licensee is investigating the circumstances involving a chemical agent detector being turned in to the Military Police (MP's) by the spouse of a serviceman stationed at Fort Bragg NC. The CAD, containing 15 millicuries of Ni-63, was being kept at the serviceman's home. The Army is trying to determine if the device was stolen . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | NC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-10-18
39301 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-10-17 16:40 | 2002-10-17 23:30 | 2002-10-18 | 24-HOUR 91-01 BULLETIN RESPONSE NOTIFICATION "At 1708 on 10-17-02, the Plant Shift Superintendent (PSS) was notified that potentially fissile (PF) waste had been discovered improperly stored at the Wet Air Pump station in the C-333 building. A pile of used absorbent pads was found in the floor at the West Air station. The absorbent pads are used to soak up oil that has leaked from the pumps. These pads should have been placed in an AQ-NCS approved 5.5 gallon drum and controlled as PF waste as they were picked up. This is a violation of the requirements of NCSA GEN-15. "The NRC Resident inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: The used absorbent pads were accumulated incorrectly; however the uranium concentration for heterogeneous waste is low and a large quantity of heterogeneous fissile material would be required for a criticality to occur. "PATHWAYS INVOLVED: In order for a criticality to be possible, the interaction process condition would also have to be violated. However, the interaction control was maintained and therefore a criticality was not possible. "CONTROLLED PARAMETERS: The two process conditions relied upon for double contingency for this scenario are interaction and geometry. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEMS(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on a minimum 2 ft. edge-to-edge spacing requirement to ensure double contingency for spacing violations involving waste drums end other items containing fissile/potentially fissile material. This control was not violated. "The second leg of double contingency is based on geometry controls of the waste when it is placed into an AQ-NCS approved waste drum and the secondary containment pans used to store the drums. Since the waste was accumulated on the floor and not into the NCS-approved container, this control was violated. The process condition was not maintained and double contingency was not maintained "Since the used absorbent pads were not generated into an AQ-NCS approved waste container, the process condition for waste accumulation was not maintained. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS: A buffer area has been established to control movement of fissile material within the area. A remediation guide will be prepared by NCS prior to removal of the used absorbent pads. *****UPDATE ON 10/18/02 AT 2120 FROM BEASLEY TO LAURA***** "As a result of continued evaluation, it was discovered that the pile of absorbent pads was with 2 feet of the 4 inch diameter wet air header. Therefore the minimum 2-foot spacing control has also been violated. Even though the spacing control was violated, the existing configuration is bounded by analysis, and it is acceptable to continue to use the header piping within 2-feet of the pile of absorbent pads. "While approved analysis does exist to safely bound the current violation configuration, both controls relied upon for the safe generation and handling of potentially fissile waste material were violated. "In order for a criticality to be possible, an additional violation would have to occur resulting in an unsafe mass of fissile material accumulating in an unsafe geometry. "Approved analysis exists which bounds the existing configuration and demonstrates it is subcritical. However, the process conditions for waste accumulation were not maintained. Therefore, double contingency was not maintained." Notified NMSS (HODGES). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-10-17
39300 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-10-17 14:30 | 2002-10-17 18:55 | 2002-11-13 | HPCI INOPERABLE DUE TO LOW INTERNAL BATTERY RESISTANCE The licensee reported that during a 250 Vdc battery surveillance the internal resistance of cell #18 was greater than the technical specification (TS) limit. As a result, the licensee declared battery bank 1D4 inoperable which also rendered inoperable the HPCI system and any containment isolation valves powered from the battery bank. This included 5 total CIVs [Containment isolation valves] from the following systems: HPCI, RWCU and MSL drain and Torus drain valves. Corrective maintenance was performed on the battery cell and the internal resistance passed the TS limit. HPCI and CIVs were returned to an operable status approximately 3 hours after being declared inoperable. At the time of this event, the RCIC system was inoperable for planned maintenance so the LCO entered for HPCI was more restrictive allowing 12 hours rather than the normal 14 day LCO for HPCI. *** THIS EVENT WAS RETRACTED AT 1357 ON 11/13/2002 BY CLARE BLEAU TO ERIC THOMAS *** The licensee is retracting this report based on the following: "On 10/17/02 Event Notification #39300 was completed pursuant to 10 CFR 50.72 (b)(3)(v)(D) due to the 250 Volt Station Battery 1D4 being declared inoperable which caused the High Pressure Coolant Injection (HPCI) system to also be inoperable. At the time that this occurred, the Reactor Core Isolation Cooling (RCIC) system was also inoperable due to preplanned maintenance. This required that a 12 hour to hot shutdown and 36 hour to cold shutdown LCO be entered per Technical Specification 3.5.1.J. Maintenance was performed on battery 1D4 and it was returned to operability. The other related LCOs were also exited prior to plant shutdown. "An operability evaluation was subsequently completed which determined that 1D4 could have performed its design function with the data taken from STP 3.8.4-05. C&D Technologies has confirmed this. Only one of the two connections needs to be below 50 micro ohms to meet TS 3.8.4.5. "If all of the discharge current were to pass through the 129 micro ohm connection, the voltage drop would be 0.06 volts. This has no bearing on the design function of the 250 VDC system. 1D4 currently has a design margin of 1.65 (65% excess battery capacity). Therefore, battery 1D4 actually was operable and capable of performing its required safety function. The PCIV [Primary Containment Isolation Valve] LCO 3.6.1.3 was also entered for 250VDC MOVs that are PCIVs. This included the HPCI outboard steam supply valve MO-2239 and the HPCI feedwater injection isolation valve MO-2312. Review of the shift logs and discussion with the shift manager confirmed that these valves were not closed so that HPCI remained available during this event. No LER is required under 10 CFR 50.73 (a)(2)(v)(D) and the 8-hour Non-emergency notification under 10 CFR 50.72 (b)(3)(v)(D) (EN#39300) can be retracted." The NRC Resident Inspector was notified of this retraction by the licensee. Notified Bruce Burgess, R3DO. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-17
39299 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-10-14 23:00 | 2002-10-17 15:50 | 2002-10-17 | INADVERTENT EFW ACTUATION ON 10/14/2000 "Per 10CFR50.73(a), Entergy is providing a verbal notification of an inadvertent actuation of the emergency feedwater (EFW) system at Waterford 3, which occurred on October 14, 2000. This event was initially determined to be not reportable, based on the reasoning that the actuation of the emergency feedwater components were initiated from the Diverse Emergency Feedwater System (DEFAS), and not from an Emergency Feedwater Actuation System (ESFAS) actuation. However, during a technical specification audit in August of 2002, questions were raised regarding the validity of this reportability determination and a condition report was initiated. A subsequent review by licensing completed on August 21, 2002 determined that the event should have been reported per the then existing 10CFR50.72 (b)(3)(iv) requirement as a 4-hour notification and reported as a follow-up LER notification per 10CFR50.73(a). The current applicable reporting criteria do not require immediate notification, however an LER or verbal notification is required per 10CFR50.73(a). Accordingly, this report is provided as a verbal notification per 10CFR50.73(a), Reportable events, which states, in part, in the case of an invalid actuation reported under 50.73(a)(2)(iv), the licensee may, at its option, provide a telephone notification to the NRC Operation Center within 60 days after the discovery of the event instead of submitting a written LER. This actuation was invalid, as described further below. "On October 14, 2000, the plant was in mode 3 in preparation for refueling outage 10, when an inadvertent actuation of emergency feedwater components occurred. This event occurred during the performance of procedure OP-904-017, Anticipated Transient System Check. While performing section 7.2, Testing of Diverse Emergency Feedwater System (DEFAS), step 7.2.12 (to replace the Diverse Emergency Feedwater Actuation System selector switch to disable) was inadvertently missed. This caused the emergency feedwater components to move to their safety positions when the DEFAS test switch was restored to its normal position. The two motor driven emergency feedwater pumps and the steam driven emergency feedwater pump started. The emergency feedwater isolation valves opened, but the emergency feedwater control valves did not open, as per design, due to adequate steam generator water levels. Accordingly, this event did not result in emergency feedwater flow or emergency feedwater injection into the steam generators. The operator immediately secured the EFW pumps and closed the EFW isolation valves. "NUREG 1022, revision 2, Event Reporting Guidelines 10CFR50.72 and 50.73 provides guidance for determining if an actuation is invalid. The NUREG states, in part, that invalid actuations include actuations that are not the result of valid signals and are not intentional manual actuations. Valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. This report documents an actuation that was not the result of a valid signal and was not an intentional manual actuation, For these reasons, this event constitutes an invalid actuation." The NRC resident inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-10-17
39298 | 0 | CREST FOAM INDUSTRIES |  |  |  |  | 2002-10-17 | 2002-10-17 14:37 | 2002-10-17 | MISSING NUCLEAR DENSITY METER The licensee reported a missing Texas Nuclear Density Meter, Model 5201, serial number B764 and source number GV1731. The meter source contains 100 millicuries of Cs-137. The licensee had already contacted the local police department to report the missing meter. The exact date of loss is not known but the last physical audit performed by the licensee was in January 2002. The meter is used to measure the thickness of the foam density. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-10-17
39297 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-10-17 11:21 | 2002-10-17 13:03 | 2002-10-17 | COMPROMISE OF SAFEGUARDS INFORMATION IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. CONTACT HOO FOR ADDITIONAL DETAILS. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-10-17
39296 | -1 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2002-10-17 05:15 | 2002-10-17 11:24 | 2002-12-04 | CONDITION WHICH COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During a post maintenance test run of the 2B Diesel Generator following a planned maintenance window, the Diesel Generator reactive load (VARs) was identified to be erratic, as the Diesel Generator was loaded. At 05:15 CDST on 10/17, it was discovered that a potentiometer in the voltage regulating circuit had erratic output. This potentiometer was not worked on during the planned maintenance window. Because this component failure could have prevented the Diesel Generator from performing its design function, and because the 2B Diesel Generator is the emergency power supply for the High Pressure Core Spray System (HPCS), which is a single train safety system, it has been determined that this failure could potentially effect the Safety Function of this system, and is reportable as an 8 hour ENS notification." "Add info on current results/status below. The required actions of Technical Specification 3.5.1 were entered when the system was made inoperable for the maintenance window on 10/13 at 1900, and are continuing to be followed for the Inoperable High pressure Core Spray System (HPCS), until the Diesel Generator is restored to Operable Status." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM LARRY R. BLUNK TO HOWIE CROUCH ON 12/04/02 AT 1913 EST * * * "UPDATE INFORMATION: RETRACTION OF NOTIFICATION (EN# 39296) "THE ROOT CAUSE DETERMINATION AND ENGINEERING EVALUATION DETERMINED THAT THE ERRATIC OUTPUT WAS DUE TO A DEGRADED MOTOR OPERATED POTENTIOMETER (MOP). THE ENGINEERING EVALUATION DETERMINED THAT THE ERRATIC OUTPUT WOULD NOT HAVE OCCURRED IF THE 2B DIESEL GENERATOR HAD BEEN OPERATING IN AN EMERGENCY (I.E. ISOCHRONOUS) MODE. THEREFORE, IN THE EVENT OF AN EMERGENCY DEMAND, THE 2B DIESEL GENERATOR WOULD HAVE BEEN CAPABLE OF PERFORMING ITS SAFETY FUNCTION ." The licensee notified the NRC Resident. The Headquarters Operation Officer informed R3DO (Ken Riemer). | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-17
39295 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-10-17 09:21 | 2002-10-17 10:27 | 2002-10-17 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) IS OUT OF SERVICE DUE TO PLANNED MAINTENANCE At 0921 hours on 10/I7/02, the Safety Parameter Display System (SPDS) was removed from service as part of preplanned work to facilitate future replacement of the Emergency Response Facility Computer System (FRFCS). Electrical service was also interrupted to the Technical Support Center rendering that emergency response facility (ERF) unavailable for use. Work should be complete by mid afternoon. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-10-17
39294 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-10-16 15:25 | 2002-10-16 16:35 | 2002-10-16 | 4 HOUR OFFSITE NOTIFICATION TO MD DEPARTMENT OF ENVIRONMENT "Calvert Cliffs made a report to the Maryland Department of the Environment for positive coliform bacteria in the [potable water for the] office facilities." The NRC Resident Inspector will be notified by the Licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-16
39293 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2002-10-16 | 2002-10-16 14:04 | 2002-10-22 | STOLEN VEHICLE AND TROXLER MOISTURE DENSITY GAUGE On the evening 10/15/02 or the early morning of 10/16/02 a 1987 red Toyota 4 Runner storing a Troxler moisture density gauge was stolen from the residence of an authorized user. The local police were notified of the theft at approximately 0800 PDT and the Oregon Radiation Protection Services at 0855 PDT on 10/16/02. The gauge is a Troxler model 3440 serial number 26707 and contains an 8 millicurie Cs-137 source, serial number 75-9841, and a 40 millicurie Am-241:Be source, serial number 47-23181. The licensee is GEOCON Northwest Inc., 8380 Southwest Ave., Beaverton, OR 97008. Oregon Radiation Protection Services will notify NRC Region 4 and plans to make a press release for this event. The Oregon event number for this incident is 020041. * * * UPDATE ON 10/22/02 AT 2329 FROM TERRY LINDSEY TO GERRY WAIG * * * Mr. Terry Lindsey, Program Manager, Oregon Radiation Protection Services called to report that the stolen Troxler moisture density gauge model #3440, serial #26707 was recovered by the Portland, OR Police Department on 10/22/02 at 1735 PDT . A HAZMAT team was called to the scene and the gauge was intact. Additional follow-up is planned for tomorrow morning (10/23/02). The owner of the gauge, GEOCON Northwest Inc., has been notified of the recovery. Notified R4DO (Anthony Gody) and NMSS (Mel Leach) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2002-10-21
39292 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2002-10-16 01:52 | 2002-10-16 12:02 | 2002-10-16 | MANUAL ACTUATION OF THE EMERGENCY FEEDWATER SYSTEM "On October 16, 2002 at about 0150 PDT, to test the normal lube oil system for Unit 3 normal feedwater pump K006, plant operators started the second (3P-109) of the two lube oil pumps for normal feedwater pump K006 at San Onofre Unit 3. For this test, after normal operation of the second pump has been observed, the first lube oil pump (3P-122) is stopped. At 0152 PDT, the first lube oil pump (3P-122) was manually stopped by plant operators and normal feedwater pump K006 automatically tripped. Because 100 percent power operation cannot be sustained with only one of the two normal feedwater pumps in operation, plant operators began reducing reactor power level to about 75 percent. As specified by plant procedures as a precautionary measure, plant operators also manually initiated the Emergency Feedwater system, which successfully started all three emergency feed water pumps. Because 10CFR50.72(b)(3)(iv)(A) requires licensees to report any event or condition that results in valid actuation of the emergency feedwater system, SCE is providing this notification to the NRC. "The cause of this event is currently under investigation and will be reported to the NRC in the required follow-up 60-day written report. "At the time of this occurrence, both Units 2 and 3 were operating at about 100 percent power. "SCE has notified the NRC resident inspectors about this occurrence and will provide them with a copy of this report." | 0 | 0 | 75 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-10-16
39291 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2002-10-15 23:56 | 2002-10-16 01:45 | 2002-10-16 | MANUAL REACTOR TRIP DUE TO DROPPED ROD "The Unit 1 Operator-At-The-Controls moved control rod bank D rods in 1/2 step for routine flux control at 2353 on 10/15/02. He immediately noticed rod F-6 indicated 198 steps. The remainder of the rods in bank D indicated 221 steps. A negative rate trip was received on Excore Nuclear Instrument N43 and reactor power decreased approximately 1/2% RTP [rated thermal power]. A manual reactor trip was initiated at 2356 in accordance with Abnormal Operating Procedure FNP-1-AOP-19.0. All plant systems responded per design to the reactor trip. The plant is currently stable in Mode 3. The cause for the rod drop is being investigated. Both motor driven auxiliary feedwater pumps and the turbine driven auxiliary feedwater pumps auto started in response to the main steam generator feed pumps trip." All rods fully inserted into the core. The Main Condenser is being maintained as the primary heat sink. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-10-16
39290 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-10-14 | 2002-10-15 19:15 | 2002-10-15 | AGREEMENT STATE REPORT INVOLVING INDUSTRIAL RADIOGRAPHY INCIDENT The following information was documented as a telecon "to file" received by State of Colorado staff: "Received phone notification today from Jeff Conners at Midwest Inspection Services concerning a source disconnect incident that happened yesterday, 10/14/02. Mr. Conners reported a radiography crew, working at a field site north of Denver, was unable to retract an Iridium-192 radiography source back into the camera. The radiographers called Mr. Conners, who is the assistant Radiation Safety Officer, for help. Mr. Conners reported that he responded to the scene and was successful in connecting the source assembly to the drive cable and retracting it back into the radiography camera. He also responded that there were no overexposures to the radiography crew or members of the public. Mr. Conners estimated his exposure for the recovery operation to be about 500 millirem, based on his pocket dosimeter readings. He stated that he would send a detailed written report to the Department within 30 days. The corporate RSO, David Ezell, was also notified of the incident." Contact the Headquarters Operations Officer for additional information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-10-18
39289 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2002-10-15 15:25 | 2002-10-15 19:18 | 2002-11-08 | AGREEMENT STATE - LOST OR STOLEN TROXLER MOISTURE DENSITY GAUGE "Description of event: The licensee reported the loss of a Troxler moisture/density gauge sometime between 1030 and 1115 on 15 October after the technician left a job site in the vicinity of Cactus and 151st Ave. The gauge had been in the back of a pickup with the tailgate down. The gauge did not have a handle lock. A search of his route for several hours failed to turn up the gauge. The gauge is a Troxler Model 3400 series, serial number 29519. It contains approximately 10 millicuries of cesium 137 and approximately 50 millicuries of americium-beryllium. The company is offering a $250 reward for information leading to the return of the gauge and truck. "The U.S. NRC, FBI, Mexico, and the states of Colorado, Nevada, Utah, New Mexico and California are being informed of this incident." *****UPDATE ON 11/8/02 AT 14:44 FROM GODWIN TO LAURA***** "At approximately 10:20 AM a non-licensee reported that a gauge has been turned in to 3777 E McDowell, Phoenix, AZ. Upon investigation the Agency determined that the gauge was the one lost Oct. 15, 2002. The Agency leak test indicated it is not leaking. The Licensee and Agency continue to investigate this event. The states of CO, NV, UT, NM and CA, as well as the U.S. NRC, U.S. FBI and Mexico are being notified of this recovery." Notified NMSS (Cool) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2002-10-18
39288 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-10-15 15:00 | 2002-10-15 17:54 | 2002-10-15 | NRC BULLETIN 2001-01 VISUAL INSPECTION DISCLOSED CRDM NOZZLE PENETRATION THROUGH WALL LEAKAGE "Event Description: During qualified bare metal visual inspection of the Unit 2 reactor vessel head and CRDM nozzle penetrations per Duke response to NRC Bulletin 2001-01, evidence of through wall leakage was witnessed on seven CRDM penetrations. The locations are nozzle 8, 9,19, 24, 31, 42, and 67. None of these seven nozzles have been previously repaired. Additional nozzle to head penetrations were masked by boron deposits suspected of being from a separate source. NDE will be performed per the Duke response to NRC Bulletin 2001-01 to characterize the status of the masked penetrations. "Initial Safety Significance: Any RCS leakage from these penetrations would have been below the threshold of measurability by the reactor coolant system leakage measurement process. "Corrective Actions: The leaking nozzles will be repaired prior to restart from the present refueling outage." The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | RESPONSE-BULLETIN |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-10-15
39287 | 0 | ALTECH CORPORATION |  |  |  |  | 2002-10-15 11:30 | 2002-10-15 15:52 | 2002-11-04 | LOST OR STOLEN TROXLER MOISTURE DENSITY GAUGES The licensee reported that two (2) Troxler moisture density gauges model number #2401 were missing from their storage area. The two gauges were serial number 2813 and 2744. Both gauges contain an 8.2 millicurie Cs-137 and 50 millicurie Am-241:Be source. The gauges are inventoried every six months and were verified in storage in March 2002. The cases (storage boxes) were verified again in August 2002. The licensee has notified local and county police of the missing gauges. Additionally, the licensee has contacted NRC Region 4 to inform them of this event. * * * * * UPDATE BY LICENSEE TO MIKE RIPLEY 1210 EST 11/4/02 * * * The licensee reported that both Troxler moisture density gauges were found and returned to the licensee. The gauges were found in the Portneauf River on 10/13/2002 by two hunters in the Blaze Creek Area near Lava Hot Springs, ID. The licensee stated that the Idaho State Police at Boise, ID, are continuing to investigate the lost gauges. Notified R4DO (C. Marschall) and NMSS EO (F. Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-10-15
39286 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-10-15 12:18 | 2002-10-15 15:32 | 2002-10-15 | REACTOR TRIP AS A RESULT OF LOSS OF TURBINE GENERATOR LOAD AT BYRON STATION UNIT 1 "At 12:18 10/15/02 Unit I reactor tripped as the result of exceeding the over-temperature Delta-temperature (OT[Delta]T) reactor trip set point. The OT[Delta]T set point was exceeded as the result of a loss of Turbine load. The loss of Turbine load is currently under investigation. "As the result of the reactor trip a feedwater isolation was initiated as expected and the auxiliary feedwater system was manually started to restore steam generator level. "As the result of high pressure in the reactor coolant system following the loss of load, the pressurizer power operated relief valves (PORV's) lifted. "Following the Unit trip 6.9kV, Bus 157 was de-energized due to unavailability of its back up feed breaker from the system auxiliary transformer. Planned maintenance on the breaker was in progress at the time of the trip. As a result the 1A reactor coolant pump was de-energized. All other reactor coolant pumps remained running. "All plant systems responded as expected." All rods fully inserted into the core and the pressurizer PORVs re-seated. There are no restrictions on restarting the 1A reactor coolant pump. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-10-15
39285 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-09-25 11:30 | 2002-10-15 11:35 | 2002-10-15 | PERSONNEL CONTAMINATION AND EXCESSIVE PACKAGE LEVELS AT NUCLEAR MEDICINE FACILITIES "A 300 millicurie multidose glass vial of technetium-99m was dropped on the floor at about 11:30 am [September 25, 2002] in a hot lab area at Baylor by a nuclear medicine technologist. About 40% of the vial contents spilled on the tech's pants, legs, and shoes. The initial radiation reading on the tech's clothing was 35.2 [millirem]/hr. An initial wipe test of the floor gave a reading of 81,012 dpm. The floor was decontaminated using radiowash until radiation wipe levels were at 366 dpm and the survey meter detected 1.8 [millirem]/hr. The tech's clothing were placed in storage for decay. "An outgoing nuclear medicine ammo box was about three feet from the spill. The box was labeled and had been surveyed and was ready for pickup by the nuclear pharmacy, Medi-Physics. The technologist did not believe the spill had contaminated the ammo box and did not perform an additional survey of it. The ammo box was picked up by a courier for the nuclear pharmacy. The courier picked up the ammo box by using the keypad lock to access the unoccupied hot lab as was his normal routine. "At around 1:00pm, as the courier was leaving the Medi-Physics facility, he surveyed his hands and noticed radiation readings. Both palms were contaminated and so was his shirt and pants. The hands gave readings of 8340 cpm's. The courier was decontaminated to approximate background levels. The only package picked up and transported by the courier was the ammo box from Baylor. The nuclear pharmacy contacted Baylor and notified the State. "The ammo box radiation readings were 2,664,800 cpm's and the main area of contamination read 150 [millirem]/hr. The courier vehicle showed contamination on the door handle, radio knob, steering wheel, and gear shift. Radiation readings were in the range of 81,649 cpm's. The ammo box was placed in storage for decay. The vehicle was quarantined, decontaminated to background revels, and returned to service the following day. "Additional information will be provided to the Agency in the Licensee's written report. An onsite investigation by the Texas Department of Health Bureau of Radiation Control identified items of noncompliance with Agency regulations." Texas Incident No. I-7938 Medi-Physics, Inc (doing business as Amersham Health of Dallas) Dallas, TX - License No. L05529 BaylorAll Saints Med Center, Ft. Worth, TX - License No. L02212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-10-18
39284 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-10-12 | 2002-10-14 16:27 | 2002-10-14 | AGREEMENT STATE - IRRETRIEVABLE WELL LOGGING SOURCE "Agreement State Agency: Louisiana Department of Environmental Quality "Event Report ID No.: LA020013 "License No.: LA-2783-L01 "Licensee: Schlumberger Technology Corp "Event date and Time: October 12, 2002 "Event Location: Miami Corp #1S in Cameron, LA "Event type: Irretrievable Well Logging Source "Notifications: Schlumberger notified the Louisiana Department of Natural Resources and the Louisiana Department of Environmental Quality. "Event description: On October 9, 2002, a well logging tool was stuck down hole. The tool contained a 1.7 Ci source of Cs-137 model number GSRZ with s/n 2009 and a 16 Ci source of Am241Be model number NSR-L with s/n 3068. There were repeated attempts to retrieve the tool. On October 12, 2002, it was decided to abandon the tool. Approval was given from the state of Louisiana on October 12, 2002, to abandon the tool. The approximate depth of the tool is 10,822 feet. A cement plug was going to be placed above the tool, cement is going to be added around the tool, and an upside down drill bit is to be used as a deflection device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-10-17
39283 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-10-14 14:15 | 2002-10-14 14:40 | 2002-10-14 | DISCOVERY THAT APPENDIX R CRITERIA NOT SATISFIED FOR ELECTRICAL CABLING "An open void was discovered (approx. 5 feet deep) that exists in the area between the Reactor and Turbine Building walls beneath the 23' floor elev. affecting Appendix R fire separation. It appears that sand has been moved / eroded away over time, thus opening a void beneath the A and B 480 V switch gear room floors. Adequate separation of the conduits between A and B trains no longer meets Appendix R separation criteria beneath the floor. "At the present time plant safety is not affected, as a compensatory measure a firewatch has been established in the affected area." The licensee has corrective action under review and has informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-10-14
39282 | 0 | MICHIGAN DEPARTMENT OF ENVIR. QUAL |  |  |  |  | 2002-10-14 07:00 | 2002-10-14 09:58 | 2002-10-14 | SYNCOR VEHICLE CARRYING RADIOPHARMACEUTICALS OVERTURNED A Syncor transportation vehicle, 2000 Ford Ranger Pickup truck, turned over near State Highway M-20 and 162 avenue which is located in Oceana County, MI west of Hesperia, MI, around 0700 ET on October 14, 2002. The driver was not injured. Three packages were damaged or potentially damaged. The first package was empty and was being returned to Syncor was totally smashed. The second package had a White Label 1 containing 16.13 GBq of Tc-99m. The third package was Yellow Label 2 contain 6.9GBq of Tc-99m and 0.001 GBq of I-123. The last two packages were being delivered to Gerber Memorial Health Center located in Fremont, MI. When the local Fire Department/Police showed up at the scene of the accident they called Gerber Memorial Health Center and informed them that they needed someone to take radiation surveys at the scene of the accident. Gerber Memorial Health Center sent a person to the scene of the accident. All radiological surveys taken at the scene of the accident indicated that the contents of packages 2 & 3 were not damaged. The inner containers inside packages 2 & 3 were intact and undamaged. The first package level was at normal background level. The person from Gerber Memorial Health Center placed the packages in the trunk of his car and took them to Gerber Memorial Health Center. Syncor went out to Gerber Memorial Health Center and picked up the packages and took them to their facility located in Jenison, MI. Also Syncor took radiation surveys at the scene of the accident and all radiation readings were normal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [10 empty] | 3 | MI | TRA | [5 empty] | 0 | 2002-10-14
39281 | 0 | IDAHO DEPT OF ENVIRONMENTAL QUALITY |  |  |  |  | 2002-10-13 10:30 | 2002-10-13 14:40 | 2002-10-13 | TWO MOISTURE DENSITY GAUGES FOUND IN IDAHO RIVER Two local citizens found two Troxler moisture density gauges in the Portneous River located near Lava Hot Springs, Idaho, in Bannock County. The citizens, seeing the trifoil radiation symbol on one of the gauges, immediately contacted the Bannock County Sheriffs Office. The Sheriff's Office called the State of Idaho and two hazardous material qualified State Police Officers were dispatched to the scene. On-scene inspection of the two gauges by the Idaho Dept. of Environmental Quality Radiation Safety Officer revealed that one of the gauges is Model 2401, serial #2813. The Model number on the second gauge is not readable but both appeared to be same model. The serial number of the second gauge is 2744. Additional information found on the gauges indicated that they are 8.2 millicurie Cs-137, 50 millicurie Am-241:Be sources. A survey of the gauges indicated a 13 millirem/hour contact reading and less than 2 times background smear survey. The sources will be transported to a secure location for storage until the owner(s) can be located and the gauges returned. Local law enforcement will continue to investigate the circumstances of the recovered gauges. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-10-13
39280 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2002-10-13 11:10 | 2002-10-13 12:56 | 2002-10-13 | OFFSITE NOTIFICATION DUE TO THE DISCOVERY OF CONTAMINATED CLOTHING IN UNRESTRICTED AREA "At 1130 EDT on October 13, 2002, Florida Power and Light made an informational notification to the State of Florida (Department of Health, Bureau of Radiation Control) regarding the discovery of contaminated clothing in an unrestricted area. "On October 12, 2002 at 1915 EDT, Health Physics personnel identified low level fixed contamination on an individual's undergarment in his hotel room. The undergarment was confiscated. Measured activity was 20,000 disintegrations per minute consisting primarily of Cobalt 58, Cobalt 60 and Chromium 51. This resulted in a shallow dose equivalent of 0.0014 rem per hour averaged over a 10-centimeter square. Conservatively assuming 16 hours of exposure results in 0.022 rem, a very small fraction of the 50-rem annual shallow dose regulatory limit. No detectable activity was found on any other item during a complete survey of the hotel room and its contents. "This notification is being made pursuant to 10CFR50.72(b)(2)(xi) in that other government agencies have been notified of an event related to the health and safety of the public or on-site personnel." The licensee notified the NRC Resident Inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-13
39279 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2002-10-12 21:14 | 2002-10-12 23:24 | 2002-10-12 | NOTIFICATION OF OFFSITE AUTHORITIES OF FIRE IN 500 KV SWITCHYARD The licensee notified offsite state and county authorities of a fire in the south 500 KV substation. The fire occurred at 2030 on the #205 circuit breaker current transformer during electrical switching. The state and county were notified of an event of public interest due to multiple emergency vehicles responding to the substation. The fire was extinguished at 2120. The #205 circuit breaker remains out of service. The circuit breaker is on one of two ring buses, on the output side of the main generators, and are located about one-half mile from the plant outside the protected area. Plant electrical systems, including safety systems, were unaffected by the fire in the switchyard. The licensee notified the NRC Resident Inspector of the event. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-12
39278 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-10-12 04:45 | 2002-10-12 21:41 | 2002-10-12 | VALID (MANUAL) ACTUATION OF A SAFETY SYSTEM "October 12, 2002, at 0445 hours while performing UF6 sampling (Mode III), X-344 Feed and Transfer Building Operations personnel manually activated the X-344A Pigtail Line Isolation System (a Safety System) this was in response to an observed out-gassing from Autoclave #2 Sample Manifold. Operations were secured, and personnel evacuated the building per procedure. Emergency response personnel monitored the area for surface and airborne contamination with all samples less than detectable. Autoclave #2 was declared inoperable. This event is being reported as a valid actuation of a Safety System per [procedure] UE2-RA-RE1030, Appendix D, Section J.2." The licensee notified the NRC Resident Inspector of the event via voice mail and the DOE. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-10-12
39277 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-10-12 16:00 | 2002-10-12 17:15 | 2002-10-12 | SPURIOUS ACTUATION OF ONE (1) OFFSITE EMERGENCY NOTIFICATION SIREN The licensee was notified by local police, Lacey Township, NJ, that one (1) of the emergency notification sirens was sounding. The licensee confirmed the actuation and notified the Ocean County Sheriffs Office, who control the siren, and had them turn off the siren. The licensee has dispatched communications technicians to investigate the cause of the spurious actuation. The licensee notified the NRC Resident Inspector of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-12
39276 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-10-12 01:30 | 2002-10-12 08:02 | 2002-10-17 | ALLEGED FITNESS-FOR-DUTY QUESTIONED DUE TO SLEEPING ON WATCH. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR . ***** RETRACTED ON 10/17/02 AT 22:10 FROM J. BROWN TO A. COSTA ***** The licensee is retracting this event since proper security was maintained in the Owner Controlled Area as required by the Order. Notified R4DO (Pick) via email. | 54 | 100 | 0 | 54 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-10-12
39275 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-10-11 17:30 | 2002-10-12 07:55 | 2002-10-12 | FOR-CAUSE TEST FOR ALCOHOL Contract supervisor while entering the site was given an initial for cause test for alcohol followed by a confirmatory test. Person tested positive for alcohol on the confirmatory test. The person's access was revoked. Call the Headquarters Operation Officer for further details. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2002-10-12
39274 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-10-11 14:45 | 2002-10-11 19:29 | 2002-10-11 | NOTIFICATION TO OFFSITE AGENCIES DUE TO SULFURIC ACID RELEASE IN EXCESS OF LIMITS "This notification is being made under 10CFR50.72 (b)(2)(xi) for an event reportable to another government agency. The EPA National Response Center was notified at 1635, the Missouri Department of Natural Resources at 1645 and the Local Emergency Planning Commission at 1650 on 10/11/2002 of a release of sulfuric acid in excess of the 40CFR302.6 and 40CFR355.40 reportable quantities outside the plant boundary. At 0045 on 10/11/2002 a failure of the sulfuric acid feed system to the cooling tower basin was detected. The failure resulted in the release of 19,000 pounds (1300 gallons) of sulfuric acid outside the plant boundary. At 0050 on 10/11/2002 cooling tower blowdown was isolated and the release terminated, The total duration of the release was 7 hours, 27 minutes." The licensee notified the NRC Resident Inspector of the event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-11
39273 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-10-10 | 2002-10-11 18:10 | 2002-10-21 | AGREEMENT STATE REPORT: LOST OR STOLEN GERMANIUM 68 SOURCE A 10 millicurie Germanium 68 source was lost or stolen while in shipment by Federal Express (Fed Ex) from Cedar Rapids, IA to Burbank, CA. Fed Ex is attempting to locate the missing source. The State of California event number for this event is 101102. * * UPDATED AT 1442 EDT ON 10/21/02 BY KATHLEEN KAUFMAN TO FANGIE JONES * * * The source has been found, it was in the company's possession the whole time, just misplaced. Notified R4DO (Anthony Gody) and NMSS (Tom Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-10-16
39272 | 0 | C&D TECHNOLOGIES, INC. |  |  |  |  | 2002-10-11 | 2002-10-11 17:15 | 2002-10-11 | PART 21 DEFECT/NONCOMPLIANCE IDENTIFIED IN NOT-YET-INSTALLED BATTERY RACKS AT PRAIRIE ISLAND "In accordance with NSP's purchase order requirements and 10CFR21, I am notifying you that C&D Technologies, Inc. has identified what it believes to be a reportable event. "On purchase order #534, line item 4, an order was placed for two (2) Single Tier racks Part No RD00-900-16EP3. Subsequent to the fabrication of these racks it was observed that a series of welds which join the horizontal cross beam to the vertical member of the frame were not welded correctly. This may affect the seismic qualification of the rack. Our understanding is that these racks have not been installed. C&D is making arrangements to replace the nonconforming frames prior to the facility's scheduled outage. "Copies of each of the following referenced drawings were supplied to [the licensee] on 10/10/02; the single tier racks (RD00900- 16 EP3) are covered by the following drawings; "M121 14 (1) and (2) are page one and two of the same drawing. These are the outline drawings for the rack. Page 1 covers the Bill of Material and shows the RD02008E frame is used in rack assembly. "Ml 104 is the frame drawing for part number RD02008E. The critical part of the drawing in our discussion is the gusset support labeled Part No. RE-263 1 (Dwg K-7406). "Drawing M6228 (1) and (2) reflect the welding details for the racks. "Detail A on page 1 shows the flare bevel groove weld that is carried across the length of the horizontal cross bar as it is welded to the vertical member of the frame. This should be carried the full distance of the intersection. "Detail J on page 2 shows the addition of the gusset to reinforce the joint. This is placed over the flare bevel groove weld above and then fillet welded in place. "We have been advised that when our sub-tier supplier, Kim Manufacturing, manufactured the frames, they preassembled and clamped the vertical member, horizontal cross member and gusset in place. They performed a flare bevel groove weld on the exposed portion of the horizontal cross member, and fillet welded the remaining sections of the cross member and the gusset. The portion of the cross member which was hidden behind the gusset was not welded with the flare bevel groove weld as it should have been. "These racks represented the first two racks manufactured by Kim Manufacturing after transfer of this manufacturing function to Kim from C&D's Conshohocken facility. To ensure that the problem did not predate C&D's relationship with Kim we have interviewed the welder responsible for this function within Conshohocken and determined that he was aware of the requirement for a full flare bevel groove weld prior to the assembly of the gusset plate. The welder reports that this was standard practice in Conshohocken. No other racks will be affected by this defect. "Kim Manufacturing first notified C&D of the defect in the welds on the afternoon of 10/8/02. After analysis by C&D's engineering department on Wednesday (10/9/02) we determined that we no longer had design traceability to the original seismic qualification of this rack and that this event should be reported. Initial contact was made with NMC Quality Assurance through [a licensee representative] on (10/10/02)." The affected facility is the NMC Prairie Island Station. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-10-11
39271 | 0 | QUEENS MEDICAL CENTER |  |  |  |  | 2002-10-09 13:00 | 2002-10-11 16:32 | 2002-10-11 | MEDICAL MISADMINISTRATION: BRACHYTHERAPY UNDERDOSE TO TREATMENT SITE A patient undergoing brachytherapy treatment for cardiac restenosis received an underdose when it was determined that the strontium 90 source did not reach the intended treatment site. The source contained 16 source beads in the source train. The cause of the under dose is suspected to have been caused by blockage along the catheter but this has not yet been confirmed. An investigation will be conducted to determine the cause of the underdose. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 35.33 |  |  |  | 0 | 2002-10-11
39270 | 0 | US DEPT OF AGRICULTURE |  |  |  |  | 2002-10-02 | 2002-10-11 14:15 | 2002-10-11 | TROXLER GAUGE MISSING WHILE IN SHIPMENT On 10/10/2002, the licensee received notification from FedEx that their Troxler Gauge (Model No. 3321, Serial No. 446 with 10 millicuries Americium 241) could not be located. The gauge was being shipped via FedEx from Colorado on 10/2/2002 for arrival in California on 10/4/2002. FedEx stated that the last confirmed location was in FedEx's Denver facility, but did not know exactly when it was lost. FedEx stated that the shipping container handle with attached shipping papers had come loose from the container and was found on their conveyor belt, but not the container itself. FedEx is continuing to locate the gauge. The licensee has not made any other notifications. Contacted R1 DO (John White) and NMSS (Fred Brown) * * * UPDATE ON 10/11/02 AT 1608 EDT FROM DANIEL SHARP TO MIKE RIPLEY * * * Mr. Sharp reported that the missing Troxler gauge was located by the shipper, Fed Ex , in Memphis, TN. Fed Ex will resend the gauge to the intended recipient. Notified R1DO (John White) and NMSS (John Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-10-11
39269 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2002-10-11 09:25 | 2002-10-11 11:03 | 2002-10-11 | CHLORINE RELEASE IN TURBINE GENERATOR BUILDING "At 0925 EDT, a release of chlorine gas was noted from the hypochlorite area, and smell of chlorine gas was noted in the Turbine Generator Building. All personnel were evacuated from the Turbine Generator Building as a precautionary measure, and personnel were dispatched to determine the concentration of chlorine gas. "All the site of the source, chlorine gas concentration was 3ppm. Per the MSDS, the IDLH limit is 30 ppm. No Emergency Action Levels were entered. Additional samples are being taken in the Turbine Generator building prior to allowing unrestricted access into the area. Both Unit's Control Rooms were placed in the recirculation mode as a precautionary measure as well. "There were no injuries from this event. "The leak has been stopped." The chlorine gas was generated while acid cleaning the hypochlorite lines with muriatic acid. The acid caused the chlorine to come out as a gas. The lines are cleaned periodically to remove the calcium buildup on the lines. The licensee is investigating why chlorine gas was released this time when it was not released when the lines were cleaned in the past. The licensee surmised that they may have used a stronger concentration of muriatic acid this time. The NRC Resident Inspector was notified of this information call by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2002-10-11
39268 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-10-10 22:22 | 2002-10-10 23:10 | 2002-10-10 | RECEIVED A GROUP II ISOLATION DURING A PLANNED REACTOR SCRAM "Inserted Manual Scram for planned outage. Received a Group II isolation (containment isolation valves) on RWL [less than] 3". Lowest indication level -10". Group II isolation confirmed by STA." Plant shutdown to replace 3 SRVs. All system operate properly. The NRC Resident Inspector was notified of this event by the licensee.. | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-10-10
39267 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-10-10 20:16 | 2002-10-10 23:08 | 2002-10-10 | AUXILIARY FEEDWATER START ON PLANNED MANUAL REACTOR TRIP THIS 8 HOUR NOTIFICATION IS BEING MADE TO REPORT THAT SALEM UNIT 1 HAD EXPERIENCED A 13 AUXILIARY FEED WATER PUMP AUTO START. THIS AUTO START OCCURRED FOLLOWING A PLANNED MANUAL REACTOR TRIP FOR A SHUTDOWN FOR REFUELING. 11 & 12 AFW PUMPS WERE STARTED MANUALLY PRIOR TO THE TRIP PER PROCEDURE. THE 13 AFW PUMP STARTED POST TRIP DUE TO VALID STEAM GENERATOR LOW LEVELS WHICH ARE EXPECTED ON A REACTOR TRIP. THE STEAM GENERATOR LOW LEVEL AUTO START SET POINT WAS RAISED FROM 9% TO 14% EARLIER THIS YEAR BASED ON INDUSTRY EVENTS. THIS MADE THE 13 AFW PUMP AUTO START MORE LIKELY DURING A PLANT TRIP. POST TRIP MAIN FEEDWATER TO THE STEAM GENERATORS WAS ISOLATED DUE TO THE 'FEED WATER INTERLOCK' WHICH IS EXPECTED WITH A REACTOR TRIP. 13 AFW PUMP HAS BEEN SHUTDOWN BY PROCEDURE SINCE 11 & 12 AFW PUMPS ARE MAINTAINING ADEQUATE FEED FLOW. SALEM UNIT 1 IS CURRENTLY IN MODE 3. REACTOR COOLANT SYSTEM TEMPERATURE IS 547 DEGREES (F) WITH PRESSURE AT 2235 PSIG. THERE WERE TWO SHUT DOWN TECHNICAL SPECIFICATIONS IN EFFECT PRIOR TO THE TRIP; ONE ASSOCIATED WITH THE 11 & 12 AFW PUMPS INOPERABLE BY PROCEDURE DUE TO THEIR FLOW CONTROL VALVES BEING CLOSED PRIOR TO THE MANUAL REACTOR TRIP. THE SECOND SHUT DOWN TECHNICAL SPECIFICATION IN EFFECT WAS ASSOCIATED WITH THE 13 CONTAINMENT FAN COIL UNIT WHICH WAS TAGGED FOR REPAIR OF A LEAK. THE 11 & 12 AFW PUMPS ARE NOW OPERABLE. THE FOLLOWING MAJOR SECONDARY EQUIPMENT WAS TAGGED FOR MAINTENANCE: 13A CIRCULATING WATER PUMP, 12 HEATER DRAIN PUMP AND 11 CONDENSATE PUMP. THE NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS EVENT BY THE LICENSEE. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-10-10
39266 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-10-10 09:45 | 2002-10-10 10:29 | 2002-10-10 | 4 HOUR OFFSITE NOTIFICATION TO MD DEPARTMENT OF ENVIRONMENT A sample of drinking water taken during a routine test come up positive for Coliform(which is a bacteria). The levels are still low enough as not to preclude the use of this water for drinking. The licensee has contacted the MD Department of Environment to take and test additional samples. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-10
39265 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-10-10 00:08 | 2002-10-10 00:20 | 2002-10-10 | TECH SPEC REQUIRED SHUTDOWN DUE TO FAILURE TO MEET 2 OFFSITE POWER SUPPLIES "Susquehanna Unit 1 initiated a Technical Specification required shutdown due to failure to meet LCO 3.8.1 Action A.3 and the Notice of Enforcement Discretion (Docket No. 50-387), for operating with one inoperable offsite power supply. The offsite power supply was originally lost due to a Transformer failure on 10/3/02 at 0230 est. The NOED allowed Unit One to continue operation until 10/1 0/02 at 0230. The shutdown requirements of LCO 3.8.1 Action F (Mode 3 within 12 hours and Mode 4 within 36 hours) are being implemented. It has been determined that replacement activities of the transformer will not be completed in time to meet the NOED, and therefore shutdown of unit 1 has been initiated as of 0008. "This event is a Technical Specification required shutdown, and is reportable as a four hour ENS Notification under 10 CFR 50.72(b)(2)(I)." The Licensee has notified the NRC Resident Inspector. ***UPDATE 1113 EDT 10/10/02 ART FITCH TO MIKE NORRIS*** "At 09:35 hours on 10/10/2002 transformer T-20 was successfully connected to start-up bus 20 restoring the second offsite power source. This allowed Unit 1 to exit LCO 3.8.1 Action F and LCO 3.8.1 Action A.3 and the Notice of Enforcement Discretion (Docket No. 50-387). Power reduction was halted at 31% and plans are currently underway to restore Unit 1 to 100% power. "Unit 2 continues in Mode 4." The Licensee has notified the NRC Resident Inspector and plans a press release. Notified R1DO (White). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-10-10
39264 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-10-09 13:59 | 2002-10-09 17:12 | 2002-10-09 | EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE "At 1518 hours on October 9, 2002 Indian Point Unit 2 commenced a controlled shutdown per T/S 3.0.1. T/S 3.0.1 was entered because Emergency Diesel Generators (EDG) 21 and 23 were declared inoperable. EDG 23 was declared inoperable at 2152 hours on October 8, 2002 due to failure of monthly test. EDG 21 was declared inoperable at 1359 hours on October 9, 2002 due to indications of jacket water in the lube oil system. EDG 23 was declared operable at 1635 hours on October 9, 2002 following corrective actions and testing at which time T/S 3.0.1 was exited. They think EDG 21 may have a cracked engine head. The reactor power reduction was stopped at 97 percent, but the are planning to return to 100%. The to the Public Service Commission was informed of the reason for the downpower at 1610 hours on October 9, 2002." The NRC Resident Inspector was notified. | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-10-09
39263 | 0 | ST PATRICK HOSPITAL |  |  |  |  | 2002-08-30 | 2002-10-09 16:38 | 2002-10-09 | MEDICAL MISADMINISTRATION A patient was receiving a gynecological implant of Cs-137 which had the incorrect activity entered into the computer. The calibrated activity was inadvertently entered instead of the current activity. The patient was also receiving external beam therapy from a linear accelerator along with the Cs-137 implant. With the incorrect data being entered into the computer, the patient received a total dose(external and implant) which deviated below the prescribed dose by approximately 16%. The implant dosage, however had greater than a 20% deviation less than the prescribed dose. This medical misadministration was discovered on 10/09/02 @ 1620 MT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | MT | HOS |  | 35.33 |  |  |  | 0 | 2002-10-09
39262 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2002-08-16 02:54 | 2002-10-09 15:30 | 2002-10-09 | INVALID SYSTEM ACTUATION DUE TO LOSS OF RPS BUS "A" "On August 16, 2002 at approximately 0254 hours, a loss of Reactor Protection System (RPS) Bus A occurred while operators were attempting to reset a half-scram on the A2 logic channel of the RPS. The A2 logic reset attempt was required in accordance with a surveillance test procedure that was in progress, PPM OSP-RPS-Q402, MSIV Closure Scram Functional. Upon loss of RPS Bus A, control room operators entered Abnormal Procedure ABN-RPS, Loss of RPS, and an operator was dispatched to investigate the problem. "The operator investigating the problem discovered that the Motor Generator Set (RPS-MG-A) that supplies RPS Bus A was running with both of its electrical protection assemblies (EPAs) in the tripped position. In accordance with procedure ABN-RPS, operators transferred RPS Bus A to its alternate power supply and then reset the half-scram and associated containment outboard isolations. The operators then exited PPM OSP-RPS-Q402. The follow-up investigation found that the loss of the RPS Bus A was due to a trip of the RPS-MG-A output breaker (RPS-MG-CB1) on over-voltage. The output breaker trip caused both downstream Electrical Protection Assemblies (RPS-EPA-3A and RPS-EPA-3C) to trip. This is the expected and required response for RPS-EPA-3A and RPS-EPA-3C." The loss of power to RPS Bus A had the following effects on the plant: An actuation of RPS trip system A (Half-Scram), Main Steam Line Radiation Monitors A and C lost power; a trip of the Balance of Plant isolation logic in control room relay Cabinet RC-1; an outboard primary containment isolation signal was received by the following (valves closed or were already closed): Main Steam Line Drain Valves, Reactor Water Sample Valve, Drywell Floor and Equipment Drain Isolation Valves, Residual Heat Removal (RHR) Discharge to Radwaste and Heat Exchanger Sample Isolation Valves, RHR Shutdown Cooling (SDC) Reactor Head Spray Isolation Valve, SDC Return Valves, Reactor Water Cleanup (RWCU) Suction Valve. All of these plant equipment responses were as expected and per plant design. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-10-09
39261 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-10-08 07:30 | 2002-10-09 11:33 | 2002-10-09 | AGREEMENT STATE REPORT INVOLVING LOST TROXLER GAUGE At 1133 EDT, the Illinois Dept. of Nuclear Safety (IDNS) reported that a materials licensee reported that a Troxler Gauge (Model 3440, S/N 24468 with 8 millicuries Cesium-137 and 40 millicuries Americium-241) was lost from the back of a pickup truck while being transported between 7:30 am and 8:00 am on 10/8/02. The licensee reported that the worker picked up the gauge at the licensee's facility, then drove to his residence, and then returned to the licensee's office where he found the gauge missing from the back of the pickup truck. The worker reported to the RSO that the chain and lock for the gauge was lost the previous day (10/7/02). The licensee stated the cause for the loss to be a failure to secure the gauge in the truck. The licensee and IDNS personnel re-traced the route twice and did not find the gauge. The licensee notified the police departments for the cities of West Chicago, Naperville, and Warrenville, IL, NRC Region 3, Troxler, Inc and the Illinois Department of Transportation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-10-14
39260 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-10-09 03:07 | 2002-10-09 03:31 | 2002-10-09 | UNUSUAL EVENT DECLARED DUE TO FIRE IN PROTECTED AREA LASTING GREATER THAN 10 MINUTES "Unusual event was classified based on a fire in the protected area lasting > 10 minutes. The fire started in the motor of the 'B' circulating water pump. It was 'contained' to that location (the CW pump motor). Motor [is]still smoldering, [but] it is controlled and contained. Steam Generator Blowdown system isolated due to high flash tank level. Multiple rad monitors went into alarm due to voltage surge." The NRC Resident Inspector will be notified. The Licensee reported that no offsite assistance was requested and that the State (NH) was notified. ***UPDATE JIM HILL TO JOHN MacKINNON 0614 EDT 10/9/02*** The Unusual Event was Terminated at 0547 EDT. The Licensee has notified the NRC Resident Inspector and the State(NH). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-10-09
39259 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-10-08 13:30 | 2002-10-08 16:57 | 2002-10-08 | THE CENTRAL CONTROL ROOM WALL IDENTIFIED AS BEING IN NON-CONFORMANCE WITH DESIGN DRAWINGS Indian Point Energy Center (Unit .2) is making an eight hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(v)(D). The Central Control Room (CCR) south masonry wall was identified as inoperable because a seismic event could cause breaches in the wall that could prevent the Control Room Air Filtration System from performing its design function of limiting operator dose. The as found condition of the CCR south wall was identified as being in non-conformance with the design drawings. At the top portion of the wall, just above the upper steel channel beam, there are steel angles welded to the lower cord of the CCR roof truss that extend about 1.5 feet towards the south wall. A shelf angle is welded to the ends of the angles that support part of the south wall. This as found condition creates a seismic interaction with the superheater building which transfers load to the south wall through the steel support. Initial analysis indicates that the CCR south wall will remain structurally intact except for several areas in the upper 6 feet of the wall where localized failure could occur. The analysis indicates these localized failures will not cause damage to safety related equipment but may cause loss of the CCR pressure boundary. Corrective action has been initiated to repair the south masonry wall locally and cut the steel causing building interaction between the superheater and control buildings. Corrective action is expected to be complete within approximately 24 hours. Loss of the CCR pressure boundary renders the Control Room Air Filtration System incapable of performing its safety function because it relies on the pressure boundary to limit in-leakage. The Control Room Air Filtration System was declared inoperable and the action statement of Technical Specification 3.3.H was entered at 1330 hours. The action statement allows 3.5 days of continued operation. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-08
39258 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2002-10-05 | 2002-10-08 15:20 |  | DEGRADATION OF RCS PRESSURE BOUNDARY AT ARKANSAS NUCLEAR ONE UNIT 1 "With the Reactor Coolant System (RCS) In Mode 3 (Hot Standby) conditions at the start of a scheduled refueling outage on October 5, 2002, a leaking weld was discovered at the connection of a drain line to a High Pressure Injection (HPI) line inside the Reactor Building. The leak rate was approximately 0.2 gpm. The immediate evaluation concluded that this leak did not result in the HPI System being inoperable. Subsequent evaluation of the condition on October 8, 2002. determined that the leak was from the RCS pressure boundary. Between the RCS and leak location are a normally open manual isolation valve and a check valve. Weld repair is complete. This condition is being reported as a serious degradation of a principal safety barrier in accordance with 10CFR50.72(b)(3)(ii)(A)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-10-08
39257 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-29 05:02 | 2002-10-08 09:03 | 2002-10-08 | RPS ACTIVATION WHILE SHUTDOWN DUE TO LO-LO STEAM GENERATOR WATER LEVEL "On September 29, 2002, McGuire Nuclear Station experienced an inadvertent actuation of the Unit 1 reactor protection system (RPS) while the unit was shutdown for a refueling outage. This occurred when the "A" and "B" train main reactor trip breakers opened as a result of an unplanned low-low steam generator level reactor trip signal. Further evaluation determined that the reactor trip signal which opened the reactor trip breakers was an invalid signal since it was not initiated in response to plant conditions or parameters satisfying the requirements for initiation of the RPS safety function. Therefore, this represented an invalid actuation reportable per the requirements of 10 CFR 50.73(a)(2)(iv)(A). However, as per 10 CFR 50.73(a) (1), McGuire is providing a telephone notification of this invalid actuation instead of submitting a written LER. The following additional information is being provided as part of the telephone notification of this event: -The Unit 1 RPS system including the "A" and "B" train main reactor trip breakers functioned successfully and completely." The Licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-10-08
39256 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-10-08 04:21 | 2002-10-08 07:22 | 2002-10-08 | T. S. REQUIRED SHUTDOWN DUE TO PRESSURE BOUNDARY LEAKAGE "During drywell entry prior to D3R17 refueling outage discovered primary system leak on 3A Reactor Recirculation pump discharge loop flow instrument line, this required entry into T.S. 3.4.4 which requires that there is No pressure boundary leakage. This requires that the unit be in MODE 3 in 12 hours and MODE 4 in 36 hours, which is a TS required shutdown." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode3: Power Operation; FMode3: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2002-10-08
39255 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2002-10-07 17:15 | 2002-10-07 19:02 | 2002-12-04 | PLANT FAILED THEIR INTEGRATED LEAKRATE TESTING During the normal outage integrated leakrate testing, it was determined the total primary containment leakage rate is in excess of allowable leakage rate. The calculated leakage rate is 216.55 scfh while the allowable leakage rate is 192.126 scfh. Repair work on the valves has been initiated. The NRC Resident Inspector will be notified. * * * RETRACTION FROM DENNIS MAY TO HOWIE CROUCH ON 12/4/02 AT 1430 EST * * * "BASIS FOR RETRACTION: "An NRC 8-Hour Non-Emergency Event Notification (#39255) was conservatively made following MSIV [Main Steam Isolation Valve] leak rate testing based upon exceeding the combined local leak rate test acceptance criterion based on a calculated maximum pathway leak rate pending further review by the Leak Rate Testing (Appendix "J") Coordinator. "NUREG 1022, Rev. 2 provides guidance for the evaluation of containment leak rate test data under the 50.72(b)(3)(ii)(A) reporting criteria that specifies the use of the total containment as-found minimum pathway leak rate. "The Technical Specification limit for the combined local leak rate test (Type B and C test) acceptance criterion is less than or equal to 0.6 La (192.126 scfh). The combined local leak rate test, calculated on a minimum pathway basis was 112.807 scfh. This value is less than the Technical Specification limit and therefore is not reportable in accordance with 10CFR50.72(b)(3)(ii)(A) or 50.73(a)(2)(ii). Therefore, ENS Event Number 39255, made on 10/07/02, is being retracted." Headquarters Operations Officer notified R1DO (Michele Evans). The licensee will notify the NRC Resident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-10-07
39254 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2002-10-07 05:07 | 2002-10-07 12:38 | 2002-10-07 | BORIC ACID CRYSTALS DETECTED IN THE AREA OF THE CONTROL ROD DRIVE MECHANISM NOZZLE On October 7, 2002, following shutdown for a scheduled refueling outage, Arkansas Nuclear One (ANO) Unit 1 personnel performed a routine visual inspection of the Reactor Vessel (RV) head area per NRC Generic Letter 88-05. This inspection revealed a small nodule of boric acid crystals in the area of Control Rod Drive Mechanism (CRDM) Nozzle #56. The boric acid residue was detected on the down hill side of the nozzle (extending 180 degrees In the nozzle annulus area), with a small nodule of boric acid at the most downhill point. Prior to unit shutdown, on October 4. the total unidentified Reactor Coolant System (RCS) leak rate was determined to be significantly less than the 1 gpm allowed by Technical Specifications. This indication is consistent with industry experience associated with Primary Water Stress Corrosion Cracking (PWSCC) in similar components that has been evaluated as part of the NRC Generic Letter 97-01 response. These cracks do not pose a significant safety risk during plant operation, ANO plans to perform repairs during the current outage. Since the visual inspection indicates leakage through the Reactor Coolant System pressure boundary, this condition is being reported as a non-emergency eight-hour report in accordance with 10CFR50.72(b)(3)(II), degradation of a principal safety barrier. Reactor vessel head inspection is continuing. Any additional findings will be reported as an update to this notification. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-10-07
39253 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-10-07 09:35 | 2002-10-07 12:14 | 2002-10-07 | AUTOSTART OF EDG FOLLOWING TRANSFER OF "1E" SWITCHGEAR TO ALTERNATE POWER SUPPLY "During Design Modification testing in the switchyard, an unplanned contact picked up which de-energized the train 'C' electrical switchgear and the '1E' switchgear to transfer to the Alternate Power (-2 bkr). Core Alterations were in progress and were suspended." Train "C" consists of four (4) electrical buses; 1A1, 1A2, 1A3 and 1A4. The -2 bkr transferred power from the 1EA1 to the 1EA2 bus which is energized from the XST1 transformer. During the slow transfer, the operating Spent Fuel Pool (SFP) pump and RHR "B" train were de-energized. There was no observed increase in SFP or appreciable increase in RCS temperatures. RHR cooling was re-established in approximately eight (8) minutes. Emergency Diesel Generator "1-02" autostarted on low voltage but did not supply power to the affected 1E buses. The cause of the EDG autostart is under investigation. Core Alterations are suspended pending completion of the investigation. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-10-07
39252 | 0 | ANVIL CORPORATION |  |  |  |  | 2002-10-04 10:30 | 2002-10-07 12:05 | 2002-10-07 | INFORMATION REPORT INVOLVING A DAMAGED GUIDE TUBE INCIDENT "[Radiographer #1 and Radiographer #2] received permission to perform x-ray on small branch connections in the tank dike of Tank 17 at the ExxonMobil refinery in Billings, MT. They had an additional two-inch post stress x-ray. They x-rayed three small branch connections at seven minutes and one at three minutes. They then set up a two-inch spool by attaching it to a pipe support and made their first exposure. "The second exposure was set up on and made at 10:30am. When the exposure was complete [Radiographer #2] tried to crank the source into the shielded position. The crank would only turn three times before stopping. [Radiographer #1] explained later that the pipe support appeared to be set in the asphalt that it was sitting on. This turned [out] not to be the case. The pipe support was only partly covered by asphalt and became dislodged during their second exposure. "[Radiographer #2] stated that the pipe stand fell approximately ten seconds before the exposure was complete. "They then went into emergency procedures. "They increased their boundary sizes and contacted the RSO Kathy Turner. Amersham 660B Camera No. B3125 Source No. 05416B 51 Curies "[Radiographer #1] has been a radiographer for approximately four years. [Radiographer #2] has been a radiographer for three months." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | MT | OTH | GEN |  |  |  |  | 0 | 2002-10-07
39251 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-10-06 16:50 | 2002-10-06 18:45 | 2002-10-06 | 4-HOUR REPORT PURSUANT TO 10 CFR 50.72(b)(2) PER LICENSEE ADMINISTRATIVE REQUIREMENTS "Results of the steam generator eddy current testing of the hot leg top of the tube sheet rotating plus point coil program indicated that greater than 1% of the tubes are defective in Steam Generator #2. "Technical Specification category C-3. 5.6.10." The licensee informed the NRC resident inspector. * * * UPDATE 2326EDT ON 10/6/02 FROM DENNIS REDINGER TO S.SANDIN * * * The licensee is updating this report to include the following additional SG inspection findings for Steam Generators #3 and #4: "Results of the steam generator eddy current testing of the hot leg top of the tube sheet rotating pancake plus point coil indicates that greater than 1% of the tubes are defective in CPSES Unit 1 Steam Generators # 3 and Steam Generators # 4. "CPSES Technical Specification states that, '[R]esults of steam generator tube inspections which fall into Category C-3 shall be reported to the Commission pursuant to 10 CFR 50.72(b)(2) within four hours of initial discovery, and in a report within 30 days and prior to resumption of plant operation.' "Note: "We understand that CPSES Technical Specification is conservative with respect to timing of reporting this condition; and that the current 10 CFR 50.72 requirements are eight hour notification. However, until the license amendment (which is in process) is issued, CPSES will continue to report this condition within four hours." The licensee informed the NRC resident inspector. Notified R4DO(Jones). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT | DEGRADED CONDITION |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW |  |  | 50.72(b)(3)(ii)(A) |  |  | 0 | 2002-10-06
39250 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2002-10-06 11:30 | 2002-10-06 18:00 | 2002-10-11 | RCIC SYSTEM DECLARED INOPERABLE Following reactor core isolation cooling system injection check valve surveillance, the check valve apparently did not fully close. This resulted in high pump suction pressure trip which would have prevented further system operation. The licensee conservatively declared the RCIC system inoperable and entered Tech Spec LCO 3.5.G.2, a 14 day action statement. Shortly afterwards the plant pressure was dropped to less than 150 psig as part of normal plant shutdown to refueling, this takes the plant out of the Tech Spec action statement as it no longer applies. The licensee is conducting an investigation of the problem with RCIC injection check valve. Repairs will be completed prior to plant restart. The licensee notified the NRC Resident Inspector and the State of Vermont. * * * RETRACTION FROM Andy Wisniewski on 10/11/02 at 1428 EDT to Gerry Waig * * * "BASIS FOR RETRACTION: NRC Event Notification 39250 was made with the concern that this condition may have rendered the Reactor Core Isolation Cooling (RCIC) system inoperable due to a 'high pump suction pressure trip'. The RCIC pump does not have this aforementioned trip device. Therefore, the predicament that Operations has been confronted with for declaring the RCIC system inoperable may be more aptly stated as; 'Could the leakage that occurred past the discharge check valve, after the RCIC system run, have over-pressurized the RCIC system suction piping and caused the system to be unavailable for service if called upon for a 'Loss of All AC Event'. A team of engineers was assembled to determine the extent of this condition that resulted in the completion of an Operability Determination on 10/08/02 by the RCIC System Engineer, concluding that the RCIC system remained operable based upon the following two facts: 1. The RCIC suction line relief valve lifts at 150 psi. 2. The outer pump discharge valve, combined with a pressure switch, provides an additional barrier of defense. The pressure switch actuates at 74 psi and causes the RCIC PUMP SUCT PRESS HI alarm in the control room. The alarm response procedure directs operators to close the isolation valve that is downstream of the discharge check valve. "Additionally, the leakage has been determined to be 'slight' and well within the capacity of the relief valve, based upon system performance and observation of the event as it occurred. The RCIC system would have performed it's specified safety function during this condition if required. "Therefore, ENS Event Number 39250, made on 10/06/02, is being retracted." The licensee notified the NRC Resident Inspector of this retraction. The R1DO (John White) was notified by the NRC Headquarters Operations Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-10-06
39249 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-10-05 11:25 | 2002-10-05 14:16 | 2002-10-05 | OFFSITE NOTIFICATION DUE TO A FREON RELEASE IN THE TURBINE BUILDING "At 0210 today, 10/5/02, we had a failure of a seal on our mechanical refrigeration unit. This resulted in 5,250 lbs of freon, R-12, being released to the environment. This required reporting to Federal, State and Local agencies that a release of greater than 5,000 lbs had occurred in less than 24 hours. The release ended at 0454 today due to the contents had completely blown down. - The National Response Center was notified at 1125 today - The Virginia Emergency Services Operations Center was notified at 1130 today - The Virginia State Dept. of Environmental Quality and the Local Emergency Planning Coordinator will be notified by the Virginia Emergency Services Operations Center. "Due to these offsite notifications we are making this 4 hour report." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-05
39248 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2002-10-04 22:14 | 2002-10-05 00:30 | 2002-10-05 | TURBINE TRIP CAUSED REACTOR TRIP DURING SHUTDOWN IN PREPARATION FOR REFUELING OUTAGE "A power reduction was in progress for entry into refueling outage 1R17. A main turbine overspeed trip test was being conducted which resulted in a turbine trip which then caused a reactor trip on RPS". All rods were automatically inserted into the core with no problems. The trip occurred from 42% reactor power. No safety systems were actuated and all plant systems functioned as designed. The Resident Inspector was notified. | 0 | 0 | 0 | 42 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-10-05
39247 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2002-10-04 | 2002-10-04 12:35 | 2002-10-04 | FUEL SUPPORT SIDE ENTRY ORIFICE LOSS COEFFICIENT IN CORE MONITORING SYSTEM DATABANK "This letter provides notification of a Reportable Condition under 10CFR 21.21(d) for Clinton and Perry 1. The basis for this conclusion is the data used for the fuel support side entry orifice (SEO) loss coefficient in the core monitoring system supplied by GE Nuclear Energy (GE)/Global Nuclear Fuel (GNF). Other plants that have a similar geometry, but for which GE/GNF did not provide the core monitoring system (Grand Gulf and River Bend) have also been informed of this issue. "The core support structure in a BWR/6 affects the fuel support casting SEO loss coefficient. Bundles may be adjacent to zero, one, or two core support beams depending upon their location as illustrated in Figure 1. The SEO loss coefficient depends upon the number of adjacent core support beams. "The core monitoring system in the affected plants uses an average SEO loss coefficient for all of the central bundles, and a separate average value for all of the peripheral bundles. This was previously evaluated for GE/GNF 8x8 fuel designs and found to be acceptable. Recent calculations have shown that the Critical Power Ratio (CPR) response for newer GE/GNF fuel designs are more sensitive to the reduced flow in bundles that are adjacent to two core support beams (which have the highest loss coefficient). Thus, the core monitoring system over predicts CPR for these bundles, and thereby, may under predict the margin to the Operating Limit Minimum CPR (OLMCPR). The CPR over prediction is approximately 0.01 in CPR, which reaches the threshold for a reportable condition on a Technical Specification Safety Limit. In actual practice, plants maintain significantly more than 0.01 CPR margin to the OLMCPR, so MCPR Safety Limit protection is not threatened." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-10-04
39246 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-10-04 10:45 | 2002-10-04 12:26 | 2002-10-07 | OFFSITE NOTIFICATION DUE TO SMALL FIRE IN TURBINE BUILDING "Press release issued to local media at 0145 CDT 10/4/2002. Press release described response to an electrical component fire that occurred at 0650 CDT 10/4/2002. The fire occurred in a cathodic protection transformer located in the turbine building. The plant fire brigade responded to the scene. Power to the component was secured which extinguished the fire. Plant operation was not affected. The fire was declared out at 0700 CDT 10/4/2002." The press release was issued to the local paper - Coffey County Republican and local radio KSNP. The New Strawn Fire Department was called, however, the fire was extinguished before they arrived. The licensee informed state/local agencies and the NRC resident inspector. * * * UPDATE ON 10/07/02 @ 1321 BY YUNK TO GOULD * * * Correct time of press release to local media was 1045 CDT on 10/4/2002 not 0145 CDT. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-10-04
39245 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2002-10-02 13:00 | 2002-10-03 14:40 | 2002-10-03 | REMOVABLE CONTAMINATION EXCEEDING LIMITS FOUND ON EMPTY CONTAINERS DELIVERED TO SITE "On Wednesday, October 2, 2002, Nuclear Management Company, LLC (NMC) received a shipment of two empty sea-land containers from U.S. Ecology at the Kewaunee Nuclear Plant. These containers were shipped by R&R Trucking of Duenweg, MO. Although these containers were empty, NMC conservatively surveyed the outside of the containers. During this survey of the containers, a masslin contamination check identified some external contamination. Further and more specific sampling techniques resulted in identifying contamination levels of 24,700 DPM/100 sq. cm. in one location on the underside of the container. Department of Transportation acceptance limits identified in 49 CFR 173.433 for this type of container are 22,000 DPM/100 sq. cm. Because these containers were considered empty, they were unlabeled. Nevertheless, because NMC identified removable radioactive surface contamination in excess of the limits of 10 CFR 71.81(i) which refer to the DOT limits of 49 CFR 173.433, this event is immediately reportable to the NRC Operations Center in accordance with 10 CFR 20.1906(d). In accordance with 10 CFR 20.1906(d), the radiation safety officer at U.S. Ecology was notified of the conditions found when the shipment was received. "Because, the area of contamination was on the underside of the container, it was not accessible during transportation. The container was secured and posted as necessary to control the contaminated areas within an RCA at the plant. NMC surveyed the flatbed trailer upon which the containers were shipped, and no contamination was found. Based on this, the trailer was released. "Additionally, the NRC senior resident inspector and the regional RP inspector were notified." UPDATE: "The correct time of discovery was 1300 CST. The U.S. Ecology contact was [ . . .]. The dose rate instrument was an RO-20 (handheld, portable, ionization chamber capable of detecting both beta end gamma radiation). The initial contamination survey equipment was a frisker (thin-end window GM detector). The contamination levels of 24,700 DPM/100 sq. cm. was found using a Baird alpha, beta, fixed geometry scalar/counter." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SURFACE CONTAM LEVELS > LIMITS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 20.1906(d)(1) |  |  |  | 0 | 2002-10-03
39244 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-10-01 09:30 | 2002-10-03 09:35 | 2002-10-03 | MISSING CPN GAUGE The Licensee had a CPN moisture density gauge in a box of his ATV he uses for transport in the agriculture fields. He stopped at a porta-potty on Duncan Road near Stockton, CA. When he came out of the porta potty the gauge was missing. The gauge is a CPN Hydroprobe model No. 503DR. Serial No: H36107151. Gauge contains 10 millicuries of Cs-137 and 30 millicuries of Am-241. The Licensee will inform the local police of the missing gauge and he will run an offer of a reward in a local newspaper for the recovery of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-10-08
39243 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-10-03 01:50 | 2002-10-03 08:12 | 2002-10-03 | POTENTIAL UNABLE TO SAFE SHUTDOWN DUE TO CORE FLOW INDICATION OUT OF TOLERANCE "During performance of procedure PNPS 9.17 Core Flow Evaluation a discrepancy in the 'A' Loop core flow between EPIC and RPS indication was noted. This caused Pilgrim to investigate and perform a calibration of the 'A' RPS Flow converter. The initial 'as found' set points were out of tolerance per the procedure. Adjustments were attempted but we were unable to calibrate the flow converter. The 'A' Flow Converter was declared inop and a half-scram signal was maintained on the 'A' RPS channel. Pilgrim is continuing its efforts to replace and/or repair the 'A' Flow converter. It is unknown at this time if the as found flow indications were acceptable to fulfill its safety function." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-10-03
39242 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-10-03 02:30 | 2002-10-03 05:15 | 2002-10-03 | MANUAL REACTOR SCRAM DUE TO LOSS OF POWER TO RECIRC PUMPS. "At 0230 on 01/3/02, the control room was notified that there was a fire at Startup Transformer T-20. Unit 2 was in the process of starting up and was at a pressure of 435 psig and range 8 on the IRMs. T-20 lost power which caused the recirc pumps on Unit 2 to trip. With no recalculation while in Mode 2, Tech Specs requires the unit to be in Mode 3 within 12 hours. Operations placed the mode switch to shutdown. All rods were inserted. Unit 1 was at 100% power at the time and continued to operate. The Station Fire Brigade was activated. The deluge system extinguished the fire in 10 minutes. An Unusual Event was declared under EAL 14.1 at 03:15. "This is a 4 hr Non-Emergency notification under 10 CFR 50.72(b)(2)(I) for a Tech Spec required shutdown and a 4 hr Non-Emergency notification under 10 CFR 50.72(b)(2)(iv)(B) for an RPS actuation." A press release will be made. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2002-10-03
39241 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-10-03 03:15 | 2002-10-03 03:33 | 2002-10-03 | UNUSUAL EVENT DECLARED PER EAL 14.1- FIRE LASTING GREATER THAN 15 MINUTES & ACTIVATION OF THE FIRE BRIGADE. "At 0230 on 10/3/02, the control room was notified that there was a fire at Startup Transformer T-20. Unit 2 was in the process of starting up and was at a pressure of 435 psig and range 8 on the IRMs. T-20 lost power which caused the recirc pumps on Unit 2 to trip. With no recirculation, operators placed the mode switch to shutdown. All rods were inserted. Unit 1 was at 100% power at the time and continued to operate. The Station Fire Brigade was activated. The deluge system extinguished the fire in 10 minutes" Non-Vital power is being supplied to T-20 Startup Transformer Bus from Startup Transformer T-10 via cross tie breaker. Offsite fire department was called but was not needed. All Emergency Core Cooling systems and the Emergency Diesel Generators are fully operable if needed. The Unusual event will be terminated after an assessment of what caused the Startup Transformer T-20 fire/failure. The licensee notified the State of PA, surrounding counties and the NRC Resident Inspector of the declaration of an Unusual Event. ***UPDATE ON 10/03/02 AT 0605ET BY SID MORGAN TAKEN BY MACKINNON *** EAL 14.1 was exited and the Unusual Event terminated at 05:52 ET. Unusual event was terminated after damage assessment of Startup Transformer T-20 was completed. R1DO (Pete Esselgroth), NRR EO (Bill Dean) & FEMA (Sweetser) notified. The NRC Resident Inspector was notified of the termination of the Unusual event by the licensee. | 100 | 0 | 0 | 100 | 1 | 0 | -1 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Startup |  | Power Operation | Hot Shutdown |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-10-03
39240 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2002-09-26 | 2002-10-02 17:58 | 2002-10-02 | 24 HOUR CONDITION OF LICENSE REPORT The following is a facsimile received from the Region 4 Duty Officer. "This facsimile is being sent to confirm a telephonic report of October 1, 2002 that was made pursuant to the Columbia Generating Station Operating License (NPF-21) condition 2.F, which states: 'With the exception of 2.C(2) the licensee shall report any violations of the requirements contained in Section 2.C, and E of this license within 24 hours by telephone and confirm by telegram, mailgram, or facsimile transmission to the NRC Regional Administrator, Region V or that administrator's designee, no later than the first working day following the violation, with a written followup report within 14 days. 'The subject of the report is the discovery that all the provisions of the Commission-approved physical security plan were not maintained in effect for a period of approximately 2 hours on September 26, 2002 when personnel gates to the independent Spent Fuel Storage Installation (ISFSI) protected area were unlocked, open, and unattended. During this time, the operable ISFSI intrusion detection system did nor detect any entry into the ISFSI protected area. A written follow-up report regarding this issue will be submitted on or before October 15, 2002.' | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW | [5 empty] | 0 | 2002-10-02
39239 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-10-02 14:53 | 2002-10-02 17:24 | 2002-10-02 | REACTOR SCRAM DUE TO TURBINE TRIP FROM A LOSS OF CONDENSER VACUUM "On Wednesday, October 2, 2002 at 1453 hours, the reactor scrammed from 100% power. Condenser vacuum was lost when circulating pump No. 2 failed. Condenser pressure went above the turbine trip setpoint. The main turbine, tripped and the reactor scrammed. All rods fully inserted. "Reactor level is stable in the normal band (197 inches). Reactor Level 3 (173 inches) was reached and level was restored to normal. "No ECCS systems actuated. No safety/relief valves opened. All systems functioned normally. Reactor level is being maintained using one reactor feed pump through the startup level control valve. Cool down is through the main turbine bypass valves to the main condenser. The following 'Level 3' isolations occurred as expected: Group 4 - RHR Shutdown Cooling and Head Spray Group 13 - Drywell Sumps Group 15 - Traversing Incore Probe Systems "NRC Senior Resident Inspector has been notified. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Any event that results in actuation of the reactor protection system (RPS) when the reactor is critical, and 10 CFR 50.72(b)(3)(iv)(A), Specified System Actuation." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2002-10-02
39238 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2002-10-02 13:44 | 2002-10-02 14:20 | 2002-10-29 | 1 HOUR SAFEGUARDS REPORT Attempted introduction of contraband into controlled access area. The NRC Resident Inspector was notified. Contact Headquarters Operations Officer for additional details. *** UPDATE ON 10/29/02 AT 1256ET BY AARON BLESS TAKEN BY MACKINNON**** "After further review of our procedures and the regulatory requirements of 10 CFR 73 Appendix G the licensee has determined the issue of the contraband which was discovered .. .. Located a significant distance from the protected area, on October 2, 2002, to be not reportable. All information was provided expeditiously to the NRC Operation Center during and after the discovery of the contraband , however the event notification is being rescinded due to the fact that the contraband was never introduced or attempted to be introduced into the protected area, material access area, vital area, or transport. The NRC Security Safeguards Staff of Region III has been informed of the plans to rescind the event notification." R3DO (Jim Creed) notified. "The NRC Resident Inspector has been notified of the update." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | SAFEGUARDS REPORTS |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) | 73.71(b)(1) |  |  | 0 | 2002-10-02
39237 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-09-24 06:00 | 2002-10-02 10:19 | 2002-10-02 | STOLEN AND RECOVERED CPN MOISTURE DENSITY GAUGE "The user stated, he picked up gauge from the temporary storage location at approximately 4:30am. He blocked, braced and locked the case to the bed of his truck and drove back to his residence to make some phone calls. When he came out to the truck between 7:30 and 8am the chain had been cut and the gauge was gone. He contacted the police and the ARSO and also talked to neighbors to see if anyone had seen anything suspicious. The ARSO contacted the RHB at approximately 10:15am to report the theft. At 11 am the ARSO contacted us to let us know that the gauge had been recovered. The gauge was found in a park approximately 2 blocks from where the gauge was stolen. The gauge was still in the case and the gauge handle was still locked. The gauge was returned to the office where a leak test was performed." Gauge stolen and recovered was a CPN Model # 501 gauge which contains 10 millicuries of Cesium-137 and 50 millicuries of AM241:Be. Leak test result (in microcuries) was less than 0.005. State of California incident number for this event is XCA 251. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-10-07
39236 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2002-10-01 | 2002-10-01 20:24 | 2002-11-18 | PART 21.21 REPORT INVOLVING STABILITY OPTION III "Subject: Stability Option III: Possible Successive Confirmation Count Resets "This letter provides notification of a 60 Day Interim Report per § 21.21 (a)(2) for plants that have selected stability long-term solution Option III. The basis for this notification is that GE Nuclear Energy (GE) has not completed the evaluation of a potential problem with the algorithm that provides the licensing basis Minimum Critical Power Ratio (MCPR) Safety Limit protection for stability Option III. The algorithm determines Successive Confirmation Count (SCC) of an oscillating power signal. A reactor trip is generated when SCC and oscillation amplitude reach their trip setpoints in accordance with the Option III and reactor protection system configuration. The concern is that the oscillation period could change for an oscillation that initiates while reactor state conditions are changing rapidly (e.g., during a two-recirculation pump trip event) and cause the SCC to reset, thus delaying the reactor scram. "GE believes that there is low potential for the MCPR Safety Limit to be violated as a result of this concern. However, a 60 Day Interim Report is required since the evaluation has not been completed. Further information is provided in the attached notification. "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: "The affected basic component is the Period Based Detection Algorithm (PBDA) of stability long-term solution Option III. The PEDA provides the licensing basis MCPR Safety Limit protection for anticipated coupled thermal hydraulic-neutronic reactor instabilities. The concern is that the Successive Confirmation Count (SCC) could reset if an oscillation develops while reactor state conditions are changing rapidly (e.g., during a two recirculation pump trip event) and delay a reactor scram beyond that assumed in the licensing basis analysis. The algorithm is more susceptible to SCC resets with a period tolerance that is near to the minimum allowed by licensing documents (e.g., 50 msec). SCC resets are less likely with higher period tolerance values (e.g., 100 to 300 msec). "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: "GE Nuclear Energy, San Jose, California "(iv) Nature of the defect or failure to comply and safety hazard which is created or could be created by such defect or failure to comply: "A reactor scram is only initiated by the PBDA when the SCC exceeds the count setpoint and the oscillation amplitude exceeds the amplitude setpoint The licensing basis is that the SCC will exceed the count setpoint before the amplitude reaches the amplitude setpoint. If the SCC resets, then the amplitude could exceed the amplitude setpoint before SCC reaches the count setpoint. This could lead to violation of the MCPR Safety Limit. "If scram is delayed, boiling transition could be experienced on a portion of some fuel bundles. This would be a violation of a Technical Specification Safety Limit and is reportable under 10 CFR 21. However, it would not produce a significant safety hazard or threat to public health and safety. "(v) The date on which the information of such defect or failure to comply was obtained: "(vi) In the case of a basic component which contains a defect or failure to comply, the number and locations of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: "A defect has not been confirmed to exist. The potentially affected plants are listed in Attachment 2. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action (note, these are actions specifically associated with the identified Reportable Condition): "GE has communicated this concern to the BWR Owners' Group Potential Issues Resolution Team (PIRT) and to the Stability Detect & Suppress Committee. "GE is continuing to evaluate the potential for the SCC to be reset for current licensed reactor operating conditions. This effort will be completed by November 18, 2002. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: "It is recommended that potentially affected licensees keep informed through the BWR Owners' Group. No specific plant actions are recommended at this time." Plants listed on Attachment 2 Clinton, Brunswick 1& 2, Nine Mile Point 2, Fermi 2, Columbia, Dresden 2 & 3, LaSalle 1 & 2, Limerick 1 & 2, Peach Bottom 2 & 3, Quad Cities 1 & 2, Perry 1, Susquehanna 1 & 2, Hope Creek, Hatch 1 & 2, and Browns Ferry 1, 2 & 3. * * * UPDATE ON 11/18/02 AT 1856 FROM JASON POST (VIA FAX) TO GERRY WAIG * * * "Subject: Final Report, Stability Option III: Possible Successive Confirmation Count Resets - Not Reportable "Reference: MFN02-063, Stability Option III: Possible Successive Confirmation Count Resets, 10CFR Part 21 60 Day Interim Report, October 1, 2002 "This letter provides closure of the reference §21.21(a)(2) 60 Day Interim Report notification for plants that have selected stability long-term solution Option III. The closure is that GE Nuclear Energy (GE) has determined that this is not a reportable condition, however, GE recommends that the BWR Owners' Group Detect & Suppress Committee evaluate the need to change the minimum allowable value for period tolerance used in the Oscillation Power Range Monitor (OPRM). "As described in the reference notification, the potential problem was associated with the algorithm that provides the licensing basis Minimum Critical Power Ratio (MCPR) Safety Limit protection for stability Option III. The algorithm determines Successive Confirmation Count (SCC) of an oscillating power signal. A reactor trip is generated when SCC and oscillation amplitude reach their trip setpoints in accordance with the Option III and reactor protection system configuration. The concern was that the oscillation period could change for an oscillation that initiates while reactor state conditions are changing towards equilibrium state (e.g., following a two-recirculation pump (2RPT) trip event) and cause the SCC to prematurely reset, thus delaying the reactor scram. "A reactor trip signal is generated when the OPRM SCC setpoint and the amplitude setpoint are reached or exceeded for at least one OPRM cell in each trip system channel required to generate the trip signal (e.g., one-out-of two taken twice). The Period Based Detection Algorithm (PBDA) determines the SCC for each OPRM cell. When an oscillation in an OPRM cell signal is detected by the PBDA it sets the base period for that cell. The period tolerance is used to determine if the period of each subsequent oscillation is within an acceptable difference from the base period. The acceptable range for period tolerance specified in stability Option Ill licensing topical reports is 100 to 300 msec. A period tolerance of 50 msec has been approved for OPRM systems that have a 25 msec sampling frequency. "GE evaluated this concern with TRACG simulations of a 2RPT event for typical Option III plants for reasonably limiting Extended Power Uprate (EPU) and Maximum Extended Load Line Limit Analysis (MELLLA) conditions. TRACG calculates channel power, which can be evaluated as representative of an OPRM cell signal through the hot channel oscillation reload licensing methodology, and evaluated by the PBDA for successive confirmation counts. "PBDA resets occur when the difference between the current period and the base period exceeds the period tolerance. The worst case would be if a spurious SCC reset occurred immediately before the amplitude trip setpoint was reached. For this case, that cell would not generate a trip signal until SCC had again counted up to the trip setpoint, which could be a delay of 10 to 12 seconds. "GE evaluated the potential for SCC spurious resets far period tolerance values of 50, 100 and 150 msec. In general, more frequent spurious resets occur with shorter period tolerance. However, the spurious SCC reset does not occur at the same time for all the OPRM cells in an OPRM channel. Some OPRM cell resets delay the trip generated by that cell, while others reset at sufficiently early times that they have again counted up to exceed the count setpoint when the amplitude setpoint is reached, and others do not reset at all. Only one OPRM cell trip in an OPRM channel is sufficient to cause an OPRM channel trip, and each OPRM channel typically has 18 to 33 OPRM cells. In addition, typical core loading schemes ensure that multiple OPRM cells respond very near the peak oscillation magnitude. The analysis concluded that even though spurious resets occur, these resets are not expected to significantly delay reactor scram. Therefore, the currently licensed PBDA provides adequate protection against a MCPR Safety Limit violation for instabilities initiated during a fast transient such as a 2RPT event. Therefore, this does not represent a Reportable Condition under 10CFR21.21. "Even tough this is not a reportable condition, the potential for some OPRM cells to prematurely reset SCC for an instability initiated during a 2RPT is not consistent with thc original design basis of the PBDA. The original design basis was that continuous confirmation counts would occur for fully coupled neutronic/thermal-hydraulic reactor instability. Since this may not occur for a 2RPT with period tolerance values of 50 and 100 msec, it is recommended that Option III plants evaluate the need to change the minimum allowable value for period tolerance." Notified (via email) R1DO (Mohamed Shanbaky), R2DO (David Ayres), R3DO ( Brent Clayton), R4DO (Dale Powers), NRREO (Stu Richards), NRR (Jack Foster). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-10-01
39235 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-10-01 08:45 | 2002-10-01 17:44 | 2002-10-31 | UNANALYZED CONDITION RELATING TO CONTROL ROOM EVACUATION "On October 1 2002, conditions were discovered that if an evacuation of the Wolf Creek Generation Station (WCGS) control room were required, due to a fire, necessary steps could not be completed within committed time requirements. The station is in Mode 1, at 100% power. "During a timed walk down of procedure OFN RP-017, 'Control Room Evacuation,' it was identified that operators did not complete Phase A actions of the procedure in the committed five minutes. Phase A provides that control of the plant will be established at the Auxiliary Shutdown Panel (ASP) and isolation of required instrumentation and other devices on the ASP will be accomplished. Phase A was performed in approximately 8 minutes. This does not meet our commitment to 10 CFR 50 Appendix R as reflected in the WCGS Fire Protection Plan. The effect of additional time to complete Phase A of the control room evacuation is being further analyzed to determine the safety significance. "Based on the guidance provided in NUREG 1022 Revision 2, this situation meets the criterion of 10CFR50.72(b)(3)(ii)(B) for an 8-hour ENS notification, as it relates to being in an unanalyzed condition." The Licensee has implemented compensatory measures at 1900 CDT, 10/1/02. The licensee has notified the NRC Resident Inspector ****RETRACTION JEFF ISCH TO MIKE NORRIS 1429 ET 10/31/02**** "BASIS FOR RETRACTION: "A safety significance evaluation was performed for the condition described above and it was determined that the circumstances do not constitute a significant reduction in plant safety. This conclusion is based on the results of simulator exercises that concluded that the 5 minute completion time was conservative and that the actions needed to place the plant in a safe condition could be performed within 8 minutes. The evaluation provides reasonable assurance that operator activities taken to complete Phase A actions within a 7 to 8 minute period does not result in consequences of safety significance. This conclusion is further validated by comparing the results with bounding conditions contained in a Westinghouse WCAP report for a similar condition involving a failed open power operated relief valve (PORV), as well as an engineering evaluation previously performed for both PORVs spuriously opening due to a fire. Therefore, per NUREG 1022, this condition is not an unanalyzed condition that significantly degrades plant safety and is not required to be reported in accordance with 10CFR50.72(b)(3)(ii)(B)." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-10-01
39234 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-10-01 09:42 | 2002-10-01 16:56 | 2002-10-01 | VALID SPECIFIED SYSTEM ACTUATION DURING TESTING ON ENGINEERED SAFETY FEATURES "Station was conducting ESF testing on the 1B train with the 1B Diesel Generator aligned to the 1B essential bus. While re-aligning from the test alignment, the 1B emergency breaker tripped open due to a problem with the Cutler-Hammer control switch. A valid blackout signal was sensed on the 1B bus. The 1B emergency breaker immediately re-closed and the 1B essential bus was re-energized from the 1B Diesel Generator. Switch repair is in progress." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-10-01
39233 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-09-30 22:10 | 2002-09-30 23:17 | 2002-09-30 | AUTOMATIC REACTOR SCRAM ON MAIN TURBINE TRIP DUE TO LOW CONDENSER VACUUM "Susquehanna Unit 2 experienced a automatic reactor SCRAM on a Main Turbine trip due to low condenser vacuum. The unit experienced a momentary loss of 2D130 (120 V AC power). The loss caused the offgas system to isolate, a runback on the A Reactor Recirc Pump and a scoop tube lock on the B reactor Recirc Pump. Efforts to re-establish the offgas system were unsuccessful. Following the SCRAM, reactor water level dropped to approx. -0.2", and was recovered by the Feedwater System. The offgas system and Condenser vacuum were restored shortly after the SCRAM to maintain the condenser available for heat removal. There were no ECCS initiations and no challenges to containment. "This event is an Reactor Protection System (RPS) actuation when the reactor is critical, and is reportable as a four hour ENS Notification under 10 CFR 50.72(b)(2)(iv)(B)." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-09-30
39232 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2002-09-30 | 2002-09-30 17:06 | 2002-09-30 | PART 21.21 REPORT REGARDING MAIN STEAM ISOLATION VALVE OUT OF SERVICE "This letter provides final notification of a Reportable Condition under 10CFR 21.21(d), as committed in the Reference letter. It was previously submitted as a Reportable Condition for Brunswick Units 1 & 2 and as a 60 Day Interim Report per §21.21 (a)(2) for other plants that may be determined to be affected. "The evaluation has been completed and it has been determined that in addition to Brunswick 1 & 2, this is a Reportable Condition for Duane Arnold, FitzPatrick, Hatch 2, Nine Mile Point 2, Perry 1 and Pilgrim. The basis for this conclusion is that GE Nuclear Energy (GE) analyses for these plants to justify operation at greater than 75% of rated power with one Main Steam line Isolation Valve (MSIV) Out of Service (OOS) (i.e., one steam line isolated) did not adequately address the long term impact of increased flow induced vibration on the remaining open MSIVs. Without a supporting bases, it cannot be assured that the open MSIVs would be able to perform their required safety function following extended operation at greater than 75% of current rated power with one steam line isolated. This could possibly result in offsite doses in excess of 10CFR 100.11 limits. "The actual impact of this condition would only be of concern if MSIV operability had not been demonstrated following extended plant operation at greater than 75% of current rated power with one MSIV OOS, or if a plant was currently in extended operation at greater than 75% of rated power with one MSIV OOS. "All other plants which have an MSIV OOS analysis provided by GE were either limited to 75% of rated power, or the impact of long term operation on the open MSIVs was adequately evaluated for the power level specified in the analysis. "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: "The Main Steam Line Valve Out-of-Service analysis for: Utility Plant Name Carolina Power & Light Brunswick 1 and 2 Nuclear Management Co. Duane Arnold Entergy Nuclear Northeast FitzPatrick, Pilgrim Southern Nuclear Operating Co. Hatch 2 Constellation Nuclear Nine Mile Point 2 First Energy Nuclear Operating Co. Perry 1 "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: "GE Nuclear Energy, San Jose, California "(iv) Nature of the defect or failure to comply and safety hazard which is created or could be created by such defect or failure to comply: "The MSIV OOS analysis performed by GE evaluated plant operation at greater than 75% of rated power with three active steam lines and one steam line isolated. The GE analysis for the affected plants did not address the effect of potential long-term flow induced vibration degradation on the open MSIVs, including the effect on the MSIV air operated controls. Without adequate justification, it cannot be assured that the open MSIVs would close following extended operation with one MSIV OOS at greater than 75% of current rated power. "If it is postulated that the plant operated for an extended period in the MSIV OOS condition and then a main steam line break were to occur in one of the three operational steam lines, then there is the potential that MSIVs would not close to terminate the release from a steam line break either from a common mode failure of both MSIVs, in the broken line, or failure of one MSIV due to the high flow induced vibration and the other MSIV as the design basis single failure. This condition would result in an un-terminated release, which would exceed the existing 10 CFR 100 radiation release limits. "(v) The date on which the information of such defect or failure to comply was obtained: "June 24, 2002 "(vi) In the case of a basic component which contains a defect or failure to comply, the number and locations of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: "A defect has been confirmed to exist in analysis provided by GE for Brunswick 1 and 2, Duane Arnold, Fitzpatrick, Pilgrim, Hatch 2, Nine Mile Point 2, and Perry 1. "(vii) The corrective action which has been, is being, or will be taken; the name of the, individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action (note, these are actions specifically associated with the identified Reportable Condition): "GE has communicated to the affected plants the 75% power limitation when operating with one MSIV OOS. "GE has revised existing internal engineering and program processes to explicitly screen any limiting configurations/conditions for current and future MSIV OOS evaluations. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: "GE recommends limiting operation to 75% of current rated power when operating with one MSIV OOS, unless there is an adequate justification to support extended operation at a higher power level." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-09-30
39231 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-09-29 19:04 | 2002-09-30 11:05 | 2002-09-30 | LOSS OF CONTROL ROOM FILTRATION SYSTEM FUNCTION "This report is being made due to a loss of function of the Control Room Envelope Filtration (CREF) system. On 9/29/2002 @ 20:05 Hrs., an operator on rounds identified that control room envelope boundary door #288-1 was open instead of closed as expected. The door was found to be hung up open due to interference between the bottom door seal and the door stop. The operator closed the door upon discovery. This door is controlled with a key card reader however it can also be opened from both sides with a thumb latch as it is not a security vital door. An initial investigation using the security computer revealed that the Fire Chief accessed the door at 19:04:26 Hrs. during daily door checks and checked it shut at that time. The next card reader activity was at 20:04:50 Hrs. by the operator on rounds who discovered the door open. With the door having been open for other than normal entry/exit, a loss of the control room envelope boundary existed. The control room envelope boundary is required for CREF operability and function. As a result, both subsystems of the CREF system were declared inoperable on 9/29/2002 @ 19:04 Hrs. in accordance with Technical Specification LCO 3.7.2 Condition A, Action A.1 and Condition B, Action B. I. Both CREF subsystems were restored to operable and applicable Conditions and Actions exited on 9/29/2002 @ 20:05 Hrs when the door was closed. LCO completion times were not exceeded. Deviation/Event Report (DER) NM-2002-4233 was written for event followup and Action Request (ACR) 02-04252 was written to correct the problem with the door hanging up on the door stop. After contacting supporting organizations to determine the reportability of the loss of the control room envelope boundary, this event was determined to be reportable in accordance with 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-09-30
39230 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2022-09-10 17:32 | 2002-09-29 20:20 | 2002-09-29 | INADVERTENT START OF A STANDBY SERVICE WATER PUMP DURING RESTORATION FROM A CALIBRATION ACTIVITY "On September 10, 2002 at 1732 hrs, a pressure transmitter in the Service Water System was being returned to service after the performance of an instrument calibration procedure. The transmitter was being vented in order to return the transmitter to service. During the venting evolution, an inadvertent start of 2SWE-P21B, B Standby Service Water Pump, occurred. The pump start was due to low pressure as seen by a second transmitter, which shares a common sensing line with the transmitter that was being vented. This second transmitter provides an input to the auto start feature for the B Standby Service Water Pump. Venting the transmitter caused low pressure in the common sensing line which activated the auto start feature. Since the low pressure was only seen locally at the transmitter and not throughout the system, this was an invalid actuation. Low service water system header pressure is the parameter which would activate this feature and low service water system header pressure was not experienced during this event. A complete actuation of the B train of the Standby Service Water System occurred and the system functioned properly. "This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since it involved an automatic actuation of an emergency service water system that does not normally run and that serves as an ultimate heat sink as per 10 CFR 50.73(a)(2)(iv)(B)(9). This actuation was not part of a pre-planned sequence and did not occur with this system properly removed from service. "However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification instead of submitting a written Licensee Event Report since the automatic actuation of the Standby Service Water pump was not generated by a valid actuation." The NRC Resident was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-09-29
39229 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-29 05:02 | 2002-09-29 13:11 | 2002-10-08 | REACTOR TRIP SIGNAL DUE TO LOW-LOW STEAM GENERATOR LEVEL. While draining the 1"D" steam generator, a reactor trip signal was generated due to a low-low steam generator level. One train of the reactor protection system was being tested, so one trip breaker opened in response to the trip signal. The low-low steam generator level was due to a planned evolution and was a valid signal. There was no safety significance because all control rods were already inserted into the fuel assemblies, the control rods were not latched to the control rod drive system, and the motor generator sets were shutdown by procedure. Although the reactor trip breaker was closed during testing, at no point was control rod withdrawal possible. They are investigating the cause. The NRC Resident Inspector will be notified **** RETRACTION ON 8/28/02 @08:58 BY THAD REAMES TO ARLON COSTA **** "On September 29, 2002, McGuire Nuclear Station notified the NRC of an inadvertent actuation of the Unit. 1 reactor protection system (RPS) while the unit was shutdown for a refueling outage. This occurred when reactor trip breakers unexpectedly opened as a result of a low-low steam generator level reactor trip signal. This event was reported as a valid actuation of the RPS in accordance with 10 CFR 50.72(b) (3) (iv) (A). Reference Event Report 39229. Further evaluation determined that the reactor trip signal which opened the reactor trip breakers was an invalid signal since it was not initiated in response to plant conditions or parameters satisfying the requirements for initiation of the RPS safety function. Therefore, this represented an invalid actuation which is not reportable per 10 CFR 5Q.72(b)(3)(iv)(A). As a result, McGuire is retracting Event Report 39229. Note that McGuire will report this event in accordance with the requirements of 10CFR 50.73." The Licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-09-29
39228 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2002-09-28 14:10 | 2002-09-28 20:45 | 2002-09-28 | SPURIOUS ACTUATION OF ONE OFFSITE EP SIREN "At 14:10 on 09128/2002, the Palo Verde Unit 1 Control Room was notified of a spurious actuation of one siren. The siren is located near Southern and Palo Verde Roads. This siren provides emergency notification to approximately 39 Members of the Public. "No press release is planned at this time, however, the event is being reported due to inquiries from the Maricopa County Department of Emergency Management to troubleshoot the siren and notification of the siren actuation to the Maricopa County Sheriffs Office. "Personnel have been dispatched to turn off the siren. "There is no event in progress and no risk to the health and safety of the public. Members of the public within audible range of the siren may have a concern for their radiological health and safety. "Unit 1 is at approximately 0% power In Mode 5 at the start of its scheduled refueling outage. Unit 2 is at approximately 99% power in Mode 1 at normal operating temperature and pressure. Unit 3 is at approximately 99% power in Mode 1 at normal operating temperature and pressure. "The NRC Resident Inspector has been informed of the siren actuation and this ENS notification. Note: The checkbox for OTHER GOV AGENCIES is referring to the Maricopa County agencies discussed above." | 0 | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-09-28
39227 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-09-28 13:45 | 2002-09-28 15:36 | 2002-09-28 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY CONTACT HOO FOR ADDITIONAL DETAILS THE NRC RESIDENT INSPECTOR WAS INFORMED. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-09-28
39226 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2002-09-27 15:00 | 2002-09-27 18:52 | 2003-04-08 | OFF-SITE NOTIFICATION On September 27, 2002 at approximately 15:00 Mountain Standard Time, Palo Verde Nuclear Generating Station (PVNGS) notified the Environmental Protection Agency (EPA) that a INITIAL NOTIFICATION OF CONTINUOUS RELEASE was being reported. The following information was provided to the National Response Center and State of Arizona: "Palo Verde Nuclear Generating Station is calling to make an initial notification of a continuous release in accordance with CERCLA Section 103(f)(2). 40CFR 302.8 (d). This is not an accidental or episodic release. Palo Verde Nuclear Generating Station will be performing a scheduled steam generator cleaning activity as part of its routine refueling outage for Unit 1. The steam generator cleaning activity will begin on Saturday, September 28 at approximately 18:00. During this activity, Palo Verde Nuclear Generating Station will exceed the Reportable Quantities for the release of ammonia and hydrazine. The same activity is scheduled to occur during the Unit 3 refueling outage, spring of 2003. The activity occurs approximately once per every five to seven years on each unit. The hazardous substances released are ammonia (CAS #7684-41-7) and hydrazine (CAS #302-01-2). PVNGS expects no adverse effects to health and welfare of the general public, nor to the environment. The NRC Resident Inspector was notified along with the State. * * * UPDATE ON 4/8/03 FROM DAN MARKS TO HOWIE CROUCH * * * The following information was received from the Licensee via facsimile: "The following event description is a follow-up notification to ENS 39226, placed at 15:12 Mountain Standard Time (MST) (18:52 ET) on 09/27/2002. "ENS 39226 informed the NRC of a government notification to the National Response Center (EPA), the State of Arizona and Maricopa County related to a continuous release in accordance with CERCLA [Comprehensive Environmental Response, Compensation, and Liability Act] Section 103(f)(2), 40 CFR 302.8(d). This was not an accidental or episodic release. The planned release was the result of steam generator cleaning activities and would result in exceeding the Reportable Quantities for the release of ammonia (CAS #7664-41-7) and hydrazine (CAS #302-01-2). "Included in the notification was the schedule to occur in Palo Verde Unit 3 during its refueling outage in the spring of 2003. "Since that original notification, Palo Verde has implemented a condensation unit that captures a large amount of the effluent prior to release. Although the Reportable Quantities will still be exceeded, the notification to the National Response Center (EPA), [Maricopa County] and the State of Arizona will identify the lower levels. "The contact name for information concerning this notification is [DELETED], Environmental Section Leader, at telephone number [DELTED]. "As during the previous notification, PVNGS [Palo Verde Nuclear Generating Station] expects no adverse effects to the health and safety of the public, nor to the environment." The Licensee has notified the NRC Resident Inspector. | 99 | 99 | 99 | 99 | 99 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-09-27
39225 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2002-09-16 16:15 | 2002-09-27 17:00 | 2002-09-27 | INVALID PRIMARY CONTAINMENT ISOLATION OF GROUP 2 AND 3 OUTBOARD VALVES This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of a specified system, specifically Primary Containment Isolation Valve (PCIV) Group 2 and 3 outboard valves. On September 16, 2002, an over-voltage on the power supply to "B" Reactor Protection System (RPS) bus resulted in a loss of power to the bus. The loss of power resulted in an invalid isolation of the outboard Secondary Containment Isolation Valves (SCIV) and outboard Group 2 and 3 PCIVs. Additionally, "B" Standby Gas Treatment (SGT) started due to an invalid auto initiation signal and RPS received an invalid half scram signal. The affected systems responded as expected for the given conditions and were subsequently returned to a normal configuration when power was restored to the B RPS bus. No deficiencies or abnormalities were noted during the event. This event has been entered into the site-specific corrective action program for resolution. The NRC resident has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-09-27
39224 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-27 08:24 | 2002-09-27 15:58 | 2002-09-27 | VALID ENGINEERED SAFETY FUNCTION ACTUATION DUE TO PARTIAL LOSS OF OFF SITE POWER "While operating at 100% power on September 27, 2002, Watts Bar experienced a loss of one off-site power source, followed about 15 minutes later by the loss of the second off-site power source. These two off-site power sources are fed from the Watts Bar Hydro plant, and are the primary power source for the 6900 V shutdown boards, via Common Station Service Transformers (CSST's) C & D. CSST C feeds shutdown bds[boards] 1A-A & 2A-A, CSST D feeds shutdown bds 1B-B & 2B-B. A fire at the hydo plant was the cause of the off-site power supply breakers opening. The breaker for the supply to the CSST C opened at 0824 (EDT). This deenergized shutdown bds 1A-A & 2A-A, initiating a valid engineered safety function (ESF) actuation that started all four standby diesel generators (DG's), two of which reenergized these shutdown bds. When the other off-site source was lost, the remaining 2 DG's then loaded onto their respective shutdown bds. The plant remain at full power since one train of shutdown power was always available. As designed, AFW started coincident with the EDG start. At this time, the 2 lines have been reenergized and the A, B, C and D Common Station Service Transformers are also energized. Preparations are being made to re-power nonsafety related loads from off-site power." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-09-27
39223 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-09-20 01:12 | 2002-09-27 14:37 | 2002-09-27 | INADVERTENT ALIGNMENT OF THE NUCLEAR SERVICE WATER TO STANDBY NUCLEAR SERVICE WATER POND On September 20, 2002, McGuire Nuclear Station experienced an inadvertent alignment of the Nuclear Service Water (EN) system to the Standby Nuclear Service Water Pond (SNSWP). This event occurred when a Unit 1 "B" Train blackout signal was inadvertently generated during surveillance testing of the 13 Diesel Generator sequencer panel. Further evaluation determined that the blackout signal which automatically aligned RN to the SNSWP was not in response to actual plant conditions or parameters satisfying the requirements for initiation of a blackout signal or the SNSWP safety function. Since alignment of RN to the SNSWP was not in response to a valid signal, this represented an invalid actuation reportable per the requirements of 10 CFR 50.73(a)(2)(iv)(A). However, as per 10 CFR 50.73(a) (1), McGuire is providing a telephone notification of this invalid actuation instead of submitting a written LER. The following additional information is being provided as part of the telephone notification of this event: "B" Train of RN actuated to align Unit 1 and Unit 2 RN to the SNSWP. "B" Train actuation of Unit 1 and 2 RN to the SNSWP functioned successfully and was complete. The NRC Resident Inspector will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-09-27
39222 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2002-09-27 07:30 | 2002-09-27 11:04 | 2002-09-27 | FOUR HOUR 91-01 BULLETIN RESPONSE At approximately 7:30 a.m. on September 27, 2002, a UO2 furnace operator reported an overload alarm condition at the Line 1 UO2 sintering furnace. Subsequent visual inspection of the furnace indicated a pellet boat "jam" had occurred inside the sintering furnace chamber. An estimated 4-5 boats are involved in the localized area in which the jam occurred. The stacking of the boats inside the furnace constitutes a loss of geometry control. The independent control on moderation remained intact, thus no unsafe condition existed, or currently exists. The UO2 sintering furnace temperature is in excess of 1700 degrees C. Following procedure, operations promptly notified nuclear safety. Safe recovery of the material and re-establishment of the geometry control will require a 2 week cool down. This condition is reported pursuant to NRC bulletin 91-01 (within 4 hours) due to a loss of geometry that requires in excess of 4 hours to re-establish. Implementation of corrective actions is pending completion of incident investigation, SAFETY SIGNIFICANCE OF EVENTS: Low safety significance - localized loss of safe slab geometry, moderation control remained intact. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Multiple failure modes required before a criticality accident could occur. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Geometry and moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST BASE CRITICAL MASS): Estimated 4-5 pellet boats involved in actual jam represent [ . . .] kgs UO2 in the form of dry fuel pellets, enriched to [ . . . ] wt% U235. Under a loss of geometry, our analyses have demonstrated a fully reflected hemisphere mass of UO2 pellets at [ . . . ] enrichment containing 5% water is ~[. . . ]kgs. Thus, a large safety margin exists for this loss of geometry Condition. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The geometry control provided by safe slab height of 3 was lost because of jam inside UO2 sintering furnace. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Controlled shutdown of sintering furnace (requires 2 weeks to cool down), recovery of material into favorable geometry containers under NSE approved procedure. Investigation of event and evaluation of additional corrective actions pending. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2002-09-27
39221 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-27 10:40 | 2002-09-27 11:01 | 2002-09-27 | DEVIATION FROM TECHNICAL SPECIFICATIONS PER 10 CFR 50.54(x) The licensee reported a deviation from license condition 2 F, which requires compliance with the Watts Bar Fire Protection Report, part 2, section 9.1, per 10 CFR 50.54(x). This section requires the minimum fire brigade staffing to be restored within two hours. The Watts Bar fire brigade was dispatched to a fire at the nearby Watts Bar Hydro Generation Station (see NRC Event Number 39220) and replacement fire brigade members had not yet arrived on-site. The licensee stated that the fire brigade can respond to a fire at Watts Bar Nuclear but response time would be greater than normal. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEVIATION FROM T SPEC |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(1) |  |  |  | 0 | 2002-09-27
39220 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-27 08:50 | 2002-09-27 09:11 | 2002-09-28 | NOUE DECLARED DUE TO LOSS OF OFFSITE POWER SUPPLY The licensee declared a notice of unusual event (NOUE),in accordance with EAL 3.1, due to the loss of two offsite electrical power supplies to the station for greater than 15 minutes. The cause of the loss of offsite power was a fire at a local hydro electric station. All systems functioned as required. All emergency diesels responded and supplied electrical power to the station shutdown electrical boards. The loss of two offsite power supplies places the station in a technical specification (TS 3.8.1 D) limiting condition for operation (LCO). The licensee notified the NRC Resident Inspector, the State of Tennessee, and the local fire department. At 0955 NRC entered Monitoring for Normal Phase Mode. * * * UPDATE ON 09/28/02 AT 0311 FROM RICKY STOCKTON TO GERRY WAIG * * * The licensee terminated the NOUE at 0308 after the second offsite electrical power supply was restored to the site at 0300 and exited technical specifications 3.8.1 limiting conditions for operation. The first offsite power supply was restored at 0125. At 0311 NRC exited monitoring for the Unusual Event Notified IRO (Wessman), R2DO (W. Rogers ), PAO (R. Virgilio ), NRR EO (M. Johnson), FEMA (K.C.), OHA Ron Brahm | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-09-27
39219 | 0 | ARCTIC PIPE INSPECTIONS |  |  |  |  | 2002-09-26 09:00 | 2002-09-26 17:06 | 2002-09-27 | LOST I-192 RADIOGRAPHY SOURCE DURING SHIPMENT A 20.3 Curie Ir-192 radiography camera SN# 94 was being shipped from Kenin, AK to AEA Technologies in Burlington, MA by Federal Express. The shipment arrived in Newark, NJ on 9/21/02 at 0257 and was scanned to leave on 9/24/02 at 0022 EDT. The Licensee reported that the camera has not arrived in MA, and that Federal Express could not account for the source's location. The source was being shipped in it's shipping container and the Licensee believed that it had a combination lock on it. ***UPDATE CHUCK CAIN TO MIKE NORRIS 1800 9/27/02*** The missing Arctic Pipe source changer has been found at the FedEx Newark terminal. The shipping container was not damaged, but had it's paperwork missing. Notified R4DO (Pellet), R1DO (Della Greca), DIRO (Wessman), NSIR IAT (Davidson) and OHS (Brahm). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-09-26
39218 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2002-09-26 10:44 | 2002-09-26 14:10 | 2002-09-26 | PART 21 REPORT FROM LICENSEE REGARDING MALFUNCTIONING OVERCURRENT SENSORS Two new EC-1 overcurrent sensors withdrawn from warehouse stock failed during bench testing in preparation for installation in the plant during the upcoming refueling outage. The failure mode was premature tripping of the magnetic (instantaneous) element of the device, such that the associated circuit breaker would have tripped early and the corresponding loads would not have remained energized to perform their required safety function. The only application of these specific EC-l overcurrent sensors is in the circuit breaker used in cubicle 71-11510, which is the emergency bus feeder breaker providing 600 VAC power to Motor Control Center (MCC)- 151. (The circuit breaker contains a total of three of these devices, one per phase.) Electrical loads powered from this MCC include various safety systems such as the Standby Gas Treatment System (SBGT), Residual Heat Removal System (RHR) and High Pressure Coolant Injection System (HPCI). The loss of the MCC could have resulted in the failure of SBGT to perform its safety function. The test information indicates that the circuit breaker would have prematurely tripped based on the starting current of the 'A' SBGT Exhaust Fan and thus the associated MCC would not have remained energized. Assuming a concurrent single failure of the 'B' SBGT subsystem, this could have resulted in the loss of both subsystems and the failure of SBGT to perform its safety function. Therefore, a substantial safety hazard existed in that the potential existed for a major deficiency/major degradation of essential safety-related equipment. No other safety functions would have been lost. Component and Supplier: GE Model Type EC-1 Trip Device General Electric Nuclear 225 Amp, 60 Cycle M/C397 Sensor Trip, Characteristic 1 B-2C 175 Curtner Ave. GE P/N QEC10225ABCG10N00 San Jose, CA 95125 Serial Nos. 77386-3A and 77386-3B The defective components were placed in a "hold" status to prevent issuance in the plant. A Corrective Action Request will be issued to General Electric for evaluation. The NRC Resident Inspector was notified | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21 |  |  |  | 0 | 2002-09-26
39217 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-09-24 07:30 | 2002-09-26 00:26 | 2002-09-26 | STOLEN AND RECOVERED MOISTURE DENSITY GAUGE "The facility [Construction Testing and Engineering, Inc.] reported a stolen gauge this morning and within an hour called back to report that the gauge had been recovered [by police]. "The gauge had been picked up from the storage location around 4:30 AM that morning and was transported by the user to his home. The gauge remained locked by chain in the vehicle. When the user returned to his vehicle between 7:30 - 8 AM he discovered the chain had been cut and the case with the gauge was missing. He contacted the police and the Alternate Radiation Safety Officer for his region." CA Rad Health Branch will follow-up with the licensee to obtain the make, model, and serial number of the stolen/recovered gauge and will forward that information to the Headquarters Operations Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-09-30
39216 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-09-25 08:30 | 2002-09-25 17:34 | 2002-09-25 | CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL DURING INITIAL IN-PROCESS SCREENING Licensee has denied individual access to the site. Licensee will notify NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2002-09-25
39215 | 0 | KENNEDY MEMORIAL HOSPITAL |  |  |  |  | 2002-09-24 17:30 | 2002-09-25 16:26 | 2002-09-25 | LOST CS-137 CALIBRATION SOURCE AT HOSPITAL The licensee reported a missing/lost Cs-137 sealed source of 4.9 millicuries which was used for diagnostic medical purposes. The licensee performed an extensive search that did not locate the missing source. The licensee speculated that the source may have been inadvertently disposed of in the waste stream for incineration. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-09-25
39214 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-09-23 18:10 | 2002-09-24 13:55 | 2002-09-24 | NRC BULLETIN 91-01 24 HOUR REPORT "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, PWR fuel fabricator for commercial light water reactors. License: SNM-1107. "Time and Date of Event: Approximately 18:10 hours, Monday, September 23, 2002. "Reason for Notification: Scrubber ventilation ductwork containing gross contamination was stacked without proper spacing. "Summary of Process: The scrubber ventilation system ductwork is non-operational and was being removed. "As Found Condition: A summary of the as found conditions is as follows: -Scrubber ventilation ductwork was found stacked in the Conversion Decontamination Room. -Gross contamination was evident in several sections of ductwork. "Criticality Safety Protection: Criticality safety protection for floor storage of material with 'gross contamination' consists of a 12-inch or greater spacing requirement. Gross contamination is defined as visually observable uranium-bearing material. A criticality would only be possible if an excessive accumulation of uranium occurs, it becomes moderated, and it is not detected before a critical configuration is formed. After assessing the situation, it was determined that this was a nuclear criticality safety event, in an analyzed system, for which less than previously documented . . . protection remains. . . Therefore, the event requires 24-hour notification in accordance with Westinghouse Operating License (SNM-1 107), paragraph 3.7.3 (c.5). "Summary of Activity: -Nuclear Criticality Safety (NCS) was notified by operations. -Removal of the ventilation ductwork was ceased. -NCS visually inspected the ventilation ductwork. -NCS required the ductwork be unstacked and placed in an authorized configuration. "Conclusions -There was a violation of spacing requirements. -At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. -The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A formal causal analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-09-24
39213 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2002-09-23 | 2002-09-24 11:43 | 2002-09-24 | MOISTURE DENSITY GAUGE LOST DURING TRANSPORT A Troxler gauge, model # 3440, serial # 19495 was lost while being transported from Beverton, OR to North Portland, OR. The gauge is an 8 millicurie Cs-137, 40 millicurie Am-Be 241 source and is licensed to GeoPacific Testing Inc, Tigard, OR 97224. The licensee discovered the lost gauge on 9/23/02 at approximately 1700 PDT and notified the State of Oregon on 9/23/02 at 1858 PDT. The gauge was lost north of Highway 26 between the intersection of Emily Lane and Northwest Bethany Blvd and Northwest Germantown Rd. A search is being conducted to recover the lost gauge. A press release is planned. The Oregon State Police, Oregon Emergency Response System, Washington County Sheriff, Beaverton Police and the Portland Police have been notified. The State of Oregon also intends to notify NRC Region 4. * * * UPDATE ON 9/24/02 AT 2138 EDT FROM TERRY LINDSEY TO GERRY WAIG * * * The Troxler moisture density gauge lost during transit was discovered by a passing volunteer fireman from Scapoose, OR. The fireman happened by the gauge, picked up the gauge and case, and secured it at the fire house. The gauge was found on 185th Ave., along the original route traveled when lost, approximately 15 minutes after it was lost. The gauge was reported found after news of the missing gauge was aired today on local media. The gauge is currently being stored by the Scapoose Fire Dept. and will be returned to GeoPacific Testing tomorrow. Notified R4DO (John Pellet) and NMSS (John Greeves) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-09-27
39212 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-09-23 23:35 | 2002-09-23 23:58 | 2002-09-24 | CONTAMINATED WORKER TRANSPORTED OFFSITE FOR MEDICAL ASSISTANCE At 2335EDT on 9/23/02 a worker involved in decontamination activities inside the Unit 3 containment was transported offsite to Lawrence and Memorial Hospital in New London, CT for medical assistance. EMTs administered oxygen to the worker who they believed was suffering from heat stress and hypertension. A rad survey conducted onsite showed contamination levels of 1000 ccpm on his right thigh. An HP technician and supervisor accompanied the worker to the hospital where he was decontaminated. * * * UPDATE 0035EDT ON 9/24/02 FROM MALONEY TO S. SANDIN * * * The HP supervisor who accompanied the contaminated worker to the hospital notified the site that rad surveys completed at 0015EDT confirmed that the ambulance, the ambulance travel path and the hospital treatment room were free of contamination and free released. The licensee will inform state/local agencies and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2002-09-24
39211 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-09-23 17:55 | 2002-09-23 21:50 | 2002-09-23 | 4-HOUR NRC BULLETIN 91-01 REPORT INVOLVING LOSS OF CRITICALITY CONTROLS "EVENT DESCRIPTION: On 09/23/02, The Plant Shift Superintendent (PSS) was notified of a violation of NCSA-705_ 039 Control # 10 related to analysis of solution transferred to the Oil and Grease Removal Unit (OGRU) in the X-705 building. Specifically, the sample results utilized did meet control # 10 of the Nuclear Critically Safety Analysis (NCSA) did not coincide with the material transferred. This represents the Loss of both controls for MASS which is a loss of double contingency controls applicable to the Fissile Material Operation (FMO). The material transferred was determined to be from a Non-Fissile Operation. "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is low. The container that was processed was from the motor cleaning operation in the X-720 Building which has determined to be a Non-Fissile Material Operation. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): Criticality could occur by processing material with a U235 mass greater than a critical mass into a unfavorable geometry container. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameter in this operation is mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The maximum amount of material in this event is 15 grams U235. The controlled enrichment is less than or equal to 20 wt. % U235. The form of the material is a water based solution that is contaminated with oil. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The NCS control that was lost is mass. The NCSA requires that before a container processed two independent samples are obtained a batch calculation is performed with the data which is verified by a second operator and then checked by a member of supervision. Since the container which was processed did not match the container both checks were not correct. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The Oil and Grease Removal Unit was declared inoperable by the Plant Shift Superintendent on 09/23/2002." Operations will inform the DOE Site Representative and has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-09-23
39210 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2002-09-21 02:30 | 2002-09-23 10:47 | 2002-09-24 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The licensee reported to the State of Oklahoma that on Friday night that one of their trucks was proceeding south on I-35 near 4th St. in Moore, OK when a Troxler gauge was bounced out of the bed of the truck. The gauge was struck by another vehicle and damaged severely. The gauge was recovered and taken to the shop where a survey indicated 8 millirem around the outside of the case. A leak test is being conducted, results are not yet available. The company has contacted Troxler concerning the gauge. More information will be available later. * * * UPDATE AT 1316 EDT ON 9/24/02 FROM PAM BISHOP TO GERRY WAIG * * * The Oklahoma Dept. of Environmental Quality called to report that the damaged Troxler gauge, model #4640, serial #750143, is licensed to APAC Oklahoma Inc, P. O. Box 580670, 3605 North 129th East Ave, Tulsa, OK 74158-0670. The source is a Cs-137, 7.1 millicurie source. The gauge has been disassembled and no external contamination was detected. Wipes and pictures of the damaged gauge have been sent to Troxler for evaluation. The damaged gauge is being held by the licensee in it's Shawnee, OK office. The APAC Radiation Safety Officer is Mr. John Ringwald (918) 438-2020. Notified R4DO (John Pellet) and NMSS (Doug Broaddus) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2002-09-26
39209 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-09-23 08:00 | 2002-09-23 09:14 | 2002-09-23 | OFFSITE NOTIFICATION DUE TO DISCHARGE PERMIT VIOLATION The licensee notified the State of New Jersey due to a fish kill of greater than 100 fish killed, this is a violation of their discharge permit. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-09-23
39208 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-09-22 16:42 | 2002-09-23 00:08 | 2002-09-23 | 24 HOUR REPORT INVOLVING A VALID ACTUATION OF A "Q" SAFETY SYSTEM DUE TO A UF6 RELEASE "At 1642, on 9-22-02 the Plant Shift Superintendent (PSS) was notified of an activation of a Q safety system in the C-333 process building. Operations personnel reported receiving a Process Gas Leak Detection (PGLD) alarm at Unit 5 Cell 9. The operators responded to the area according to their emergency response procedure and reported that a haze was visible in the area. Building personnel then reported that multiple PGLD alarms were received from other cells in the area. The location of the PGLD detectors that were alarming indicated that the UF6 release was located at the Unit 5 cell bypass housing. All cells in Unit 5 were shutdown to reduce the process pressure to below atmosphere. Following shutdown of the equipment, air sampling in multiple locations through out the building were obtained by the plant emergency squad. After it was determined that all air samples showed no indication of an ongoing release, an all clear on the emergency was given by the PSS. Trouble shooting by building personnel is in progress to determine the location of the system breach. "The PSS determined that this event is a 24 Hour Event Report due to the valid activation of a TSR required Q safety system. "The NRC Resident inspector has been notified of this event." The duration of the release was estimated as approximately 10 minutes. Urine samples for four (4) maintenance personnel and ten (10) operators working in the area will be processed as a precautionary measure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-09-23
39207 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2002-09-22 01:46 | 2002-09-22 03:19 | 2002-09-22 | AUTOMATIC REACTOR SCRAM DURING MAIN TURBINE TRIP TESTING "At 0146, Reactor Scram occurred when the Main Turbine Tripped during the weekly testing of the Main Turbine Protection Devices Trip Test Instruction. The tripping of the Main Turbine caused a Turbine Control Valve Fast Closure Scram. All rods inserted. Reactor Level dropped below Level 3 due to the Scram. The Main Feed System restored level above Level 3, following the Scram. No Safety Related Injection Systems were required to maintain Reactor Level. Currently the Reactor is being maintained in Hot Stby Mode 3 with RPV Pressure at 900 PSIG and RPV level at 196 [inches] with the Feed System. "The Main Turbine Protection Device Trip Test did not function properly and caused the Main Turbine to trip. A team is being formed to determine why the trip lockout test failed to prevent a Main Turbine Trip." Decay heat is being rejected to the Main Condenser. Plant electrical loads transferred to the Startup Transformer as required. The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-09-22
39206 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-21 11:00 | 2002-09-21 15:40 | 2002-09-21 | PARTIAL LOSS OF OFFSITE POWER CAUSED EDG START AND AFW PUMP START "While operating at 100% power on September 21, 2002, Watts Bar Unit 1 experienced a momentary loss of the 161kV offsite power feed to Common Station Service Transformer (CSST) D. WBN's two offsite power supplies are fed from a remote switchyard located at the Watts Bar hydro electric plant. The one affected offsite power source and the CSST D are the primary power sources for 6900V Shutdown Boards 1B-B and 2B-B, The partial loss of offsite power was caused by the inadvertent manual operation of a breaker at the hydro electric plant switchyard. The opening of the breaker occurred at 11:00:20 (EDT) and the breaker was reset to provide offsite power at 11:00:34 (EDT). Due to this event, and the loss of the primary feed to the shutdown boards, a valid engineered safety function (ESF) actuation occurred which started all four of the standby diesel generators (DGs), along with, as designed, the 1B-B Motor Driven Auxiliary Feedwater (AFW) Pump and the Turbine Driven AFW Pump. The DGs provided power to the affected Shutdown Boards and other required blackout loads during the event. All components at the hydro plant were restored to their normal configuration at 11:44 (EDT). Affected Plant components are currently being restored to normal configurations." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-09-21
39205 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-09-20 10:02 | 2002-09-20 16:30 | 2002-11-15 | HPCI INOPERABLE DUE TO PRESSURE AND SPEED FLUCTUATIONS "On 9/20/02 at 10:02 AM EDT, the Unit 1 HPCI system was declared inoperable due to observation of speed and pressure fluctuations while operating in the manual mode. HPCI was being run for the quarterly surveillance test. Site engineering is currently troubleshooting. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) for failure of a single train accident mitigation system." The NRC resident inspector was notified. *** UPDATE ON 11/15/02 AT 1032 EST BY PETER GARDNER TO HOWIE CROUCH *** "Troubleshooting identified that the output of the Ramp Generator and Signal Converter (RGSC) was fluctuating. The HPCI RGSC and Electronic Governor [-Motor] (EG-M) were replaced and the post maintenance testing (PMT) was successfully completed. The HPCI safety function requires the system to provide adequate coolant makeup to the reactor pressure vessel (RPV) in the automatic mode for the spectrum of analyzed events. The small break LOCA [Loss of Coolant Accident] event (one-inch diameter pipe break) requires the greatest HPCI flowrate. HPCI must provide adequate RPV coolant makeup to maintain core coverage and prevent an actuation of ADS [Automatic Depressurization System] during this event. HPCI successfully completed the portion of the surveillance test that required operation in the automatic mode just prior to the observed speed fluctuation. Two successful HPCI runs were performed following the replacement of the RGSC and EG-M in June 2002. The speed fluctuation occurred intermittently in the manual mode of operation following a reduction in speed to 3150 rpm. Failure analysis of the RGSC and EG-M did not reveal any condition that would have prevented HPCI from providing the required coolant makeup." Therefore, the licensee is retracting this event. Licensee notified the NRC resident of the retraction. NRC region 1 duty officer (Harold Gray) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-09-20
39204 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-05-29 | 2002-09-20 15:29 | 2002-09-20 | AGREEMENT STATE REPORT INVOLVING A MEDICAL DIAGNOSTIC MISADMINISTRATION "Background: On June 12, 2002 the licensee Radiation Safety Officer reported a diagnostic misadministration which occurred on May 29, 2002. An elderly patient had been scheduled for an iodine-123 uptake and scan. When she arrived, the nuclear medicine technologist noticed a scar on her neck from a thyroidectomy. Based on this observation, and interview with the patient, the nuclear medicine technologist presumed that the patient needed a neck and head scan with iodine-131. She was given 3.0 mCi of iodine-131 without discussing it with the physician. It turned out that she only had a partial thyroidectomy, and her partial right lobe had approximately a 22% uptake. There was a delay in notifying this Department because the physician felt it wasn't a misadministration, as the primary care physician had ordered the wrong exam to begin with. Dose with iodine-123 would have been 7.0 rads, dose with 3.0 millicuries of iodine-131 was 3087 rads to the thyroid. "Regulatory Issues: This incident was reported within 15 days as required by the California Code of Regulations, title 17, section 30322. The RSO sent a June 18, 2002 letter describing the root cause of the event and corrective actions to prevent the likelihood of a recurrence. This letter was received in this office on July 10, 2002. During a September 11, 2002 telephone conversation, I was told that the Nuclear Medicine Department procedures were changed so that scheduling for these type of procedures are now performed by nuclear medicine technologists and not clerical personnel. "This was reportable to the NRC because it involved over 39 millicuries of I-131. Cedars-Sinai Medical Center will be cited for violation of the California Code of Regulations, title 17, sections 30521, which requires nuclear medicine technologists to be under General Supervision when performing nuclear medicine technology procedures, and 30502 which defines General Supervision as meaning that the supervisor is responsible for, and has control of all of the following: 1. Quality, technical and medical aspects of all nuclear medicine technology procedures; 2. Radiation health and safety of patients, ancillary personnel and other persons; 3. Ascertaining that nuclear medicine technologists maintain their competency by participation in management sponsored or formal continuing education or training offered by professional organizations or societies, or institutions of higher learning. "Contrary to the above, the nuclear medicine technologist who administered the 3 millicuries of I-131, and under the General Supervision of the authorized user, made decisions regarding the procedure and dose to be administered without consultation with the authorized user. "Health and Safety Concerns: The patient received an unnecessary dose. Her thyroid should have received only about 7 rads had she received 200 microcuries of I-23, but instead she received 3,087 rads. The information needed was obtained, and an additional dose was not given. Because there is a possibility of reduction in thyroid function, Cedars-Sinai Medical Center has said the patient will be followed by her physician. "Conclusion: The referring physician's written order on file at the hospital was not examined during the investigation because neither the document, or a copy of this document, could be released to this office due to a new patient privacy law, according to the RSO." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-09-25
39203 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-09-17 16:00 | 2002-09-20 12:30 | 2002-09-20 | AGREEMENT STATE REPORT INVOLVING A LOST AND FOUND MOISTURE DENSITY GAUGE "The department was contacted on 9/18/02 by SCI Engineering, Inc., regarding an event that happened around 4:00 p.m. the previous day. He reported that one of their drivers noticed when he looked in his rear view mirror after rounding a curve approximately 2 miles from the SCI office, that the Humboldt Model 5001 moisture/density gauge containing approximately 11 millicuries Cs-137 and 44 millicuries Am-241, was no longer in the back of his truck. He then turned around and proceeded down the road to search for the gauge. Meanwhile, an Ameritech employee in a truck was behind the SCI truck and watched the gauge fly out the back. He then stopped to get the device. Nearby was a friend of his that worked for a construction company and was familiar with nuclear gauging devices. He noted the type of the device and the serial number and called SCI to report the find. SCI had, in the interim, already sent two technicians to help look for the device after hearing of the loss from the SCI truck driver. This all occurred in approximately 10 minutes according to SCI. "The State expressed concern to the licensee in the timeliness of the notification and the fact that a gauge was allowed to 'fly' out the back of one of their trucks. The licensee agreed and stated that a report would be filed with the department as soon as possible. The department will take appropriate measures to ensure that there will be no recurrence of this type of an event by this licensee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-09-25
39202 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-09-20 01:12 | 2002-09-20 04:12 | 2002-09-27 | INADVERTENT ACTUATION OF BLACKOUT SIGNAL ON UNIT 1 DURING SURVEILLANCE TESTING "Inadvertent Actuation of B Train Blackout Signal on Unit 1. Actuation occurred during testing of the 1B Diesel Generator sequence panel. The actuation caused the B Train Nuclear Service Water System to realign to the standby Nuclear Service Water Pond on both Unit 1 and Unit 2. Unit 2 was not affected due to the realignment. The Unit 1 Boric Acid pump transfer pump automatically secured and various containment and Auxiliary Building Ventilation components were affected due to the actuation. The procedure used for testing the sequencer simulated an undervoltage signal on the B Train Emergency Bus. Plans are being evaluated to restore the sequencer from the test alignment and realign all affected equipment." Neither reactor residual heat removal cooling or spent fuel pool cooling were affected by this event. Electrical buses remained energized and no EDG autostart occurred since the blackout signal was simulated and not based on an actual undervoltage condition. The licensee is attributing the cause preliminarily to an inadequate procedure. The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 9/27/02 @ 1437 BY JOHNSON TO GOULD * * * RETRACTION Further evaluation determined that the blackout signal which automatically aligned RN to the SNSWP was not in response to actual plant conditions or parameters satisfying the requirements for initiation of a blackout signal or the SNSWP safety function. Since alignment of RN to the SNSWP was not in response to a valid signal, this represented an invalid actuation which is not reportable per 10 CER 50.72(b) (3) (iv) (A). In addition, 10 CFR 50.72(b) (3) (iv) (B) does not identify the ultimate heat sink portion of RN systems as a system applicable to 10 CFR 50.72(b) (3) (iv) (A). Therefore, McGuire is retracting Event Report 39202. Note: McGuire will report this event in accordance with the requirements of 10 CFR 50.73. (see event # 39223) The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-09-20
39201 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-09-18 | 2002-09-19 16:28 | 2008-01-02 | MOISTURE DENSITY GAUGE STOLEN FROM THE BACK OF A PICKUP TRUCK "The writer received a call from [an employee] of Building and Earth Sciences at approximately 9:00 AM on September 19, 2002. The employee reported that a Troxler Model 3430 gauge (S/N 30199) had been stolen sometime during the night of September 18, 2002, from their truck working under reciprocity in Memphis, Tennessee. "The gauge had been left chained in the back of the truck overnight at [ . . . . . ]. The chain had been cut, and the gauge taken. The licensee's employee had contacted both the State of Tennessee and had filed a report with the local police. "The licensee is continuing their investigation, and considering additional methods to expedite recovery of the gauge." Contact the Headquarters Operations Officer for additional information. * * * UPDATE ON 1/2/2008 AT1215 FROM BOBBY SMITH TO MARK ABRAMOVITZ * * * The State provided the following information via email: "[Mississippi] DRH [Division of Radiological Health] received a phone call from Desoto County [MS] EMA [Emergency Management Agency] on 12-20-07 about a Troxler Model 3430 moisture/density gauge ( Serial # 30199 ) that was found by a member of the public in the woods. The moisture/density gauge had been stolen on September 19, 2002, (NRC Event No. 39201) in Memphis, Tennessee, while Building & Earth Sciences was working under reciprocity of their Alabama Radioactive Material License AL-1266. The theft was originally reported to Alabama Radiation Control, Tennessee Division of Radiological Health, and the Memphis Police Department. The gauge was picked up by Mississippi Division of Radiological Health on 12-21-07 and returned to our office where it was leak tested and stored. Building & Earth Sciences was contacted and is going to pick the gauge up on 1-3-08. No leakage was detected." Notified the R1DO (Conte) and FSME EO (Flannery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-09-24
39200 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2002-09-18 20:25 | 2002-09-19 00:41 | 2002-09-19 | REACTOR SCRAM DUE TO AUTOMATIC REACTOR PROTECTION SYSTEM ACTUATION "A reactor scram occurred at River Bend Station @ 2025 on 09/18/02. The plant was operating at 100% reactor power at the time of the scram. The plant systems performed as required post scram. Reactor pressure and water level are stable with reactor level being controlled by the reactor core isolation cooling system. This event is being reported pursuant to 10 CFR 50.72 (b)(2)(iv)( B)(1) a reactor protection system (RPS) scram while critical (a 4 hour report) and a manual actuation of the reactor core isolation cooling system (RCIC) pursuant to 10 CFR 50.72 (b)(3)(iv)(B)(5). The cause of the scram is still under investigation." The licensee reported that all control rods fully inserted during the scram and that there was no indication of SRV actuation during the event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-09-19
39199 | -1 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2002-09-17 16:52 | 2002-09-18 17:10 | 2002-10-10 | HEAT BALANCE CALCULATION ERROR ON REACTOR POWER "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "Palo Verde Nuclear Generating Station Units 1, 2, and 3 are evaluating the potential that the Maximum Power Level of 3876 megawatts thermal (100% power), specified in Operating License Condition 2.C(1) may have been exceeded in the past due to an unconservative value of reactor coolant pump (RCP) heat in the secondary calorimetric calculation since initial plant operation. The value of total energy input due to RCP operation used in the calorimetric is 29.53 megawatts (MW) in Unit 1, 29.61 MW in Unit 2 and 31.88 MW In Unit 3. Conservative engineering calculation of actual RCP heat input based on electrical load is as low as 24.72 MW. Similarly, conservative engineering calculation of actual RCP heat input based on fluid power (pump differential pressure) is as low as 22.86 MW. Thus, the calorimetric error may be as large as (31.88-22.86) 9.02 MW or approximately 0.23%. "The error could have resulted in core power levels above the Operating License limit of 3876 MW thermal. Due to current operating limitations on reactor coolant system hot leg temperature, none of the Palo Verde units are presently exceeding the licensed power limit. Unit 1 is at approximately 99% power (3837 MW thermal, 39 MW margin). Unit 2 is at approximately 98% power (3798 MW thermal, 78 MW margin). Unit 3 is at approximately 99.6% power (3861 MW thermal, 15 MW margin) "This report is being made because a review of historical operating data may reveal that the Maximum Power Level was exceeded. "The Palo Verde safety analyses bound a power level of 102%, thus the Units remain within the safety analyses. As a compensatory measure, the station has established an administrative limit of 99.75% power pending resolution of this issue. "No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The NRC Resident Inspector has been notified. * * * RETRACTION FROM DANIEL HAUTALA ON OCTOBER 10, 2002 AT 1534 EDT TO MIKE RIPLEY * * * "The following event description is based on information currently available. If through subsequent reviews or this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This notification is a retraction to the September 17, 2002, ENS #39199 which reported a calorimetric input error that could have resulted in core power levels above the Operating License limit of 3876 MW thermal at Palo Verde Nuclear Generating Station Units 1, 2, and 3. Further evaluation of the calorimetric power calculation indicated the installed values were conservative and no correction is required. "The NRC Resident Inspector has been notified." Notified R4 DO (William Jones) | 99 | 98 | 99 | 99 | 98 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW | [5 empty] | 0 | 2002-09-18
39198 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2002-09-18 14:28 | 2002-09-18 17:19 | 2002-09-18 | HPCI DECLARED INOPERABLE "This report is being made under 10CFR50.72(b)(3)(V). "On September 18, 2002 at 14:28 HPCI declared INOPERABLE due to placing the Auxiliary Lube Oil Pump [control switch] To Pull-to-lock. This prevents the HPCI Turbine from automatically starting. The Auxiliary Lube Oil pump [control switch] was taken to pull-to-lock in accordance with station operating procedures due to receiving a HPCI Gland Steam Exhauster Condenser Hotwell high level alarm that did not clear due to failure of the Gland Seal Condenser Condensate pump to automatically start. "NRC Senior Resident has been informed of the HPCI inoperability." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-09-18
39197 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-07-21 | 2002-09-18 15:34 | 2002-09-18 | NOTIFICATION UNDER 10 CFR PART 21 FOR LEAKING FUEL PUMP ON FAIRBANKS MORSE EMERGENCY DIESEL ENGINE The following are the contents of a facsimile: "This initial notification addresses the reporting requirements of 10 CFR 21.21(d)(3)(i) and provides preliminary information applicable to 10 CFR 21.21 (d)(4). 1. Name and address of the individual informing the Commission. G.M. Dugger Vice President Operations Entergy Nuclear Operations, Inc. Pilgrim Nuclear Power Station 600 Rocky Hill Road Plymouth, MA 02360 2. Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. Facility Pilgrim Nuclear Power Station Component Fuel Injector Pump for ALCo (Fairbanks Morse), model 251 F, Emergency Diesel Generator, Part Number 23200127, Serial Number 9611071 3. Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. Supplier Coltec Industries Fairbanks Morse Engine Division 701 White Avenue Beloit, WI 53511-5492 4. Nature of the defect or failure to comply and the safety hazard, which is created or could be created by such defect or failure to comply. The fuel injector pump was found to be leaking excessively through a nameplate rivet hole that had been drilled through-wall in the pump body. The drilled hole allowed fuel to leak through the pump body. This fuel injector pump was being installed on a safety-related emergency diesel generator. It was through visual observation of the pump during the post work test that the fuel leak through the nameplate rivet hole was detected. If the leak had not been identified during the post work test, the leak could have gone unnoticed during subsequent emergency diesel generator operation. The failure of the fuel injector pump could have adversely impacted emergency diesel generator operation and prevented the emergency diesel generator from being able the supply all of the necessary accident loads. 5. The date on which the information of such defect or failure to comply was obtained. The defect was discovered during post work testing on July 19, 2002 while the emergency diesel generator was tagged out of service for the overhaul that installed the subject fuel injector pump. A determination that the defect could create a substantial safety hazard was completed on September 12, 2002. In accordance with 10 CFR 21.21 (a)(3) and Pilgrim Station procedure, the Pilgrim Site Vice President was notified of the conclusion. The notification was made on September 17, 2002. 6. In the case of a basic component which contains a defect or fails to comply, the number and location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations of this part. At Pilgrim Station, there are two emergency diesel generators and one Station Blackout Diesel Generator (SBODG). There are 18 fuel injector pumps installed on each emergency diesel generator and 12 fuel injector pumps on the SBODG. Except for the defective fuel injector pump that was installed while the emergency diesel generator was tagged out service for overhaul, none of the fuel injector pumps installed on either emergency diesel generator or the SBODG have exhibited a similar leak (through-wall rivet hole leak in the pump body). 7. The corrective action, which has been taken, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. The fuel injector pump that contained the through-wall rivet hole in the pump body was removed from the emergency diesel generator and was replaced with a spare fuel pump. The spare fuel pump was visually inspected for leak tightness when the emergency diesel generator was post work tested after the defective pump was replaced. The emergency diesel generator post work testing was completed With satisfactory results and returned to operable status on July 21, 2002. The defective pump was not retained. There are currently no (zero) fuel injector pumps located in the Pilgrim Station warehouse. 8. Any device related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. Pilgrim Station discussed the condition of the defective pump on September 16, 2002, with the pump supplier. The supplier acknowledges modifying the mounting of the nameplate label to the pump prior to supply. Pilgrim Station has not supplied any spare fuel injector pumps to a purchaser or other licensee." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 21.21 |  |  |  | 0 | 2002-09-18
39196 | 0 | ANDERSON ENGINEERING |  |  |  |  | 2002-09-18 07:30 | 2002-09-18 12:12 | 2002-09-18 | CPN MOISTURE DENSITY GAUGE WAS STOLEN FROM THE BACK OF A PICKUP TRICK. At 0730 CT 09/18/02 an employee of Anderson Engineering found that a CPN moisture density gauge which had been chained to the back of his 1992, open-bed, Ford Pickup truck was missing. The gauge was in its case at the time that it was stolen. The last time he saw the CPN gauge was at 1500 hours CT on 09/17/02 when he parked his pickup truck in the back of his house. He discovered that the CPN gauge had been stolen when he got up this morning and went to his truck to go to work. The caller stated that it is company policy that the gauge be dropped off and stored at the main office before the worker goes home. The Model number of the stolen CPN moisture density gauge is MC-1-DR and the serial number of the gauge is MD01205992. The gauge contains 10 millicuries of Cesium-137 and 50 millicuries of Am-241/Be. The licensee will notify the Joplin, MO Police Department and informed them that one of their CPN moisture density gauges has been stolen. The licensee notified NRC Region 3 (Cassandra Frazier) of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-09-18
39195 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2002-09-17 15:50 | 2002-09-17 18:27 | 2002-09-17 | A LICENSED SUPERVISORY OPERATOR TESTED POSITIVE FOR ALCOHOL DURING A RANDOM FITNESS-FOR-DUTY TEST The employee's access has been suspended. The NRC Resident Inspector was notified. Contact the HOO for additional information. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 26.73 |  |  |  | 0 | 2002-09-17
39194 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-09-16 14:35 | 2002-09-17 10:25 | 2002-09-17 | STOLEN TROXLER MODEL 3216 GAUGE During the afternoon of September 16, 2002, a roof moisture gauge in its locked case was stolen from a locked van belonging to an Illinois Radioactive Material Licensee--IL Roof Consulting Associates, Inc. with license IL-01713-01. The Radiation Safety Officer (RSO) reported the break-in and theft to the IDNS and the Chicago Police within an hour of the theft. The gauge was a Troxler Model 3216, Serial Number 00173 with 40 millicuries of americium-241and was used for roofing moisture measurements. The van was parked in front of a Chicago public school while two workers were on the roof of the school--Leif Ericson Scholastic Academy--at 3600 W. 5th Avenue, Chicago. Near the end of the job the RSO had joined the two workers and then discovered the theft that occurred approximately 1435 as he was returning to the van with a second gauge that had been in use. The windows of the van were tinted to reduce visibility except for the drivers side window. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-09-20
39193 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2002-09-17 06:30 | 2002-09-17 08:25 | 2002-09-17 | REACTOR RECEIVED POOL LEVEL ALARM DUE TO LEAK FROM A DIFFUSER LINE An unusual event occurred when the pool level alarm tripped due to the pool level going below the setpoint. This occurred due to a leak possibly on a pool diffusion system line. Approximately 10,000 gallons of water leaked into the sump and is being pumped into their liquid storage tanks. They believe the leak may be due to a faulty coupling. They isolated the leak and refilling the pool at the rate of 25gpm. There was no increase in radiation levels and the core was not uncovered (a minimum of 15' of water is above the core). * * * UPDATE ON 09/17/2002 @ 0929 BY SPELLMAN TO GOULD * * * The NOUE was terminated at 0820 CDT when the pool level was return to above the pool level alarm setpoint. Notified RDO (Loveless), NRR EO(Marsh), PM (Mendonca via NRR EO), and FEMA (Duncan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 4 | TX | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-09-17
39192 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-09-15 14:00 | 2002-09-15 18:08 | 2002-09-15 | NRC BULLETIN 91-01 4 HOUR NOTIFICATION At 0845 CDT, On 9-15-02 the Plant Shift Superintendent (PSS) was notified of the following: At approximately 0500 CDT, on 9-15-02 the Front Line Manager in the C-337 Building observed the pressure in the Unit 3 Cell 2 Freezer-Sublimer (F/S) vessel to be above the required pressure level. NCSA CAS-001 Freezer-Sublimers at the Paducah Gaseous Diffusion Plant, requires the system pressure be maintained below a certain level and, If exceeded, immediate actions must be taken to reduce the system pressure. Pressure was not immediately restored to below NCS pressure limits. At 0923 CDT on 9-15-02. the pressure was reduced to below the required limit. The NRC Senior Resident inspector has been notified of this event, | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-09-15
39191 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-09-14 20:12 | 2002-09-14 22:14 | 2002-10-07 | BORIC ACID RESIDUE DISCOVERED DURING A BARE HEAD INSPECTION OF THE REACTOR VESSEL HEAD Two reactor vessel head penetrations on Unit 2 ( #21 and # 31) appear to have exhibited some amount of leakage during the past cycle of operation. This conclusion is based on the boric acid residue found at these locations during the bare head inspection. This is a preliminary finding, further NDE and Liquid Penetrant Inspections will be performed and a repair plan will be developed during this outage. A inspection of the reactor vessel head was performed last year and no boric acid residue was noted. The NRC Resident Inspector will be notified of this event by the licensee. * * * UPDATE ON 10/07/02 @ 1647 FROM JOHNSTONE TO GOULD * * * Preliminary results obtained during the fall refueling outage are as follows: A bare head visual inspection resulted in the identification of two penetrations that appeared to have exhibited some amount of leakage (penetrations 21 and 31 as previously reported), four additional penetrations are suspected of leaking, and several penetrations are masked with boric acid residue (due to a conoseal leak) that made their status indeterminate. Inspection of 59 J-groove welds with eddy current (ET) was performed. The ET inspections identified at least one indication of greater than 6 mm in length in about 83% of the J-groove welds. Additionally six J-groove welds, on thermocouple locations that could not be interrogated by ET, were examined by liquid penetrant test (PT) and found to have rejectable (greater than 1/16'" linear) indications. Three of the penetrations with indications discovered by PT had been previously repaired with an embedded flaw technique that now is believed to have been improperly executed. All penetrations exhibiting leakage and suspected of leakage based on the bare head visual inspection had ET indications> 6 mm in length or rejectable PT indications. One of the suspected leaking penetrations was one of three previously repaired. Thirty five penetration inspections from the tube ID utilizing an open housing ET and ultrasonic inspection (UT) probe have been conducted. Numerous axial and circumferential ID and OD indications have been found. Most of the OD indications lie in the penetration tube between the toe and the root of the J-groove weld. About 20% of the penetrations have tube OD circumferential "crack like" indications. All are located between the root and the penetration side toe of the J-groove weld. Penetration (54) has two OD circumferential tube indications, the most limiting being about 80 degrees and .226 inches deep (tube wall .62 inches). This penetration had no leakage. Penetration 54 is bounding for the inspections completed. A boat sample from one suspected leaking penetration was obtained and sent to a vendor lab for analysis. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-09-14
39190 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-09-12 21:20 | 2002-09-13 20:15 | 2002-09-13 | LOSS OF ONE BARRIER OF DOUBLE CONTINGENCY NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 2120 CDT, on 9-12-02 the Plant Shift Superintendent (PSS) was notified of the following: The C-337A south crane does not meet the intent of NUREG-0554 as required by NCSA 042 SRI 5.5.6, NUREG 0554 section 6.3 requires the crane to have malfunction protection which should include controls to sense and respond to conditions such as excessive electric current, excessive motor temperature, over speed, overload and over travel. Over speed protection is not provided in the event of a gearbox failure. The NCSE/A requires that the crane meet specifications equivalent to NUREG-0554 when lifting cylinders over autoclaves that contain cylinders with liquid UF6 greater than or equal to 1.0 wt.% U235. Following discovery, the use of this crane to move cylinders over liquid cylinders that contain equal to/greater than 1.0 wt.% U235 was suspended. The NRC Senior Resident Inspector has been notified of this event. SAFETY SIGNIFICANCE OF EVENTS: The crane used to move cylinders over liquid UF6 cylinders did perform as intended and no cylinder was dropped. Therefore, the process conditions were not lost. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR In order for a criticality to be possible, a cylinder would have to be dropped on an autoclave that houses a liquid cylinder such that the liquid cylinder ruptured. The rupture liquid cylinder contents would then have to be moderated sufficiently to support a criticality. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.) Double contingency for lifting cylinders over liquid cylinders located in autoclaves is maintained by requiring the crane to be single-failure proof. Therefore, in the event part of the crane fails, a second design feature would prevent the cylinder from falling onto an autoclave, rupturing rupturing a cylinder, and releasing liquid UF6 into the autoclave, which may contain water and/or steam. The integrity of the cylinder is intended to prevent moderation of the UF6 when placed in the autoclave. Therefore dropping a cylinder onto an autoclave containing a liquid UF6 cylinder could cause a criticality by allowing water or steam(I.e. moderator) to react with UF6. The first leg of double contingency is based on the unlikely event of dropping a cylinder from an overhead bridge crane that has been designed to lift cylinders. Since the overhead bridge crane that was used has a 20-ton capacity and the proper slings and lifting fixtures were used, this leg of double contingency was maintained. The second leg of double contingency is based on using a single-failure proof crane to move cylinders over liquid cylinders that contain greater than or equal to 1.0 wt% U235. Because the crane is not single-failure proof meeting the requirements equivalent to NUREG-0554, this leg of double contingency was not maintained. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): 10 ton liquid UF6 Cylinder with a net weight of 20750 lbs UF6 enriched to ---- wt.% U235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES Crane was determined not to be single fail-proof as per applicable NCSE and NCSA requirements. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Further use of this crane to move cylinders over liquid that contain greater than or equal to 1.0 wt% U235 was immediately suspended and procedure changes initiated to reflect requirement. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-09-13
39189 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-09-13 14:16 | 2002-09-13 15:03 | 2002-09-13 | Contract guard accidentally discharged a weapon in the protected area. Immediate compensatory measures were taken upon discovery. NRC Resident Inspector will be notified by the licensee of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2002-09-13
39188 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-09-13 09:22 | 2002-09-13 09:35 | 2002-09-13 | UNUSUAL EVENT DECLARED BASED ON EMERGENCY DIRECTOR JUDGMENT The licensee declared a UE at 0922 EDT based on the judgment of the Emergency Director and the previous physical security report EN #39187. The licensee commenced a search of all vital areas for explosives or other threats at 0900 EDT. Also, an offsite notification to the FBI was made. The licensee informed the state and the NRC Resident Inspector. * * * UPDATED AT 2026 EDT ON 9/13/02 BY LARRY PRUETT TO FANGIE JONES * * * The licensee terminated the UE at 2002 EDT after completing a thorough search. The licensee notified the NRC Resident Inspector and the state. Notified R2DO (Mike Ernstes), NRR EO (William Ruland), IRO (Joseph Holonich), NSIR (Roy Zimmerman), FEMA (Cibock), and OHS (Brahm). The NRC entered Monitoring for this event at 0855 EDT and exited at 2045 EDT. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2002-09-13
39187 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-09-13 06:45 | 2002-09-13 07:45 | 2002-09-13 | 1-HOUR SECURITY REPORT INVOLVING UNAUTHORIZED ENTRY INTO THE PROTECTED AREA Unauthorized entry into PA. Immediate compensatory measures taken upon discovery,. Licensee will inform the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-09-13
39186 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-09-12 18:41 | 2002-09-12 20:18 | 2002-09-12 | BOTH TRAINS OF CONTROL ROOM HIGH EFFICIENCY AIR FILTRATION WERE INOPERABLE AT THE SAME TIME. "PNPS I&C Design Engineering determined that modifications of CRHEAF-B humidistat after removal of temporary modification bypassing the switch caused the switch to not perform per design. This would inop the system if high humidity was present because the wiring configuration would turn off the heater if high humidity was present. The system would not perform its design function for the mission length required due to this. Due to this both trains of CRHEAF have been determined to have been inop at the same time while the CRHEAF-A was tagged out for planned maintenance. CRHEAF-A has been returned to operable status while repairs to CRHEAF-B are in-progress. Both trains were inoperable for approximately 4 and 1/2 hours. An ACTIVE LCO for 36 hours was entered." The NRC Resident Inspector was notified of this event by the licensee. | 74 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-09-12
39185 | 0 | FAIRMOUNT GENERAL HOSPITAL |  |  |  |  | 2002-09-12 12:30 | 2002-09-12 17:39 | 2002-09-12 | RADIOACTIVE MEDICAL WASTE PACKAGE A patients radioactive waste was inadvertently sent from Fairmount General Hospital on 08/28/02 to Stericycle, Medical Waste Facility located in Warren, Ohio. When the package arrived at the Stericycle Medical Waste Facility it triggered their radiation monitor. On 09/06/02 Stericycle informed Fairmount General Hospital that they had received a radioactive waste package from them and that they were not licensed to hold radioactive materials at their facility. Fairmount General Hospital picked the package up today from Stericycle and it is has been placed in a radioactive decay room at the Hospital. The source of the radioactivity at this time is unknown. The package has only internal fixed contamination and the internal radioactive level of the package is 0.2 millirems per hour. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | WV | HOS | [5 empty] | 0 | 2002-09-12
39184 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2002-09-12 08:05 | 2002-09-12 09:46 | 2002-09-12 | THE PLANT LOST EMERGENCY THE NOTIFICATION SYSTEM TO THE STATE OF VERMONT The plant lost the primary and alternate Nuclear Alert System telephone links to the State of Vermont at 0740. They verified communication with alternate state police barracks. The system was returned to service at 0920. The NRC Resident Inspector was notified. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-09-12
39183 | 0 | BRANSCOME, INC. |  |  |  |  | 2002-09-12 05:00 | 2002-09-12 07:07 | 2002-09-12 | POTENTIAL DAMAGE TO TROXLER GAUGE DURING FIRE A structure fire at the Branscome, Inc. facility located at 1922 W. Pembroke Ave., Hampton, VA 23166 may have damaged their Troxler Model 4640-B gauge, S/N 855. This gauge which is used to measure asphalt thickness contains a 9 millicurie Cs-137 source. The licensee has visually confirmed that the case is melted, however, no rad surveys have been performed in that the Hampton FD is restricting access to the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | VA | MAT | [5 empty] | 0 | 2002-09-12
39182 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-09-11 | 2002-09-11 23:35 | 2002-09-11 | 1-HOUR SECURITY REPORT INVOLVING AN UNACCOUNTED FOR SECURITY WEAPON A security weapon was discovered missing from its' stored location. Immediate compensatory measures taken upon discovery. The licensee informed local law enforcement and will inform the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-09-11
39181 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-09-11 09:00 | 2002-09-11 22:54 | 2002-09-11 | NRC BULLETIN 91-01 24 HOUR REPORT "At 0900, on 9-11-02 the Plant Shift Superintendent (PBS) was notified of the following: During removal of two 4-Inch valve subassemblies that ultimately connects to 12-Inch crossover piping in C-337, fireproof covers were not properly attached to the adjacent piping such that it could not perform Its intended function. The covers were installed using tape instead of the required clamp. NCSA GEN-10, Removal and Handling of Contaminated Equipment from the Cascade at PGDP, requires fireproof covers to be installed on cascade system openings greater than 10-inches in diameter, to prevent the introduction of moderator from a sprinkler activation, lube oil leak, or RCW leak. "Double Contingency is maintained by an unlikely event and control on moderation. The control on moderation was not properly implemented end was therefore lost. The unlikely event (moderation entering the piping) did not occur. This event resulted In a loss of one leg of double contingency. "The NRC Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: The improper installation of fireproof covers caused them to not be able to perform their criticality safety related function. However, no moderator was available to enter the system. Therefore, the process condition was not lost. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S1 OF HOW CRITICALITY COULD OCCUR In order for a criticality to be possible, a fire would have to unseat the fireproof covers and activate the sprinkler system. The moderator would have to fill over 300 ft of maximum diameter 6-inch piping before accumulating in the unsafe geometry 12-inch piping. "CONTROLLED PARAMETERS (MASS MODERATION, GEOMETRY CONCENTRATION ETC) Double contingency is maintained by an unlikely event and 8 control on moderation control "ESTIMATED AMOUNT , ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): No known mass of licensed material exists in the affected piping. "NUCLEAR CRITICALITY SAFETY CONTROLS(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The first leg of double contingency is based on the unlikely event of a moderator release (Sprinkler, RCW, oil) into the open process system during the time the system is open. Since there was no moderator release Into the system, this leg of double contingency was maintained. The second leg of double contingency is based on the fireproof cover preventing a moderator release from entering the open process system. Since the fireproof covers were not attached such that a waterproof seal would be maintained In the unlikely event of a fire or solution release, the ability to prevent introduction of moderator was lost. The control was violated and double contingency was lost. Since double contingency is based on an unlikely event and a control on moderation, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "The fireproof covers have been properly installed with the approved clamps." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-09-11
39180 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-09-10 14:00 | 2002-09-10 18:10 | 2002-09-10 | MEDICAL EMERGENCY INVOLVING CONTRACT EMPLOYEE "On September 10, 2002, at approximately 2:00 p.m. a report was received in the Wolf Creek Generating Station control room of a non-work related medical emergency involving a contract employee. Onsite medical personnel responded and commenced first aid including CPR. An ambulance was dispatched and the individual was transported offsite to a local hospital. Wolf Creek personnel were subsequently notified by hospital personnel that the individual had passed away. At this time no press release is planned. OSHA has been informed of the fatality. The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-09-10
39179 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-09-09 15:59 | 2002-09-09 22:30 | 2002-09-09 | FAILED RELAY CARD CAUSE AUTOMATIC START OF THE "A" EDG AND THE TURBINE DRIVEN AUXILIARY FEED WATER PUMP "On September 9, 2002 at 1559, with Wolf Creek in Mode 1 at 100 % power, the Control Room received annunciator 19E, NB01 degraded voltage. Approximately 90 seconds later, the NB01 normal feeder breaker opened. The 'A' Emergency Diesel Generator (EDG) started and loaded onto the bus as expected. After the 'A' EDG restored NB01 bus voltage to normal, annunciator 19E remained locked in. The cause of the actuation appears to be a failure of the relay driver card that supplies the degraded voltage signal to the Load Sequencer Emergency Load Shedder (LSELS). Instrumentation and Control Technicians (INC) expect repairs to be complete by 0000, September 10, 2002. "As expected, an automatic start of the turbine driven auxiliary feedwater pump occurred upon the under voltage condition on NB01. After the bus was re-energized, the shutdown sequencer actuated and emergency loads sequenced as expected. "Based on the guidance provided in NUREG 1022, Revision 2, this situation meets the criteria of 10 CFR 50.72 (b)(3)(iv)(A) for an 8-hour ENS notification as it relates to actuation of the emergency ac electrical power systems, which includes emergency diesel generators. "The licensee has notified the NRC resident inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-09-09
39178 | 0 | ROSEMOUNT NUCLEAR INSTUMENTS, INC |  |  |  |  | 2002-09-09 | 2002-09-09 15:15 | 2002-09-09 | NOTIFICATION UNDER 10 CFR PART 21 FOR MODEL 1153 DIFFERENTIAL PRESSURE TRANSMITTERS The following is taken from a facsimile report sent by Emerson Process Management: "Pursuant to 10 CFR Part 21, section 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that: (a) certain Model 1153 differential pressure transmitters with model codes beginning with '1153D' or '1153H' shipped between March 2001 and August 2002, and (b) spare sensor modules shipped between March 2001 and August 2002 with kit part numbers: 01153-0320-0232 01153-0320-0352 01153-0320-0252 "may not meet RNII's published temperature effect specification. Other Model 1152, 1153 and 1154 pressure transmitters are not affected. A list of affected Model 1153 pressure transmitters and spare sensor modules shipped to the end user's facility is provided in Attachment A. "1.0 Name and address of the individual providing the information: Mr. Jeffrey W. Schmitt Vice President & General Manager Rosemount Nuclear Instruments, Inc. 12001 Technology Drive Eden Prairie, MN 55344 "2.0 Identification of items supplied: Certain Model 1153 differential pressure transmitters with model codes beginning with 1153D or 1153H shipped between March 2001 and August 2002 and; "Spare sensor modules shipped between March 2001 and August 2002 with kit part numbers: 01153-0320-0232 01153-0320-0352 01153-0320-0252 "See Attachment A for complete listing of affected equipment shipped to the end user's facility. "3.0 Identification of firm supplying the item: Rosemount Nuclear Instruments, Inc. 12001 Technology Drive Eden Prairie, MN 55344 "4.0 Nature of the failure and potential safety hazard: During the course of quality testing and data review, RNII has determined that certain Model 1153 differential pressure transmitters and spare sensor modules may not meet the published temperature effect specification. The temperature effect specification establishes an expected analog output error interval during normal ambient temperature variations occurring between 40 [degrees] F (4.4 [degrees] C) and 200 [degrees] F (93.3 [degrees] C). While analysis is still ongoing, the root cause of the potential nonconformance has been narrowed to the effect of temperature changes on the transmitter module. Based on data review and analysis, RNII has established the following ambient temperature effect specification for transmitters affected by this notification. This specification supercedes the published temperature effect specification for all pressure transmitters affected by this notification. All Range Codes: ± 3.0% of Upper Range Limit per 100 [degrees] F (55.6 [degrees] C) RNII does not have sufficient information relative to each end user's specific applications to determine the potential safety-related impact to each end users plant. Each end user must determine the impact on its plant operations and plant safety and take action as deemed necessary. "5.0 The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action: (a) RNII has expanded its temperature effect test screen to include all model 1153 pressure transmitters to assure that all further shipments of model 1153 pressure transmitters meet RNII's published temperature effect specification. (b) RNII has placed a hold on spare sensor module shipments. (c) RNII has established a new temperature effect specification for pressure transmitters impacted by this notification as noted in Section 4.0. (d) RNII will verify ambient temperature effect performance to the original specification on any returned Model 1153 differential pressure transmitter or sensor module affected by this notification and repair or replace if required. (e) RNII will continue root cause analysis of the temperature effect potential non-conformance. Action will be taken consistent with the findings of this analysis to assure conformance to RNII's published temperature effect specifications. Anticipated completion date: 1 November 2002. (f) RNII will remove the hold on spare sensor modules when actions per 5.0 (e) are complete. "6.0 Any advice related to the potential failure of the item: The end user must determine the impact of this potential non-conformance upon its plant's operation and safety and take action as deemed necessary. If the end user determines that return of a pressure transmitter or sensor module is required, RNII should be contacted to facilitate the return process. Rosemount Nuclear Instruments, Inc. has a strong commitment to the nuclear industry and assures you that we are dedicated to the supply of high quality products and services to our customers. We are sorry for any potential impact that this notification might cause. If there are any questions, or you require additional information related to this issue, please contact Mike Dougherty (952) 828-5626, Gerard Hanson (952) 828-3951, Bob Cleveland at (952) 828-8255, or Matt Doyle at (952) 828-3480." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2002-09-09
39177 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-05-05 | 2002-09-09 15:15 | 2002-09-09 | AGREEMENT STATE REPORT OF POTENTIAL OVEREXPOSURE "Two employees received an excessive exposure at this facility. Landauer read the badges again with the same results. One employee had a dose of 34.6 rem and the other had a dose of 19.3 rem. A cause for the over exposure could not be identified. On August 29 and 30, 2002, a representative of LDEQ investigated the over exposure. After the investigation, it was concluded that the two employees did not actually receive the dose." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-09-12
39176 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-09-05 | 2002-09-09 15:15 | 2002-09-09 | TWO RADIOACTIVE SOURCES FOUND "American Radiation Services discovered two 1.5 curie sources of Cs-137 at Shield Coat, Inc. while performing a survey for naturally occurring radioactive material. The sources were identified as pipe wall thickness caliper sources, The source with serial number 5171 was manufactured on November 4,1982 by Ludlum, Inc. The source with serial number 3344 was manufactured on January 25, 1983. Upon discovery the area was roped off and the sources surveyed. Readings of 4.5 mr/hr and 5 mr/hr were found at one foot from the sources. A smear of the source housings detected no alpha or beta activity. The sources will be secured in a locked building until the can be returned to Ludlum. The building will be posted with 'Caution: Radiation Area', The last known possessor of the sources with the above mentioned serial numbers was Randolph Clay in Houma, LA. An investigation is ongoing at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-09-12
39175 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-09-09 10:08 | 2002-09-09 13:58 | 2002-09-09 | MEDICAL EMERGENCY INVOLVING CONTRACT EMPLOYEE "Today at approximately 10:08 AM a report was received in the control room of a medical emergency involving a contract employee at the Point Beach nuclear power plant. Onsite medical personnel responded and commenced first aid including CPR. CPR was continued until ambulance personnel arrived on site. The individual was transported to a local hospital. "We have been informed by a subsequent report from the hospital that the individual died from an apparent heart attack. "The Manitowoc County coroner's office and OSHA have been informed of the fatality. At this time no press release is planned." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-09-09
39174 | 0 | US INSPECTIONS SERVICES |  |  |  |  | 2002-09-07 06:30 | 2002-09-07 13:45 | 2002-09-08 | STOLEN RADIOGRAPHIC EXPOSURE DEVICE The licensee reported that one of their work trucks was stolen, which contained a radiographic device, from a worker's home located in Louisville, Kentucky. The device was manufactured by Sentinel (AEA TECHNOLOGY) and contains a radioactive source of 90 curies of IR-192. The exposure device serial number is B4175. The source serial number is 05970B. The device was locked in the safe position. The device is used to perform X-Rays of piping welds. The incident was reported to the Jefferson County Sheriff's office by the licensee. The licensee has an NRC license from Indiana and was doing work under reciprocity in Kentucky which is an Agreement state. The licensee reported notifying the Agreement State, Kentucky. Subsequently, the Jefferson's County Sheriff's office located the truck but the device was missing. ***UPDATE 1026 EDT 9/8/02 DAMON LAMB TO MIKE NORRIS*** Device was recovered and has no damage to the device or locking mechanism. Notified NSIR (Zimmerman, Warren, Tracy and McGinty), R2DO (Decker), R2IAT (Boland), R3DO (Hills), R3 IAT (Creed), NMSS (Federline and Cool), NMSS EO (Essig), EDO (Shea), PAO (Beecher) and OSP (Picone). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | KY | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-09-07
39173 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-09-07 09:06 | 2002-09-07 09:22 | 2002-09-07 | OFFSITE NOTIFICATION TO STATE AND LOCAL GOVERNMENTS OF SHUTDOWN FOR REFUELING OUTAGE "At approximately 0040 on September 7, 2002, Millstone Unit No, 3 was shutdown for a planned refueling and maintenance outage which is scheduled to last greater than 72 hours. This notification is made in accordance with reporting requirements imposed by the State of Connecticut. The shutdown is routine and was conducted in accordance with plant procedures and without incident. The NRC is being notified in accordance with the requirements of 10CFR50.72(b)(2)(xi) as this constitutes a report made to an outside agency." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-09-07
39171 | 0 | MARYLAND RADIATION HEALTH PROGRAM |  |  |  |  | 2002-09-06 12:40 | 2002-09-06 17:30 | 2002-09-06 | MARYLAND AGREEMENT STATE REPORT ON CANCER TREATMENT EQUIPMENT MALFUNCTION The Agreement State reported a malfunction of a cancer treatment machine made by Nucletron Corporation, model 105.999, serial number 31307. The malfunction occurred at the end of a treatment session when the device emergency motor failed to return the source to the shielded position. The source got hung up in the guide tube. The radioactive source is 4.9 curies of IR-192. The source was manually cranked into the shielded position by the medical physicist. No personnel overexposure occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | MAT | [5 empty] | 0 | 2002-09-06
39170 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-09-05 | 2002-09-05 12:18 | 2002-09-05 | MATERIAL/WATER IN SCRUBBER VENTILATION DUCT AT FUEL FACILITY "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched PWR fuel fabricator for commercial light water reactors. License: SNM-l 107. " "Time and Date of Event: Approximately 17:00 hours, Wednesday, September 4, 2002.' "Reason for Notification: Material and liquid detected in wet scrubber ventilation system in Uranium Recycle and Recovery area." "Summary of Process: This ventilation system draws from the safe geometry dissolver system in the Uranium Recycle and Recovery area." "As Found Condition: A summary of the as found conditions is as follows: Material and liquid was found in ventilation ductwork during a planned shutdown and inspection. The ventilation system and associated processes remained shutdown and the Nuclear Criticality Safety (NCS) function was notified." "Double Contingency Protection: Double contingency protection for the wet side of scrubber ventilation ducts greater than 10 inches in diameter consists of preventing accumulation through prudent system design and operation, configuration control, and detection/mitigation through periodic visual inspection and/or gamma surveys of selected lines. A criticality would be possible in a ventilation duct given an excessive accumulation of uranium occurs in a scrubber vent line greater than 10 inches in diameter, and it becomes moderated, and it is not detected before a critical configuration is formed." "After assessing the ductwork, it was determined that this was a nuclear criticality safety event, in an analyzed system, for which less than previously documented double contingency protection remains. The event requires 24-hour notification in accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5)." "Summary of Activity: Nuclear Criticality Safety (NCS) participated with engineering and operations to determine the source of the material and liquid. This investigation is continuing. The ventilation ductwork was inspected. Samples from the ductwork are being obtained for analysis. The ventilation and associated processes are shutdown and in a safe condition." "Conclusions: There was a loss of double contingency protection. At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A formal causal analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-09-05
39169 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-09-04 16:21 | 2002-09-04 17:41 | 2002-09-04 | SAFEGUARDS LOG ENTRY INVOLVING UNDECLARED FIREARM During delivery of a chiller unit, the truck driver under contract to GE, failed to declare an unloaded firearm in his vehicle. The driver was denied access to the site and local law enforcement was notified. There is no indication that this incident involved any malevolent attempt to introduce a firearm inside the PA. The licensee will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0 | 2002-09-04
39168 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-09-04 09:40 | 2002-09-04 15:23 | 2002-09-04 | LOSS OF BOTH ENS AND COMMERCIAL TELEPHONE LINES DUE TO CABLE CUT "Loss of communications capability. Determined commercial phone lines were not working. This loss included ENS and NARS phones. "Cause: The loss was caused by a backhoe digging north of the plant. A phone line was impacted resulting in a loss of numerous phone lines. "ETR [Estimated Time to Recovery]: Commercial phone lines, ENS phones have been restored. "A cell phone was made available for outgoing calls calls, including calls to NRC Ops Center. No incoming phone was available to the Main Control Room. "Off-Site pager was made available for NRC contact as well as a phone contact via the ComEd Electric Operations Center. A phone line in the EOF was manned which provided a method to transfer calls to the main control room " The licensee informed both state agencies and NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-09-04
39167 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2002-09-04 09:00 | 2002-09-04 14:45 | 2002-09-04 | LOSS OF 2 OFFSITE EMERGENCY NOTIFICATION SIRENS "At approximately 9:00 am on 9/4/02, 2 of the 10 Emergency Sirens in Putnam County were discovered to be inoperable. These sirens lost power due to an electrical storm during the night. As of 12:00 pm these sirens were returned to operable status, returning the number of available sirens in that county to greater than 90%. At this time the Putnam County officials and the Local [Resident] NRC Inspectors have been notified of the event. This notification is being made for both IPEC Unit 2 and Unit 3." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-09-04
39166 | 0 | ALCO CORP |  |  |  |  | 2002-09-03 18:00 | 2002-09-04 11:46 | 2002-09-04 | MOISTURE DENSITY GAUGE RUN OVER BY VEHICLE A moisture density gauge, make: CPN, model: MC-1 was damaged when run over by an asphalt truck. The gauge contains 10 millicuries Cs-137, 40 millicuries Am-241/Be source. The event occurred at route 199/52 Paseo, San Juan, PR. The licensee reported that the sources remained intact and no radiation leakage was detected. The gauge is currently secured and the licensee is planning to return it to the vendor (CPN) today or tomorrow. The licensee notified the U.S. National Response Center at 2050 on 9/3/02 (Incident Report # 621851). The National Response Center notified the NRC Ops Center via facsimile on 9/3/02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | PR | OTH | GEN |  |  |  |  | 0 | 2002-09-04
39165 | 0 | PALISADES | 1 |  |  | [1] CE | 2002-09-03 09:35 | 2002-09-03 12:20 | 2002-09-03 | EMERGENCY RESPONSE DISPLAY SYSTEM (ERDS) DATA LINK FAILED DURING QUARTERLY TESTING The licensee was unable to establish the ERDS data link during quarterly testing. Troubleshooting is currently in progress. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-09-03
39164 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-09-02 21:00 | 2002-09-02 22:22 | 2002-09-02 | PLANT ENTERED TS 3.5.3 DUE TO THE RCIC TURBINE SYSTEM BEING DECLARED INOPERABLE The plant commenced reactor shutdown at 2100 CDT due to the RCIC turbine bearing oil system not maintaining the proper oil level. They are currently troubleshooting the problem but have not yet determine the cause. The TS 3.5.3 requires the plant to be in mode 3 by 0028 on 9/3/02 and reduce reactor steam pressure to less than or equal to 150 lbs. By 0028 on 9/4/02. The NRC Resident Inspector was notified. | 7 | 0 | 0 | 9 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-09-02
39163 | -1 | U. S. STEEL-GARY WORKS |  |  |  |  | 2002-09-01 05:02 | 2002-09-01 14:42 | 2002-09-04 | DAMAGED SOURCE HOLDER ON STEEL CASTER LEVEL GAUGE A radioactive source holder on a steel caster unit was damaged from metal overflow at the U. S. Steel - Gary Works, Steel North Facility #2 Caster, located in Gary, Indiana. The gauge is a Berthold Mold Level Gauge, Model LB300ML, Serial Number 2849-12-96. Originally a 10 millicurie Cobalt 60 (Dec 1996) source, it is currently estimated by the licensee to be about 5 millicuries. The damage was limited to the source holder outer casing. Neither the shutter closing mechanism nor the source shielding (tungsten) were damaged. The damaged area involved a top plate where a lock can be applied to the shutter mechanism and steel lifting lugs. The source was verified in the source holder and the shutter closed. A radiation survey of the area was conducted and no contamination or abnormal readings were detected. The licensee has secured the shielded source and is making arrangements for repair. * * * UPDATE ON 9/4/02 BY KUNKLE TO GOULD * * * RETRACTION After a conversation with Region 3 if was determined that this event is not reportable since the shutter was still operable, shielding was intact and no leak or exposures occurred. Therefore, the licensee is retracting this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN |  |  |  |  | 0 | 2002-09-01
39162 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-08-31 01:20 | 2002-08-31 16:52 | 2002-08-31 | NRC BULLETIN 91-01 24 HOUR REPORT - IMPROPER ISOLATION OF PUMP PRESSURE ALARMS The following is taken from a facsimile report. At 0120, on 8-31-02 the Plant Shift Superintendent (PSS) determined that a loss of double contingency had occurred in the C-337 process building. In preparation for maintenance work on the #2 dual Speed Purge and Evacuation (P&E) pump Instrument Maintenance had been requested to disable the two delta pressure alarms associated with this pump. The delta pressure alarms are safety related items (SRI). The SRI requires that both delta pressure alarms be functional while the P&E pump is isolated from the cascade. Building Operations personnel later discovered that one of the delta pressure alarms that had been disabled was an alarm for the #3 P&E pump which was not undergoing maintenance. Both delta-pressure alarms for the #3 P&E pump were required to be in service at the time. The C-337 Front Line Manager and Instrument Maintenance responded to the alarm panel and restored the alarm to the #3 P&E pump. At that time, double contingency was restored. This event resulted in a loss of one leg of double contingency in which double contingency was restored within 4 hours. The NRC Resident Inspector has been notified. SAFETY SIGNIFICANCE OF EVENTS: While the R-114 was demonstrated to be dry, an SRI for double contingency was rendered not functional without the knowledge of the operator. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) In order for a criticality to occur, an unsafe mass uranium deposit would have to be present in the process gas system, an R-114 leak to the process gas system would have to occur, the R-114 would have to contain an unacceptable amount of moisture and moderate the deposit. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY. CONCENTRATION, ETC Double contingency is maintained by implementing two controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORMS OF LICENSED MATERIAL (INCLUDES PROCESS LIMIT AND % WORST CASE CRITICAL MASS): No known mass of licensed material exists in the #3 Dual Speed P & E pump. NUCLEAR CRITICALITY SAFETY CONTROL SYSTEM(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The first leg of double contingency is based on the delta pressure switch alarming to alert the operator to take action to either verify the R-114 is dry or to isolate the RCW and remove the R-114 from the system in order to prevent water from leaking into the process gas system. This delta pressure alarm was maintained as operable, the SRI was maintained and the control was not violated. The second leg of double contingency is based on the independent delta pressure switch alarming to alert the operator to take action to either verify the R-114 is dry or to isolate the RCW and remove the R-114 from the system in order to prevent water from leaking into the process gas system. The independent delta pressure alarm was disconnected without first isolating the RCW system violating the SRI. The Independent delta pressure switch was reconnected immediately upon discovery. This re-established double contingency. Since double contingency is based on two controls (i.e. SRIs) on one parameter, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Make the #3 dual speed P&E alarm operable. 2. Independently sample the #3 dual speed P&E R-114 system for moisture. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-08-31
39161 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-08-30 01:05 | 2002-08-30 17:02 | 2002-08-30 | REPORT INVOLVING A VALID ACTUATION OF A "Q" SAFETY SYSTEM "At 0105 hrs, Autoclave (AC) #4 in the X-344 facility experienced a steam shutdown due to condensate level alarms A and B actuating. AC #4 was in an applicable TSR mode II (heating) when the alarms actuated. This is considered a valid actuation of a 'Q' safety system. The AC was placed in mode 7 (shutdown). An investigation is underway to determine the cause of the actuation." Operations informed both the DOE Site Representative and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-08-30
39160 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-08-30 | 2002-08-30 15:30 | 2002-08-30 | AGREEMENT STATE REPORT INVOLVING LOSS/RECOVERY OF GENERAL LICENSED MATERIAL "Hugo Neu-Proler Company received a load of scrap material today from BHL Industries that set off our gate radiation detectors. We processed the load and found a piece of equipment with the following information on it: Manufacturer: Texas Nuclear Products, Cs-137, 200 mCi [millicuries] measured January '93. Series: SG, Model: 5202, Serial No. B1865. "The piece of equipment was segregated and is currently being temporarily stored at Hugo Neu-Proler, pending [...issuance of shipping approval]." The State of California contacted the source owner who is arranging for return shipment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-09-04
39159 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC |  |  |  |  | 2002-08-30 | 2002-08-30 14:05 | 2002-08-30 | PART 21 INVOLVING NON-CONFORMING ROSEMOUNT PRESSURE TRANSMITTERS AND SPARE PARTS The following information was received via fax: "Re: Notification under 10 CFR Part 21 for Model 1153 and 1154 pressure transmitters with optional adjustable damping circuit boards, and spare adjustable damping circuit boards "Pursuant to 10 CFR Part 21, section 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that: (a) certain Model 1153 and 1154 pressure transmitters with special adjustable damping options N0037, N0039, N0058, N0085, N0102, N0108, N0120 shipped between December 2000 and July 2002, and (b) certain spare adjustable damping circuit boards with part number 01154-0021-0004 shipped between December 2000 and July 2002, may not meet RNII's published Nuclear Steam Pressure/Temperature specification and/or RNII's published Post DBE Operation specification. Model 1153 and 1154 transmitters which do not contain the special optional adjustable damping circuit board are not affected. The adjustable damping feature establishes the time constant of the transmitter's output. A list of affected Model 1153 and 1154 transmitters and spare adjustable damping circuit boards shipped to the end user's facility is provided in Attachment A. "1.0 Name and address of the individual providing the information: Mr. Jeffrey W. Schmitt Vice President & General Manager Rosemount Nuclear Instruments, Inc. 12001 Technology Drive Eden Prairie, MN 55344 "2.0 Identification of items supplied: Model 1153 and 1154 Pressure Transmitters with special adjustable damping options N0037, N0039, N0058, N0085, N0102, N0108, N0120 as identified by the appropriate model code. The applicable model codes begin with either '1153' or '1154' and end with the applicable N option number, for example '1154DP5RAN0037.' and; Spare adjustable damping circuit boards with part number 01154-0021-0004. See Attachment A for complete listing of affected equipment shipped to the end user's facility. "3.0 Identification of firm supplying the item: Rosemount Nuclear Instruments, Inc. 12001 Technology Drive Eden Prairie, MN 55344 "4.0 Nature of the failure and potential safety hazard: This notification impacts: (a) certain Model 1153 and 1154 pressure transmitters with special adjustable damping options N0037, N0039, N0058, N0085, N0102, N0108, N0120 shipped between December 2000 and July 2002 and (b) certain spare adjustable damping circuit boards with part number 01154-0021-0004 shipped between December 2000 and July 2002, which may not meet RNII's published Nuclear Steam Pressure/Temperature specification and/or RNII's published Post DBE Operation specification. American Capacitor Corporation, the manufacturer of a capacitor used on the adjustable damping circuit board recently informed RNII that capacitors shipped to RNIIs adjustable damping circuit board supplier after June 2000 were inadequately tested for conformance to the required high temperature insulation resistance (IR) as specified by RNII's procurement documents. Subsequent RNII testing confirmed that the capacitors were non-conforming to RNII's IR specifications. These non-conforming capacitors were assembled into certain transmitters and spare circuit boards that were shipped from RNII between December 2000 and July 2002. Further RNII testing demonstrated that model 1153 and 1154 transmitters with the optional adjustable damping circuit boards containing non-conforming capacitors would not meet RNIIs published Nuclear Steam Pressure/Temperature and Post DBE Operation specifications for the published temperature profile. Due to the transmitter performance variation present in the test results, RNII cannot provide an interim specification. Testing has demonstrated that affected adjustable damping circuit boards do meet product specifications at normal operating temperatures (40-200 degrees F) RNII does not have sufficient information relative to the end user's specific applications to determine the potential safety-related impact to its plant. The end user must determine the impact on its plant operations and plant safety and take action as deemed necessary. "5.0 The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action: (a) Upon notification from the capacitor manufacturer of this issue, RNII placed holds on all shipments containing potentially affected equipment (model 1153 and 1154 transmitters with the special adjustable damping options N0037, N0039, N0058, N0085, N0102, N0108, N0120 and spare adjustable damping circuit boards with part number 01154-0021-0004). (b) The capacitor manufacturer identified the specific capacitor lots that were inadequately tested. Only adjustable damping circuit boards built with capacitors from these lots are affected. (c) RNII performed subsequent testing and established that Model 1153 and 1154 transmitters with special adjustable damping options N0037, N0039, N0058, N0085, N0102, N0108, N0120 having adjustable damping circuit boards containing capacitors that do not meet RNII IR specifications would not meet the published Nuclear Steam Pressure/Temperature specification and/or Post DBE Operation specification for the published temperature profile. Testing has demonstrated that affected adjustable damping circuit boards do meet product specifications at normal operating temperatures (40-200 degrees F), (d) RNII has initiated actions with the adjustable damping circuit board supplier to ensure that all capacitors received from sub-suppliers are tested to demonstrate compliance with the IR specifications prior to installation on adjustable damping circuit boards. (e) Replacement capacitors have been identified and tested which conform to RNII's procurement specifications. RNII will audit the quality system of the new supplier to assure its quality system meets the requirements of 10CFR Part 50 Appendix B and all requirements of a qualified supplier to RNII. Completion: 6 September 2002. (f) RNII will repair or replace any affected adjustable damping circuit board at the end user's request. Completion: As required. "6.0 Any advice related to the potential failure of the item: "The end user must determine the impact of this deviation upon its plant's operation and safety and take action as deemed necessary. If the end user determines that replacement of the affected special adjustable damping circuit boards is required, please contact Rosemount Nuclear Instruments, Inc. to obtain a replacement adjustable damping circuit board." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2002-08-30
39158 | 0 | LANCASTER LABS |  |  |  |  | 2002-08-20 12:00 | 2002-08-29 09:57 | 2002-08-29 | LOSS OF FOUR (4) GENERALLY LICENSED ELECTRON CAPTURE DETECTORS EACH CONTAINING 15 MILLICURIES OF NICKEL-63. On August 20, 2002 Lancaster Labs discovered that they were missing four (4) Electron Capture Detectors. Each detector contained 15 millicuries of Nickel-63. These electron capture detectors are used in gas chromatograph to measure environmental samples. Three of the electron capture detectors were manufactured by Varian and the fourth on was manufactured by Agilent Technologies. The serial number of the three electron capture detectors manufactured by Varian are A4076, A6796, & A4789. The serial number for the electron capture detector manufactured by Agilent Technologies is F2355. F2355, A4076 and A6796 were last accounted for in the year 1999. A4789 was last accounted for in the year 2000. Lancaster Labs believes that they may have accidentally sold them. Lancaster Labs occasionally sells their used equipment. NRC Region 1, Kathy Modes, was notified of this event by Lancaster Labs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-08-29
39157 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2002-08-29 | 2002-08-29 09:49 | 2002-08-29 | LOSS OF GEOMETRY CONTROL NRC BULLETIN 24 HOUR NOTIFICATION "At approximately 4:30 p.m. on August 28, 2002, two (2) rod storage cabinets were determined to have empty stainless steel trays missing from behind the "nuclear safety blank" position in the rod storage cabinet. The stainless steel tray is included in the model used to analyze the configuration and required as part of the geometry control for the rod storage cabinets. The missing stainless steel structure in the two affected rod storage cabinets constitutes a loss of geometry control. "The independent control on moderation remained intact, thus no unsafe condition existed. "A total of fifteen (15) rod storage cabinets are used in bundle assembly. The remaining 13 cabinets were confirmed to contain the empty stainless steel rod tray behind the nuclear safety blank positions. "The geometry control was re-established at 6:30 p.m. by re-installation of the required empty trays within 4-hours of discovery. This condition is reported pursuant to NRC bulletin 91-01 (within 24 hours) due to a loss of geometry control. Implementation of additional corrective actions is pending completion of incident investigation. "SAFETY SIGNIFICANCE OF EVENTS: "Low safety significance - rod trays limited to [...] rods; moderation control remained intact. "POTENTIAL CRITICAL PATHWAYS INVOLVED ((BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR)): "Multiple failure modes required before a criticality accident could occur. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Geometry and moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST BASE CRITICAL MASS): "Only two (2) rod storage cabinets impacted: the first cabinet contained only 5 loaded and 13 empty authorized storage locations. The second cabinet contained only 2 loaded and 16 empty authorized storage locations. The critical safety analysis for the affected rod storage cabinet models [..] rods per tray. Operational procedures limit each tray to [...] rods maximum. The rod storage cabinet analysis conservatively assumes each tray under full water moderation, optimal interunit H2O, full water reflection conditions, for 5% enriched UO2 rods. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The geometry control provided by rod storage cabinet design incorporates 304SS rod trays, including 304SS empty trays structure located behind the nuclear safety blank positions. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Storage of additional loaded rod trays was suspended. Geometry control was restored by re-installing the required empty stainless steel rod trays behind the nuclear safety blank positions. This activity was completed at 6:30 p.m. on 5/28/02 "Investigation of event and evaluation of additional corrective actions pending." Licensee will notify NRC Region 2 of this event notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2002-08-29
39156 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-08-26 | 2002-08-28 00:35 | 2002-08-28 | AGREEMENT STATE REPORT INVOLVING A LOST/STOLEN TROXLER GAUGE A Troxler gauge, model 3411, was found missing from a storage building at a Redlands, CA location. The gauge, serial number 12878, contains Cs-137 and Am-241/Be. Local law enforcement has been notified and a reward has been offered for it's return. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-08-30
39155 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-08-27 | 2002-08-27 16:06 | 2002-08-27 | AGREEMENT STATE REPORT - REPORT OF LEAKING SEALED SOURCE "On August 27, 2002, Niton Corporation provided a report of a leaking sealed source that was discovered by Niton on July 5, 2002 during removal of a source from a Niton XLi Series X-ray fluorescence device source holder. The seal source is AEA Model IEC.A1, S/N 8740LG containing Fe-55. The estimated leakage was 130,000 dpm (0.059 microcuries). "The leaking source was placed in a lead pig. The source holder was decontaminated. The workbench and surrounding area were surveyed and found to be free of contamination. The leaking source and all decontamination material were placed into the licensee's waste stream." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-08-30
39154 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-08-27 11:00 | 2002-08-27 15:38 | 2002-08-27 | CONTRACT SUPERVISOR TESTED POSITIVE FOR ILLEGAL DRUGS A contract supervisor was determined to be under the influence of an illegal drug during a random test. The contractor's access to the plant has been terminated. Contact the HOO for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2002-08-27
39153 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2002-08-27 10:55 | 2002-08-27 12:01 | 2002-08-27 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF DEAD AMERICAN CROCODILE The licensee discovered a dead crocodile (about 8 feet long) near the plant in the cooling canal. US Fish and Wildlife Service and Florida State Fish and Wildlife Conservation Commission will be notified. The death appears to be the result of attack by another crocodile. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-08-27
39152 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-08-24 20:00 | 2002-08-25 00:45 | 2002-09-18 | GAS VOIDING IN ECCS PIPING "At 0425 hrs on 8/24/2002, a gas void was identified in Emergency Core Cooling System (ECCS) piping at Beaver Valley Power Station (BVPS) Unit No. 2 that exceeded the gas void volume limit of .872 cubic feet. A gas void which exceeds .872 cubic feet could potentially disable a single High Head Safety Injection (HHSI) pump if ingested. The gas void was located in the 'B' train piping which would be used (only) following the transfer-to-recirculation phase of a Loss of Coolant Accident (LOCA). Technical Specification Action 3.5.2.a and 3.5.2.d was entered for 'B' ECCS train not being operable. The piping where the void was located leads to a common HHSI pump suction header which connects to both trains' HHSI pumps. "At 1345 hrs on 8/24/2002, an isolation valve (2SIS-MOV863B) was de-energized closed. De-energizing this isolation valve prevents the gas void traveling to the common HHSI suction header during transfer-to-recirculation flow. This was done as a general precaution to strengthen the operable 'A' HHSI train during the ongoing gas void generation investigation since this gas void generation process was not yet fully understood. "At 1638 hrs on 8/24/2002 it was calculated that the actual gas void volume in the 'B' train piping was 1.3 cubic feet. It was also identified that the previously established gas void volume limit of .872 cubic feet was incorrect and the applicable gas void volume limit was .319 cubic feet. With an evaluation of the new gas void limit, it was concluded at 2000 hrs that BVPS Unit No. 2 had been vulnerable to a degradation of both trains' HHSI pumps between 0425 and 1345. This would be possible since the gas void could potentially have split in half (0.65 cubic feet) and migrated during post-LOCA transfer-to-recirculation flow through the common HHSI suction header. Each half-sized void could enter each train's HHSI pump, potentially affecting both trains of HHSI pumps (.65 cubic feet would exceed the limit of .319 cubic feet for each pump). This is reportable pursuant to 10CFR50.72(b)(3)(ii)(B) as being in an unanalyzed condition that significantly degraded plant safety. This is also reportable pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of systems needed to mitigate consequences of an accident. "Currently with 2SIS-M0V863B de-energized closed, the gas void can not travel to the 'A' train HHSI pump. Actions are being initiated to eliminate this gas void. BVPS Unit No. 2 remains in Tech Specification Action 3.5.2.a and 3.5.2.d for one ECCS subsystem inoperable. The investigation of the gas void generation process is continuing." The NRC Resident Inspector was notified. ***RETRACTION KEN TIEFENTHAL TO MIKE NORRIS 9/18/02 1743 EDT*** "Beaver Valley Power Station (BVPS) Unit No. 2 retracts the notification made on 08/25/2002 at 00:45 hrs regarding the event reported under 10 CFR 50.72(b)(3)(ii)(B) and 50.72(b)(3)(v)(D) [ENS #39152]. "Subsequent analysis of the event identified that the gas void previously located in the Emergency Core Cooling System (ECCS) piping at BVPS Unit No. 2 would not have rendered either train's High Head Safety Injection (HHSI) pump incapable of performing its intended safety function. A detailed evaluation of the void size and the exact piping arrangement concluded that for an analyzed void size of 3 cu. ft. (which bounds the as-found void), the void fraction reaching the HHSI pump would have been 5% or less. At this level of void fraction, a HHSI pump at BVPS Unit No. 2 would have continued to operate and pass flow through the discharge lines to the RCS during the short duration when the void was present. The small temporary degradation in flow would also not have adversely affected any transient in progress. Therefore, the HHSI pumps would have been able to pass the void and continue to perform its safety function if the ECCS had been called upon to operate. "Given that both trains of HHSI were able to perform their safety functions, this void was not a condition that significantly degraded plant safety and did not prevent the ECCS system from being able to fulfill its safety function." The Licensee has notified the NRC Resident Inspector, notified R1DO (Kinneman). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2002-08-25
39151 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-08-24 07:50 | 2002-08-24 10:40 | 2002-08-24 | LOSS OF CALVERT COUNTY EP SIREN ACTIVATION SYSTEM DUE TO LIGHTNING STRIKES "At 07:50 on 8/24/02, notified by system engineer that Calvert County sirens are out of service due to multiple lightning strikes affecting the Calvert control center siren activation circuit. The county is using route alerting as a compensatory measure." The NRC resident inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-08-24
39150 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-08-24 08:26 | 2002-08-24 09:33 | 2002-08-24 | PLANNED LOSS OF THE EOF FOR 20 HOURS "During performance of planned maintenance, the Emergency Operation Facility (EOF) will be without ventilation capabilities. These maintenance activities, including electrical isolation and restoration are expected to last approximately 20 hours. Contingency plans for emergency situations have been established. "This event is reportable per 10 CFR50.72(b)(3)(xiii) since this constitutes a loss of an emergency response facility for the duration of the evolution. "The NRC Resident has been notified." * * * UPDATE AT 1445EDT ON 8/24/02 FROM STEVE KOCHERT TO S. SANDIN * * * At 1335CDT on 8/24/02 the EOF was declared functional and restored to operation. The licensee will inform the NRC Resident Inspector. Notified R4DO(Johnson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-08-24
39149 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2002-08-24 07:50 | 2002-08-24 08:50 | 2002-08-29 | PLANNED OUTAGE ON ERFIS SYSTEM "Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS) inoperable due to planned outage of the Emergency Response Facility Information System (ERFIS). "At 07:50 Hours on August 24, 2002, the H. B. Robinson Steam Electric Plant, Unit No. 2, ERFIS computer system was removed from service for a planned outage to upgrade this system. The expected duration of the outage is approximately 5 days. During this time, the ERDS and SPDS will be unavailable. Alternate means are identified in the HBRSEP, Unit No. 2, emergency preparedness procedures to collect and distribute data that would normally be available by the SPDS. The HBRSEP, Unit No. 2, Emergency Response Organization remains able to respond to an event during the time the ERFIS is unavailable. "The planned ERFIS changes. when completed, are not expected to change the ERDS transmission format or data point library. Therefore, additional reports in accordance with 10 CFR 50, Appendix E, VI. 3. a and b are not expected. "The NRC Resident Inspector has been notified." * * * UPDATE 1540EDT ON 8/29/02 FROM CHRIS CHURCH TO S. SANDIN ERFIS was returned to service as of 1058EDT on 8/29/02. The licensee will inform the NRC Resident Inspector. Notified R2DO(Cahill). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-08-24
39148 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2002-08-23 | 2002-08-23 15:45 | 2002-08-23 | 10 CFR 21 REPORT: MAIN STEAM LINE OUT-OF-SERVICE The following is taken from a facsimile report: "This letter provides notification of a Reportable Condition under 10CFR 21.21(d) and as an interim report per §21.21.(a)(2) for other plants that may be determined to be affected. The basis for this conclusion is that a 1988 GE Nuclear Energy (GE) analysis for Brunswick Units 1 and 2 full power operation with one Main Steamline Isolation Valve (MSIV) Out of Service (OOS) provided to Carolina Power and Light (CP&L) did not adequately address the increased flow induced vibratory loads on the MSIVs to assure they would be able to perform their required safety function which could result in potential offsite exposures in excess of those in 10CFR100.11. "The GE MSIV OOS analysis evaluated plant operation at 100% power with three active steamlines and one set of MSIVs closed (OOS). The GE analysis did not address the increased steam flow hardware effect of potential long-term flow induced vibration degradation on the MSIVs, including the effect on the MSIV air operated controls. During three steamline operation the steam flow in each line would increase to approximately 133% of normal flow. No vibration measurements (empirical or experimental data) exist for either Brunswick Units during operation up to this increased steam flow level. "If it is postulated that the plant operated for an extended period in the MSIV OOS condition and then a main steam line break is postulated to occur in one of the three operational steam lines, then there is the potential that neither MSIV would close to terminate the release from a steamline break. Because GE has no analytical or experience basis (no available empirical or experimental data) to support higher main steam line flow rates greater than previously tested, it could be postulated that a common mode failure of both MSIVs, in the broken line, could occur. Alternatively, failure of one MSIV due to the high flow induced vibration and the other MSIV as the design basis single failure, would result in an un-terminated release, which would exceed the existing 10 CFR 100 radiation release limits. "GE has verbally communicated to CP&L the need for the 75% power limitation when exercising the MSIV OOS flexibility and will follow-up with a written communication. "GE is reviewing all other MSIV OOS analyses performed by GE for other BWRs and will communicate to any similarly affected utilities, similar corrective actions. GE will notify all affected utilities that GE recommends operation at the 75% power level when operating with one MSIV 005, unless there is sufficient test data to support operation at a higher power level. This effort will be completed by September 30, 2002." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-08-23
39147 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-08-23 | 2002-08-23 14:00 | 2002-08-23 | AGREEMENT STATE REPORT INVOLVING OVEREXPOSURE OF RADIOGRAPHY COMPANY EMPLOYEE "Event Report ID No.: LA020010 "Event Date and Time: June 10, 2002 to July 9, 2002 "Event Location: Gonzales Industrial X-ray in Prairieville, LA "Event type: Overexposure "Notifications: The LDEQ received a letter from the facility on August 23, 2002. "Event description: [An employee] received an overexposure of 20864 mrem from June 10, 2002 to July 9, 2002. In the letter received from Ronald Williams, Sr. (RSO), it was stated that [the employee] had constantly misplaced his Landauer badge and would later find it in the area where they were performing radiography. In another instance [the employee] left his Landauer badge in equipment bag while it was adjacent to the camera. The facility requested an investigation by Landauer to see if the exposure was accurate. Landauer stated that the badge was assessed again and judged to be accurate. [The employee's] daily dosimeter readings were recorded, but never went off scale." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-08-28
39146 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-08-23 | 2002-08-23 14:00 | 2002-08-23 | AGREEMENT STATE REPORT INVOLVING OVEREXPOSURE OF TWO RADIOGRAPHERS DURING 2001 "Event Report ID No.: LA020009 "Event Date and Time: January 2002 "Event Location: Gonzales Industrial X-ray in Prairieville, LA "Event Type: Overexposure "Notifications: The LDEQ received a letter from the facility on August 23, 2002. "Event Description: Two industrial radiographers received an excessive exposure for the year 2001. [One Radiographer] received a dose of 5181 mrem and [the other] received a dose of 5408 mrem. These two employees utilize Ir-192 for radiography jobs. The procedures have been changed to prevent this type of occurrence. The facility has started a computerized database that will track the exposure levels daily and monthly for each employee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-08-28
39145 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-08-22 16:50 | 2002-08-22 17:25 | 2002-08-22 | UNIT 2 DECLARED AN UNUSUAL EVENT DUE TO A FIRE IN THE TURBINE BUILDING "Fire in Turbine Building at H2 Dryer lasting for greater than 15 minutes. Fire out at 1655 [hours]. Fire reported at 1633 [hours]." The Fire Brigade responded and extinguished the fire. The Hydrogen Dryer has been isolated. Offsite assistance was not requested. There were no injuries reported. A preliminary assessment revealed extensive damage to the Hydrogen Dryer as a result of the fire. The cause of the fire is under investigation. There were no maintenance activities, e.g., welding, in progress at the time. Operators manually tripped Unit 2. All rods fully inserted. The plant responded as expected. No secondary reliefs lifted. Auxiliary Feedwater autostarted to maintain Steam Generator water levels. The Main Condenser is in-service removing decay heat via the main steam dumps. Cooldown limits were not exceeded during the transient. Unit 2 will remain in mode 3 pending completion of the investigation. The licensee informed state/local agencies and the NRC Resident Inspector. * * * UPDATED AT 1855 EDT ON 8/22/02 BY DENNIS MOORE TO FANGIE JONES * * * Unusual Event terminated at 1830 EDT. The fire extinguished when the hydrogen isolation valve was closed, automatic sprinkler system actuated which allowed personnel access to the isolation valve. The licensee notified the NRC Resident Inspector. Notified the R2DO (Ken Barr), NRR EO (John Hannon), IRO (Joe Holonich), and FEMA (David Barden). * * * UPDATED AT 2023EDT ON 8/22/02 BY WAYNE HOYLE TO S. SANDIN * * * The licensee furnished the following additional information: "On August 22, 2002 at 1636 hours, a manual reactor trip was initiated on McGuire Unit 2 in response to a fire in a hydrogen dryer in the hydrogen supply to the Unit 2 Turbine Generator. As a result of the fire, the hydrogen supply to the turbine generator experienced a low pressure condition and plant operators manually tripped the reactor (RPS Actuation) to prevent damage to the turbine generator. Following the trip, the Unit 2 Auxiliary Feedwater Pumps started due to loss of Unit 2 Main Feedwater Pumps (Auxiliary Feedwater System Actuation). Subsequent to the start of the Unit 2 Auxiliary Feedwater Pumps, the 2C Steam Generator experienced a HI-HI water level. Level was restored and the water level in all four Steam Generators is currently in the normal band for existing plant conditions. "The fire in the Unit 2 hydrogen dryer has been extinguished. Plant equipment necessary to safely shutdown Unit 2 operated correctly and the Unit is stable and in Mode 3. The Unit 2 Auxiliary Feedwater Pumps are still running supplying the Steam Generators. An investigation into the cause of the fire is in progress. "The NRC Resident Inspector has been notified." Notified R2DO(Barr). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 0 | 2002-08-22
39144 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-08-22 16:33 | 2002-08-22 17:06 | 2002-08-23 | UNANALYZED CONDITION CONCERNING STEAM GENERATOR ATMOSPHERIC RELIEF VALVE BYPASS VALVES Historical analysis deficiencies associated with the steam generator atmospheric dump bypass valves, a condition that during a fire could cause seriously degrade the safety of the plant. "The system affected is main steam, there are no actuation signals. The cause is historical analysis deficiencies. There are no affects on the plant. There are no actions taken or planned at this time and there is no additional information. The NRC Resident Inspector was notified. The State and Local Authorities have been notified." * * * UPDATE 1605EDT ON 8/23/02 FROM MICHAEL MARTELL TO S. SANDIN * * * The following information from Millstone Condition Report CR-02-08666 was provided by the licensee as an update: "On August 22, 2002, with Millstone Unit 3 in Mode 1, and as a result of transient analysis of the fire shutdown scenarios, the potential for spurious operation associated with the Main Steam atmospheric dump valve bypass motor operated valves (3MS*MOV74A thru D) from a hot short was found to result in non-compliance with the BTP 9.5-1 performance criteria. The Millstone Unit 3 licensing basis regarding BTP 9.5-1 performance criteria provides that a fire in an alternate shutdown area shall pose a transient no more severe than a reactor trip due to loss of normal power and that pressurizer level remain in the indicating range. Spurious operation of plant components due to credible hot shorts must be postulated and have methods for mitigation that do not require the use of any other component potentially affected by the fire. The current BTP 9.5-1 compliance report and shutdown methods address the spurious opening of the Main Steam atmospheric dump valve bypass motor operated valves. Fire safe shutdown procedures provide methods for mitigating this spurious actuation. "On-going effort to validate assumptions used in the fire safe shutdown analysis concluded that insufficient operator response time was available to support mitigation of this transient. It has been determined that spurious opening of one of the dump valves could cause pressurizer level to go below the indicating range in a time frame shorter than originally assumed. This condition is being reported as an unanalyzed condition that significantly degrades plant safety, pursuant to 50.72 (b)(3)(ii)(B). "It should be noted that, consistent with the Licensing Basis, this analysis assumes a fire of sufficient magnitude to result in an instantaneous hot short. Such fires are viewed to be very low probability events. The fire areas of concern are the control room and cable spreading area. The control room is continuously manned, and currently a continuous compensatory fire watch is required in the cable spreading room for other conditions. No additional compensatory actions are judged to be necessary at this time. Corrective actions are under evaluation in accordance with the Millstone corrective action program." The licensee informed the NRC Resident Inspector. Notified R1DO(Noggle). | 0 | 0 | 95 | 0 | 0 | 95 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-08-22
39143 | 0 | VA NATIONAL HEALTH PHYSICS PRGM |  |  |  |  | 2002-08-20 | 2002-08-22 12:34 | 2002-08-22 | REPORT OF POSSIBLE MISADMINISTRATION AND/OR SAFETY EQUIPMENT FAILURE On 8/20/02 a patient was being prepared for treatment in a Co-60 teletherapy unit by two technicians when the beam turned on with no operator action. The beam was on for about 50 seconds. The event is being investigated and the unit has been placed out-of-service. It is unknown at this time whether the patient was in position or not and received an exposure to the right or wrong site. The investigation will determine if there was an actual misadministration, exposure to the wrong area. The two technicians' dosimeters were processed and the results showed no exposure in excess of limits, actual reading was 20 millirem for both badges. The licensee will update this report when more information is determined. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | SAFETY EQUIPMENT FAILURE | [8 empty] | NON EMERGENCY | 1 | NY | HOS |  | 35.33 | 30.50(b)(2) |  |  | 0 | 2002-08-22
39142 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-08-21 14:00 | 2002-08-21 21:03 | 2002-09-13 | UNANALYZED CONDITION REGARDING RCS BORATION REQUIREMENTS "On August 21, 2002, with Callaway Plant in Mode 1 at 100 % power, it was determined that a potential unanalyzed condition had existed regarding Reactor Coolant System (RCS) boration requirements when in Mode 3 below the P-11 setpoint of 1970 psig RCS pressure. During an extent of condition review, a concern had been identified regarding the Westinghouse analysis of Steam Line Breaks in Mode 3 below P-11. In order to conclude that acceptable core performance results would be obtained for a lower Mode 3 Steam Line Break, the Westinghouse analyses assumes that the plant is borated to cold shutdown conditions prior to blocking P-11. Discussions with Westinghouse confirmed this requirement was applicable to Callaway. Callaway Plant procedures did not specifically require that the plant be maintained at Cold Shutdown boron concentrations with P-11 blocked. A historical review documented that the Callaway Plant shutdown twice within the last three years. During these shutdowns, the plant maneuvered through Mode 3 below P-11 once during each plant shutdown and once during each plant startup. "A review of historical data is being conducted for those periods to establish actual boron concentrations versus calculated requirements for past conditions. Preliminary reviews for three of those periods have been completed and document actual boron concentrations of 1397 ppm or greater. "This condition is being reported as an unanalyzed condition until historical reviews determine otherwise. Compensatory actions taken included determining a boron concentration that would satisfy accident analysis requirements for present plant conditions and revising Callaway Plant procedures to require boration to specified boron concentrations for Mode 3 operation with P-11 blocked." P-11(Pressurizer SI Block Permissive) enables BLOCK switches to allow the operator to block low Pressurizer pressure SI. The NRC Resident Inspector has been notified. The Licensee has discussed this condition with Wolf Creek. ****RETRACTION ON 09/13/02 AT 1527ET BY E. HENSON TAKEN BY MACKINNON**** Upon completion of a review of historical data encompassing the previous three years of plant operation, it was determined that sufficient boron concentrations were maintained to ensure compliance with accident analysis requirements when in Mode 3 below P-11. Based upon this information, no unanalyzed condition existed and Event Notification # 39142 is being retracted. R4DO (Jack Whitten) notified. The NRC Resident Inspector was notified of this event retraction. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-08-21
39141 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-08-19 | 2002-08-21 15:02 | 2002-08-21 | AGREEMENT STATE REPORT INVOLVING MEDICAL MISADMINISTRATION "The licensee reported that a patient received 2640 cGy (rad) during a cardiac intravascular brachytherapy treatment instead of the intended 2000 cGy (rad), a 32% overexposure. The patient was being treated with the Guidant Corporation Galileo intravascular brachytherapy high dose rate remote afterloader device (serial #27958502) with a model GDT-P32-2 source wire (serial #020807016) containing 4.44 GBq (119.9 [millicuries]) of P-32 at time of treatment. The patient's vessel size was larger than the automatically calculated maximum diameter treatment. A manual calculation of dwell time was required, based on the dose rate tables available in the Guidant Manual (section 6.13 table 5). However, the dose rate for a 4.6 mm diameter (3.30 mm treatment depth) was inadvertently used instead of 4.05 mm diameter (3.03 mm treatment depth). This resulted in a delivered dose of 2640 cGy (rad) at 3.03 mm. The cause of the event is human error. The licensee's corrective action is to have a second independent calculation performed by Physics and Dosimetry staff prior to treatment whenever a manual calculation using the dose rate tables is necessary. No adverse consequences are expected. The referring physician and the patient were notified of the overexposure." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-08-26
39140 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2002-08-21 07:30 | 2002-08-21 08:59 | 2002-08-21 | UNUSUAL EVENT DECLARED DUE TO FIRE AFFECTING EMERGENCY CORE COOLING SYSTEM Loss of "A" Train Service Water as a result of a fire on the "1C" Service Water pump. The "1C" pump tripped and the "1A" Service Water was out of service for maintenance. Fire was out at 0724 CDT. Actions being taken to restore the "A" Train Service Water. The "1B" Service Water pump remained running during the entire event. System pressure remained at required value. The Fire Protection System for the "1C" Service Water pump actuated and extinguished the fire. When the fire brigade arrived the fire was already out. The licensee did not need offsite help for the fire. "B" Train Service Water is operating. The licensee notified State and local officials of the declaration of an Unusual Event. The NRC Resident Inspector was notified of this event by the licensee. ****UPDATE AT 0931 ET ON 08/21/02 BY BOB VANDERBYE TAKEN BY MACKINNON**** Unusual event has been terminated at 0814 CT as a result that there was no fire and the plant is stable. No fire was seen but a large arc was seen when the "1C" Service Water pump tripped. State and Local officials will be notified by the licensee that the Unusual event was terminated at 0814 CT. R2DO (Ken Barr), NRR EO (Terry Reis), & FEMA (Ken Ciboch) notified. The NRC Resident Inspector will be notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-08-21
39139 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-08-20 10:30 | 2002-08-20 16:50 | 2002-08-20 | UNANALYZED CONDITION FOR POST FIRE SAFE SHUTDOWN "On August 20, 2002, conditions were discovered where a postulated fire could cause the loss of both Centrifugal Charging Pumps (CCP) capability to successfully inject borated water to the reactor and to keep the Reactor Coolant Pump (RCP) seals cool. Wolf Creek is in Mode 1, at 100% power. "During reviews associated with post fire safe shutdown reanalysis work, Wolf Creek personnel discovered that power and control cables for both CCP train minimum flow valves, both train CCP discharge valves to the RCP seals, and both train CCP suction valves from the Volume Control Tank (VCT) and Refueling Water Storage Tank (RWST) are routed in electrical raceways in the same fire area with intervening combustibles between the two redundant trains. This does not meet our commitments to 10CFR50 Appendix R.lll.G as reflected in our approved Fire Protection Plan. "Following a fire In the plant that requires a plant shutdown, the function of the CCP is to inject borated water into the reactor to maintain reactor water inventory, maintain shutdown reactivity margin, and to maintain a cooling water flow to the RCP seals to prevent damage to the seals. A fire in this fire area has the potential to cause the above-mentioned valves to not function properly and cause a loss of the capability to borate, maintain inventory, and to cool the RCP seals. "Based on the guidance provided in NUREG 1022, Revision 2, this situation meets the criterion of 10CFR50.72(b)(3)(ii)(B) for an 8-hour ENS notification, as it relates to being in an unanalyzed condition. "The licensee has previously implemented a 1-hour fire watch in this fire area." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-08-20
39138 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-06-28 | 2002-08-19 16:47 | 2002-08-19 | AGREEMENT STATE REPORT INVOLVING 2 MEDICAL MISADMINISTRATIONS "Alabama licensee identifies two misadministrations from previous year. "By telephone notification on June 28, 2002 the University of South Alabama (Alabama Radioactive Material License No. 582) notified the State of Alabama that during their annual Quality Management Program review they identified two possible misadministrations of Iodine-131 from the previous year. "By letter dated July 8, 2002, and received by the State of Alabama on July 11, 2002, the University of South Alabama confirmed that a review of the records revealed that: "A. On April 3,2002, a patient was given 3.9 [millicuries] of iodine-131 for a total body diagnostic scan when 3.0 [millicuries] had been prescribed by the authorized user. The administered dose exceeded the prescribed dose by 30%; and "B. On August 7,2001, a patient was administered 0.702 [millicuries] of iodine-131 for a whole body diagnostic scan when 0.500 [millicuries] had been prescribed by the authorized user. The administered dose exceeded the prescribed dose by 40%. "In both cases the patients attending physician concluded that these doses had 'no clinical significance to either patient and therefore no untoward effects.' He ordered that this not be reported to the patients. "According to the licensee, these events occurred because the nuclear medicine staff was operating under a window wider than the 20% maximum deviation allowed in the 420-3-26-.07(2)(m)1.b of the Alabama Rules for Control of Radiation. The licensee stated that the nuclear medicine department had been using criteria from an article published in the Journal of Nuclear Medicine which 'quoted NRC regulations with a greater tolerance.' "The licensees corrective action was to notify nuclear medicine staff members both verbally and in writing of the current Alabama regulations. The State of Alabama considers the licensee's actions to be appropriate and the matter closed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-08-22
39137 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-08-19 | 2002-08-19 16:33 | 2005-02-14 | AGREEMENT STATE REPORT INVOLVING THEFT OF MOISTURE/DENSITY GAUGE "The licensee reported the theft of a Campbell Pacific Nuclear moisture/density gauge (model MC-1DRP, serial number MD01005902). The gauge contained a 1.85 GBq (50 [millicuries]) Am-Be source and a 0.37 GBq (10 [millicuries]) Cs-137 source. An authorized user had been working at a temporary job site for two weeks. On Sunday, August 18 at 8:00 p.m. the authorized user parked his pick-up truck in the parking lot of a local motel in Centralia. The gauge was in back under the locked canopy, but visible. The gauge box was locked but not secured within the bed of the truck. When the authorized user went out to his truck at 6:00 a.m. on Monday the 19th the gauge was gone. The back window of the canopy had been forced open. Nothing else was missing from the truck (not much else of value was in the truck). The theft was reported to the Centralia police and to the licensee's RSO. The RSO notified the Department." * * * * UPDATE FROM STATE (A. SCROGGS) VIA EMAIL 02/14/05 1800 EST * * * * The following information was received from the State via email: "On Friday February 4, 2005 an employee of another engineering firm noticed the gauge at a garage sale in Centralia, Washington. The employee noted the gauge ID specifics and had his RSO contact the gauge manufacturer for information. When informed by the manufacturer that it had been stolen, the employee was able to involve the police and secure the gauge. The individual responsible for the garage-sale was subsequently arrested. The owner, URS Corporation was notified and is presently having the gauge serviced and leak tested by a licensed technical service provider. They plan to retake ownership when this work is completed." Notified R4 DO (J. Whitten) and NMSS EO (W. Reamer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-08-22
39136 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-08-19 02:32 | 2002-08-19 10:36 | 2002-08-22 | REACTOR BUILDING EMERGENCY RECIRCULATION UNIT COOLER ANOMALY IDENTIFIED DURING ROUTINE SURVEILLANCE TEST "On August 19, 2002 at 0232, Reactor Building Emergency Recirculation Unit Cooler, 2HVR*413A, was declared inoperable due to Reactor Building Emergency Recirculation Unit Cooler Inlet Damper, 2HVR*AOD6A, not reaching its full open position during testing. Failure of 2HVR*AOD6A to fully open may affect the flow-rate through the Reactor Building Emergency Recirculation Unit Cooler and may prevent the Standby Gas Treatment System from performing its Post-LOCA Secondary Containment drawdown function. The manual operating mechanism was returned to its withdrawn position and 2HVR*AOD6A was verified to be capable of being fully opened. Opposite train components were inspected to confirm that a similar condition does not exist on Train "B". This notification is being made as a conservative measure. Evaluation coritinues into the actual affect on Post-LOCA drawdown function." The NRC Resident Inspector was notified. * * * 1410EDT on 8/22/02 from Dave Richardson to S. Sandin * * * The licensee is retracting this report based on the following: "The purpose of this communication is to retract event report number 39136 which was initiated at 1030 hours on 08-19-2002, by Nine Mile Point Unit 2. This event, reported under 10CFR50.72 (b)(3)(v)(C), involved unplanned inoperability of a Reactor Building Emergency recirculation unit cooler due to its inlet damper being found partially overridden shut. "Evaluation revealed that, when called upon to reposition to its emergency position, the damper was approximately 97% open. Based on Engineering analysis, with the damper in this position, there is 'no appreciable increase in system resistance' that would adversely impact the HVR (reactor building ventilation) or GTS (standby gas treatment) system flowrates. As a result, this condition would not have precluded the aforementioned systems from performing their respective safety functions." The licensee informed the NRC Resident Inspector. Notified R1DO(Anderson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2002-08-19
39135 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-08-16 14:15 | 2002-08-16 20:48 | 2002-08-19 | STEAM GENERATOR BLOWDOWN VALVE 1MS-5959 MAY NOT CLOSE AGAINST FULL STEAM GENERATOR PRESSURE. "A draft calculation (01109-C-015) and a review of this calculation concluded that 1MS-5959 would not shut against the maximum differential pressure (dp) assumed within the calculation. The actual dp used for the calculation review is based on the SG atmospheric dump valve set point of 1085 psig. This is the SG pressure assumed for aux feed flow requirements to the SGs. At this dp (1085 psig), 1MS-5959 blow down isolation valve would not shut (1MS-5959 HX-1A SG-Blow down isolation ). All other (3) steam generator blowdown valves would shut against this d/p. "The blowdown isolation valves are required to isolate to support two functions; 1) containment isolation and , 2) steam generator pressure boundary isolation. The containment isolation function is a class 4 containment penetration (FSAR page 5.2-3), which is a normally operating line connected to a closed system inside of containment, provided with at least one manual valve located outside of containment, and missile protected throughout its length. FSAR Figure 5.2-51-2 lists manual valve 1MS-265 as the containment isolation valve, but also lists 1MS-5959 as an isolation valve inside of containment. Although 1MS-5959 may not be able to close at full SG pressure, it is expected to be able to close at the maximum containment design pressure (60 psig), which may occur if a SG is faulted. Since the requirement for class 4 penetration is still met by using 1MS-265, and 1MS-5959 would still function under the conditions of a faulted SG, the containment isolation function of 1MS-5959 is considered to be operable. "The function to establish the SG pressure boundary is based on the requirements of the Chapter 14 accident analysis for the Loss of Normal Feedwater (LONF, Section 14.1.10) and the Loss of All AC Power to the Station Auxiliaries (LOAC, Section 14.1.11). The accident analyses credit 200 gpm AFW flow delivered to the SGs after a five minute delay. The acceptance criteria for both accidents is that the pressurizer does not overfill. Overfilling of the pressurizer could result in a small break LOCA due to the assumed failure of a pressurizer safety valve or PORV when passing liquid. If the SG blowdown valve cannot perform its isolation, then an undetermined (although significant) portion of the AFW will be diverted from flowing around the u-tube region. Heat removal assumed in the analysis will not meet the minimum credited in the accident analysis based on a full 200 gpm AFW flow. "1MS-5959 was shut based on engineering judgement and declared inoperable at 1415, 08/16/02. The valve operator on 1MS-5959 was adjusted per routine maintenance procedure (RMP) 9141, Air operated valve testing and adjustment, such that the valve would shut under the analyzed conditions. 1MS-5959 was declared operable at 1925 08/16/02." The NRC Resident Inspector was notified of this event by the licensee. **UPDATE CHUCK KRAUSE TO MIKE NORRIS 1409 EDT 8/19/02** Update to make corrections to initial report. Referenced FSAR figure 5.2-51-2 should be FSAR figure 5.2-50-1, and manual valve 1MS-265 should be 1MS-266. Notified R3DO (Lanksbury). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-08-16
39134 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-08-14 | 2002-08-16 11:02 | 2002-08-16 | AGREEMENT STATE REPORT - PERSONNEL OVER EXPOSURE "Cyclotron chemistry technician received 4.56 rem TEDE in one week. The worker's exposure for the calendar year is now 5.79 rem. The cause of the additional exposure is related to work performed directly with cyclotron target material. This exposure was incurred over a period of one week. The details of the event are under investigation." The exposure took place the week of July 28 to August 4, 2002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-08-21
39133 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-08-15 16:00 | 2002-08-16 10:54 | 2002-09-11 | NRC BULLETIN 91-01 24 HOUR REPORT - LACK OF APPROVED NCS EVALUATION FOR OPERATION The following is taken from a facsimile report: At 1613, on 08-15-02, the Plant Shift Superintendent (PSS) was notified that a fissile material operation was identified without an approved NCS evaluation. Two full 2S sample cylinders, which originated outside of C-310, were evacuated to the cascade via the sample cabinet in C-310. No NCSE exists to cover refeed operations of 2S cylinders in the C-310 Liquid Sampling System. Thus, no NCSA controls have been established to perform this operation in C-310. The NRC Senior Resident inspector has been notified of this event. SAFETY SIGNIFICANCE OF EVENTS: Two full 2S cylinders do not contain sufficient mass of uranium to support a criticality. However, double contingency was not maintained because no NCSA controls have been established to perform this operation in C-310. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) In order for a criticality to be possible, more than a critical mass would have to be accumulated in an unsafe geometry. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY. CONCENTRATION, ETC Since this operation does not have an NCSA for it, there is no controlled parameter. ESTIMATED AMOUNT, ENRICHMENT, FORMS OF LICENSED MATERIAL (INCLUDES PROCESS LIMIT AND % WORST CASE CRITICAL MASS): 2S Cylinder N-260 - [ ]grams UF6 with an enrichment of [ ]% U-235. 2S cylinder N-19 - [ ] grams UF6 with an enrichment of [ ]% U-235. NUCLEAR CRITICALITY SAFETY CONTROL SYSTEM(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES Refeed of 2S cylinders in the C-310 Liquid Sampling System has not been evaluated for nuclear criticality safety. Therefore, double contingency was not maintained, CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Revise procedures to prevent the refeed of 2S cylinders, which originated outside of C-310, in the C-310 Liquid Sampling System. * * * UPDATE ON 9/11/02 AT 2224 FROM THOMAS WHITE TO GERRY WAIG * * * "During the event investigation, it was discovered that no NCSE/A exists to cover the transport of 2S cylinders containing fissile material from another facility to C-310. Therefore, no NCSA controls have been established to perform this operation. "Double contingency was not maintained because no NCSA controls have been established to transport 2S cylinders containing fissile material to C-310. "Transport of 2S cylinders containing fissile material to C-310 has also not been evaluated for nuclear criticality safety, Therefore, double contingency was not maintained." The licensee has notified the NRC Resident Inspector of the event report update. Notified R3DO (Christine Lipa) and NMSS EO (Janet Schlueter). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-08-16
39132 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-08-15 21:26 | 2002-08-16 00:49 | 2002-08-16 | AUTOMATIC REACTOR TRIP DUE TO LOW BUS VOLTAGE ON REACTOR COOLANT PUMPS "An automatic reactor trip occurred at 2126 on 8/15/02. The reactor trip was caused by low bus voltage for reactor coolant pumps and the cause is under investigation. All safety systems responded properly. Both motor driven AFW pumps automatically started due to low steam generator level. At 2155, a second AFW actuation was received due to low steam generator level in one steam generator while recovering level. Both motor driven AFW pumps were already running in response to the first actuation signal." A voltage transient occurred when central distribution near Raleigh, NC (about 20 miles away) was restoring a 230 kV to 115 kV bank that had tripped due to a lightning strike. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-08-16
39131 | 0 | U.S. ARMY |  |  |  |  | 2002-08-14 15:05 | 2002-08-15 14:38 | 2002-08-15 | MUZZLE REFERENCE SENSOR (MRS) CONTAINING 10 CURIES OF TRITIUM LOST A New Jersey National Guard Cavalry Tank was at the tank gunner range at Fort Dix on 07/08/02. During the gunnery exercise a beam splitter containing 10 curies of Tritium from an MRS was lost at range. A search of the area did not find the missing beam splitter. The missing beam splitter is cylindrical in shape, 2 inches long by 1 inch wide. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-08-15
39130 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-08-14 13:00 | 2002-08-14 15:15 | 2002-08-14 | HPCI DECLARED INOPERABLE DUE TO FAILURE OF THE HPCI TURBINE CONTROL SYSTEM The Unit 1 High Pressure Coolant Injection (HPCI) turbine control oil pressure control valve diaphragm was discovered ruptured. This prevents HPCI (a single train system) from operating. The plant entered a 14 day LCO with this condition. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-08-14
39129 | 0 | METRO TRANSIT |  |  |  |  | 2002-08-13 | 2002-08-13 22:15 | 2002-08-13 | TROXLER GAUGE WAS LEFT AT A CONSTRUCTION SITE AT THE PENTAGON A Metro Transit police officer noticed a plastic container at a construction site at the Pentagon which gave him a reading of 4 on his radiation detection pager. This item turned out to be a Troxler gauge which was stored in a box near the construction fence at the Pentagon. The Arlington, Va. hazmat team responded and measured 369 microR at the device and secured it. The responsible licensee is Craig Testing Laboratories Inc. located in Region 1. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | VA | OTH | GEN |  |  |  |  | 0 | 2002-08-13
39128 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-08-13 | 2002-08-13 15:40 | 2002-08-13 | THE STATE OF NORTH CAROLINA RECEIVED NOTICED THAT A NITON ALLOY ANALYZER WAS STOLEN. On August 13. 2002 the North Carolina Radiation Protection Section was notified by Southern Resources, 3826 Raleigh St., Charlotte, NC 28208 that a Niton Alloy Analyzer [Model XL 801S] containing a 10 millicurie Cd-109 sealed source [assay date 10/01] was stolen from their office. The local police-department is investigating. The NC Radiation Protection Section, Southern Resources, Niton Corp. and local law enforcement agencies are working together to recover the device. The State has not yet determined if Southern Resources is a State Licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-08-16
39127 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-08-13 11:58 | 2002-08-13 12:39 | 2002-08-13 | TRANSPORTATION EVENT INVOLVING CONTAMINATED TOOLS A truck transporting radioactive material consisting of contaminated tools to Indian Point Unit 2 struck a bridge overpass causing damage to a tool container. None of the material (tools) in the container were released from the container. The licensee reported that the bill-of-laden indicted that the truck had a contact reading of 50 millirem/hour and 5 millirem peripheral reading. The event occurred about 2 miles north of the Indian Point site on Rt. 9. There were no reported injuries and no continuing danger exists. The licensee notified the NRC Resident Inspector. Local law enforcement (Peekskill Police Department) was also notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2002-08-13
39126 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2002-08-13 08:51 | 2002-08-13 11:21 | 2002-08-13 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO EQUIPMENT FAILURE "Loss of Unit 4 Emergency Response Data System transmission capability. Unit 4 data could be sent via the Unit 3 transmission line, however, the simultaneous data transmission capability from both units is inoperable. Troubleshooting revealed a defective modem. Repair plan in progress." The licensee will inform the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-08-13
39125 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2002-08-12 10:30 | 2002-08-13 10:39 | 2002-08-14 | AGREEMENT STATE REPORT - LOST PORTABLE MOISTURE DENSITY GAUGE "A Troxler Electronic Laboratories, Inc. Model 3430, portable gauging device serial number 30302, containing 8 millicuries of cesium-137 (source serial number 750-4769), and 40 millicuries of americium-241/beryllium (source serial number 47-25522) was lost from the bed of a pickup truck while traveling from the licensee's office in Sandy, Utah to a temporary jobsite in West Jordan, Utah." The Utah event report number for this event is UT-02-0002 * * * UPDATE ON 8/14/02 @ 1152 BY FELICE TO GOULD * * * The device was found by another Utah licensee as soon as it dropped off the truck. It was returned to the owner and it did not appear to be damaged. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2002-08-16
39124 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-08-11 12:00 | 2002-08-12 15:24 | 2002-08-12 | EMERGENCY SIRENS DECLARED INOPERABLE The licensee determined at 1427 on 8/12/02 that 17 out of 17 sirens in St Mary's county failed their weekly silent alarm test on 8/11/02 @ 1200. They believe the problem is due to a transmitter malfunction possibly caused from being moved and improperly mounted in their new location. They are currently troubleshooting the problem. The NRC Resident Inspector was notified. They will notify State and Local Agencies | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-08-12
39123 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-08-09 16:00 | 2002-08-09 16:54 | 2002-09-04 | INOPERABLE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM The RCIC System was declared inoperable and the plant entered a 14 day Limiting Condition for Operation (LCO) per Technical Specification 3.5.D. The system was declared inoperable due to an oil leak discovered on the RCIC pump during operability testing. The source of the oil leak is under investigation. The licensee notified the NRC Resident Inspector. * * * RETRACTED AT 0952 EDT ON 09/04/02 BY ERIC OLSON TO FANGIE JONES * * * The licensee is retracting this event notification. The licensee conducted a review of the event and determined that the RCIC System could have performed it's intended function and thus was operable. The licensee notified the NRC Resident Inspector. R1DO (Richard Barkley) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-08-09
39122 | 0 | ROCKBESTOS SURPRENANT CABLE CORP |  |  |  |  | 2002-07-24 | 2002-08-09 13:12 | 2002-08-09 | NOTIFICATION UNDER 10 CFR PART 21 OF FAILURE OF ELECTRIC CABLE TO COMPLY WITH REQUIREMENTS The following text is a portion of a facsimile received from Rockbestos Surprenant Cable Corp.: "This letter shall serve as the initial notification by Rockbestos-Surprenant Cable Corp. that a basic component supplied for use in nuclear power plants may contain a defect or fail to comply, which is reportable under the requirements of 10 CFR 21. "Written notification shall be provided by September 8, 2002. "The following information is supplied in accordance with the requirements of 10 CFR 21. "I. Name and address of individual informing the Commission: Richard C. Brown-Quality Assurance Manager The Rockbestos-Surprenant Cable Corp. 20 Bradley Park Road East Granby, CT 06026 "II. Identification of the basic component supplied which fails to comply or contains a defect: "The cable identified below failed to comply with the vertical tray flame test when subjected to the requirements as described in IEEE-383-1974 section 2.5.4: 2/C 14 AWG 600V Firewall SR (Silicone Rubber) with overall Rockhide braid Sales Order: 52727 Shop Order: 220557 Item: C643385 Reel No.: 02F0693G "This cable was subsequently placed in an MRB location an[d] issued a nonconformance report on 7/24/02. "III. Identification of the firm supplying the basic component which fails to comply or contains a defect: " The Rockbestos-Surprenant Cable Corp.. East Granby, CT facility "IV. Nature of the defect or failure to comply and the safety hazard which is created: "Nature of Defect: Incorrect lacquer material applied to overall Rockhide braid. Potential Hazard: The lacquer material applied to the overall Rockhide braid may contribute to the propagation of flame, resulting in a burn of the entire length of the tray as described in IEEE-383-1974 section 2.5.4. "V. The date on which the information of such defect or failure to comply was obtained: "On the basis of our testing and evaluation it was determined on 7/24/02 that a defect or failure to comply as defined by 10 CFR 21 existed. "VI. The number and location of all basic components which contain a defect or fails to comply: "Our initial investigation indicates that the affected cables are limited to eight part numbers/shipments of multiconductor Firewall SR (Silicone Rubber) cables with overall Rockhide braid manufactured from 1999 through July 2002. "VII. The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: "Production and shipment of all Firewall SR (Silicone Rubber) cables with overall Rockhide braid was stopped on 7/24/02 and all cables in house were identified and nonconformance reports issued as a result of the flame test failure. "Manufacturing instructions and bills of material for all Firewall SR (Silicone Rubber) with overall Rockhide braid products are being reviewed to ensure that all process documents specify approved lacquers. "After review by Applications Engineering, samples of the 2/C 14 AWG nonconforming cables were over braided and lacquered with approved lacquers, and again subjected to the vertical tray flame test of IEEE-383-1974 section 2.5.4. These samples successfully withstood the requirements of the standard. Processing documents for the 2/C 14 AWG and other constructions which were in production, were subsequently issued temporary engineering changes allowing over braid and subsequent lacquer with approved materials. "An additional cable sample of 3/C 12 AWG 600V Firewall SR (Silicone Rubber) without the over braid and utilizing an approved lacquer, was subjected to; and successfully withstood the vertical tray flame test requirements of IEEE- 383-1974 section 2.5.4. "Further flame testing of Firewall SR (Silicone Rubber) cables with overall Rockhide braid is planned on various sizes and configurations to determine the extent of the failure mode, "Production and shipment of cables have resumed for those products originally placed on hold after acceptable results were obtained for the vertical tray flame test as described in IEEE 383-1974 section 2.54. "VIII. Any advice related to the defect or failure to comply about the basic component that has been, is being, or will be given to purchasers: "Purchasers of Firewall SR (Silicone Rubber) products that were manufactured with the overall Rockhide braid and lacquer from 1999 through July 2002 will be notified of the failure mode described above by letter on 8/12/02. Purchasers will be requested to stop any current or planned installation of the aforementioned cables and to notify Rockbestos-Surprenant Cable Corp. for return of any cables not installed. Advice related to installed cables will be provided based on the installed conditions. "The following personnel may be contacted regarding the preceding notification: James Morganelli Senior Quality Engineer (860) 653-8319 Richard Brown Quality Assurance Manager (860) 653-8322 Robert Konnik Director of Applications Engineering (860) 653-8340" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 21.21 |  |  |  | 0 | 2002-08-09
39121 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-08-09 12:10 | 2002-08-09 12:31 | 2002-11-18 | NOUE DECLARED DUE TO LOW WATER LEVEL IN LAKE ANNA The plant declared an NOUE due to lake level falling below 246' which was caused by lack of rainfall. This level may continue to decrease if the drought continues. If the level reaches 244', they will enter TS 3.7.5.1 requiring the plant to be in hot standby within 6 hours and cold shutdown within 30 hours at which time they can exit the NOUE. However, if the level increases to 246.4' they will also exit the NOUE. The NRC Resident Inspector was notified along with State and Local agencies. *** UPDATE ON 11/18/02 at 08:55 FROM RON BUTLER TO RICH LAURA *** Notification on 11/18/02 at 08:55 by the Licensee (Ron Butler) that Lake Anna levels increased above the minimum level of 246'4'' to 246'9'' on 11/18/02 and the UE was terminated at 08:51. Notified R2DO (David Ayres), NRR EO (Stuart Richards), FEMA (Rene Zapata) and DIRO Manager (Joe Holonich). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-08-09
39120 | 0 | FLETCHER ALLEN HEALTH CARE |  |  |  |  | 2002-08-06 14:00 | 2002-08-08 14:13 | 2002-08-08 | MEDICAL MISADMINISTRATION DUE TO EQUIPMENT PROBLEMS A patient receiving brachytherapy treatment received partial treatment due to a fault error message for the guidance intervascular brachytherapy system. This resulted in the wire being withdrawn too soon and the patient only receiving 76 centigrays when the prescribed treatment was 2000 centigrays. The patient and physician were notified and the patient was retreated. NRC Region I was notified by the licensee on 8/6/02 by voice mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | VT | HOS |  | 35.33 |  |  |  | 0 | 2002-08-08
39119 | 0 | ADVANCE TESTING CO |  |  |  |  | 2002-08-06 14:30 | 2002-08-08 12:34 | 2002-08-08 | TROXLER MOISTURE DENSITY GAUGE DAMAGED During a paving job at the intersection of Route 95 and Route 7 in Fairfield, CT, a Troxler Moisture Density Gauge, Model # 3411B, Serial #16237, was run over by an asphalt roller. The gauge contains 8 millicuries of cesium 137 and 40 millicuries of Am-241/Be. The damaged Troxler Gauge was removed from the asphalt and placed in a secure container. The area was isolated and surveyed for contamination. No contamination was identified. The licensee notified the Connecticut Department of Transportation and NRC Region 1 of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN |  |  |  |  | 0 | 2002-08-08
39118 | 0 | US ARMY |  |  |  |  | 2002-08-07 14:00 | 2002-08-07 16:18 | 2002-08-07 | SAFETY EQUIPMENT FAILURE INVOLVING A RADIOGRAPHY CAMERA SHUTTER On 8/7/02 during a training exercise the shutter on a Picker Cyclops Camera Unit failed to close. The licensee manually cranked the shutter to the closed position and locked/tagged the device to prevent operation. The licensed maintenance technician was notified to initiate repairs. The Camera is used by the Crane Army Munitions Activity for certification training of radiographers. The Cyclops Camera is a model 590 manufactured by Picker Corp. The source is 1645 Curies of Cobalt-60, S/N T1520, manufactured by Neutron Products. There was no personnel exposure associated with this incident. Similar report, see EN # 38632. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-08-07
39117 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-08-06 05:30 | 2002-08-07 13:13 | 2002-08-07 | AGREEMENT STATE REPORT - FIRE IN DUST COLLECTION SYSTEM "A fire occurred at approximately 5:30 am on 8/6/02 in the Torit Dust Collection System. The fire burned in this system for approximately 5 minutes until extinguished by the temperature activated fire suppression system. This dust collection system filters air from a number of processing system rooms, including the Wastewater Evaporator Room. It consists of a series of 24 cartridges in an enclosed filtration system. The fire was confined to this system. "There was no additional exposure to plant personnel. It is not expected that any releases occurred that exceeded regulatory limits. The isotope of concern is depleted uranium in aerosol particulate sized form. Air samples taken in the Wastewater Evaporator Room during the event resulted in an air concentration of approximately 1E-14 microcuries/cubic centimeter of depleted uranium in aerosol form (micron sized particles). "The Wastewater Evaporator System and dust collection system are shut down until the damage from the fire can be evaluated and repaired. The filters in the dust collection system will be extracted and counted for radioactivity as soon as the extent of damage is evaluated and the systems can be opened. The sample filters in the affected stack have been extracted and counted. Preliminary counting of the stack filters demonstrate that a release had not occurred. Final results from filtration counting will not be available for approximately 48 hours to allow for the decay of radon." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-08-12
39116 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-08-06 10:10 | 2002-08-07 11:17 | 2002-08-07 | AGREEMENT STATE REPORT ON STOLEN GAUGE "Gauge operator went to dinner around 20:30 on 08-06-02 and confirmed seeing the CPN model MC-3 gauge locked in its case and chained and locked to the bed of his truck parked outside his hotel room. At 21:30 the operator returned to the truck to get some cigarettes and discovered that the gauge had been stolen. The chain had been cut with bolt cutters and the lock was still intact. The operator stated that the case the gauge was contained in also was locked. He immediately contacted the RSO, emergency management and the local police." The licensee also reported the gauge was a moisture density gauge, CPN Model MC-3 and contained 11 millicuries of CS-137 and 50 millicuries of AM-241. The theft occurred in the parking lot of the Super 8 Motel located at 200 Mercantile Drive, Winston-Salem, NC 27105. NC Incident Number: 02-28. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-08-12
39115 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-08-07 10:37 | 2002-08-07 11:15 | 2002-08-07 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL A malfunction occurred on the "A" main feed pump that resulted in a low water level in the no. 1 steam generator causing an automatic reactor trip from 55% reactor power. Operators manually started auxiliary feed water to control water level during post trip conditions. The steam generator water level did not decrease low enough to prompt an automatic start of the auxiliary feed water system. All control rods properly inserted into the core. The cause of the loss of the "A" main feed pump is being reviewed as part of the post trip review. The NRC Resident Inspector was notified by the licensee. | 0 | 0 | 0 | 0 | 55 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-08-07
39114 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-08-06 10:00 | 2002-08-06 16:08 | 2002-10-03 | LICENSEE DISCOVERED A POST-FIRE SAFE SHUTDOWN FUNCTION THAT MAY NOT BE MET "On August 6, 2002, conditions were discovered where a postulated fire could cause the pressurizer to blow down to the pressurizer relief tank (PRT). Wolf Creek is in Mode 1, at 100% power. "During reviews associated with post-fire safe shutdown reanalysis work, Wolf Creek personnel discovered that power and control cables for a pressurizer power operated relief valve (PORV) and its associated motor operated block valve are routed in electrical raceways with no horizontal separation. The two valves are in the same electrical separation group but are redundant in their post-fire safe shutdown function to prevent reactor coolant system (RCS) blowdown to the PRT. Further investigation determined that the power and control cables in the opposite separation group have the same configuration. This does not meet our commitments to 10 CFR 50 Appendix R.lll.G as reflected in our approved Fire Protection Plan. "During a fire in the plant, it is the function of PORV valves and block valves to provide a barrier to blowing down the RCS into the PRT. A fire in any of the affected fire areas in which the circuits are routed has the potential to damage cables in a manner that cause a the PORV to spuriously open (due to a hot short), and to damage cables in a manner that causes the block valve to not respond to a close signal (due to an open circuit or a hot short). This would cause a non-isolable RCS blowdown to the PRT. "Based on the guidance provided in NUREG 1022 Revision 2, this situation meets the criterion of 10 CFR 50.72(b)(3)(ii)(B) for an 8-hour ENS notification, as it relates to being in an unanalyzed condition. "The licensee has implemented a 1-hour fire watch and is developing compensatory measures. "The licensee notified the NRC Resident Inspector." * * * RETRACTED AT 1544 EDT ON 10/3/02 BY STEVEN HENRY TO FANGIE JONES * * * "Wolf Creek has reevaluated the routing of the cables for the PORV and its associated block valve using the guidance contained in Generic Letter 86-10 and in NUREG 1022 Revision 2, and has determined that this condition is not reportable. The reevaluation shows that the reactor core will never be uncovered even if the PORV were to remain open and that a diverse means is available via the deenergization of a dc bus to close the PORV in the event of a fire. A fire initiated spurious opening of the PORV will not result in a condition that significantly degrades plant safety. This is based on the plant design, low probability of occurrence and actions to mitigate this event. Therefore, per NUREG 1022, this condition is not an unanalyzed condition that significantly degrades plant safety and is not required to be reported in accordance with 10CFR50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. Notified R4DO (Kriss Kennedy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-08-06
39113 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-08-02 | 2002-08-06 13:30 | 2002-08-06 | AGREEMENT STATE REPORT INVOLVING A MEDICAL MISADMINISTRATION "I received a call from Gerald White, of Colorado Associates in Medical Physics (CAMP) late on Friday August 2, 2002. He called to report a medical administration that occurred at Centura Health Penrose St. Francis Hospital in Colorado Springs (RML 197-02) earlier that day concerning a high dose rate afterloader (HDR) treatment. "Apparently, an incorrect catheter length was entered into the software for the HDR unit, resulting in the patient receiving zero therapy dose. Since the source left the housing, there was an exposure to the patient. "The physician is determining the path forward with respect to treatment. We are awaiting more information from CAMP. I sent them an e-mail yesterday evening (8/5/02) requesting more Information." Colorado Department of Public Health and Environment, Laboratory and Radiation Services Division, Report Number M03-01. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-08-09
39112 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-08-06 07:53 | 2002-08-06 10:16 | 2002-08-06 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO BOTH RESIDUAL HEAT REMOVAL SERVICE WATER SUBSYSTEMS BEING DECLARED INOPERABLE. "Initiated plant shutdown in accordance with Tech Spec 3.7.1, Required Action E.1 due to required actions and associated completion times not meet (met) for both Residual Heat Removal Service Water subsystems being inoperable. Per Tech Specs, plant is required to be in Mode 3 by 1933 hours today (8/6/2002) and in Mode 4 by 1933 hours on 8/7/2002. Plant shutdown was commenced at 0753 hours today. "This report is being made under 50.72(b)(2)(I), 'The initiation of any nuclear plant shutdown required by plant's Technical Specifications." All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable. The licensee will reduce reactor power down to between 10 to 15 percent power then manually scram the reactor. The NRC Resident Inspector was notified of this event by the licensee. See event # 39111 for background information. | 62 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-08-06
39111 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-08-05 23:33 | 2002-08-06 04:34 | 2002-08-06 | LOSS OF RESIDUAL HEAT REMOVAL (RHR) HEAT REMOVAL CAPABILITY. "At 23:33 on 8/5/02 both loops of RHRSW (Residual Heat Removal Service Water) were declared inoperable due to experiencing high differential pressure greater than 12 psid across the 'A' loop RHRSW strainer and the 'B' loop RHRSW strainer. "On 8/4/02 while running a surveillance for the 'B' RHRSW pump a high strainer differential pressure annunciator was received, which comes in a 6 psid. 'B' pump flow at the time was 2400 GPM. The in plant operator was sent locally to investigate the local differential pressure indication and discovered the instrument was pegged high at > (greater than ) 15 psid. The pump was secured and the corresponding Limiting Condition of Operation of 7 days was entered for the 'B' RHRSW loop. Maintenance was immediately planned and begun to clean the 'B' RHRSW strainer. At the time plans were also made to inspect the 'B' RHRSW/ESW (Emergency Service Water) pit and Stilling Basin. "On 8/5/02 after inspections of the Stilling basin found algae growth, plans were made to run the 'A' side RHRSW pumps to determine operability of the 'A' loop of RHRSW. At that time the Stilling basin cleaning also began. After the completion of stilling basin cleaning on 8/5/02, the 'A' RHRSW pump was started and strainer differential was between 2.5 - 4.5 psid at a pump flow of 2400 GPM which was held for 15 minutes. At this time the 'C' RHRSW pump was started and flow raised to 4100 GPM at which time strainer differential pressure was steady at 5.5 - 6.0 psid. As flow was raised to 5000 GPM Strainer differential pressure pegged high at > (greater than) 15 psid within 3 minutes. The 'A' RHRSW pump was then secured and flow lowered to 2100 GPM where strainer differential pressure remained at 10 - 12 psid and then pegged high at greater than 15 psid. The 'C' RHRSW pump was then secured and the 'A' RHRSW loop was declared inoperable at 23:33 on 8/5/02. The LCO for both loops of RHRSW inoperable was then entered at 23:33 on 8/5/02. "This report is being made under 50.72(b)(3)(v)(B) 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.' " All other Emergency Core Cooling Systems are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2002-08-06
39110 | 0 | BENEFIS HEALTH CARE |  |  |  |  | 2002-08-05 | 2002-08-05 17:36 | 2002-08-05 | MEDICAL MISADMINISTRATION - DOSE GIVEN APPROXIMATELY 22% LESS THAN PRESCRIBED This report is made due to failure to provide test per NRC Notification Notice 2002-19. A review of the administration records indicate that 6 patients received palliative doses of samarium since 12/99 that were about 22% low. Benifis Health Care does not use unit dose vials, they receive multidose vials and withdraw a dose out into a plastic syringe. After receipt of a calibration source, the RSO determined that radiation readings for a dose in a plastic syringe was 21.6% higher than in a glass syringe. A correction factor has been put in place for plastic syringes to insure proper dosages in the future. The patients have been determined to have no adverse affects, they all had relief of pain even with the lower dose. The patients and attending physicians have not been informed at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | MT | HOS |  | 35.33 |  |  |  | 0 | 2002-08-05
39109 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-08-03 11:42 | 2002-08-03 12:40 | 2002-08-03 | PLANT ENTERED A REQUIRED TECHNICAL SPECIFICATION SHUTDOWN DUE TO RCS LEAKAGE The licensee detected a through wall leak on the charging system header discharge that is <0.1gpm. They have declared the ECCS inoperable, but available. Plant entered TS 3.0.3 and will be in cold shutdown within 30 hours. At this RCS leakage rate they have not exceeded any TS limits. The reason for the leakage has not yet been determined. The NRC Resident Inspector, State and local agencies have been notified. There will be a press release. |  | 99 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-08-03
39108 | 0 | BARLETTA MATERIAL & CONSTR., INC. |  |  |  |  | 2002-08-03 07:50 | 2002-08-03 08:02 | 2002-08-03 | TROXLER MOISTURE DENSITY GAUGE DAMAGED During a paving job on SR2032 near Pittston, PA, a Troxler Moisture Density Gauge, Model # 3430, was run over by a roller. The area around the damaged Troxler gauge was cordoned off and the Radiation Safety Officer is driving from Hazleton to Pittston to determine the amount of damage to the Troxler gauge. The gauge contains 10 millicuries of Cesium-137 and 40 millicuries of Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN |  |  |  |  | 0 | 2002-08-03
39107 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-08-02 15:00 | 2002-08-02 19:23 | 2002-08-02 | UNOPENED CAN OF BEER WAS DISCOVERED IN A REFRIGERATOR IN THE PROTECTED AREA An individual stated he inadvertently brought a can of beer to work along with 3 cans of sodas thinking it was also a can of soda. The 3 cans of soda were also in a blue color can as the beer. The individual's unescorted access was suspended, and a for cause test was requested, which resulted in negative results for alcohol as well as drugs. The individual was neither a supervisor nor licensed operator. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2002-08-02
39106 | 0 | US ARMY |  |  |  |  | 2002-07-29 | 2002-08-02 15:12 | 2002-08-02 | THE 503 CHEMICAL DETACHMENT IN HEIDELBERG, GERMANY LOST A CHEMICAL AGENT DETECTOR During an inventory check on 6/13/02, by the 503rd Chemical Detachment in Heidelberg, Germany, it was discovered that a M43A1 Chemical Agent Detector containing 300 microcuries of Americium - 241 was unaccounted for. An investigation was made but the device was not located. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-08-02
39105 | 0 | US ARMY |  |  |  |  | 2002-07-15 | 2002-08-02 15:12 | 2002-08-02 | THE GEORGIA ARMY NATIONAL GUARD LOST TWO CHEMICAL AGENT DETECTORS During an inventory check by two units(Hineville, Ga and Tifton, Ga) of the Georgia National Guard, it was discovered that two Chemical Agent Detectors(M43A1) each containing 300 microcuries of Americium-241 were unaccounted for. These detectors were taken to Bosnia during the Guard's deployment and were to have been brought back when the National Guard returned. It is undetermined at this time if the two guard units brought the detectors back or if they were lost at their post in Georgia. Investigation is still ongoing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-08-02
39104 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-08-02 08:30 | 2002-08-02 10:08 | 2002-08-02 | EOF PHONE SYSTEM LOST "Normal power was lost at the EOF due to a storm during the early morning hours. The EOF phone system switched over to battery backup power and eventually drained the batteries. The Shift Manager was notified at 0830. A portable diesel generator is being brought to the EOF to repower the facility. If the EOF requires staffing at this time, portable lighting and cell phones could be used. AEP is working on restoring the normal power supply to the Buchannan Office and EOF as well." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-08-02
39103 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-08-01 12:54 | 2002-08-01 16:16 | 2002-08-01 | CERTIFICATE HOLDER REPORTED TO THE STATE THAT IT EXCEEDED ITS OPACITY LIMITS On 8/01/02 at 1254 the "A" side of #1 precipitator at the X-600 Steam Plant experienced problems after being energized while placing #1 boiler in service. The precipitators were energized at 1230 and had readings of 20.8% at 1254 and 31.9% at 1300. This resulted in the exceedance of the opacity limit of 20% twice in one hour. At 1543 the Plant Shift Superintendent notified the Ohio EPA of the X-600 Steam Plant opacity exceedance. UE2-RA-RE1030, App. D, section P requires a 4 hour NRC event when other government agencies are notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-08-01
39102 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2002-07-09 14:00 | 2002-08-01 13:50 | 2002-08-01 | THE LICENSEE REPORTED A LOSS OF LICENSED MATERIAL During preparation activities for the removal of the reactor vessel, site personnel detached a vessel external neutron flux dosimeter assembly from the vessel and released the dosimeter assembly to the sump area below the vessel for future recovery and disposal. The neutron flux dosimeter was used during plant operation to measure neutron fluence to the immediate adjacent outside wall of the reactor vessel. Subsequently, site personnel were provided access to the area for retrieval and disposal of the dosimeter capsules. One of the dosimeter capsules apparently had become dislodged from the assembly during the earlier release and personnel were unable to locate the dislodged capsule. The dosimeter contains small quantities of dosimetry material including Neptunium 237 (6.46 microcuries) and Uranium 238 (.009 microcuries). Subsequent limited inspections have been unsuccessful in locating this capsule. The constrained annulus area between the reactor vessel and adjacent neutron shield tank and storage of radioactive material and bagged asbestos in the reactor vessel sump area continues to limit area for a thorough inspection. Additional inspection of the area is scheduled for January of 2003. Maine Yankee is reporting the loss of licensed material in accordance with 10 CFR 20.2201(b). The licensed material was lost in a restricted area and the Neptunium 237 material is of a quantity greater than 10 times the quantity specified in appendix C to Part 20. The missing dosimeter capsule surface dose rate is estimated to be around 1000 cpm and therefore of minimal exposure to workers in this radiation control area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-08-01
39101 | 0 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2002-07-29 12:30 | 2002-07-30 09:49 | 2002-07-30 | MEDICAL MISADMINISTRATION A coronary brachytherapy of the intermediate artery was performed with a Sr-90, 40 mm source train. The written directions called for a treatment time of 2 minutes and 52 seconds which would result in a total dose of 18.4 Grays. The catheter had a kink near the proximal marked location which caused the source train to get stuck before the distal portion of the catheter. This caused an unintended treatment of an area proximal to the treatment site. The source was observed out of position by panning the table and using the fluoroscopy tube, at this time the source was retracted. The source was in the patient for 2 minutes and 32 seconds, resulting in a total dose of 16.4 Grays. The hospital has implemented process improvements to prevent another occurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0 | 2002-07-30
39100 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-07-27 12:27 | 2002-07-27 15:47 | 2002-07-27 | AUTOMATIC REACTOR SCRAM ON MAIN GENERATOR LOAD REJECT "On 7/27/02 at 1227 CDT, Browns Ferry Unit 2 scrammed due to a Main Generator load reject signal, when the Main Generator breaker opened. The breaker trip was caused by a Generator Neutral Overvoltage relay trip. The cause of the Generator Neutral Overvoltage is under investigation. All systems responded as required to the scram signal, no ECCS initiations occurred as a result of the scram signal. As expected, Main Steam Relief Valves (MSRVs) opened due to the high reactor pressure as a result of the Main Turbine/Generator trip." The licensee is investigating the cause of the trip and will remain in Hot Shutdown until everything is known prior to plant startup. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-27
39099 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2002-07-27 01:10 | 2002-07-27 13:36 | 2002-08-01 | INFORMATION CALL THAT INVOLVES LOCAL AUTHORITIES AND POSSIBLE MEDIA ATTENTION The licensee's security personnel discovered a stub end of a hand rolled cigarette of questionable material in the room above diesel generator 'A.' It appeared old and had no odor. Fairfield County Sheriff's Department was contacted and they dispatched a unit. They potentially identified the contents as marijuana and took custody of the cigarette. They will submit it to the South Carolina State Law Enforcement Division for analysis. The analysis will take about a week or more and followup notification will be made if needed. This notification was made due to Fairfield County involvement and possible media coverage. There is no impact on plant operation. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 8/01/02 @ 1403 BY TURKETT TO GOULD * * * EVENT RETRACTION The analysis determined that the material found in the hand rolled cigarette was not marijuana, therefore the licensee is retracting this event. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2002-07-27
39098 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-07-26 21:24 | 2002-07-27 01:04 | 2002-07-27 | DRY FUEL STORAGE CASK FILLED WITH WRONG GAS "At 09:24 p.m. on 7/26/02, the Shift Manager was notified by the Refueling Floor Manager that a Dry Fuel Storage cask had been accidentally filled with an argon/helium gas mix in lieu of 100% helium gas as required by the certificate of compliance for Susquehanna's Dry Fuel Cask Storage program. The affected cask was in the process of being sealed and prepared for shipment from the Refueling Floor to the Horizontal Storage Module located on site. Site Engineering and the vendor have been contacted to provide guidance on the affect of the argon gas on the Storage System. Temperature monitoring is in progress to detect any changes in the loaded canister until a final determination can be made. Because of the reduction in the thermal conductivity of the argon/helium mixture, this defect is believed to represent a potential significant reduction in the effectiveness of the spent fuel confinement system and is reportable under 10 CFR 72.75(b)(2) and 10 CFR 72.75(b)(3)." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SPENT FUELCASK DEFECT | SPENT FUEL CASK EFFECTIVENESS REDUCTION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 72.75(b)(2) | 72.75(b)(3) |  |  | 0 | 2002-07-27
39096 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-07-26 16:45 | 2002-07-26 19:30 | 2002-08-05 | AGREEMENT STATE REPORT - MISSING I-125 SEEDS The following is from a facsimile report: "At approximately 4:45 PM Friday July 26, 2002, I [Colorado Department of Health and Environment] received a call from ..., RSO and Medical Physicist at St. Mary's Hospital in Grand Junction, Colorado. "[RSO] informed us he is missing 3, I-125 prostrate seeds (approx. 0.36 mCi [millicuries] each). He was made aware of the loss late this morning. Surveys were conducted in all suspect areas of the hospital to no avail. It is possible that either the seeds never arrived due to poor inventory control of the supplier, or that the seeds went to the trash, which left the hospital around 7:00 A.M. Since the seeds are shielded, they would probably not be detected at the landfill." * * * UPDATED AT 1800 EDT ON 8/5/02 BY TIME BONZER TO FANGIE JONES * * * The final report is that the seeds were not found, it is indeterminate whether the seeds actually made it to the hospital. The hospital will take additional steps to insure that they actually receive the seeds they are suppose to receive. The hospitals action plan is as follows: "We are revising our QA processes. We will return to performing our own source counts and not be dependent on others so we do not go looking for something we may have never received. We also will increase our needle-prep area monitoring to include a more thorough area survey Including removing the lead shielding" Notified the R4DO (Chuck Cain) and NMSS EO (E. William Brach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-07-31
39095 | 0 | NORWALK HOSPITAL |  |  |  |  | 2002-07-23 | 2002-07-26 10:00 | 2002-07-26 | I-125 SEED UNACCOUNTED FOR FOLLOWING IMPLANTATION On 7/23/02 a male patient underwent surgery for implantation of Iodine-125 seeds as part of the treatment plan for prostate cancer. Following the surgery, the technician discovered that only 7 instead of 8 of the original 110 seeds delivered to the OR [Operating Room] were remaining. A survey of the area was unable to locate the missing seed [338 millicuries]. The RSO believes that either the missing seed was inadvertently washed down the OR sink drain during cleanup or that 103 instead of 102 seeds prescribed were implanted. The licensee will submit a written report within 30 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-07-26
39094 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-07-26 | 2002-07-26 08:44 | 2002-07-26 | AGREEMENT STATE REPORT INVOLVING CRASH OF AIRCRAFT CARRYING RAD MATERIAL The Florida Bureau of Radiation Control was notified that a FEDEX aircraft carrying Rad I/II material, isotopes and quantities unknown, had crashed at the Tallahassee airport between 0745-0800EDT on 7/26/02. The State of Florida was responding and did not request NRC assistance at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 0 |  | OTH | AGR |  |  |  |  | 0 | 2002-07-31
39093 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-07-25 17:05 | 2002-07-25 19:06 | 2002-07-26 | BOTH TRAINS OF CONTROL ROOM AREA CHILL WATER INOPERABLE The train 'A' control room area chill water was declared inoperable at 1350 EDT due to a refrigerant leak. Subsequently the train 'B' control room area chill water tripped and at 1705 EDT technical specification 3.0.3 was entered due to both trains being inoperable. At 1747 EDT the train 'A' was declared operable and the technical specification 3.0.3 was exited. The report is made due to the 42 minutes both trains were inoperable which could have prevented the performance of a safety function. Troubleshooting continues on train 'B'. The licensee notified the NRC Resident Inspector. * * * RETRACTED AT 1305 EDT ON 7/26/02 BY JIM DEAN TO FANGIE JONES * * * The licensee is retracting the event based on further determination that the 'A' train of the control room area chill water system remained operable and capable of performing its safety related function in the presence of the refrigerant leak. The licensee notified the NRC Resident Inspector. The R2DO (Mark Lesser) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-25
39092 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2002-07-25 09:30 | 2002-07-25 13:46 | 2002-07-25 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING CRITICALITY CONTROLS "At approximately 10:30 AM today (7/25/02), NCS Management was notified of a potential unusual event in the Research Test Reactors and Targets (RTRT) facility at BWXT, Nuclear Products Division. The Arc-Melt furnace in RTRT is used to melt aluminum powder and uranium metal together into a 'button.' The button is then crushed and the material homogenized to form a UAIx powder for further processing to fuel compacts. U-metal pieces (chunks) and aluminum powder is placed into six small cavities in a graphite hearth and an electrode used to melt the material. The hearth rests on a metal plate that is cooled from the underside by a cooling coil loop containing solution. "At approximately 9:30 AM today (7/25/02) a knowledgeable individual discovered a small pinhole leak in the coolant loop on the bottom of the plate supporting the hearth. Approximately one cup of coolant was found in the bottom of the furnace. At no time did coolant contact fuel material in the furnace, and the U-metal/aluminum remained in the cavities of the hearth. The loading in the furnace during the time the leak existed was [quantity of] U-235. "The Arc-Melt furnace has an NCS limit of [quantity] U-235. When the furnace is used to re-melt UAlx powder, a large leak of water into the furnace could result in a mixture of U-metal/water in an unfavorable geometry since the material may 'wash out' of the cavities. Accordingly, the coolant is 'poisoned' with boric acid such that a homogenous sphere of U-metal/coolant is subcritical (below our license k-effective limit of 0.95). "Our Integrated Safety Analysis (ISA) of the Arc-Melt operation postulated a catastrophic leak in the furnace coolant as an initiating event in a criticality accident scenario. The ISA appropriately identified the mass of fissile material and the boron content of the coolant as protection measures against a criticality accident given the occurrence of a major leak. The leak that occurred on 7/25/02 was of a lesser magnitude than assumed in the ISA analysis, however, because control of the coolant as a moderator was degraded, BWXT is reporting this event under the guidelines of Bulletin 91-01. "Appropriate corrective actions have been taken. Fuel was removed from the furnace, operation of the furnace was immediately suspended, and an investigation team is being assigned. The leak has been cleaned up and the pinhole will be repaired and tested prior to re-start of operations." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | VA | FUE | [5 empty] | 1 | 2002-07-25
39091 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-07-03 | 2002-07-25 12:00 | 2002-08-28 | AGREEMENT STATE REPORT - MISSING SOIL DENSITY GAUGE Atlantic Drilling Supply shipped a CPN Model NC3 moisture density gauge (serial number M310800431, containing 10 millicuries Cs-137 and 50 millicuries Am-241:Be) to CPN International in Martinez, CA for calibration. The gauge was shipped via Conway Southern Express. The shipment has been traced to Jacksonville where there is paperwork indicating shipment on to Atlanta. There is no paperwork or other indication of the shipment arriving in Atlanta. There is an investigation ongoing to determine the actual location of the shipment. ***UPDATE 0922 8/28/02 CHARLEY ADAMS (e-mail) TO MIKE NORRIS*** "Gauge was shipped to CPN for calibration on 7-3-02 from Orlando. It was finally found in the shipper's facility in Denver, Colorado. It had arrived with no shipping papers, no owner, origin, and destination were unknown. It was placed in the lost and found bin until the owner was determined. Gauge was returned to owner on 8-23-02. Gauge was undamaged and had not been opened. Gauge will be sent to CPN for calibration via FEDEX. This office will take no further action on this incident." Notified R2DO (Cahill), R4DO (Graves) and NMSS (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-07-30
39090 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2002-07-24 | 2002-07-25 11:30 | 2002-08-06 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE A Troxler gauge model 3440, serial number 31621, was stolen out of the bed of a truck in front of a private residence. The vehicle was parked at 2300 on 7/24/02 and the gauge was found missing at 0700 on 7/25/02. The gauge contains 8 millicuries of Cs-137 and 40 millicuries of Am-241:Be. Local law enforcement has notified and a press release is planned for the local newspaper. * * * UPDATED AT 1220 EDT ON 8/6/02 BY JOSH GRISHAM TO FANGIE JONES * * * The gauge has been recovered in good condition. Notified R2DO (Caudle Julian) and NMSS EO (Charlie Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0 | 2002-07-30
39089 | -1 | US ARMY |  |  |  |  | 2002-07-25 | 2002-07-25 10:40 | 2002-08-01 | UNPLANNED CONTAMINATION RESTRICTING ACCESS >24 HOURS The ARMY is conducting an investigation as to the disposal of 75 to 100 Pm-147 target sights. Each sight was originally 3 millicuries with a manufacture date of approximately 1975. The ARMY is restricting access into a building where these gun sights were disposed of in 1997. * * * UPDATE ON 8/01/02 @ 1513 BY CROOKS TO GOULD * * * EVENT RETRACTION A wipe test was performed at the area in question and from the 18 wipes taken 16 were clean and one measured 5 dpm and a second measured 6 dpm. Therefore the licensee is retracting this event since there was no contamination present. Notified Reg 2 RDO(Ernstes), Reg 3 RDO(Burgess) and NMSS(Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2002-07-25
39088 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2002-07-24 16:28 | 2002-07-24 17:47 | 2002-07-24 | MANUAL REACTOR TRIP DUE TO DECREASING OIL LEVEL AND INCREASING THRUST BEARING TEMPERATURE ON ONE OF FOUR REACTOR COOLANT PUMPS Indications of lowering oil level were observed on the 11A reactor coolant pump. While the licensee was investigating whether or not the indications were valid, thrust bearing temperature began to increase. As a result, operators manually tripped the reactor from 100% power at 1628, and operators subsequently secured the 11A reactor coolant pump. All control rods fully inserted, and all systems function as required in response to the manual reactor trip. None of the primary or secondary relief valves lifted, and there were no emergency core cooling system injections and engineered safety feature actuations. The unit is currently stable in Mode 3 (Hot Standby). Normal charging and letdown, pressurizer heaters and sprays, and the remaining three reactor coolant pumps are currently being utilized for primary system level, pressure, and transport control. Water is currently being supplied to the steam generators via normal condensate and feedwater, and secondary steam is being dumped to the condenser. The auxiliary feedwater system remains in standby. Containment parameters remain normal, and offsite power is available. All emergency core cooling systems and engineered safety features are operable and available with the exception of the 1B emergency diesel generator, which was removed from of service for planned maintenance this morning. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-24
39087 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-07-24 12:26 | 2002-07-24 15:14 | 2002-07-24 | OFFSITE NOTIFICATION REGARDING A DISCHARGE OF APPROXIMATELY 13 GALLONS OF FUEL OIL TO THE CHESAPEAKE BAY Approximately 13 gallons of #2 fuel oil was released to the Chesapeake Bay via the storm drain when the 1B diesel generator fuel oil day tank was overfilled during the calibration of the level switches. The control room was notified at 1226, and the release has been secured at 1355. The spill mitigation plan and ERPIP were both implemented, and the boom is in place at the outfall to catch any residual. The licensee notified the Maryland Department of the Environment, National Response Center, and NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-07-24
39086 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC |  |  |  |  | 2002-07-24 | 2002-07-24 11:42 | 2002-07-24 | NOTIFICATION UNDER 10 CFR PART 21 FOR HIGH LINE PRESSURE CORRECTION METHODOLOGY (INACCURATE TECHNICAL ADVICE RELATED TO ROSEMOUNT TRANSMITTERS) The following text is a portion of a facsimile received from Rosemount Nuclear Instruments, Inc.: "Pursuant to 10 CFR Part 21, Paragraph 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you of an instance in which RNII provided inaccurate technical advice related to high line pressure correction of Rosemount transmitters to one customer. The technical advice was transmitted to Rochester Gas and Electric via letters sent to this customer in April 1991. The letters were intended to provide supplemental guidance to the published RNII product manuals for calibration of pressure transmitters with high line pressure applied. The result of implementation of the technical guidance in these letters would be to improperly correct for the effect of line pressure on transmitter output. A recent communication between RNII and this customer alerted RNII to the inaccurate supplemental technical guidance. RNII has subsequently corrected this advice. The standard procedure for correcting for high line pressure contained in RNII's product manuals is accurate." "[...]" "2.0 Identification of items supplied:" "Model 1152 and Model 1154 Pressure Transmitters are specifically addressed in the communications to the customer. The concept of high line pressure correction is applicable to all RNII pressure transmitter models." "[...]" "4.0 Nature of the failure and potential safety hazard:" "This notification relates to an instance in which RNII provided incorrect, application specific supplemental line pressure correction advice to a single customer. This incorrect advice was contained in letters sent to Rochester Gas and Electric in April 1991. The high line pressure correction procedures provided in RNII pressure transmitter product manuals are not affected and are accurate." "RNII does not have sufficient information relative to the applications to determine the safety significance of this situation." "5.0 The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action:" "Corrective Action:" "RNII has contacted the affected customer, and through a series of verbal and electronic communications, provided the correct supplemental technical information relative to high line pressure effect for the application in question. RNII will follow up these communications with a formal detailed letter to this customer. Completion Date: 31 July 2002." "Internal RNII Corrective Actions:" "1. The customer provided RNII with copies of the information originally supplied by RNII regarding the supplemental high line pressure correction advice. RNII reviewed this information along with the current request for clarification of the supplemental high line pressure correction for a specific application." "2. Transmitter testing was performed to establish additional assurance that the current technical advice given to the customer was correct." "3. Other customer correspondence files were reviewed to look for occurrences of incorrect supplemental technical information. No occurrences were identified." "4. Training of appropriate RNII personnel reinforcing the importance of providing accurate supplemental technical information will be performed. Completion Date: 2 August 2002." "5. Current administrative procedures and controls will be reviewed to provide confidence that supplemental technical information being transmitted to customers is accurate. Following this review, further corrective action will be initiated and implemented if appropriate. Completion Date: 16 August 2002." "6.0 Any advice related to the potential failure of the item:" "This notification specifically addresses detailed, supplemental technical information provided to one customer. There should not be any potential failure concern relative to hardware, and RNII's pressure product manuals are unaffected." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2002-07-24
39085 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-07-23 16:32 | 2002-07-23 17:30 | 2002-07-23 | MANUAL REACTOR SCRAM DUE TO THE LOSS OF CONDENSER VACUUM FOR UNKNOWN REASONS The following text is a portion of a facsimile received from the licensee: "Limerick Unit 2 was manually scrammed due to a loss of main condenser vacuum. All systems functioned as expected during the scram. No [emergency core cooling system injections] occurred. All rods fully inserted. No [safety relief valves] lifted. The unit is currently stable in Mode 3. Investigation into the loss of vacuum is continuing." The licensee stated that the main steam isolation valves remained open during the event. There were no reactor core isolation cooling system injections, and none were required. There were no related surveillance or maintenance activities ongoing at the time of the reactor scram, and there was nothing unusual or misunderstood with the exception of the cause for the loss of condenser vacuum. The licensee also stated that reactor vessel level and pressure control are currently being maintained via normal condensate and feedwater and via normal turbine bypass, respectively. The main condenser is available as the heat sink, and main condenser vacuum is being maintained via the steam jet air ejectors. The mechanical vacuum pump had also been prepared and is available to maintain condenser vacuum if needed. Containment parameters were reported to be normal. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-23
39084 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2002-07-23 12:39 | 2002-07-23 16:52 | 2002-07-23 | AGREEMENT STATE REPORT INVOLVING THE DISCOVERY OF A CPN MOISTURE DENSITY GAUGE BY A THIEL GEOTECH CLIENT IN OMAHA, NEBRASKA, AND THE SUBSEQUENT REPORT OF THE LOSS OF THE SAME GAUGE BY GEOTECHNICAL SERVICES, INC. At approximately 1100 CDT on 07/23/02, an engineering company (Thiel Geotech) notified the Nebraska Division of Radioactive Materials that one of their clients had found a CPN moisture density gauge. The gauge was discovered in a pad-locked transport container at a construction site (approximately 180th and Harrison) in Omaha, Nebraska. Thiel Geotech is licensed to use/hold similar gauges, and representatives of Thiel Geotech transported the gauge to their office in order to secure it. The State reported that the gauge (model CPN-131, serial number MD00105439) contained a maximum of 50 millicuries of americium-241/beryllium and a maximum of 10 millicuries of cesium-137. At the request of the State, Thiel Geotech broke through the padlock to check the gauge and to perform surveys. There was no observable damage, and the survey results were normal. The State was able to identify the owner of the gauge fairly soon via an ownership label and the serial number. At approximately 1239 CDT on 07/23/02, Geotechnical Services, Inc., notified the Nebraska Division of Radioactive Materials of the loss of the same gauge. Geotechnical Services, Inc., also notified local law enforcement. The Nebraska Division of Radioactive Materials has had several conversations with both companies and has also been in contact with local law enforcement. The State requested Thiel Geotech to hold the gauge pending the State's investigation, which is currently planned for tomorrow. (Call the NRC operations officer for a Nebraska Division of Radioactive Materials contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2002-07-26
39083 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2002-07-22 16:30 | 2002-07-22 21:26 | 2002-07-22 | INOPERABILITY OF BOTH CONTROL ROOM VENTILATION TRAINS The following text is a portion of a facsimile received from the licensee: "Both control room ventilation (CRV) trains [were] declared inoperable. While [the] 'B' CRV was inoperable for testing, [the] 'A' CRV chiller compressor tripped causing [the] 'A' CRV to be inoperable. [A] 24-hour [limiting condition for operation (LCO)] was entered per [Technical Specification] 3.17.A.3.a. 'B' CRV was restored to operable and [the] 24-hour LCO [was exited] at 1701 [CDT]. [The] 'A' CRV is in a 30-day LCO per [Technical Specification] 3.17.A.2.a. [The] 'A' CRV chiller compressor trip cause [is] unknown." The licensee plans to notify the NRC resident inspector as well as applicable state and local officials. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-22
39082 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2002-07-22 17:10 | 2002-07-22 19:14 | 2002-08-21 | DISCOVERY OF A HIGH PRESSURE COOLANT INJECTION (HPCI) FLOW CONTROLLER INDICATION OF 500 GPM DURING RESTORATION FROM A CORE SPRAY SYSTEM SURVEILLANCE TEST AND WITH THE HPCI SYSTEM IN STANDBY The following text is a portion of a facsimile received from the licensee: "During restoration from surveillance testing on the 'B' core spray system, the flow controller for the HPCI system (23FI-108-1) was observed to be reading 500 gpm with the HPCI system in standby. The HPCI system was declared inoperable, and [Technical Specification] 3.5.C.1.b was entered requiring [either] restoration of 'B' core spray or HPCI to operable status within 24 hours or [commencement of a unit] shutdown. 'B' core spray was restored to operability at 1732, and the plant exited [Technical Specification] 3.5.C.1.b and entered [Technical Specification] 3.5.C.1.a placing the plant in a [7-day limiting condition for operation (LCO)]." "Since no actuations occurred and [since] no shutdown was initiated, this is only reportable under 10CFR50.72(b)(3) criteria, specifically 10 CFR 50.72(b)(3)(v)(D). This is based on the guidance in NUREG 1022, Rev. 2. Since HPCI is a single train system, even though [technical specifications] allow a 7-day LCO, declaring HPCI [inoperable] is reportable." "The only unusual/not understood thing associated with this is the flow indication of 500 gpm. There were no actuations required so all equipment functioned and continues to function as expected. There are no radiological releases associated with this event." The licensee plans to notify the NRC resident inspector. ****RETRACTION ON 08/21/02 AT 0959 ET BY RICH PLASSE TAKEN BY MACKINNON***** "During troubleshooting, it was noted that manipulation of terminal screws on one of the components caused a step output change similar in magnitude to that observed on the indicator. Components were replaced and the instrument calibrations re-performed, with the resulting indication returning to normal. A review of plant data indicated that an intermittent indication problem was evident in the instrument loop after April 30, 2002, when maintenance had been performed that included the replacement of several instrument loop components. Thus, it appears that the intermittent problem began as a result of this maintenance activity. "Based on the review of both calibration information as well as satisfactory performance of the two HPCI System surveillances during the affected time frames (including when HPCI was in the "faulted condition"), it was determined that the observed condition had no impact on the capability of the HPCI System to perform its safety function, and thus the system remained operable. Therefore, the above referenced notification is being retracted". NRC R1DO (Cliff Anderson) notified. The NRC Resident Inspector was notified of this Retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-22
39081 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-07-22 00:45 | 2002-07-22 02:33 | 2002-07-22 | REACTOR AUTOMATICALLY TRIPPED FROM 100% POWER ON REACTOR TRIP/TURBINE TRIP The reactor trip/turbine trip from 100% power was caused by a loss of main turbine condenser vacuum that occurred while flushing the condenser waterboxes. The cause is unknown and being investigated at this time. All control rods fully inserted, no ECCS actuated and all emergency and non-emergency systems functioned as designed. The main steam stop valves were manually closed to arrest RCS cooldown. RCS temperature was stabilized using the atmospheric relief valves. The NRC Resident Inspector was notified, | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-22
39080 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-07-21 20:33 | 2002-07-21 22:48 | 2002-07-21 | AUTOMATIC REACTOR SCRAM CAUSED BY TURBINE TRIP The licensee reported that an automatic reactor scram occurred due to a turbine trip. The cause of the turbine trip is under investigation. Group 2 and 3 isolations occurred as expected during post scram conditions. The lowest reactor vessel water level was 0 inches. All systems functioned as designed. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-21
39079 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2002-07-20 16:45 | 2002-07-20 22:15 | 2002-07-20 | AUTOMATIC EDG START DUE TO LOSS OF THE OFFSITE POWER TRANSFORMER "On July 20, 2002 at 1645, the "A" Emergency Diesel Generator automatically actuated and powered the "A" 4160V Engineered Safeguards bus. This event is Reportable as an 8-Hour Notification per 10 CFR 50.72 (b) (3) (iv) (B) (8). The actuation occurred due to the loss of the Off-Site Power Transformer. The cause of the transformer loss has been identified to be a faulted cable between the Off-Site Power Transformer and the "A" 4160 V Engineered Safeguards bus." The licensee reported the unit was entered into a 72 hour LCO action statement per TS 3..8.1.A. Corrective maintenance has been started to replace the cable within the specified TS AOT. The licensee reconfigured the electrical line-up and was able to secure the EDG. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-07-20
39078 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-07-19 09:45 | 2002-07-19 18:09 | 2002-07-19 | APPENDIX R CABLE SEPARATION AND BREAKER COORDINATION ISSUES AT WOLF CREEK "On July 19, 2002 at approximately 0945 CDT, based on discussions with Callaway, conditions were discovered where a postulated fire could lead to the loss of motor control centers that power post fire safe shutdown equipment in both trains. Wolf Creek is in Mode 1, at 100% power. "A postulated fire in the Auxiliary Building 1974' Fire Area A-1 could cause loss of motor control centers NG01A ("A" train) and NG02A ("B" train). NG01A and NG02A supply post fire safe shutdown equipment such as "A" and "B" train pump room coolers and miscellaneous valves. "10 CFR 50 Appendix R requires that one train of systems necessary to achieve and maintain post fire safe shutdown will be available. Conditions have been identified where there is mis-coordination of the ground fault protection on feeder breakers. This could cause the entire MCC to be lost in the case of a ground fault. Feeder breakers on both MCCs have been identified as having ground fault protection mis-coordination. The cables for the associated loads have less than 20 feet of horizontal separation causing the above identified MCCs to be potentially lost due to a fire in Fire Area A-1. This does not meet the requirements of 10 CFR 50 Appendix R.lll.G. "In addition, it has been identified that post fire safe shutdown cables in Fire Area A-I for the "A" and "B" RHR pump room coolers have less than 20 feet of horizontal separation and do not meet the separation requirements of 10 CFR 50 Appendix R.lll.G. "Based on the guidance provided in NUREG 1022 Revision 2, this situation meets the criterion of I0 CFR 50.72(b)(3)(ii)(B) for an 8-hour ENS notification, as it relates to being in an unanalyzed condition. "The licensee has implemented a 1-hour fire watch and is developing compensatory measures. "The licensee is continuing its review to determine if there are any other cable separation/breaker mis-coordination issues that may lead to similar consequences." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-07-19
39077 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-07-19 09:45 | 2002-07-19 17:33 | 2002-07-19 | APPENDIX "R" BREAKER COORDINATION AND SEPARATION ISSUES AT CALLAWAY "On July 2,2002, with Callaway Plant in Mode 1 at 100% power, an Operability Determination was completed that revealed the potential for Safety Related components and electrical load centers to experience a common cause failure if a fire were to occur in a specific location. If the postulated fire were to occur in 1974' Auxiliary Building Fire Area A-1, safety related load centers NG01A and NG02A (opposite trains) could experience a fire induced ground fault condition due to cable damage on downstream loads. This ground fault condition could cause the loss of either or both NG01A and NG02A. NG01A and NG02A supply post fire safe shutdown equipment such as the "A" and "B" Residual Heat Removal (RHR) pump room coolers. Discussions with Wolf Creek on July 19, 2002 in conjunction with the ongoing evaluation concluded this scenario could impact post fire safe shutdown equipment. "In addition, it has been identified that cables in Fire Area A-1 for the "A" and "B" RHR pump room coolers, which are post fire safe shutdown equipment, have less than 20 feet of horizontal separation and do not meet the separation requirements of Appendix R lII.G.2, as committed to. "Based on the guidance provided in NUREG 1022, Revision 2, this situation meets the criterion of 10 CFR 50.72(b)(3)(ii) for an 8-hour notification. "The following compensatory actions have been taken: - An hourly fire watch was established for the affected area on 7/2/02 as the evaluations were completed. - Circuit Breakers associated with Essential Service Water Sump Heaters have been isolated, pending completion of a design change to address electrical coordination consistent with the FSAR. - An Operations Night Order detailing actions to be taken to restore NG01A and or NG02A if a fire were to occur that affected these load centers. Actions include measures to isolate faulted circuits. - Permanent revisions to Fire Area Pre-plans are under evaluation to incorporate the guidance of the Operations Night Order. "The licensee is continuing its review to determine the extent of Cable Separation/Breaker Coordination issues that may lead to similar consequences." The NRC Senior Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-07-19
39076 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2002-07-19 | 2002-07-19 16:16 | 2002-07-19 | LOSS OF COMMUNICATIONS CAPABILITY AT THE JOINT EMERGENCY NEWS CENTER "The following event description is based on information currently available. It through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 1OCFR5O.73. "On July 19, 2002 at approximately 10:30 AM Mountain Standard Time Palo Verde Emergency Planning personnel were notified that installed communications to and from the Joint Emergency News Center (JENC) had been totally disabled when an underground cable was cut. The affected cable and the JENC are located in Phoenix, AZ. "This loss of communications capability does not affect the assessment or response capability of Palo Verde, state or county personnel in the event of an emergency The JENC and its communications capability are an integral part of media notification and information dissemination as described in the Palo Verde Emergency Plan. "As a compensatory measure, the state has access to cellular phones for use in the JENC. The state will deploy those phones in the event of an actual emergency. In addition, most media personnel normally carry their own cellular phones The phone company has assigned their highest priority to this repair. The latest estimate for repair is approximately one-half day. "The cable was cut yesterday at approximately 3:00 PM on Thursday, July 18, 2002 but the state was not informed until approximately 09:00 AM today and then the state notified Palo Verde at approximately 10:30 AM." The NRC Resident Inspector was notified. *****UPDATE ON 7/19/02 AT 19:22 FROM MARKS TO LAURA***** "The state has notified Palo Verde that JENC communications were restored at 13:28 MST on July 19, 2002." Notified R4DO (L. Howell). | 99 | 98 | 99 | 99 | 98 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-07-19
39075 | 0 | ELI LILLY & COMPANY |  |  |  |  | 2002-06-20 | 2002-07-19 15:40 | 2002-07-19 | LOST/MISSING NUCLEAR MATERIAL AT A RESEARCH FACILITY During an annual audit, Eli Lilly & Company became aware of lost nuclear material involving 9.4 milli-curies of Carbon-14. The last accounting of the material was in December, 1999. The material is used for basic metabolic research purposes. The licensee suspects that the material may have been disposed of as radwaste. The licensee investigation will continue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-07-19
39074 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-07-19 14:13 | 2002-07-19 15:15 | 2002-07-19 | OFFSITE NOTIFICATION AT IP2 OF ONSITE FATALITY The licensee reported an onsite fatality occurred that prompted the need to notify the New York State Public Service Commission and the local Fire Department which responded to the site. Specifically, a contract worker was electrocuted while trimming trees onsite, behind the emergency diesel generator building, adjacent to a 138 KV feeder. The event resulted in the protective relaying tripping the feeder and a loss of offsite power (LOOP) resulted. The plant remained online at 100% power. The emergency diesel generators were started and powered two of the safeguard buses. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-07-19
39073 | 0 | IOWA RADIATION PROTECTION |  |  |  |  | 2002-07-17 09:00 | 2002-07-19 12:03 | 2002-07-19 | BROKEN RADIOGRAPHER CAMERA "As a result of one of our cameras had a source jammed because the camera fell from a ladder it was sitting on during an exposure, we are submitting the following response. "Project Information: "Date: July 17, 2002 at approx. 9:00 A.M. Rural water tower, south of Osceola, Iowa approx. 4 miles Jobsite- down a dead-end road, in a field Source S.N. 04016B 40.5 curies Contractor: Phoenix Fabricators & Erectors, Inc. "Stork-Twin City Testing Corporation was at a temporary project site performing radiographic testing when the camera fell off a ladder the camera was sitting on (approx. 3 feet to the ground). The source would not crank back into it's shielded position. I asked him, if they had resecured the area and his response was that they had and that they had also informed the contractor at the site of this incident. I told him, I was on my way and arrived at the site approx. one hour later. I loaded my truck with lead shielding and tools that might be needed to free up the source. Arriving at the project site, I surveyed the guide tube from a distance and found that the source was approx. 1 foot from the camera. They had the crank apart, so you could pull on the cable, in which I had them do prior to my arrival, but they said it would not move, I then tried this myself. I pushed on the cable and then pulled it and the source went in the camera to it safe position. We surveyed the camera and the guide tube and confirmed it was secured in the camera. We then unconnected the control cable and checked the source end with a nogo gauge and found it to be OK, we also cranked the cable out and checked it for any bends or other damage and found it to be OK. We removed the bent guide tube and replaced it with a good tube. We then cranked the source out and made sure everything was functioning properly. "We then had an onsite safety meeting, which concluded that this would be avoided in the future, by tying the camera to a stationary object so the camera cannot fall to the ground and bend the guide tube. "There was no over exposure to the public (contractor's personnel) or to the radiographers during this incident and the radiographers performed their duties in a satisfactory manner, concerning the safety for all and the following of our accident procedures." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2002-07-24
39072 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2002-07-17 14:30 | 2002-07-19 11:30 | 2002-07-19 | AGREEMENT STATE REPORT: EQUIPMENT FAILURE "On July 17, 2002, the Arizona Radiation Regulatory Agency was notified by the Licensee that a Novoste Beta-Cath system utilizing 55mCi (2.04GBq) of Strontium-90 had failed to retract after completing treatment of a patient. Within seconds of determining that a failure had occurred, the Licensee implemented emergency withdrawal procedures and successfully removed the source without causing a misadministration. The patient was surveyed and confirmed that all treatment radioactive material had been removed. "Initial examination by the Licensee did not determine a probable cause of the failure of the return of the source to the shielded condition. The entire system is being returned to the manufacturer for evaluation. Georgia is aware of this event. "Agency continues to investigate this event. "No press coverage is occurring or expected for this event. "First Notice: 02-9 "The State of Georgia and the U.S. NRC, is being notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2002-07-24
39071 | -1 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-07-18 22:55 | 2002-07-19 06:30 | 2002-07-25 | UNIT 2 CORE COOLING BAR ON THE SAFETY PARAMETER DISPLAY SYSTEM (SPDS) WAS NOTED TO BE INOPERABLE. At 2255 hours on 07/18/02, the Unit 2 Core Cooling Bar on the SPDS was noted to be inoperable. A reboot the system was attempted, but the SPDS indication did not change. Further checks showed that multiple computer points (46 total) had been turned off (off scan), which made the data points invalid. These points would not have been immediately available if needed. The points were all placed on scan, and the Unit 2 Core Cooling SPDS Bar returned to its normal condition. The remaining SPDS functions were functional during this time, only the Unit 2 Core Cooling SPDS Bar was affected. The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTED AT 1344 EDT ON 7/25/02 BY JOHN DUFF TO FANGIE JONES * * * The licensee determined after further review that the loss of the Unit 2 Core Cooling Bar on the SPDS did not constitute a major loss of emergency assessment capability. There were other indications readily available and the balance of the SPDS was operable. This event notification is retracted. The licensee notified the NRC Resident Inspector. The R2DO (Mark Lesser) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-07-19
39070 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-07-18 | 2002-07-18 18:43 | 2002-07-18 | ATMOSHERIC STEAM DUMP VALVE PRESSURE LOCKING CONCERN "At approximately 1600 hours on July 18, 2002, an engineering evaluation concluded that under certain conditions 1MS-156, a manually operated main steam atmospheric dump valve (ADV), could have been susceptible to Pressure Locking which could have prevented the opening of the valve during a postulated event. This notification involves a single unit 1 ADV (1MS-156) on 1 of 2 steam flow paths. Due to a dissimilar valve design, this condition does not affect either the unit 2 or unit 3 ADVs "Research into the condition has determined that 1MS-156 was potentially susceptible to pressure locking during the time of reactor operation, from initial valve installation in November 1997, to when this condition was rectified on July 10, 2002 (by the installation of a pressure relief device on the valve bonnet) . Since the cause of the pressure locking has been fixed, there is no current operability concern. "The ADVs are credited for opening for decay heat removal and cooling down the Reactor Coolant System to reduce pressure. In several event scenarios involving postulated Steam Generator tube leaks, this is desirable in order to minimize offsite dose releases. Failure of 1MS-156 during such an event could increase the time required to achieve cold shutdown (Mode 5) and the postulated off-site doses associated with the accident analysis. However, the analyses for such events (for example, the UFSAR Chapter 15 accident analysis for SG tube rupture) do not assume any failures of the ADVs. "This is a historical condition reportable under 10 CFR 50.72(b) (3) (v) . This regulation requires that an 8-hour ENS report be made of any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) . Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) . Control the release of radioactive material; or (D) - Mitigate the consequences of an accident. "Investigation into the cause of this condition is ongoing." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2002-07-18
39069 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2002-07-18 10:19 | 2002-07-18 11:35 | 2002-07-18 | OFFSITE NOTIFICATION FOR OIL SPILL >10 GALLONS Licensee notified the National Response Center and State Department of Environmental Protection of an oil spill >10 gallons. Hydraulic oil spilled from a fork lift onto the ground inside plant property and cleanup is in progress. Site has no resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-07-18
39068 | -1 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2002-07-12 16:00 | 2002-07-18 11:40 | 2002-07-18 | AGREEMENT STATE REPORT INVOLVING A MEDICAL MISADMINISTRATION "The Technologist (S.H) received a request to perform a Bone Scan on an inpatient. She selected an MDP Dose (25.1 mCi) and proceeded to the room listed on requisition. She approached the patient stated the name. The patient acknowledged the name. The technologist explained the procedure and injected the patient. When the patient presented to the Nuclear Medicine Department with hospital chart it was discovered that the misadministration had occurred. The technologist notified the authorized user, the referring physician [and] the Radiation Safety officer. The referring physician agreed to notify the patient. The Technologist was reinstructed to check the hospital chart for a written order and verify the patients identity by checking the hospital ORM board." Used Tc-99m MDP Bone. *****RETRACTED ON 7/18/02 AT 15:27 EDT FROM VOLPE TO LAURA***** The licensee determined the event was NOT reportable since the dose was below the threshold (greater than 5 REM whole body or greater than 50 REM for organs) for reportability. Notified R2DO (C. PAYNE) and NMSS (F. Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | KY | OTH | AGR |  |  |  |  | 0 | 2002-07-23
39067 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-07-16 13:19 | 2002-07-16 18:15 | 2002-08-22 | TECH SPEC 3.0.3 ENTERED AFTER DECLARING BOTH TRAINS OF CONTROL ROOM VENTILATION INOPERABLE "On 7/16/02 at 1319 hours, the Hope Creek Generating Station experienced a trip of the in-service 'B' train of Control Room Ventilation and it's associated Chiller. The standby 'A' Train attempted to start, but it's chilled water pump tripped precluding a successful start. This condition rendered both trains of Control Room Emergency Filtration INOPERABLE. In accordance with Technical Specifications 3.7.2, both trains were declared Inoperable and Technical Specification 3.0.3 was entered. At 1400 hours the 'B' Control Room Ventilation train was successfully restored to service and Operable status and Technical Specification 3.0.3 was exited. This event is being reported in accordance with 10CFR50.72(b)(3)(v) because both trains of Control Room Emergency filtration were unavailable for approximately 40 minutes. There was no power reduction associated with this event. No additional safety related equipment was inoperable at the time of the event. "The initiating condition is still under investigation, but is believed to have been induced as the result of an associated cooling coil fill evolution that caused a low head tank level and potential air induction that resulted in the trip of the in-service cooling train and subsequently the standby train. As of the time of this report the 'A' Control Room Emergency Filtration Train is still inoperable pending completion of fill and vent of the supporting chilled water system." The licensee will inform the Lower Alloways Creek Township and has informed the NRC Resident Inspector. ***RETRACTION ON 08/22/02 AT 1021 ET BY ERV PARKER TAKEN BY MACKINNON**** "Subsequent evaluation determined that if a postulated accident had occurred during the time that both trains of the Control Room Emergency Ventilation system were INOPERABLE, control room dose would be less than the acceptance criteria specified in 10CFR50.67 and Regulatory Guide 1.183 and bounded by our current analysis. The site boundary doses are not affected. The dose impact of the condition as it existed would be bounded by the current analysis. Thus, the safety function would have been fulfilled, and the notification event number 39067 is retracted" R1DO (Cliff Anderson) notified. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-16
39065 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-07-11 | 2002-07-16 14:08 | 2002-07-16 | AGREEMENT STATE REPORT INVOLVING Cs-137 SOURCE FOUND IN SCRAP STEEL "SUBJECT: North Carolina Incident No. 02-21 "On July 11, 2002 the North Carolina Radiation Protection Section was notified by AmeriSteel Corp., Charlotte Steel Mill Division that they had discovered a radioactive source in their scrap stream. The source has been isolated and secured by AmeriSteel personnel. Exposure rates of 120 microR/hr @ 3" have been reported by AmeriSteel personnel. Using an Exploranium GR-130 AmeriSteel personnel have identified the source as Cesium-137. The North Carolina Radiation Protection Section is continuing to gather information and work with the facility to provide appropriate action." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-07-19
39064 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2002-07-12 08:30 | 2002-07-16 12:05 | 2002-07-16 | AGREEMENT STATE REPORT INVOLVING EQUIPMENT FAILURE OF SHIPPING CONTAINER "Event Report ID No.: TN-02-094 "License No.: R-73008 "Licensee: Duratek Radwaste Processing, Inc. "Event date and time: July 12, 2002, 0830EDT "Event location: Oak Ridge, Tennessee "Event type: Equipment failure "Notifications: USNRC Region II "Event description: Duratek Radwaste Processing, Inc., a Tennessee licensee, called the Knoxville Field Office Manager to report that a sealand container of metals from Calvert Cliffs Nuclear Power Plant was received at the Duratek facility on July 12, 2002. During performance of the receipt survey/inspection, metal from the interior was observed protruding approximately 1/2" from a penetration in the side of the container. No detectable contamination was found on the accessible item or on the adjacent sealed surfaces. The penetration in the container wall was covered to permit undisturbed storage pending further investigation. "Media attention: None" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2002-07-19
39063 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2002-07-10 | 2002-07-16 10:51 | 2002-07-17 | PARTIAL SHIPMENT OF SCANDIUM - 46 LOST IN TRANSIT A FedEx shipment from the Spectra Tek in Albuquerque to Protechnics in Lafayette, LA. of six packages of scandium - 46 at 40 millicuries each arrived at its destination one package short on 7/10/02. They are tracing the shipment and determined it was last scanned on 7/9/02 in Memphis, TN. **** Update at 1152 ET on 07/17/02 by Bill Floyd taken by MacKinnon **** The missing package containing the scandium-46 was found on the FedEx loading dock in Lafayette , LA. The package will be delivered to Protechnics. R4DO (Linda Howell) & NMSS EO (Fred Brown) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2002-07-19
39062 | 0 | JEFF ZELL CONSULTANTS |  |  |  |  | 2002-07-15 18:00 | 2002-07-16 09:52 | 2002-07-16 | DAMAGED TROXLER MOISTURE GAUGE On 07/15/02 in the evening an asphalt roller damaged the side of a Troxler Moisture Density Gauge, Model # 3411. The sources were not damaged but the outer casing of the Troxler gauge was damaged and the top of the source rod was bent. Normal radiation readings of the gauge of 0.2 mr/hr at 3' were taken by a Geiger counter. The gauge was run over near Lancaster, PA. on Old Philadelphia Pike. The gauge is now back at Jeff Zell Consultants located in Coraopolis, PA. Jeff Zell Consultant's said that they were going to send the gauge back to Troxler late this week. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2002-07-16
39061 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-07-15 18:52 | 2002-07-15 20:18 | 2002-07-15 | OFFSITE NOTIFICATION INVOLVING AIRCRAFT FLYOVER OF OWNER CONTROLLED PROPERTY "A 1852 a low flying aircraft flew near (~ 3000 feet) from the facility at an altitude of approximately 500 feet. The aircraft was a military style helicopter. The FAA was notified at 1901 [Fort Worth Air Traffic Control]. Flight path was from the southwest to the northeast." The licensee informed the FAA, local law enforcement and will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-07-15
39060 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-07-15 14:35 | 2002-07-15 17:20 | 2002-07-15 | "THIS IS A COURTESY NOTIFICATION AND DOES NOT FALL WITHIN 10CFR50.72 GUIDELINES "At 1435 hours on 07/15/02, smoke was reported within the Simulator portion of the Susquehanna Learning Center, however, no flames were visible. The Learning Center is located outside the Protected Area of the Site. The offsite fire department was notified for assistance and the on-site Fire Brigade was activated. The source of the smoke was determined to be from a discharge of the HVAC refrigerant into the supply ducting to the Simulator. There are no plans to issue a Press Release at this point in time. "This event was reviewed and determined not to be reportable under 10CFR50.72(b)(2)(xi). This is a courtesy call based on the potential media interest in the event." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2002-07-15
39059 | 0 | CRAIG TESTING LAB, INC. |  |  |  |  | 2002-07-15 13:15 | 2002-07-15 14:47 | 2002-07-15 | DAMAGED TROXLER MOISTURE DENSITY GAUGE Early this afternoon a Model # 3430 Troxler Density gauge was run over and damaged at Hopewell High School, Hopewell, NJ. The gauge contains 10 millicuries of Cs-137 and 40 millicuries of Americium-241. The caller said that the sources for the gauge were intact and not damaged. The gauge has been placed back in its carrying case and is now being transported back to Craig Testing Lab., Inc., which is about 1.5 hours driving time from Hopewell, N.J. The caller said that the gauge would be surveyed when the gauge was returned to Craig Testing Lab., Inc. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NJ | MAT | [5 empty] | 0 | 2002-07-15
39058 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-07-13 16:22 | 2002-07-13 18:42 | 2002-07-13 | AUTOMATIC TURBINE TRIP/REACTOR TRIP DUE TO ACTUATION OF A MAIN TRANSFORMER DIFFERENTIAL ELECTRICAL RELAY The following text is a portion of a facsimile received from the licensee: "At 1622 on July 13, 2002, the Unit 1 reactor tripped due to an automatic signal. All plant safety systems were in service at the time of the trip, and all systems responded as designed. All control rods inserted as required, and the Auxiliary Feedwater (AFW) System initiated as expected." "The reactor trip resulted from a turbine trip signal that was generated as a result of a main transformer differential electrical relay actuation. The cause of the differential relay actuation is under investigation at this time." "The plant is currently stable in Mode 3 and will remain in this mode until completion of the investigation." The licensee stated that there were no related maintenance or surveillance activities ongoing at the time of the event but that there were heavy rains in the area earlier in the day. The licensee also stated that normal charging and makeup, pressurizer heaters and sprays, and the reactor coolant pumps are currently being utilized for primary system inventory, pressure and transport control. Secondary system steam is being dumped to the condenser, and the main feedwater pumps are supplying water to the steam generators. The auxiliary feedwater system has been secured, and containment parameters are normal. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-07-13
39057 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-07-13 01:10 | 2002-07-13 02:57 | 2002-07-13 | MANUAL REACTOR TRIP DUE TO DEH MALFUNCTION "Manual Rx trip due to DEH malfunction during initiation of downpower for scheduled valve testing. Automatic AFW actuation due to low S/G level following trip. 'C' S/G PORV remained open below lift setpoint. Valve shut manually from MCB." The licensee further noted that only the motor driven AFW pump started on a single low level signal as expected. The plant is stable in Mode 3, with normal feedwater and steam dumps to the condenser. An investigation will be completed prior to plant startup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-07-13
39056 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-07-12 22:23 | 2002-07-13 01:45 | 2002-07-13 | REACTOR TRIP ON UNDERVOLTAGE ON REACTOR COOLANT PUMP BUSSES "At approximately 2223 on 07/12/2002, Sequoyah Unit 2 (SQN-2) received an Automatic Reactor Trip on Reactor Coolant Pump Busses undervoltage. The cause of the undervoltage was due to the loss of the Unit 2, 2B and 2D unit boards as a result of a loss of the 2B Start Bus. The 2B and 2D Unit Boards are the 6.9 kV electrical feeds to the 2-2 and 2-4 RCPS, respectively. Plant response as a result of the loss of the Unit Boards was as expected, including the emergency start of all emergency diesel generators and the 2A-A Shutdown board being fed from Its emergency diesel generator. "Plant personnel were in the process of returning the 'B' Common Station Service Transformer (B-CSST) to service at the time of the event. The plant is currently being maintained in Mode 3 at NOT/NOP, 547 degrees F/ 2235 psig respectively, by use of the plant's auxiliary feedwater system and steam dump system. "The cause of the trip of the 25 start bus is unknown at this time and investigation is on going. The Unit 2 Loop 4 atmospheric relief valve (2-PCV-1-30) which opened on the Reactor Trip and did not reclose. Manual operator action was taken to close the affected valve." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-07-13
39055 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-07-12 | 2002-07-12 17:12 | 2002-07-12 | AGREEMENT STATE REPORT REGARDING INCORRECT ENTRY OF CATHETER POSITION/LENGTH INTO THE TREATMENT PLANNING SYSTEM RESULTING IN MISMATCHED HDR DWELL TIME AND CATHETER AT SWEDISH MEDICAL CENTER IN SEATTLE, WASHINGTON The following text is a portion of an e-mail received from the WA Department of Health, Division of Radiation Protection: "This is notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection." "STATUS: new" "Licensee: Swedish Medical Center" "City and state: Seattle, WA" "License number: WN-m008-1" "Type of license: medical broad scope" "Date of event: July 11, 2002" "Location of Event: Seattle, WA" "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH onsite investigation; media attention) Incorrect entry of catheter position/length into the treatment planning system resulted in mismatched HDR dwell time and catheter. The error was noted after the second of four planned treatments. Estimates of the actual doses already delivered indicated from 17% to 25% underexposure to certain target volumes and 25% to 50% additional exposure to adjacent normal tissue. Each of the four treatments was intended to deliver 600 centigray through three catheters with varying dwell times. In effect, two catheters were 'reversed' in the planning system and a 'long' dwell was used in a 'short' catheter, and vice versa. At the end of the second treatment, a significant volume of the target tissue received only 900 to 1000 centigray instead of the intended 1200 centigray. The licensee determined that the overall therapy was "salvable" and by modifying subsequent treatments would be able to correct the dose to the target tissue and at the same time minimize any additional dose to the adjacent normal tissue. No adverse effects are anticipated. The licensee generates a customized plan and treatment verification flow chart under its quality assurance program for each patient. The licensee has determined that the sign-off for 'number of catheters' needs to be modified to 'number and labeling of catheters' as the appropriate corrective action." "What is the notification or reporting criteria involved? WAC 246-240-050 Notifications, records, and reports of therapy misadministrations." "Activity and Isotope(s) involved: 3.3 Ci Ir-192" "Device (HDR, etc.) Mfg., Model; computer program: Nucletron MicroSelectron-HDR 'Classic' " "Exposure (intended/actual); consequences: 1200 centigray intended/900 centigray actual" "Was patient or responsible relative notified? (will be)" "Was written report provided? (not yet)" "Was referring physician notified? YES" "Consultant used? NO" (Contact the NRC operations officer for State contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-07-17
39054 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2002-07-05 10:00 | 2002-07-12 11:22 | 2002-07-12 | SYNCOR PHARMACY REPORTED THAT A DELIVERY VEHICLE CONTAINING TECHNETIUM 99 WAS STOLEN A courier vehicle carrying a Yellow II labeled package containing 125 millicuries of Technetium 99m was stolen in Omaha, NE on 7/5/02. The driver had stopped briefly to perform a personnel errand while he was on a delivery to Norfolk, NE. As of this date, neither the vehicle nor the nuclear pharmaceutical have been located. The local police have been notified and there has been some media interest. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2002-07-17
39053 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-07-11 18:00 | 2002-07-11 22:02 | 2002-07-11 | DISCOVERY THAT THE ALTERNATE POST-LOSS OF COOLANT ACCIDENT (LOCA) BORATION DILUTION FLOW PATH FOR ALL UNITS IS OPENED IF THE PRIMARY PATH FAILS The following text is a portion of a facsimile received from the licensee: "Event: At 1800 hours on 7/11/02, a review of the small break LOCA mitigation section of the [emergency operating procedure (EOP)] determined that the alternate post-LOCA boron dilution flow path for all units is opened if the primary path fails. This alternate flow path was designed to be opened during a large break LOCA. Current analyses do not exist to support opening the flow path under elevated [reactor coolant system] pressures. With this being the case, execution of the EOP during a [small break LOCA] could open the alternate flow path under conditions that may potentially degrade portions of the [low pressure injection (LPI)] system (e.g. [reactor building emergency sump] screen, LPI pump). Since analyses do not exist to support operation of the flow path under elevated pressures, this condition is being conservatively reported under 10 CFR 50.72(b)(3)v." "Initial Safety Significance: The potential safety significance of this issue is that opening the alternate boron dilution flow path under elevated pressures could adversely impact the reactor building emergency sump. This flow path would only be opened following a single failure of the primary path. Oconee is conservatively reporting this condition. Analyses are being performed to determine whether the EOP guidance related to opening this flow path could have impaired sump recirculation." "Corrective Action(s): Guidance has been provided to the operating shifts to not open the alternate flow path. An EOP change will be expeditiously made to resolve this procedural issue." The licensee notified the NRC resident inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-11
39051 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2002-07-11 02:41 | 2002-07-11 04:00 | 2002-07-11 | INITIATION OF PLANT SHUTDOWN FROM 82% AS REQUIRED BY TECH SPEC 3.0.3 It was determined that reasonable assurance of continued operability of Safety System Components associated with Unit 2 steam lines could not be supported. They had noticed perturbations since the beginning of June indicating a problem with their steam separators. They have since had an operability and loose parts evaluation for this and recently experienced another perturbation that's calling into question the loose parts evaluations. Therefore, the licensee is assuming that there may be a loose parts problem, so they have commenced plant shutdown at 0241 and are to be in hot shutdown in 12 hrs and cold shutdown in 36 hrs. The NRC Resident Inspector was notified. | 0 | 80 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-07-11
39050 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-07-10 15:15 | 2002-07-10 18:48 | 2002-07-10 | ALERT NOTIFICATION SYSTEM SIRENS FOUND INOPERABLE "At approximately 1515 CDT, a routine test of the Alert and Notification System sirens in Manitowoc County, WI revealed that all 14 of 14 sirens in the county could not be activated remotely from the county's dispatch center. This event did not affect the ability to activate these 14 sirens remotely from Point Beach Nuclear Plant. The county believes that their transmitter tower had been hit by lightning. Powering down and restarting the transmitter restored the county's siren activation system to operation at 1657. All sirens are now fully operational. "Although no major loss of sirens actually occurred, this notification is being conservatively made because the county is the entity that normally activates the sirens and would not have been able to do so without first contacting Point Beach Nuclear Plant. " The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-07-10
39049 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-07-09 23:04 | 2002-07-10 03:26 | 2002-08-27 | CONTAINMENT ATMOSPHERE DILUTION NITROGEN INVENTORY NOT MEETING TS REQUIREMENTS During routine daily instrument checks on July 9, 2002, the control room operator found the Containment Atmosphere Dilution (CAD) Nitrogen inventory just above the Technical Specification required inventory line of 67,000 scf (2150 psig and 90°F). The previous day instrument check had the CAD nitrogen inventory at 2250 psig and 94°F (approximately 69,000 scf). An operator was dispatched to the CAD compressor building to raise nitrogen pressure by operating the CAD compressor. As the in-plant operator was starting the CAD compressor, the control room operator again checked the pressure and temperature of the CAD storage bottles and found that it fell just below the require 67,000 scf line (2110 psig and 84°F). The startup of the CAD compressor requires the draining of the suction receiver and opening of the suction and discharge valves. This process consumed enough nitrogen inventory to go below the Technical Specification value of 67,000 scf. At 2304, the CAD system was declared inoperable per Technical Specification 3.6.3.1. A and a seven day LCO entered. The CAD compressor was operated to restore CAD nitrogen volume and the CAD LCO was exited at 2330 when CAD inventory was greater than the required Technical Specification of 67,000 scf. During subsequent investigation, it had been determined that surveillance NS 730301, Functional Check and Calibration of Containment Atmosphere Dilution System had been performed during the dayshift on July 9, 2002. During this surveillance, it performs a functional check of the CAD system by performing a flow of nitrogen from the CAD bottles through a test rig thus using a portion of the CAD nitrogen inventory. At the completion of the surveillance, the check of the CAD nitrogen inventory was just above the Technical Specification line. The surveillance was completed at 1404 and at that time no action was undertaken to restore margin to the CAD nitrogen inventory Technical Specification requirement. The NRC resident Inspector was notified * * * RETRACTED AT 1200 EDT ON 8/27/02 BY STEVE KOTTENSTETTE TO FANGIE JONES * * * "A follow up root cause of the event was conducted, and as part of that effort, the associated pressure indicator was recalibrated. It was found to be reading about 50 psig Low in the range (2200 pounds) where the reading was taken for nitrogen inventory determination. This means that actual CAD inventory remained greater than 67,000 SCF at all times. Although there was conservative indication of CAD inventory, the CAD system was always capable of performing its required safety function and was never actually inoperable. No LER is required under 10 CFR 50.73 (a)(2)(v) and the immediate notification under 10 CFR 50.72 (b)(3)(v) should be retracted." The licensee notified the NRC Resident Inspector. The R3DO (Kenneth Riemer) was notified. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-10
39048 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-07-09 11:55 | 2002-07-09 15:53 | 2002-07-09 | TECH SPEC REQUIRED SHUTDOWN DUE TO THE LOSS OF BOTH CONTROL ROOM AIR CONDITIONING UNITS "Ft Calhoun Station entered Technical Specification 2.0.1 requiring plant shutdown at 1155 due to having both Control Room air conditioning units inoperable. The Tech Spec was exited at 1220 when one of the two installed units was restarted and confirmed to be providing adequate cooling. Both air conditioner units were inoperable for 25 minutes. No plant shutdown preparations were made during this time. VA-46A remains inoperable with Tech Spec 2.12.2(1) 30 day limiting condition of operation in effect. "At 1150 the Control Room temperature was observed to be rising but below the 80 degree F log setpoint with the VA-46B unit running. "At 1155 preparations to start the other unit, VA-46A were made. These startup preps require the momentary opening of the VA-46A disconnect switch, rendering it inoperable during this short period. After starting VA-46A maintenance technicians informed the Control Room staff that the VA-46A compressors had tripped due to low oil level rendering the unit inoperable. Maintenance technicians informed the Control Room that the VA-46B unit compressors were found tripped at 1155 rendering it inoperable. "The VA-46B unit (the unit originally in operation at the start of this event) was shutdown, reset, and restarted. All compressors loaded. Control Room temperature were observed to be lowering. VA-46B unit was declared operable at 1220. Tech Spec 2.0.1 was exited at 1220. "Highest temperature observed in the Control Room was 80 degrees" The licensee is investigating what caused the low oil level in the VA-46A compressors. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-07-09
39047 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-07-08 16:00 | 2002-07-08 16:42 | 2002-07-08 | OFFSITE NOTIFICATION TO STATE OF THE CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION In a Material Engineering Lab storage cabinet a 250 milliliter container approximately 25% full was found to contain liquid picric acid. The Material Engineering Lab is located in a Warehouse in the Owners Control Area but is not in the Protected Area. A contract HAZMAT team, Onyx, was called to the site to remove the container. The State of Connecticut Department of Environmental Protection was notified of this information. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-07-08
39046 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-06-19 12:00 | 2002-07-08 15:27 | 2002-07-08 | MISSING THICKNESS MEASURING GAUGE On 07/08/02 Mayo Construction company notified the Massachusetts Radiation Control Program that a 50 millicurie Sr-90 thickness paper measuring gauge has been missing since April/May of this year. It is believed that it was sent out as scrap metal to the Prolerized New England scrapyard which is located in Everett, MA. Mayo Construction company recently acquired Perkit Folding Box Corp, which had the general license for the missing gauge and they were unaware of the thickness measuring gauge. The gauge manufacturer is Fife\DMC\Radiometry of Gaithersburg, Md. The source was manufactured by Amersham. The source was installed in a C-ARM type gauge in 1991 by TechControl of Mountain City, Georgia. The gauge is contained in a black box measuring 4"x11"x11" and it is labeled on the outside as containing radioactive material. The serial number on the gauge is 2412BC. Radiation levels on the outside of the gauge with its shutter closed is 40 to 50 milliRad/hr. Prolerized New England scrapyard has been notified and the licensee is still searching for the missing gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-07-11
39045 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-07-07 23:12 | 2002-07-08 02:57 | 2002-07-08 | AUTOMATIC REACTOR TRIP "At 2312 on 07/07/2002 Unit 2 Reactor automatically tripped from full power due to a high high Steam Generator Level In the 2B Steam Generator. Prior to the trip Vital distribution panel 1202 lost power when it's normal power supply inverter failed. All of the controlling channels of Steam Generator level were powered from this distribution panel and failed low on the loss of power. Operators were in the process of taking manual control of all Feed Water Regulating valves when the Main Turbine trip was actuated due to the high high level in Steam Generator 28. A Reactor Trip occurred due to Turbine Trip above 50% power. The unit is stable in Mode 3 with RCS temperature at 567 degrees Fahrenheit, and RCS pressure of 2235 pslg. "We also make the following report per 10CFR50.72(b)(3)(iv): Following the Reactor Trip the Auxiliary Feed Water System automatically actuated on low Steam Generator level. This is normal for a trip in Unit 2 from full power with the Model E Steam Generators. "The following information is also provided: "Did the control rods fully insert? Yes "Did steam bypass to the condenser or to atmosphere? The Steam Dump system automatically operated to maintain temperature. No steam bypass to atmosphere occurred. "Did any primary/secondary relief valve lift? NO "Any significant TS LCOs entered? TS 3.8.3.1 Action b. was entered due to vital DP 1202 not being powered from its normal power supply inverter. We must reenergize the AC distribution panel from its associated inverter connected to its associated D.C. bus within 24 hours or be in at least HOT Standby within the next 6 hours and in Cold Shutdown within the following 30 hours. "Item not understood: Channel 1 of P-13 Reactor Trip System interlock status light is currently blinking. This condition must be understood and corrected prior to restart." The NRC resident inspector was notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-07-08
39044 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2002-07-07 23:20 | 2002-07-08 03:00 | 2002-07-08 | BULLETIN 91-01 REPORT DUE TO A LIQUID LEAK AT NFS FUEL FACILITY The licensee reported a liquid spill that resulted when a column broke. This represented a loss of geometry control for criticality controls. One worker had skin contamination as a result of this event with contamination levels up to 100,000 DPM/CM SQUARED. The worker was in the process of being decontaminated. The liquid spill will be cleaned up using approved procedures. The licensee will notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 1 | 2002-07-08
39043 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-07-07 00:15 | 2002-07-07 04:50 | 2002-07-07 | HPCI BECAME INOPERABLE WHILE REPLACING AN INDICATING LIGHT BULB AT PILGRIM "On 07 July 2002, at 0015 hrs, HPCI was declared inoperable when it was discovered that the control power fuses for the HPCI pump discharge valve, MO-2301-8 had blown. The MO-2301-8 is a normally closed direct current (DC) motor operated valve. At the time of the event, control room operators were attempting to replace a burned out main control room light bulb for the closed indication for the valve. The operators reported that the light socket was loose. The newly installed bulb failed to illuminate. A field operator was dispatched to the alternate shutdown panel (ASP) for HPCI and reported that there was no light indication for the MO-2301-8 at the ASP as well. Qualified personnel then inspected the control power fuses within the DC breaker for the valve. It was determined that an instantaneous short circuit occurred due to the loose light socket when the light bulb was replaced, causing the control power fuses to blow. The light socket was tightened, the control power fuses were replaced, proper MO-2301-8 position indication was verified, and HPCI was declared operable at 0045 hrs." The USNRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-07-07
39042 | 0 | GEORGE WASHINGTON UNIVERSITY |  |  |  |  | 2002-07-05 17:00 | 2002-07-05 17:45 | 2002-07-05 | CONDITION OF LICENSE REPORT INVOLVING A STUCK IRRADIATOR SOURCE The RSO at George Washington University discovered during testing that the nominal 5,000 Ci Cs-137 source (measured 8/24/1986) used in their J.L. Shepherd Mk I irradiator had stuck in the up position. Radiation readings were immediately taken which indicated no excess personnel exposures were involved. The highest lateral reading at a distance of 30cm was approximately 0.18mr/hr. The door interlock is functioning properly preventing personnel from opening the device with the source withdrawn. As a precaution, access had been restricted to the area. The licensee will continue their efforts to contact the manufacturer or his service representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | DC | MAT | [5 empty] | 0 | 2002-07-05
39041 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2002-07-04 01:33 | 2002-07-04 05:57 | 2002-07-04 | REACTOR SCRAM FROM 94.6% POWER DUE TO TURBINE TRIP CAUSED BY GENERATOR TRIP AND LOCKOUT On July 4, 2002, at 0133, Clinton Power Station scrammed from 94.6% due to a Turbine Trip from a Generator Trip and Lockout. The initiating event for the scram is not presently known at this time but it is believed to be a problem with the Main Power Transformer (MPT) B. The Sudden Pressure MPT B alarm came simultaneously with the reactor scram. The Sudden Pressure MPT B alarm is brought in by the Sudden Pressure Fault Relay, which initiates a Main Generator trip and lockout, which trips the Main Turbine and initiates a reactor scram. The MPT B deluge system initiated, however, there was no physical evidence of any damage to MPT B. After conducting a visual inspection of MPT B, the deluge system was secured. A clearance is being applied to MPT B for investigation. The plant is presently in Mode 3, maintaining reactor pressure within a pressure band of 550 to 650 psig and level between Level 3 and Level 8, which is the normal level band. The plant responded normally on the scram. All rods fully inserted, no ECCS injection occurred and no relief valves lifted. The NRC Resident Inspector and the State were notified. - | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-04
39040 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-06-24 | 2002-07-03 12:09 | 2002-07-03 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following is taken, in-part, from a facsimile report: "A patient received 5 fractions of brachytberapy using an lr-192 HDR unit and a tandem/ovoids applicator. During the treatment planning process, an incorrect magnification factor for the orthogonal films on which the Dosimetry was based had been used. This resulted in an underdose of approximately 50% or more depending on the part of the treatment volume used for comparison. "The initial and corrected dosimetry has been reviewed by 3 additional physicists. The corrected Dosimetry has been verified using an independent film digitization system and TPS. A composite Dosimetry summary of the treatment as delivered has been prepared and verified. Based on that information the prescribing physician will administer an additional brachytherapy application to compensate for the lower than prescribed dose from the initial 5 fractions. [The original prescribing physician] "contacted the patient tonight, 2 July 2002. He reported the underdose, recommended an additional brachytherapy procedure and described the misadministration report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-07-09
39039 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-07-03 07:55 | 2002-07-03 09:40 | 2002-07-03 | SEA TURTLE CAPTURED AT OYSTER CREEK PROMPTING OFFSITE NOTIFICATION The licensee captured a live sea turtle at the site's dilution plant. The turtle is being transported to the Brigantine Marine Mammal Stranding Center. The licensee notified the National Marine Fisheries Service. The NRC resident inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-07-03
39038 | 0 | US ARMY |  |  |  |  | 2002-07-03 | 2002-07-03 09:39 | 2002-07-03 | US ARMY LOST A CHEMICAL AGENT AT FORT CUSTER IN MICHIGAN The US ARMY reported a lost chemical agent detector, model M43A1, at Fort Custer in Michigan. This occurred during a training exercise and an investigation has been started. The detector has a source of 300 microcuries of AM-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-07-03
39037 | 0 | POWER RESOURCES |  |  |  |  | 2002-07-01 | 2002-07-02 13:34 | 2002-07-02 | MONITOR WELL EXCEEDED TWO OF ITS THREE UPPER CONTROL LIMITS Monitor well FM6 in the F well field exceeded two of its three upper control limits (UCLs). A confirmation sample was collected on July 1, 2002. Date 7/1/02 Chloride (UCL 18 mg/l) 40 mg/l Conductivity (UCL 1121 umhos/cm) 793 umhos/cm Bicarbonate (UCL 230 mg/l) 233 mg/l Uranium (UCL 0.1 mg/l) 0.1 mg/l The licensee notified NRC Project Manager (Rick Weller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | WY | MAT | [5 empty] | 0 | 2002-07-02
39036 | 0 | ADAMS CONSTRUCTION COMPANY |  |  |  |  | 2002-07-01 15:40 | 2002-07-02 11:00 | 2002-07-02 | DAMAGED TROXLER MOISTURE DENSITY GAUGE Adams Construction Company reported that an asphalt roller ran over part of a Troxler moisture density gauge, model number 4640B, serial number 1752. The source remained intact and was not leaking. The gauge was transported to the asphalt plant located in South Boston, VA. The gauge will be examined by Troxler for evaluation and repair. The gauge contained a source of 8 millicuries of CS-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | VA | MAT | [5 empty] | 0 | 2002-07-02
39035 | 0 | US ARMY |  |  |  |  | 2002-07-01 19:30 | 2002-07-02 10:42 | 2002-07-02 | US ARMY LICENSE VIOLATION INVOLVING A CHEMICAL AGENT DETECTOR The US Army reported that License Item 15 was violated when a technician attempted to disassemble the cell assembly of a chemical agent detector at Fort Richardson. The cell assembly contains a radiological source of 300 microcuries of AM-241. The model number is M43A1. An investigation was initiated by the US Army to review this event. At this time there were no known personnel contaminations or radiological overexposures. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | MD | MAT | [5 empty] | 0 | 2002-07-02
39034 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-05-19 11:00 | 2002-07-02 10:47 | 2002-07-02 | RADIATION MONITOR DECLARED INOPERABLE While operating in Mode 1, in the process of a controlled shutdown to perform an elective repair of a condenser tube leak, Division "A" Refuel Pool Radiation Monitor lost power resulting in a Group 3A Primary Containment Isolation System (PCIS) actuation. The Group 3A isolation function as designed. Radiation levels in the area of the monitor were normal and the actuation was considered invalid. The Radiation Monitor was declared inoperable for maintenance. The monitor was declared operable at 1049 CST on 05/20/02 at which time the Group III isolation was also reset. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-07-02
39033 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2002-06-27 08:00 | 2002-07-01 08:16 | 2002-07-01 | RADIATION ALARM AT A WASTE TRANSFER STATION WAS ACTIVATED BY A TUCK CONTAINING REFUSE. A truck containing a roll off refuse container set off the radiation monitor at the Montgomery County Waste Transfer Station located in Rockville, MD at 0800 hours on 06/27/02. The refuse container was searched and a bag containing paper towels and rags found to be contaminated with cobalt-60 with a radiation reading of 0.5 mr/hr. The load was rejected and sent back to Neutron Products Incorporated, Dickerson, MD. The load was evaluated and the radioactive material was removed and placed into storage with radioactive waste. Neutron Products was cited by the State of Maryland for improper disposal of radioactive waste and inadequate surveying and monitoring. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2002-07-04
39032 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2002-06-30 18:58 | 2002-07-01 00:33 | 2002-07-01 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR PRESSURE DUE TO TWO ADDITIONAL STEAM DUMP VALVES FULLY OPENING DURING STARTUP. System Affected "Primary: Rx Trip, CEA, RCP's stayed on, PLCS" "Secondary: SBCS Open, MSIV's, ADV, MFW, AFW" Actuations and Their Initiating Signals "MSIS A & B @ 741 PSIA. Lowest Seen = MSIS setpoint" Causes "Prelim: 4 SBCS All Fast Open . . . " Effect Of Event Plant "Low S/G Pressure Rx Trip, Turbine Trip, MSIS isolated secondary. CVCS remained in service. MSIS verified and rest, then AFW initiated. (Did not want cooldown from steam-driven AFW Pp. Adequate S/G water level maintained throughout. Approx. 50% NR)." Actions Taken or Planned "EOI's: S023-12-1 (SPTA's), S023-12-2 (RTR), OI: S023-S-1.3.1 S0123-0-14 4 Hour" "E-PLAN Review P S/G" [decreased]) The licensee was going to bring the main turbine on line which was rolling at 1800 rpm. Two steam dump bypass valves were open dumping steam to the main condenser to help maintain reactor power at 18%. Unexpectedly two additional steam dump bypass valves opened. When these two additional steam dump bypass valves opened the first two open valves initial started to close then they went full open. Steam generator pressure decreased to the low steam generator pressure setpoint of 741 psia at which point an automatic reactor trip plus a main steam isolation signal (MSIS) was generated, main steam isolation valves (MSIV's) closed. All rods fully inserted into the core. Atmospheric steam dump valves were used to maintained proper reactor coolant system temperature. The licensee said that they did not have any leaking steam generator tubes. Proper steam generator water inventory was verified at which time the MSIS signal was reset, then one Motor Driven Auxiliary Feedwater Pump was manually initiated to maintain proper steam generator water level. Main feedwater system isolated due to the MSIS signal and the reactor trip. All emergency core cooling systems, emergency diesel generators are fully operable if needed. The electrical grid is stable. The licensee is investigating why the two additional steam dump bypass valves opened. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 |  | 18 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-07-01
39031 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-06-29 14:38 | 2002-06-29 16:43 | 2002-06-29 | SOUTH TEXAS NUCLEAR PROJECT SPURIOUS ACTUATION OF OFFSITE NOTIFICATION SIREN "At 14:38 on 6/29/02, received notification that a South Texas Nuclear Project Offsite Emergency Notification siren located in the Tres Palacios Oaks subdivision was spuriously going off over the last 4 hours. This notification was from a resident in the subdivision. This siren is going off while thunderstorms are moving through the area. The Matagorda County Sheriff's Department was informed by site personnel of these spurious alarms and personnel have been dispatched to resolve the issue with the siren." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0 | 2002-06-29
39030 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-06-29 08:52 | 2002-06-29 12:44 | 2002-06-29 | BROWNS FERRY SPURIOUS ACTUATION OF OFFSITE EMERGENCY NOTIFICATION SIRENS "At 0852 on 06/29/02, the Operations Duty Specialist (ODS) notified the Browns Ferry Shift Manager of a spurious actuation of the Off Site Emergency Notification Sirens for a duration of less than 3 minutes in Lawrence County, Alabama. A TVA news release is not planned at this time, however, the event is being reported due to inquires from county representatives to the TVA ODS regarding the siren activation. A review of the cause of the actuation is in progress. "This event is reportable per 10CFR50.72 (b)(2)(xi) as 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an onsite fatality or inadvertent release of radioactive contaminated material'." The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-29
39029 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-06-29 02:00 | 2002-06-29 05:51 | 2002-06-29 | OFFSITE NOTIFICATION KEMP'S RIDLEY SEA TURTLE CAUGHT AND GIVEN TO THE MARINE MAMMAL STRANDING CENTER. OFFSITE NOTIFICATION MADE TO THE NATIONAL MARINE FISHERY SERVICES. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THIS EVENT BY THE LICENSEE. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-29
39028 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-28 18:30 | 2002-06-28 21:12 | 2002-06-28 | OFFSITE NOTIFICATION OF OIL SPILL AT DC COOK DURING SWITCHYARD MAINTENANCE "At 18:30 EDT on 6/28/2002, while transporting the 1-TR-N1-CT2, Unit 1 Palisades to 345 KV Bus #1 Air Blast Breaker 52-Ni Phase #2 Current Transformer, the insulator dropped off the forklift and cracked, causing an oil leak of approximately 25 gallons onto the ground. The Michigan Department of Environmental Quality Pollution Emergency Alert System was notified at 20:15 on 6/28/02, requiring 4-Hr Non-Emergency 10 CFR 50.72 (b)(2)(xi) event notification to be made. There is no impact to plant personnel or operating equipment. A permit has been generated to allow removal of the affected soil for proper disposals" The licensee was performing maintenance in the switchyard at the time. The current transformer was the old one which was replaced. The oil spill did not directly impact the ongoing maintenance activity. The NRC resident inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  |  | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-28
39027 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-06-27 18:00 | 2002-06-28 13:43 | 2002-06-28 | LICENSED THERMAL POWER LIMIT EXCEEDED AT HOPE CREEK The following is taken from a facsimile sent by the licensee: "On May 26, 2002, an equipment failure related to the feedwater crossflow correction factor resulted in the Hope Creek Generating Station operating above its' Licensed Power Limit of 3339 megawatts thermal for a period of approximately 8 hours. Upon identification of an anomalous indication associated with the crossflow indication, operators conservatively lowered Reactor power to a value below the station's licensed limit pending evaluation of the condition. Subsequent detailed evaluation has since confirmed that a malfunction of the crossflow instrumentation correction factor caused an overpower condition. The event date and time coincide with the completion of the evaluation. Contrary to regulatory guidance for power maintenance, the facility operated at approximately 100.25% for greater than 2 hours. However, at no time did the station power level exceed 100.47%, nor was the shift average power level limit exceeded. This 24 hour report is being made for violation of the requirements contained in the Operating License (Hope Creek Operating License Number NPF-57, section 2.F, specifically Section 2.C (1)-exceeding the maximum power level of 3339 megawatts thermal.[)]" The licensee notified the NRC Resident Inspector. | 24 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2002-06-28
39026 | 0 | US ARMY |  |  |  |  | 2002-06-26 | 2002-06-28 10:20 | 2002-06-28 | LOSS OF A CHEMICAL AGENT DETECTOR IN KOREA A chemical agent detector (model M43A1) containing 300 microcuries was lost by an Army unit in Korea. Aberdeen was notified on 06/26/02 and there are no further details at this time. The unit will investigate and send in a report to Aberdeen. The detector posses little or no threat to the public. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-28
39025 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-06-28 01:52 | 2002-06-28 09:47 | 2002-06-28 | POTENTIAL LOSS OF CONTROL CENTER HVAC ACCIDENT MITIGATION CAPABILITY DURING MAINTENANCE ACTIVITIES " Control Center HVAC access panel opened at 2152 hours on 6-27-02, unfiltered air in-leakage potentially allowed into the operating division of [the] Control Center HVAC , potentially affecting post accident dose assessment per 10 CFR 50.72 (b) (3)(v)(D). " Control Center access panel closed at 2222 hours on 6-27-02, maintenance activities halted on CCHVAC. "Tech Spec 3.0.3 entry recognized at 0152 hours 6-28-02. Tech Spec exited within 30 minutes, no actions taken to commence plant shutdown." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-06-28
39024 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2002-06-27 12:10 | 2002-06-27 15:20 | 2002-06-28 | OPERABLE EP SIRENS BELOW MINIMUM NUMBER AT INDIAN POINT Two counties located in the emergency planning zone went below the minimum number of operable EP sirens. Westchester County had 12 sirens inoperable out of a total of 77 sirens. Orange County had approximately 8 sirens not working out of a total of 16. The minimum number operable criteria is 90% operating out of the total number in each county. The licensee attributed the inoperable sirens due to a storm that passed through the area yesterday. Compensatory measures were in place including route alerting. The NRC resident inspector was notified. *****UPDATE LEONE TO LAURA ON 6/28/02 AT 13:48***** The licensee reported that Westchester County had greater than 90% of their sirens working by 18:20 on 6/27/02. All EP sirens in the 4 counties within the EPZ were working as of 11:28 on 6/28/02. The NRC resident inspector was notified. Notified R1DO (M. Modes). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-06-27
39023 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-06-27 10:33 | 2002-06-27 14:02 | 2002-06-27 | TS REQUIRED SHUTDOWN INITIATED DUE TO LOSS OF CONTROL ROOM AIR CONDITIONING "At 10:21 the standby control room HVAC unit, VA-46A, was started due to rising Control Room (CR) temperatures. The running CR HVAC unit, VA-46B, was declared inoperable due to its inability to maintain CR temperature. TS 2.1.2 paragraph 2 was entered, 30 day LCO. At 10:33 it was determined that VA-46A was not cooling and it was declared inoperable. With both CR HVAC units inoperable, AOP-13-Loss Of Control room Air Conditioning, was entered and TS 2.0.1 was entered which requires 6 hours to be in Hot Shutdown. At 10:34 the electrical disconnect was reset on HVAC unit, VA-46B. Control Room temperature was verified to be lowering at 10:40, 78 degrees F. Highest temperature in Control Room was 79 degrees F. At 11:00, VA-46B was verified to be operating normally with Control Room temperature continuing to lower. VA-46B was declared operable with CR temperature 74 degrees F and lowering. TS 2.0.1 was exited with no power reduction occurring. AOP-13, Loss Of Control Room Air Conditioning Abnormal Operating Procedure was exited also. We remain in TS 2.12.2 for VA-46A (30 day LCO) with maintenance ongoing for VA-46A. Current CR temperature at 12:10 is 72 degrees F." The NRC Resident inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-06-27
39022 | 0 | MILFORD HOSPITAL |  |  |  |  | 2002-06-27 | 2002-06-27 10:00 | 2002-06-27 | HOSPITAL WASTE SET OFF TRASH DISPOSAL PORTAL ALARM The Milford Hospital was contacted by the State of Connecticut Department of Environmental Protection (DEP) that a trash truck hauling trash from the hospital set off the portal alarm on entry at the disposal site at Bridgeport, Connecticut. DEP incident report number is 02-75. The truck was returned to the hospital and the contents checked, 0.025 millirem/hour was measured at the truck. Tc-99m was found contained in patient waste, which had been properly and legally disposed of. The trash will be held for decay at the hospital before being sent back to the waste disposal site. The hospital will be contacting NRC Region 1. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | HOS | [5 empty] | 0 | 2002-06-27
39021 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-06-26 22:52 | 2002-06-27 06:45 | 2002-07-08 | BOTH CHANNELS OF OFFGAS RADIATION MONITORS DECLARED INOPERABLE Both channels of offgas radiation monitors declared inoperable due to a common mode failure. Both channels detect offgas radiation levels in the same sample volume. The sample volume filled with condensate suppressing the radiation levels. The offgas radiation monitors provide for isolation of the main condensers on indications of fuel element failure. This puts the licensee in a 72 hour clock allowing for repairs or shutdown, per Technical Specification Table 3.1.1 Instrument Operability. The licensee intends to notify the NRC Resident Inspector. * * * RETRACTED AT 1412 EDT ON 7/8/02 BY STEVE FULLER TO FANGIE JONES * * * The licensee is retracting the event notification after reviewing the event and determining that the monitors do not perform a safety function that is relied on in the safety analysis of the plant. Also, the monitors do not affect the plant or its safety barriers. The licensee intends to notify the NRC Resident Inspector. The R1DO (Brian McDermott) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2002-06-27
39020 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-06-26 10:02 | 2002-06-26 14:04 | 2002-06-26 | A SUPERVISOR PERSONNEL WAS DETERMINED TO BE UNDER THE INFLUENCE OF ALCOHOL Employees access was terminated. The NRC Resident Inspector was notified. Contact the HOO for additional information. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2002-06-26
39019 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2002-06-25 21:00 | 2002-06-26 10:20 | 2002-06-26 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following is taken from a faxed report: Event Report ID No.: TN-02-083 License No: TN-02-083 Licensee: Tennessee Division of Radiological Health Event date and time: June 25, 2002, 2100 EDT Event location: R-19017 Event type: Stolen moisture density gauge Notifications: USNRC Region II, Knox County Sheriffs Department Event description: Tennessee Department of Transportation, Region 1, called the Division at 0818 CDT to report a stolen moisture density gauge. The gauge is a Troxler model 3430, serial number 23117 containing 8 millicuries of Cesium-137, serial number 75-4928 and 40 millicuries of Am-241:Be, serial number 47-18934. The gauge was inside a white Ford Aerostar van. License number S4-PE83, owned by the State. The van was parked at the operator's home on McGinnis Road in Corryton, TN. Media attention: None at this time. A press release will be issued by TDEC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2002-07-01
39018 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-25 18:00 | 2002-06-25 21:36 | 2002-06-25 | LICENSEE DISCOVERED A SEALED AMERICIUM - 241 CALIBRATION SOURCE HAD BEEN DAMAGED The sealed source was found damaged while performing calibration of a PCM whole body monitor. The Am - 241 source was found to contain only a small fraction(>1%) of the original activity of 2.44E-2 µCi. A thin mylar type covering was missing from the source when it was discovered damaged. No loose contamination has been detected on the source or in the work area the source was used. The thin mylar type covering was apparently removed sometime between 4/10/02 (last time source was used) and 6/25/02. At this time it is not known how the source was damaged. No theft is suspected at this time and they are still investigating. The NRC Resident Inspector was notified. State and local agencies will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-06-25
39017 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2002-06-25 08:00 | 2002-06-25 15:22 | 2002-06-25 | EMERGENCY NOTIFICATION SIRENS INOPERABLE Peach Bottom Units 2&3 were notified by the Emergency Preparedness Group that all of the emergency notification sirens for Peach Bottoms EP Zone were inoperable between the hours of 08:00 and approximately 10:30 hours this morning (6/25/02). The problem appears to be due to a "stray" radio signal at the base station which controls the transmit signal to the sirens. While that stray radio signal was present, the base station could have been prevented from sending a signal to activate the sirens. Investigation and recovery efforts are underway for the siren system and at this time 96 of 97 sirens have been restored. The last siren is expected to be returned to an operable status this evening by 18:00 hours. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-06-25
39016 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-06-24 21:00 | 2002-06-25 00:33 | 2002-06-25 | 4-HOUR 91-01 NRC BULLETIN REPORT INVOLVING LOSS OF DOUBLE CONTINGENCY PROTECTION "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (</= 5.0 wt. % U-235) PWR fuel fabricator for commercial light water reactors "License: SNM-1107 "Time and Date of Event: Approximately 21:00 hours, Monday, June 24, 2002. "Reason for Notification: Moisture detected in dry ventilation system in Uranium Recycle and Recovery area. "Summary of Process: This ventilation system draws on several processing hoods in the Uranium Recycle and Recovery area. One set of hoods process dry uranium bearing materials for dissolution and the other set of hoods typically process low uranium bearing materials for oxidation. "As Found Condition: A summary of the as found conditions is as follows: -Damp material was found in ventilation ductwork, filters, and filter housing. -The ventilation system and associated processes were immediately shutdown and the Nuclear Criticality Safety (NCS) function was notified. "Double Contingency Protection: Double contingency protection for the ventilation ductwork, filters, and filter housing is based on moderation control. Criticality in the ductwork and filters was determined to be 'not credible' based upon a bounding assumption of less than 10 weight percent water. Criticality safety limits for the filter housing were based upon the same bounding assumption. After assessing the ductwork, filters, and filter housing, it was determined that this was an unanticipated event and therefore the incident requires 4-hour notification in accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (b.4). "Summary of Activity: -Nuclear Criticality Safety (NCS) participated with engineering and operations to determine the source of moisture. This investigation is continuing. -The ventilation ductwork was inspected near the suspected moisture source. -The filters were removed, weighed, and inspected. -Samples from the ductwork, filters, and filter housing were obtained for analysis. -The ventilation and associated processes are shutdown and in a safe condition. "Conclusions: -There was a loss of double contingency protection. -At no time was greater than a safe limit of moderator involved in the filters. -At no time was there a nonfavorable geometry in the ductwork or filter housing. -At no time was criticality possible. -At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. -The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed." The process will remain shutdown until the investigation is completed and the appropriate corrective actions are identified. It is not known at this time whether this shutdown will impact the overall production schedule. The licensee will inform the RII Fuel Facility Inspectors and brief the Headquarters NMSS Representative (Schwink) who is scheduled to visit the facility tomorrow. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-06-25
39015 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-06-24 12:45 | 2002-06-24 14:35 | 2002-06-26 | MINIMUM SECURITY PERSONNEL STAFFING REQUIREMENTS NOT MET Compensatory measures taken upon discovery. The NRC Resident Inspector will be informed. Refer to the HOO for additional details. * * * UPDATE ON 6/26/02 BY ROWLAND TO GOULD * * * RETRACTION The licensee is retracting this event and classifying it as a loggable event and not a reportable one. The NRC resident inspector was notified. Reg 3 RDO(Stone) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-06-24
39014 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-06-24 10:35 | 2002-06-24 12:42 | 2007-07-26 | AGREEMENT STATE REPORT - SOURCE LOST IN SHIPMENT AEA Technology QSA, Inc. (AEA) called to notify the State of the report to their office of the receipt of a package of very low activity Pu-242/Am-243 (12 Bq each) by Knolls Atomic Power Laboratory. AEA was notified by Knolls Atomic that the package, received by them on 12/6/01 or 12/7/01, was opened on or around 5/20/02, at which time the inner container appeared to have been opened, and all contents were absent. The State Agency was informed by the licensee they received the shipment from England on 12/5/01, checked the outer cardboard container for damage, and resent the shipment to their customer, Knolls Atomic Power Laboratory in New York. The package was received 12/6/01 or 12/7/01. At Knolls, the radiation safety staff received the shipment and confirmed the outer package was undamaged and delivered it to the end user in the Chemistry Department. The user opened the package on or around 5/20/02. Knolls Atomic informed AEA they believe the seal on the inner plastic container was intact, but that the final container, a flame-sealed glass container, appeared to have been opened and the contents removed, in addition, AEA was informed that the Federal Bureau of Investigation (FBI) was notified. * * * UPDATE FROM GALLAGHAR TO KNOKE AT 0952 ON 07/26/07 * * * The State provided the following information via email: "The following information is provided to close NMED Item Number 020624: "Material was shipped to the Knolls Atomic Power Laboratory (KAPL) and received there on or around 12/6 or 12/7/2001 and not opened until Mid-May of 2002. Investigation by AEA Technology QSA, Inc. (AEA) and KAPL revealed that the shipment arrived at the laboratory intact with no apparent damage; when later opened it appeared that the materials had been used. "Based upon the condition of the shipping containers when they arrived at KAPL it appears likely that the vials were used at the customer location, apparently without their knowledge." Notified R1DO (Finney) and NMSS (Flannery) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-06-27
39013 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2002-06-24 07:30 | 2002-06-24 09:14 | 2002-06-24 | OFFSITE NOTIFICATION DUE TO SMALL OIL SPILL ONSITE The control room was notified at 0730EDT that a 40T small crane had developed a hydraulic leak. Approximately one (1) pint of oil was released to the storm drain system which was subsequently collected. The licensee notified the State Nuclear Inspector, the NRC Decommissioning Office, the Maine Department of Environmental Protection and the National Response Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-24
39012 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2002-06-22 22:17 | 2002-06-23 02:38 | 2002-06-23 | AUTOMATIC REACTOR SCRAM FOLLOWING SERVICE TRANSFORMER LOCKOUT FOR REASONS UNKNOWN "At 2217 CDT on 6/22/02, GGNS scrammed from 100% CTP. The scram was the results of a lockout trip on service transformer 21 (ST21). Exact cause of [the] scram has not been determined yet.. [The] Plant is stable and all parameters are being controlled. [The] scram is suspected to be due to loss of feedwater (i.e., Rx Low Level) when ST21 tripped. Div 2 and 3 buses did deenergize and [their] respective Diesel Generators started and carried [the] buses." All control rods fully inserted. RWCU is currently in-service removing decay heat. ST21 remains out-of-service. Electrical loads have been shifted to ST11 (500KV feed) and the ESF transformer (115KV feed). The unit is not in any TS A/S for offsite power since 2 of the 3 sources are available. The licensee notified the NRC Resident Inspector. * * * UPDATE 0404 EDT ON 6/23/02 FROM ROBERT BRINKMAN TO S. SANDIN * * * "This is an update to Event Notification #39012. This call in is to report the 8 hr non-emergency call in under 10CFR50.72(b)(3)(iv)(A). As reported earlier, Division 2 and 3 electrical buses deenergized when service transformer 21 tripped. Division 2 and 3 Diesel Generators started and energized these buses. The actuation of Division 2 and 3 Diesel Generators is the 'Specified System Actuation' reported by this notification. Also, Div. 2 Control Room A/C failed to automatically restart following Div. 2 bus being re-energized. [The] breaker was closed manually and Control Room A/C (Div. 2) restarted." The licensee informed the NRC Resident Inspector. Notified R4DO(Marschall). * * * UPDATE 0555 EDT ON 6/23/02 FROM ROBERT BRINKMAN TO S. SANDIN * * * "This notification is to report an 8 hr non-emergency call in under 10CFR50.72(b)(3)(xiii). At 0425 CDT, on 6/23/02, the GGNS Control Room was notified that the EOF had no electrical power. The site power loop was deenergized when service transformer 21 tripped, which caused the EOF to become de-energized (see EN #39012). The EOF backup generator did not start as required, therefore the EOF (Emergency Operations Facility) did not have any electrical power. Normal electrical power was restored to [the] EOF at 0415 hrs CDT on 6/23/02. [The] backup EOF was available at all times." The licensee informed the NRC Resident Inspector. Notified R4DO(Marschall). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  | 0 | 2002-06-23
39011 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-06-21 01:00 | 2002-06-22 17:02 | 2002-07-24 | SHIFT SECURITY STAFFING BELOW SECURITY PLAN LEVEL A security guard failed a random drug test and was immediately removed from duties. This placed the site below the minimum security level for approximately 1 hour. (Contact the HOO for more details.) ***** RETRACTION RECEIVED AT 1805 EDT ON 07/24/02 FROM JAY GERONDALE TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "On 06/22/02, PBNP provided a courtesy notification regarding a situation where for a brief period of time security shift staffing fell below the minimum staffing levels specified in the PBNP security plan. The purpose of this notification was for information only and not because the licensee had determined the event to be reportable in accordance with either 10 CFR 73.71 or 10 CFR 26.73. Further, the situation did not result in violation of security plan requirements since the security plan provides an allowable period of time for call in of replacement personnel when unanticipated absences occur. Replacement personnel were called in and reported for duty well within the period of time specified in the security plan." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Chris Miller). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW | [5 empty] | 0 | 2002-06-22
39010 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-06-22 14:16 | 2002-06-22 18:27 | 2002-06-26 | AUTOMATIC SCRAM AT HOPE CREEK DUE TO TURBINE TRIP "Immediately following the RPS actuation, the success of the SCRAM was evaluated. Initially, the Rod Worth Minimizer indicated that some control rods were not fully inserted and control rod 22-31 indicated full out on the Full Core Display. Alternate Rod Insertion (ARI) was initiated as per established operating procedures. The STA observed all Control Rods except 22-31 to be fully inserted on the Core Monitoring System before ARI was initiated, indicating the reactor was shutdown without ARI. The indicated position of CR 22-31 did not change immediately following the SCRAM, but changed over time consistent with a known problem with its position-indicating probe. "Both Reactor Recirculation Pumps tripped as expected from the turbine trip above 30% power (End-of-Cycle Recirculation Pump Trip function), and remain out of service. The Reactor is presently shutdown. Reactor pressure is 700 psig and slowly lowering and reactor level is 32 and stable (normal band 30-39). Efforts are underway to stabilize and normalize reactor coolant and metal temperatures to allow the restarting of a Reactor Recirculation Pump." The NRC resident inspector was notified by the licensee. * * * UPDATE ON 6/26/02 @ 1530 BY REG 1 TO GOULD * * * This update is to clarify the above event report by including the first paragraph which was originally inadvertently omitted from the NRC write-up. The paragraph is included below. "This 4 hour report s being made pursuant to 10CFR50.72(b)(2)(iv)(B) for actuation of the Hope Creek Reactor Protection System (RPS) with the plant critical. At 14:16 hours the Hope Creek Reactor RPS actuated, resulting in a Reactor SCRAM. Preliminarily the RPS actuation appears to have been caused by a Main Turbine trip from high moisture separator level that was caused by a trip of the B Secondary Condensate Pump and automatic intermediate runback of the Reactor Recirculation Pumps. Follow-up investigation will be performed to validate this information." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-06-22
39009 | 0 | BUREAU OF INDIAN AFFAIRS |  |  |  |  | 2002-06-21 09:00 | 2002-06-22 13:00 | 2002-09-27 | STOLEN TROXLER MOISTURE DENSITY GAUGE On 9:00 a.m. CDT on 6/22/02, the licensee discovered that their storage shed had been broken into and a Troxler moisture density gauge was stolen. The model number is 3440, which contains 8 millicuries of CS-137 and 40 millicuries of Am-Be 241, and serial numbers 18746 and 18745. The licensee contacted the local police, Fairfax City Police and Osage County Sheriffs office. The storage shed is located 2 miles east of Highway 20 and Highway 18 in Osage County, Oklahoma. * * * UPDATE ON 9/27/02 @ 1528 BY FAVORS TO GOULD * * * The licensee has recovered the Troxler gauge. It was returned to them undamaged with the source lock intact by the Fairfax, Ok. Police Dept. on 9/25/02. HOO notified MNSS EO(Brown) and REG 4 RDO(Pellet) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | OK | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-22
39008 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-21 13:12 | 2002-06-21 13:30 | 2002-06-21 | VOLUNTARY INFORMATION REPORT ON PLANNED SPDS OUTAGE AT SALEM "The safety parameter display system (SPDS) is being removed from service to perform planned upgrades to the system. The removal of SPDS from service for Salem Units 1 & 2 also affects the transmission of data from the emergency response data system (ERDS). Appropriate compensatory measures are in place while the SPDS system is out of service. SPDS is expected to return to service by end of August. This is considered a condition warranting voluntary/courtesy NRC notification" The NRC resident inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2002-06-21
39007 | 0 | IDAHO NAT ENGR & ENVIRONMENTAL LAB |  |  |  |  | 2002-06-20 15:08 | 2002-06-20 18:18 | 2002-06-20 | DOE DECLARED ALERT AT INDEPENDENT SPENT FUEL STORAGE INSTALLATION (ISFSI) IN IDAHO DOE INEEL declared an ALERT at 15:08 MDT due to wild land fires on DOE controlled property. The ISFSI containing the TMI spent fuel was not directly threatened. The fire was approximately 5 to 10 miles from the ISFSI. Fire fighting efforts were underway to extinguish the fire. Wind speeds varied from 10 to 15 miles per hour. DOE INEEL notified the State of Idaho, all surrounding counties and DOE Headquarters. The NRC entered the Monitoring mode at 18:57 EST. *****UPDATE 20:00 EST ON 6/20/02 FROM GARCIA TO LAURA***** The fire is contained and the licensee exited the ALERT declaration at 18:20MDT. The NRC exited the Monitoring mode at 20:04 EST. Notified R4 (E. Merschoff), DIRO (J. Holonich), NMSS (W. Brach, J. Greeves), FEMA (G. Belcher), DOE (J. Stambaugh), DOT-NRC (A. Brown), and sent fax of the event to HHS, EPA and USDA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | ID | MAT | [5 empty] | 0 | 2002-06-20
39006 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-06-20 | 2002-06-20 15:52 | 2002-06-21 | AGREEMENT STATE REPORT OF INJURED AND POTENTIALLY CONTAMINATED WORKER "A group of workers were returning to their work location in the back of a pickup truck. The crew was dressed out in normal exclusion PPE which includes anti-C coveralls, tyvek inner booties, yellow latex outer booties, latex and cloth gloves along with hard hat, safety glasses, and steel toe shoes. They were returning to the Pond 3 excavation which was removing moderate activity (50-100 pCi/g) material from a former waste water treatment pond. Prior to the crew's return, a water truck had passed by for dust control. Surfaces were wet, muddy, and slippery. "The pickup stopped, and while climbing out of the back of the pickup truck, the injured person (articulated quarry truck driver) slipped and fell to the ground. [...] The rest of the crew rendered assistance and made him comfortable but it was rapidly determined that the extent of the injury would require a trip to the emergency room and an ambulance (West Chicago Fire Department) was called. "[... A] decision was made to bring the ambulance directly into the exclusion zone rather than try and transport him to the control point. Paramedics were provided with booties and gloves and their contact with potentially contaminated surfaces was monitored by licensee HP technicians. The paramedics set their stretcher down in the mud and moved him to it. They exposed his [injury] by cutting his coveralls and his personal clothing underneath (jeans). They loaded the stretcher into the ambulance and transported him to Central Dupage Hospital in Winfield, IL. A licensee HP technician rode in the ambulance to the hospital. " Prior to leaving the site, the ambulance tires were frisked for contamination and none was found. Had contamination been found, a clean water truck was standing by to rapidly decontaminate the tires. This turned out not to be necessary. "Two additional licensee HP technicians and the IDNS resident inspector followed the ambulance to the hospital. The IDNS inspector called ahead to the hospital to make sure the hospital staff knew they were receiving a potentially contaminated patient. They asked questions and were advised to used their closest treatment room to the ambulance entrance and to put absorbent paper on the floor. They asked about PPE and were told that normal gown and glove requirements were sufficient. They also indicated that they had a specific room to deal with contaminated patients and it was the closest room to the entrance, in fact it had a separate entrance into the ambulance entrance bay. "The ambulance arrived at the facility and the ambulance crew failed to use the separate entrance and brought the patient up the main entrance carpeted ramp. Due to the potential for contamination, the hospital closed down their ambulance entrance per their own procedures. "In the treatment room, the individual was cut out of the rest of his contaminated (muddy) PPE and transferred to a new gurney covered with absorbent material and given an initial exam by a physician. His body was frisked and he was then transferred to a third clean gurney and taken to a regular emergency room treatment area for further evaluation and tests. "The ambulance gurney/stretcher was decontaminated (visible mud removed) along with the ambulance floor and a second frisk of the tires. HP technicians also surveyed the room and ramp to return both to service. Licensee has detailed survey results and smear counts. All confirmatory surveys and smear counts were at or below background levels. No measurements were taken on the bag of suspect contaminated material. "The individual's PPE, along with PPE used by hospital and paramedics was collected, bagged, and returned to the licensee as radioactive waste, as was bedding and absorbent material used both in the ambulance and in the decon room." ***** UPDATE FROM TOM SEIF TO LEIGH TROCINE VIA EMAIL AT 0854 ON 06/21/02 ***** The following text is a portion of an email received from the Illinois Department of Nuclear Safety: "An email detailing this event was forwarded to the Operations Center yesterday. Personal medical details of the individual involved were inadvertently included. Please ensure that this information is not released in any public record." This event was updated to remove the personal medical details of the individual involved. (Call the NRC operations officer for a state contact telephone number and for additional details.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-06-25
39005 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2002-06-20 09:45 | 2002-06-20 11:03 | 2002-06-20 | FIRE IN FILTER BANK The licensee declared an alert at 0945 CDT due to a flaming fire in their charcoal filter bank which began at 0934 CDT. The licensee shut a ventilation damper to minimize any potential effluent release. Site personnel are currently fighting the fire and off-site fire department has been called and are on the way to the site. The NRC entered the Monitoring Phase of Normal Mode at 1129 at EDT. Notified the Chairman's Office (Rathburn), DOT-NRC (Johnson), DOE (R. Dasualua), HHS (S. Hanson), and USDA (K. Barret). * * * UPDATE ON 6/20/02 AT 1235 BY HAYES TO GOULD * * * The smoldering fire was extinguished at 1105 CST by removing filters and placing them in 55 gallon barrels. The alert was terminated at 1135 CST. A Commissioners Assistant briefing was conducted at 1300 EDT. Participants included: DIRO (R. Wessman), OPA (R. Virgilio), OSATP (C. Maupin), NMSS (R. Pierson, E. Leeds), IP (J. Ramsey), EDO (B. Smith), DEDMRS (C. Paperiello), SECY (K. Hart), Chairman Meserve (K. McConnell), Comm. Dicus (J. Olencz), Comm. McGaffigan (H. Astwood), Comm. Diaz (R. Davis), and Comm. Merrifield (J. Thoma). The NRC exited the Monitoring mode at 1332 EDT. Notified FEMA (B. Carr), OHS, DOT-NRC (Johnson), DOE (R. Dasilua), HHS (S. Hanson), USDA (K. Barret) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 3 | MO | FUE |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-06-20
39004 | 0 | US ARMY |  |  |  |  | 2002-06-14 03:55 | 2002-06-20 08:53 | 2002-06-20 | LOSS OF A CHEMICAL AGENT DETECTOR DURING A FIELD TRAINING EXERCISE IN WIESBADEN, GERMANY A chemical agent detector (model M43A1) was lost by an Army unit during a field training exercise in Wiesbaden, Germany. It was discovered to be missing at approximately 0200 on 06/07/02. The missing chemical agent detector contained 300 microcuries of americium-241. Aberdeen was notified of this incident via email at 0355 on 06/14/02. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-20
39003 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-06-19 14:30 | 2002-06-19 16:30 | 2002-06-19 | POTENTIAL FOR HOT-SHORT CAUSING THE RWST TO DRAIN "On 6/7/02, Wolf Creek Nuclear Operation Corporation notified Callaway Plant of a potential hot short issue involving the possibility to drain the Refueling Water Storage Tank to the containment recirculation sump during a fire. Initial evaluations indicate a potential for this issue to be applicable to Callaway Plant. "The issue discovered was that control cables for 2 redundant motor operated valves are routed in the same electrical raceway. The 2 valves are on the same electrical separation group, but are redundant in their function of conserving water inventory in the RWST. Further investigation determined that the other electrical separation group has the same configuration. The licensee has implemented an hourly fire watch as a compensatory action. Engineering analyses are being conducted to determine if further modifications are necessary. Appropriate changes or compensations will be instituted into the corrective action system as identified." The licensee informed the NRC Resident Inspection. Related Event #38970 at Wolf Creek | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2002-06-19
39002 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-06-18 | 2002-06-18 15:58 | 2002-06-18 | AGREEMENT STATE REPORT - LOST RADIOACTIVE MATERIAL SHIPMENT The Massachusetts Radiation Control Program was contacted by the Joslin Diabetes Center about a missing shipment of 500 microcuries of P32. The shipment was shipped from Perkin-Elmer on 6/10/02 and received on 6/11/02 at the center. The package was discovered missing on 6/14/02 and notification to the state was on 6/18/02. The center has been searched and further searches are ongoing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-06-21
39001 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-06-18 08:42 | 2002-06-18 11:10 | 2002-06-18 | OFFSITE NOTIFICATION TO LOCAL AUTHORITIES DUE TO DISCOVERY OF SUICIDE VICTIM FOUND ON UTILITY PROPERTY OUTSIDE THE OWNER CONTROLLED AREA "On 06/18/02 at 0842 Oconee Nuclear Station security discovered an apparent suicide victim parked on Duke Energy property outside the owner controlled area. The control room was notified and dispatched a Medical Emergency Response Team, which was unable to revive the victim. The individual was determined not to be a Duke Energy employee. Pickens County (South Carolina) authorities were notified and have responded to the scene. Pending the result of the coroner's investigation, cause of death is apparently self-induced carbon monoxide poisoning. A suicide note was found at the scene." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-18
39000 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2002-06-17 18:55 | 2002-06-17 22:43 | 2002-06-17 | REACTOR TRIP ON LOW-LOW STEAM GENERATOR LEVEL The plant was operating at 100% when the 'C' main feedwater pump tripped for an unknown reason, trouble shooting continues. The turbine load was being reduced to a power level the remaining feedwater pumps could sustain. The level in steam generator 'A' dropped to the low-low level trip setpoint before the load reduction could be completed. The reactor trip occurred at 1902 EDT. All systems functioned as expected except for the nuclear instrument intermediate range N35 which was very erratic with fluctuations of 6 decades. The emergency feedwater system motor and turbine driven pumps started as expected on low-low steam generator level (ESF signal) and continue to provide feedwater flow to the steam generators. Excess heat is being removed via the steam dumps to the main condenser. The plant is stable in Mode 3. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-06-17
38999 | 0 | MIDWEST ENGINEERING |  |  |  |  | 2002-06-17 16:30 | 2002-06-17 17:43 | 2002-06-17 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM WORKER'S TRUCK A Troxler moisture density gauge (model 3430) containing 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be was stolen from a worker's truck parked at his home located in Griffith, IN. The gauge was last seen on 6/16/02 in the evening when it was locked up in the back of the worker's truck. It was discover missing 6/17/02 at about 1630 CDT. Griffith police department will be notified, the first call was to the NRC Operations Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-17
38998 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-06-17 13:00 | 2002-06-17 16:54 | 2002-06-17 | PROMPT ALERT SYSTEM INOPERABLE The licensee determined that the "Prompt Alert Notification System" was inoperable, believed to be caused by a failed siren. Troubleshooting is ongoing and repairs are expected to be completed today. Alternate means of notification have been put in place. The licensee intends to notify the NRC Resident Inspector and has notified the Local and State Agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-06-17
38997 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-06-17 15:00 | 2002-06-17 15:43 | 2002-06-17 | 17 SIRENS FAILED WEEKLY SILENT TEST The licensee was conducting the weekly silent test for the offsite notification sirens. 17 of them failed the test in Calvert County. Technicians are troubleshooting the system and believe they will have them operational by tonight. Alternate means of notification have been put in place. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-06-17
38996 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2002-06-17 10:48 | 2002-06-17 14:16 | 2002-06-17 | AUTOSTART OF THE "A" EDG DUE TO THE LOSS OF THE OFFSITE POWER TRANSFORMER DURING INCLEMENT WEATHER "On June 17, 2002 at 1048, the 'A' Emergency Diesel generator automatically actuated and powered the 'A' 4160V Engineered Safeguards bus. This event is Reportable as an 8-Hour Notification per 10 CFR 50.72 (b) (3) (iv) (B) (8). The actuation occurred due to the loss of the Off Site Power Transformer. The cause of the transformer loss has not been identified but is suspected to be related to inclement weather." The Off Site Power Transformer has been tagged out for inspection although there is no apparent damage. Operations is evaluating placing the Backup ES Transformer (BEST) in service. The 'A' 4160V ES bus remains energized with the 'A EDG in service at this time. Unit 3 is currently in a 72-hour LCO A/S 3.8.1 Condition A. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-06-17
38995 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-06-15 08:30 | 2002-06-15 14:54 | 2002-06-15 | FITNESS-FOR-DUTY QUESTIONED DUE TO FAILURE OF ALCOHOL TEST COMPENSATORY MEASURES TAKEN THE RESIDENT INSPECTOR WAS NOTIFIED Refer to HOO for additional details | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2002-06-17
38994 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-06-13 14:30 | 2002-06-14 17:28 | 2002-06-14 | STATE LICENSEE REPORTED THAT THREE OF TEN I-125 SEEDS WERE LOST IN THE SEWER DRAIN At 2:30pm on June 13, 2002 the radiation safety officer (RSO) for City of Hope National Medical Center reported that during the course of an iodine-125 prostate permanent implant procedure, three of the ten seeds were lost down the autoclave sink located in the operating room. The initial report from the preliminary investigation was that the operating room technician wanted to wash off the three seeds prior to autoclaving them. They were not going to be used in the procedure. During this process they ended up being washed down the drain of the autoclave sink. Although this occurred at approximately 5:00pm on June 12, 2002, the RSO was not notified until approximately noon on June 13, 2002. They requested the RSO investigate the reason(s) for the delay in reporting the incident. The activity of the iodine -125 seeds was 0.344 mCi each (for a total of 1.032 mCi) at 5:00pm on June 12, 2002. At noon on June 13, 2002 the activity was 0.340 mCi (for a total of 1.02 mCi). On June 14, 2002 a request was made to remove the sink trap and piping in an effort to locate the seeds. At approximately 10:00am it was reported that the seeds were not located, even with the use of a NaI probe and visual examination. This information was forwarded to ICE Supervisor for reporting to the NRC. Investigation # 061402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-06-19
38993 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-06-14 14:43 | 2002-06-14 17:14 | 2002-06-14 | REACTOR MANUALLY TRIPPED FROM 88% POWER DUE TO LOSS OF THE EAST MAIN FEED PUMP ON LOW CONDENSER VACUUM At 1443 the unit one reactor was manually tripped from 88% reactor power due to the loss of the East Main Feedwater pump on low condenser vacuum. Loss of East Main Feedwater Pump Condenser Vacuum occurred during the start of #13 Main Circulating Water Pump. It is believed that this was caused by high differential pressure across the feed pump condenser and it appeared that the circulating water pump transferred some debris from the forebay into the condenser resulting in the loss of condenser vacuum, but this incident is still under investigation. All rods fully inserted, no ECCS injection and no safety relief valves lifted. Plant is currently stable in Mode 3. All plant equipment functioned as designed. Event Investigation is currently in progress. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-06-14
38992 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-06-13 11:30 | 2002-06-14 11:24 | 2002-07-08 | 24 HOUR REPORT ON LICENSE CONDITION 2F " At 1130 hours on 6/13/02 it was discovered that the Safety Relief Valve (SRV) Position Indication Channel for one of the SRVs controlled from the Remote Shutdown Panel was inoperable. The inoperability was due to both alarm card inhibit switches for associated acoustic monitoring channel being found to be in the inhibit position. These switches are normally in the "alarm" position. With the switches in the "inhibit" position the SRV position indication from a high vibration condition would not provide an open position indication for the SRV in the Control Room or at the Remote Shutdown Panel. Immediate Action was to return the switches to the alarm position and all other SRV acoustic monitoring switches were verified to be in the correct "alarm" position. "Technical Specification LCO 3.3.3.2 requires that the Remote Shutdown System Functions shall be OPERABLE. With this channel inoperable, Required Actions require restoration to OPERABLE status within 30 days OR placing the Unit in Mode 3 within the following 12 hours. Since the potential exists that this condition has existed in excess of the 30-day requirement this event may be considered a Condition Prohibited by Technical Specifications. "This report is being made in accordance with Section 2F of Operating License NPF-69 for Nine-Mile Point Unit 2. Section 2F requires that the initial notification of a violation of any requirement contained in Section 2C to the Operating License (License Conditions) be reported to the NRC Operations Center via the Emergency Notification System within 24 hours with written follow-up with 30 days. License Condition 2C requires that Nine Mile Point Nuclear Station, LLC shall operate the facility in accordance with the Technical Specifications." The NRC Resident Inspector has been notified. ****Retraction on 07/08/02 at 1634 ET by Mr. Cigler taken by MacKinnon **** "A subsequent investigation concluded that there is no firm evidence that the switches were in the wrong position in excess of 30 days. Based on the guidance of NUREG 1022, Rev 2, section 3.2.2, the previous report made is being retracted." R1DO (Brian McDermott) The NRC Resident Inspector was notified of this retraction by the licensee. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2002-06-14
38991 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-14 04:35 | 2002-06-14 07:14 | 2002-06-14 | MANUAL REACTOR TRIP FOLLOWING CLOSURE OF A FEEDWATER ISOLATION VALVE DURING SURVEILLANCE TESTING The following text is a portion of a facsimile received from the licensee: "At 04:35 [CDT] on 06/14/2002, operators manually tripped the reactor following closure of feedwater isolation valve 2C during surveillance testing. The cause of the feedwater isolation valve failure is unknown at this time. Also, both source range nuclear instruments failed to energize following the reactor trip, but both extended range nuclear instruments are available. The auxiliary feedwater system actuated as expected on steam generator low-low level." "Did the rods fully insert? yes Did steam bypass to the condenser or to atmosphere? condenser Did any primary/secondary relief valves lift? no Any electrical bus transfer problems? no State normal operating temperature and pressure (NOT/NOP)[:] 590 degrees 2235 psig Any significant TS LCOs entered? no" The licensee stated that there was nothing unusual or misunderstood with the exception of the cause of the feedwater isolation valve failure and the cause of the failure of both source range nuclear instruments to energize following the reactor trip. All systems functioned as required with the same exceptions. The licensee also stated that the unit is currently stable in Mode 3 (Hot Standby). Normal charging and letdown, pressurizer heaters and sprays, and the reactor coolant pumps are currently being utilized for primary system level, pressure, and transport control. Secondary steam is being dumped to the condenser, and auxiliary feedwater is supplying water to the steam generators. Operators are in the process of transferring from auxiliary feedwater to main feedwater. All engineered safety feature equipment and emergency core cooling systems are operable and available if needed. The licensee notified the NRC resident inspector. * * * UPDATE ON 6/14/02 @ 2243 BY REDDIX TO GOULD * * * Licensee reported that after further investigation it was determined that both source range instruments did energize as expected, however, after indicating some counts erratically, they decayed away to zero. Both source range detectors are inoperable at this time. The NRC Resident Inspector was notified. Notified Reg 4 RDO(Gody) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-06-14
38990 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-13 12:00 | 2002-06-13 16:50 | 2002-06-13 | LICENSEE NOTED THAT A 4160 VOLT BUS MAY NOT HAVE BEEN ADEQUATELY PROTECTED FROM A POTENTIAL MODERATE ENERGY SPRAY INTERACTION During a plant walk down as a corrective action for a previous issue, it was noted that 4160 volt vital bus 2ETA may not have been adequately protected from a potential moderate energy spray interaction. It was noted that a section of fire protection system piping was identified as a potential source for moderate energy spray onto 2ETA. Engineering performed a review of both the spray distances assumed in the moderate energy spray criteria and the requirement to postulate moderate energy cracks in piping at every weld location. The fire protection system in question is low pressure, low temperature. This review concluded that a moderate energy pipe rupture (crack) in the fire protection system piping could lead to a loss of the vital 4160 volt bus 2ETA. A concurrent single failure of the opposite train vital 4160 volt bus (2ETB) could prevent the fulfillment of safety function of systems or structures. UFSAR section 3.6 describes the requirements for protection against dynamic effects associated with the postulated rupture of piping. Specifically the general design requirements for postulated piping breaks other than reactor coolant system requires that the design be of a nature that to mitigate the consequences of the break so that the reactor can be shutdown safely and eventually maintained in a cold shutdown condition. Maintenance has placed a spray deflector on the affected area of piping to preclude postulated spray interaction with 2ETA. Engineering has reviewed the other safety related 4160 volt bus on Unit 2 and both safety related 4160 volt buses on Unit 1 and determined that they do not have any spray interaction issues. The root cause of this issue is still under investigation. The NRC Resident Inspector, States and local agencies will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-06-13
38989 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-06-13 12:30 | 2002-06-13 14:30 | 2002-06-13 | LOSS OF EMERGENCY NOTIFICATION NETWORK (ENN) TO STATES OF ALABAMA AND GEORGIA "The ENN (Emergency Communications Equipment) [was] declared inoperable at 1230 central on 13 June 2002 due to [the] inability to communicate with the states of Alabama and Georgia. Action has been initiated to correct [the] problem. All other communication equipment is available including the designated backup capability provided by the Southern Link Radio System." The licensee will inform the states of Alabama and Georgia and the NRC Resident Inspector. * * * UPDATE ON 6/13/2002 @ 1723 BY HOBSON TO GOULD * * * At 1414 CDT they restored capability to contact one state agency in both Alabama and Georgia. The NRC Resident Inspector will be informed | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-06-13
38988 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-06-13 11:20 | 2002-06-13 13:02 | 2002-06-13 | OFFSITE NOTIFICATION MADE TO LOCAL FIRE DEPARTMENT FOR ASSISTANCE A fire in the owner controlled area 1/2 mile outside the protected area occurred at their training facility and a call for offsite assistance was made. The fire turned out to be a lot of black smoke coming from a burned out fan motor in the training facilities ventilation system. Everything was under control within a half hour and the licensee logged out of their procedures at 1237. The NRC Resident Inspector was notified along with state and local agencies. A press release may be made. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-13
38987 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-06-12 23:41 | 2002-06-13 00:57 | 2002-06-13 | OFFSITE NOTIFICATION REGARDING A RELEASE OF RAW SEWAGE TO THE CHESAPEAKE BAY The licensee reported that an air leak caused a level detector in a large inlet pumping well to fail low. As a result, the sump pumps stopped and did not restart when actual level reached the high level setpoint. The inlet sump of the onsite sewage treatment plant subsequently overflowed, and raw sewage was released to the Chesapeake Bay. The licensee estimates that the quantity of raw sewage involved was between 2,500 and 7,200 gallons. Additional calculations are currently being performed. The level detector malfunctioned has since been repaired. The licensee notified the NRC resident inspector and local county and plans to notify the Maryland Department of Environmental Protection. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-13
38986 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-06-12 06:30 | 2002-06-12 21:53 | 2002-06-12 | 24 HOUR BULLETIN 91-01 REPORT AT PADUCAH "At 0820 CDT, on 6-12-02 the Plant Shift Superintendent was notified of an NCS violation that had occurred in the C-335 process building. The calibrated AQ-NCS pressure chart recorders for C and E surge drum banks had previously failed. As a result of this failure the shiftly pressure checks were performed using non AQ-NCS pressure instrumentation and therefore were not valid. The purpose of the pressure check is to identify if wet air inleakage has begun on surge drum bank. An alternate AQ-NCS pressure instrument has now been connected to the system and follow-up pressure readings have been taken. The pressure readings indicate there has been no wet air inleakage. The required checks have been restarted. Double contingency has been restored. "This is an event is which a violation of the double contingency principle occurred and where double contingency was re-established within four hours of the initial observation of the event. The NRC Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: Although pressure readings were taken on a shiftly basis, these readings were not valid because the instrumentation used was not AQ-NCS. Therefore double contingency was not maintained. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for a criticality to be possible a surge drum would have to contain a critical mass of UO2F2 in an unfavorable geometry, wet air inleakage would need to occur, and the uranium mass would have to be sufficiently moderated. "CONTROLLED PARAMETERS: Double contingency is maintained by implementing two controls on moderation. "NUCLEAR CRITICALITY Y SAFETY CONTROL(S): The first leg of double contingency is based on maintaining the integrity of the surge drum system against wet air inleakage. This integrity is assured by an SRI for the unlikely breach of the surge drum system. Structural integrity of the drum is intact, therefore this SRI is maintained. The second leg of double contingency is based on the performance of the shiftly pressure checks of an AQ-NCS instrument as an indication of wet air inleakage. The required checks were performed using an uncalibrated instrument. Since an uncalibrated instrument was used, the shiftly checks were invalid resulting in a loss of this control. Since there are two controls on one parameter, double contingency was not maintained. "CORRECTIVE ACTIONS: 1) Isolate the affected surge drum banks until the original pressure indication equipment is repaired. The drums were isolated at 1025 CDT on 6-12-02. 2) Connect AQ-NCS pressure indication equipment and monitor in accordance with procedure CP4-CO-CN6069 until the original pressure indication equipment is repaired. An alternate AQ-NCS approved instrument was connected, and readings were taken at 1040 CDT on 6-12-02." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-06-12
38985 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-06-12 12:00 | 2002-06-12 17:30 | 2002-06-12 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "A technician was transporting a gauge that was chained, locked, and secured on the back of a pickup truck. He stopped at a restaurant for a take out lunch. Upon returning to the truck, he noticed the gauge was missing. The chain was cut. Some other items, including test equipment and a sand cone, were taken. Gauge: Troxler Model 3430, ser#26992 Sources: 8 mCi Cs-137 ser#750-171 [and] 40 mCi Am-241 ser#47-23560." The local police, Troxler Electronics and the TXDOT were informed. Texas Incident No.: I-7907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-06-17
38984 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-12 15:34 | 2002-06-12 16:24 | 2002-06-12 | OFFSITE NOTIFICATION DUE TO OIL SPILL Licensee notified the Michigan Department of Environmental Quality of a spill of greater than 5 gallons of oil due to a switchyard breaker explosion and fire. | 69 | 100 | 0 | 69 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-12
38983 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-12 14:05 | 2002-06-12 14:17 | 2002-06-12 | ALERT DECLARED AT DC COOK DUE TO FIRE IN SWITCHYARD The licensee reported an explosion and subsequent fire that occurred in the station's 345-kV electrical switchyard. Neither reactor plant was directly affected by the event and both remained at power. The licensee declared an Alert at 1405 based on the switchyard fire potentially affecting safety related equipment such as the reserve power to safety-related electrical buses. Several switchyard breakers tripped open at 1345 placing the units in TS 3.0.5. One injury was reported. Planned maintenance was in progress in the switchyard at the time of the event. The NRC entered the Monitoring Phase of Normal Mode at 1447 EDT on 06/12/02. Notified the Chairman's office (Mike Tschiltz), USDA (K. Barrett), EPA NRC (Ms. Edwards), EPA EOC (T. Tanner), DOE (T. Yates), FEMA (C. Cleveland), HHS (Carol Cleveland), and OHS (D. Edwards). ***** UPDATE AT 1730 EDT ON 06/12/02 ***** A Commissioners' assistants briefing was held at 1730 EDT. Participants included: NRR (J. Johnson, S. Collins), DIRO (R. Wessman), EDO (H. Nieh), HQ PAO (W. Beecher), OSATP (P. Lohaus), IP (J. Dunn-Lee), CA (L. Gerke), SECY (A. Bates), Comm. Meserve (M. Tschiltz), Comm. Dicus (Kerri Kavanaugh), Comm. Merrifield (J. Thoma), Comm. McGaffigan (J. Sharkey) and Comm. Diaz (D. Simpkins). ***** UPDATE FROM JIM KOBYRA TO LEIGH TROCINE AT 2354 EDT ON 06/12/02 ***** At 2157, the licensee declared the Unit 2 east essential service water pump operable, and Unit 2 exited Technical Specification 3.0.5 at that time. Unit 1 exited Technical Specification 3.0.5 approximately 5 minutes earlier. At 2347, both units exited Technical Specification 3.8.1.1 when the licensee restored transformer 4 to serve the Unit 2 reserve auxiliary transformers and isolated it from Unit 1 (which is being fed by transformer 5). As a result, the licensee terminated the Alert and exited the Emergency Plan at 2354 EDT on 06/12/02. The licensee plans to notify the NRC resident inspectors, State of Michigan, and Berrien County. The NRC exited the Monitoring Phase of Normal Mode at 2355 on 06/12/02. The NRC operations center notified the R3DO (Jim Creed), NRR EO (Bill Bateman), DIRO (Tim McGinty), PAO (Bill Beecher), EDO (Ho Nieh), Chairman's office (Mike Tschiltz), USDA (Lori Thomas and Kathleen Barrett), EPA via the National Response Center (Ms. Arsenault), DOE (Odell Bartlett), FEMA (Al Austin), HHS (Karen Cleveland), and OHS (Ron Brahm). | 69 | 100 | 0 | 69 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-06-12
38982 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-06-12 11:38 | 2002-06-12 14:03 | 2002-06-12 | OFFSITE NOTIFICATION AT DUANE ARNOLD DUE TO A SMALL OIL SPILL "Notified Iowa DNR, Linn County Sheriff, and the US National Coast Guard National Response Center of a reportable spill of petroleum oil into the Cedar River (sheen on the river) per applicable reporting procedures. While performing river water supply pit cleaning, the cleaning pump leaked about 1 pint of oil into the Cedar River. The pump has been removed from the river." | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-12
38981 | 0 | US ARMY |  |  |  |  | 2002-06-12 | 2002-06-12 09:28 | 2002-06-12 | LOSS OF FOUR DETECTORS AT FORT HOOD, TEXAS Four detectors each containing 15 millicuries of nickel-63 were lost at Fort Hood, Texas. On 05/29/02, Fort Hood received the report that the detectors might be missing. Apparently, they were misplaced during preparations to send them to a maintenance shop for wipe testing. The detectors were verified to be missing on 06/05/02, and Fort Hood notified Aberdeen on 06/11/02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-06-12
38980 | 0 | US ARMY |  |  |  |  | 2002-06-11 | 2002-06-12 09:28 | 2002-06-12 | LOSS OF ONE CHEMICAL DETECTOR AT A TRAINING SITE IN SEOMOUL CITY, SOUTH KOREA A chemical detector containing 300 microcuries of americium-241 was lost at the site of a training activity in Seomoul City, South Korea. An investigation is currently ongoing. The detector was verified to be missing on 06/11/02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-12
38979 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-06-11 | 2002-06-11 19:50 | 2002-06-11 | AGREEMENT STATE REPORT FROM CA REGARDING POTENTIAL PERSONNEL OVEREXPOSURE The California state radiation safety officer called in a potential 20.2202 personnel overexposure incident that occurred at The Boeing Company in Anaheim, California. The licensee utilizes irradiator facilities large enough for an individual to enter. The individual's dosimeter was read by the personnel monitoring vendor (i.e., Landauer) as 94 Rem DDE, 94 Rem LDE and 112 Rem SDE. The dosimetry was worn during the period of April 1 to April 30, 2002. The licensee commenced an investigation to determine the validity of the high and unexpected reading. The licensee will conduct an interview with the individual and also the State indicated a blood test will most likely be performed. The State indicated the badge received a "static" exposure, and it will probably turn out to be a dosimeter-only exposure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-06-14
38978 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-06-10 21:20 | 2002-06-11 00:26 | 2002-07-03 | BUS GROUND ON HOUSE SERVICE TRANSFORMER 4160V VITAL BUS TRANSFORMER At 2120 CT Ft. Calhoun Station control room received an alarm indicating a T1A3 4160V Bus Ground on house service transformer 4160V vital bus 1A3 transformer. Licensee referenced ARP and plant AOP's 31 and 32, for all 4160V buses fed from 22KV and Loss of 4160V bus power. Subsequent securing of possible 4160V bus loads did not isolate the ground. Subsequently transferred 4160V bus 1A3 feed from 4160V transformer T1A3 to 22KV Transformer T1A1. Alarm and ground indications went away upon transfer. Per Technical Specification 2.7.(2)b Nuclear Regulatory Commission Operations Control Center shall be notified within 4 hours of transformer inoperability. System Engineering and Electrical Support Staff are on site investigating. Plant is in a severe thunderstorm warning until 2300 CT. Diesel operability has been verified. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATED AT 1545 EDT ON 7/3/02 BY ERICK MATZKE TO FANGIE JONES * * * "Following a root cause investigation it was determined that the event of June 10, 2002, did not result in the inoperability of either house service transformer T1A-3, or vital bus 1 A3. The misdiagnosis of the event was caused by a disconnected ground detector. The ground was on a 4160 to 480 volt vital transformer and did not result in the inoperability of plant equipment." The licensee notified the NRC Resident Inspector. The R4DO (Dale Powers) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2002-06-11
38977 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-06-09 23:55 | 2002-06-10 20:55 | 2002-06-10 | NRC BULLETIN 91-01 CRITICALITY CONTROLS AT PADUCAH PLANT "At 0045 CDT, on 6-10-02 The Plant Shift Superintendent (PSS) was notified that a violation of criticality controls had been discovered in the C-337 process building. C-337 Unit #2 Cell #2 was isolated from the cascade and in the process of being evacuated without an independent verification that a known R-114 coolant leak did not exist, in violation of NCSA CAS-002. The building Front Line Manager checked documentation to see if any other evolutions had taken place without completing this verification. C-337 Unit #1 Cell #2 was also discovered isolated and evacuated to a UF6 negative without an independent verification that a known R-114 coolant leak did not exist, in violation of NCSA CAS-002. The purpose of this check is to determine actions when transitioning to different moderation controls, i.e. removal of fluorinating environment to R-114 and RCW controls. The subject independent verification and coolant sampling were subsequently performed with successful results. These actions re-established double contingency within four hours of the time of discovery. Due to the loss of double contingency and the re-establishment of NCS controls, this event is being report as a 24-Hr. Event Report. The NRC Resident inspector has been notified of this event. "SAFETY SIGNIFICANCE: Significant R-114 leaks to process gas systems should be readily apparent, however no checks for leaks were performed. Both controls were violated and double contingency was not maintained. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for a criticality to occur, an R-114 leak to the process gas system would have to occur. In addition, the R-114 would have to contain an unacceptable amount of moisture and the moisture would have to be absorbed in a deposit of unsafe mass. "CONTROLLED PARAMETERS: Double contingency is maintained by implementing two controls on moderation. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(s) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on ensuring wet R-114 coolant does not moderate existing uranium deposits. NCSA CAS.002 requires that prior to the initial evacuation of UF6, a check be made to determine if a known R-114 to process leak exists. This check was not performed and the control was violated. Until the check was performed successfully, the process condition was not maintained and double contingency was not maintained. The second leg of double contingency is based on independent verification that a known R-114 leak into the process gas system does not exist. This independent check was not performed violating the control. Until the check was independently performed successfully, the process condition was not maintained and double contingency was not maintained. Since double contingency is based on two controls on one parameter and both controls were violated, double contingency was not maintained." The NRC Resident Inspector was notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-06-10
38976 | 0 | STATE OF MONTANA - RSO |  |  |  |  | 2002-05-28 08:30 | 2002-06-10 16:04 | 2002-05-28 | LOST/MISSING RADIOACTIVE MATERIAL AT ROCKY MOUNTAIN LABS The Montana State RSO reported that Rocky Mountain Laboratories located in Hamilton, Montana is missing approximately 12 millicuries of Sulfur-35. This material is a low energy beta emitter which is used for biological research including protein mapping. The material was in the form of pellets and was in the bottom of microfuge tubes which were wrapped in a double bag. The bag was last seen in building 1, room 102, on May 24, 2002 at 17:00. The material was discovered missing at 8:00 am on May 28, 2002. A search was conducted and also waste streams were checked. The State of Montana notified the NRC Region IV (Christy Maier). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-10
38975 | 0 | ROTORK CONTROLS, INC |  |  |  |  | 2002-06-10 | 2002-06-10 13:11 | 2002-06-10 | PART 21 ON ROTORK NA1 ACTUATOR The name of the manufacturer is Rotork Controls, Inc. The defective components the Rotork NA1 type electric Valve Actuators fitted with an Add-on-Pak 1 (AOP1) Assembly which was manufactured between 1978 and October 2001 and have a safety function used for end of travel indication. The problem is that moulded components within the AOP1 assembly cannot be confirmed to the same specifications as those originally tested and qualified at Wyle in 1978. No list of affected plants was available at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2002-06-10
38974 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-06-10 | 2002-06-10 12:40 | 2002-06-10 | AGREEMENT STATE REPORT OF MEDICAL MISADMINISTRATION "Patient who was suppose to receive 32 millicuries I-131 was given 120 millicuries I-131. As patient's thyroid was to be ablated anyway, no ill effects to patient. The doctor gave her the wrong dose." The cause of the misadministration is being reviewed at the time of the report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-06-13
38973 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2002-06-07 21:15 | 2002-06-08 13:50 | 2002-06-08 | AGREEMENT STATE REPORT - EMPLOYEE DEATH DUE TO NONNUCLEAR ACCIDENT With the source in the stored position, an employee of Isomedix Operations, entered the sterilization chamber of the irradiator to try freeing some jammed product carriers. The employee was killed when his head was caught between the carriers as they moved together. This report is made as a conservative measure as this was not nuclear related, but occurred at a licensee's facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0 | 2002-06-12
38972 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-06-06 | 2002-06-07 17:07 | 2002-06-07 | AGREEMENT STATE REPORT - SOURCE NOT ATTACHED TO SOURCE ROD "On June 6, 2002 at 4:30 p.m. the Arkansas Department of Health was notified by Albemarle Corporation in Magnolia, Arkansas that a fixed density gauge source had been damaged. Albemarle has Arkansas Radioactive Material License ARK-717-BP-11-99. The device is a Ronan Engineering Company Model SA-15 containing two 5 millicuries sources of Cesium-137. The device was locked out on June 3, 2002. On June 6, 2002 while the source housing was being adjusted it was noted that the source rod was in a different configuration. Radiation surveys were performed and it appeared that one of the 5 millicuries sources was not attached to the source rod. The immediate area was secured and access has been restricted. Albemarle has contacted a consultant to assist in retrieval and packaging of the source for return to the manufacturer. "The Department has sent two inspectors to the facility to investigate and assess the Incident on June 7, 2002. It appears that there may have been personnel radiation exposure due to this incident. This incident is under investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2002-06-12
38971 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-06 16:10 | 2002-06-07 14:10 | 2002-06-07 | OFFSITE NOTIFICATION TO THE STATE DUE TO SEWAGE SPILL At about 1500 CDT on 6/6/02 a bobcat backed into a sewage treatment trap resulting in a spill of about 350 gallons of untreated sewage. About 50 gallons found its way into the Squaw Creek Reservoir. The other 300 gallons was recovered. The licensee notified the Texas Natural Resource Conservation Commission, DFW Regional Office, Solid Waste Group at 1610 CDT on 6/6/02. The licensee notified the NRC Resident Inspector at 1640 CDT on 6/6/02. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-06-07
38970 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-06-07 08:15 | 2002-06-07 12:46 | 2002-06-07 | CONDITION EXISTS THAT COULD LEAD TO DRAINING THE REFUELING WATER STORAGE TANK The licensee was performing a fire area inspection as part of a post fire safe shutdown study and discovered a condition existing that could lead to draining the refueling water storage tank (RWST) to the containment recirculation sump due to a fire. It was discovered that control cables for 2 redundant motor operated valves are routed in the same electrical raceway. The 2 valves are on the same electrical separation group, but are redundant in their function of conserving water inventory in the RWST. Further investigation determined that the other electrical separation group has the same configuration. The licensee has implemented a continuous fire watch and is working on procedure changes to insure compensatory actions are in place. Further changes will be made after engineering analysis including rerouting the cables for the affected valve operators. The licensee notified the NRC Resident Inspector. The licensee also informed the Callaway plant which is the same series of plant and could have the same condition. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2002-06-07
38969 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-06-06 19:24 | 2002-06-06 22:21 | 2002-06-06 | REACTOR TRIP CAUSED BY TURBINE TRIP The reactor tripped due to a turbine trip due to a main generator trip caused by a high vibration on the main generator primary water pump shaft. All systems functioned properly. The plant is stable in Mode 3 with steam generator level being maintained with auxiliary feedwater (started automatically on low steam generator level) and excess heat being removed via the steam bypassed to the main condenser. Primary water pump vibration trip is a 2 out of 2 channel coincidence. There was no indication of high vibration on the plant recorder. At the time of the trip, an investigation was ongoing on one of the channels that was in alarm. An investigation continues into the sensors and circuits associated with the high vibration trip. The plant will remain in Mode 3 until the problem is identified and corrected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-06-06
38968 | 0 | BJ SERVICES COMPANY |  |  |  |  | 2002-06-06 | 2002-06-06 10:57 | 2002-06-06 | GENERAL LICENSE CESIUM-137 SOURCE COULD NOT BE ACCOUNTED FOR BJ Services, an oil field service company, determined that a general licensed source could not be located. The source, 250 mCi Cs-137 sealed in special form manufactured circa 1984, was installed in a Kay Ray Model 7063 instrument, S/N 28820, used for slurry density measurements. The last recorded location was Rock Springs, WY, on September 8, 1990 for a leak test. The instrument was then owned by Western Company which was acquired by BJ Services in 1995. BJ Services has discussed this incident with R4(Donovan) and will continue their investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-06-06
38967 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-06-05 23:00 | 2002-06-06 02:51 | 2002-06-06 | UNIT 1 DECLARED AN UNUSUAL EVENT DUE TO RCS LEAKAGE > 25 GPM DURING SURVEILLANCE TESTING "D.C. Cook Unit One declares entry and exit of an Unusual Event due to Reactor Coolant System leakage of greater than 25 gallons per minute. On June 5 @ 23:00 while performing an 18 month surveillance [1-IHP-4030-102-017 'Pressurizer PORV/Actuation Channel Calibration with Valve Operation'] on the Pressurizer Power Operated Relief Valves (PORVs) an unblocked PORV lifted and discharged to the Pressure Relief Tank (PRT) for approximately 15 seconds. This lifting discharged approximately 100 gallons to the PRT. The Initiating Condition for this Unusual Event is Reactor Coolant System leakage greater than 25 gallons per minute. "The plant is and was in Mode 4. Conditions remain stable after manual isolation of the PORV with the Control Switch of the Block Valve by the assisting Reactor Operator." The licensee attributed this occurrence to the recently revised procedure identified above which did not address blocking the other PORVs during testing. The licensee informed state and local agencies and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-06-06
38966 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-06-04 14:20 | 2002-06-05 13:18 | 2002-06-05 | NRC BULLETIN 91-01 RESPONSE -- FAILURE TO MAINTAIN A DOUBLE CONTINGENCY INVOLVING TWO CONTROLS ON THE MASS PARAMETER (24-Hour Report) The following text is a portion of a facsimile received from Paducah personnel: "A container of improperly exempted uranium hexafluoride compressor parts was discovered in the C-333 process building which had not been characterized for storage as a group, in violation of the governing Nuclear Criticality Safety Approval NCSA GEN-010. NCSA GEN-010 requires individual items to be either spaced or grouped. Grouping is allowed if mass requirements are met. These items were not identified as GEN-010 items and had been stored as an unanalyzed group. The purpose of the GEN-010 requirement is to ensure that only safe mass items/groups are handled." "The NRC Resident Inspector has been notified of this event." "PGDP Assessment and Tracking Report No. ATR-02-2713; PGDP Event Report No. PAD-2002-017, Event Worksheet 38966" "Responsible Division: Engineering" "SAFETY SIGNIFICANCE OF EVENTS:" "Double contingency was not maintained because the independent determination of mass had not been performed. The independent determination of mass has since been performed and [was] found to be less than the maximum safe mass." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR:" "In order for a criticality to be possible, more than a critical mass would need to be accumulated in an unsafe geometry." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.):" "The controlled parameter is mass." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS):" "A non-destructive analysis was conducted and determined the mass of U235 in the parts was less than 91 grams; the always-safe mass at the assay involved is [ ] grams of U235." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES:" "Double contingency is maintained by implementing two controls on the mass parameter." "The first leg of double contingency is based on determining the mass of the group. The mass was not determined during the legacy characterization process. Therefore, the control was violated." "The second leg of double contingency is based on independently determining the mass of the group. The mass was not determined during the legacy characterization process; therefore, the control was violated. Since there are two controls on one parameter, the mass parameter was not maintained and double contingency was not maintained." "Since double contingency is based on two controls on one parameter, double contingency was not maintained." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED:" "Use the independent NDA results in conjunction with approved plant procedures to establish and post these items as a GEN-010 group." Paducah personnel reported that the information provided via facsimile (and quoted above) does NOT contain sensitive information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-06-05
38965 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-06-05 10:45 | 2002-06-05 13:10 | 2002-06-05 | NRC BULLETIN 91-01 RESPONSE -- FAILURE TO MAINTAIN A DOUBLE CONTINGENCY INVOLVING MATERIAL TRANSFER INTO THE ERBIA MODCON AREA WITHOUT MOISTURE RESULTS (24-Hour Report) The following text is a portion of a facsimile received from the licensee: "Facility Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched ([<=]5.0 wt. % U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107." "Time and Date of Event Approximately 10:45 hours, Wednesday, June 5, 2002." "Reason for Notification Thirteen packs of oxidized U3O8 were improperly transferred into the Erbia Modcon area without proper moisture analysis results." "Summary of Process UO2 powder is oxidized to U3O8 to be used as addback in powder blends. After staying in an oven at a high temperature for over one hour, the material is screened and put into polypaks. Each pack is sampled for moisture and stored pending results of the moisture analysis. Then the material is bar code scanned and transferred into the Modcon area using a polypak elevator interlocked with the moisture analysis results." "As-Found Condition A summary of the as-found conditions is as follows: * Thirteen packs of material were found to have been taken into the Modcon area via a freight elevator, bypassing the bar code scanning interlock. The packs did not have moisture analysis results completed and posted. * The packs were immediately removed from the area, and the Nuclear Criticality Safety (NCS) function was immediately notified. * The material in question was oxidized U3O8, visually dry." "Double Contingency Protection Double contingency protection for the erbia blender and bulk containers is based on moderation control, that is, (1) prevent greater than 20.48 liters of water equivalent from becoming available to the mixer or container, and (2) prevent 20.48 liters of water equivalent from entering the mixer or container. It was determined that double contingency protection was bypassed because, for the 13 packs involved, there were no effective controls to prevent material with undocumented moisture from being brought into the Modcon area. It is also noted that at no time was greater than the safety limit of moderator involved. Therefore, the incident requires 24-hour notification in accordance with Westinghouse Operating License (SNM- 1107), paragraph 3.7.3(c.5)." "Summary of Activity * The packs were immediately removed from the area, and the Nuclear Criticality Safety (NCS) function was immediately notified. * The Erbia Process Engineer stopped all erbia powder blending operations." "Conclusions * There was a loss of double contingency protection. * At no time was greater than a safe limit of moderator involved. * At no time was criticality possible. * At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. * The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed." The licensee reported that the information provided via facsimile (and quoted above) does NOT contain sensitive information. The licensee notified an onsite NRC Region 2 inspector (Bill Gloersen) and plans to notify the NRC Region 2 office (Manuel Crespo) and NMSS (Dennis Morey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-06-05
38962 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2002-06-03 15:00 | 2002-06-03 17:02 | 2002-06-03 | DISCOVERY OF AN OPEN MANUALLY-OPERATED HEADER VENT VALVE RESULTING IN INOPERABILITY OF THE ISOLATION VALVE SEAL WATER SYSTEM The following text is a portion of a facsimile received from the licensee: "Indian Point Unit 3 is making an [8-hour] non-emergency notification that the Isolation Valve Seal Water System (IVSWS) was found in an inoperable condition on June 2, 2002. A manually operated header vent valve (IV-1428) was found mispositioned in an open position. [The] IVSWS is designed to provide a water seal for certain containment isolation valves by injecting water between the seats and stem packing of globe and double disc type isolations valves and piping between other closed containment isolation valves. Water under pressure is supplied from a single seal water tank to five IVSWS headers for valve sealing. IVSWS is designed to provide the water seal for 24 hours, without operator action, after a postulated loss of coolant accident, in order to mitigate bypass leakage. The open vent valve could have prevented pressurization and drained the seal water in the IVSWS tank, requiring operator action to refill it, in less than 2 hours. The inoperable IVSWS is not expected to result in any significant effect on public health and safety since the containment isolation valves remain operable. The containment Isolation valves are not pneumatically 10 CFR [Part] 50, Appendix J, Type C tested because they are supplied with seal water but they have been leak tested with water. The inoperable IVSWS is required to be operable by Technical Specification 3.6.9." "On discovery, the operator closed the vent valve and restored the IVSWS to operability. The condition report issued at that time called for a past operability report. The inoperable IVSWS was identified while performing this evaluation. The duration of the mispositioned valve is still under investigation." The licensee stated that this event was determined to be reportable at approximately 1500 EDT today (06/03/02). The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2002-06-03
38961 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-06-03 13:02 | 2002-06-03 16:38 | 2002-06-03 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL BECAUSE A MAIN FEEDWATER REGULATING VALVE FAILED CLOSED The following text is a portion of a facsimile received from the licensee: "The unit was at approximately 86% power, ramping to 92% power following [the eleventh Unit 1 refueling outage (1R11)]. The main feedwater regulating valve for steam generator 1 failed closed. Attempts to open the valve manually failed. The [Shift Foreman] ordered a manual reactor trip, but an automatic trip occurred before operators could trip the reactor. The unit is currently stable in Mode 3." The licensee stated that the automatic reactor trip signal was two out of three steam generator 1-1 low level. All control rods fully inserted, and auxiliary feedwater automatically initiated as designed. There were no emergency core cooling system (ECCS) injections or engineered safety feature (ESF) actuations, and none were required. Other than the cause of the main feedwater regulating valve failure, there was nothing unusual or misunderstood, and all systems functioned as required. There were no related maintenance or surveillance activities ongoing at the time of the automatic reactor trip. The licensee also stated that normal charging and letdown, pressurizer heaters and sprays, and the reactor coolant pumps are currently being utilized for primary system level, pressure, and transport control. Auxiliary feedwater being utilized to supply water to the steam generators, and secondary steam is being dumped to the condenser. Containment parameters are normal, and all ECCS and ESF systems are available if needed. The unit is currently on offsite power, and the emergency diesel generators are available if needed. The licensee notified the NRC resident inspector, who is currently in the control room, and may issue a press release. | 0 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-06-03
38960 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2002-06-03 08:00 | 2002-06-03 11:14 | 2002-06-03 | REMOVAL OF EMERGENCY SIRENS FROM SERVICE DUE TO MAINTENANCE Planned maintenance of the offsite siren system will result in each of the sirens in Putnam County being removed from service. There are 10 sirens in Putnam County and Indian Point Energy Center considers a loss of 10% of the sirens in a county to be a major loss of emergency assessment capability. The removal of sirens from service in Putnam County will continue on an intermittent basis from June 3, 2002 until June 21, 2002. The first siren was removed from service at 8 a.m. on June 3, 2002. The planned maintenance is intended to replace the siren actuation/verification system in order to improve reliability and maintainability. The replacement process will install the new actuation/verification system, connect the actuation/verification system, and terminate the connection of the old controls. This work is currently scheduled on one siren per day. Testing of the new actuation/verification system will not occur until the next day at the request of Putnam County. If this plan is followed, a 10% loss of the offsite communications occurs when the old controls are terminated until the new actuation/verification system is tested. This increases to 20% if the testing does not occur prior to the next siren being taken out of service. Putnam County will use route alerting to notify the public in lieu of the non-operational sirens. County officials are aware of the scheduled activities, and newspaper ads have been placed regarding testing. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-06-03
38959 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2002-06-02 01:02 | 2002-06-02 01:37 | 2002-06-02 | PLANT HAD CARBON DIOXIDE INJECTION INTO THE E3 DIESEL ROOM This "Cardox system" injection occurred at 0033 during diesel testing. An alert was declared at 0102 due to the detection of toxic gases(CO2) within a vital area. The room was evacuated(only two people were in the room at that time) safely and there were no injuries. There was no fire damage and the CO2 tank was isolated. The NRC Resident Inspector, State and local agencies were notified by the licensee. Notified FEMA (Sweetser), DOE(Morroney), EPA/DOT/NRC(Thomas), CDC(Rhyne), FDA(Shandruk) and OHS(Edwards) * * * UPDATE ON 6/2/02 @ 0420 BY CAMPBELL TO GOULD * * * The Alert was terminated at 0301. Notified DOE(Yates), CDC(Rhyne), EPA/NRC/DOT(Thomas), FEMA(Sulivan), OHS(Edwards) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-06-02
38958 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2002-06-01 18:40 | 2002-06-01 20:27 | 2002-06-01 | AUTOMATIC REACTOR TRIP DURING STARTUP "During plant startup, a spike occurred on the N32/N36 channel of source/intermediate range excore neutron flux detectors. The reactor tripped automatically. All system[s] operated normally. Emergency feedwater was already in service for the startup, no actuation occurred." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-06-01
38956 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2002-05-30 14:00 | 2002-05-31 17:28 | 2002-05-31 | LOSS OF LICENSED NUCLEAR MATERIAL IN HELICOPTER ACCIDENT An Air Force Pave Hawk Helicopter crashed approximately 800 feet from the summit of Mount Hood. Each of the 4 rotors contains a 500 microcurie Sr-90 source. More information will follow as it becomes available. The State will be contacting R4. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2002-06-05
38955 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2002-05-31 09:30 | 2002-05-31 13:42 | 2002-06-04 | STOLEN TROXLER MOISTURE/DENSITY GAUGE "Description of event: The licensee reported the loss of a Troxler moisture/density gauge and company truck when a technician failed to report to a designated job site. The gauge is a Troxler Model 3440, serial number 21935. It contains approximately 8 millicuries of Cesium 137 (source serial number 75-3524) and approximately 40 millicuries of Americium-Beryllium (source serial number 47-17271). The company vehicle is a 1999 white Ford F-150 extended cab pickup, company number 50, Arizona license [ ]. The Tempe police have been notified and are investigating. The company is offering a $250 reward for information leading to the return of the gauge and truck. "The U.S. NRC, FBI, Mexico, and the states of Colorado, Nevada, Utah, New Mexico and California are being informed of this incident." * * * UPDATE ON 6/4/02 BY WRIGHT (BY FAX) TO GOULD * * * The gauge and truck have been recovered. The FBI, Mexico and the states of Colorado, Nevada, Utah, New Mexico and California were informed. Notified Reg 4 RDO (Pellet), NMSS (Brown), IAT (Davidson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2002-06-07
38954 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-05-31 01:16 | 2002-05-31 02:02 | 2002-05-31 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO GENERATOR PROTECTION ACTUATION "On May 31, 2002 at 0116EDT, Unit 2 was at 71% reactor power and increasing to 100% when the reactor tripped due to a failure with the generator stator cooling water system. All systems responded as designed. The plant is currently in mode 3, full temperature and pressure." Both motor-driven and the steam-driven auxiliary feedwater pumps actuated and are currently supplying the Steam Generators with the Main Condenser removing decay heat. The steam-driven auxiliary feedwater pump was subsequently secured and returned to standby. All rods fully inserted with all EDGs available, if necessary. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 71 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-05-31
38953 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2002-05-30 20:30 | 2002-05-31 01:08 | 2002-05-31 | HPCS DECLARED INOPERABLE FOLLOWING FAILURE OF ASSOCIATED EDG DURING POST MAINT TESTING "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D), Event or Condition That Could Have Prevented Fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During a post maintenance test run of the 2B Diesel Generator following a planned maintenance window, the Diesel Generator reactive load (VARs) was identified to be extremely erratic as the Diesel Generator was loaded. At 20:30 Central Daylight Savings Time, it was discovered that a potentiometer in the voltage regulating circuit had failed. This potentiometer was not worked on during the planned maintenance window. Because this component failure could have prevented the Diesel Generator from performing its design function, and because the 2B Diesel generator is the emergency power supply for the High Pressure Core Spray System (HPCS), which is a single train safety system, it has been determined that this failure is reportable as an 8 hour ENS notification. The failed component has currently been replaced and further testing of the Diesel Generator is in progress. The required actions of Technical Specification 3.5.1 were entered when the system was made Inoperable for the maintenance window, and are continuing to be followed for the Inoperable HPCS system until the Diesel Generator is restored to Operable status." The licensee anticipates completing testing by the end of dayshift on 5/31/02 and has informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-06-30
38952 | 0 | ALT & WITZIG ENGINEERING, INC |  |  |  |  | 2002-05-03 | 2002-05-30 18:00 | 2002-05-30 | LOSS AND RECOVERY OF TROXLER MOISTURE/DENSITY GAUGE Troxler Nuclear Moisture/Density gauge Model #3430 and serial # 23264 was secured with a chain and lock in the bed of a pickup truck. The truck was driven non stop from Niles, MI to Laporte, IN and it was discovered that the tailgate had fallen to the open position and the gauge was missing. An immediate search of the travel route ensued. Shortly thereafter, Alt & Witzig Engineering's Corporate office was notified that the gauge had been found by a private citizen and was in the custody if the Dowagiac, MI police department. The case was pad locked and uncompromised, as was the source rod. A leak test was performed on the gauge, Sat. The gauge contained 8 mCi of Cs-137 and 40 mCi of Am/Be-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-05-30
38951 | 0 | WESTERN RESEARCH INSTITUE |  |  |  |  | 2002-03-05 | 2002-05-30 16:01 | 2002-05-30 | LOST LICENSED NUCLEAR MATERIAL >10 TIMES "On or about March 5th, 2002, Western Research Institute (WRI) received a telephone call from [ ], of Princeton Gamma-Tech. Inc. (PGT) [ ] inquiring about the status of a PGT-100 X-Ray Chemical Analyzer (s/n 192) originally purchased by one of WRI's predecessor organizations in February, 1976. This instrument contained a sealed 50 mCi iron (Fe-55) source (NER-462) and was used to measure the sulfur concentration in materials by means of X-ray fluorescence. We have conducted a search of our records to determine the history of this device. "WRI is not licensed to possess Fe-55, nor does the PGT analyzer appear in WRI's radiation safety records, which began in August of 1992. The analyzer does, however, appear in WRI's property records up to about 1990 when we believe it was disposed of in one of three procedures being used at that time. These procedures included disposal in the local landfill, sale or transfer as surplus property, and sale as scrap metal. Unlike other items disposed of before and after that time, the excess-property transfer form for the PGT- 100 was not signed or dated, providing no leads to the ultimate fate of the PGT- 100 and its Fe-55 source. On one property listing dated May 14, 1990, there is a hand written note: 'EX 6-8-88 to U/W' [ ]. Neither the properly office nor radiation safety office at the University of Wyoming has found a record of the PGT analyzer. "To assist our search for the instrument [ ] faxed copies of the POT records concerning the analyzer [ ]. These records show that the Fe-55 source was replaced and wipe tested on approximately two-year intervals: Jun. 1, 1978; Oct. 29, 1980; Sep. 22, 1982; and Aug. 8, 1984. There are no records concerning the analyzer at PGT after August of 1984. Based on a half-life of 2.6 years for Fe-55, the remaining activity of the source as of April 2002 is about 0.45 mCi, still 4.5 times the level requiring labeling. "WRI's predecessor organizations during the relevant time period were the Lararnie Energy Research Center (LERC), an office of U. S. Energy Research and Development "Administration (ERDA, 1975-l977): and the Laramie Energy Technology Center (LETC), a field office of the U. S. Department of Energy (DOE, 1977-1983). In April of 1983, the organization was de-Federalized and absorbed by the University of Wyoming as the Western Research Institute, an independent research corporation operated as an adjunct to UW as a wholly owned subsidiary of the UW Research Corporation. While operating as a field office for ERDA and DOE, LERC and LETC were exempt from NRC licensing. As WRI, from April of 1983 to August of 1992, radiation activities at WRI were conducted under the umbrella of the University of Wyoming's NRC license. In August of 1992, WRI received its own NRC license. "Although the undocumented transfer or disposal of the PGT analyzer occurred prior to WRI obtaining its NRC license, WRI has made an effort to find the analyzer and documentation of its disposal. We have exhausted the obvious avenues of search and cannot determine with certainly the fate of the PGT analyzer and its Fe-55 source." R4 (Garcia) was informed by Licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-05-30
38950 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-05-30 | 2002-05-30 10:08 | 2002-05-30 | AGREEMENT STATE REPORT - TEXAS REPORTS STOLEN NUCLEAR GAUGE "Gauge had been in use at a job site in San Antonio. The gauge was secured in the bed of a company pickup and was discovered missing at 8 a.m. on May 20, 2002. The gauge, a Troxler Thin-Lift Asphalt Gauge Model 4640B, Serial No. 1825, with an 8 millicurie Cs-137 source, Serial No. 75-8669, was removed from the case which was pried open in the back of the pickup. A police report was filed with the San Antonio Police Department. Transport case was left secure in the rear of the pickup. Only the gauge was stolen. Other details are lacking and will be reported by the Licensee to this Agency within 30 days." This is tracked under Texas Incident No. I-7901. The R4DO (G. Sanborn) and NMSS (F. Brown ) was notified. The local police department was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-06-04
38949 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-05-29 17:05 | 2002-05-29 20:59 | 2002-05-29 | OFFSITE NOTIFICATION TO OHIO EPA DUE TO EXCEEDING OPACITY LIMIT "On 5/29/02 at 1705 hours, the voltage and current failed to zero on X-600 #1 Precipitator B-side. This equipment failure caused two opacity readings (six minute averages) to be above 20% within one hour. The opacity was 38.1% for 12 minutes. This requires a verbal notification to the Ohio Environmental Protection Agency (OEPA). "At 2025 hours, the Plant Shift Superintendent notified OEPA of the X-600 Steam Plant opacity exceedance. UE2-RA-RE1030, App D, section P requires a 4 hour NRC event [report] when other government agencies are notified." Operations informed both the NRC Resident Inspector and the DOE Site Representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-05-29
38948 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2002-05-29 | 2002-05-29 11:15 | 2002-05-29 | OFFSITE NOTIFICATION AT TURKEY POINT 3 INVOLVING A DEAD SEA TURTLE "Site personnel notified the State of Florida, Florida Fish and Wildlife Commission, of finding a dead green sea turtle on FPL property. FPL will also be notifying the U.S. Fish and Wildlife service." The NRC Resident Inspector was notified. Notified the R2DO (K. Landis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-05-29
38947 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-05-28 02:31 | 2002-05-28 09:38 | 2002-05-28 | DIGITAL ROD POSITION URGENT FAILURE DURING TESTING While performing rod withdrawal testing in Mode 4, a digital rod position indication (DRPI) "Urgent Failure " alarm was received for rod L-5 in control bank 'A' at the 72 step position. Control bank 'A' was the only bank withdrawn at the time. The reactor trip breakers were opened and all rods fully inserted in accordance with Tech Spec 3.1.3.3. The cause of the failure was a card failure, which has been repaired. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-05-28
38946 | -1 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-05-26 08:35 | 2002-05-26 15:24 | 2002-06-17 | PERSONNEL ACCESS DOOR BETWEEN UPPER AND LOWER CONTAINMENT COMPARTMENTS FOUND OPEN Maintenance technicians discovered a personnel access door (submarine hatch) open between the upper and lower containment compartments. The seals and sealing surfaces were inspected and the door was closed immediately in compliance with LCO 3.6.14. While the door was open, containment divider integrity was not intact per LCO 3.6.14. This LCO establishes the minimum equipment requirements to ensure that the divider barrier performs its safety function of ensuring that bypass leakage, in the event of a DBA, does not exceed the bypass leakage assumed in the accident analysis. The divider barrier functions with the ice condenser to limit the pressure and temperature that could be expected following a DBA. An analysis performed to support a 6 hour completion time in LCO 3.6.14 condition B indicates that an open hatch(7.5 sq. ft bypass area) during a DBA does not impact the design pressure or temperature of the containment. The submarine hatch is 2 ft in diameter(3.19 sq. ft), thus the safety significance is considered minimal at this time. The NRC Resident Inspector will be notified along with the states of N Carolina and S Carolina. Also the nearby counties were notified. * * * RETRACTED ON 6/17/02 AT 1648 EDT BY JIMMY BURGESS TO FANGIE JONES * * * The licensee is retracting this event notification as further analysis has shown that the divider barrier seal would have been able to perform its safety function. The expected post-accident pressure increase resulting from the increased bypass leakage through the hatch opening would be within the containment pressure accident analysis limits. The licensee will send a License Event Report to the NRC within 60 days of the event. The licensee notified the NRC Resident Inspector. The R2DO (Kerry Landis) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-05-26
38945 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-05-24 14:20 | 2002-05-24 17:06 | 2002-05-24 | OFFSITE NOTIFICATION REGARDING THE DISCOVERY OF AN OLD SPENT BLASTING CAP IN THE YARD OUTSIDE THE PROTECTED AREA The following text is a portion of a facsimile received from the licensee: "Offsite agency assistance [was] requested to assess a spent blasting cap found outside the Protected Area in the yard. A City of Rock Hill explosives expert was requested by security to assess/take possession of the spent blasting cap." "The explosives expert determined that the blasting cap was spent[. The explosives expert also] determined its age as 10-20 years at least and [that it] was leftover from the construction of the site. The officer took possession of the spent blasting cap and removed it from the site at 1507 EDT." The licensee notified the NRC resident inspector and City of Rock Hill Police Department in South Carolina. The licensee also plans to notify the States of North Carolina and South Carolina as well as York, Gaston, and Mecklenburg Counties. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-05-24
38944 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-05-20 | 2002-05-24 16:29 | 2002-05-24 | DISCOVERY OF A LEAKING RADIUM STATIC ELIMINATOR AT A SCRAP METAL RECYCLING FACILITY LOCATED IN DENVER, COLORADO On the morning of 05/20/02, a leaking radium static eliminator was discovered at a scrap metal recycling facility (Metal Management, Inc.) located in Denver, Colorado, when the facility's portal monitors alarmed. The static eliminator was on what appeared to be labeling equipment, and it does not appear to be licensed due to its age (vintage 1930s or 1940s). State representatives responded on the afternoon of 05/20/02, and smears were taken on the horizontal surfaces of the areas adjacent to the static eliminator. The results of these smears are expected to be received by close of business today. An attempt will be made to identify the original owner. However, the state is in the process of issuing the scrap metal facility a provisional license which would allow the facility to make arrangements with a broker if the original owner of the static eliminator cannot be found. The state plans to contact the Environmental Protection Agency (Region VIII). (Call the NRC operations officer for a state contact telephone number and for the address of the metal recycling facility.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-05-30
38943 | 0 | US ARMY |  |  |  |  | 2002-05-24 11:30 | 2002-05-24 14:39 | 2002-05-24 | DISCOVERY OF CONTAMINATION/TRITIUM LEAKAGE ON AN M-1 TANK MUZZLE REFERENCE SENSOR AT THE US ARMY ABERDEEN TEST SITE TANK RANGE While preparing a tank for shipment, the licensee discovered that an M-1 Tank Muzzle Reference Sensor (MRS) containing 10 curies of tritium was leaking and discharged to the atmosphere. The exact time that the leak occurred is not currently known. Apparently, 200 rounds were fired from this tank, and then the MRS was checked prior to shipment of the tank to Michigan. Three swipe counts were performed, and the contamination levels ranged between 150,000 and 170,000 dpm/100 cm². The licensee stated that there were no personnel contaminations as a result of this event. A swipe count was performed on the hands of the individual who installed the MRS, and it was negative. Urinalysis is also being performed as a precautionary measure, and the results are pending. Apparently, no other personnel came into contact with the leaking MRS. The leaking MRS was removed, double bagged, and placed in storage. The licensee plans to dispose of it as radioactive waste. There was minimal contamination on the tank gun tube, and it was cleaned to acceptable levels (below limits). The licensee plans to ship the tank without the MRS. (Call the NRC operations officer for a contact telephone number for the licensee's Radiation Safety Officer.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-05-24
38942 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-05-23 19:34 | 2002-05-24 12:33 | 2002-05-24 | A CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL DURING A RANDOM FITNESS-FOR-DUTY TEST (24-Hour Report) A contract supervisor failed a random drug and alcohol fitness-for-duty test. The individual tested positive for alcohol, and the results of the drug portion of the test have not yet been received. The individual's unescorted site access was terminated at 1937 on 05/23/02, and the licensee plans to perform a review of the individual's work for the last 30 calendar days or for the duration of the individual's employment (which ever is shorter). (Call the NRC operations officer for additional details.) The licensee notified the NRC resident inspector and plans to notify the NRC Region 1 office (Greg Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NH | POW |  | 26.73 |  |  |  | 0 | 2002-05-24
38941 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2002-05-23 14:00 | 2002-05-24 09:26 | 2002-05-24 | FITNESS FOR DUTY REPORT A non-licensed contract supervisor was determined to have provided a tainted sample during a random drug test. The employee's access to the plant has been terminated. Refer to the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2002-05-24
38940 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2002-05-23 14:02 | 2002-05-23 21:36 | 2002-05-31 | HIGH THRUST BEARING TEMPERATURE DURING HIGH PRESSURE COOLANT INJECTION (HPCI) OPERABILITY SURVEILLANCE TESTING HPCI was declared inoperable due to high thrust bearing temperature during performance of pump operability surveillance. There was nothing unusual or misunderstood other than the cause of the high thrust bearing temperature. As a result, the unit entered a 14-day limiting condition for operation. The licensee plans to notify the NRC resident inspector. * * * 1522 EDT 5/31/02 THIS EVENT WAS RETRACTED JOHN TWAROG TO MIKE NORRIS* * * "On 05/23/02 during a plant start-up with the reactor at approximately 19.5% power, a High Pressure Coolant Injection (HPCI) turbine thrust bearing temperature high alarm (SO 12) occurred while performing operational surveillance testing of the HPCI system. The turbine thrust bearing displayed a constant temperature rise until the alarm set point of 200 F was reached. The turbine was secured a few minutes later and the temperature indication on the thrust bearing peaked at approximately 200 F before indication of cool down appeared. "The Manager of Maintenance Mechanical/Electrical consulted a Kingsberry Thrust bearing Company Engineer who stated that temperature-induced bearing damage will not occur until the bearing temperature exceeds 250 F. The maximum indicated bearing temperature received was less than 210 F. Additionally, an oil sample was taken and visually examined with no indication of gross suspended particulate. "System Engineering completed an assessment of this condition on 05/24/02 which revealed evidence that provided credible justification using sound engineering judgment that the thrust bearing temperature indication was false and an actual high temperature condition did not exist at any time during the surveillance testing. Insulation had been removed from the turbine casing around the turbine gland seal during the mid-cycle outage. This resulted in an elevated temperature indication of the thrust bearing due to radiant and convective heat transfer to the temperature indicator's thermocouple external to the thrust bearing. Steam leaking past the gland seal may have also contributed to the temperature increase. When the exposed area of the HPCI turbine was reinsulated, indicated temperature began to rapidly decrease. Subsequent HPCI system operation supported these conclusions. The maximum thrust bearing temperature indication received during this surveillance was 158 F. Trend analysis demonstrated that the maximum temperature would have peaked at approximately 175 F." The NRC Resident Inspector has been notified. R1DO (Rogge) was notified. | 27 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-05-23
38939 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-05-23 16:41 | 2002-05-23 17:45 | 2002-05-23 | PLANNED OFFSITE NOTIFICATION REGARDING TWO RADIATION MONITOR DETECTORS SOLD AS SURPLUS MATERIAL BUT CONTAINED RADIOACTIVE MATERIAL The following text is a portion of a facsimile received from the licensee: "On May 22, 2002, STP Nuclear Operating Company (STPNOC) was notified by an individual that two radiation monitor detectors he purchased from South Texas Project as surplus material might contain radioactive material. The detectors had never been installed in the plant but were excess material stored in the site warehouse since their purchase in 1993. STPNOC personnel were sent to investigate the issue and confirmed that the detectors did contain check sources in sealed containers attached to the detectors. These sources, when purchased in 1993, were 8 microcuries of cesium-137 and attached to the detectors in separate sealed housings. The sources were surveyed and found to have a dose rate of 0.18 millirem per hour on contact." "The sources were removed from the detectors and transported back to the site." "The resident inspector has been notified of this event and that offsite agency notifications are planned." "STPNOC will be notifying the Texas Bureau of Radiation Control and the Matagorda County Judge of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-05-23
38938 | 0 | SCHLUMBERGER |  |  |  |  | 2002-05-23 13:00 | 2002-05-23 17:35 | 2002-05-23 | DISCOVERY THAT A 1.7-CURIE CESIUM-137 LOGGING SOURCE HAD BEEN UNSHIELDED ON A RIG FLOOR IN EASTERN MONTANA FOR APPROXIMATELY 48 HOURS RESULTING IN EXPOSURE TO RIG, CASING, AND CEMENT CREW MEMBERS At approximately 1615 CDT, the Schlumberger Radiation Safety Officer was notified by a field location in Williston, North Dakota (an agreement state), of an incident at a job location in Eastern Montana (not an agreement state) involving a 10-year-old, 1.7-curie (nominal), cesium-137, logging source. It was reported that the source had been outside of its source shield for a period of approximately 48 hours. There is a number of members of the public that have been exposed to this source. It appears that the logging engineer failed to properly make the transfer of the source from the logging tools into the shield, and it is believed that the source was left on the rig floor. After the licensee's crew left, it is suspected that rig crew members and possible casing and cementing crew members may have wandered in and out of the applicable area for various amounts of time. These individuals were not badged, and are being considered by the licensee to be members of the public. When the logging job (well) was finished, the rig was moved about 5 miles to the next lease (which is where the source is presently located). The rig has been sitting at the new lease site unoccupied for 12 to 15 hours. The source, which is approximately 3/4 of an inch long and approximately 3/4 to 1 inch in diameter, was discovered to be missing today at approximately 1300 CDT when licensee representatives were preparing for another job. The source has since been located, and licensee representatives are currently in the process of getting it back into the proper shield and proper storage. The licensee also plans to contact Pan Canadian (the client) to identify rig crew members in order to conduct interviews with all of the individuals on the rig from the time that the Schlumberger crew left until the time the rig was parked at the new lease location (unmanned). (Call the NRC operations officer for licensee contact telephone numbers.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2002-05-23
38937 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2002-05-23 10:30 | 2002-05-23 17:31 | 2002-05-24 | AGREEMENT STATE REPORT REGARDING A REPORTED MISADMINISTRATION At approximately 1030 CDT, the Oklahoma Department of Environmental Quality (DEQ) received a call from a consultant , and the consultant reported that a cardiologist had called him. Apparently, a radioactive isotope (technetium-99m) had been injected by a Nuclear Medicine Technician to image a breast. However, according to the consultant, the license that the cardiologist was on did not authorize breast imaging. According to the consultant, the technician was out for knee surgery and would not be back until 05/28/02. The consultant gave a very vague hospital name which could not be identified in the license files. However, the State searched under the doctor's name in the Board of Medical Licensure, and the doctor is affiliated with the Heart Clinic in Edmond, Oklahoma. The State DEQ stated that although the doctor's practicing privileges are at the Heart Clinic, the Heart Clinic does not have a license. The State DEQ plans to perform an investigation at the Heart Clinic tomorrow (05/24/02). The consultant estimated that this event involved an administration of 4 to 6 millicuries of technetium-99m. The consultant stated that the physician learned about this on Monday (05/20/02) and that the injection happened some time prior to that date. (Call the NRC operations officer for a state contact telephone number and the cardiologist's name.) ***** UPDATE AT 1528 EDT ON 05/24/02 FROM MIKE BRODERICK TO LEIGH TROCINE ***** The state performed an investigation today and called to provide additional clarifying information. The license (OK-27669-01) is written to the cardiologist, and the cardiologist/physician is doing business as the Heart Clinic. The cardiologist is also the owner of the clinic. The physician was only licensed for cardiac treatments, and the treatment in question involved a breast scan. The facility was not licensed to perform the breast scan, and the breast scan was not prescribed by a physician. Apparently, a patient did not show up for a cardiac treatment, and the Nuclear Medicine Technician (a certified Emergency Medical Technician) took the initiative to give the dose to another individual for a breast scan rather than waste the technetium-99m dose. The individual that received the breast scan has since taken the scan results to the women's clinic of the hospital. It was reported that the cardiologist informed the consultant who in turn notified the State. The NRC operations officer notified the R4DO (Linda Smith), NMSS EOs (Fred Brown and Tom Essig), and DIRO (Nader Mamish). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2002-05-30
38936 | 0 | CONSUMERS ENERGY COMPANY |  |  |  |  | 2002-05-23 | 2002-05-23 15:41 | 2002-05-23 | 10 CFR PART 21 NOTIFICATION REGARDING THE SALE OF CONSUMERS ENERGY COMPANY MIDLAND UNIT 2 REACTOR PRESSURE VESSEL HEAD FOR USE AT DAVIS BESSE (Call the NRC operations officer for Consumers Energy Company contact information.) The following text is a portion of a facsimile received from Consumers Energy Company: "Consumers Energy Company (Consumers) has entered into an agreement with Framatome ANP, Inc. (FRA-ANP) and First Energy Services Company, for itself and as agent for First Energy Nuclear Operating Company, The Illuminating Company, and Toledo Edison Company (collectively 'First Energy'), to sell the Midland Unit 2 reactor pressure vessel (RPV) head to FRA-ANP for use at the Davis-Besse Nuclear Power Station. Upon consummation of that agreement which applied 10 CFR Part 21 to the transaction, Consumers determined that a conservative reading of 10 CFR Part 21 indicated that there could have been 'failure to comply' within the meaning of 10 CFR Part 21, e.g., because since 1986 when Midland Unit 2 was cancelled, the RPV head has not been maintained in accordance with the requirements of 10 CFR Part 50, Appendix B, 'Quality Assurance Criteria for Nuclear Power Plants and Fuel Reprocessing Plants.' Consumers is not in a position to make a definitive finding as to whether a substantial safety hazard was created. [...] This [information is] submitted by Consumers to fulfill the requirement for a written report to provide the information requested by 10 CFR § 21.21(d)(4)." "Also, in an abundance of caution, in accordance with 10 CFR § 21.21(b), Consumers has informed FRA-ANP and First Energy that Consumers does not have the capability to perform an evaluation to determine whether any deviation relating to the Midland Unit 2 RPV head exists." "Consumers understands that FRA-ANP and First Energy, as the purchasers, will conduct any evaluation required pursuant to 10 CFR § 21.21(b) and undertake any needed corrective action." "REPORT MADE PURSUANT TO 10 CFR § 21.21 BY CONSUMERS ENERGY COMPANY [on] May 23, 2002" "[...] (ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. [...] Consumers Power Company (now Consumers Energy Company) ('Consumers') was the holder of Construction Permits CPPR-81 and CPPR-82 for the Midland Plant, Units 1 and 2 ('Midland'), Docket Nos. 50-329 and 50-330. The units were cancelled on July 1, 1986, and the construction permits were revoked on December 18, 1986. Prior to that time, Consumers had procured a number of components for that facility in accordance with a quality assurance program meeting the requirements of 10 CFR Part 50, Appendix B. Among such components was a reactor vessel head for Midland Unit 2. As Consumers did not intend to operate the Midland units, it abandoned a number of components in-place, terminated its quality assurance program for Midland, ceased applying the requirements of Appendix B to components it had procured for Midland, and did not systematically retain records associated with the vessel head, including its procurement, any nonconformances or any corrective actions. Since that time, the vessel head has not been maintained in accordance with a Quality Assurance Program." "In May 2002, Framatome ANP, Inc. on behalf of First Energy Nuclear Operating Company agreed to purchase the Midland vessel head for possible use at the Davis-Besse facility. Inasmuch as the vessel head meets the definition of 'basic component' contained in 10 CFR § 21.3 as it is a component that affects a nuclear power plant's safety function necessary to assure the integrity of the reactor coolant pressure boundary, the procurement document specified that the provisions of Part 21 apply." "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. [...] Consumers is supplying the basic component which fails to comply and which may contain a defect." "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. [...] Consumers did not maintain the vessel head under a Quality Assurance Program and does not have records regarding the serviceability and suitability of the vessel head at another nuclear facility, e.g., the suitability of design, the quality assurance program under which it was designed, constructed, handled, shipped and stored, procurement document control, whether the components met their procurement documents, whether appropriate inspections were conducted and the results, whether materials were controlled, and the adequacy of any corrective action. Consumers presently does not have the expertise necessary to assess the consequences of this condition and whether the reactor vessel head has any defect and does not know the circumstances of its intended use at the buyer's facility." "(v) The date on which the information of such defect or failure to comply was obtained. [...] This situation arose on May 22, 2002, the date which the procurement document specified the applicability of Part 21." "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part. [...] The report only applies to the reactor vessel head being procured for possible use at the Davis-Besse facility." "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. [...] Consumers has notified the purchaser pursuant to 10 CFR § 21.21(b) that it does not have the capability to perform the evaluation to determine if a defect exists. The purchaser has agreed to evaluate this condition and make a determination on the suitability of the reactor vessel head for its potential intended use and any required corrective or other necessary actions, including its reportability." "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. [...] None." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MI | OTH | PAR | 21.21 |  |  |  | 0 | 2002-05-23
38935 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-05-21 10:00 | 2002-05-22 17:49 | 2002-05-22 | STOLEN HUMBOLDT GAUGE CONTAINING CESIUM-137 AND AMERICIUM-241 THAT WAS LATER RECOVERED On May 21, 2002, a Humboldt 5001EZ gauge was stolen between the hours of 1000 hours and 1200 hours from a truck parked behind the Licensee's office, HVJ Associates, Inc. located in Austin. The gauge was discovered missing at 1230 hours and was later found at 1400 hours. The gauge was found by security at a local shopping plaza. The gauge was secure inside the yellow container on the ground near a dumpster. The shielding remained intact and no one was exposed to the excessive radiation levels. The local police had been notified of the gauge being stolen. The serial number for the Humboldt gauge is 3776. No media attention. Texas Incident No. I-7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-05-28
38934 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2002-05-03 15:40 | 2002-05-21 18:59 | 2002-07-02 | UNANALYZED CONDITION THAT SIGNIFICANTLY DEGRADED PLANT SAFETY On May 3, 2002, approximately 20 gallons of water was spilled on the floor of the cable spreading room (CSR). Some of the water leaked down into rooms below the CSR floor, resulting in an electrical ground on the on the 125-VAC Division 2 battery bus S1-2. The S1-2 bus remained operable. It has since been determined that the pathway for leakage through the floor of the CSR was cracks in the concrete due to abandoned concrete anchors, and through shrinkage cracks in the reinforced concrete floor slab. Shrinkage cracks are also located in the 525' elevation floor above the Control Room. These two floors are considered essential fire rated assemblies and are required to be "leak tight". These floors have not had a qualified paint/sealant applied that would render them "leaktight". Other floors that are fire rated assemblies are believed to have had the appropriate paint/sealant applied, but this is being verified. Should a fire system actuate, or develop a leak in either the CSR or the room above the Control Room, there is the potential for leakage through the floors to impact Division 1 or 2 safety-related equipment in the rooms below. A barrier impairment has been initiated for the CSR on May 6, 2002 and for the 525' elevation above the Control Room on May 7, 2002 with compensatory action to include these areas on an hourly fire/flood tour. With the hourly fire/flood tours in place, the floors of the CSR and the room above the Control Room have been declared "operable but degraded" per formal assessment of operability, and no longer represent an unanalyzed condition that significantly degrades plant safety. The cracks associated with the abandoned anchor bolts have been sealed. Hourly fire/flood tours remain in effect until both floors have been properly sealed. The NRC Resident Inspector has been notified of this event. * * * RETRACTED AT 1600 EDT ON 7/2/02 BY BOB BROWNLEE TO FANGIE JONES * * * The licensee is retracting this event notification. It was originally postulated that due to the prevalence of unsealed concrete cracks, a design basis flooding scenario would create a significant amount of water leakage into critical equipment rooms below the floors. After further evaluation it has been concluded that flooding events in either room would result in minimal leakage into rooms below, and therefore this condition can not be characterized as an unanalyzed condition that significantly degrades plant safety. The CSR floor and the room above the Control Room are "operable but degraded." Hourly fire/flood tours will remain in effect until both floors have been properly sealed. The cracks responsible for the observed leakage for this event have been sealed. Columbia Generating Station will submit a voluntary Licensee Event Report on this issue due to its generic interest to both the NRC staff and the nuclear industry. The licensee notified the NRC Resident Inspector. The R4DO (Dale Powers) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-05-21
38933 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-05-20 15:30 | 2002-05-21 15:52 | 2002-05-21 | FIRE PROTECTION CARBON DIOXIDE IN SAFETY RELATED AREAS REPORTED UNDER FIRE PROTECTION LICENSE CONDITION 2.C.X Tracer gas testing was being performed for the following fire areas at Salem Unit 1 and Unit 2: (1) Unit 1 EL. 78 Lower Electrical Penetration Area (2) Unit 1 EL. 64 4160V Switchgear Room (3) Unit 2 EL. 78 Lower Electrical Penetration Area The tracer gas test, along with a door fan test were being performed to determine actual field conditions for inclusion in a re-analysis of the carbon dioxide fire suppression system for these areas. At 1730 hours on 05/20/02, preliminary results were obtained for tests 1 and 2 above that indicated a significant amount of leakage through the ventilation control dampers in these areas that would prevent the carbon dioxide system from achieving the required concentration of 50% and a hold time of 20 minutes as required by NFPA-12. The results for Test 3 have not been completed but identify a similar condition for the Unit 2 Lower Electrical Penetration Area. The problem with leakage from these fires areas appears to be from a high differential pressure across the ventilation dampers that close on a carbon dioxide discharge, however, the ventilation fans continue to operate. Based on this information, the Unit 2 4160 VAC Switchgear Room, the Unit 1 460 VAC Switchgear Room and the Unit 2 460 VAC Switchgear Room have a similar configuration on carbon dioxide actuation and will most likely not meet the 50% concentration requirement. As a result, the carbon dioxide system for all six areas above were impaired and continuous fire watches were established. Although air leakage from the ventilation supply and exhaust dampers affects the ability to achieve or maintain the carbon dioxide design concentration in accordance with NFPA-12, the carbon dioxide discharge into the room still provides a fire suppression function. Automatic early warning (ionization) fire detection will alert the dedicated onsite fire brigade, who will respond and extinguish any fire using manual fire suppression methods. The fire brigade can manually activate an additional carbon dioxide system discharge. Based on the above, there is reasonable assurance that the plant can achieve and maintain safe shutdown. Failure to meet the carbon dioxide concentration in all six of these areas is a violation of the Fire Protection Program License Condition 2.C.5 (Unit 1) and 2.C.10 (Unit 2). Failure to meet Unit 2 License condition 2.C.10 requires a 24-hour report accordance with Unit 2 License Condition 2I and a follow-up 14 day special report. The NRC Resident inspector will be notified of this event by the licensee. | 0 | 98 | 0 |  | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2002-05-21
38932 | 0 | GME CONSUTANTS |  |  |  |  | 2002-05-20 10:00 | 2002-05-20 14:57 | 2002-05-20 | DAMAGED MOISTURE DENSITY GUAGE AT CONSTRUCTION SITE A construction vehicle ran over a CPN moisture density guage, model number MC3. The radiation safety officer responded to the site. Radiological surveys were performed and the damaged guage was collected in an appropriate container. The guage was then returned to the licensee storage facility where it will be shipped out for repair. The guage was closed and locked at the time of the event. No personnel contaminations were reported. The guage contained less than 50 millicuries of AM-241 and less than 10 millicuries of CS-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-05-20
38931 | 0 | GILES ENGINEERING |  |  |  |  | 2002-05-20 09:30 | 2002-05-20 12:30 | 2002-05-20 | DAMAGED MOISTURE DENSITY GAUGE AT CONSTRUCTION SITE IN WISCONSIN The licensee reported that a moisture density guage was damaged when a construction vehicle accidentally ran over the guage. The gauge was manufactured CPN and was model number MC1DR. The guage contained 10 millicuries of CS-137 and 50 millicuries of AM-241-BE. The company radiation safety officer responded to the site and established a 75 foot exclusion area. Surveys revealed no release of radioactive materials. The guage was in the safe position with the ram in the lead shield. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-05-20
38930 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-05-20 05:00 | 2002-05-20 05:43 | 2002-05-20 | PLANNED MAINTENANCE RESULTING IN THE LOSS OF AN EMERGENCY RESPONSE FACILITY FOR THE DURATION OF THE EVOLUTION The following text is a portion of a facsimile received from the licensee: "During performance of planned maintenance, the Emergency Operation Facility (EOF) will be de-energized. These maintenance activities, including electrical isolation and restoration, are expected to last approximately 16 hours. Contingency plans for emergency situations have been established." "This event is reportable per 10CFR50.72(b)(3)(xiii) since this constitutes a loss of an emergency response facility for the duration of the evolution." "The NRC Resident was previously notified that this activity was scheduled to occur and will be informed of this ENS notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-05-20
38929 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-05-19 16:00 | 2002-05-19 20:59 | 2002-05-19 | GREATER THAN 1% OF STEAM GENERATOR 1-2 TUBES ARE DEFECTIVE On May 19, 2002, during the Unit 1 eleventh refueling outage, analysis of eddy current data on steam generator (SG) 1-2 indicated that greater than one percent of the total tubes inspected on SG 1-2 were defective. Thirty-six (36) defective tubes in SG 1-2 were detected and are being plugged. Most of the pluggable indications are due to outside diameter stress corrosion cracking at the tube support plate intersections. Review of the eddy current inspections are complete. Results of the SG tube inspection fall into Category C-3, which requires a 4-hour non-emergency report in accordance with Technical Specification Table 5.5.9-2 and 10 CFR 50.72(b)(3)(ii) an 8-hour requirement. The other three SGs' tubes have been checked. An NRC teleconference in accordance with Technical Specification 5.6.10.d to report the results of the voltage-based repair criteria implemented for the tube support plate intersections is currently scheduled for Monday May 20, 2002, at 1230 hours EDT. The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-05-19
38928 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-05-19 04:47 | 2002-05-19 06:03 | 2002-05-19 | MANUAL REACTOR TRIP DUE TO A CONTROL ROD SYSTEM URGENT FAILURE ALARM DURING LOW POWER PHYSICS TESTING While in Mode 2 (Startup) with reactor power at 10E-6 in the intermediate range as part of a refueling outage, Unit 2 was manually tripped at 0447 EDT on 05/19/02. During the performance of low power physics testing, the unit experienced a control rod system urgent failure alarm. Operators were inserting Shutdown Bank 'B,' and the Shutdown Bank 'B' Group 2 step counter failed to step. Rod movement was stopped. After performance of an evaluation, operators noticed that reactivity was increasing slightly. Operators then attempted to insert Control Bank 'D,' and the Control Bank 'D' Group 2 step counter also failed to step. After evaluating rod control problems, the reactor was manually tripped. All control rods fully inserted as a result of the manual reactor trip, and all systems functioned as required. There were no engineered safety feature actuations or emergency core cooling system injections, and none were required. The licensee currently suspects that there may be a blown fuse in the rod control cabinet. The investigation is currently underway. The unit is currently stable in Mode 3 (Hot Standby). Normal charging and makeup, pressurizer heaters and sprays, and the reactor coolant pumps are being utilized for primary system inventory, pressure, and transport control. Main feedwater is supplying water to the steam generators, and secondary steam is being dumped to the condenser. Containment parameters are also normal. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-05-19
38927 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-05-19 00:54 | 2002-05-19 03:33 | 2002-05-19 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP FOR UNKNOWN REASONS The following text is a portion of a facsimile received from the licensee: "[A] Unit-1 reactor scram occurred at 0054 hours on May 19, 2002. The reactor scram occurred as a result of a main turbine trip. The cause of the turbine trip is under investigation. All systems actuated as designed. The unit is being maintained in Hot Shutdown at normal [reactor pressure vessel] level. This report is being made pursuant to [10 CFR] 50.72(b)(2)(iv)(B) due to actuation of the reactor protection system (RPS). No [safety relief valves] lifted, and currently [one] reactor recirculation pump has been restarted[. The] scram has been reset." The licensee stated that reactor vessel level control is currently being maintained via normal condensate and feedwater. The main steam isolation valves are open, the condenser is available as a heat sink, and reactor vessel pressure control is being maintained via normal electrohydraulic control pressure control. Containment parameters are normal. The licensee also stated that the all control rods fully inserted, that there were no engineered safety feature actuations or emergency core cooling system injections, and that none were required. There was nothing unusual or not understood with the exception of the cause of the turbine trip. Prior to this event, the unit had been operating at reduced power to facilitate the performance of turbine stop valve testing. The licensee stated that a combined intermediate valve (CIV) was being stroked at the time of the turbine trip/reactor scram but that stroking of the CIV is currently believed to be unrelated to the turbine trip. At this time, the licensee believes that the cause of the turbine trip may have been related to the thrust bearing wear detector. However, the final root cause of the turbine trip remains under investigation. The licensee notified the NRC resident inspector, applicable State and local agencies (including Montgomery, Chester, and Berks Counties), and the Pennsylvania Emergency Management Agency. | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-05-19
38925 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-05-17 11:30 | 2002-05-17 14:55 | 2002-05-17 | EP SIREN INADVERTENTLY ACTUATED FOR ONE MINUTE PROMPTING AN OFFSITE NOTIFICATION "A South Texas Project Offsite Emergency Notification siren was inadvertently going off. The Matagorda County Sheriffs office notified the station a siren had activated for approximately 1 minute. This happened at the same time a thunderstorm was moving through the area. Onsite personnel have verified the sirens are operational and in a standby condition. The Matagorda County Sheriffs office was the only offsite agency that was contacted during this event." The NRC Resident Inspector was notified. | 100 | 1 | 0 | 100 | 1 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Startup |  | Power Operation | Startup |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-05-17
38923 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-05-16 | 2002-05-16 18:29 | 2002-05-16 | AGREEMENT STATE REPORT ON MEDICAL MISADMINISTRATION "[ ]Med. Physicist called on the date of this memo. It was regarding the placing of 111 seeds [of I-125] when the prescribed dose was 110 seeds. Per the physicist he could not see the additional seed because of the blood. After doing a source count he believes the additional seed was implanted into the patient. The additional seeds activity was 0.33 mCi. Additional information will follow." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-05-21
38922 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-05-15 11:00 | 2002-05-16 17:25 | 2002-05-16 | AGREEMENT STATE REPORT INVOLVING THEFT OF LICENSED MATERIAL >1000 TIMES "At 11:00 am PDT on May 15, 2002, four packages were stolen from an unsecured Airborne Express truck parked at 39 Congress Avenue, Pasadena, Ca. Due to a mix-up by the driver, it was not known that one of the packages contained radioactive material until the next day, when Huntington Memorial Hospital's Radiation Safety Officer[ ], realized that they had not received one of the packages of Palladium-103 seeds that they were expecting. [The RSO] reported the loss to the California Radiologic Health Branch at 12:15 PM PDT on May 16, 2002. "The package was supposed to have contained 72 seeds at 1.54 mCi/seed, or a total of 110 mCi of Pd-103, which would produce a field of about 230 mR/hr at one foot from the unshielded material. "Los Angeles County personnel took the initial call from the hospital, and is following up on this incident. Los Angeles County is a Contract County in California's Agreement State Program. The L.A. County inspector talked to the hospital about issuing a press release, and they are currently preparing one. The inspector will also obtain information on the package dose-rates, when it was shipped by Imagyn in TX, and the calibration dates for the seeds.. The seeds were purchased from Theragenics, shipped to Imagyn for some preparation, then shipped to the California licensee in two packages. The first package was received in tact. The second was stolen from the Airborne Express truck. There has been no indication by any of the parties that the other three packages stolen contained any radioactive material." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-05-21
38921 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-05-13 05:15 | 2002-05-15 15:30 | 2002-05-15 | LATE DECLARATION OF AN UNUSUAL EVENT FOR TORNADO The licensee reported that on May 13, 2002, the national weather service issued a tornado warning for Central Ocean County, NJ. The Oyster Creek Station was within the tornado warning area. At 15:30 on May 15, 2002, the licensee determined that an Unusual Event should have been declared. No tornados were sighted nor did the conditions affect safe station operation. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2002-05-15
38920 | 0 | SOLIDSTATE CONTROLS, INC |  |  |  |  | 2002-04-15 | 2002-05-15 15:07 | 2002-05-15 | 10 CFR 21 NOTIFICATION-POTENTIAL DEFECT INVOLVING FAN ASSEMBLIES FOR UPS SYSTEMS "The attached 10 CFR Part 21 record, Attachment A, is submitted to report a potential for a defect in fan assemblies used in Uninterruptible Power Systems manufactured under the Solidstate Controls, Inc., 10CFR50 Appendix B Program. "Nature of the defect: "PROBLEM SEEN: The above assembly contains a component part - an aluminum, five-wing fan blade, which potentially could separate from the hub. If the blade should come loose there may not be an alarm indication of loss of cooling. Additionally, the loose blade may cause a short circuit if it falls into the equipment and should land across opposing current carrying devices. "CAUSE: We have determined that one fan blade style from one specific manufacturer of part number 03-470100-00 could, under certain conditions, separate from its hub. "EFFECT ON SYSTEM PERFORMANCE: Fan Assembly - THE SEPARATION OF THE BLADE FROM THE HUB COULD CAUSE THE SYSTEM TO DROP POWER TO THE LOAD. If the worst case failure mode described above were to occur, it would result in the motor continuing to operate, thereby, not allowing the internal alarm mechanism to activate. Further, the blade itself could fall into the operating equipment causing a short circuit. It is important to note that the short circuit situation has not been reported. "US NUCLEAR PLANT IMPACTED BY THIS ACTION: There are approximately 30 plants listed" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2002-05-15
38919 | 0 | ABB, INC. |  |  |  |  | 2002-05-14 | 2002-05-14 08:05 | 2002-05-14 | NOTIFICATION OF A POTENTIAL DEFECT REGARDING K-LINE MECHANISM FAILURES TO CHARGE AND CLOSE The following text is a portion of a facsimile received from ABB, Inc.: "In August of 2001, Southern California Edison, San Onofre Nuclear Generating Station, reported and submitted an operating mechanism for evaluation to the ABB, Inc., Florence, SC Breaker Manufacturing Facility due to suspected shipping damage causing 'failure to charge' symptoms. The mechanism was a special configuration of the base 709774 Model '05' mechanism manufactured in 10/1997. This mechanism was in a Nuclear Safety-Related application. The mechanism was received by the factory in September of 2001, and the reported failure mode was not duplicated in Florence. However, under the auspices of a 'refurbishment,' ABB, Inc., personnel performed an evaluation of critical characteristics for parts that could be contributory to the failure mode described herein." "On 7 February 2002, Ameren - Union Electric's Sioux Generating Plant reported a failure to charge and close of a Model '05' K-Line K-600S circuit breaker (Serial Number 935461B--010496) manufactured 04/96. This breaker was purchased for a Non-1E application. The cause of the breaker failure was determined to be a culmination of energy utilization deficits. Specifically, the condition of lubricant (Anderol 757), the surface and finish of parts critical to the charging operation, and the interaction of critical latching surfaces serve to impede the ability of the mechanism to fully charge through the end of the charge cycle." "In March 2002, Dominion Virginia Power's Surry Nuclear Station reported the failure to charge and close of a 1993 K-800M (Serial Number 865613B033--010793). In this case the breaker was refurbished in the hopes of alleviating the symptoms, only to find they returned a short time after return to service. ABB, Inc., had already initiated Part 21 reporting proceedings as this latest failure was announced, and the Florence Breaker Manufacturing Facility is awaiting a customer report to verify the failure mode." "In all cases, the end user is observing a failure to charge and/or close in electrically operated mechanisms. These failures are due to one of the following two scenarios:" "1. A failure to charge and close, either mechanically or electrically, until the needed energy is supplied to rotate the charging cam over the center-point into a fully charged position -- either by mechanical vibration or operator rotation of the charging cam." "2. A failure to close where the above scenario does not exist but the fully charged mechanism does not close due to the fact that the primary close latch does not fully clear in response the secondary close latch actuation." "With the introduction of the Model '07' mechanism in December 1998, while maintaining backward compatibility with pre-existing models, ABB has facilitated improvements to be incorporated into every mechanism that is built at the Florence Breaker Manufacturing Facility. ABB recognizes that this failure mode may exist in any K-Line circuit breaker manufactured or having undergone mechanism repair, refurbishment, or replacement between January 1, 1988 and December 31, 1998 and, therefore, recommends that utilities address this issue at the next available maintenance interval. This includes any 'spare' K-Line mechanisms manufactured during the afore determined time frame that may be in stock." "Three equally viable options are available to rectify this situation. They are, listed in order of ABB preference, most desirable first:" "1. Replacement of suspect K-Line operating mechanism (ABB part number 709774T##) with a Model '07' mechanism (ABB part number 716785T##). This option will require the purchase of an Engineering Qualification Report Addendum so that 1E dedication traceability is maintained." "2. Upgrade of suspect K-Line operating mechanism to a Model '07' mechanism utilizing one of ABB upgrade kits, numbers 716659T03 through T10. This option will require the purchase of an Engineering Qualification Report Addendum so that 1E dedication traceability is maintained." "3. Improvement of suspect K-Line operating mechanism within the original model class utilizing ABB repair kit number 716659T01 or T02." "Work required by the options listed above should only be performed by personnel trained and/or authorized by ABB, Inc. ABB is available to perform the work in the Florence, South Carolina, factory or perform in-factory training if non-ABB personnel are to be used or contracted." "Note: If work associated with options 2 or 3 above is performed by personnel outside of the Florence, SC factory, one minor configuration change must be noted. During mechanism re-assembly, technicians must relocate the washer (ABB part number 650351A57) from its original location on the control device side on the Primary Close Latch Pivot Pin (ABB part number 702883D00) to the charging motor side." "ABB [plans to] notify all Nuclear Utility Companies." Call the NRC operations officer for ABB, Inc., contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2002-05-14
38918 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-05-13 00:25 | 2002-05-13 15:49 | 2002-05-13 | OPERATING LICENSE REPORT OF SIGNIFICANT ELECTRICAL TRANSIENT DUE TO LIGHTNING STRIKE "On May 13, 2002, at 0025, Hope Creek Generating Station experienced a significant electrical transient as a result of lightning strike that caused the trip and re-closure of the New Freedom Line. "The most significant impact was the loss of Feedwater Heating Transient due to the trip of the 6A, 6B, and 6C Feedwater Heaters. This Feedwater trip resulted in a peak transient power level of 105% power. "Hope Creek Generating Facility Operating License (NPI-57) item 2.C(1) specifically authorizes operation of the facility not in excess of 3339 megawatts thermal (100%). "Additionally, Operating [License] Item 2.C(11) prohibits operating the facility with Feedwater Heater capacity that would result in a rated power Feedwater Heater temperature less than 400 degrees. "Both of these Operating License conditions were challenged during this transient and are reportable IAW section 2F of the Operating License. "Station power was manually reduced and subsequently stabilized at approximately 75% to deal with the transient, and the Feedwater Heaters were restored to service. "Additional equipment affected as a result of the electrical transient is as follows: 'C' ECCS keep fill Jockey pump tripped; Hydrogen Water Chemistry Injection system tripped; the North and South plant Ventilation Radiation Monitoring system tripped; the Drywell Leak Detection system tripped; Cooling Tower Blowdown Radiation Monitor tripped; the 'B' 1E Panel room Ventilation Train tripped and the standby 'A' train started; the 'A' Control Room Ventilation train tripped and the 'B' train auto started. The unit sustained a loss of Drywell cooling, and the 'B' Fuel Pool Cooling Pump tripped. The RWCU system pumps tripped. "The plant is stable, and the event is under investigation." The NRC Resident Inspector has been notified. | 72 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2002-05-13
38917 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-05-13 11:18 | 2002-05-13 15:04 | 2002-05-13 | FITNESS-FOR-DUTY REPORT A contract supervisor tested positive for drug use during a follow-up test. The individual's site access has been terminated. Contact the NRC Operations Center for additional information. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Hot Standby |  | Refueling | Hot Standby |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2002-05-13
38916 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2002-05-13 00:16 | 2002-05-13 03:21 | 2002-05-13 | AUTOMATIC REACTOR SCRAM ON HIGH WATER LEVEL DUE TO THE FAILURE OF THE STARTUP LEVEL CONTROLLER DURING EXTENDED POWER UPRATE TESTING ON FEEDWATER LEVEL CONTROL The following text is a portion of a facsimile received from the licensee: "With the reactor at 86% power, extended power uprate testing on feedwater level control was in progress. A six-inch level step change from 32" to 38" was inputted for testing. Feedwater was being controlled by the startup level controller. The startup level controller failed to respond, allowing reactor water level to go high and cause a reactor scram on level 8, 52". All other systems responded normally." The licensee stated that all control rods fully inserted due to the automatic reactor scram and that the highest reactor water level was 53". There were no safety injections or emergency core cooling system actuations, and none were required. The licensee stated that the unit is currently in Hot Shutdown. Normal feedwater is being supplied to the reactor vessel for level control, and pressure is being controlled via the main steam line drains which go to the condenser (the heat sink). The outboard main steam isolation valves were manually closed. Containment parameters are normal. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-05-13
38915 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-05-12 23:01 | 2002-05-13 02:39 | 2002-05-14 | AUTOMATIC REACTOR TRIP DUE TO AN INSTRUMENTATION RACK POWER SUPPLY FAILURE WHICH CAUSED A STEAM GENERATOR FEEDWATER REGULATING VALVE TO FAIL CLOSED The following text is a portion of a facsimile received from the licensee: "DC Cook Unit 2 tripped from full power due to an instrumentation rack power supply failure on 05/12/02 [at] 2301. All control rods fully inserted. No Safety Injection was required. The Unit 2 Reactor is stable and subcritical. The Steam Generator Stop Valves were manually closed by the Operating Crew to stabilize RCS Temperature in accordance with Plant operating procedures. Reactor Coolant Temperature is being maintained manually on the Steam Generator Atmospheric relief valves at No-Load T(ave) in accordance with plant procedures." "This instrumentation rack power supply failure caused the #21 Steam Generator Feed Regulating Valve to fail CLOSED. The Unit 2 Reactor subsequently TRIPPED on Low Level in [the] #21 Steam Generator coincident with Low Feedwater Flow. Several control systems were affected by the control rack instrumentation failure: Pressurizer Pressure Control - transferred control to manual and restored Pressurizer pressure, Pressurizer Level Control - transferred control to manual and restored Pressurizer water level, Refueling Water Sequence - Manually transferred Charging Pump Suction to the RWST. Manual Operator response maintained and restored critical plant parameters in MANUAL to normal parameter values." "Unit 2 entered Technical Specification 3.0.3 for 34 minutes because the control system failures and plant system response temporarily caused the Boration Flow paths from both the Refueling Water Storage Tank and Boric Acid Storage Tanks to become INOPERABLE. Both Boration flow paths were subsequently returned to OPERABLE status by manual Operator action." "The Reactor trip is reportable in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an actuation of the Reactor Protection System (RPS) when the Reactor was critical. The Reactor TRIP was the result of an instrumentation rack power supply failure and was not part of any preplanned test or evolution." The licensee stated that the unit is currently stable in Mode 3 (Hot Standby). The reactor coolant pumps are available for primary system transport control. Pressurizer level and pressure control are in manual. Normal charging and makeup are available, but the automatic function of the refueling water sequence is not available. The auxiliary feedwater pumps automatically started as expected and are currently being utilized to supply water to the steam generators. Secondary steam is being dumped to atmosphere. There is no evidence of steam generator tube leakage, and containment parameters are as expected. There were no safety injections and none were required, and none of the primary power-operated relief valves lifted. The licensee notified the NRC resident inspector. ****UPDATE 5/14/02 At 13:20 From B. Bates To R. Laura**** The initial report stated that the reactor coolant temperature is being maintained manually on the steam generator atmospheric relief valves at no-load Tave in accordance with plant procedures. Temperature control was actually established in automatic on the steam generator atmospheric relief valves and remains in automatic. A statement was made in the original report that Unit 2 entered Technical Specification 3.0.3 for 34 minutes. Upon further review, there was no requirement to enter Technical Specification 3.0.3. The control system failures and plant system response caused the boration flowpaths from both the Refueling Water Storage Tank (RWST) and Boric Acid Storage Tanks to become inoperable. Therefore, the Unit was actually in Technical Specification 3.1.2.2 actions (a)and (b) concurrently. This did not constitute an entry into Technical Specification 3.0.3 because entry into both actions is not prohibited. Another statement was made that both boration fiowpaths were subsequently returned to operable status by manual operator action. The boration flowpath from the boric acid storage tanks was returned to operable. However, after further investigation, it was determined that the boration flow path from the RWST remained inoperable due to the inability of the refueling water sequence to automatically initiate. The NRC Resident Inspector was notified. Notified R3DO R. Gardner. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-05-13
38912 | 0 | WATERFORD | 3 |  |  | [3] CE | 2002-05-09 14:30 | 2002-05-10 14:20 | 2002-05-10 | LICENSE CONDITION VIOLATION OF THERMAL POWER AT WATERFORD 3 "During initial installation of the LEFM Check-Plus ultrasonic feedwater flow measuring system installed as part of the Appendix K Power Uprate Project at Waterford 3, it was noted that the three available reactor core calorimetric thermal power indications calculated by the Core Operating Limits Supervisory System (COLSS) were not in agreement. This disagreement was noted on 4/20/02. These thermal power indications consist of: Main Steam venturi Secondary Calorimetric (MSBSCAL), Feedwater Flow venturi Secondary Calorimetric (FWBSCAL) and the Calorimetric indication generated by the newly installed LEEM Check-Plus ultrasonic flow measuring system (USBSCAL). The LEFM Check-Plus ultrasonic flow measuring system was certified for use on May 9, 2002. "Preliminary information indicates the mismatch in indication is likely the result of biases factored into the MSBSCAL indication as well as possible degradation of the secondary side of the plant over time since August 1997. These biases, based on the most accurate USBSCAL indication, are approximately 0.22% power beyond the accepted power measurement uncertainty of 1.68% power for the MSBSCAL. indication. Thus, Waterford 3 may have operated at average power levels in excess of the 100% licensed power limit since approximately August 1997. "Waterford 3 is currently in Mode 1 at 99.9% power using FWBSCAL, the most conservative indication of reactor power. This report is being made per Waterford 3 License Condition 2.F for potential violation of License Condition 2.C.1, "Maximum Power Level." The investigation for this condition is ongoing". The NRC resident inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2002-05-10
38911 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-05-09 17:50 | 2002-05-09 21:02 | 2002-05-09 | LOSS OF CONTROL ROOM HVAC AT DRESDEN "At 1750 hours on May 9, 2002 the B Control Room HVAC Refrigeration and Condensing Unit (RCU) would not stay running during surveillance testing. The B RCU is a single train system and therefore is reportable per SAF 1.8 & LS-AA-1400, Event Reporting Guidelines Section 3.2.7. The B RCU is required to operate during a design basis accident to remove the heat from the Main Control Room. The Air Filtration Unit (AFU) of CREVS remains operable. This places both units in a 30 day LCORA per Tech Spec 3.7.5. Required Action A. 1." Train "A" is not fully qualified but is available to maintain proper control room temperatures. The NRC Resident Inspector was notified. | 0 | 96 | 100 | 0 | 96 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-05-09
38909 | 0 | ROCKWELL AUTOMATION |  |  |  |  | 2002-05-09 | 2002-05-09 16:30 | 2002-05-17 | PART 21 ISSUE ON ELECTRIC MOTORS Rockwell Automations report a potential defect involving insufficient slot fill in electric motor windings used to drive fan assemblies. They have contacted Hayden Company located in New Philadelphia, Ohio who was supplied with these motors. The motors may be in use at commercial nuclear power plants. ***UPDATE Curt Pratt to Mike Norris 5/16/02 13:59 EDT*** This update listed the Licensees that have these motors: Davis Besse, Oconee and Braidwood. Notified NRR (Hodges) , Reg 2 RDO(Fredrickson) and Reg 3 RDO(Gardner). ****UPDATE J. Thigpen to R. Laura on 5/17/02 at 13:19 by fax***** The licensee identified 1 additional motor and the customer was the same as the others. Notified NRR (Hodges) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2002-05-09
38908 | -1 | GEORGE WASHINGTON UNIV. HOSPITAL |  |  |  |  | 2002-05-09 10:30 | 2002-05-09 16:25 | 2002-05-17 | PRELIMINARY ESTIMATED EXPOSURE OF 63 ROENTGEN TO THE HANDS OF A MEDICAL PHYSICIST While using a Cordis delivery system to insert a ribbon containing Ir-192 seeds into a patient, the ribbon came out into the hands of the Medical Physicist. The screw and cap of the Cordis delivery system had been loosened and the ribbon containing the Ir-192 seeds was supposed to be pushed into patient via a catheter but somehow the ribbon containing the Ir-192 seeds ended up in the hand of the Medical Physicist. George Washington Hospital Radiation Safety Officer preliminarily estimated the minimum exposure to the Medical Physicist hand was 63 roentgens. The Medical Physicist walked 5 or 6 feet into another room where the Radiation Oncologist was located and dropped the ribbon to the floor. The Radiation Oncologist, wearing gloves, picked the ribbon up and placed it in a safe location. The Radiation Safety Officer for George Washington Hospital said that the Radiation Oncologist received a dose to his hand while carrying the ribbon. An estimated dose calculation to Radiation Oncologist hands, etc., had not been made at the time of the notification. ****UPDATE ON 5/17/02 at 11:15 FROM A. CHOWDHURY TO R. LAURA**** Further licensee investigation revealed that an actual overexposure did not occur. The initial calculations of this event were too conservative. NRC Region 1 inspectors made a site visit to review this event. Notified R1DO (D. Holody) and NMSS (D. Cool). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 20.2202(b)(1) |  |  |  | 0 | 2002-05-09
38906 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-05-08 17:07 | 2002-05-08 18:43 | 2002-05-08 | REACTOR TRIP FROM 100% POWER ON STEAM GENERATOR LOW/LOW LEVEL SIGNAL A channel operational test of Tavg, delta T, and pressurizer pressure for protection set two was being performed by I&C technicians. While swapping steam generator level channels, they placed the "D" feedwater reg valve in manual per procedure. The feedwater reg valve failed closed and they attempted to manually open the valve, but there was no response. When they put the controller in automatic, the valve started to reopen, but the response was not fast enough and the reactor tripped on steam generator lo-lo level. The auxiliary feedwater actuated as designed and all rods fully inserted. No relief valves lifted. The licensee is investigating the cause of the valve malfunction. The NRC Resident Inspector was notified and the licensee will issue a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-05-08
38905 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-05-07 07:30 | 2002-05-07 09:58 | 2002-05-07 | OFFSITE EMERGENCY NOTIFICATION SIRENS DETERMINED TO BE INOPERABLE Emergency preparedness personnel identified that the Prompt Alert Notifications System (PANS) was inoperable. Troubleshooting and repair activities are ongoing for the system. The licensee has notified the local towns and compensatory measures are in place in event of emergency plan activation for public notification. The licensee has notified the NRC Resident Inspector and the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-05-07
38904 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2002-05-07 03:31 | 2002-05-07 05:41 | 2002-05-07 | SAFETY PARAMETER DISPLAY SYSTEM DETERMINED TO BE INOPERABLE "At 0331 hours on 5/7/02, the reactor operators determined that the Safety Parameter Display System was not being updated with data from the Plant Process Computer System. "This is being conservatively reported as a major loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). The control room board indications and annuciator system remain in service and are routinely used by the operators to monitor and assess the plant during normal and emergency situations." The computer group has been notified and will be investigating the problem. The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-05-07
38902 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-05-06 14:35 | 2002-05-06 15:34 | 2002-05-06 | MULTIPLE SIREN FAILURE The plant had multiple siren failures during the silent test of the Calvert County Public Notification and Alert System, more than 10 sirens failed. The cause is being investigated. An alternate method of public notification is available for use. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-05-06
38901 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-04-03 | 2002-05-06 13:58 | 2002-05-06 | OCCUPATIONAL RADIATION EXPOSURE EXCEEDED ANNUAL LIMIT On April 3, 2002, it was identified that a radiographer had received a total occupational exposure of 5.227 Rem Total Effective Dose Equivalent for the monitoring period of January 1, 2001 through December 31, 2001. While compiling Occupational Exposure Reports it was determined that the dose received by a radiographer was in excess of the limits allowed by RH 4.6.1.1.1. The Corporate Radiation Safety Department then notified the Denver Lab Manager of the findings. Exposure records have been reviewed to verify the accuracy of the reported exposure. It has been determined that the reported total is accurate as stated. The radiographer received an exposure of 5.227 Rem Deep Dose Equivalent, and 5.157 Rem Shallow Dose Equivalent for the period of January 1, 2001 through December 31, 2001. Throughout the monitoring period the radiographer worked at various jobsites. The isotope utilized to perform the radiography was Iridium 192. Varying curie strengths from 10 curies to 100 curies were used throughout the year. The root cause of the excessive exposure was due to a lack of attention paid to the cumulative exposure total by the Radiation Safety personnel and by the Radiographer. On August 1, 2001 CONAM Inspection switched to a new dosimetry processor. The result was two dosimetry reports, neither having a cumulative total for the year. The radiographer failed to notify his Radiation Safety Officer of the amount of his total exposure and his proximity to the annual limit. Additionally, the Radiation Safety Officer and the Corporate Radiation Safety Department failed to identify the radiographers proximity to the annual limit and remove him from radiographic activities. The following corrective actions and program enhancements have been made. The Corporate Radiation Safety Department has added a staff member to assist with the oversight of the radiation safety program All monthly exposures in excess of 420 mR now require an ALARA review. All monthly dosimetry reports are reviewed by the lab and by the corporate radiation safety departments to prevent this type of incident. CONAM Inspection intends to utilize our current dosimetry company for the remainder of the monitoring period eliminating the dual reports. The entire radiography staff has been informed of this incident. They have also been instructed of their responsibility to prevent this type of incident. The Radiation Safety Officer has been retrained on his responsibility to ensure that all employees are maintaining their exposure ALARA. When the results from the June monitoring period become available, any employee in excess of 2.5 Rem TEDE will be removed from radiographic activities. Additionally, an employee receiving in excess of 4 Rem will be removed from radiographic activities for the remainder of the monitoring year. The corrective actions are in place as of the date of this letter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-05-09
38900 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2002-05-05 11:43 | 2002-05-05 13:53 | 2002-05-05 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 1143 CDT, the Kewaunee Nuclear Power Plant commenced a plant shutdown. The plant shutdown was initiated due to an expected inability to restore the Component Cooling (CC) heat exchanger 'A' to an operable status prior to exceeding it's 72 hour LCO action time. The 72 LCO action time expires at 0934, Monday, May 6, 2002. The CC heat exchanger was declared inoperable when it was removed from service to investigate CC system leakage of approximately 0.37 gpm. With only one CC heat exchanger operable, Kewaunee T.S. require that after 72 hours, with one CC heat exchanger inoperable, a plant shutdown commences to < 350 F. Current plans are to shut the plant down <350 F and repair the CC heat exchanger. CC heat exchanger 'B' has no detectable leakage." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-05-05
38899 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2002-05-03 | 2002-05-03 18:51 | 2002-05-03 | AGREEMENT STATE REPORT-DAMAGED DENSITY GAUGE "RSO for the above licensee called on the date of this memo to report a CPN (model MC-1) was run over. The gauge was run over with the Cs-137 source in the ground, the user turned to get something out of his truck, which was near by and a roller ran over the gauge and then since people were waving at him, backed over the gauge. Per the RSO, the CPN representative in Denver will take possession of the gauge and return [it]." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-05-06
38898 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-05-02 18:34 | 2002-05-03 17:33 | 2002-05-03 | ABILITY TO MEET 10 CFR 50 APPENDIX R III.G.3 NOT ANALYZED "Operating License Condition 2.C(9) - Modification for Fire Protection ( Section 9.5.1 SSER #5 and SSER #6) "On May 2, 2002 at 1834 hours, during a Fire Protection Self-Assessment field walk down of procedure 20.000.18, 'Shutdown From Outside The Control Room', a procedure step was identified that could not be performed as written. Valve N2000F636, 'Condenser Hotwell Emergency Makeup Bypass Valve' could not be manually operated without the use of a ladder. No ladders were staged for this purpose, and the requirement for a ladder was not specified in the procedure. The time required to procure a ladder and perform the required operation has not been analyzed for impact on the ability to meet safe shutdown requirements of 10CFR50 Appendix R III.G.3. "The condition was documented in the corrective action program and a ladder has been staged at the valve. This condition is being reported as a potential non conformance with Operating License Condition 2.C(9)." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2002-05-03
38897 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-05-03 11:30 | 2002-05-03 17:07 | 2002-05-03 | AGREEMENT STATE REPORT-SHIPMENT WITH LOOSE SURFACE CONTAMINATION LEVELS > LIMITS "At 11:30 am on May 3, 2002, the writer was advised by [the], Assistant Radiation Safety Officer at the University of Alabama at Birmingham (UAB) in Birmingham, Alabama that their nuclear medicine department had received a radiopharmaceutical package that was found to have removable radioactive contamination on the external surface of the package that exceeded 22,200 disintegration's per minute (dpm) per 100 square centimeters. The package was received on the afternoon of May 2, 2002 from Central Pharmacy Services, Inc., d/b/a as Birmingham Central Pharmacy in Birmingham, Alabama. Central Pharmacy Services, Inc. is authorized to prepare and distribute radiopharmaceuticals under Alabama Radioactive Material License No. 1168 and the University of Alabama at Birmingham is authorized to receive radioactive material under Alabama Radioactive Material License No. 266. The package as delivered contained unit doses of Tc-99m and a vial of I-131. These inside containers were found not to be contaminated. The actual contamination was found to be on a magnetic Department of Transportation transport label. The maximum amount of removable contamination was 150,000 dpm on a wipe sample of the magnetic label. Spectrum analysis indicate that the isotope was Tc-99m. The package was isolated. "Central Pharmacy Services, Inc. was notified of the incident. The cause of the incident is currently being investigated by this office." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-05-06
38896 | 0 | BOSTON SCIENTIFIC |  |  |  |  | 2002-04-03 | 2002-05-03 15:25 | 2002-05-03 | 5 LOST AIR NOZZLE SOURCES Licensee reports that 5 static eliminator Po-210 sources are missing. All of the sources are 10 micro-curie, with the following serial numbers and dates: #119686 19 Apr 00, #104160 28 Jul 98, #108071 18 Jan 99, #108072 Jan 18 99, and #111277 10 May 99. The Licensee is still looking for the missing sources and has contacted the vendor which has indicated that the sources were never shipped back to the vendor. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-05-03
38895 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2002-05-03 13:21 | 2002-05-03 14:42 | 2002-05-03 | AUTOMATIC REACTOR TRIP DUE TO INDICATED LOSS OF RCS FLOW RPS indicated that there was a loss of RCS flow to 1 loop, which resulted in an automatic reactor trip. All three loops of RCS flow were in operation throughout the event. All rods fully inserted, no ECCS systems actuated, and decay heat is being removed by the Auxiliary Feedwater system. The Licensee indicated that the electrical grid was stable and that a post trip investigation is ongoing. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-05-03
38893 | 0 | MAXIM TECHNOLOGIES INCORPORATED |  |  |  |  | 2002-05-02 | 2002-05-02 22:00 | 2002-05-02 | STOLEN TROXLER DENSITY GAUGE The licensee reported a stolen troxler density gauge which was secured in the rear of a work truck located in Independence, Missouri. The licensee reported the theft to the Independence Police Department. The gauge was model number 3340 with a serial number of 22323. The isotopes and activities used in the gauge are 8.0 millicuries of CS-137 and 40 millicuries of AM-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-05-02
38892 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2002-03-22 | 2002-05-02 15:22 | 2002-05-02 | GROUP 3A CONTAINMENT ISOLATION AT DUANE ARNOLD "While operating in Mode 1, a fuel pool exhaust radiation monitor spiked, resulting in a Group 3A Primary Containment Isolation System (PCIS) actuation. Radiation levels in the area of the monitor were normal and the actuation was considered invalid. The "A" train of the Standby Gas Treatment System (SBGT) auto-started and the Group 3A isolation functioned as designed. The isolation was reset 14 minutes after the trip." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-05-02
38891 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-05-01 15:00 | 2002-05-01 15:45 | 2002-05-01 | LOSS OF OFFSITE EP SIRENS The licensee reported an unexpected loss of the prompt alert notification system (i.e., sirens) due to unknown reasons. Compensatory measures are in place and an investigation was started to determine the cause of the problem. The NRC Resident Inspector has been notified. Also, the licensee informed the State and local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-05-01
38889 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2002-05-01 10:00 | 2002-05-01 12:34 | 2002-05-01 | RECEIPT OF A BREACHED PACKAGE CONTAINING URANIUM AND/OR THORIUM COMPOUNDS AND DISCOVERY OF CONTAMINATION ON THE EXTERIOR OF THE PACKAGE, TRUCK BED, AND FED EX DEPOT IN LYNCHBURG, VA The following text is a portion of a facsimile received from the licensee: "Description of Transportation Incident at BWXT, Lynchburg Technology Center, Lynchburg, VA At approximately 10:00 a.m. on May 1, 2002, at the BWXT, Lynchburg Technology Center (LTC), it was discovered that a limited quantity package [...] from Environmental Enterprises ([...], Ruthersford, PA) arrived damaged (1-inch hole). The package ([approximately] 1 ft3) contained eleven small bottles of dry material containing, what is believed to be uranium and/or thorium compounds. Contamination was found on the exterior of the package and on the floor of the truck as follows: * Alpha activity: [approximately] 20,000 dpm/100 cm2 * Beta activity: [approximately] 200,000 dpm/100 cm2 * Contact radiation level: [approximately] 10 mR/hr * Radiation level at 1 meter: [approximately] 0.12 mR/hr The truck was decontaminated to background levels. The shipper and the trucking company (Fed Ex: [...]) have been notified." We have also surveyed the Fed Ex depot in Lynchburg and found small amounts of contamination. BWXT has contained this contamination." The licensee stated that the package was received from either Ruthersford, PA or NJ; that the dry, white, granular material in the broken bottle was believed to be composed of thorium compounds; that two previous drop off points (one at BWXT and one at Falwell Aviation in Lynchburg, VA) were surveyed with no contamination identified; that the contamination identified at the Fed Ex terminal in Lynchburg was discovered in a large steel box; and that the 10-mR/hr surface contact radiation level reported above was on the surface of the package. The licensee notified the NRC Region 2 office (Deborah Seymour) and plans to call the Department of Transportation. (Call the NRC operations officer to obtain contact telephone numbers for the licensee, Environmental Enterprises, and Federal Express, and the Department of Transportation.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(1) |  |  |  | 1 | 2002-05-01
38888 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2002-04-30 18:01 | 2002-04-30 19:13 | 2002-05-01 | UNUSUAL EVENT AT ANO2 DUE TO BORON RESIDUE AT PRESSURIZER HEATER SLEEVE N-2 "On 4/30/02, while performing a planned Reactor Coolant System Integrity Inspection following the 2R15 refueling outage, with the Reactor Coolant System at normal operating temperature and pressure (Mode 3), an inspector discovered small traces of boric acid on pressurizer heater sleeve N-2. Based on the subsequent evaluation, pressurizer heater sleeve N-2 has been determined to have had pressure boundary leakage. No current leakage is detectable. The Unit 2 Tech Spec 3.4.6.2 does not allow operation in Modes 1-4 with any pressure boundary leakage. Therefore a plant cooldown is being initiated to place Unit 2 in Mode 5. Based on this criteria, the condition is reportable upon declaring a Notification of Unusual Event (EAL 2.1) and Degraded Condition which is reportable per 1OCFR50.72(b)(3)(ii)(A)". The NRC Resident Inspector was notified. * * * UPDATE ON 5/1/02 @ 0331 BY AHO TO GOULD * * * NOUE terminated at 0221CDT. Plant in mode 5 (cold shutdown) The NRC Resident Inspector will be notified. Notified FEMA(Zapata), REG 1 RDO(Spitzberg), EO(Black) and IRO(McGinty) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 4 | AR | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-04-30
38887 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-04-30 | 2002-04-30 17:26 | 2002-04-30 | PRESSURIZER SAFETY VALVE SETPOINT DRIFT AT POINT BEACH UNIT 2 "On April 24, 2001, a vendor conducting offsite testing of the Point Beach Nuclear Plant (PBNP) Unit 2 RCS pressurizer safely valves' reported that safety valve 2RC-435 failed to lift at a test pressure of 2660 psig. The lift pressure specification for this valve is from 2440 to 2551 psig. In accordance with code requirement, the second in-service Unit 2 pressurizer safety valve was sent to the vendor for set point testing. The vendor also initiated an investigation to determine why the first valve failed to lift. "On April 29, 2002, our engineering department received a telecopy report of that investigation. After evaluation, we determined this event to be reportable at 1129, 4-30-02. The valve at position 2RC-435 was last tested in November 2000 by the same vendor. At that time the valve set point was determined to be within specification. In accordance with the vendor's normal practice, a jack and lap procedure was done following the set point test to lap the valve disc and nozzle to insure that the valve is leaktight with undamaged seats. It was during this process that the valve became incapable of lifting at the specified pressure. The valve assembly was corrected and the set point retested with satisfactory results. The second safety valve that was shipped for testing subsequent to the failure of the first valve has also been tested and was found to lift within the specified range. Our investigation of the circumstances of the event is continuing. "The required design capacity for the RCS pressurizer safety valves assumes the use of 2 valves based on RCS pressure not exceeding the maximum code allowable 110% of design pressure for the maximum calculated in surge of reactor coolant into the pressurizer. We have concluded that we operated PBNP Unit 2 with one inoperable pressurizer safety valve for the past cycle. The second Unit 2 safety valve has been tested and proven to be operable. This event is reportable both as a condition prohibited by the Technical Specification (LCO 3.4.10) and as an event or condition that resulted in an unanalyzed condition that had the potential to significantly degrade plant safety. An evaluation of the significance of this condition will be performed." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-04-30
38886 | 0 | FMC IDAHO LLC |  |  |  |  | 2002-04-29 15:30 | 2002-04-30 15:37 | 2002-04-30 | MALFUNCTIONING (RUPTURED), CESIUM-137, INSERTION SOURCE ON A BERTHOLD DENSITY DEVICE AT FMC IDAHO LLC IN POCATELLO, IDAHO Prior to the event, a representative from FMC Idaho LLC (an elemental phosphorous plant which has been shutdown) contacted Thermo Measure Tech (used to be TN) to remove several density devices at the plant. The plan was to have several devices removed, packed up, and shipped back to Thermo Measure Tech. During the process of removing a Berthold (model number LB300, serial number 2576-10-94) device with a 15-millicurie, cesium-137, insertion source (used to monitor tank levels), the cable which lowers the source pellet into the tube parted. Workers improvised, got a hold of the wire, and pulled it back up. When the source came out of the top, it became obvious that it had ruptured. All of the contaminated items (the source, a rag, a pair of gloves) were then put back into the tube, and the top was placed back on. The area was surveyed, and there was no contamination outside of the tube. Everything was locked up, and the area was marked off. The licensee contacted Berthold USA. Because the device was manufactured in Germany, Berthold USA notified Berthold in Germany. The licensee anticipates that Berthold will arrange to take possession of the device. A manufacturer representative told the licensee that they had never had one of these devices rupture in this fashion before. The licensee notified the NRC Region 4 office (Christine Maier and Mark Shaffer). (Call the NRC operations center for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-04-30
38885 | 0 | VA MEDICAL CENTER |  |  |  |  | 2002-04-30 | 2002-04-30 15:35 | 2002-04-30 | VA REPORTS LOST RADIOACTIVE MATERIAL LATER LOCATED IN A LANDFILL "1. Part 20.2201(a) [telephone report]: a. A telephone report was not made since the circumstances related to the loss of licensed materials were identified to the licensee by the Nuclear Regulatory Commission (NRC) and are not based on specific information verified by the license or on official records. b. Neither the NRC nor the state regulatory agency (Illinois Department of Nuclear Safety) with purview over the landfill has provided the licensee any information other than telephone summaries and digital photographs. C. The estimate of the quantity of lost licensed materials was completed post hoc and is not based on measurements performed by the licensee. d. The licensee became aware of loss of licensed materials on March 29, 2002. 2. Part 20.2201(b)(i) [description of the licensed material involved, including kind, quantity, and chemical and physical form]: a. The licensed material was I-131 as identified by spectral analysis at the landfill by the state regulatory agency. Since the material could not be recovered, the exact chemical form could not be determined. However, in light of subsequent investigation, the form was probably inorganic NaI bound to Sephadex beads. b. The gamma factor for I-131 is 2.2 R./hr per mCi @1cm. c. The state regulatory agency reported the following exposure rates measured using a Bicron internal chamber meter. (1) 125 mR/hr @ contact (2) 50 mR/hr through side of truck (3) 0.65 mR/hr @ 1 meter d. The three different readings appear to be somewhat contradictory. However, since the actual distance for the first two measurements is uncertain and less error is likely in exposure rate measurements at a known distance. the third measurement is considered the most accurate to use to estimate activity. e. The waste materials from the laboratory were not specifically recovered or identified. The following three possible basis were used to estimate activity: the exposure rate measurements by the state regulatory agency, the usual laboratory protocols, and recreation of exposure rate measurements in a laboratory setting. (1) Using corrected distances for the exposure rate measurements and the gamma factor for I-131, the measurement at one meter calculates to an estimated activity of approximately 3 mCi. (2) The usual laboratory protocol is to use either 1 or 2 mCi I-131 run through a column. The highest activity possible on the column is 1.9 mCi, corresponding to a maximum doping of 2 mCi, with the poorest binding success of 5%. (3) Laboratory measurements were taken using a 16 uCi I-131 capsule and a GM detector calibrated to CS-137 and with a thick-walled tube. The exposure rate measurement at contact with the thin plastic container with the capsule nearest the probe was 45 mR/hr. This represents the closest likely proximity implied by contact. Under this geometry, a reading of 125 mR/hr could be produced by as little as 44 uCi I-131. However, the rate drops to less than 0.05 mR/hr at 6 inches, due in part to the influence of the beta component. This indicates an activity in the millicurie range was involved in the incident, and the contact exposure rate measurement was likely not taken at contact, but at about 8 cm. (4) The estimate for activity is approximately 2 mCi. 3. Part 20.2201(b)(ii) [a description of the circumstances under which the loss or theft occurred]: a. The loss of licensed materials involved the Roxanna, Illinois, landfill. The loss was identified by the landfill operator during routine radiation monitoring for incoming waste shipments on March 28, 2002. The landfill operator reported higher than expected radiation monitoring results and notified the state regulatory agency. The state contacted the NRC. The NRC contacted the VA National Health Physics Program who then contacted the licensee. b. The loss involved I-131 contaminated glassware which was identified in a truck hauling waste from the licensee to the landfill. The landfill is approximately 20 miles from the licensee, John Cochran Division, in downtown St. Louis: The waste was probably generated in a research laboratory in Building 1 of the John Cochran Division. c. Workers assigned to the licensee Environmental Management Service (EMS) collect waste at the end of each work day from research laboratories. The waste is initially placed in carts and then relocated to a dumpster at the loading dock. The contract waste carrier empties the waste collected in the dumpster on a daily basis, normally at night. The waste is then transported to a transfer station and consolidated with other waste. The consolidated waste is relocated to the landfill using a semi-trailer. 4. Part 20.2201(b)(iii) [a statement of disposition. or probable disposition, of the licensed material involved] a. Disposition of the radioactive materials was under the purview of the state regulatory agency. b. The state regulatory agency directed the landfill operator to bury the waste materials. 5. Part 20.2201(b)(iv) [exposures of individuals to radiation, circumstances under which the exposures occurred, and the possible total effective dose equivalent to persons in unrestricted areas]: a. The following individuals had the most potential for exposure (1) EMS (Environmental Management Service, i.e. Housekeeper) personnel picking up waste and transporting it to dumpster (2) Driver of truck hauling waste from VA to transfer point ( first truck ) (3) Driver of truck hauling consolidated waste from transfer point to landfill ( 2nd truck ) (4) State of Illinois (IDNS) responding personnel (5) Landfill personnel were not involved in the effort to recover the contaminated object. The potential exposure of personnel other than the above must be considered small in comparison. b. Estimated exposure (1) EMS workers Estimated duration of exposure = 10 min (0.16 hr) Average proximity 3 feet (bag of waste is carried in large cart with other bags) Inverse-square correction, using 0.65 mR/hr at 1.13 meters 0.83 mR/hr Add 20% for lack of shielding by dump truck =1.0 mR/hr Estimated exposure 1.0 mR/hr x 0.16 hr = 0.16 mR (2) Driver of first truck Estimated duration of exposure 1 hr Average proximity = 10 feet (3 m) Inverse square correction, using at 0.65 mR/hr @ 1.13 m. through truck bed 0.65 mR/hr x (1.13/3)squared = 0.09 mR/hr Total estimated exposure: 1 hr x 0.09 mR/hr = 0.09 mR (3) Driver of 2nd truck (semi-trailer) . Estimated duration of exposure = 1 hr Average proximity 17 feet (5 m) Inverse square calculation, staring at 0.65 mr/hr @ 1.13 m, through truck bed 0.65 mR./hr x (1.13/5) squared = 0.03 mR/hr Total estimated exposure: 1 hr x 0.03 mR/hr =0.03 mR (4) IDNS responding personnel = N/A; occupationally exposed and monitored 6. Part 20.2201(b)(v) [actions that have been taken, or will be taken, to recover the material]: a. Disposition of the radioactive materials was under the purview of the state regulatory agency. b. The state regulatory agency directed the landfill operator to bury the waste materials. c. The licensee attempted to recover the material by driving to the landfill, prior to being informed that the material had been buried. The licensee does not have any authority to take further actions to recover the material nor is recovery currently possible. 7. Part 20.2201(b)(vi) [procedures or measures that have been, or will be, adopted to ensure against a recurrence of the loss or theft of licensed material]: a. Investigation by the licensee verified that current policies and procedures regarding waste control are adequate and should have prevented such an incident. At some point, therefore, procedures were apparently not followed. Lab workers can not recall any breach of procedures. Similar waste has been produced many times in the past without incident, and the ergonomics of the laboratory do not point to any probable mis-step. Therefore, remediation efforts will be broader than a focus on handling of the specific type of waste in question. b. The corrective actions will involve screening of all waste generated from areas where external radiation detectable by NaI instruments is produced. All laboratories possessing photon-producing isotopes of energies greater than approximately 20 KeV, in quantity greater than 1 micro-curie, will be required to screen all sanitary and DIS waste with a NaI detector prior to release into the environment. The new standards will require that equipment, procedures, and competency of screeners be reviewed and approved by the RSO for each area. The level of detail in the existing procedure for screening of DIS waste has been increased to include removing interposed shielding, measuring each container at multiple positions, using the most sensitive scale, and a standard for the background reading. This more detailed procedure will be applied to all labs utilizing DIS, and will also be applied to screening of sanitary waste by those labs required to do so. The procedure will be reviewed by the Radiation Safety Committee on May 2, 2002. Users will be required to implement the new procedure by June 1, but will probably do so earlier. NaI detectors have been ordered; first deliveries are expected by the May 1. Until the equipment arrives and the program is fully implemented, routine trash pickups of affected areas has been halted. All waste is screened by the RSO, using the limited NaI technology currently available, before release. c. The requirement for sanitary waste screening will become a condition during both permit approval and renewal, and whenever an affected isotope is added to the authorization. This condition will apply equally in Nuclear Medicine and Research laboratories at the St. Louis site of use. RSO review of equipment specifications and operator competency will be included in the approval process. This program has already been implemented. d. Certain logistics of the waste-handling process, such as: how long waste is accumulated before screening, whether waste storage is centralized, arid how unscreened waste is stored, etc., can only be developed through practice. However, once best practices are developed, affected labs will be required to adopt diem, and will not be allowed to change them without review and approval of the RSO. Logistics will be under review through May, 2002; final practices will be in place by June 1, 2002. e. DIS procedures and compliance will continue to be monitored during routine inspections and the results reported to the Radiation Safety Committee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-04-30
38884 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2000-06-01 | 2002-04-30 15:05 | 2002-04-30 | AGREEMENT STATE REPORT OF RADIOGRAPHER OVEREXPOSURE FROM TWO YEARS AGO "On April 29, 2002, the department completed its investigation into a reported radiography incident that may have occurred in June 2000. After a review of all available information, the department cannot definitively eliminate the possibility that an industrial radiographer received a radiation burn while performing industrial radiography at a temporary jobsite near Channahon, Illinois. The radiographer was using an 81.2 Ci lr-192 source while performing radiographs on 8-inch pipe welds. The radiographer alleges that after cranking the source back in, he approached the area without looking at his survey meter. He set the meter behind the camera and knelt down in front of the camera, He changed out the film and then changed out the band and numbers for the next shot. He then disconnected the guide tube and saw 4-6 inches of the drive cable. He looked over at the survey meter and saw that it was pegged. He then immediately went to the controls and cranked the source fully into the camera. He performed a survey of the area and saw that the source was shielded properly. He looked at his alarming rate meter and saw that the battery indicator showed low battery. His self-reading pocket dosimeter showed off-scale. What happened after that is even more unclear but the radiographer continued working for the rest of the day. The radiographer did not report the incident to the RSO nor did the other radiographer on the two certified radiographer team. In fact, the other radiographer denies knowing anything about the reported incident. The allegedly overexposed radiographer states that after one or two weeks, he noticed a red area, about the size of a nickel, on his leg. He stated that it was a red area with what appeared to be white scar tissue in the center. It was not until May or June of 2001 that he realized that it may have been a radiation burn. During August or September 2001 his condition apparently worsened and the area would not heal. In early January 2002 the Radiation Safety Officer finally became aware of this matter, and notified the department on January 15, 2002. In early January 2002 the radiographer was apparently examined by a physician. The radiographer stated that the physician took a biopsy and the diagnosis was either sarcoma or radiodermatitis. A preliminary report was provided to the department by the licensee on January 16, 2002. The department recommended the licensee seek assistance from the REAC/TS Center in Oak Ridge, which they did. The information pertaining to this incident was provided to REAC/TS by the licensee and REAC/TS concluded that the medical condition could be attributed to the event in June 2000. After thoroughly reviewing all the information available and scheduling interviews for involved out of state personnel, the department conducted interviews and time in motion studies on February 25, 2002. Subsequent to the interviews and time in motion studies, careful review was performed as well as additional clarifying information was requested and reviewed. Finally on April 29, 2002, the department concluded that it could not definitively eliminate the possibility that this industrial radiographer received a radiation burn while performing industrial radiography at a temporary job site near Channahon, Illinois in June 2000. The radiographer underwent skin grafting on February 26, 2002, and was released after several days. The radiographer currently remains under medical surveillance and reports that the graft was less than successful. The licensee has been issued a Notice of Violation and will take appropriate actions to prevent a recurrence. The radiographer may be subject to additional department enforcement action related to his industrial radiographer certification resulting from this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-05-03
38883 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-04-22 10:25 | 2002-04-30 11:03 | 2002-04-30 | MEDICAL MISADMINISTRATION The following event description is taken from a facsimile: "On April 22, 2002, the technologist injected a patient with a syringe labeled Tc-99m MAG 3 in order to image the kidneys. The gamma camera showed uptake in the liver-kidney indicating a sulfur colloid dose. The patient was prescribed a 4.5 mCi dose of Tc-99m MAG 3, but received a 4.5 mCi dose of Tc-99m Sulfur Colloid. The patient and the pharmacy were notified of the error. The dose for a patient receiving 5 mCi of Tc-99m Sulfur Colloid is estimated as the following: Liver - 12.15 Rad, Spleen - 7.65 Rad, Bone Marrow - 0.05 Rad, Testes - 0.02 Rad, Ovaries - 0.2 Rad, and Total Body - 0.675 Rad." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-05-03
38881 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2002-04-27 11:40 | 2002-04-27 15:51 | 2002-04-29 | OFFSITE NOTIFICATION REGARDING A BOATING ACCIDENT ON THE SITE'S COOLING LAKE On April 27, 2002, at 1140 CDT, the Main Control Room received a report from Outside Rounds Operator that a fishing boat had capsized on the station cooling lake and that two individuals aboard the capsized boat were at the Wastewater Treatment Facility after swimming ashore. One individual aboard the capsized boat remains missing. Currently, the boat has been recovered, but after a search of the lake perimeter, the third individual remains missing. The Ottawa Search and Rescue Team was on site to perform rescue operations but has determined that lake conditions are too rough to perform a water based rescue operation. State Police and LaSalle County Sheriff have been notified. Marseilles and Seneca Fire Departments are coming to the site to assist in a ground search. Department of Natural Resources officials are also assisting with the missing person search. The NRC Resident Inspector was notified. ***** UPDATE FROM LARRY BLUNK TO LEIGH TROCINE AT 1245 EDT ON 04/29/02 ***** At approximately 0940 CDT on 04/29/02, the body of the individual missing from the boating accident was found in LaSalle's cooling lake. The LaSalle County Coroner responded to the scene and took possession of the body. All parties subsequently left the vicinity of the station. The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Brent Clayton). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-27
38880 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-04-26 15:51 | 2002-04-26 16:10 | 2002-04-26 | POTENTIAL FOR HOT SHORTS IN PORV CIRCUITS "Recent review of Station Procedures regarding fire in the Control Room and other specific fire areas reveals an inconsistency with the plant Licensing Basis. The unit Licensing Basis takes credit for prevention of spurious operation of the PORVs by removing power from the valves prior to spurious operation. Current procedures require removing power from the PORVs but does not require removal of power prior to spurious operation. Spurious operation of the PORVs due to a hot short is an unanalyzed event. "Compensatory actions to minimize risk of fire in areas of concern are being implemented which include increased surveillances to verify operability of detection and suppression, control of transient combustibles and ignition sources. The PORVs are considered operable. "This event is being reported lAW 10CFR50.72(b)(3)(ii)(B) as an event or condition that results in the Nuclear Power Plant being in an unanalyzed condition that significantly degrades plant safety." The NRC Resident Inspector was notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-04-26
38879 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2002-04-23 | 2002-04-26 13:06 | 2002-04-26 | AGREEMENT STATE REPORT OF A MEDICAL MISADMINISTRATION A medical misadministration occurred on April 23, 2002 that resulted in the patient receiving a 36% overdose (i.e., 10.9 gray vice 8 gray) during brachytherapy to treat coronary vessels. The isotope being used for the treatment is IR-192. The error was discovered on April 25, 2002 when the hospital was setting up to treat another patient. Specifically, a wrong decay table was used in the calculations. No adverse effect on the patient was anticipated. The patient has been notified. The State reported that RIII (K. NULL) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2002-04-29
38878 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-04-26 08:35 | 2002-04-26 09:06 | 2002-04-26 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) INOPERABLE DUE TO PLANNED OUTAGE OF THE PLANT PROCESS COMPUTER SYSTEM The following text is a portion of a facsimile received from the licensee: "On [April 26, 2002,] at 0835 hours EDT, the Indian Point Unit 2 plant ERDS was taken out of service to perform planned modifications to the plant process computer system. ERDS will remain inoperable until approximately May 4, 2002." "This report is being made in accordance with the requirements of 10 CFR 50.72(b)(3)(xiii); any event that results in a loss of offsite communications capability." "The Senior Resident Inspector has been briefed on the modifications and schedule. The NRC was previously notified of this planned outage via letter dated April 4, 2002." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-04-26
38877 | 0 | GRIFFIN HOSPITAL |  |  |  |  | 2002-04-25 | 2002-04-25 16:05 | 2002-04-25 | TRASH BURNING FACILITY RADIATION MONITORS ALARM ON WASTE SHIPMENT FROM GRIFFIN HOSPITAL The Bridgeport RESCO trash burning facility notified the Griffin Hospital that a waste shipment from the hospital set off the radiation monitors. A consultant from the hospital was dispatched to the trash facility to identify the cause of the alarm. The consultant reviewed the waste records from the hospital and preliminarily determined that a radioactive diaper was most probably the source of the radioactivity. ***UPDATE S. KORZHIN to R. LAURA on 4/25/02 at 1830*** Investigation found approximately 5 or 6 diapers with patient waste that had a maximum surface reading of 10 millirem per hour. The radioactive isotope involved was iodine-131. The diapers will be transported back to the hospital where they will be stored for radioactive decay. Also assisting the hospital contractor was the Connecticut Department of Environmental Protection. Notified R1DO (C. Anderson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | HOS | [5 empty] | 0 | 2002-04-25
38876 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2002-04-25 05:13 | 2002-04-25 12:23 | 2002-04-25 | START OF DIVISION III DIESEL DUE TO GRID VOLTAGE DIP "On 4/25/02 at 0513 while lining up to backfeed through the main power transformers in preparation for a Reserve Auxiliary Transformer outage, a low grid voltage condition occurred, resulting in the auto start of the Division 3 Diesel Generator. "The Procedure to backfeed power from the switchyard to the plant electrical buses was in progress. This procedure was being used to support removing one of the offsite power sources supplied through the Reserve Auxiliary Transformer (RAT) which was being removed from service for maintenance. When the disconnect was closed in the switchyard completing the backfeed, the Static Var Compensators (SVC) for the two offsite powers sources, the RAT SVC and the Emergency Reserve Auxiliary Transformer (ERAT) SVC tripped. The offsite power sources supplying the RAT and ERAT remained energized "The SVCs maintain voltage from the RAT and ERAT to the plant within a constant voltage band. Without the SVCs, low grid voltage may result in low 4160kv bus voltage. At the time this occurred the Division 1 and 2 buses were being supplied from the RAT, which has three 345kv sources, and the Division 3 bus was being supplied from a separate 138kv source. It was the 138 kv source that experienced the degraded voltage that resulted in thc Division 3 ERAT supply breaker opening (offsite power source) and the Division 3 Diesel Generator starting and closing in on the Division 3 bus. "Following the grid voltage transient, grid voltage returned to the pretransient level. The RAT and ERAT SVCs were restored to service and both offsite power sources were made operable. No damage to plant equipment was observed during the initial investigation. The Division 3 Diesel Generator was paralleled to the ERAT offsite power source and loaded. The diesel generator has been divorced from the ERAT and the Division 3 bus is being carried by the ERAT in the normal lineup." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-04-25
38875 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-04-24 | 2002-04-24 18:10 | 2002-04-24 | AGREEMENT STATE REPORT OF LOST IRIDIUM-192 SOURCE The Alabama State Radiation Control Office reported that the University of Alabama Medical Center was missing a 250-millicurie iridium-192 source. The source is used for cardiology purposes and was last seen on April 22, 2002. The hospital was conducting searches to try to locate the missing source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-04-27
38874 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-02-26 14:38 | 2002-04-23 11:04 | 2002-04-23 | INVALID SPECIFIED SYSTEM ACTUATION WHILE TESTING "Title: Invalid Safety Injection actuation during testing. "This is a verbal report being made in accordance with 10 CFR 50.73(a)(2)(iv)(A). It is NOT considered a Licensee Event Report (LER) "Description: "On February 26, 2002, at 1438 CST, an inadvertent actuation of Unit 2; Train B; Safety Injection occurred. Unit 2 was in Mode 4, during start-up from the Refueling Outage. During performance of the 'Test of Reactor Trip and Bypass Breakers Auxiliary Contacts' procedure, electricians were installing volt meter test probes on terminals to obtain voltage readings during the test. While installing the test probe, the electrician inadvertently made contact with an adjacent terminal. This contact shorted two terminals causing a complete actuation of Safety Injection -Train B. Following the actuation, operators promptly identified that the signal was not valid and took action to realign equipment as necessary to stabilize the plant. "All Unit 2, Train B safeguards equipment started and functioned as required. D6 Diesel Generator started as required but did not load because normal power remained available. "The reactor was not critical at the time of the event. The Reactor Protection System did not actuate as all control rods were fully inserted with the Reactor Trip Breakers open prior to the event." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-04-23
38873 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-04-22 12:05 | 2002-04-22 13:36 | 2002-04-22 | EMERGENCY SIRENS ACTUATED DURING A SILENT TEST Inadvertent Emergency Response Siren actuation occurred in Calvert County during the weekly silent test. All 49 sirens sounded for approx. 15 seconds. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-22
38872 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-22 06:00 | 2002-04-22 13:17 | 2002-04-22 | MICHIGAN STATE POLICE AT DC COOK PLANT ENTRANCE. The following is a courtesy call regarding an event that occurred at the DC Cook Nuclear Power Plant at 0600 on 4/22/02. The following has not been issued as a Cook Plant news release but it is believed that the news media is already aware of this via other means. At 0600 on 4/22/02, Michigan State Police (MSP) arrived at the Cook Plant main entrance. MSP told Cook Plant Security that they were waiting for an individual known to work at Cook to show up. MSP had previous encounters with this individual and knew this person had concealed weapons permit, was known to carry a weapon in the car and had been previously advised by MSP to not carry a weapon on Cook property. When the individual, a contractor, arrived, Cook Plant Security personnel asked him if had a weapon in his car. He stated that he did not, having stashed it offsite on the highway. At this point the MSP advised him that he would take them to the location of the weapon. About 15 minutes later MSP and the individual returned, with MSP in possession of the weapon. MSP stated that they would retain possession of the weapon pending further investigation. Having no other reasons to deny access, the individual was allowed on site. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2002-04-22
38871 | 0 | SEIMENS MEDICAL SOLUTIONS USA, INC |  |  |  |  | 2002-04-20 02:00 | 2002-04-22 11:03 | 2002-04-22 | LOSS/STOLEN NUCLEAR LICENSED MATERIAL >1000X Two calibration sources were stolen from a rental car in Oahu, Hawaii on 4/19/02. The sources, 2 millicuries of Am-241 and 2 millicuries of Co-57, were in tungsten shielded containers with screwed on lead caps. The sources were in a locked tool box, which was in the locked trunk. The thief pulled out the driver door lock, pried open the glove box and opened the trunk. The source numbers and dates were as follows: Am-241, #0191LX, 8-4-89 and Co-57, #5971 LC, 10-13-00. The Kaneohe Police Department was notified, report # 02-145893. Ads will be placed in the local newspapers. Licensee indicated that there were no measurable dose rates on the outside of the shielded container. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-04-22
38870 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-04-22 01:15 | 2002-04-22 02:43 | 2002-04-22 | MANUAL RPS ACTUATION "Susquehanna Unit 1 was at 20% power and in the process of preparing to further increase power following a Refueling and Inspection Outage. At 0016 on 4/22/02, the B Reactor Recirculation Pump tripped for an unexplained reason. During a review of the plant response to the transient, it was discovered that the unit was operating to the left of the expected Power to Flow curve. There was no indication of power flux oscillations from the nuclear instrumentation, but no guidance was available on how to respond to this condition. Reactor Engineering and Operations Management were contacted and it was decided to manually scram the unit. At 0115 the Mode Switch was taken to Shutdown and all control rods inserted. This was an unplanned RPS Actuation and in accordance with 10 CFR 50.72(b)(2)(iv)(B) requires a four-hour ENS Notification. Reactor water level dropped below level 3 which is expected during a scram, feedwater level control responded to return level to normal and all level 3 isolations went to completion. There were no ECCS initiations, no challenges to containment, and no indication of radiation releases. Operations is currently performing a controlled cooldown to mode 4, an investigation into the cause of the recirc pump trip is ongoing." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-04-22
38869 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2002-04-20 16:57 | 2002-04-20 20:34 | 2002-04-20 | UNPLANNED LOSS OF CONTROL ROOM ANNUNCIATORS LESS THAN 15 MINUTES The licensee reported the loss of control room annunciators for 9 minutes when the electrical supply breaker tripped free. The breaker was reset and closed which restored the annunciators. However, later the same electrical breaker tripped free again resulting in the loss of control annunciators lasting for 14 minutes. The breaker was reset and closed for the second time. Maintenance troubleshooting revealed that the breaker needed to be replaced. The isolation for this corrective maintenance will result in a planned loss of control room annunciators greater than 15 minutes. Alternate plant monitoring will be utilized for the duration of the breaker change out. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-04-20
38868 | 0 | YANKEE ROWE | 1 |  |  | [1] W-4-LP | 2002-04-20 06:51 | 2002-04-20 07:49 | 2002-04-20 | USUAL EVENT DECLARED DUE TO SEISMIC ANOMALY Licensee felt tremors in the control room lasting more than 5 seconds and declared an Unusual Event at 0700 and immediately downgraded at 0701. Walkdowns were performed and no damage was noted. Licensee does not have any has seismic monitors. Offsite notifications have been made to the states of MA and VT. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-04-20
38867 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-04-20 05:12 | 2002-04-20 06:52 | 2002-04-20 | MANUAL RPS ACTIVATION DUE TO LOSS OF FEEDWATER "Unit 1 was at approximately 30% power and preparing to synchronize the Main Generator to the grid. The A Main Feedwater Pump mini flow valve was isolated per plant procedures. The isolation of the mini flow valve caused the Steam Generator levels to rise. A Hi-Hi Steam Generator level occurred in #4 Steam Generator. This resulted in a trip of the Main Feedwater Pump, a Feedwater Isolation Signal, and the trip of the Main Turbine. The Reactor was tripped due to having no Main Feedwater available to the Steam Generators in anticipation of a low-low Steam Generator level trip at 38% level. Both Motor Driven Auxiliary Feedwater pumps did start as a result of the only running Main Feedwater pump being tripped." All rods fully inserted into the core. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-04-20
38866 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-04-19 07:00 | 2002-04-20 01:27 | 2002-04-20 | NRC BULLETIN 91-01 RESPONSE (24-Hour Report) "At 0700, on 04-19-02, the Plant Shift Superintendent (PSS) was notified errors were found in historical data associated with three 30 gallon drums. Research to support remediation activities associated with NCS-INC-01-025 revealed that information used to characterize waste drums had been incorrectly entered onto the Request For Waste Classification (RWC) sheets for these three 30 gallon waste drums of NCS Spacing Exempt classified waste, violating requirements of NCSA WM-03 and WMO.001. This violated the Double Contingency principal. These drums were transitioned to storage under WMO.001 upon deletion of WM-03. The purpose of the requirement is to ensure the correct Information is available on the RWC for classification. "This Is a legacy issue; upon review of the correct data associated with these drums, the classification status of NCS Spacing-Exempt is correct. The drums are currently being properly controlled. "The NRC Senior Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: "Although the calculations were incorrectly performed and the independent verification failed to catch the error, the correct data associated with these drums was reviewed and the drums are still NCS Spacing-Exempt and controlled properly. However, the paperwork needs to be updated to assure downstream problems are avoided. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR In order for a criticality to be possible, the mass in multiple adjacent waste drums stored as NCS Spacing Exempt would each have to be greater than the safe mass determined for that container size and these waste drums would have to be stored together or recontainerized into unfavorable geometry containers. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC) "The controlled parameter is mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "The correct data indicated that the mass of the drums was less than the always safe mass of 120 grams of U-235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Double contingency is maintained by implementing two controls to ensure the uranium mass used for classification is correctly listed on the RWC. "The first leg of double contingency is based on correctly calculating and transcribing the mass result onto the RWC. The wrong analytical result was used for the calculation. This wrong calculational result was transcribed onto the RWC. The control was violated. Since there are two controls on one parameter, double contingency was not maintained, "The second leg of double contingency is based on independently verifying the mass was correctly calculated and transcribed onto the RWC. The incorrect calculation and transcription was not discovered during the independent verification. The control was violated. Since there are two controls on one parameter, double Contingency was not maintained. "Since double contingency is based on two controls on one parameter, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Correct the RWCs." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-04-20
38865 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-04-19 16:54 | 2002-04-19 18:50 | 2002-04-19 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS ON UNIDENTIFIED DRYWELL FLOOR LEAKAGE "This report is being made pursuant to 10 CFR 50.54(z); 50.72(a) (1) (ii) and 50.72(b) (i) the initiation of a nuclear plant shutdown required by the plant's Technical Specifications. Plant E. I. Hatch, unit one has commenced a plant shutdown as required by Technical Specifications 3.4.4 A (RCS Operational Leakage). The Reactor Coolant System unidentified leakage has been calculated to be greater than the Technical Specification limit of 5 GPM. The leakage has been calculated to be 6.85 GPM at 1647 Hrs. Eastern Time, The plant was operating at 19% rated thermal power (RTP) and commenced a power reduction at 1650 Hrs. Eastern Time. The current power is 9% RTP and shutdown is in progress." The licensee notified the Resident Inspector. | 9 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-04-19
38864 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-04-19 14:03 | 2002-04-19 14:25 | 2002-04-19 | AUTOMATIC REACTOR TRIP AT MILLSTONE UNIT 2 The licensee reported that all control rods inserted properly and all systems functioned as designed. The reactor trip was initiated from a main turbine protective trip which may be related to a stator cooling malfunction. The plant is currently stable in Hot Standby. The licensee has begun investigating the cause of the event. The Resident Inspector has been notified. Additionally, the licensee notified the State and Local officials. | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-04-19
38863 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-04-18 17:35 | 2002-04-18 21:04 | 2002-04-18 | OFFSITE NOTIFICATION REGARDING THE RESCUE OF TWO WORKERS FROM A MAN-BASKET THAT WAS SUPPORTED BY A DISABLED CRANE The following text is a portion of a facsimile received from the licensee: "At 1735 hours on 04/18/02, Coast Guard assistance was requested to remove two personnel from a man-basket that was supported by a disabled crane which had been performing ASME Section XI IWL Containment concrete inspections. The rescue was completed by helicopter at 1938 hours." The licensee stated that Unit 2 is currently in Hot Shutdown after refueling and prior to going critical. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-18
38862 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-04-17 09:50 | 2002-04-17 16:46 | 2002-04-17 | CONTRACT SUPERVISOR FITNESS-FOR-DUTY TEST POSITIVE FOR ALCOHOL A contract supervisor tested positive for alcohol and has been referred to the employee assistance program. (Contact the NRC operations officer for additional details.) The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2002-04-17
38861 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-04-12 | 2002-04-17 16:30 | 2002-04-17 | AGREEMENT STATE REPORT/MEDICAL MISADMINISTRATIONS INVOLVING THREE PATIENTS AT MEMORIAL MEDICAL CENTER-BAPTIST CAMPUS IN NEW ORLEANS, LOUISIANA The following text is a portion of a facsimile received from the Louisiana Department of Environmental Quality: "Event Report ID No.: LA020007" "License No.: LA-0349-L01" "Licensee: Memorial Medical Center-Baptist Campus" "Event [Date] and Time: At the beginning of March 2002" "Event Location: [... New Orleans, LA ...]" "Event [Type]: Misadministration" "Notifications: Notified the patients and physician." "Event [Description]: On April 12, 2002, it was discovered that [three] patients received a misadministration on a therapy procedure. All three patients were to receive therapy doses to the prostate. While planning the therapy, the Dosimetrist put Nucletron Source Positioning Simulator (Part #111.094) together the wrong way. The design of the Simulator allows it to be put together backwards. The correct distance for the dose was 1408 mm, but the actual distance was 1117 mm. The dose the patient received was calculated as 70 centigray to the knees, thighs, and scrotum of the three patients. As of now, there appears to be no observable effects to the patients. All three patients were notified and agreed to have the therapy again for the correct site. This facility uses a Nucletron Vectrave HDR with a 10-Ci source of Ir-192. The activity during the patient therapy was 8.06 Ci for one patient, 5.45 Ci for another, and 4.8 Ci for the third patient. The policy has been changed so that the physicist will check the position simulator before use. Further details will be placed in the NMED database as soon as the details are available." "Transport [Vehicle Description]: NA" "Media [Attention]: NA" Call the NRC operations officer for state contact information and event location details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-04-20
38860 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-04-13 | 2002-04-17 15:17 | 2002-04-17 | AGREEMENT STATE REPORT/POSSIBLE RADIOACTIVE MATERIAL INCIDENT INVOLVING DISCOVERY AND DISPOSAL (AS TRASH) OF CONTAINERS WITH RADIOACTIVE LABELS IN NORTH CAROLINA The following text is a portion of a facsimile received from the North Carolina Department of Environment and Natural Resources, Division of Radiation Protection: "On April 17, 2002, the North Carolina Division of Radiation Protection, Radioactive Material Section, was notified by the North Carolina Hazardous Material staff of an ongoing event possibly involving radioactive material. During the clean up of an unoccupied home (located in Asheville, NC) by a church group, several containers with radioactive labels were discovered and disposed of as trash (on April 13, 2002). The containers (approximately 10 in number) were described as 3 inches in diameter (possibly lead), labeled with the radiation symbol, and labeled 'TC'. Local authorities have concluded the trash was deposited at the local landfill (Buncombe Co.) and is currently under 1,500 tons of trash. Local authorities have performed radiation exposure measurements at the landfill and home site[. They] report no significant measurements above background levels. The North Carolina Division of Radiation Protection is continuing to gather information." Call the NRC operations officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-04-19
38859 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2002-04-17 13:30 | 2002-04-17 14:49 | 2002-04-17 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY VIA ALL EMERGENCY SIRENS DUE TO A LOW VOLTAGE CONDITION ON A CIRCUIT BOARD WHICH MAY HAVE RESULTED FROM AN ONGOING HEAT WAVE IN THE NORTHEAST A low voltage condition on a circuit board is believed to have resulted in the loss of offsite communication capability via the emergency sirens. Preliminary investigations revealed that the failure may have been heat related (the result of an ongoing heat wave in the northeast). Troubleshooting is currently in progress. The licensee notified all of the towns within the emergency planning zone, and the Fire Departments within the affected area plan to perform route alerts (make announcements locally) if there is a need to notify the public before the emergency sirens are returned to service. The licensee notified the NRC resident inspector but does not plan to issue a press release. ***** UPDATE FROM FRANCIS CLIFFORD TO LEIGH TROCINE AT 1546 ON 04/17/02 ***** The following text is a portion of a facsimile received from the licensee: "At 1330 on April 17, 2002, the Prompt Alert and Notification system (offsite communication capability - 112 sirens) was determined to be inoperable. This event was due to a failed siren that was broadcasting a continuous radio frequency transmission to the remaining sirens in the system. This condition prevented activation of the remaining 111 sirens. The Emergency Planning group is presently attempting to locate and isolate the problem. All affected towns have been notified of the loss of siren capability. A backup plan is in place (route alerting) in the event of an emergency at Pilgrim Station." "FOLLOWUP: At 1530 on April 17, 2002, the Prompt Alert and Notification system was restored to operable status. The failed siren has been isolated and will be repaired shortly. The remaining 111 sirens are operational. All affected towns have been notified that the system has been restored." "Notification References: 10CFR50.72(b)(1)(v) and 10CFR50.72(b)(3)(xiii)." The licensee plans to notify the NRC resident inspector and the Fire Departments. The NRC operations officer notified the R1DO (John Rogge). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-04-17
38858 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-04-16 13:55 | 2002-04-16 22:10 | 2002-04-16 | NRC BULLETIN 91-01 RESPONSE - CRITICALITY CONTROL 24-HOUR REPORT The following text is a portion of a facsimile received from the Portsmouth personnel: "On 04/16/02, [a Recirculating Cooling Water (RCW)]/FREON status walkdown was performed to ensure compliance with the Nuclear Criticality Safety (NCS) controls of NCSA-0333_015A06. During the walkdown, it was found that the R-114 level on cell 33-6-9 Even and the East 'A' Booster could not be seen on the [sight] glass. The RCW supply block valves were found to be open." "NCSA-0333_015.A06 requires that: 'The liquid R-114 level on shutdown cells shall be monitored weekly unless the R-114 is drained. If the R-114 level is not visible on the level indicator for the coolant system, the RCW supply block valve shall be closed.' " "Since the R-114 was not visible on the [sight] glasses and the RCW supply block valves were open, the NCSA control was violated." "SAFETY SIGNIFICANCE OF EVENTS: The safety significant of this event is low. The equipment involved contains less than a safe mass of material, and for water to get to material contained in the process side of the equipment, the condenser tubes must leak (filling the coolant system with water up to the level of the cooler tubes), and the cooler tubes must leak allowing the water to enter the process side of the equipment. The pressure of the coolant system for Cell 33-6-9 Even is approximately 8 psig, and the pressure of the East 'A' Booster coolant is greater than 30 psig. Therefore, neither the condenser nor the cooler tubes appear to be leaking." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, water must leak across the coolant system (i.e., both the condenser and cooler heat exchange tubes must be breached) and into the process side of the equipment. Once on the process side of the equipment, the water has to cause material to relocate and accumulate such that the resulting mixture contains more than a critical mass." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameters in the event are Mass and Moderation." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The enrichment on cell 33-6-9 Even is 1.431 wt. percent 235U, the enrichment on East 'A' Booster is 1.763 wt. percent 235U, and there is no equipment in the X-333 facility that has a greater than safe mass deposit. The safe mass of uranium at 2 wt. percent is 341.6 pounds." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The RCW supply block valve was not closed." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Required actions were initiated for an NCS Anomalous Condition. Under the direction of NCS personnel, the RCW supply block valves were closed, thus regaining compliance with the NCSA." Portsmouth personnel notified the NRC resident inspector and plan to notify the Department of Energy site representatives. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-04-16
38857 | 0 | NORTHERN ENGRAVING |  |  |  |  | 2002-04-16 15:00 | 2002-04-16 16:33 | 2002-04-16 | DISCOVERY THAT AN AMERICIUM-241 SOURCE WAS MISSING FROM NORTHERN ENGINEERING IN GALEVILLE, WISCONSIN At approximately 1500 CDT, the licensee discovered that an americium-241 source with an activity of about 11 millicuries was missing from the Galeville facility. It had previously been used as a static eliminator. Apparently, the licensee discontinued use of these static eliminators some time ago. Two had been returned to the supplier (NRD), one was found in an unusual location, and one was unaccounted. The licensee stated that the corporate office was located in Sparta, Wisconsin. The licensee notified the NRC Region 3 office (Mike Lafranzo). (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-04-16
38856 | 0 | MICHIGAN DEPT OF ENVIRONMENTAL QUAL |  |  |  |  | 2002-03-15 | 2002-04-15 16:00 | 2002-04-15 | LOSS OF POLONIUM-210 STATIC ELIMINATOR "This letter is pertinent to the lost of an anti-static air gun. The model number is P-2021. The serial number A2AW9S4 is on lease number 007136 and was shipped on 3/19/01. The device was used for spraying acrylic and also to prevent dust. The device was used in the Plastic Shop. It was last used during the month of August, 2001. To my knowledge, the device was misplaced or stolen. The efforts that was made was searching of the shop and questioning the shop personnel. This situation has been brought to management attention, The decision was made to not replace the anti-static gun." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-04-17
38855 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2002-04-15 07:33 | 2002-04-15 12:04 | 2002-04-15 | DEGRADED PRESSURE BOUNDARY AT ARKANSAS NUCLEAR ONE UNIT 2 "Boron deposits were discovered on five pressurizer heater sleeve penetrations during visual inspection. Two additional heater penetrations are suspected of leaking, but further inspection activities are required to confirm these leaks. Pressurizer heater sleeve penetration leakage is considered RCS pressure boundary leakage. Small amounts of boron were discovered at each of the five nozzle penetration interfaces. Prior to shutdown for refueling, RCS unidentified leakage was about 0.22 gpm. Currently, Unit 2 is in reduced inventory with the pressurizer empty." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-04-15
38854 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-15 00:16 | 2002-04-15 02:59 | 2002-04-15 | PLANT HAD ESF ACTUATION RESULTING IN AUTOMATIC REPOSITIONING OF AUX FEEDWATER VALVES. Unit 2 was in mode 3 and stable following the completion of a preplanned shutdown for a refueling outage. The aux feedwater was in service at the time of this actuation. The AFW Level Control Valves had been throttled, the "B" Main Feedwater Pump reset and Feedwater Isolation (FWI) reset to accordance with procedures. The RCS Tavg drifted above 550°F. When the RCS Tavg dropped below 550°F, a FWI signal was generated causing the reset Main Feedwater Pump to trip and the Aux Feedwater valves to reposition open. The Aux Feedwater pumps were already running. An investigation is ongoing. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-04-15
38853 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-04-14 12:00 | 2002-04-14 16:25 | 2002-04-14 | POTENTIALLY CONTAMINATED PERSON TRANSPORTED OFFSITE BY AMBULANCE. This report is being made to communicate the transportation of a potentially radioactive contaminated person to an offsite medical facility for treatment under 10CFR 50.72 (b)(3)(xii). At 1138 EDT the Unit 1 Control Room was notified that an individual had fallen on the Refueling Floor striking her head on the floor. The First Responders and Health Physics personnel responded to attend the individual and requested that the injured person be transported offsite to the Appling General Hospital in Baxley, Ga. At 1200 EDT the individual was transported offsite via ambulance. The individual left offsite prior to the initial onsite survey for radioactive contamination had been completed. This report is being made since there was a potential for contamination. The initial survey was completed at the hospital and it was determined that neither the individual nor any clothing was contaminated. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2002-04-14
38852 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2002-04-13 13:17 | 2002-04-13 14:51 | 2002-04-13 | LOSS OF ERDADS/ERDS The licensee reported that the Emergency Response Data Acquisition and Display System (ERDADS) and Emergency Response Data System (ERDS) became inoperable due to the loss of both trains of the Data Link System. The licensee is currently attempting to restore the DLS. The NRC resident inspector will be informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-04-13
38850 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-12 08:38 | 2002-04-12 17:37 | 2002-04-12 | FITNESS FOR DUTY REPORT A contract supervisor tested positive for alcohol use during a for-cause test. The individual's site access has been terminated. Contact the NRC Operations Center for additional information. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2002-04-12
38849 | 0 | WYLE LABORATORIES |  |  |  |  | 2002-04-12 | 2002-04-12 17:05 | 2002-04-12 | 10 CFR PART 21 REPORT "Pursuant to the 10 CFR Part 21 requirements, this letter notifies the NRC of a Potential Part 21 condition. "An error in irradiation dose units is identified in the attached letter from Georgia Tech letter dated March 15, 2002, which was received by Wyle on April 11, 2002. The error applies to all equipment irradiated with the cobalt-60 sources in the Georgia Tech hot cell from 7/24/1997 to 7/6/2001. Georgia Tech reported radiation doses in units of rads-air (absorbed dose in air) instead of Roentgens. Since one Roentgen is equal to 0.877 rad, the actual dose is less than the reported value. "Wyle will perform an evaluation to determine "1. Wyle projects that include irradiation with the cobalt-60 sources in the Georgia Tech hot cell from 7/24/1997 to 7/6/2001. "2. The actual dose absorbed by equipment in said projects. "3. Whether the actual dose in said projects envelops the customer-specified requirements. "Wyle Laboratories has the capability and chooses to perform the evaluation to determine if a defect exists. It is the responsibility to Wyle Laboratories to inform the purchaser(s), and any affected licensees. "Wyle will complete the specified evaluation of the circumstances within sixty (60) days of discovery of the potential defect. The NRC will be provided a copy of Wyle's evaluation report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | AL | OTH | PAR | 21.21 |  |  |  | 0 | 2002-04-12
38848 | 0 | BRISTOL-MYERS SQUIBB |  |  |  |  | 2002-04-12 | 2002-04-12 16:15 | 2002-04-12 | POTENTIAL OVEREXPOSURE OF EXTREMITIES While investigating high ring dosimeter readings for two radiopharmacists involved in dispensing doses of Tc-99m, the licensee discovered that these individuals may have exceeded their occupational dose limits to the extremities for 2001. Ring dosimeter readings of 30-40 rem were recorded for the individuals. During followup investigations, a certified health physicist, using fingertip dosimetry, determined that the individuals were receiving fingertip doses 3 to 7 times higher than those recorded on the ring dosimeters. Therefore, the individuals may have exceeded the annual occupational dose limit of 50 rem to the extremities. The licensee will be providing a report to NRC Region II next week. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 2 | PR | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2002-04-12
38847 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-04-11 09:30 | 2002-04-11 13:42 | 2002-04-11 | CONTROL ROOM VENTILATION SYSTEM INOPERABLE "At 1835 on 4/10/02, the Control Room Emergency Ventilation system automatically repositioned to the 'purge' mode due to an apparent faulty smoke detection circuit. It has been subsequently determined that while in the 'purge' mode, the system is incapable of performing it's required safety function. The Control Room Emergency Ventilation system is a single train system utilized to mitigate the consequences of an accident and this event is reportable under 10 CFR 50.72 (b) (3) (v) (D)." The NRC Resident Inspector has been notified. | 0 | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-04-11
38846 | 0 | BETHLEHAM STEEL |  |  |  |  | 2002-04-10 08:00 | 2002-04-11 09:41 | 2002-04-11 | SHUTTER FAILED TO OPEN ON A DMC/RADIOMETRIE GAUGE. A DMC/Radiometrie Model E6 source housing shutter failed to open. The licensee swapped out the housing and will send the defective housing back to Radiometrie, located in Gaithersburg, MD. The DMC/Radiometrie Model E6 gauge contains one curie of Americium-241 which is used to measure the thickness of thin sheets of steel. Bethlehem Steel Company has 30 or 40 of these in the plant and this is the first time that a shutter on one of these gauges has failed to open. The licensee stated that they have had these gauges since the 1970's. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-04-11
38845 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-10 18:30 | 2002-04-10 20:44 | 2002-04-10 | OFFSITE NOTIFICATION OF ADEQUACY OF SECURITY QUESTIONED IN PRESS RELEASE "On April 10, 2002 Representative Edward Markey, (D-MA), issued a press release alleging that security clearance practices for temporary access in vital areas at US nuclear plants is not sufficient. Representative Markey within the body of a letter to NRC Chairman Meserve states that a senior security officer at Salem raised concerns about the adequacy of the NRC's security background check requirements and that temporary workers with less than a complete background check were allowed in vital areas without being escorted by security officers. "The NRC issued an order on February 25 directing specific activities to increase security at all commercial nuclear power plants. The information and specifics of the order is confidential and cannot be shared. The order also gave each nuclear utility until August 31, 2002 to come into compliance with the specifics of the order. "One component of the order issued, referred to vital area access control for workers with temporary security clearance. PSEG Nuclear developed a program to come into compliance with this particular element of the order, and implemented the program prior to the start of the current refueling outage. We are confident that our program, as designed, is in compliance with the NRC order, and that we have fully implemented the stringent requirements of our own security program. "Since media interest may be generated by Representative Markey's press release, PSEG Nuclear is making a 4-hour report in accordance with 10CFR50.72(b) (2) (xi)." The licensee made state (NJ & DE) and local (LAC township) notifications of this event. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-10
38844 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-04-10 04:00 | 2002-04-10 16:29 | 2002-04-10 | OVEREXPOSURE TO GAMMA RADIATION The following is taken from a facsimile report: "A radiographer was [radiographing] welds on a vessel shooting with a 35 curie Co-60 source and entered the vessel to change the source location without cranking the source into the shielded position. The radiographer has been taken for blood samples which will be repeated in 72 hours. Initial calculations indicate a possible whole body exposure of 70 rems. Further information forthcoming after investigation scheduled for May 14." The Texas Incident Number for this event is I-7882. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-04-12
38843 | 0 | VA NATIONAL HP PROGRAM |  |  |  |  | 2002-04-09 08:31 | 2002-04-09 10:25 | 2002-04-09 | RECEIPT OF PACKAGE WITH A CONTAMINATED LABEL A magnetic label on a radioactive transport container (metal "ammo" box') was found to be contaminated with Technetium-99m upon arrival at the VA Medical Center in Birmingham, AL. This was found during a receipt inspection survey and the contamination level was 70 DPM/CM squared. The package originated at Central Pharmacy in Birmingham, Alabama. The vendor and the State were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | AL | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2002-04-09
38842 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2002-04-08 19:07 | 2002-04-08 20:55 | 2002-04-08 | OFFSITE NOTIFICATION OF MINOR OIL SPILL "IAW [In Accordance With] AP-09.03, Oil Spill Prevention Control and Countermeasures Plan, reported to NYSDEC and USCG National Response Ctr [an] oil spill in which oil and lubricant [less than 1 gallon] washed off a road sander during rain showers entered storm drain. Slight sheen observed at outfall for storm drains to Lake Ontario." The NRC Resident will be notified of the event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-08
38841 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2002-04-08 15:15 | 2002-04-08 18:15 | 2002-04-08 | OFFSITE NOTIFICATION OF FATALITY At 1300 EDT on 4/8/2002 a contract worker was transported from the site by ambulance to Mid Coast Hospital in Brunswick, Maine. Prior to being transported, the worker was treated by onsite EMT and other medical personnel. The worker was not working in a radioactive contaminated area and was not contaminated at the time of the event. The licensee later learned that the worker died of an apparent heart attack. The licensee safety department reported the death to OSHA at 1515 EDT. The licensee reported that R1 (Randy Ragland) has been notified of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-08
38840 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2002-04-08 10:52 | 2002-04-08 17:13 | 2002-04-08 | UNSUCCESSFUL TEST OF THE SIREN SILENT TEST "During the siren silent test performed on 4-08-02 at the Cobbs Hill location, all sirens indicated failure to reply. A subsequent test was performed from the Monroe County 911 center. All sirens indicated failure to reply. A single activation test on siren #1 in Monroe County was performed. The siren did not receive a signal to activate. Continuous radio traffic was detected on the siren radio frequency. This prevented a signal from being received by the sirens. Wayne and Monroe County were notified to utilize route-alerting procedures in the event that notification to the public was necessary. A technician was dispatched with a radio signal detection instrument to determine the source of the radio traffic on thc siren frequency. Siren #22 in Monroe County was found to have a strong continuous active radio signal. Siren #22 was de-energized and the continuous radio signal stopped. Siren #22 is quarantined as part of a root cause investigation. Follow up testing is planned." The NRC Resident Inspector was notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-04-08
38839 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2002-04-08 03:00 | 2002-04-08 11:03 | 2002-04-08 | LOSS OF EMERGENCY PREPAREDNESS CAPABILITIES "At 0300 one of the two belts on the Emergency Outside AIR Fan (OAF-2) for the Technical Support Center (TSC) / Operations Support Center (OSC) was found broken. The other fan belt appeared to be degrading rapidly. The fan was taken out of service. OAF-2 provides outside air to the TSC / OSC that is filtered. Unavailability of this fan could prevent the use of the TSC / OSC in the event of a radiological release. "Station Procedure 5.7.7, activation of the TSC section 4, Evacuation of the TSC, provides guidance for the evacuation of the TSC and the relocation of TSC personnel. Station Procedure 5.7.8.1, Activation of the Alternate OSC, provides guidance for the evacuation of the OSC and the relocation of OSC personnel. In the event of an emergency that requires activation of the TSC / OSC, the TSC / OSC will be activated and atmospheric monitoring will be performed in accordance with existing station procedures. If conditions require the evacuation of the TSC / OSC, TSC / OSC personnel will be relocated in accordance with existing station procedures. "Currently repairs to replace the belts on OAF-2 are underway. OAF-2 should be returned to service today." The NRC Resident Inspector has been notified. * * * UPDATED ON 03/08/02 AT 1542 EDT BY WILLIAM GREEN TO GERRY WAIG * * * "At 1340 CDT OAF-2 was returned to service after a replacement of the damaged belts. The fan has been inspected by Maintenance and determined to be operating properly. Damage to belts appears to be from normal wear." The NRC Resident Inspector was notified by the licensee. R4DO (Kriss Kennedy) was notified by the Headquarters Operations Officer. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-04-08
38838 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-04-06 13:14 | 2002-04-06 20:37 | 2002-04-06 | SPECIFIED SYSTEM ACTUATION -- FULL REACTOR SCRAM (WHILE SHUTDOWN) DURING THE PERFORMANCE OF CONTROL ROD DRIVE SYSTEM TESTING AND TROUBLESHOOTING The following text is a portion of a facsimile received from the licensee: "During [the] Unit 3 Cycle 10 Refueling outage, while performing 0-TI-20, CONTROL ROD DRIVE SYSTEM TESTING AND TROUBLESHOOTING, a full reactor scram occurred while resetting a half scram on channel 'B.' One rod was withdrawn and being inserted for timing [in accordance with (IAW)] 0-TI-20 and was at approximately position 26 when the scram occurred. The rod scrammed in as expected. All other rods were already fully inserted. The initial investigation indicates that during the resetting of the half scram, an auxiliary contact in the 'A' channel of [reactor protection system (RPS)] momentarily picked up in conjunction with a stuck contact in the 'B' channel, energizing the backup scram valves and initiating a scram on low scram pilot air header pressure. Testing IAW 0-TI-20 was stopped, and personnel were dispatched to investigate the cause of the loss of scram pilot air header pressure." "This event is reportable as an 8-hour report per 10CFR50.72(b)(3)(iv)(A) as any event or condition that results in valid actuation of any of the systems listed in (b)(3)(iv)(B), specifically RPS. This is also reportable per 10CFR50.73(a)(2)(iv)(A) for the above conditions as 60-day written report." The licensee stated that there was nothing unusual or misunderstood. The licensee also stated that all systems functioned as required. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | A/R | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-04-06
38837 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-04-05 22:00 | 2002-04-05 22:52 | 2002-04-05 | OFFSITE NOTIFICATION REGARDING COMMENCEMENT OF A UNIT SHUTDOWN FOR MAINTENANCE The licensee notified state and local officials of commencement of a unit shutdown for maintenance purposes. The shutdown was commenced at 2100 because 'A' reactor coolant pump seal package assembly leakage was becoming excessive. The outage is currently scheduled to last between 72 and 96 hours. Event classification for the offsite notification was made at 2200. The licensee also notified the NRC resident inspector. | 0 | 79 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-05
38836 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-05 15:10 | 2002-04-05 17:08 | 2002-04-05 | TECHNICAL SPECIFICATION 3.0.3 ENTRY DUE TO INOPERABILITY OF BOTH RESIDUAL HEAT REMOVAL SYSTEM TRAINS FOLLOWING THE DISCOVERY THAT A DISCHARGE CHECK VALVE WAS STUCK OPEN The following text is a portion of a facsimile received from the licensee: "Unit 2 entered [Technical Specification] 3.0.3 at 1510 due to both trains of [the] residual heat removal systems being inoperable. During the performance of [a] residual heat removal/containment spray systems dose reduction flush procedure, it was determined that the discharge check valve for [the] 2A residual heat removal pump was stuck open. This diverted flow from the operable train (2B). The 2A residual heat removal pump discharge isolation valve was closed at 1523, and Unit 2 exited [Technical Specification] 3.0.3. The 2A residual heat removal system was logged inoperable under a 72-hour [technical specification limiting condition for operation] until the check valve is repaired." The licensee stated that all systems functioned as required and that the cause of the discharge check valve failure was under investigation. The licensee also stated that there was nothing unusual or misunderstood other than the cause of the discharge check valve failure. The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2002-04-05
38835 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-04-03 13:00 | 2002-04-05 15:29 | 2002-04-05 | AGREEMENT STATE REPORT REGARDING YTTRIUM-90 CONTAMINATION OF THE HARRISON MEMORIAL HOSPITAL NUCLEAR MEDICINE HOT LAB DUE TO RECEIPT OF AN IMPROPERLY SEALED OR PACKAGED INNER CONTAINER SENT FROM TACOMA CENTRAL PHARMACY The following text is a portion of an e-mail received from the Washington State Department of Health, Division of Radiation Protection: "Licensee: Harrison Memorial Hospital City & State: Bremerton, Washington License #: WN-M0168-1 Type license: Nuclear Medicine" "Date of event: April 3, 2002 Event Location: Nuclear Medicine Hot Lab" "Abstract: Harrison Memorial (licensee) reported that they had received a nuclear medicine shipment, at about noon on April 3. It went directly into the hot lab after going through preliminary receipt procedures at the licensee's receiving department. The shipper was Tacoma Central Pharmacy, License Number WN-NP005-1. The licensee reported that the shipment had checked in normal including negative dose-rate and wipe receipt surveys. The shipper indicated the activity and isotope to be 24.8 millicuries of yttrium-90. The dose was unpackaged and placed into the dose calibrator for activity verification. At that time, it measured 18.5 millicuries." "The CNMT realized there was a problem and began to look for the remainder of the dose. Extensive wipe and direct surveys of the hot lab and other areas were performed. The majority of the dose had spilled and remained inside the transportation box (ammo can). Contamination was also found in the hot lab. Prior to being cleaned, the CNMT found between 1700 to 3500 counts per minute on the hot lab counter top and 1700 cpm at the 'L' shield block. The CNMT had used gloves and wore usual hot lab clothing so was not personally contaminated. The CNMT decontaminated the affected areas. A large trash bag of waste was collected. The CNMT was the only person involved in the incident. All activity was contained within the nuclear medicine hot lab. The pharmacy will be responsible for disposal of the waste." "The CNMT discovered and cleaned up prior to notifying the department. A report with surveys from the licensee is forthcoming. The apparent cause of the incident was an improperly sealed or improperly packaged inner container (syringe) sent from the pharmacy. Both the licensee (Harrison Memorial) and Tacoma Central Pharmacy are due for routine inspections. The incident will be investigated during each of those inspections. The investigation will remain open until on site inspections are complete." (Call the NRC operations officer for state contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-04-05
38834 | 0 | HOWARD UNIVERSITY HOSPITAL |  |  |  |  | 2002-04-04 16:30 | 2002-04-05 15:27 | 2002-04-05 | LOST LICENSED MEDICAL MATERIALS >1000 TIMES LIMIT RSO at Howard University Hospital reported that a 2.6 millicuries of Ir-192 was lost. The material was in ribbon form, containing 4 seeds and was used for brachytherapy on a patient. The material was believed to have been lost down the sewer system (which is an unmonitored system). The patient and work areas were surveyed with negative results. The material is reported to be reading 1 mRem/hr at 1 meter and has a half life of 74 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-04-05
38833 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2002-04-05 10:28 | 2002-04-05 14:26 | 2002-04-05 | MANUAL REACTOR SCRAM ON HIGH RPV LEVEL "At 10:28 [CST] on 04/05/02, Unit 2 inserted a manual SCRAM due to RPV high water level. All control rods inserted to 00 with the manual SCRAM, reactor pressure was maintained with the turbine bypass valves, reactor level was restored to normal and is being controlled with the feedwater system. Group 2 and 3 isolations initiated on low reactor level as expected. Initial investigations are focusing on a potential failure of reactor water level instrumentation, sensing a false low level which caused increased feedwater flow. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv) and 10 CFR 50.72(b)(3)(iv)." Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-04-05
38832 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-04 21:14 | 2002-04-04 23:30 | 2002-04-05 | INITIATION OF TS REQUIRED SHUTDOWN AT COOK INVOLVING BATTERY SURVEILLANCE TEST "At 1812 04/04/02 Cook Unit 2 entered T.S. action statement 3.8.2.3.b due to 250 vdc battery, 2-Batt-AB. having 3 cells exhibiting cracking on top covers between the post seal and the sample tube. Cook U-2 Surveillance T.S. 4.8.2.3.2.c.1 requires '....no visual indication of physical damage or abnormal deterioration.' Since literal compliance with the T.S. was not maintained, the LCO for T.S. 3.8.2.3.b was entered . This LCO allows 2 hours for return the battery to OPERABLE status or be in at least HOT STANDBY within the next 6 hours. The battery was not returned to OPERABLE within 2 hours and initiation of the Unit shutdown was commenced at 21:14 on 04/04/02. Unit shutdown required by the plant's T.S.s is a 4 hour report to the NRC as per 10 CFR 50.72(b)(2)(i). This is that required report." The NRC Resident Inspector was notified. * * * UPDATE 0155 4/5/2002 FROM COBB TAKEN BY STRANSKY * * * The unit shutdown has been terminated. A Notice of Enforcement Discretion (NOED) has been granted to the licensee by the NRC. The NRC resident inspector has been informed. Notifed R3DO (Hills). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-04-04
38831 | 0 | GUARDIAN AUTOMOTIVE, INC |  |  |  |  | 2002-04-04 | 2002-04-04 14:25 | 2002-04-04 | TWO STATIC ELIMINATORS DISCOVERED MISSING "Guardian Automotive, Inc. is using this letter to notify your agency that two (2) isotopes cannot be accounted for at our facility. The isotopes contained Polonium 210 with 0.04 total Curies each. "The isotopes are found in a device used to air spray plastic parts to reduce the static charge prior to the part being painted. Guardian Automotive, Inc. received the devices on approximately 2/28/01. Serial numbers of the devices were A2AV902 and A2AV903. Guardian Automotive, Inc. currently utilizes approximately 20 of these devices at the Evansville Plant. "The devices were last used in mid-January (2002) in Department #23A for the purpose described above. An extensive search was conducted upon realizing that the devices were missing. It appears that the barrel of the device that contained the isotope was broken off from its handle and could not be located during the search. "Guardian Automotive, Inc. has written procedures for handling and tracking these devices as part of our QS 9000 and ISO 1.4001 systems. These systems have been effective over the past several years to accounting for approximately 20 devices in other departments. "Department #23A has not used such devices since the time of the incident. A daily check sheet will be utilized by Department #23A should they go back to using the devices. Furthermore, all employees that use the devices in Department #23A will be retrained on internal written QS 9000 and ISO 14001 procedures." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-04-04
38830 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2002-03-27 09:00 | 2002-04-04 11:30 | 2002-04-04 | LOST/STOLEN LNM>10X "Background "DEMCO placed vacuum cleaner 01-589 into service 10/11/01 for use in accordance with Radiological and Environmental procedures. The vacuum cleaner was labeled with PCB, Hazardous Waste and Radiological stickers based on anticipated use for paint abatement. The vacuum cleaner location was verified weekly during RCRA Satellite Area inspections and monthly during PCB inspections. In late January the vacuum cleaner was moved to the Waste Disposal Building for personnel decon of asbestos workers. Weekly and monthly inspections of the vacuum cleaner's location continued including a weekly inspection that was performed on Thursday 2/21/02. "On Monday morning 2/25/02, DEMCO workers could not find the vacuum cleaner where they had left it. "Immediate Actions "2/25/02 DEMCO personnel searched areas that were likely to contain the vacuum cleaner (including all levels of the Waste Disposal Building, the hazardous waste storage area of the PAB, the RRF, the Hot Shop, and PCB storage areas). "2/25/02 DEMCO enlisted Bechtel and HP personnel to help in the search and to validate the vacuum cleaner inventories. "2/25/02 The night shift workers, who were cleaning up the area, were questioned about the vacuum cleaner, but could provide no insight into the vacuum cleaner's whereabouts. They were requested to look for the vacuum cleaner. "2/26/02 A CR was written in the morning. "Subsequent Searches "Various informal and formal searches have been performed by DEMCO, Bechtel labor, HP Ops, Duratek, CY Ops and Bechtel Management. "Seven suspect B-25 boxes and six suspect seavans were searched by removing their contents completely. These containers had been loaded in the relevant timeframe or contained asbestos. "Areas searched (including grid by grid searches) include the Waste Disposal Building, PAB, Containment Building, Turbine Building, Pipe Chase and Pipe Trench, Service Building, Auxiliary Boiler Room, Diesel Generator Building, Screenwell House, Administration Building, Spent Fuel Building, Radwaste Reduction Facility, Spent Resin Facility, CY Maintenance Shop, Fire Brigade Shop, Chemical Warehouse, Resin Storage Building, Recycle Warehouse and Operating Engineers Maintenance Shop, Steam Generator Mock-up Building, Storage Seavans, and asbestos enclosures. "The vacuum cleaner was not found during these searches." The NRC Resident Inspector has been notified. The state of CT Department of Environmental Protection has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-04-04
38829 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-02-06 09:30 | 2002-04-04 09:25 | 2002-04-04 | 60 DAY REPORT-INVALID SPECIFIED SYSTEM ACTUATION "This 60 -day optional report as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Nuclear Service Water System (NSWS). On February 6, 2002, at 0930, with Unit 1 in MODE 1 at 100% power and Unit 2 in MODE 1 at 100% power, an invalid actuation of the NSWS suction transfer on Low Pit Level was generated from NSWS train B on Unit 2. Maintenance technicians were in the process of implementing a plant modification to replace a relay in the Unit 2, Train B, NSWS suction transfer circuit. As a part of the plant modification, an isolation plan had been developed by engineering to prevent any actuation of this circuit. However, upon removal of the relay, the NSWS suction transfer on low pit level occurred. The control room operators entered appropriate procedures and verified proper equipment operation for the exiting plant conditions." "This was a complete actuation for Train B and the system performed as designed for the existing plant conditions. At the time of the invalid signal, the NSWS system had been transferred from the normal supply (Lake Wylie) to the backup supply [Standby Nuclear Service Water Pond (SNSWP)] and appropriate valves had been already repositioned. This event has been entered into the site specific corrective action program for resolution." The Licensee has notified the NRC Resident Inspector. The Licensee will be notifying the states of NC and SC, and will be notifying local (York, Gaston and Meekenburg) counties. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-04-04
38828 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2001-10-17 | 2002-04-03 16:05 | 2002-04-03 | AGREEMENT STATE REPORT OF MEDICAL MISADMINISTRATION "On October 17, 2001 a patient was being treated with a P-32 impregnated balloon. This balloon is part of an FDA study sponsored by Radiance. This treatment is designed to be a sequence of inflations and deflations at the treatment site. During the record review on March 21, 2001, the patient was feeling significant discomfort, so the Doctor ordered for the balloon to be deflated. Since there was a deviation in protocol, all records were appropriately documented. "During the record review on March 21, 2002, it was noted that the order for the treatment to be given in the deflated state was approximately half of the original order. The order was supposed to be that the entire treatment time would be in the deflated stage, but unfortunately, only the deflated stage was administered. The dose was approximately 11 Gy (55%) of the original order of 20 Gy. No other deviations were noted. "The patient and primary physician have been notified. Procedures are in the process of being reviewed to ensure future compliance. The name and identification number of the patient involved has been attached on a separate sheet." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-04-03
38827 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-04-03 11:59 | 2002-04-03 15:54 | 2002-04-19 | 24-HOUR NRC BULLETIN 91-01 (CRITICALITY CONTROLS) ISSUE AT PORTSMOUTH GASEOUS DIFFUSION PLANT "At 1159 hours today after Nuclear Materials Engineering completed a review of their databases for batched items stored in 55 gal. drums, it was discovered that 26 drums with questionable Segmented Gamma Scanner (SGS) values were located in the XT-847. The concern about the SGS not correctly counting the U-235 mass was identified earlier but at that time no drums were identified in the United States Enrichment Corporation (USEC) leased spaces. The mass counting error identified between the SCS and the Low Density Waste Assay Monitor (LDWAM) was at times off by a factor of 10 or more. Because of the questionable SGS measurements it could not be assured the 350 gram U-235 limit per batched drum was maintained. The governing NSCA X-0847_ 001. A04 Operation of the XT-847 Facility in it's NCSE accounted for an error of a factor of two in mass calculations, as a bounding condition. Thus with the loss of the bounding calculations and the potential error in mass calculations, this resulted in the loss of both legs of the double contingency basis (mass & the factor of two bounding error) for NCSA X-847_001.A04. At the present time Waste Material handlers in the XT-847 are moving all 26 drums from their storage area to another storage location within the building to allow for remeasurement of the drums. The guidance for moving and relocating these drums for remeasurement is covered by existing procedures and NCSAs. "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is low because the actual uranium mass content of the drums in question would not be expected to contain more than a safe amount of uranium bearing material. Other similar drums of trapping material batched during the same period using LDWAM measurements contain considerably less than a safe mass of U-235. The uranium mass limits assume optimum moderation and 100% enrichment. The drums in question are known to contain less than 10% enrichment (based upon process knowledge or sampling) and the material stored in the XT-847 is dry trapping material (alumina, etc). Even with the maximum potential error in the SGS measurements, the total mass in any drum (or group) would be less than the safe mass of uranium at an H/U of 4 (wet air moderation of approximately 7.9 kg of U-235 (100% enrichment) "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events would be required: One or more drums must contain greater than a minimum critical mass of uranium (at this time, the measurement results are in question, but greater than a safe mass has not actually been measured in any drum), the contents of the drums would need to be moderated by water or oil (the material is dry trapping material), and some amount of reflection would be required (for the drums, or groups of drums, currently spaced 2 feet edge-to-edge apart). "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY. CONCENTRATION, ETC.): The drums were filled by batching small diameter containers of trapping material based upon NDA or sample measurements of the uranium mass present. The batching limits are 43.5% of the minimum critical mass assuming optimum moderation, concentration, geometry, reflection, etc. In the applicable NCSE, credit is taken for a double batch scenario bounding potential uranium mass upsets; however, the potential error in the SGS measurements may be greater than a factor of two. Spacing is controlled for drums, or groups of drums, unless categorized as containing less than 15 grams U-235. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The contents of the drums are dry trapping material from the cascade buildings, and are known to be enriched to 10% or less. At the time they were filled, the total mass was calculated to be less than 350 grams U-235. However, the SGS used to measure source containers has been questioned. The variability of the SGS results indicate that the total uranium mass in containers batched into a drum could be non-conservative by a factor of 10 or more. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Recent NDA measurements performed on the Low Density Waste Assay Monitor (LDWAM) have identified discrepancies in the gram quantity of U-235 when compared to the Segmented Gamma Scanner (SGS) measured values (see PR-PTS-02-01398). The SGS values are biased low which could have resulted in underestimatlng the total batch quantity for previously batched drums. Until confirmatory measurements of the drums are obtained, the potential mass content represents a loss of both legs of double contingency as described in the applicable NCSE. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: These drums are not safety systems but corrective actions to regain compliance was started at 1530 hours 4/2/02." The NRC Resident Inspector was notified by the certificate holder. ****UPDATE 4/19/02 at 1533, J. McCleery to R. Laura**** "Update 1: There is no safety significance for this event because all 21 drums have now been confirmed to contain less than a safe mass for the enrichment of material. While one drum was found to exceed the 350 grams U-235 control limit. The actual U-235 mass is less than a safe mass and the process conditions credited for double contingency were maintained. All potential drum groups that could have exceeded 350 gram U-235 were examined, the maximum mass for a drum group would have been approximately 620 grams U-235, at a maximum of 5% enrichment. Therefore, all drum groups would have been below safe mass at process conditions. Criticality was determined noncredible given the new measurements for these drums." Notified R3DO (J. Madera) and NMSS (F. Brown) of this update. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-04-03
38826 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2002-04-03 02:30 | 2002-04-03 17:05 | 2002-04-03 | 24-HOUR NRC BULLETIN 91-01 (CRITICALITY CONTROLS) ISSUE AT FRAMATONE ANP RICHLAND "Background: FRA-ANP routinely uses 45-gallon drums that contain a neutron absorbing spider assembly for processing and storing unmoderated urania powder. The spider assembly is inserted into the drum and bolted to the drum bottom. This spider assembly is designed such that it will prevent criticality in a single drum even if the drum is accidentally filled with an optimum mixture of UO2 and water and is also fully reflected by water. Accidental disassembly is prevented by the spider assembly design. However, when a drum reaches the end of useful service, or if the drum will no longer be used for dirty or Gd contaminated powder, the neutron absorbing spider assembly is removed and reused with a new 45-gallon drum. The old drum sans insert is then destroyed. "Event Description: On swing shift April 2, 2002 process operators removed the neutron absorbing spider assemblies from three 45-gallon drums per standard operating procedure (SOP). Operators moved these three drums to the old waste area. "Around midnight, a process operator retrieved one of the 45-gallon drums in the old waste area instead of going to the powder storage area to retrieve a 45-gallon drum. He transferred it to a nearby utility hood and used it to prepare a blend of unmoderated dirty urania powder for subsequent dissolution. The process operator failed to perform a required visual inspection of the interior of the 45-gallon drum prior to transferring 250 kg of urania powder enriched to 2.7 wt.% U-235 into it. The same process operator secured the lid and transferred it per SOP to another process enclosure where the drum lid is removed and a drum tumbling lid is installed. When the process operator removed the drum lid at about 0230, he noticed the drum did not have a neutron absorbing spider assembly and contacted supervision. Supervision immediately contacted Criticality Safety. "Safety Significance of Event: The safety significance of this event is low. The urania powder placed in this drum was known in advance to contain less than 1 wt.% moisture equivalent hydrogen. Two process operators had previously verified the material had acceptable laboratory analysis results and that the correct material had been selected for the blend. "A sphere of 250 kg UO2 powder enriched to 5 wt.% U-235, with a bulk density of 4 g/cc, and containing 10 wt.% water that is fully reflected by water has a keff of 0.95. Therefore, the material in the drum would have to have more than 10 times the limit before criticality could occur in the drum. "Potential Criticality Pathways Involved (Brief Scenario(s) Of How Criticality Could Occur): Criticality could only occur if moderation control on the material placed in the drum is lost. This could hypothetically occur if powder containing over 10 times the allowed limit were placed into the drum or if a similar amount liquid water entered a drum from an external source. "Controlled Parameters (Mass, Moderation, Geometry, Concentration, Etc.): The process parameter controlled in this portion of the process is moderation. An additional design control is the neutron absorbing insert. When installed, this insert will keep the drum sub-critical even if moderation control is completely lost in a single drum. "Estimated Amount, Enrichment, Form of Licensed Material ( Include Process Limit and % Worst Case Critical Mass): The amount of material involved is 250 kg of urania powder enriched to 2.7 wt.% U-235. The material contained <0.2 wt.% moisture. The process limit is 1.0 wt.% moisture. More than 10 wt.% water and a full water reflector is required for keff to exceed 0.95 at 5.0 wt.% U-235. "The minimum critical mass for optimally moderated urania powder enriched to 2.75 wt.% U-235 with full water reflection is about 124 kg. "Nuclear Criticality Safety Control(s) or Control System(s) and Description of the Failures or Deficiencies: The moderator control system requires that any material placed into a 45-gallon drum have at least on assurance that the material contains less than 1.0 wt.% moisture. The moderation control system includes two operators verifying that acceptable lab analysis results have been obtained and that the correct material has been selected for being dumping into a 45-gallon drum. These operators are also aided by a computer controlled inventory system that also checks for acceptable moisture results on each item being placed on a blend make up list. "In addition to moderation control, the neutron adsorbing spider assemblies will keep the drum subcritical even if it is filled with optimally moderated UO2. This control failed because a drum without the required insert was inadvertently used in the process. This occurred because the process operator failed to perform a required visual inspection prior to filling the drum. Also, the operating procedure for disassembling 45-gallon drums with neutron absorbing spider assemblies did not require an out of service sign to be posted on the drum. "Corrective Actions To Restore Safety Systems and When Each Was Implemented: Manager of Criticality Safety convened an Incident Investigation Board at 0330. "The material involved was transferred to a drum containing a neutron absorbing spider assembly and handled per standard operating procedures. The transfer was completed by 0615. "All drums that do not contain neutron absorbing spider assemblies were tagged with out-of-service signs and then removed from the area and smashed. "Drum disassembly, and blend make-up operations have been placed on hold pending completion of procedure revisions and training. "Additional corrective actions are being evaluated." Framatome notified Region 4 (B. SPITZBERG). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 4 | WA | FUE | [5 empty] | 0 | 2002-04-03
38825 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2002-04-03 08:27 | 2002-04-03 11:34 | 2002-04-03 | FITNESS FOR DUTY REPORT INVOLVING CONTRACT SUPERVISOR A non-licensed contractor supervisor tested positive for alcohol during a for-cause fitness for duty test. The individual's site unescorted access has been removed. Contact the Headquarters Operations Officer for additional information. The NRC Resident Inspector was notified of the event by the licensee. The licensee also notified NRC Region 4 (Dennis Schaefer) of the event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.73 |  |  |  | 0 | 2002-04-03
38824 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-04-02 | 2002-04-02 22:35 | 2002-04-02 | POTENTIAL MEDIA INTEREST GENERATED DURING SITE TOUR "On April 2, 2002, at the request of the New Jersey National Guard, New Jersey State Assembly persons toured the owner controlled area and the security center of the Salem and Hope Creek Generating Stations. The tour did not include the protected area. Prior to the tour, National Guard personnel conducted a briefing for the Assembly persons regarding actions being taken by the National Guard in support of station security. In that briefing, the national guard attempted to communicate the level of threat that still exists and referenced general documents pertaining to nuclear power plants that were found in a cave in Afghanistan. This information was miscommunicated and the Assembly persons left with a belief that documents specific to Salem were found in a cave vs. general information related to nuclear power plants. Subsequently, in a debrief with the media following the tour, an Assembly person restated the misinformation that he understood from his briefing with the National Guard. Since media interest may be generated as a result of this tour, PSEG Nuclear is making a 4-hour report lAW 50.72(b)(2)(xi). To our knowledge, there has been no information before, and there is no new information regarding any credible threat against Salem and Hope Creek Generating Stations." The NRC Resident Inspector was notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-04-02
38823 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-04-02 10:40 | 2002-04-02 11:10 | 2002-04-02 | ALERT DECLARED DUE TO LOSS OF MCB ALARM ANNUNCIATORS Notified at 1110 EST by the licensee that 3 (three) annunciator panels (2H11-P601, P602, AND P603) were not functioning and that an alert was declared at 1040 EST. The plant remained operating at 100% reactor power. The NRC entered the monitoring mode at 1130 EST. "At 0955 eastern standard time, alarms started flashing in Unit 2 main control on panels 2HII-P601, P602 and P603. About half the alarms on each panel are constantly alarming and clearing. Operations and I&C immediately started troubleshooting per the HII abnormal operating procedure. The alarms still functioned when tested. At 1040 hours it was determined the alarms were not functional and an ALERT emergency was declared based on loss of most of the control room annunciators." The NRC Resident Inspector was notified. ***UPDATE 4/2/02 1255 EST Dees TO MacKinnon*** The licensee determined that a failure of an electrical supply to the panels was the source of the problem affecting all three annunciator panels. The power supply and a related inverter component were replaced and the annunciator panels restored to service. Subsequently, the licensee exited the Alert at 1237 EST. The NRC Resident Inspector was notified. At 1315 EST the NRC exited the Monitoring mode. The R2DO (R. Musser) was notified of exiting the Alert declaration. The NRC Status Officer notified the following federal agencies of this event: FEMA (K. Cyboch), DOE (J. Stambaugh), HHS (A. Kaufmann), USDA (R. Conley), EPA (Ms Bennett), and OHS(Dan Vanbuskirk). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-04-02
38822 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-04-02 00:29 | 2002-04-02 00:49 | 2002-04-02 | UNUSUAL EVENT DECLARED DUE TO FIRE SUPPRESSION SYSTEM CO2 DISCHARGE IN TURBINE BUILDING The licensee declared an unusual event at 0029 EST due to a broken hose reel on the turbine building fire suppression CO2 system during work activities. The turbine building, reactor building, radioactive waste building, and control building were evacuated. The control room was not evacuated. The broken hose reel was isolated to terminate the release of CO2. No personnel injuries were identified as a result of the event. The NRC Resident Inspector will be notified by the licensee. * * * UPDATE ON 4/2/02 AT 0123 BY ROGER LONGLEY TO GERRY WAIG * * * The licensee terminated the unusual event at 0120 EST. Notified R1DO (Glenn Meyer), NRR EO (Hannon) and FEMA (Ken Sweetser) * * * UPDATE ON 04/02/02 AT 1615 ET BY DAN CIFONELLI TAKEN BY MACKINNON * * * The licensee made the following clarification: The turbine building, reactor building, switchgear building, and the control building were evacuated. The radioactive waste building was not evacuated as stated above. R1DO (Meyer) notified. The NRC Resident Inspector was informed of this by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Refueling; FMode2: Refueling | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-04-02
38821 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-04-01 18:00 | 2002-04-01 21:23 | 2002-04-01 | CONTROL ROD DRIVE MECHANISM NOZZLE NO. 7 PENETRATION FOUND TO HAVE A SMALL LEAK PATH. Qualified visual inspection of the Unit 1 reactor vessel head Control Rod Drive Mechanism head penetrations found two penetrations with very slight boron accumulations. Ultrasonic testing of these penetrations has determined that one nozzle (No. 7, near the center of the reactor vessel head) has a potential reactor coolant system leak path. Any reactor coolant system leakage from penetration No. 7 would have been so small it would be below the threshold of measurability by the reactor coolant system leakage measurement processes. The leaking nozzle will be repaired prior to restart from the present refueling outage. The NRC Resident Inspector will be notified by the licensee of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-04-01
38820 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2002-04-01 14:36 | 2002-04-01 18:46 | 2002-04-01 | DURING SURVEILLANCE TEST "A" DIVISION OF CONTROL ROOM VENTILATION SYSTEM FAILED TO AUTOSTART ON A LOW FLOW SIGNAL. At 1436 CT on 04/01/02, during a low flow start surveillance test the "A" division of the Control Room Ventilation System failed to autostart. At the time, the "B" division was disabled in order to perform the test. Thus, the Control Room Ventilation System accident mitigation function was lost. Division "B" Control Room Ventilation was restored to operability at 1600 hours CT. The "A" division is operating with the control switch in the run mode. The cause of the failure to Autostart is under investigation. The NRC Resident Inspection will be notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-04-01
38819 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-04-01 09:17 | 2002-04-01 13:05 | 2002-05-17 | NITROGEN BACKUP SYSTEM FOR CHARGING PUMP SPEED CONTROL FOUND NOT TO SATISFY APPENDIX R FIRE ASSUMPTION. At 0917 CT on 04/01/02, it was determined that a condition identified on 03/28/02 potentially represents a significant degradation of plant safety during response to an Appendix R event. The Appendix R credited nitrogen backup system for charging pump speed control is unable to satisfy its design function of controlling Charging System flow to the Reactor Coolant System (RCS) for the time required to place the plant in Mode 5 (Cold Shutdown). During an Appendix R fire it is assumed that the normal motive force (instrument air) for charging control is unavailable and an installed backup is credited. This installed nitrogen system allows inventory control while in Mode 3 (Hot Standby) and is used to control RCS inventory and pressure while the RCS is cooled down and depressurized from Mode 3 (Hot Standby) to Mode 5 (Cold Shutdown). A nitrogen bottle 12-pack is calculated to last for approximately 8 hours. PBNP has 1 spare approved nitrogen pack on site - - it has been calculated that up to 15 spares would be required for 72 hours of charging pump operation. Mode 5 (Cold Shutdown) is expected to be reached in 30 hours but may be as long as 72 hours. This issue places the plant in an unanalyzed condition that has the potential to significantly degrade plant safety (RCS Inventory Control) and thus is reportable. The associated charging pumps have been declared out of service for Appendix R use and compensatory actions undertaken that establish appropriate fire rounds. Fire rounds will be continued until the condition is corrected or a suitable evaluation is completed. The NRC Resident Inspector was notified of this event by the licensee. ****RETRACTION ON 5/17/02 AT 13:10 FROM R. Robbins to R. Laura**** "ENS Event Notification #38819 was reported at 1205 CST on April 1, 2002. This event was reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) for identification of an unanalyzed condition that had the potential to significantly degrade plant safety. The condition involved postulated Appendix R fire scenarios for which the safe shutdown analyses assumes that the normal motive force for charging pump control (instrument air) is unavailable due to fire-induced damage. Certain Appendix R fire scenarios require the availability of a single charging pump, operable at greater than minimum pump capacity, in order to meet the Appendix R performance goal of maintaining adequate RCS inventory control without loss of pressurizer level. An installed back-up nitrogen supply is credited with maintaining the ability to control charging pump flow for the duration of the 72 hour Appendix R coping period. The unanalyzed condition identified in this notification was that the installed back-up nitrogen supply, based on a conservative calculation, would have adequate capacity to provide the motive force for the Single Charging pump control function for only 8 hours. After that time, the variable speed charging pump would run back to minimum speed, which equates to a pumping capacity of approximately 18 gpm. "We have subsequently completed an engineering evaluation to estimate the transient behavior of the RCS in the event of these Appendix R fire scenarios assuming only 8 hours of Charging pump speed control is available. This evaluation was based on conservative assumptions regarding reactor coolant pump seal leakage and unavailability of normal cooling and safety systems. This evaluation provided estimates of key RCS transient parameters based on engineering analysis and predicts that upon reducing the available charging pump flow to the pump minimum, pressurizer pressure and level will no longer be maintained. Although RCS sub-cooling is lost and some voiding in the RCS occurs, the core remains covered during the entire 72 hour Appendix R coping period and core cooling is maintained throughout the transient. "We have therefore concluded that this previously unanalyzed Appendix R scenario would not have resulted in a condition that would have significantly degraded plant safety. Therefore, this condition is not reportable under 10 CFR 50.72 and we are hereby retracting this event notification. "Until corrective actions are completed to ensure that the Appendix R safe shutdown performance goal to maintain reactor coolant inventory control within the level indication in the pressurizer can be satisfied, appropriate fire rounds will continue." The NRC Resident Inspector was notified. Notified R3DO (R. Gardner) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-04-01
38818 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-31 04:10 | 2002-03-31 05:32 | 2002-04-08 | DIESEL GENERATORS DECLARED INOPERABLE FOR SHORT TIME PERIOD "During performance of 24 month Division 1 Diesel Generator LOCA/LOOP surveillance testing, two pump start timers failed to meet the required acceptance criteria. The A RHR Pump timer actuated at 3.72 seconds (criteria: 2.7 sec. to 3.6 sec) and the C ESW Pump timer actuated at 39.24 seconds (criteria: 39.6 sec. to 48.4 sec). With failure of the timers proper loading on the Diesel Generators is not assured, and they ['A' and 'C'] were declared inoperable until the associated pump control breakers were opened. The Susquehanna safety analysis requires three operable Diesel Generators to safely shutdown the plant. Therefore with only two operable Diesel Generators, the condition requires an 8 hr ENS notification in accordance with 10CFR50.72(b)(3)(v) and (vi)." With Unit 1 shutdown the 'A' RHR pump is not needed, but the 'C' ESW pump does need to be operable resulting in part of the 8 hour report. The licensee notified the NRC Resident Inspector. * * * RETRACTED ON 04/08/2002 AT 1433 EDT BY GRANT FERNSLER TO GERRY WAIG * * * "On 3/31/2002, Susquehanna LLC made an ENS notification per 10CFR50.72(b)(3)(v) and (vi). The event was the result of two load sequence timers for separate diesel generators found outside of the allowable values. The associated diesel generators were declared inoperable. "Upon subsequent engineering review, it was determined that although the timers were not within the design specifications all equipment would have been able to perform its safety function, as evidenced by the emergency generators maintaining voltage and frequency, and the loads energizing and running during the testing. Additionally, the requirements of the Technical Specification Actions were followed for all inoperable equipment. With all equipment remaining capable of performing its design function, this ENS Notification EN#38818 is retracted." "The NRC Resident Inspector was notified by the licensee. The R1DO (Bradley Fewell) was notified by the Headquarters Operations Officer. | 0 | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2002-03-31
38817 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-29 23:40 | 2002-03-30 03:12 | 2002-03-30 | TECHNICAL SPECIFICATION 3.0.3 ENTRY DUE TO LOW SERVICE WATER SUCTION PRESSURE AND THE SUBSEQUENT LOSS OF CHILLERS FOR THE CONTROL ROOM EMERGENCY OUTSIDE AIR SUPPLY (CREOAS) AND CONTROL ROOM FLOOR COOLING The following text is a portion of a facsimile received from the licensee: "Unit 1 was in Mode 5, day 28 of a refuel and inspection outage. Unit 2 was in Mode 1, 24% power for scheduled maintenance work requiring River Water Makeup to both units' cooling towers [to be] out of service." "At 2340 hours, Unit 1 began to experience low suction pressure to the 'C' Service Water pump, the only pump in service at the time. Service Water takes suction from the Unit 1 Cooling Tower, and this condition resulted in low system discharge pressure and flow. Service Water is the normal cooling source for Units 1 [and] 2 Control Structure [Heating Ventilation and Air Conditioning (HVAC)]. The 'A' Control Structure chiller tripped, and the 'B' Control Structure chiller failed to start due to the low flow condition on service water. With both chillers tripped and unavailable for CREOAS and Control Room Floor Cooling, [the Limiting Condition for Operation (LCO) for Technical Specification] 3.0.3 was entered on Unit 2. This represented a Loss of Safety Function for Accident Mitigation and requires an [8-hour] ENS notification in accordance with 10CFR50.72(b)(3)(v)." "The Control Structure chillers were realigned to Emergency Service Water (ESW), its backup emergency cooling source. The 'A' Chiller failed to re-start, but the 'B' Chiller was successfully placed in service. LCO 3.0.3 was able to be exited on Unit 2 at 0012 hours on 3/30/02." "An investigation is ongoing into why the 'A' Control Structure failed to re-start and the cause of the low suction pressure on Service Water." The licensee stated that all systems functioned as required. The licensee notified the NRC resident inspector. | 0 | 24 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-03-30
38816 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-03-28 | 2002-03-28 23:00 | 2002-03-31 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The following is the text from a NC Department of Environment and Natural Resources News Release: "A truck stolen about 4:30 this afternoon in Forsyth County was transporting an instrument containing eight millicuries of Cesium-137, a radioactive material that is a potential health and safety risk if handled improperly or broken open. "The truck is a white Ford F150. The instrument is a Troxler brand portable moisture density gauge model 4640B. It is yellow and has a stainless steel handle with a radiation symbol protruding from a heavy base. It is about 20-30 pounds and 24x12x14 inches. Its serial number is 1996. The gauge was in a yellow box 24x12 inches and marked as containing radioactive material. The box should be locked and chained to the truck. "The gauge uses radioactive materials to test conditions of soil and asphalt during construction. Any health risk would occur only if a person were directly exposed to the sealed radioactive source inside the instrument. "Employees of Thompson-Arthur Division APAC-Carolina, Inc., a paving company in Greensboro, left the truck unattended. The company's license with the state Division of Radiation Protection requires that the instrument not be left unsecured. "Anyone who believes he or she has found the truck, box or gauge should stay at least ten feet away and contact the local sheriffs office, police department or state highway patrol immediately." NC Incident No. 02-12. * * * UPDATED AT 0012 EST ON 3/31/02 BY LEE COX TO FANGIE JONES * * * The truck has been recovered by the Sheriff's department and will be picked up by the North Carolina Division of Radiation Protection until the licensee can take possesstion. The gauge in it's storage box was recovered separately. The gauge and box appear undamaged and a survey will be conducted when the North Carolina Division of Radiation Protection arrives on scene. An additional report willl be sent later in the week. The R2DO (Carolyn Evans) and NMSS EO (Patricia Holahan) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-03-28
38815 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2002-03-28 16:43 | 2002-03-28 20:30 | 2002-03-28 | OFFSITE NOTIFICATIONS DUE TO UNPLANNED EMERGENCY SIREN ACTUATION "At 1643, it was discovered that a single River Bend Station Emergency Siren located in East Baton Rouge Parish had intermittently sounded. A notification was made to the Louisiana Office of Emergency Preparedness and a subsequent message is to be broadcast on local radio stations informing the public that this is an equipment related issue with this siren and no emergency exists." The licensee informed state/local agencies and the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-28
38814 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-03-27 | 2002-03-28 13:39 | 2002-03-28 | AGREEMENT STATE REPORT FOR LOSS OF STATIC ELIMINATOR "General licensee reported the loss of a Po-210 static eliminator device. The Licensee presumes that the device was recently lost during routine manufacturing operations. The device is manufactured by NRD and is Model P-2021, Serial no. A2BA986 containing approximately 2 mCi of Po-210. The Licensee will continue to search and file the required written report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-03-28
38813 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-03-27 | 2002-03-28 13:39 | 2002-04-15 | AGREEMENT STATE REPORT FOR A LOST GAUGE "A general licensee reported the loss of an NDC Infrared Engineering Model 103, serial no. 773, containing 100 mCi of Am-241. The gauging device was initially installed in 1982. The general licensee is a manufacturer of packaging products. The device was apparently installed at one time in a plastic extruder line. In November 2000 it was reported to the Department as being on the laminator in the plant. While performing the inventory for the most recent Departmental self-inspection, the licensee was unable to account for this device. Licensee states that it conducted an extensive investigation of the circumstances surrounding the disappearance of the device. Their investigation continues and they will file the required report as soon as possible. The department's investigation is ongoing." *****UPDATE State of Illinois to R. Laura on April 15, 2002 at 16:30**** The lost gage was found during renovations in the building. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-03-28
38812 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-03-28 | 2002-03-28 12:52 | 2002-03-28 | AGREEMENT STATE REPORT FOR STOLEN MOISTURE DENSITY GAGE "Just received word of a moisture density gauge that was stolen overnight. Licensee is #4165-37 North County Compaction Engineering Inc., from Escondido, CA. [ ]. The device is a CPN, model MC-1, S/N M14065450 stolen from the cab of the operator's truck which he did take to his residence in Long Beach, CA. Police report filed. The gauge contains nominally 10 mCi of Cs-137 and 30 mCi of Am-241. The licensee will place an announcement in the local paper describing [the] device and offering a reward for the return of the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-03-28
38811 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-03-27 | 2002-03-28 11:08 | 2002-03-28 | MEDICAL MISADMINISTRATION "On March 21, 2002, the physician ordered a Resting Myoview scan on a patient. This patient was assigned a different room and the Nuclear Medicine department was not notified. When the technologist went to inject the patient he verbally identified the patient and injected the wrong patient with 20.6 mCi of Tc-99m Myoview. The technologist was suppose to identify the patient by the ID bracelet but did not. The technologist has been retrained in the procedure. This misadministration was discovered when the correct patient was called in for the scan and the patient had not been injected. The patient that received the misadministration was notified. There was no apparent harm or injury to the patient. The patient that received the misadministration was not suppose to be injected with radiopharmaceuticals at all. The physician received enough information from the stress test on the correct patient so that patient did not need to be injected again." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-03-28
38810 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-28 03:00 | 2002-03-28 09:54 | 2002-03-28 | SINGLE TRAIN HPCI DECLARED OOS "During valve surveillance testing, Motor Operated Valve 2E41F104 failed to indicate OPEN. This is one of two in-line Primary Containment Isolation Valves (PCIV) that provide vacuum breaker isolation capability for the High Pressure Coolant Injection (HPCI) Steam Turbine Exhaust line. This failure resulted in the PCIV being declared INOPERABLE at 0300 on 03-28-2002. To comply with TS 3.6.1.3.B.1, the companion PCIV, 2E41F111, was CLOSED and deactivated. This resulted in the HPCI system being declared INOPERABLE, requiring a notification per 10CFR 50.72 for failure of a single train system. The HPCI system was scheduled to be removed from service for pre-planned maintenance, however, the failure of the 2E41F104 was not part of the pre-planned maintenance activities. The HPCI system has been removed from service, as scheduled, for performance of the pre-planned maintenance work. "As of 0904, the 2E41F104 has been repaired, the equipment clearance restored, and the valve has been satisfactorily functionally tested. Complete functional testing and return to service of the HPCI system is in progress, but has not been completed at this time. It is expected that the HPCI system will be returned to service today (03-28-2002)." The NRC Resident has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-03-28
38809 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-03-27 22:30 | 2002-03-28 01:24 | 2002-05-24 | SPURIOUS OPERATION OF THE REACTOR HEAD VENT VALVES IN THE SAFE SHUTDOWN REPORT(SSR) IS NOT CONSISTENT WITH THE NRC SAFETY EVALUATION REPORT. Specifically the Section 3.4.3 of the SER states that spurious operation of the Reactor Head Vent (RHV) valves {SO-2(3)-0220-46 ann SO-2(3)-0220-47} which would result in Reactor Coolant inventory loss, will be prevented by a pre-fire action to ensure closure by removing power from these valves. However, the current SSR dispositions this postulated concern based upon the assumption that spurious operation of greater than one normally closed valve in a series combination is not considered a credible failure mode except for high/low pressure systems. As a result, there is no pre-fire action to ensure closure by removing power to RHV valves. The documentation (FPR revision and 50.59) that supports the change in the licensing position of these valves from that described in the SER to the current SSR has not been located. A review was performed on the Fire Protection Report (FPR) which includes the Fire Hazard Analysis & Safe Shutdown Analysis, to evaluate the options for additional sources of water to address the loss of reactor inventory from the spurious actions of the reactor head vent valves. This review indicated that no specific circuit analysis was performed to determine what other available sources of water could be used for makeup of reactor inventory via the reactor head vent valves spurious operation. Therefore, in the event of a fire in the various assumed Appendix R fire zones, a qualified makeup source would not be available to mitigate the inventory loss introduced by the spurious operation of both RHV valves. Fuses have been pulled to remove power to and close a RHV valve on both Unit 2 and Unit 3 to comply with the SER. The action puts the plant in the configuration required if the RHV valves are considered a high-low pressure boundary. Completion of this action restores the plants compliance with the referenced SER. Dresden Engineering will perform an evaluation that documents the RHV valves as a high-low pressure boundary and that the actions taken above are adequate to mitigate the multiple spurious failures which must be postulated when these valves are considered a high/low pressure boundary. A revision to the FPR will be made to document the results of this evaluation. The NRC Resident Inspector will be notified. ***** RETRACTION AT 1815 EDT ON 05/24/02 FROM WARREN DEAGLE TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "On March 27, 2002 at 2230 CST, Dresden Station made an ENS Notification (EN 38809) regarding fuses that had not been removed from reactor head vent (RHV) valves. It was reported that the station's methodology for addressing fire induced spurious operation of the RHV valves in the safe shutdown report was not consistent with the NRC safety evaluation report. During preliminary reviews, it was postulated that a fire could result in spurious operation of these valves that in turn would result in reactor inventory loss. The postulated water source in the scenario was the opposite unit's Control Rod Drive system, which may not provide the makeup capability to maintain reactor water level above the top of active fuel (TAF)." "The condition was reported in accordance with 10 CFR 50.72(b)(3)(ii)(B), as an Unanalyzed condition that significantly degraded plant safety." "Upon further evaluation, it has been determined that a credible fire that would cause spurious operation of the RHV valves would not result in a loss in the High Pressure Coolant Injection (HPCI) system. Therefore, the HPCI system would have been available and capable to provide inventory makeup to the reactor vessel. Vessel water level would have been maintained above TAF. Based on the subsequent evaluation, the safety function (inventory control) would have been maintained at all times during post-fire safe shutdown of the unit." "Therefore, based on the above conclusion, this notification is being retracted." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Christine Lipa). | 0 | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-03-28
38808 | 0 | RESEARCH MEDICAL CENTER |  |  |  |  | 2002-03-27 14:45 | 2002-03-27 16:08 | 2002-03-27 | POSSIBLY MISSING IRIDIUM SEEDS The licensee was notified that a package containing Ir-192 brachytherapy seeds was being returned to the facility from Alpha-Omega Services because of a discrepancy between the shipping papers and the actual package contents. The shipping papers indicated that 71 seeds were included in the shipment; however, only 63 seeds were actually present in the package. The package did not appear to have been opened or damaged during transit. The licensee determined that the 8 missing seeds (1.39 mCi total activity) were, in fact, still in a secure location at their facility. They had been separated from the other sources and inadvertently excluded from the shipment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-03-27
38807 | 0 | SPECTRUM HEALTH HOSPITALS |  |  |  |  | 2002-03-27 | 2002-03-27 16:00 | 2002-03-27 | MEDICAL MISADMINISTRATION A female patient received an underdose during a gynecological treatment when an applicator containing the brachytherapy source being used was displaced from her body. The prescribed dose was 2240 cGy (rads); however, a dose of only 1212 cGy was actually administered. The sources were secured in a safe location and the patient has been discharged from the facility. The licensee has already contacted NRC Region III regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0 | 2002-03-27
38806 | 0 | US ARMY CORPS OF ENGINEERS |  |  |  |  | 2002-03-26 | 2002-03-27 11:18 | 2002-03-27 | THE ARMY CORPS OF ENGINEERS IN VICKSBURG, MS. REPORTED A STOLEN TROXLER GAUGE A Troxler nuclear density gauge model 3440 serial #22605 containing two sealed sources(8 millicuries Cs-137 and 40 millicuries Am-241/Br) was stolen from a trailer at Ft Polk, La. This occurred between 1617 on 3/26/02 and 0650 on 3/27/02. The technicians left the gauge in the locked trailer on 3/26/02, but when they returned the next morning the back door of the trailer had been broken into and the gauge along with other items had been stolen. The Military police and CID were notified. The gauge was stolen in its locked case. Local parish law enforcement was notified. Law enforcement in nearby states will also be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | MS | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-03-27
38805 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-27 | 2002-03-27 10:15 | 2002-03-27 | A PACKAGE RECEIVED ONSITE EXCEEDED EXTERNAL RADIATION LIMITS The licensee reported the discovery of a container on a shipping vehicle which exceeded the external radiation limits of greater than 200 millirem/hour. The bottom of the container read as high as 1000 millirem/hour. The container had not been opened yet. The container contains a refueling tool called a stellite ball punch. The licensee notified the carrier, shipper and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2002-03-27
38804 | 0 | LEHIGH VALLEY HOSPITAL |  |  |  |  | 2002-03-01 | 2002-03-27 08:27 | 2002-03-27 | LOST LICENSED NUCLEAR MATERIAL >10 TIMES APPENDIX C QUANTITIES Licensee reports that on 3/1/02, I-125 medical seeds ordered, arrived from a shipper in Texas. After the Licensee conducted their inventory, it concluded that 95 of the 96 seeds ordered had arrived. The Licensee conducted 2 searches at the hospital, with negative results, and notified the shipper of the inventory shortage. The shipper conducted inventory and searches at it's facility, also with negative results, and believes that the materials were shipped. The seeds were nominal .305 to .33 millicuries of I-125, which has a half-life of approximately 60 days. Each seed reads 450 mrem/hr on contact and 500 micro Rem/hr at 30 centimeters. The Licensee will be informing the carrier(believed to be Fed Ex at the time of report) of this lost of material. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-03-27
38803 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-03-26 17:52 | 2002-03-26 22:01 | 2002-03-27 | PRESS RELEASE REGARDING INJURED ELECTRICAL MAINTENANCE WORKERS The licensee reported that four maintenance workers were injured while working on the "3B" 4160 VAC board. The individuals, who were not contaminated, were transported offsite for medical treatment. As a result of the event, the board deenergized and the "3C" and "3D" emergency diesel generators automatically started and loaded to supply power to their associated shutdown boards. The licensee plans to make a press release regarding this event. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-03-26
38802 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-03-26 16:00 | 2002-03-26 18:20 | 2002-03-26 | OFFSITE NOTIFICATION DUE TO INOPERABLE EFFLUENT RADIATION MONITOR The licensee notified the Ocean County Utilities Authority, the Ocean County Radiological Officer and the Lacey Municipal Utilities Authority that a sewage radiation monitor has been inoperable for greater than 24 hours. The NRC resident inspector will be informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-26
38801 | 0 | PACIFIC RADIOPHARMACY |  |  |  |  | 2002-03-06 08:00 | 2002-03-26 17:34 | 2002-03-26 | EXTREMITY OVEREXPOSURE "[An individual] was observed by inspector Randy Erickson, Health Physicist with Region IV, dispensing radiopharmaceuticals that have caused an extremity exposure in excess of the limits allowed in 10 CFR 20.1201(a)(2)(ii). "[The individual's] left hand index fingertip exposure is estimated at 700 R/yr. The assumptions for the dose estimate is based on the following calculation with the left hand index finger supporting a vial containing 100 mCi of Tc-99m so it does not fall out of its lead shielding. Page 94 of the article 'Fingertip and Whole Body Exposure to Nuclear Medicine Personnel' references fingertip exposure of 56 R/year based on 100 mCi vial of Tc-99m, 1000 draws/year at 6 seconds per draw. This scenario nearly matches the procedure followed by [the individual]. "40 draws/day x 6 seconds/draw x 6 days/week x 50 weeks/year = 20 hours/year "Based on the article, 1.6 hrs/year exposure to the finger = 56 R. Therefore, 56 R/1.6 hrs x 20 hrs = 700 R. "An NRC form 5 has been completed for [the individual] for calendar year 2001. His total effective dose equivalent and total organ dose equivalent, maximum organ does not exceed the limits in 10 CFR 20.1201(a)(1) and (2)(i)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2002-03-26
38800 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2002-03-26 11:45 | 2002-03-26 17:22 | 2002-03-26 | EMERGENCY SIRENS INOPERABLE "At 10:15 on March 25, 2002 a silent test was performed from the Monroe County Radio Center at Cobb's Hill. The silent test results showed a failure of all 24 sirens. A siren reset report printed out shortly afterwards showing all 24 sirens normal. The personnel performing the test were unfamiliar with the two different types of reports. They thought that the reset report was another silent test report. A RG&E technician was informed of the siren failure. He contacted Cobb's Hill and determined that the system was operating adequately. "At 11:43 on March 26, 2002, the siren system engineer went to the Monroe County 911 Center and performed a silent test. All 24 sirens passed the silent test. The test was repeated from West Ave and Cobb's Hill with 100% success at these locations. No documentation could be found of any silent tests performed on 3/25/02 after the initial failure from Cobb's Hill." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(v) |  |  |  | 0 | 2002-03-26
38799 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2001-10-29 | 2002-03-25 16:08 | 2002-03-25 | OFFSITE NOTIFICATION REGARDING UNPLANNED EFFLUENT RELEASES The licensee notified the State of Maine regarding three separate inadvertent liquid releases which occurred during the period from 10/29/2001 through 11/12/2001. Each release involved approximately 1800 gallons of water, with a combined total activity of 0.03 Ci. The licensee stated that the official notification had been delayed due to disagreements regarding the wording of the notification with the state. NRC Region 1 has been informed of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-25
38798 | 0 | LANGAN ENGINEERING |  |  |  |  | 2002-03-25 07:00 | 2002-03-25 12:01 | 2002-03-25 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM A CONSTRUCTION TRAILER A Troxler moisture density gauge containing 8 microcuries of Cs-137 and 40 microcuries of Am-241/Be was stolen from a construction trailer located on the corner State Highway 22 and Greenwich Street. The gauge was last seen on 3/23/02 at 1330 EST when it was locked up in a construction trailer. It was discover missing 3/25/02 at 0700. Greenwich NJ police department have been notified. The gauge was a Troxler model 3440, serial number 29562. The Licensee notified R1 (Lodhi). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-03-25
38797 | 0 | SPECTRUM PHARMACIES INCORPORATED |  |  |  |  | 2002-03-25 09:40 | 2002-03-25 10:48 | 2002-03-25 | SHIPPING CONTAINER WITH REMOVABLE SURFACE CONTAMINATION EXCEEDING THE LIMITS The licensee received a shipping container (i.e., return ammunition can) that had external contamination on the latch. An incoming survey found that a contamination level of 227,345 DPM/300 centimeters squared of Tc-99m. The can was opened and segregated and no internal contamination was found. The driver and the steering wheel of the shipping vehicle was being surveyed. The package originated from Memorial Hospital in South Bend, Indiana. The licensee notified Memorial Hospital of the event. There were no known personnel contamination at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2002-03-25
38796 | 0 | WATERFORD | 3 |  |  | [3] CE | 2002-03-23 10:20 | 2002-03-23 11:40 | 2002-03-23 | ALERT DECLARED FOR INABILITY MAINTAIN COLD SHUTDOWN CONDITION While placing Shutdown Cooling into service, it was found that the Licensee was not able to open Safety Injection valves (SI-405 A&B, Reactor Coolant Loop Suction Isolation Valves). Due to the inability to open these valves, the Licensee declared an Alert per their Emergency Action Level's for the inability to maintain cold shutdown condition. All other Emergency Core Cooling Systems are fully operational and the Emergency Diesels are available. Licensee is maintaining Hot Shutdown conditions by using natural circulation and dumping steam to atmosphere with the Steam Generator Atmospheric Dump Valves. There is no indicated primary to secondary leakage. US NRC entered Monitoring Mode at 1149 EST. Normal offsite power is available and weather conditions are favorable. NRC Resident has been notified. Notified EPA (Edwards), DOE (Bartlett), USDA (Conley) and HHS (Burger). At 1250 EST, the Licensee terminated the Alert due to the SI-405 A&B valves opening. At 1400, a Commissioner's Assistant brief was conducted by R4RA Ellis Merschoff. R1DO (Conte), R2DO (Henson), R3D0 (Hiland), R4DO (Powers), R4 (L. Howell), NRR (Collins), IRO (Wessman), CAO (Keeling), PAO (Hayden), NRR PM (Kalyanam), NRR (Richards), DEDMRS (Dr. Paperiello), SECY (Vietti-Cook), EDO (Morris), IPO (Doroshuk), SPO (Piccone), Chair Assist (Tschiltz), COMM Dicus Assit (Hiltz), COMM McGaffigan Assist (Sharkey), COMM Merrifield Assist (McCabe), COMM Diaz Assist ( ), Sr Resident Insp (Farnholtz), FEMA (Earp), LA State Police and LA Department of Environmental Quality (Wascom). At 1435 EST, US NRC exited Monitoring mode as per R4RA (Merschoff), NRR (Collins) and IRO (Wessman). Notified FEMA (Zapata), EPA (Edwards), DOE (Bartlett), USDA (Conley) and HHS (Burger). ***UPDATE TO EVENT 3/23/02 1813 EST PIPKINS TO NORRIS*** "This notification supplements the Alert Declaration made by Entergy at Waterford 3 at approximately 10:20 CST this morning (Saturday, March 23, 2002) and subsequently reported to the NRC via the ENS. The Purpose of this supplement is to notify the NRC that this condition is also reportable pursuant to 10 CFR 50.72(b)(3)(v) as a condition that could have prevented the fulfillment a safety function. Specifically the safety function of removing decay heat via the Shutdown Cooling mode of the Low Pressure Safety Injection System was temporarily prevented by the inability to open valves SI-405A and SI-405B (Reactor Coolant Loop Suction Isolation Valves). As previously reported, the Alert condition was exited at approximately 11:50 CST. Shutdown cooling is currently in operation and a safe and orderly cooldown is in progress. The root cause of the condition is currently being investigated." Licensee notifed NRC Resident. Notifed R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | POT RHR INOP |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | ALERT | 4 | LA | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(v)(B) |  |  | 0 | 2002-03-23
38795 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2002-03-22 | 2002-03-22 21:07 | 2002-03-22 | GROUP III PRIMARY CONTAINMENT ISOLATION "Received a group III PCIS isolation signal affecting RWCU and the recirculation sample valves while pressurizing RWCU following a RWCU system outage. This event resulted in containment isolation signal affecting valves in multiple systems. Licensee is performing an investigation as to the cause of this event." The Licensee has notified the NRC Resident. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 |  | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-03-22
38794 | 0 | MICHIGAN DEPT OF ENVIRONMENTAL QUAL |  |  |  |  | 2001-08-01 | 2002-03-21 15:52 | 2002-03-21 | LOSS OF POLONIUM-210 STATIC ELIMINATOR The lost source was a 10 millicurie source (3/01) manufactured by NRD Inc. The following is taken from a letter from Mr. Larry Hathorne, Ford Motor Co. to Mr. David Minnar, Michigan Dept of Environmental Quality dated March 15, 2002: "This letter is pertinent to the lost of an anti-static air gun. The model number is P-2021. The serial number A2AW954 is on lease number 007136 and was shipped on 3/19/01. The device was used for spraying acrylic and also to prevent dust. The device was used in the Plastic Shop. It was last used doing the Month of August, 2001. To my knowledge, the device was misplaced or stolen. The efforts that was made was searching of the shop and questioning the shop personnel. This situation has been brought to management attention. The decision was made to not replace the anti-static gun." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-03-21
38793 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-01-08 | 2002-03-21 10:30 | 2002-03-21 | AGREEMENT STATE REPORT FOR EQUIPMENT FAILURE THAT OCCURRED IN AMELIA, LA "There were three equipment failures that were not reported until March 18, 2002. The one on January 8, 2001 was a locking mechanism failure on a INC IR-100 radiography camera with serial number 4473. The one on January 30, 2001 also involved a locking mechanism failure on a the same model radiography camera with serial number 4470. The one on July 30, 2001 involved a locking mechanism failure. It is the same model of camera with the 4471 serial number. All of the cameras were sent to Source Production Equipment Company for repair. These cameras utilize Ir-192. The rest of the information has been entered in NMED. " The State of Louisiana logged this event as Event Report ID No.: LA020004. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-03-21
38792 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2001-12-03 | 2002-03-21 10:30 | 2002-03-21 | AGREEMENT STATE REPORT FOR EQUIPMENT FAILURE THAT OCCURRED OFFSHORE "This incident occurred on December 3, 2001. This was an equipment failure involving a INC IR- 100 radiography camera with serial number 4473 and the source was an AEA Model 37703 Source Assembly with serial number 00519B. This piece of equipment was returned to Source Production Equipment Company because the source would not crank out. Upon removal, the source was found to have been fabricated from a length of steel drive cable. The source assembly was found to be broken, at the capsule side of the locking ball, into two separate pieces. The failure of the cable material was due to severe corrosion having taken place. The material was so corroded, it would not flex to allow proper insertion of the pigtail into the C-1." The state of Louisiana logged this event as Event Report ID No.: LA020005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-03-21
38791 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2002-03-21 03:13 | 2002-03-21 10:11 | 2002-03-21 | RPS LOGIC ACTUATION WHILE SHUTDOWN "At 0315 on March 21, 2002, during Refueling at Nine Mile Point Unit 2, an actuation of the Reactor Protection System (RPS) logic occurred when air was lost to the scram air header. "The RPS logic actuation was caused by high water level in the Scram Discharge Volume (SDV) as a result of loss of motive air to control rod scram valves. The loss of air was experienced as a result of incorrectly written procedure step sequence while securing the plants Instrument Air system. "This event is reportable under 10CFR50.72 (b)(3)(iv)(A), Any event or condition that results in valid actuation of the Reactor Protection System (RPS)." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-03-21
38790 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-03-20 15:43 | 2002-03-20 22:56 | 2002-04-03 | UNIT-1 HPCI SYSTEM FAILED TO MEET REQUIRED RESPONSE TIME DURING SURVEILLANCE TESTING "On 3/20/02 at 15:43 the Unit-1 HPCI system failed to meet required system response time during surveillance testing. Testing was being performed to establish HPCI operability during reactor startup with reactor steam dome pressure at 204 psig. The HPCI system failed to achieve rated system flow within the required time from system initiation. Troubleshooting is currently in progress and a determination is underway to determine if this problem was related to maintenance activities performed during the refueling outage. "This report is being made in pursuant to 10CFR50.72(b)(3)(v)(D) for failure of a single train accident mitigation system." The licensee notified the NRC Resident Inspector. ***UPDATE (EVENT RETRACTION) 4/3/02 at 1533 from Stan Gamble to Rich Laura*** "This is a retraction of the event notification made on 3/20/02 at 22:56 hours. This event (#38790) was initially reported as a safety system functional failure under the requirement of 10CFR50.72(b)(3)(v)(D). Unit 1 High Pressure Coolant Injection (HPCI) failed to meet the required system maximum response time during surveillance testing. Testing was being performed during reactor startup with reactor steam dome pressure at 204 psig. "Rated flow was not achieved within the 59-second maximum response time specified in the test due to motor operated valve (MOV) and flow controller manipulations performed during the unsatisfactory testing. The test was re-performed successfully and the system was declared operable on 2/21/02 at 02:15 hours. System repair was not required. "The system response was verified to be as designed considering the test conditions. A condition did not exist at the time of discovery that could have prevented the fulfillment of the safety function." Notified R1DO (G. Meyer) | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-03-20
38788 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2002-03-20 12:30 | 2002-03-20 14:27 | 2002-03-20 | EMERGENCY DIESEL GENERATOR TURBOCHARGER FIRE While operating the Division 1 emergency diesel generator (EDG) for monthly surveillance testing, an operator noticed a small fire in the vicinity of the turbocharger. The EDG was immediately (manually) unloaded and secured. The fire was reported to be out in less than one minute of the initial report. The affected EDG had been at full load for approximately 35 minutes at the time of the event. No personnel were injured as a result of this event. Offsite fire department assistance was NOT requested. The diesel has been declared inoperable and the station has entered the applicable technical specification LCO. The back-up EDG is available. Further inspection and investigation of the EDG fire is being conducted at this time. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2002-03-20
38787 | 0 | U.S. AIR FORCE |  |  |  |  | 2002-03-20 | 2002-03-20 11:22 | 2002-03-20 | REPORT FROM AIR FORCE ON CHEMICAL AGENT DETECTOR FOUND IN BRIDGEWATER, MA. The U.S. Air Force Headquarters reported that children playing in the woods in West Bridgewater, MA found a chemical agent detector. The detector was turned over to the local fire department and then passed on to the Otis Air Force. The device was sealed and contains 250 microcuries of Americium 241. The serial number of the device is 203D-31535 and is from lot number DDD086E00.133. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | MA | MAT | [5 empty] | 0 | 2002-03-20
38786 | 0 | U.S. ARMY |  |  |  |  | 2002-03-08 | 2002-03-20 10:14 | 2002-03-20 | UNPLANNED CONTAMINATION EVENT AT FORT KNOX The licensee reported an unplanned contamination event that occurred on March 8, 2002 in a Storage Room at Fort Knox Army Base located in Kentucky. Two army tank muzzle reference sensors were removed from tanks and wrapped in plastic bags. The bags were stored in a Storage Room on the base. Contamination levels were found to be 8000 DPM to 118,000 DPM. Radiological surveys were performed on the ventilation system which was found to be clean. Subsequently, the two damaged sensors were properly bagged and the two individuals involved received bioassay tests. The results from the bio assay test were not yet available. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | KY | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2002-03-20
38785 | 0 | U.S. ARMY |  |  |  |  | 2002-03-19 | 2002-03-20 10:14 | 2002-03-20 | LOST/MISSING ARMY TANK SIGHT DEVICE The licensee reported a missing sighting device (ie., beam splitter) for the main gun on an Abrams tank. It is believed that the beam splitter vibrated out on the Yano live firing range located on the Fort Knox Army Base. The beam splitter contains 10 curies of tritium inside a container that is approximately 1.5 inches long and 1 inch in diameter. The licensee is conducting a search to locate the missing beam splitter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | KY | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-03-20
38784 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2002-03-15 06:30 | 2002-03-19 19:02 | 2002-03-19 | NON WORK RELATED FATALITY NOTIFICATION IN ACCORDANCE WITH 10CFR50.72 "At approximately 06:30 MST on March 15, 2002, a non-work related on-site fatality occurred at the Palo Verde Nuclear Generating Station. The fatality was not related to the health and safety of the public or onsite personnel. Specifically, a contract carpenter was found by coworkers in the carpenter shop before work hours with no pulse or life signs. The individual was promptly attended by Palo Verde Emergency Medical Technicians (EMTs) and an air evacuation was completed. The individual was pronounced dead upon arrival at the hospital. "The individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved. The work location was outside of the Protected Area. "Palo Verde has not observed any heightened public, media or government concern as a result of the fatality. Since the fatality is unrelated to Palo Verde's industrial or radiological health and safety, no news release is planned. "Since the fatality was not work-related, nor the result of an accident, no notification to other government agencies was made at the time. However, Palo Verde is now making a notification to the Arizona Department of Occupational Safety and Health (ADOSH) due to a requirement to report any cardiac arrest on-site. Thus this ENS notification is in response to a notification to another government agency in accordance with10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-19
38783 | 0 | ST FRANCIS HOSPITAL & HEALTH CTR |  |  |  |  | 2002-02-28 | 2002-03-19 17:31 | 2002-03-19 | MEDICAL MISADMINISTRATION DURING STENT RESTENOSIS IRRADIATION "On 02/28/02, patient was scheduled for irradiation of an in stent restenosis using the Novoste Beta-Cath system, specifically 30 mm serial number 88746. "The cardiologist stated the reference vessel diameter was 2.7 mm "The standard dose for a reference diameter of 2.7 mm is 18.4 Gy delivered in 3'22". "The patient was identified, and pre-procedure patient survey was performed. The novoste unit was prepped, placed in sterile bag and catheter attached, by the authorized user, system was pressurized to verify water flow through the system. The sources were sent to the treatment position in the catheter and verified visually by authorized user and medical physicist that the sources were in the proper location within the catheter. The sources were returned to the source holding area with a green light indicating they were in the safe position. "The authorized user took the Novoste system to the patient and the cardiologist inserted the treatment catheter through the arrow sheath protector and forwarded the treatment catheter to the desired treatment location, verified via fluoroscopy. "When the treatment catheter was in place, the cardiologist indicated the location to be correct, the authorized user indicated he was ready to send the sources, and upon acknowledgement the sources were sent to treatment location under fluoroscopy. The distal marker was visualized but the proximal marker wasn't seen. The cardiologist rotated the C-arm to change the perspective of the image. The proximal marker still wasn't visualized. "The authorized user then attempted to return the sources to the safe position in the Novoste device. There was no indication of the sources returning to safe position. The catheter was immediately removed from the patient and taken to the safety box. The medical physicist then attempted to return the sources to the safe position and verify their location. This attempt was unsuccessful. "The patient was surveyed and found to be at background. "Utilizing multiple wet gauze pads, the catheter was wiped clean in an attempt to locate the sources visually. The sources were not seen. The catheter was then passed over the survey meter, with the unit in the box to determine if the sources were in the catheter. There were no sources in the catheter, "At this time, the cardiologist was asked if he wanted to change systems and continue the treatment. The authorized user and cardiologist decided to abort the procedure. The patient was notified of the decision by the cardiologist at this time. "The Novoste system was removed from the Cath lab in the safety box. Under visual inspection there appeared to be 6 source pellets and proximal marker in the source holding area of the Novoste unit. The remaining 6 source pellets and distal marker appeared to be in the base of the catheter that fits into the Novoste unit. "All sources were visually accounted for, Novoste was called, and problem reported. "Novoste representative arrived within 2 hours of notification, and was able to return all sources to the safe location, with the unit indicating the safe condition, "Upon inspection, there was some type of material (black) in the source holding chamber. This material apparently restricted movement of the source pellets out of the source holding chamber, "The Novoste unit was immediately removed from service and it and the catheter was placed in the lead shield container to be returned to Novoste for evaluation. "The time estimate for the time the distal marker was seen and the system removed from patient was approximately 30 seconds. "The treatment was never actually started as the proximal marker was never visualized and that is the indication to start the timer, thus starting the treatment. "The only definite location of the sources is that the distal marker was at the proper location in the catheter. "If one assumes the six pellets were behind the distal marker for 20 seconds, then the dose would be approximately 1.8 Gy to a length of 0.5 - 0.75 mm. "This would be a maximum dose estimate, as part of the time they were being remove from the patient, and in vessels that were much large than 2.7 mm diameter." The licensee stated that NRC Region 3 was notified of this event on 2/28/02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2002-03-19
38782 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-03-19 10:56 | 2002-03-19 14:15 | 2002-03-19 | LOSS OF SPDS DEGRADES COMMUNICATION/ASSESSMENT/RESPONSE CAPABILITY "During the performance of a software update to the Primary Plant Process Computer System (PPCS) the Unit 2 PPCS servers failed rendering Reactor Thermal Output and Safety Parameter Display functions for Unit 2 inoperable. At the time of the failure the software update was only being performed on Unit 2. Unit 1 PPCS was verified operable and was not affected because the software update was only being applied to the Unit 2 Servers. "Abnormal Operating Procedure AOP-21, PPCS Malfunction was entered and Reactor Power was reduced approximately 2% and is currently being controlled by Control Board Delta-T. The Safety Parameter Display System was also rendered inoperable and is the bases for making this Notification. "Presently the Unit 2 PPCS servers are being re-booted, and it is expected that PPCS will be available in about 2 hours. It is not known what the exact failure mechanisms for Unit 2, only that it is either the software or the procedure that caused the PPCS failure to unit 2." The licensee also notified the NRC Resident Inspector. * * * UPDATE ON 3/19/02 @1732 BY HARRSCH TO GOULD * * * As of 1534 CST, the PPCS system was returned to service for Unit 2. All required functions were verified operable, including Reactor Thermal Output (RTO) and the Safety Parameter Display System (SPDS). The initial failure was related to the installation of a software upgrade and the problem has been corrected. With the RTO function now Operable, Unit 2 will be returning to full power from 98%. The NRC Resident Inspector was notified. Reg 3 RDO(Phillips) was informed | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-03-19
38781 | 0 | ABB INC |  |  |  |  | 2002-03-18 | 2002-03-19 12:53 | 2002-03-19 | INITIAL NOTIFICATION OF POTENTIAL DEFECT CLASS 1E TYPE CV-2 AND CV-22 RELAYS "This letter is the initial notification of a deviation concerning our Class 1E type CV-2 and CV-22 relays. "One of our customers notified us that several of the CV-2 relays they had recently received did not have a particular assembly on the moving disc which other CV-2 relays on the same order did have. Discussions with this customer concluded they were speaking of a weight assembly that is used in balancing the moving disc and is required as a part of the completed relay. "Upon visual examination of the CV-2 relays returned to us for corrective action this deviation was confirmed. A preliminary investigation showed that our manufacturing system allowed for the potential for this deviation to occur. "Details will be provided in our written notification forthcoming within the next thirty days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | FL | OTH | PAR | 21.21 |  |  |  | 0 | 2002-03-19
38780 | 0 | WEST VALLEY MEDICAL CENTER |  |  |  |  | 2002-03-11 13:05 | 2002-03-18 17:03 | 2002-03-18 | MEDICAL MISADMINISTRATION The West Valley Medical Center reported that a possible medical misadministration occurred when a patient, who had an order from his physician for a bone scan, was injected with 25 millicuries of technetium-99 HDP, but after gathering more information from the patient, it turns out the physician had misordered the procedure he wanted. The patient's physician was contacted and he verified the procedure he actually wanted was a bone densitometry scan(DEXA scan) which does not require the injection of nuclear medicine as a bone scan does. The patient and physician were notified and there was no adverse affect to the patient. This was discovered during their Radiation Safety Committee meeting. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 35.33 |  |  |  | 0 | 2002-03-18
38779 | 0 | WEST VALLEY MEDICAL CENTER |  |  |  |  | 2002-02-15 11:00 | 2002-03-18 17:03 | 2002-03-18 | MEDICAL MISADMINISTRATION The West Valley Medical Center reported that during the preparation for a patient's lung scan, 5 millicuries of technetium-99 MAA was inadvertently injected into an artery instead of a vain. The patient and physician were notified and no adverse affects occurred. The lung scan was performed the same day following a second injection of technetium into the vain. This was discovered during their Radiation Safety Committee meeting. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 35.33 |  |  |  | 0 | 2002-03-18
38778 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2002-03-16 09:00 | 2002-03-18 14:48 | 2002-03-18 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The Maryland Department of the Environment reported that over the weekend a moisture density gauge was stolen from a construction trailer in Howard County, Maryland. The model number of the gauge is 3430 with a serial number of 22798. The gauge uses 8 millicuries of Cs-137 and 40 millicuries of Am- 241. The theft was reported to the Howard County Police Department. The device is not a radiological hazard provided the source remains locked in its device. The gauge is owned and licensed to Professional Services Industries who is an NRC licensee doing work in Maryland under reciprocity. The state issued a press release. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2002-03-18
38777 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2002-03-18 12:15 | 2002-03-18 14:11 | 2002-03-18 | OFFSITE NOTIFICATION DUE TO AN INADVERTENT EP SIREN ACTUATION An inadvertent actuation of all Calvert County EP sirens (49 total) occurred at 1215EST due to a personnel error that occurred during testing. The testing was performed by the Calvert Control Center Operators. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-18
38776 | -1 | SOUTHEAST MO STATE UNIVERSITY |  |  |  |  | 2002-03-15 16:30 | 2002-03-18 11:53 | 2002-04-15 | PERSONNEL OVEREXPOSURE POSSIBLE IF UNCHARACTERIZED ALPHA EMITTER ABSORBED BY AIRBORNE INHALATION During a routine radiological survey, the school found a table in Johnson Hall that was contaminated with 150 DPM/100 centimeters squared [initially estimated to be approximately 30,000 dpm or 14E-3 microcuries] of Americium-241. Johnson Hall, room 222, is normally locked with restricted access and the cause of the contamination is historical in nature. The table was decontaminated and wrapped in plastic for proper disposal. There were no known personnel overexposures due to this event. However, "if 100% was absorbed by airborne contamination and deposited on bone surface, it would exceed the ALI by 2.3." The licensee discussed this report with R3(Null). * * * RETRACTION ON 4/15/02 @ 0845 BY LILLY TO GOULD * * * After reviewing this event with Region 3 personnel it was determined that it was not reportable based on a model which shows that the maximum dose would be about 2 millirem/yr. Notified REG 3 RDO (Riemer) and NMSS EO (Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2002-03-18
38775 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-03-17 15:25 | 2002-03-17 17:03 | 2002-03-17 | OFFSITE NOTIFICATION DUE TO BRUSH FIRE NEAR SITE The licensee contacted the local volunteer fire department to respond to two small brush fires burning under the plant access road bridge. The fire department responded at 1537 CST and both fires were extinguished by 1556 CST. The licensee believes that the fires were caused by a passing train. The NRC resident inspector has been informed of this event by the licensee. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-17
38774 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2002-03-16 12:15 | 2002-03-16 13:55 | 2002-03-16 | PLANT SHUTDOWN IN ACCORDANCE WITH TECHNICAL SPECIFICATIONS "This notification is being made pursuant to 10CFR50.72(b)(2)(i), and Exelon Reportability Manual section SAF 1.2. At 1215 CST on 03/16/02, during Unit 2 steady state operation at 100% power, a unit shutdown was initiated due to an increase in Reactor Coolant System Unidentified Leakage in excess of Technical Specification limits. RCS unidentified leakage has increased by 2.1 gallons per minute over a 24 hour period, from 0.9 gpm to 3.0 gpm, which is above the Tech Spec limit of less than or equal to 2 gpm. On 3/16/02 at 0555 CST, a 12 hour timeclock was entered to be in Hot Shutdown by 1755 CST, followed by Cold Shutdown on 3/17/02 at 1755 CST. Current plans are to enter Cold Shutdown in order to enter the Primary Containment, and determine and correct the cause of the unidentified leakage." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE 2214 EST 3/16/2002 FROM DANIEL COVEYOU TAKEN BY BOB STRANSKY * * * "This notification provides an update of EN #38774 and is being made pursuant to 10CFR50.72(c)(2) and Exelon Reportability Manual section SAF 1.2. "As of 1540 CST, the indicated increase in the Unit 2 unidentified leakage rate over the previous 24 hr period has decreased to 1.7 gpm. As this value meets the LCO requirements of LaSalle Technical Specification 3.4.5 (<2 gpm increase within previous 24 hours), the plant shutdown initiated at 1215 CST is no longer required. "The increase (and subsequent decrease) in the indicated unidentified leakage rate is consistent with previously observed behaviors following primary containment cooling equipment lineup changes that induce containment air temperature changes. Initial chemistry analyses of the primary containment environment (air and sump samples) indicate that there has been no increase in reactor coolant system leakage. "The shutdown was terminated with the reactor operating at 69% power. Current plans are to return the unit to full power operation." The NRC resident inspector has been informed of this update by the licensee. Notified R3DO (Phillips). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-03-16
38773 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-16 02:40 | 2002-03-16 06:59 | 2002-03-16 | UNIT 2 ENTERED TS 3.0.3 AFTER DECLARING ESS BUSES INOPERABLE DUE TO ERROR IN CLEARANCE "On 3/16/02 at 0240 hours, a field operator was directed to remove a clearance and rack in 4 Kv breakers for the Unit 1 A & B Control Rod Drive system. The system had been out of service for maintenance during the refuel outage. Upon arrival at the load center, the operator found both breakers racked out but not secured with the required seismic restraints. According to plant procedures, this renders the associated bus inoperable. Shift supervision was notified and the Unit 1 'A' and 'D' ESS Busses were declared inoperable. The immediate effects were for Unit 2 to enter TS 3.0.3 which was exited 30 minutes later, once the breakers were returned to their racked-in position. In review of the Loss of Safety Function, it was discovered that, with the 'A' and 'D' ESS Busses inoperable, the Control Structure chillers were inoperable resulting in an event or condition that could have prevented fulfillment of a Safety Function required to Mitigate the consequences of an accident. In accordance with 10CFR50.72(b)(3)(,v)(D) this loss of safety function requires an 8 hour ENS Notification." The 4 Kv breakers were racked out 8 days ago. Due to an oversight in preparation of the clearance, the procedure requiring installation of the seismic restraints was not referenced. The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-03-16
38772 | 0 | WV RADIOLOGICAL HEALTH PROGRAM |  |  |  |  | 2002-03-02 | 2002-03-15 17:37 | 2002-03-15 | COURTESY NOTIFICATION The West Virginia Radiological Health Program was notified by the Ohio Bureau of Radiation Protection that a shipment of medical waste from the Weirton Medical Center activated a radiation detector at the Stericycle medical waste incineration facility in Ohio. The dose rate at the surface of the package was greater than 500 microR/hr (as of 3/15/02, it was 200 microR/hr). The incinerator facility is holding the package in a secure location until the Weirton Medical Center is able to retrieve it. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | WV | OTH | GEN |  |  |  |  | 0 | 2002-03-15
38771 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-03-14 15:00 | 2002-03-15 12:55 | 2002-03-15 | 24-HOUR NRC BULLETIN 91-01 REPORT "During Field-testing of the west annex floor, the floor failed to maintain the solution in a safe slab by allowing water to seep in cracks along the wall. This is a violation of NCSA- 0705_076 (inadvertent containers) administrative controls on potential inadvertent containers. While an unsafe amount of solution was NOT lost in this event, the cracks represent a loss of one leg of double contingency control as defined in NCSE- 0705_076. "Background information: On March 6, a low level probe for the storage columns in the West Annex developed a leak and allowed uranium-bearing solution to accumulate on the floor. The amount of spilled solution on the floor was estimated at that time to be no more than 18.4 liters. The spill amount did not meet the definition of an unsafe amount of uranium bearing material, the process conditions credited for meeting double contingency in the NCSE's were maintained. "On March 14, after completing repairs to the low level probe, the solution level in the West Annex storage columns was remeasured. The solution volume lost, calculated from the system sight glasses was calculated to be approximately 97.5 liters. Given the known assay and concentration of uranium, the spilled solution still did not represent an unsafe amount of uranium bearing material even when the volume was increased from 18.4 liters to 97.5 liters. "On March 14, an NCS engineer and Operations personnel investigated the difference between the amount of solution observed on the floor and the amount estimated by the level of the sight glass. A field test was conducted where as water was observed to seep into cracks between the floor and the wall. "SAFETY SIGNIFICANCE OF EVENTS: Low. The solution in question could not support a criticality in any geometry. Less than a safe mass amount of solution was involved. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events are required. The West Annex blending system would have to be operating and processing solution with a high concentration of uranium and assay. Then a leak would have to occur such that an unsafe amount of solution would collect on the floor. The solution would then flow into the cracks on the floor into an unsafe geometry. Depending on the amount of solution collected some reflection would be required to maintain a critical chain reaction. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): N/A. Volume or Geometry "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Based upon the amount of solution that leaked on the floor, 51 grams U235. This represents 3% of the required amount of solution "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Cracks between the floor and the wall could allow solution to enter an unknown unfavorable geometry in the event of a spill. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The PSS directed remaining in an anomalous condition until the repairs to the cracks can be made." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-03-15
38770 | 0 | FOX CHASE CANCER CENTER |  |  |  |  | 2002-03-15 | 2002-03-15 10:23 | 2002-03-15 | P-32 SOURCE USED IN RESEARCH DISCOVERED MISSING The following preliminary information was provided by the licensee: "This is to inform you of an incident that occurred at our facility involving a recent shipment of 250 microcuries of phosphorous-32 [P-32] deoxyguanosine 5 triphosphate. The shipment was delivered to our facility (License # 37-02766-01) on March 8, 2002 as an excepted package, limited quantity [49 CFR173.421]. The package was delivered to the recipient lab and the blue plastic container was placed in a freezer that was locked for storage of the material. On March 11, 2002 when the freezer was unlocked and the blue container was removed for use there was no vial of P-32 inside. The lab worker immediately reported the situation to her Principal Investigator. Initially the assumption was simply that the facility was shortchanged a vial and indeed that is our conclusion after investigation of the incident. The Radiation Safety Officer [RSO] was notified via e-mail at or about the time the purchasing department was notified. "The RSO immediately began an investigation of the incident. It was determined that the initial recipient did not follow the facilities procedure for opening packages of radioactive material and failed to monitor the surface of the package or look inside and verify the contents. The shipper, Perkin Elmer, was notified and asked to investigate the matter. The distribution coordinator at Perkin Elmer indicated that there might have been other incidents where primary vials have been omitted from a shipment. She declined to give further details until they finish their investigation. The RSO was informed that each package is not routinely surveyed by Parker Elmer even though an exposure rate was indicated on the packing slip. "Physical inventories of the laboratory concerned and an adjacent laboratory were conducted and there were no discrepancies. Hospital security has been notified and they are conducting an investigation. A radiation survey using a Ludlum Model 3 survey meter with a 44-9 probe was performed of the lab in question, as well as the tissue culture room where the material was stored, and the Principal Investigator's Office. The shelves, drawers, cabinets, sinks, trashcans were surveyed in these areas with no positive results. A water cooler in the vicinity was swipe tested on the advice of our consultant. The water cooler showed no evidence of P-32 contamination. All the bottles next to the water cooler were also surveyed via a meter and no levels were found. "The Principal Investigator [ ] was interviewed by the RSO. She indicated that she was not aware of any personal conflicts within her lab nor any other labs at the facility. She indicated that not only is their radioactive material kept locked within a freezer dedicated to radioactive materials storage, but that the tissue culture room is kept locked when not in use. "Access to the building requires an access card and there is a record of all personnel who entered the building during the period March 8-11. They are in the process of interviewing those personnel on the list. "Shipping and Receiving was checked for other shipments from Perkin Elmer but none were received on March 8. "We have completed the following corrective actions. A review of package receipt procedures including survey of the package and inspection of the primary vial was done with the personnel in the lab that received the shipment. The lab in question also developed a procedure checklist that includes not only the above but also the step of matching the lot number on the vial with that on the shipping papers. A memo has been sent to all of the other research labs reminding them of the procedures for receiving packages include a survey of the surface of the package even though regulations do not require that for an exempt quantity package and an email send as urgent went to all research areas, Nuclear Medicine and Radiation Oncology. A review of the incident and package receipt procedures will be included in annual inservices and information conveyed during routine inspections of radioactive materials laboratories. "We have concluded that the primary vial was probably not shipped, because the material was secured within the building, the tissue culture room, and within the freezer from the time delivered until the attempt to use it. No evidence of any irregularity resulted from the investigations conducted by the RSO and Security. But since we cannot rule out that the vial was shipped we are notifying the Nuclear Regulatory Commission. Security has always been a priority at Fox Chase Cancer Center and we are aware of the heightened concerns due to the terrorist attacks of September 11". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-03-15
38769 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-03-06 21:03 | 2002-03-14 14:42 | 2002-03-14 | INVALID EMERGENCY DIESEL GENERATOR ACTUATION DURING TESTING "This is a verbal report in accordance with 10 CFR 50.73(a) (2)(iv)(A). It is not considered a Licensee Event Report. This event occurred with Unit 3 at 94 percent power while performing scheduled testing of the common accident signal logic. On March 6, 2002, at 2103 hours, an invalid signal caused the automatic actuation of the 3B Emergency Diesel Generator (EDG). The EDG functioned successfully, it was not required to tie to its respective 4kV shutdown board by design because the board was energized. The Reactor Protection System did not actuate. No other systems listed in 10CFR 50.73(a)(2)(iv)(B) were affected." The licensee stated that the inadvertent actuation resulted from an insulator finger dislodging from an electrical contact during surveillance testing. The licensee will notify the NRC Resident. | 0 | 0 | 94 | 0 | 0 | 94 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-03-14
38768 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2002-02-28 17:52 | 2002-03-14 14:42 | 2002-03-14 | INVALID ACTUATION OF TWO DIESEL GENERATORS DURING TESTING "This is a verbal report in accordance with 10 CFR 50.73(a)(2)(iv)(A). It is not considered a Licensee Event Report. This event occurred with Unit 2 at full power while performing scheduled testing of the common accident signal logic. On February 28, 2002, at 1752 hours, an invalid signal caused the automatic actuation of the B and D Emergency Diesel Generators (EDGs). The EDGs functioned successfully. They were not required to tie to their respective 4kV shutdown boards because their boards were energized. The Reactor Protection System did not actuate. No other systems listed in 10CFR 50.73(a)(2)(iv)(B) were affected." The licensee stated that the inadvertent actuation resulted from a surveillance test procedural compliance issue. The licensee will contact the NRC Resident. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-03-14
38767 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-03-13 12:30 | 2002-03-14 09:51 | 2002-03-14 | 24 HOUR NRC 91-01 REPORT INVOLVING OIL CONTAMINATION ON ADU BULK CONTAINER "Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt.% U-235) PWR fuel fabricator for commercial light water reactors, License: SNM-1107. "Time and Date of Event: Approxirnatcly 12:30 hours, Wednesday, March 13, 2002. "Reason for Notification: When an empty bulk container was returned to the bulk blending room after having been emptied on the erbia production line, an operator noticed a film of oil on the outside of the container and its feeder valve, and on an horizontal structural plate of the container. "Summary of Process: UO2 powder is blended in 1750 kg bulk containers in the bulk blending room (a moderation control (Modcon) area) prior to being used on a pellet line. After blending, the bulk containers are taken to a production line, and placed into a second Modcon area for processing. After processing, the empty containers are returned to the bulk blending room. "As Found Condition; a summary of the as found conditions is as follows: The Nuclear Criticality Safety (NCS) function was immediately notified, and an NCS engineer went immediately to the floor to evaluate the situation. The bulk container was empty. A film of oil was found on the side of the container and its feeder valve, and on a horizontal structural plate of the container. The total quantity of oil is estimated to be no more than a few ounces. The container was inspected, and found to apparently be intact, that is, the integrity intact and the gaskets in place and firmly secured. "Double Contingency Protection: Double contingency protection for the ADU bulk container(s) is based on moderation control, that is, (1) prevent greater than 20.48 liters of water equivalent from becoming available to a bulk container, and (2) prevent greater than 20.48 liters of water equivalent entering a container. It was determined double contingency protection was lost because of the failure of controls to prevent moderating material from coming in contact with a bulk Container without prior written authorization, It is also noted that at no time was greater than the safety limit of moderator involved. Therefore the incident requires 24-hour notification in accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5). "Summary of Activity: The NCS engineer made the preliminary determination that the incident was significant because moderator had come into contact with a bulk container. The container was removed from service. No additional immediate corrective action was required for the affected container because it was empty. The feeder valve was removed, and the gasket and interior of the container and feeder valve were inspected for oil contamination. None was found. "Conclusion: There was a loss of double contingency protection. At no time was greater than a safe limit of moderator involved. At no time was criticality possible. At no rime was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-03-14
38766 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2002-03-10 | 2002-03-14 07:54 | 2002-03-14 | AGREEMENT STATE REPORT INVOLVING A STOLEN MOISTURE DENSITY GAUGE "A construction trailer [located at the Home Depot construction site in Loganville, GA] was broken into during the night of 3/10/02. A moisture density gauge along with other equipment was stolen. Police [and FBI] were notified and investigated. The gauge was a CPN Model MC-1, serial number: M17077782." The moisture density gauge contained two sources; 10 mCi Cs-137 and 50 mCi Am-241. Georgia Event Report ID No. GA-2002-07. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | GA | OTH | AGR |  |  |  |  | 0 | 2002-03-14
38765 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2002-03-13 18:30 | 2002-03-13 20:21 | 2002-03-21 | HIGH PRESSURE CORE SPRAY SYSTEM INOPERABLE "During the performance of a surveillance (E22-T2004) for high pressure core spray system (HPCS), the condensate storage tank suction check valve (1E22F0002) failed to seat properly. The operability determination for the check valve determined that there was significant potential that the check valve springs had broken resulting in foreign material in the HPCS system. Since the long-term operation of the system was potentially impacted, the system was declared inoperable at 1830. HPCS is a single train safety system." The licensee verified the operability of RCIC within one hour. The licensee notified the NRC Resident. ***THIS EVENT WAS RETRACTED 1641 EST 3/21/02 KEN RUSSELL TO MIKE NORRIS*** "On 3/1 3/02. a notification was made in accordance with 10CFR50.72(b)(3)(v)(D) for a potential Loss of Safety Function of the High Pressure Core Spray (HPCS) system, a single train safety system. The reason for this determination was the potential that foreign material may nave been introduced to the HPCS system. "During the regularly scheduled performance of a surveillance (1E22-T2004) for the HPCS system, the condensate storage tank suction check valve ( E22F0002) failed to seat properly. The operability determination for the check valve concluded that the valve did not directly impact system operability, but there was significant potential that the likely failure mode of the check valve was a broken spring, resulting in foreign material in the HPCS system. Since the long-term operation of the system was potentially impacted, the system was conservatively declared inoperable at 1830 on 3/13/02, although the system remained available and aligned for injection, had its operation been required. "The valve was subsequently disassembled and inspected. The inspection identified that the valve springs were still intact, but had weakened to the point that the check valve failed the closure verification test. Therefore, it was determined that the check valve failure had not introduced foreign material to the HPCS pump or piping and therefore the HPCS system would not have been prevented from performing its safety function. Since the HPCS system remained capable of performing its safety function this event is not reportable." The Licensee notified the NRC Resident. Notified R3DO (Phillips) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-03-13
38764 | 0 | YALE UNIVERSITY |  |  |  |  | 2002-03-13 15:00 | 2002-03-13 16:37 | 2002-03-13 | TWO TRITIUM EXIT SIGNS MISSING FROM MOUNTING BRACKETS During a review and inventory of tritium exit signs to be replaced with non-tritium signs, two exit sign brackets, without signs, were identified. Both missing signs were from the Arts and Architecture building and were 11.5 curies each. The signs were manufactured by Isolite, model #880. The licensee intends to contact the contractor who originally installed the signs, students, faculty, and the building supervisor for information to locate the missing signs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-03-13
38763 | 0 | WHEELING PITTSBURG STEEL CORP. |  |  |  |  | 2002-03-12 | 2002-03-13 13:43 | 2002-03-13 | SOURCE SHIELD SHUTTER WOULD NOT CLOSE A Cs-137, 2 curie source (1978), shield shutter would not close to secure source in the shield on the coke line. Licensee took compensatory measures to secure source by manually closing and blocking the shutter in the closed position. Additionally, a cable and counter-weight have been utilized to maintain the shutter in the secure condition. No personnel exposures were received as a result of this event. The licensee plans to remove the defective unit on 3/15/02 and ship it to a vendor (Texas Nuclear) for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-03-13
38762 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-03-12 14:30 | 2002-03-12 20:51 | 2002-04-19 | UNANALYZED CONDITION, APPENDIX R VALVE UNABLE TO SATISFY DESIGN FUNCTION "At 1430 on 3/12/02, an Appendix R credited valve was determined to be unable to satisfy its design function of providing a flow path from the Charging System to the Reactor Coolant System (RCS). The credited flow path is necessary to control RCS inventory and maintain the plant in Mode 3 (Hot Standby) during an Appendix R fire. The flow path is also utilized procedurally in controlling RCS inventory while the RCS is cooled down and depressurized from Mode 3 (Hot Standby) to Mode 5 (Cold Shutdown). "This issue places the plant in an unanalyzed condition and thus is reportable under 50.73 (a)(2)(ii). "The specific valve is 1/2CV-1296 Auxiliary Charging Line Isolation valve. The valve's design function is to open on a differential pressure of 200 psid (with or without instrument air) between the discharge of the charging pumps and the RCS. This line is not utilized during normal operations but is an available charging path to the RCS and utilized during plant shutdown in the event of an Appendix R fire. The valve is an air operated valve that is assumed to have failed close due to a loss of instrument air. It has been found that the valve will not open until a much higher differential pressure is reached. If the RCS is at normal operating pressure (2235 psig), and the actual lift pressure of the valve is greater than 500 psid, charging flow will be unavailable to the RCS. A relief on the discharge of the outlet of the charging pump will lift at 2735 and prevent flow to the RCS. The charging pump maximum discharge pressure is 3000 psig. "Compensatory actions have been undertaken that establish plantwide fire rounds. Fire rounds will be continued until the condition is corrected or a suitable evaluation is completed that establishes other actions." The licensee notified the NRC Resident. ****RETRACTION 4/19/02 at 1821 from Mike Holzmann to Rich Laura**** "RETRACTION OF EVENT NOTIFICATION #38762 "At 2051 EST on March 12, 2002, ENS Event Notification # 38762 was made in accordance with 10 CFR 50.72(b)(3)(ii)(B) for identification of an unanalyzed condition that had the potential to significantly degrade plant safety involving the Appendix R safe shutdown fire analysis. PBNP Unit 1 and 2 valve CV-1296, 'Auxiliary Charging Line Isolation Valve,' are air-operated valves. These valves, one in each unit, are credited with opening at 200 psid to provide a charging system flow path to control RCS inventory and to maintain the plant in Mode 3 (hot standby) during the Appendix R safe shutdown fire with loss of instrument air. The notification was made when we identified that the CV-1296 valves will not open until a much higher differential pressure is reached and; therefore, the flow path through the valve may not be capable of providing the Appendix R function of controlling RCS inventory. At the time of this notification an evaluation of the consequences of this Condition had not been assessed, and the report was made because of the potential for the plant being in an unanalyzed condition that significantly degrades plant safety. "We have subsequently completed an engineering evaluation which identified the differential pressure necessary to permit charging flow through the CV-1296 valve. This evaluation is based on the measured lifting force of the valve stem with zero differential pressure across the valve. We have further determined, based on engineering analysis supported by MAAP4 computer runs, and using a more conservative RCS injection pressure then identified above, that the RCS pressure would drop low enough to permit charging flow into the RCS, before the RCS pressurizer level is lost. We have thus concluded that the condition identified in our event notification would not result in a significant degradation of plant safety. Therefore, this condition is not reportable under 10 CFR 50.72 or 50.73, and we are hereby retracting this event notification." The Senior Resident Inspector has been informed. The R3DO (J. Madera) has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-03-12
38761 | -1 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-03-12 08:30 | 2002-03-12 14:50 | 2002-04-24 | UNANALYZED CONDITION - SI MINIFLOW LINE VALVE INTERLOCK MIS-WIRED "In the analysis for certain design bases accidents, credit is taken for a recirculation mode of operation that ensures continued cooling to the reactor core following an injection mode. During the current Unit 1 refueling outage, it was found that a safety injection (SI) miniflow line valve (1HV-8813) interlock was mis-wired. The interlock wiring should have allowed a second valve (1HV-8804B) to be opened during switchover from injection mode to recirculation mode once 1HV-8813 has been closed but would not. This wiring error was subsequently corrected. 1HV-8804B is opened to provide a suction source from the discharge of the Train B residual heat removal (RHR) pump to the suction of the SI pumps. 1HV-8804B must open for recirculation to begin if the opposite train is unavailable. A review has found that this mis-wiring has existed since at least 1996. "Based on preliminary evaluation, on 3-12-2002, at 0830 EST, we concluded that this may represent an unanalyzed condition that significantly degrades plant safety and is reportable per 10 CFR 50.72 (b)(3)(ii)(B). Further evaluation is being performed to determine the significance of the mis-wiring." The NRC Resident was notified by the licensee. ***** RETRACTION FROM JOHN WILLIAMS TO LEIGH TROCINE AT 1047 EDT ON 04/25/02 ***** The following text is a portion of a facsimile received from the licensee: "RETRACTION - Further review of the event reported on 03/12/02 via Notification #38761, and described [above], has concluded that it is not a condition that significantly degrades plant safety. It is hereby retracted." The licensee notified the NRC resident inspector and plans to make a 60-day report. The NRC operations officer notified the R2DO (Ann Boland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-03-12
38760 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2002-02-20 | 2002-03-11 17:03 | 2002-03-11 | SEALED GADOLINIUM SOURCE LOST During an inspection on 2/20/2002 by the VA at the Central California Health Care System, Fresno, CA a sealed Gd-153 (980 microcuries) source was determined to be missing as of 5/11/2001. The source is a solid Gadolinium pellet sealed in a titanium capsule and in a lead shield with a spring operated shutter. Present activity is calculated to be 430 microcuries. A search of the facilities, personnel interviews, and an inventory was conducted. It has been determined that in most probability the source inside its lead shield was mistakenly discarded with non-radioactive hospital waste and is presently buried in the municipal landfill. A visit to the landfill determined that recovery was very unlikely. There was little likelihood that this event resulted in measurable radiation doses to hospital workers or any member of the public. The RSO has been retrained in proper disposal of sources and methods for decay and storage. It is believed that sufficient corrective actions have been taken to date to prevent a reoccurrence of this event, however further actions are being researched and developed. The VA has contacted NRC Region 4 (Cain). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | CA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-03-11
38759 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-11 04:10 | 2002-03-11 04:12 | 2002-03-21 | PLANNED LOSS OF SAFETY PARAMETER DISPLAY SYSTEM FOR MAINTENANCE "This report is being conservatively made under 10CFR50.72(b)(3)(xiii) as a result of removing the Unit 2 Safety Parameter Display System (SPDS) from service for the purpose of implementing a modification to replace the system. This is a planned activity. The primary means of monitoring the critical parameters remains available to the operating crew and they will continue to be able to perform necessary actions regarding emergency assessment in the unlikely event of a situation necessitating its use." The NRC Resident Inspector has been notified. * * * UPDATE 3/21/02 AT 1443 EST BY AL DEES TO GERRY WAIG * * * Unit 2 SPDS returned to service at 1300 EST. The licensee notified the NRC Resident Inspector. Notified the R2DO (Jay Henson) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-03-11
38758 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-03-09 01:00 | 2002-03-09 05:32 | 2002-04-03 | LOCAL LEAK RATE TEST FAILURE Appendix J Local Leak Rate Testing of Containment Penetration for Drywell Sprays failed Tech Spec Acceptance Criteria for Secondary Containment Bypass Leakage. The leakage limit is 9 standard cubic feet per hour and the test results were 10.5 standard cubic feet per hour. The identified degraded condition is reportable as a condition of the nuclear power plant, including its principle safety barriers being seriously degraded per 10CFR50.72(b)(3)(ii) The NRC Resident Inspector will be notified of this event by the licensee. ***UPDATE (RETRACTION) ON 4/3/02 at 1147 EST FROM ROBERT BOESCH TO RICH LAURA*** "On 03/09/02, Appendix J Local Leak Rate Testing (LLRT) of a primary containment penetration for Drywell Sprays failed Tech Spec Acceptance Criteria for Secondary Containment Bypass Leakage. The test results were attributed to the tested Containment Isolation Valve (CIV), HV151F016A. The identified condition was reported in EN#38758 as a Degraded Condition per 10 CFR 50.72(b)(3)(ii)(A). "As a result of observations made during the testing, one of the test boundary valves, HV151F021A, was refurbished. Significant valve seat degradation was noted after the test boundary valve was disassembled. After the refurbishment of the test boundary valve, the Appendix J LLRT was repeated for the tested CIV, HV151F016A, with acceptable results. Since no significant maintenance was performed on the tested CIV that would affect its leak-tightness, the subsequent test results are valid for as-found leakage of the tested CIV. The total As-Found Secondary Containment Bypass Leakage was less than the Tech Spec limit. Based on this evaluation, ENS Notification EN#38758 is retracted." The NRC Resident Inspector was notified. The R1DO (G. Meyer) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-03-09
38757 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2002-03-08 13:45 | 2002-03-08 17:57 | 2002-03-08 | PRINCIPLE SAFETY BARRIER IN DEGRADED CONDITION Background "On February 27, 2002, a notification (Event number 38732) was made to the NRC in accordance with 10CFR50.72(b)(3)(ii)(a) to report a pressure boundary leakage path found by ultrasonic testing (UT) of a Control Rod Nozzle penetration number 3. The leakage path was found to be through the J -groove weld. During the initial stages of repair for Control Rod nozzle #3, it was determined that there was apparent material degradation of the reactor vessel head material adjacent to the nozzle penetration. After removal of the nozzle itself, and cleaning of the area, the condition was further investigated by performing ultrasonic thickness measurements of the reactor vessel head material. These measurements showed that the carbon steel material next to the nozzle was degraded as described below." Event "Ultrasonic thickness measurements indicate wastage of the carbon steel material adjacent to the nozzle that extends out from the nozzle penetration bored hole approximately 5 inches, at an approximate width of 4 to 5 inches at the widest part. The wastage of material is such that the remaining thickness of the reactor vessel head inner surface is approximately 3/8 inch thick including the reactor vessel cladding material." This condition is different than originally reported in Event Report 38732. As a result, this is being reported as a new non-emergency, 8-hour report in accordance with I0CFR50.72(b)(3)(ii)(a), a condition that resulted in the nuclear power plant, including its principal safety barriers being seriously degraded." The NRC Resident was notified by the licensee. Notified R3DO (John Madera) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-03-08
38756 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-08 11:10 | 2002-03-08 15:25 | 2002-03-08 | EMERGENCY OFFSITE SIRENS INOPERABLE "On March 8, 2002 at 1110 hours it was determined that all 165 of Limerick Generating Station's Emergency Offsite Sirens were inoperable. The sirens were rendered inoperable due to loss of electrical power to the siren controller located at Limerick Generating Station. Power was restored at 1140 hours. The Emergency Offsite Sirens were tested satisfactorily and are currently operable." The NRC Resident was notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-03-08
38755 | 0 | UNIV OF MICHIGAN |  |  |  | 2000 KW POOL | 2002-03-05 | 2002-03-07 20:08 | 2002-03-07 | 24-HOUR REPORT DUE TO TS VIOLATION INVOLVING A FUEL ELEMENT NOT INSERTED IN ITS PROPER LOCATION DURING REFUELING "This is a 24-hour Notification regarding a violation of Technical Specification 3.4.3. Following a major refueling and rod calibrations, the reactor was started up in accordance with Operating Procedure 101, Reactor Startup. The reactor reached 2 MW on 6 March 2002 at 19:22 hours. The following morning 7 March 2002 at 08:16 hours, the reactor was promptly shut down when the Day shift operating staff noted that core location 77 was open, and did not contain a fuel element, reflector, sample holder or experimental facility as required by Technical Specification 3.4.3." "The licensee identified safety concerns with respect to Technical Specifications 2.1.1 (safety' Limits in the Forced Convection Mode), 2.1.1 (Safety Limits in the natural Convection Mode), and 3.1.4 (Reactivity Limits). This occurrence may also involve unanalyzed conditions with respect to their Safety Analysis Report. The safety concerns and unanalyzed conditions include: reactor operation in forced convection at 2MW with an open grid location providing bypass flow: a fuel element being in natural convection cooling mode with the reactor operating above 100 KW; and a fuel element outside the normal configuration while the reactor is critical." "Description of Occurrence" "4-5 March - Refueling during dayshift 5 March 18:15 - Commence reactor startup in forced convection mode for Rod Calibrations between 5 and 59 KW. 6 March 16:05 - Complete Rod Calibrations, shut down reactor 17: 10 - Reactor Startup 17:29 - 500 KW Checks 17:32 - 1 MW, Calorimeter commenced 18:50 - Calorimeter completed 19:22 - Raise reactor power to 2 MW" "7 March 08:1 6 - Reactor Shutdown" "During this time indicated primary coolant flow was between 1053 to 1073 gallons per minute. A review of all nuclear instrument channel recorders showed no unusual indications. The core excess reactivity and measured core worth were all normal." "Core inspections were performed by many members of the operating staff as required by procedures during this time. During refueling, all fuel handling was done with at least two persons observing. A core inspection was performed immediately after refueling was completed. In addition, three core inspections were performed during building checks while rod calibrations were in progress, a core inspection was made during the Reactor Startup's 500 KW checks, and core inspections were made by the Swing and Mid shifts during building checks while operating at 2 MW. No abnormalities were noted on any of these inspections. Shortly after 08:00 on March 7, the Day shift operating staff inspected the core and noted that location 77 was open. The shift supervisor promptly shut down the reactor and informed both the On-Call Supervisor and the Reactor Manager." "A review of this occurrence has concluded that when grid location 77 was refueled, fuel element #304 ended up with its bottom nose cone outside the grid plate, while the bottom edge of the fuel element came to rest on the outside edge of the grid plate. The top of the slightly tilted fuel element was directly over location 77. Thus the element appeared, when inspected from above, to be correctly seated. Eventually, the element shifted to a vertical orientation caught between the edge of the grid plate and the nearby pneumatic tube bundle. Once the element shifted, the open location 77 became apparent and the reactor was shut down." "Safety Implications" "Two main issues have been identified: (1) The effect of an open grid location on forced convection operation at 2 MW; and (2) the effect on the fuel element #304 of operating it in natural convection mode. Analyses are being performed on both issues. A pool water sample was taken and analyzed. The pool water analysis was compared to past analyses of fuel element cladding failures. No fission products were noted. Fuel element #304 has been temporarily secured with a line to prevent failing off the grid plate. Procedures are being developed to remove the fuel element and will receive approval of the Safety Review Committee prior to implementation. The reactor remains in operation as required by Technical Specifications, but is shutdown (zero power). Analyses are being performed on these conditions to determine their full impact." "Root Causes" "The Reactor Manager and Operations staff reviewed the occurrence. The root cause investigation is ongoing." "Immediate Corrective Actions" "The reactor was shut down and will not be restarted for sustained operation until an operational review of this reportable occurrence is made and presented to the Safety Review Committee. An initial outside review of this occurrence has been made by the Dow Chemical Company, Midland, Michigan. A closed-mouth hook (carabiner) has been lowered on a line with a stainless steel leader and attached to the handling bail of element #304 to ensure it does not fall off the grid plate." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 3 | MI | NPR | [5 empty] | 0 | 2002-03-07
38754 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2002-03-07 14:00 | 2002-03-07 20:03 | 2002-03-07 | POTENTIAL LOSS OF SAFE SHUTDOWN CAPABILITY "At Oconee, TS 3.4.9 requires a minimum of 126 kW of Pressurizer heaters to be operable and capable of being powered from an emergency power supply. These heaters are needed to compensate for ambient heat loss from the Pressurizer in order to maintain single phase RCS natural circulation flow during various design basis events. In addition, TS 3.10.1 requires that the Standby Shutdown Facility (SSF) be operable for certain emergency conditions. One subsystem of the SSF is the Auxiliary Service Water (ASW) system. This system supplies a back-up emergency feedwater supply to any or all of the three Oconee Units. The Bases for TS 3.10.1 document that, in order to maintain single phase RCS natural circulation flow, an adequate number of Pressurizer heaters must be OPERABLE and capable of being powered from the SSF power supply. On March 7, 2002, Oconee Nuclear Site Engineering personnel concluded that heat transfer losses from the Reactor Coolant System Pressurizer to the reactor building environment exceeded the value previously used in system calculations and analyses. This conclusion was based on recent analysis of operational data on all three Oconee Units. There are two results of this conclusion: 1.Engineering concluded that the TS 3.4.9 requirement for a minimum of 126 kW of heater capacity is nonconservative. Operations personnel were notified. The operable capacity greatly exceeds the minimum so current compliance with the intent of TS 3.4.9 is not considered an issue. 2.Engineering recommended to Operations that the SSF-ASW system be declared inoperable because the existing heater capacity powered from the SSF is less than the minimum needed to fully compensate for the ambient heat losses as calculated from the recent analysis. Event: At 1400 hours on March 7, 2002, Oconee Operations accepted the Engineering recommendation and conservatively declared the Standby Shutdown Facility (SSF) ASW system inoperable and entered TS 3.10.1, Condition A, which has a 7 day completion time. The SSF-ASW was declared inoperable due to the discovery by site Engineering that heat transfer losses from the Pressurizer to the reactor building environment exceeded the capacity of Pressurizer heaters powered from the SSF power source. At the time of the discovery, there was no analysis to justify that single phase natural circulation could be maintained during all SSF design scenarios using the new loss values as inputs. Therefore Engineering concluded that there was a potential that two phase cooling might occur. At this time, the judgment of Engineering personnel is that two phase cooling would be adequate to protect the affected unit from any core damage, but two phase cooling is outside the TS basis documented for TS 3.10.1. Analyses are in progress to support a revision of applicable Abnormal Procedure to provide interim compensatory guidance to Operators. It is expected that this guidance will allow the Operator to avoid two phase flow. Oconee personnel will evaluate more permanent corrective actions after additional analyses are completed. This event is conservatively being reported under 10 CFR 50.72(b)(3)(v) as a condition that, at time of discovery, could have prevented the fulfillment of the safety function of the SSF ASW system to maintain a safe shutdown condition. The NRC Resident was notified at 1900 hours." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-03-07
38753 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-02-26 | 2002-03-07 14:57 | 2002-03-25 | ST BERNARD'S REGIONAL MEDICAL CENTER MEDICAL MISADMINISTRATION The following event description is taken from a faxed report. "Description of Event: Following initial source send, the proximal gold marker could not be discerned under fluoroscopy due to wire suture in the patients sternum. Twenty-four seconds elapsed between the arrival of the distal marker at the treatment site to source return to the delivery device. Two additional source sends were attempted with immediate return of the sources due to the inability to discern the proximal marker. Upon return of the sources to the delivery device, all sources were visible in the source chamber but the distal marker was not visualized. The treatment catheter was removed from the patient while still attached to the delivery device. The catheter and delivery device were placed into the bail-out box. The sources and distal cold marker were successfully returned to the delivery device following conclusion of the case." ***EVENT UPDATED 3/25/02 1135 EST BY FAX TO MIKE NORRIS*** The following was taken from a facsimile received from the Arkansas Department of Health, Radiation Control and Emergency Management on 3/25/02: "The Department received the licensee's written report via facsimile on March 19, 2002, with the original mailed hardcopy received on March 21, 2002. "The Department arranged for two qualified medical experts, a Radiation Oncologist and an Interventional Cardiologist, both approved for the Novoste Beta-Cath Devise, to review hardcopy cine images as well as a CD copy of the cine film. Neither expert could visualize the proximal marker on the images. In addition, one expert stated that they were unable to locate the source beads on the images and therefore could not determine their location in the body. In the final report, however, the licensee maintains that although the proximal marker could not be visualized they believe that the entire source train was delivered to the treatment site. "The licensee also submitted a dose calculation based on a 24-second dwell time. This dwell time equated to a dose of 2.4 Gy delivered at a distance of 2 mm from the centerline of the sources. The license's final report indicated that the written directive had been revised to note a delivered dose of 2.4 Gy to the target. The Department requested this revised written directive, however, it was not provided. "Based on the information provided to the Department by the two qualified experts, the Department does not agree with the licensee's determination that the dose was delivered to the target area. Therefore, the Department is classifying the event as a misadministration based on a 2.4 Gy dose delivered to an unintended and undetermined area of the body. "The licensee's report indicated that the suggested cause of the device failure was an inadequate connection of the treatment catheter or the fluid management system. This conclusion was supported by the amount of fluid accumulated in the sterile bag as well as the lack of pressure experienced by the radiation oncologist during the case. In order to prevent further occurrence, the licensee will perform an additional test run using the active source. This test run will be conducted outside the patient on a table located away from the cath lab staff. "In accordance with Department regulations, both the patient and the referring physician were notified of the misadministration. A copy of the licensee's final report was sent to the referring physician. "The Department considers this event closed." The NRC operations officer notified the R4DO (Chuck Cane) and NMSS EO (Janet Schlueter). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2002-03-07
38752 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-03-07 07:00 | 2002-03-07 13:42 | 2002-03-07 | C-3 STEAM GENERATOR CLASSIFICATION BECAUSE GREATER THAN 1% OF THE INSPECTED TUBES WERE DISCOVERED TO BE DEFECTIVE "At 0700 EST on March 7, 2002, with Watts Bar Unit 1 in Mode 6, steam generator inspections were being performed in accordance with Technical Specification (TS) 5.7.2.12, 'Steam Generator (SG) Tube Surveillance Program.' The results of the inspections performed on SG Number 4 indicated that greater than 1% of the inspected tubes were defective. Based on TS 5.7.2,12, this determination results in the classification of C-3. The current inspection results do not meet the criteria specified for steam generator tube degradation in Revision 2 of NUREG 1022, Event Reporting Guidelines 10 CFR 50.72 and 50.73. However, for classification C-3, WBN TS 5.9.9, 'SG Tube Inspection Report', requires that the results of the inspection be reported under 10 CFR 50.72. At this time, the submittal of a Licensee Event Report in accordance with 10 CFR 50.73 is not planned." The NRC Resident has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2002-03-07
38751 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-03-07 05:41 | 2002-03-07 06:41 | 2002-03-07 | PLANNED LOSS OF POWER TO EOF DUE TO MAINTENANCE "During performance of planned maintenance, the Emergency Operation Facility (EOF) will be de-energized. These maintenance activities, including electrical isolation and restoration are expected to last approximately 8 hours. Contingency plans for emergency situations have been established. "This event is reportable per 10CFR50.72(b)(3)(xiii) since this constitutes a loss of an emergency response facility for the duration of the evolution. "The NRC Resident was previously notified that this activity was scheduled to occur and will be informed of this ENS notification." * * * UPDATE ON 3/7/02 @ 2231 BY WEEKLEY TO GOULD * * * Power restored at 20:34 CT. Notified RDO(Loveless). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-03-07
38749 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-03-04 | 2002-03-04 11:37 | 2002-03-04 | UNUSUAL EVENT DUE TO UNCONTROLLED FLAMMABLE GAS LEAK ONSITE At 0946 CST, 3/4/02, an Unusual Event was declared due to a non isolable leak on a propane tank. The tank is approximately 500 to 750 gals, and is 55 % full. The tank is leaking at the rate of 5% decrease every 20 minutes. The tank is 25 to 30 yards out in the Owner Controlled Area and a local area evacuation has been performed. The Two Creek Fire Department is on the scene. NRC Resident Inspector has been notified. At 1147 EST, NRC entered Monitoring for Normal Phase Mode. ***EVENT UPDATED AT 1309 EST ON 3/4/02 BY MARK HANSON TO FANGIE JONES*** At 1154 CST, Licensee terminated Unusual Event due to leak isolated. At 1310 EST, NRC exited monitoring for the Unusual Event. Notified IRO (Holonich), R3DO (Madera), NRR (Grimes), PAO (Dricks), FEMA (Snyder). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-03-04
38748 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-03-04 08:41 | 2002-03-04 10:13 | 2002-03-04 | MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER "Manual reactor trip due to falling level in 1A Steam Generator (S/G), (RPS Activation). Level decrease occurred after the Feedwater Regulating Valve (FRV) for the 1A S/G failed closed upon loss of the normal and backup electrical power to the valve solenoid. After the reactor trip, the 1A S/G experienced a LO-LO Level Alarm which auto started both motor driven Auxiliary Feedwater pumps, (ESF Actuation). All S/G levels are now at normal levels and Unit 1 is stable. An investigation is in progress to determine the loss of electrical power to the FRV solenoid for the 1A S/G." The plant is dumping steam to the Main Condenser with no known Primary/Secondary leakage. There was no actuation of primary safety valves. All safety systems are operable and normal electrical distribution is available. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-03-04
38747 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-03-03 03:00 | 2002-03-03 06:04 | 2002-03-03 | MSIV LEAKAGE EXCEEDS ALLOWABLE LIMIT "Leak Rate Testing on Unit 1 Main Steam Isolation Valves has identified that the total minimum pathway leak rate exceeds the required limit of 300 scfh. The MSIV pathway combined leak rate was 1051 scfh. The identified degraded condition is reportable as a condition of the nuclear power plant, including its principal safety barriers being seriously degraded per 10CFR50.72(b)(3)(ii)." The NRC resident inspector will be informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-03-03
38746 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-03-03 02:18 | 2002-03-03 04:25 | 2002-03-03 | OFFSITE NOTIFICATION DUE TO OIL SPILL INTO DELAWARE RIVER "On March 3, 2002 at 0218 a cooling line to 12B circulating water pump upper motor bearing ruptured inside the upper oil reservoir. Oil was displaced from the oil reservoir and approximately 50 gallons of oil entered the Delaware River. 12B circulating water pump was removed from service and the leak was terminated. Cleanup efforts by onsite personnel are in progress. A 15 minute report was made to the New Jersey Department of Environmental Protection. A two hour report was made to the National Response Center in accordance with the site spill plan. Salem Unit 1 was initially at 100% power with 13B circulating water pump out of service for scheduled maintenance. Power reduction is currently in progress in response to the loss of 12B circulating water pump with a target power level of 40%." The NRC resident inspector has been informed of this notification by the licensee. | 45 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-03-03
38745 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-03-01 | 2002-03-01 18:14 | 2002-03-27 | UNANALYZED CONDITION DUE TO FIRE BARRIERS NOT INSTALLED PER DESIGN "On March 1, 2002, Harris Nuclear Plant personnel determined that an unanalyzed condition existed due to a required three-hour fire barrier not installed per design. The applicable fire barrier was designed to provide required separation between redundant train cables supplying A-SA Emergency Diesel Generator and B-SB Emergency Diesel Generator. Harris Nuclear Plant has initiated a continuous fire watch as a compensatory measure until the affected barrier could be restored to the design configuration. This issue is being reported in accordance with 10 CFR 50.72 as an unanalyzed condition." The licensee notified the NRC Resident Inspector. * * * RETRACTED ON 03/27/02 AT 1500 BY JOHN CAVES TO GERRY WAIG * * * "Reference Event Notification (EN) # 38745. On March 1, 2002 at 1814, Harris Nuclear Plant (HNP) submitted an eight hour report per 10 CFR 50.72 (b)(3)(ii)(B) for an unanalyzed condition related to a three-hour fire barrier. HNP subsequently determined that the as-found condition is consistent with the HNP Licensing Basis. Therefore, Harris Nuclear Plant is withdrawing the report EN # 38745." The licensee notified the NRC Resident Inspector. R2DO (Carolyn Evans) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-03-01
38744 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-02-22 18:30 | 2002-03-01 15:05 | 2002-03-01 | AGREEMENT STATE REPORT - LOCK MALFUNCTION ON CAMERA "On Friday February 22, 2002, a radiographer from METCO discovered that the lock on the Amersham 660 radiography camera with 60 curies of Ir-192 would not release to allow an exposure. The Environmental Manager from LA Pigment believed the auto-lock on the exposure device failed. The RSO at METCO responded within 30 minutes. The RSO stated that he cleaned the lock with WD-40 and the lock functioned after that. The RSO believes the lock was just dirty." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-03-01
38743 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-03-01 02:59 | 2002-03-01 10:20 | 2002-03-20 | UNIT EXPERIENCED MOMENTARY LOSS OF RHR COOLING "At approximately 0259 on March 1, 2002, with the Watts Bar Unit 1 reactor in Mode 6 with RCS temperature at approximately 100 degrees, during a refueling outage, operators isolated the common flowpath to the residual heat removal (RHR) pumps on two occasions over a 2 minute span. At the time of the event, operators were performing full flow testing of ECCS lines in conjunction with reactor cavity fill for refueling activities. The circumstances of the event are currently under investigation by the Site staff." No observable RCS heatup occurred during the period that RHR was isolated. The NRC resident inspector was notified. * * * RETRACTED ON 3/20/02 AT 1503 FROM PAUL PACE TO GERRY WAIG * * * "On March 1, 2002. TVA's Watts Bar Nuclear Plant reported the following event to the NRC Operations Center under 10 CFR 50.72 (b)(3)(v)(B). (Event Number 38743): "At approximately 0259 on March 1, 2002, with the Watts Bar unit 1 reactor in Mode 6 with RCS temperature at approximately 100 degrees, during a refueling outage, operators isolated the common fiowpath to the residual heat removal (RHR) pumps on two occasions over a 2 minute span At the time of the event, operators were performing full flow testing of ECCS lines in conjunction with reactor cavity fill for refueling activities... "A subsequent detailed review of the event described above and the guidance of NUREG 1022 has determined that there was no 'reasonable expectation of preventing fulfillment of the safety function' to remove residual heat. Therefore the event is not considered reportable under 10CFR 50.72 and is withdrawn." The licensee notified the NRC Resident Inspector. The R2DO (J. Henson) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2002-03-01
38742 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-02-14 | 2002-03-01 08:52 | 2002-03-01 | AGREEMENT STATE REPORT INVOLVING A STUCK LOGGING WELL SOURCE "Well logging tool became stuck at 17,125 feet, top of tool is 17,106 feet. Attempted fishing on 3 consecutive days, unsuccessful. Pumped 466 feet of red cement to secure source on February 14, 2002, to plug well. Top of plug is 16,640 feet. Permanent identification plaque is under construction for emplacement on the wellhead. Abandoned at Frank Bell #1 RE, Leon County, Texas, AP# 42-289-30432. Source abandoned IAW Texas Regulations. "Isotope Products Laboratory, sealed logging source (Capsule Type), Model # HEG-241, Serial # NN-082, 250 microcuries Am-241. Last leak tested 09/07/01 (No leakage). Manufactured September 25, 1998, pressure tested to 25,000 psi." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-03-01
38741 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-03-01 02:16 | 2002-03-01 02:29 | 2002-03-01 | SECURITY REPORT Unescorted access granted inappropriately to contract employee. Immediate compensatory measures taken upon discovery. The licensee will inform the NRC resident inspector. Contact the Headquarters Operations Officer for additional details. | 87 | 100 | 0 | 87 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-03-01
38740 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-02-28 16:25 | 2002-02-28 20:55 | 2002-02-28 | SAFE SHUTDOWN CAPABILITY IMPACTED BY NON-CONSERVATIVE SG NR SETPOINT "At 1625, Callaway Plant entered Technical Specification 3.0.3 because of Steam Generator (S/G) water level instrument channels being inoperable due to a non-conservative S/G Low-Low Level setpoint. "Based upon a review of information provided by Westinghouse and Operating Experience 13294 from Diablo Canyon regarding unexpected response of S/G Narrow Range level trips not responding as expected, an assessment was performed of the S/G Narrow Range (NR) Low-Low Level trip setpoints at Callaway. This assessment determined that the present Low-Low Level trip at 14.8% did not account for the uncertainties associated with the differential pressure (dP) created by the steam flow past the mid-deck plate in the moisture separator section of the S/G. This dP phenomena will cause the S/G NR level channels to read higher than actual water level at high steam flows. Thus, the Low-Low Level trip setpoint is non-conservative. "In the unlikely event of a Main Feed Line Break inside Containment, the potential exists that a required reactor trip on Low-Low S/G levels may be delayed or may not be received at all. In this scenario, other trip functions such as overtemperature delta-T would be expected to actuate in response to the initiating event. However, preliminary analyses indicates these would arrive in a different sequence, with preliminary calculations indicating that overtemperature delta-T trip actuation occurring early. The net effect on the UFSAR Chapter 15 accident analysis results is unknown. Thus, a condition exists in that a safety function could have been prevented. "A plant power reduction was commenced at 1658, 2/28/02, to decrease reactor power to below 30% where engineering calculations indicate the S/G mid-deck plate dP condition will no longer result in a non-conservative setpoint. Actions needed to return to 100% reactor power are being evaluated under an Operability Determination in accordance with Generic Letter 91-18 and Admin Letter 98-10." The licensee notified the NRC Resident Inspector. See similar events, EN #'s 38697, 38702, 38713 NOTE: Exited TS 3.0.3 at 2205 CST on 2/28/02 | 29 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  | 0 | 2002-02-28
38739 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2002-02-28 | 2002-02-28 19:44 | 2002-02-28 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR GAUGE, SOURCE STILL SHIELDED The following is taken from a faxed report: Event Report ID No. NV-02-001 Desert Geotechnical, 3355 Spring Mountain Road, #4, Las Vegas, NV 89102 License No. 00-11-0370-01 Technician left gauge unattended while calibrating it. Gauge (Troxler 3440 No. 25287) was run over by a heavy truck. The source rod remains in the shielded position. Job site was Peaceway 9440 Peaceway, Las Vegas. Date of occurrence is Feb 28, 2002. Nominal radionuclide, activity Cs-137 is 8 mCi and Am-241:Be is 40 mCi. Licensee corrective actions are to be determined. Enforcement Actions will be determined when on-site investigation is concluded. The gauge has been placed in its shipping case and returned to the licensee's facility. Las Vegas personnel will conduct an on-site investigation to determine the condition of the gauge and perform radiation readings. The licensee will contact gauge manufacturer for shipping instructions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2002-02-28
38738 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-02-28 14:15 | 2002-02-28 17:03 | 2002-02-28 | CONTROL ROOM VENTILATION SYSTEM DECLARED INOPERABLE "On February 26, 2002 at 1030 hours it was discovered that Unit 1 Electrical Auxiliary Building Fire Damper 3V111VFF314 was in its failed closed position. On February 27, 2002 at 1035 hours, it was determined that with the 'A' and 'C' Trains of the Control Room Ventilation system in Emergency Makeup and Cleanup Filtration mode the Control Room environment was not at a 0.125 inches water gauge positive pressure with respect to adjacent areas as required by Surveillance Requirement 4.7.7.e.3. The 'A' and 'C' trains of Control Room Ventilation system were declared inoperable. The 'B' Train of Control Room Ventilation was already inoperable at this time as part of a planned Train 'B' maintenance window. This condition (all three trains of Unit 1 Control Room ventilation inoperable) placed the unit in Technical Specification 3.7.7 LCO Action Statement 'c', requiring restoration of at least one train within 12 hours, or be in Hot Standby within the next 6 hours. The fire damper was repaired, and flow balancing of the affected ventilation system was performed. Following satisfactory completion of operability surveillance testing to verify that the required differential pressure was restored, Trains 'A' and 'C' of Control Room Ventilation were declared operable at 2045 hours on February 27, 2002. Although the 'A' and 'C' Trains were fully capable of providing the emergency CRE [Control Room Envelope] makeup and cleanup filtration function during the degraded condition, a 0.125 inches water gauge positive differential pressure between the control room and adjacent spaces required by Technical Specifications was not maintained. Therefore, the safety function of the Control Room Ventilation system to mitigate the consequences of radiological dose to operators during accident conditions nay not have been fulfilled, and this notification is being made pursuant to 10 CFR 50.72(b)(3)(v)." The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-02-28
38737 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2002-01-13 22:26 | 2002-02-28 16:42 | 2002-02-28 | INVALID PRIMARY AND SECONDARY CONTAINMENT ISOLATIONS The following report is taken from a 60 day report faxed to the Headquarters' Operations Center: Invalid Primary and Secondary Containment Isolations Due to Spurious Upscale Spikes of the Reactor Building Ventilation Radiation Monitor B Event Description: At 2226 hours on January 13, 2002, and at 0258 hours on January 18, 2002, with the plant operating at 100 percent of rated thermal power, the Reactor Building (Secondary Containment) Ventilation Exhaust Radiation Monitor B spiked upscale due to invalid actuation signals. The plants response was identical on both occasions. The radiation monitor upscale spikes resulted in automatic closure of outboard isolation valves and, therefore, isolation of the following systems or functions; 1. Primary Containment Drywell and Suppression Chamber pressure sensing for alarm and indication functions only, 2. Primary Containment Continuous Atmosphere Monitoring (CAM) for particulate and gaseous radioactivity monitoring, and 3. Primary Containment Hydrogen and Oxygen Analyzer B. The trip signals also resulted in automatic isolation of the Reactor Building (Secondary Containment) Ventilation System and starting of the Standby Gas Treatment subsystem B to maintain the Reactor Building atmosphere at a slightly negative pressure. System performance was in accordance with the design. Examinations of operating records indicated that the redundant monitor, other monitoring systems, and the plant computer system did not detect any abnormal radioactivity during the two events. Shift operating and radiation protection personnel investigated and did not detect any abnormal radiological conditions. A root cause evaluation determined the reasons for the intermittent high scale spiking were fluctuations in DC voltage within the radiation monitor high voltage power supply. These fluctuations directly affected the Geiger-Mueller tube causing it to produce spurious high count-rate outputs of short duration. Actions Taken: 1. Verified system responses were in accordance with the design. 2. Replaced the degraded high voltage power supply. 3. Successfully completed radiation monitor post work testing. 4. Restored the affected systems to service. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-02-28
38736 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2002-02-28 | 2002-02-28 13:44 | 2002-02-28 | AGREEMENT STATE REPORT - DISCOVERY OF AN ABANDONED GAUGE "The NC Division of Radiation Protection was notified (on February 28, 2002) of the discovery of an abandoned Cesium 137 'fixed' gauge at a metal scrap yard located in Hertford, NC (NucorSteel). Most labels on the gauge are intact with the following information: Texas Nuclear, LX-303, Series CN, Model 5207, S/N B34, Cs 137 - sealed source, 2.00 Ci (12-83) The condition of the gauge is reported as 'shielded and the shutter closed'. The gauge has been secured and isolated from the public. The NC Division of Radiation Protection has contacted Thermo Measure Tech and determined the reported gauge information to be accurate and further determined the gauge was sold/shipped to Essex Industrial Chemical(s) in January 1984 (there were a total of four gauges shipped S/Ns B31 - B34). The NC Division of Radiation Protection has not been unable to contact Essex Industrial Chemical(s), but will continue attempts. The Maryland State radiation protection program has been notified of the incident and is assisting." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2002-02-28
38735 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-02-27 10:00 | 2002-02-28 10:29 | 2002-02-28 | AGREEMENT STATE REPORT INVOLVING DAMAGE TO A FIXED GAUGE "On the afternoon of February 27, 2002, the Alabama Office of Radiation Control was advised by McWane Cast Iron Pipe of Birmingham, Alabama, Alabama License No. 507 that at approximately 10:00 am that morning that a recently installed Ohmart Vega Model SHLG device containing 4.5 Ci of Cs-137, had been exposed to excessive heat causing part of the device's internal lead shielding to melt. A consultant, Don Hamner, Alabama License No. 695 was contacted by McWane. Mr. Hamner surveyed the device and wiped the device finding no removable contamination and reading of 0.8 mR/hr on the top, 2.0 mR/hr on the front, and 30 mR/hr on the bottom, confirming that the shielding had been compromised on the bottom. The maximum level at one foot from the device was 5 mR/hr. No one was overexposed or injured. "This device was installed on 2/15/02 to replace the device that was damaged by heat two weeks earlier 2/13/02. See Alabama Incident 02-09 and NRC PNO-ll-02-007. "The State of Alabama has advised McWane Cast Iron Pipe not to place another radioactive gauge of this type in this same location until a method to prevent future overheating at the location or a device designed to withstand the heat has been agreed to by the state. "Alabama is conducting an on site investigation today. Additional details will be available Friday afternoon 3/1/02 or Monday morning 3/4/02." HOO note: Refer to event number 38699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-02-28
38734 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2002-02-27 16:30 | 2002-02-28 10:48 | 2002-02-28 | FITNESS FOR DUTY REPORT "On 02/27/02 at approximately 1630, confirmed results from an unannounced follow-up Fitness for Duty (FFD) test of a non-licensed supervisory individual, who performs duties with in the scope of 10CFR26, indicated positive for controlled substances." The individual's site access has been suspended and the licensee is conducting a review of the individual's recent work. The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2002-02-28
38733 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2002-02-26 | 2002-02-27 16:01 | 2002-02-27 | AGREEMENT STATE REPORT REGARDING THE LOSS OF CONTROL AND RECOVERY OF AN ACS ENGINEERING GROUP, CONSTRUCTION, MOISTURE/DENSITY GAUGE IN TEMPE, ARIZONA The following text is a portion of Preliminary Notification PNO-IV-02-013 received from NRC Region 4: "On February 26, 2002, the Arizona Radiation Regulatory Agency (ARRA) notified NRC Region IV by facsimile of the loss of control and recovery of a portable gauge. The ARRA was informed by the Gilbert, Arizona fire department on February 26, 2002, that a Troxler moisture/density gauge, Model 2401 (Serial No. MD91 005368) containing a 370 megabecquerel (10 millicurie) source of americium-241/beryllium and a 1.48 gigabecquerel (40 millicurie) cesium-137 source had been recovered by a motorist that saw the device fall off of a truck. The motorist picked up the gauge and turned it into the local police department. ARRA determined that the truck was operated by two employees of ACS Engineering Group, Construction, an Arizona licensee. The gauge was not damaged. The licensee reclaimed the device on February 26, 2002. ARRA will be investigating the event. Media interest included reports by three local television stations." "Region IV received notification of this occurrence by facsimile from ARRA at 2:35 p.m. (CT) on February 26, 2002. Region IV has informed OEDO, NMSS, STP, and OPA." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2002-02-27
38732 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2002-02-27 13:30 | 2002-02-27 15:42 | 2002-03-09 | IDENTIFICATION OF AXIAL THROUGH-WELD INDICATIONS (REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE) ON ONE CONTROL ROD DRIVE MECHANISM NOZZLE The following text is a portion of a facsimile received from the licensee: "On February 26, 2002, following shutdown for a scheduled refueling outage, the Davis-Besse Nuclear Power Station performed a qualified visual examination of the Reactor Vessel head per NRC Bulletin 2001-01. This examination revealed evidence of boric acid build up around Control Rod Drive Mechanism (CRDM) nozzles but was inconclusive due to the previous known boric acid deposits. At approximately 1330 hours on February 27, 2002, Ultrasonic Testing (UT) data identified axial through weld indications on one CRDM. Engineering evaluation of this data confirmed Reactor Coolant System pressure boundary leakage exists. Technical Specification 3.4.6.2.a states that Reactor Coolant System leakage shall be limited to no pressure boundary leakage. As a result this is being reported as a non-emergency, 8-hour report in accordance with 10CFR50.72(b)(3)(ii)(a), a condition that resulted in the nuclear power plant, including its principal safety barriers being seriously degraded." The licensee stated that UT inspections are continuing on other nozzles. The licensee plans to notify the NRC resident inspector. * * * UPDATED AT 1921 EST ON 3/5/02 BY TERRY PLOEGER TO FANGIE JONES * * * "All inspections have been completed at this time. UT data for CRDM nozzles 1 and 2 (locations H-8 and G-7, respectively) has been evaluated to exhibit axial indications that represent pressure boundary leakage. This completes evaluation of the extent of the condition for the report communicated on February 27." The licensee notified the NRC Resident Inspector. The R3DO (John Madera), NRR EO (David Matthews), and IRO (Tim McGinty) have been informed. * * * UPDATE ON 3/9/02 @ 1258 BY WOLF TO GOULD * * * Clarification to Event Number 38732: The Control Rod Drive Mechanism nozzle reported on February 27, 2002, as having pressure boundary leakage due to an axial through-weld indication was CRDM nozzle 3 (location G-9). The completed inspections revealed a total of 3 nozzles that exhibited axial indications that represent pressure boundary leakage - nozzles 1, 2, and 3. The NRC Resident Inspector was informed. Notified RDO(Madera), EO(Matthews) and IRO(Wessman) * * * HOO NOTE - SEE EN# 328757 FOR ADDITIONAL INFORMATION * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | RESPONSE-BULLETIN |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2002-02-27
38731 | 0 | CANBERRA INDUSTRIES, INC. |  |  |  |  | 2002-01-28 13:00 | 2002-02-27 15:13 | 2002-02-27 | LOSS OF LICENSED NUCLEAR MATERIAL On 1/28/02 at 1300, it was discovered that 13 Cl-36 sources were missing. The sources were 10 microcuries each and were manufactured on Nov 1995. The sources were 1 inch diameter, flat disc with mylar window, and assembled with an ion chamber instrument. Each source was individually packaged in a 2ft x 1ft x 1ft cardboard box. The assemblies were packaged for shipment on 1/28/02 and stored on a shelf prior to shipment. A clean up had been performed recently and it is believed by the Licensee, that these materials had been thrown into a waste dumpster for disposal. There was no detectable radiation levels on the shipping container, and it is believed by the Licensee that there is no threat to the general population. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-02-27
38730 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2002-02-27 10:43 | 2002-02-27 14:54 | 2002-02-27 | AUTOMATIC TURBINE TRIP/REACTOR TRIP DUE TO A LOSS OF OFFSITE POWER ON UNIT 3 DURING THE PERFORMANCE OF SWITCHYARD MAINTENANCE Prior to this transient, the 220-kV, switchyard, section-B, west bus was de-energized to facilitate the performance of maintenance activities. During the performance of local breaker failure backup testing on the switchyard, section-B, west bus; the switchyard section-B east bus tripped at 1043 PST resulting in a loss of offsite power on Unit 3. The loss of offsite power in turn caused a turbine trip/reactor trip signal to be generated. All rods fully inserted. An emergency feedwater actuation signal (EFAS) initiated as expected on steam generator shrinkage, and a containment cooling actuation signal (CCAS) was manually initiated. The loss of offsite power also resulted in a loss of all non-1E power. The reactor coolant pumps remained running because their power supply automatically transferred to Unit 2, and the Unit 3, 1E, 4-kV buses remained energized from Unit 2. The emergency diesel generators automatically started but did not load due to the automatic power supply transfers to Unit 2. Preliminary indications revealed that the primary safety valves remained closed. The licensee stated that all systems functioned as required and that there was no impact on Unit 2. Unit 3 is currently stable in Hot Standby with emergency feedwater supplying water to the steam generators and secondary steam being dumped to atmosphere via the atmospheric dump valves (due to a loss of condenser vacuum). The licensee reported that there was no steam generator tube leakage. Containment parameters remain normal. The Unit 3 east and west switchyard buses have been re-energized, and all non-1E power was restored to the 4-kV buses at 1120 PST. The emergency diesel generators have been secured. The licensee currently plans to perform secondary equipment inspections, and the event evaluation is ongoing. The licensee notified the NRC resident inspector and may make a press release. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-02-27
38729 | -1 | UNIV OF MICHIGAN |  |  |  |  | 2002-02-27 08:30 | 2002-02-27 12:00 | 2002-02-28 | 10 CFR PART 21 NOTIFICATION REGARDING FAILURE OF A J.L. SHEPHERD & ASSOCIATES, MARK-1, MODEL-25, IRRADIATOR, DOOR INTERLOCK During the performance of a pre-operations inspection, an operator discovered that an irradiator door interlock could be defeated and that the door could be raised and expose the source. The irradiator involved is a J.L. Shepherd & Associates, Mark 1, Model 25, irradiator which contains 780 curies of cesium-137, and it is used for irradiating biological specimens. The university has been contacted. The licensee notified the NRC Region 3 office (Darryl Weideman), and the licensee plans to notify the vendor. (Call the NRC operations officer for a licensee contact telephone number.) * * * RETRACTED AT 1530 EST ON 2/28/02 BY MARK DRISCOLL TO GERALD WAIG * * * After discussion with NRC Region 3 (George Parker) MSU Rad Safety Officer (Mark Driscoll) called to retract the event as it should not have been reported under 10CFR21. Mr. Driscoll stated that the event will be reported to NRC Region 3 under Paragraph 5 of a NRC Order dated July 3, 1984. Notified R3DO (Lipa) and NMSS (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 21.21 |  |  |  | 0 | 2002-02-27
38728 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-02-26 15:00 | 2002-02-27 11:59 | 2002-02-27 | NRC BULLETIN 91-01 RESPONSE INVOLVING A C4 DISSOLVER ACID WASH PUMPOUT (24-Hour Report) The following text is a portion of a facsimile received from the licensee: "Facility -- Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (<=5.0 wt. % U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107." "Time and Date of Event -- Approx. 15:00 hours, Tuesday, February 26, 2002." "Reason for Notification -- During an internal procedure review by Operations, it was discovered that a current Process Information Form (PIF) for flushing and pumping out the lines of the C4 dissolvers did not contain all the required criticality controls. The operating procedure for pumpout of UN product to non-favorable geometry bulk storage requires sampling for grams U-235 per liter, pH, and % free acid. The PIF required only % free acid." "Summary of Process -- During normal processing, uranium is recovered from scrap materials in the favorable geometry C4 dissolvers system. The resulting uranyl nitrate (UN) is sampled and released. It is then pumped through gamma monitors, an active engineered control, to the non-favorable geometry UN bulk storage tanks." "When needed for uranium accountability purposes, the C4 dissolver system tanks are filled with water to the 40% level and then with water and acid to the 43% level (approximately 102.3 gallons total) to flush the system." "As-Found Condition -- A summary of the as found conditions is as follows: * The condition was found during an internal procedure review - not during acid wash pumpout. * The PIF was approved for use on February 14, 2002. * The PIF required only sampling for free acid. * The gamma monitors were functioning properly." "Double Contingency Protection -- Double contingency protection for this situation is based on concentration control, that is (1) preventing solutions with >10 grams U-235 per liter from being transferred into the UN bulk storage tanks, and (2) detecting any increasing concentration of U-235 in the tanks and taking corrective actions. It was determined, however, that documented double contingency protection was lost because sampling for pH was not required on the PIF. Double contingency protection was immediately restored by withdrawing the PIF. Therefore, the incident requires notification in accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3(c.5), in which less than previously documented double contingency protection remains in an analyzed system, but less than safe mass is involved." "Summary of Activity -- * The PIF was immediately withdrawn. * Immediate instructions were given to Operations to ensure that all required sampling was performed. * A causal analysis will be performed to determine corrective actions needed to prevent recurrence." "Conclusions -- * Loss of documented double contingency protection did occur, but was immediately restored. * At no time was criticality possible because the gamma monitors ensure that the concentration remains <5 grams U-235 per liter. * At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. * It has been determined that this is a safety significant incident in accordance with governing procedures. A root cause analysis will be performed." The licensee notified the NRC Region 2 office (David Ayres) and NMSS (Dennis Morey). (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-02-27
38727 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2002-01-28 15:00 | 2002-02-27 09:47 | 2002-02-27 | AGREEMENT STATE REPORT INVOLVING POSSIBLE MISADMINISTRATION "Event description: Cordis Checkmate IVBT system was used to treat a coronary artery on 1/28/02. On 1/31/02 dosimetry and physicist records were being reviewed by licensee physics staff and it was discovered that the 'diameter' of the vessel was used in the calculation instead of the 'radius'. Agency was contacted by phone on 14 February 2002 to inform Agency of possible misadministration. At this time the actual increase in dose had not been determined. On 14 February 2002 the Agency was notified by FAX that, in fact, a misadministration had occurred. Estimated dose received by the outer portion of the coronary artery was 14.6 Gy rather than the intended 8 Gy. Patient and physician were notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2002-02-27
38726 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-02-26 13:02 | 2002-02-26 13:52 | 2002-02-26 | SECURITY REPORT INVOLVING UNESCORTED ACCESS GRANTED INAPPROPRIATELY Contract employee granted unescorted access inappropriately. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-02-26
38725 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-02-25 15:30 | 2002-02-25 23:30 | 2002-02-25 | NRC BULLETIN 91-01 RESPONSE (24-Hour Report) "At 1530 [CDT], on 02-25-32, the Plant Shift Superintendent (PSS) was notified that the adjacent system post-removal NDA or visual inspection was not performed as required by GEN-10 for the accumulator in C-310. The post-removal NDA for the adjacent system is required to be performed within 24 hours of the equipment being removed. The post-removal NDA measurement is used to independently verify the mass of any potential adjacent system deposit is less than an always-safe mass and can be characterized as Uncomplicated Handling (UH), The pre-removal NDA indicated a UH deposit in the adjacent system." "The post-removal NDA measurement was subsequently performed which confirmed the adjacent system to be UH." "In summary, actions required by the NCSA were not completed within the time frame specified." "The NRC Senior Resident Inspector has been notified of this event." "PGDP Assessment and Tracking Report No. ATR-02-1040; PGDP Event Report No. PAD-2002-009, Event Worksheet [38725]." "Responsible Division: Operations" "SAFETY SIGNIFICANCE OF EVENTS:" "Double contingency was not maintained because the independent verification of mass In the adjacent system was not performed within 24 hours of equipment removal. The control relied upon for independent verification of less than an always-safe mass was violated. However, a second independent post-removal NDA result confirmed an always-safe mass." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR:" "In order for a criticality to be possible, the pre-removal NDA would have to be in error and a uranium deposit would have to exceed the always-safe mass of approximately 30 pounds at 5.5 wt. %235 U. The deposit within the adjacent system would then need to become moderated through wet air in-leakage or introduction of moderator from a sprinkler activation, RCW leak, etc." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.:" "The controlled parameter is mass." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS):" "The adjacent equipment post-removal NDA indicated <15 pounds of U with an assay of 5.27% with <325 grams of U235." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES:" "Double contingency for the adjacent system of the equipment removed relies on the control of mass by two independent verifications. The mass process condition is controlled by two independent verification of an always-safe mass using NDA or visual inspections." "The first leg of double contingency is established by the requirement to perform a pre-removal NDA measurement to ensure the adjacent system contains lass than an always-safe mass prior to making the first cut. The pre-removal NDA was performed and showed less than an always-safe mass. This control was maintained." "The second leg of double contingency is established by the independent verification of less than an always-safe mass by a post-removal NDA measurement or visual inspection performed on the adjacent system within 24 hours of equipment removal. The post-removal NDA or visual inspection was not performed within the required time frame. Therefore, neither the control nor the process condition was maintained." "The post-removal NDA measurement or visual inspection on the adjacent system was not performed within the required 24-hour time limit. Therefore, double contingency was not maintained." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED:" "Post-removal NDA has been completed with the results indicating the adjacent piping is Uncomplicated Handling (UH)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-02-25
38724 | 0 | VA NATIONAL HP PROGRAM |  |  |  |  | 2002-02-25 14:15 | 2002-02-25 16:10 | 2002-02-25 | RECEIPT OF A PACKAGE WITH A CONTAMINATED LABEL A thallium 201 transport container (metal "ammo" box) was found to be contaminated with Technetium-99m upon arrival at the VA Medical Center in Birmingham, AL from a vendor in Birmingham, AL. The removable contamination was 969 DPM/cm² (limit =222 DPM/cm²) and identified as coming from a magnetic sticker affixed to the box. The vendor, a commercial radiopharmacy, was notified, and the licensee planned to notify the State of Alabama. The licensee indicated that a similar event occurred at this hospital about 2 years ago. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | AL | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2002-02-25
38723 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-02-25 14:00 | 2002-02-25 15:00 | 2002-02-25 | INABILITY TO MAINTAIN TEMPERATURES IN RELAY AND SWITCHGEAR ROOMS DUE TO CONTROL STRUCTURE HVAC SYSTEM INOPERABILITY The following is a portion of the facsimile from the Licensee: "During review of the station deficiency report the following reportable condition was identified [at approximately 1400]. At 1855 on 2/22/02 while placing the 'B' Control Structure Chiller handswitch from "auto" to "start", the chiller tripped due to a trip of the Ventilation Supply Fan breaker. The breaker was able to be reset and the Chiller was restored after 6 minutes. The 'A' Control Structure Chiller was already inoperable with post maintenance testing in progress. With the loss of Control Structure HVAC System the ability to maintain temperatures in various spaces including Relay rooms and Emergency Switchgear rooms was lost. The failure requires an 8 hr ENS notification in accordance with 10CFR50.72(b)(3)(v)." The Resident Inspector was notified. | 81 | 100 | 0 | 81 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2002-02-25
38722 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-02-25 04:15 | 2002-02-25 04:25 | 2002-03-08 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) OUT OF SERVICE The SPDS was removed from service for the purpose of implementing a modification to replace the system. The primary means of monitoring the critical parameters remains available to the operating crew and they will continue to be able to perform the necessary actions regarding emergency assessment. The NRC Resident Inspector will be notified. * * * UPDATE 0942EST ON 3/8/02 FROM GUY GRIFFIS TO S. SANDIN * * * The licensee is updating this report to include the following information: "This report is being made to communicate the repair and return to service of the Safety Parameter Display System (SPDS) under 10CFR50.72(b)(3)(xiii). All systems have been verified to be operating properly. This system was reported Out of Service on NRC event # 38722 on 02-25-2002." The licensee informed the NRC Resident Inspector. Notified R2DO(Henson). | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-02-25
38721 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-02-23 16:25 | 2002-02-23 16:40 | 2002-02-23 | OFFSITE NOTIFICATION TO STATE POLICE "At 10:45, [the Control Room] received notification from Shift Security Supervisor that at 09:45 a security officer on duty in the central alarm station was escorted offsite and remanded to State Police for questioning following an apparent incident of horseplay with a duty weapon. The security officer surrendered his weapons to company security personnel and was immediately relieved of duty. The Shift Security Supervisor notified the USNRC Region I security inspector at approximately 11:00. The security force remained fully staffed throughout this event and remains fully staffed." The licensee determined that the notification to the State Police was reportable as an offsite notification per 10CFR50.72(b)(2)(xi) at 1625EST. The NRC Resident Inspector was informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-23
38720 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-02-22 16:30 | 2002-02-23 10:58 | 2002-03-06 | ACTIVATION OF THE WATER INVENTORY CONTROL SYSTEM At 1630 CST, on 2/22/02 the Plant Shift Superintendent (PSS) was notified of an activation of the Water Inventory Control System (WICS) on #1 autoclave in the C-360 building. Approximately 50 minutes into the heat cycle, the Hi Primary Condensate alarm was received, and steam supply to the autoclave was automatically isolated. Operators investigated the alarm. The autoclave was removed from service, and the WICS was declared inoperable. Further investigation will be performed by the System Engineer and Instrument Maintenance to determine the exact cause of the alarm. The purpose of the WICS is to limit the amount of water in the autoclave and is a safety system required by TSR 2.1.4.3. The PSS determined that this event is a 24 Hour Event Report due to a valid automatic activation of a Q safety system. The NRC Senior Resident Inspector has been notified of this event. * * * RETRACTED AT 1519 EST 03/06/2002 BY TOM WHITE TO GERRY WAIG * * * "Based on evidence found during post-event investigation, this actuation was initiated by a spurious signal (not a condition that this system is designed to protect against). This investigation revealed an equipment problem that generated a spurious electrical signal causing a false (invalid) actuation of the Water Inventory Control System (WICS). The secondary WICS cable was discovered to be resting in hydraulic oil and to have a small insulation injury exposing the wire. The conduit, which houses the cable, was inadvertently filled with hydraulic oil from a spill that occurred on Jan 22, 2002. This cable was repaired and system retested satisfactorily with no anomalies. The NRC Senior Resident Inspector has been notified of the retraction." Notified R3DO (John Madera) and NMSS (John Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-02-23
38719 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2002-02-22 15:00 | 2002-02-22 17:34 | 2002-02-22 | LOSS OF ASSESSMENT CAPABILITY DUE TO FAILURE OF THE ERDADS SYSTEM "A failure of the ERDADS [Emergency Response Data Acquisition and Display System] computer due to errors in the primary and backup systems. This resulted in the loss of all ERDADS data. The failure also resulted in the loss of offsite communications capability (ERDADS link)." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-02-22
38718 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-02-22 14:48 | 2002-02-22 17:18 | 2002-02-22 | UNIT 2 COMMENCED A TS REQUIRED SHUTDOWN AFTER DECLARING A SI PUMP INOPERABLE "On February 20, 2002, at approximately 0100 CST. OI-163, 'SI, RHR, and CS Pump Runs,' was being performed on Safety Injection (SI) pump 2P-15B. This procedure is used to bump the pump to ensure bearing lubrication as a preventive maintenance activity. When the pump was started, motor current increased as normal, but then decayed to less than 10 amps. Additionally, the pump appeared to develop no discharge pressure. In the field, the auxiliary operator noted a loud bang near the end of the coastdown and further noted excessive seal leakage. At approximately 0105 CST, SI pump 2P-15B was declared inoperable, LCO 3.5.2 was declared not met, and TS Action Condition A.1 was entered. Tech Spec LCO 3.5.2. ECCS-Operating, requires two ECCS trains to be operable in Modes 1, 2, and 3. LCO 3.5.2, Condition A, requires an inoperable ECCS train to be restored to an operable status within 72 hours. "Subsequent inspection of the pump following disassembly of the casing revealed damage to the rotating element, the coupling and shaft keys between the pump and the motor, the pump internal wear rings, and other components. At this time, we believe the pump damage was due to gas binding in the pump as a result of back leakage through two check valves. This allowed nitrogen saturated water from the 'A' SI accumulator to migrate to the 2P-15B pump. Repair of the pump has proceeded with the expectation that the pump would be repaired, tested and returned to service prior to the expiration of the 72 hours allowed in the action statement. However, as of approximately 1400 CST, we determined that we were unlikely to complete the remaining repairs and the required pump testing before the expiration of the action statement. Accordingly, at that time activities were initiated to commence a shutdown of PBNP Unit 2 and at approximately 1448 CST the shutdown of the unit was initiated." The licensee is decreasing power at 30%/hr and anticipates entry into Mode 3 at approximately 1930CST. The licensee informed the NRC Resident Inspector. | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-02-22
38717 | 0 | DANBURY HOSPITAL |  |  |  |  | 2002-02-22 14:00 | 2002-02-22 16:11 | 2002-02-22 | MEDICAL MISADMINISTRATION INVOLVING UNDERDOSE TO CANCER PATIENT A female patient undergoing brachytherapy treatment for cancer at the Danbury Hospital in Norwalk, CT, was prescribed 4600 Rad using a Cs-137 source. One of the five seeds (21.23 mg Radium equivalent) was found in a trash can. This resulted in an estimated delivered dose of 3458 Rad which is 24.8% less than prescribed. All hospital staff entering the area where the trash can was located had personal dosimetry such that no unmonitored exposures occurred. The licensee is conducting a review to determine appropriate corrective actions. The prescribing physician has been informed by the hospital. The licensee notified RI Office(Bhalla). Call the Headquarters Operations Officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.33 |  |  |  | 0 | 2002-02-22
38716 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2002-02-21 | 2002-02-22 13:58 | 2002-02-22 | AGREEMENT STATE REPORT INVOLVING POTENTIAL SALE OF CONTAMINATED TOOLS TO THE GENERAL PUBLIC The Utah Department of Environmental Quality issued an Information Notice on February 21, 2002, (text below) concerning the potential of radiologically contaminated tools in Tooele County. "A recent investigation involving Envirocare of Utah, a commercial low-level radioactive waste site in western Tooele County, has revealed that a former employee of Envirocare's contractor, Broken Arrow Inc., removed contaminated tools that were to be disposed of as waste from the Envirocare facility and eventually sold the tools to Oquirrh Trading Company, a pawn shop located in Tooele, Utah. Records of the Trading Company have revealed the potential for a number of tools to have been sold to the public. The period of time of concern is from January to December 2001. The tools involved may include large ratchet and socket sets, large crescent wrenches and other hand tools. The tools may or may not be marked with U.S., U.S. CCC, US EC and may be painted red. Some of these contaminated tools were recently recovered by inspectors of the Division of Radiation Control at the Trading Company. Citizens who may have purchased tools at the Trading Company during the period January 2001 - December 2001 may have their tools assessed at the Tooele County Health Department, 151 North Main, Tooele beginning Wednesday, February 27, 2002, from 10:00 am. - 5:00 p.m., Thursday, February 28, 2002, and Monday, March 4, 2002, from 1:00 p.m. - 7:00 p.m.. Tools suspected to be contaminated should be handled as little as possible and wrapped in a plastic bag to be brought to the Health Department offices for assessment. Persons handling suspected tools should wash their hands afterwards. If tools are determined to be contaminated, local and state environmental health officials will arrange for their proper disposal. "'While we do not believe these contaminated tools present any significant health threat to members of the public, it is prudent to make sure that these tools are rounded up and properly disposed,' said Bill Sinclair, Director of the Division of Radiation Control. 'We are happy to provide facilities and cooperate with the Department of Environmental Quality in assuring that our Tooele citizens can have the opportunity to assess if there is a problem with tools that may have been purchased at the Trading Company,' stated Myron Batman of the Tooele County Health Department. "Division of Radiation Control inspectors have visited all pawn shops in Tooele County and are satisfied that this problem is confined to the one business. The investigation is continuing and if the problem is more widespread, additional information will be issued as necessary." UT Event Report ID No.: UT-02-0001. Call the Headquarters Operations Officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2002-02-22
38715 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-02-21 08:15 | 2002-02-21 13:18 | 2002-02-21 | 4-HOUR NRC BULLETIN 91-01 REPORT INVOLVING DISCOVERY OF ADDITIONAL MATERIAL DURING WALKDOWN "At 0815, on 02-21-02, the Plant Shift Superintendent (PSS) was notified that a fissile material operation was identified without an approved NCS evaluation. As a result of the event reported in NRC Event Report PAD-2001-045, event worksheet number 38428, walk downs are being performed to determine if other fissile material operations exist that are not covered by NCSAs. The C-310 East and West MgF2 traps between cells 7 and 9 on the cell floor have been identified as a fissile material operation without an approved NCS evaluation. At 1200 CST the PSS was notified by the Non-Destructive Analysis Group that the West trap contains a Planned Expeditious Handling (PEH) mass of material. "SAFETY SIGNIFICANCE OF EVENTS: The MgF2 traps are separated from the purge cascade by air gaps. The traps have not been previously identified as a fissile material operation. This operation has not been evaluated for nuclear criticality safety. Therefore, double contingency was not maintained. The traps are located more than two feet inside the cell housing and fissile material is not stored inside the cell housing. Therefore, it is not feasible to have spacing violations. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): The traps are of favorable geometry for the plant maximum assay at the time the traps were cut from the cascade. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Since this equipment does not have an NCSA for it, there is no controlled parameter. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): West Trap - <446 lbs U with an enrichment of 2.0% U-235. East Trap - <250 lbs U with an enrichment of 2.0% U-235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The MgF2 traps are separated from the purge cascade by air gaps. The traps have not been previously identified as a fissile material operation. This operation has not been evaluated for nuclear criticality safety. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The area is being controlled per CP2-EG-NS1031. No fissile or potentially fissile material will be moved into or within the area without NCS and PSS approval." The NRC Resident has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-02-21
38714 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-02-20 12:40 | 2002-02-21 00:20 | 2002-02-21 | 24 HOUR AGREEMENT STATE REPORT - STOLEN NUCLEAR DENSITY GAUGE "Area office received notification that a CPN [Campbell Pacific Nuclear] moisture density gauge, MC3-S/N, M38088381 was stolen from a storage container between the evening of 2/19/02 to the morning of 2/20/02 from a job site at Pine and Butterfield Ranch in Chino Hills, CA. "Local sheriff contacted and report filed. Licensee to run an add in local paper describing device and offering reward for return of gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2002-02-21
38713 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-02-20 15:00 | 2002-02-20 16:34 | 2002-02-21 | SAFE SHUTDOWN CAPABILITY IMPACTED BY NON-CONSERVATIVE SG NR SETPOINT "Based on the review of [Operating Experience (OE)] 13294 from Diablo Canyon regarding unexpected response of Steam Generator [(SG)] Narrow Range level trip not responding as expected, an assessment was performed of the narrow range (NR) Steam Generator level channels at Sequoyah 1 and 2. This assessment determined that the current 10.7% lo-lo level trip setpoint did not account for the uncertainties associated with the differential pressure (dP) created by the steam flow past the mid-deck plate in the moisture separator section of the steam generator. This dP phenomena will cause the SG NR level channels to read higher than actual water level at high steam flows. Thus, the lo-lo level trip setpoint is non-conservative. "In the unlikely event of a Loss of Normal Feedwater or a Loss of Offsite Power, the potential exists that a required reactor trip on lo-lo steam generator level may be delayed or may not be received at all. In this scenario, other trip functions such as overtemperature delta-T would be expected to actuate in response to the initiating event. However, these would arrive in a different sequence, and the net effect on the UFSAR Chapter 15 accident analysis results is unknown. Thus, a condition exists in that a safety function could have been prevented. "As a conservative measure, upon identification of this condition by Westinghouse via NSAL 02-3, the environmental allowance monitor (EAM) was actuated on U-1 and U-2 on Friday, February 15, 2002. This feature changes the S/G Lo-Lo Level Rx Trip setpoint from 10.7% to 15%. Since the known S/G channel uncertainty is 8.3% with a narrow range span uncertainty of 5.3%, it was determined that operating with the EAMs continuously actuated will allow continued operation. After further evaluation of this condition, it has been determined that 10 CFR 50.72(b)(3)(v)(A) applies as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition. "EAMs actuated on U-1 at time of discovery (vent in progress). EAMs actuated at 1814 on 2/20/02." The licensee informed the NRC Resident Inspector. * * * UPDATED AT 0800 EST BY MICHAEL HOWARD TO FANGIE JONES * * * Correction to statement above ".. EAMs actuated at 1814 on 2/20/02," should have said EAMs actuated at 1814 on 2/15/02 on U-2. The licensee informed the NRC Resident Inspector. The R2DO (Leonard Wert) has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2002-02-20
38712 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-02-20 08:00 | 2002-02-20 13:25 | 2002-02-20 | FITNESS FOR DUTY REPORT A non-licensed Supervisory employee was determined to have failed to comply with FFD procedures during random test. The employee's access to the plant has been terminated. Contact the HOO for additional details. The Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2002-02-20
38711 | 0 | MONTGOMERY HOSPITAL |  |  |  |  | 2002-02-20 10:00 | 2002-02-20 13:17 | 2002-02-20 | SHIPMENT WITH REMOVABLE RADIOACTIVE SURFACE CONTAMINATION EXCEEDING THE LIMITS A shipment of 170 millicuriesTc-99 diagnostic vials was shipped to Montgomery Hospital, Morristown PA from Mallinckrodt Pharmacy, Philadelphia, PA. An incoming survey on the outside of the shipping package indicated loose smearable levels of 938,000 to 1,000,000 dpm/smear of beta-gamma contamination. Surveys of the shipping vehicle and driver indicated no removable contamination. No personnel at the Hospital were contaminated and the shipping package is stored in the hospital hot cell. The material was shipped non-exclusive use. Licensee contacted Michelle Beardsley at R1 and the shipper. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2002-02-20
38710 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2002-02-19 15:30 | 2002-02-20 09:26 | 2002-02-20 | FITNESS FOR DUTY REPORT A contract supervisor tested positive on pre-access screening drug test. Access was never granted to site. The licensee notified the NRC Resident Inspector and will notify the State of Connecticut. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0 | 2002-02-20
38709 | 0 | PRINCETON UNIVERSITY |  |  |  |  | 2002-01-23 | 2002-02-19 11:35 | 2002-02-19 | MISSING RAT CARCASSES CONTAMINATED WITH TRITIUM On 1/23/02 the Radiation Safety Officer was informed that 15 rat carcasses contaminated with 14 mCi of tritium were missing from the freezer. This was discovered on 1/21/02 when a scheduled pickup for disposal was made and the 2 bags of rat carcasses were not located. A thorough search of the laboratories and freezers was made. It is believed that the 2 bags were mistakenly picked up on 11/7/01 when a scheduled pickup for disposal of non-contaminated rat carcasses was made. The 2 bags were last seen in October when the bags were placed in the freezer. New procedures have been put in place to prevent this event from being repeated. A written report will be submitted within 30 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-02-19
38708 | -1 | UNIVERSITY OF WISCONSIN AT MADISON |  |  |  |  | 2002-02-15 | 2002-02-19 08:12 | 2002-02-19 | MEDICAL MISADMINISTRATION DUE TO AN EQUIPMENT MALFUNCTION A BetaCath Systems device containing strontium-90 produced by Novoste was being used to treat a patient. On sending the active sources to the target area, a fluid leak occurred which slowed the movement of the seeds into the target vessel/position (Left Anterior Descending Artery). Not able to see the active seeds on the fluoroscopy monitors, a decision to have the active seeds returned to the holding device was made. A total time of 17 seconds elapsed from the time of delivery until the active seeds were returned to the holding device. On close inspection of the treatment catheter/device, one of the sealing O-rings was found to be ruptured. This was the ultimate cause of the fluid leak and consequently the slow movement of the active seeds to the target position. With a dose rate of 0.095 Gy/s at 2 mm, the artery wall along the approximately 1 m track over which the source traveled out and back for its 17 sec would be calculated as: Speed equals 2 * (100 cm)/17 s = 11.8 cm/s Time wall was exposed to the 4 cm source = 4 cm / 11.8 cm/s = 0.34 s, but this time is doubled since it is exposed coming and going, to 0.68 s. Dose to the wall = 0.68 s * 0.095 Gy/s = 0.0646 Gy = 6.5 rads. The normal dose to the wall (assuming an 8 s round trip) would be 3.0 rads. A new catheter was tested with the non-active device and the treatment was continued. The treatment was timed, checked for the return of the active sources and surveyed the patient/room post treatment. No problems were encountered with the new treatment catheter. * * * UPDATE 1745EST ON 2/19/02 FROM ABDUL BEN-ZIKRI TO S. SANDIN VIA E-MAIL * * * The following is a portion of an e-mail received at hoo1@nrc.gov: "I am retracting my event report (Event # 38708). I took a conservative action and reported this event based on preliminary written information. "Our Hospital staff followed all standard operating & emergency procedures, and retracted the source when they realized that they did not arrive to the area of clinical interest as indicated in the report below. Based on the investigation analysis, we conclude that there was no misadministration to report." Notified R3DO(Jorgensen) and NMSS(Brach). . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 35.33 |  |  |  | 0 | 2002-02-19
38707 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-02-18 18:15 | 2002-02-19 01:27 | 2002-04-12 | BOTH EMERGENCY DIESEL GENERATORS INADVERTENTLY MADE INOPERABLE "On 02/18/02, at 1815 hours, the licensee discovered that the Beaver Valley Unit 2 #1 Emergency Diesel Generator had been rendered inoperable inadvertently, by the posting of a clearance at 1408 hours on 2/14/02. The #2 Emergency Diesel Generator had previously been removed from service for maintenance activities. Upon discovery that the #1 Emergency Diesel Generator was inoperable, action was immediately initiated to restore the #1 Emergency Diesel Generator to Operable status. These actions were completed and the #1 Emergency Diesel Generator was restored to Operable status at 1830 hrs on 02/18/02. "The #1 Diesel Generator was rendered inoperable at 1406 hrs on 02/14/02. During the period of inoperability, the licensee conducted core alterations including core reload during the ongoing ninth refueling outage. During the affected period, there were no challenges to the offsite power sources, and core cooling was maintained. Investigation into this event is ongoing. "This event is being reported under 10CFR50.72(v)(A) and 10CFR50.72(v)(B) as a loss of Safe Shutdown Capability, and RHR Capability, respectively. There were no radiological releases associated with this event," The licensee intends to notify the NRC Resident Inspector. * * * RETRACTION 1314 4/12/2002 FROM TOM COTTER TAKEN BY BOB STRANSKY * * * "Subsequent review and analysis of the event identified that the Unit 2 #1 Emergency Diesel Generator (EDG) retained its capability to fulfil its safety function. During the time that the potential transformer fuses were inadvertently removed from the Unit 2 #1 EDG, the EDG would still have started and accelerated to proper speed and output voltage if a station loss of offsite power had occurred. However, the output breaker would not have automatically closed and the EDG would not have automatically supplied emergency AC power to the Unit 2 A train emergency bus. Control room indications, powered by station DC sources, would have confirmed that the EDG was running at rated speed. Following station procedures, operations personnel would have attempted to locally close the A train EDG output breaker. The EDG output breaker would have closed, the EDG sequencer would have then have been automatically energized, and the required emergency loads would have been automatically sequenced on to the A train emergency bus. It is conservatively estimated that this action would have been completed within approximately 20-30 minutes. Unit 2 Residual Heat Removal (RHR) pumps are not automatically loaded onto an emergency bus for any postulated station loss of offsite power and would have to be manually loaded onto an emergency bus after a EDG is started. The estimated time frame to close the EDG output breaker and to load the RHR pump onto the EDG in this condition for a postulated loss of offsite power showed no significant adverse Unit results. Therefore, the EDG retained its capability to fulfill its safety function. "This event will be reported as a Licensee Event Report pursuant to 10CFR50.73(a)(2)(i)(B)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2002-02-19
38706 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2002-02-18 20:20 | 2002-02-18 22:42 | 2002-02-18 | UNIT COMMENCED TECH SPEC REQUIRED SHUTDOWN AFTER DECLARING TWO MSIVs INOPERABLE "Plant entered Tech spec 3.0.3 at 2020 on 2/18/2002. Two Main Steam Isolation Valves (MSIVs) were determined to have operating air pressures outside the required 70 - 80 psig operating range, which rendered the valves inoperable per Tech Spec 3.7.1.5, Main steam line isolation valves. At 2055 commenced power reduction per Tech Spec 3.0.3. At 2102 one of the MSIV valve operating pressures was restored to operable. Terminated power reduction at 99.5% and exited Tech Spec 3.0.3. Tech Spec 3.7.1.5 was still applicable. At 2129 the remaining MSIV operating pressure was restored to the normal tech spec required pressure, exited Tech Spec 3.7.1 .5. "(An operator making a plant tour found XVM02801C-MS at 82 psig and XVM02801A-MS at 95 psig.)" Partial MSIV stroke time testing was performed earlier today with MSIV operating pressure verified in the 70-80 psig range. The licensee informed the NRC Resident Inspector. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-02-18
38705 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2002-02-18 11:13 | 2002-02-18 13:26 | 2002-02-18 | OFFSITE NOTIFICATION TO OTHER FEDERAL AGENCY A member of the licensee's staff received an e-mail from a former contractor requesting a meeting with senior Energy representatives.. The licensee notified the local FBI office. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-18
38704 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-02-15 22:00 | 2002-02-16 11:11 | 2002-03-04 | SAFETY EQUIPMENT FAILURE - PROCESS GAS LEAK DETECTION FAILURE "At 2200 CST, on 02-15-02 the Plant Shift Superintendent (PSS) was notified of a failure of the Process Gas Leak Detector (PGLD) system in the C-333 building. During above atmospheric operation a PGLD alarm was received in the Area Control Room [ACR] on C-333 Unit 4 Cell 4. An operator responded to the local cell panel to investigate according to the alarm response procedure. Upon arriving at the cell panel the operator discovered that the Ready light was not Illuminated on the PGLD panel. At this time the operator attempted to test fire the PGLD system, however the system would not respond. The Front Line Mgr. and the PSS were immediately notified of the system failure. At this time, required TSR 2.4.4.1 LCO continuous smoke watches were put in place in the affected areas until repair of the system was completed. Following replacement of the power supply by Instrument Maintenance and testing by Operations, ten Unit 4 Cell 4 PGLD system was declared operable by the PSS at 2340 CST. At this time the TSR required smoke watches were discontinued. "The PGLD system is designed to detect the leakage of process gas from the process system and is required to be operable while operating in Cascade Mode 2 (Above Atmospheric Pressure). Due to the failure of this TSR required system; the PSS has determined that this is reportable as a 24 hour Event Report. "The NRC Resident inspector has been notified of this event." * * * RETRACTED AT 0346 EST ON 02/22/02 BY ERIC WALKER TO FANGIE JONES * * * "This event has been retracted. Even though the power loss causes the system to be incapable of annunciating additional alarms from this system in the ACR, the same is true when a PGLD head actuates in response to smoke. The system Is designed to alert operators of a release or loss of system power. Operator response and the initiation of a smoke watch provide the safety function after the initial alarm is annunciated. The NRC resident inspector has been notified of this update." The R3DO (Bruce Jorgensen) and NMSS EO (E. William Brach) have been notified. * * * UPDATED AT 1750 EST ON 3/4/02 BY TOM WHITE TO FANGIE JONES * * * "Following discussions with NRC Region III and the PGDP NRC Senior Resident Inspector. USEC has determined that a rescission of the retraction made on 2/21/02 will be necessary in response to NRC concerns related to this matter. Therefore, USEC hereby rescinds the subject retraction and will be submitting the written report required by 10CFR76.120(d)(2). The NRC Senior Resident Inspector has been notified of the rescission." Notified the R3DO (John Madera) and NMSS EO (C. W. Reamer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2002-02-16
38703 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2002-02-15 20:30 | 2002-02-15 21:16 | 2002-02-15 | OFFSITE NOTIFICATION REGARDING A SCHEDULED UNIT SHUTDOWN FOR A PLANNED REFUELING OUTAGE The licensee notified the State Department of Environmental Protection and local county that the unit is in the process of reducing power to enter a planned refueling outage. The licensee also notified the NRC resident inspector. | 0 | 60 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-15
38702 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-02-15 18:15 | 2002-02-15 20:15 | 2002-02-15 | DISCOVERY OF A NON-CONSERVATIVE LO-LO LEVEL TRIP SETPOINT DUE TO A DIFFERENTIAL PRESSURE PHENOMENA THAT CAUSES STEAM GENERATOR NARROW RANGE LEVEL CHANNELS TO READ HIGHER THAN ACTUAL WATER LEVEL AT HIGH STEAM FLOWS "Based on the review of [Operating Experience (OE)] 13294 from Diablo Canyon regarding unexpected response of Steam Generator [(SG)] Narrow Range level trip not responding as expected, an assessment was performed of the narrow range (NR) Steam Generator level channels at Salem 1 and 2. This assessment determined that the current 9% lo-lo level trip setpoint did not account for the uncertainties associated with the differential pressure (dP) created by the steam flow past the mid-deck plate in the moisture separator section of the steam generator. This dP phenomena will cause the SG NR level channels to read higher than actual water level at high steam flows. Thus the lo-lo level trip setpoint is non-conservative." "In the unlikely event of a Loss of Main Feedwater to the Station Auxiliaries, or a Main Feedwater Rupture, the potential exists that a required reactor trip on lo-lo steam generator level may be delayed or may not be received at all. In this scenario, other trip functions such as overtemperature delta-T would be expected to actuate in response to the initiating event. However, these would arrive in a different sequence, and the net effect on the UFSAR Chapter 15 accident analysis results is unknown. Thus, a condition exists in that a safety function could have been prevented." The licensee stated that operators were in the process of decreasing power on Unit 1 to below 38% based on engineering information. The licensee plans to maintain Unit 2 operations at 78% power. The licensee plans to notify the NRC resident inspector and the Lower Alloways Creek Township. (Refer to event #38697 for a similar issue reported by Diablo Canyon.) | 77 | 78 | 0 | 77 | 78 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2002-02-15
38701 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-02-14 | 2002-02-15 15:10 | 2002-02-15 | AGREEMENT STATE NOTIFICATION OF LOST NEUTRON GENERATOR BETWEEN HOUMA, LA AND PEARLAND, TEXAS The following is a portion of the facsimile received from the State of Louisiana: "Agreement State Agency: Louisiana Department of Environmental Quality" "Event Report ID No: LA020002" "License No.: LA-2187-LO1" "Licensee: Baker Atlas" "Event date and Time: January, 3-3 1, 2002" "Event Location: Between Houma, LA and Pearland, TX" "Event type: Lost Neutron Generator" "Notifications: Licensee notified State Police, Highway Maintenance, LA Department of Environmental Quality, and the State of Texas. Has not notified media yet." "Event description: Baker Atlas requested two Neutron Generator tools with 0.878 Ci of H-3 in sponge form in each tool from Pearland, TX. The tools are shipped in four sections for each tool for a total of 8 sections. The night watchmen in Houma, LA recorded on January 3, 2002, that 8 sections were delivered and then placed in storage. On January 31, 2002, Pearland wanted the tools back. It was discovered that there were only 7 sections instead of eight. The section that was missing contained the H-3. The RSO was notified of the lost source on February 14, 2002. The RSO notified the LA Department of Environmental Quality on February 14, 2002. The night watchmen was interviewed and said he thought there were 8 sections delivered." "Transport vehicle description: Flatbed truck (Hot Shot Transport Company)" "Media attention: Media not notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-02-15
38700 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-02-14 15:35 | 2002-02-15 14:25 | 2002-02-15 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR DENSITY GAUGE February 14, 2002 / 3:35 p.m. Hallsville, Texas (between Longview and Marshall, Texas along U.S. Highway 80, north of Interstate Highway 20) - Hallsville High School near small concession stand. Damaged nuclear density gauge - Troxler Model 3430, Serial No 29993; Source Cs-137 Serial No. 7504631, activity 8 millicuries; Source Am-24 :Be Serial No. 47-26971, activity 20 millicuries. Last leak tested December 5, 2001. Texas Bureau of Radiation Control was notified of the incident at approximately 4 p.m. February 14, 2002. Troxler Electronic Labs has been contacted to leak test the damaged gauge and to arrange repair/disposal. Event description: The gauge operator was preparing to conduct density tests when a dump truck passed. The operator prepared to drive the pin to provide a hole for the source rod. As he was performing this task he noticed that the truck was now backing toward him. He jumped out of harms way and immediately began banging on the side of the truck with his hammer near the tailgate to get the driver's attention. However, the driver was looking in his other mirror and talking on either a cell phone or radio. The truck's rear dual wheels backed over the gauge. The driver then sensed he had hit something and immediately stopped the vehicle. The gauge's source rod was in the up and locked position. After the impact the rod was bent but still intact. The gauge case was severely damage but the integral source retained it's structural integrity. The area was roped off. A radiation survey was performed, in place, on the damaged gauge. A NDS Survey Meter Model ND 2000, Serial No 25207 obtained readings of 2.5 to 3.5 mRem/hour near at the surface of the damaged device. After assessment, the gauge was removed from the site and placed in its transport container in the company transport vehicle. The soil under the damaged gauge was removed to check for debris (none found) and surveyed with no measurable radiation detected. The gauge was transported to the Longview headquarters site and locked in a storage closet pending a leak test of the device by Troxler. Radiation levels at the closet were consistent with those taken at the incident site. Arrangements for transportation and repair/disposal of the damaged gauge are pending with the Troxler Office in Arlington, Texas. Transport vehicle description: Not applicable. Gauge was in use. Gauge was damaged by a loaded dump truck belonging to the K.K. Mobbs Construction Company, Kilgore, Texas. The vehicle was surveyed and released. Media attention: None known | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-02-15
38699 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-02-14 16:45 | 2002-02-15 13:53 | 2002-02-15 | AGREEMENT STATE REPORT - DAMAGED FIXED GAUGE SUBJECT: Damage to Fixed Gauge Containing Radioactive Material. On February 14,2002 at 4:45 PM CDT, a representative of McWane Cast Iron Pipe Company notified the Agency that on February 13,2002, the burner on a cupola caused a partial melting of the shielding of a mounted Ohmart model A2104 gauge containing 4,500 millicuries of Cesium-137 to melt. McWane Cast Iron Pipe Company possesses and uses radioactive material under Alabama Specific License No. 507. A hole was burned in the side of the source holder and approximately one quart of lead flowed to the floor. A consultant was hired and performed surveys and leak tests of the device. No excessive radiation levels were noted and the leak test results were within acceptable limits. The gauge remains mounted and is isolated. The manufacturer's representative is scheduled to come to the facility on February 15, 2002 to replace the device. The incident did not cause any exposure of radiation above applicable limits. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-02-15
38698 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-02-15 03:53 | 2002-02-15 05:36 | 2002-02-15 | DISCRETIONARY DECLARATION OF UNUSUAL EVENT DUE TO "INCREASED PLANT AWARENESS" During a dewatering evolution of the Spent Resin Storage Tank, some spent resin entered the tank vent header. This caused an elevated reading of 263 mrem on a single area radiation monitor (RM-081). The licensee declared an Unusual Event in accordance with EAL 11.4, "Increased Plant Awareness." Additional personnel are being called in to the site to assist in devising a plan to flush the resin from the affected piping. The licensee estimates that it will take two to three hours to complete this evolution. The NRC resident inspector and state and local government agencies have been informed of this event by the licensee. * * * UPDATE 1045 2/15/02 FROM LUIKENS TAKEN BY STRANSKY * * * The licensee has terminated the UE as of 0945 CST. The licensee has developed a plan to flush the resin from the inappropriate areas and will be commencing the activity shortly. The affected areas have been properly surveyed and posted. The NRC resident inspector has been informed of this update. Notified R4DO (Smith), NRR (Koshy), FEMA (Zapata). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-02-15
38697 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-02-14 16:20 | 2002-02-14 20:30 | 2002-02-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN OF BOTH UNITS BECAUSE STEAM GENERATOR WATER LEVEL INSTRUMENT CHANNELS ARE INOPERABLE DUE TO A NON-CONSERVATIVE WATER LEVEL-LOW LOW SETPOINT The following text is a portion of a facsimile received from the licensee: "During the investigation into the Unit 2 manual reactor trip on February 9, 2002 (Event Number 38687), PG&E discovered a potentially unanalyzed condition. The narrow range (NR) steam generator (SG) water level instrumentation did not respond as expected to initiate an automatic reactor trip and auxiliary feedwater actuation on SG water level-low low." "The SG NR water level-low low setpoint is 7.2 percent. This instrumentation is part of the Reactor Trip System (Technical Specification (TS) Table 3.3.1-1 Function 14.a), and Engineered Safety Feature Actuation System (ESFAS) (TS Table 3.3.2-1 Function 6.d), Auxiliary Feedwater (AFW)." "On February 9, 2002, main feedwater regulating valve (MFRV) FW-2-FCV-540 failed closed, resulting in a rapid decrease in SG 2-4 water level. Indicated NR water level fell to approximately 7.5 percent and leveled out. Operators tripped the reactor within approximately one minute of the MFRV closing. Based on investigations and conversations with Westinghouse today, PG&E believes the actual SG 2-4 NR water level fell below the 7.2 percent setpoint before the reactor was tripped. Westinghouse attributes this water level discrepancy to a previously unaccounted for differential pressure (dP) created by steam flow past the mid-deck plate (MDP) in the moisture separator section of the SG. This dP phenomena will cause the SG NR to read higher than actual at high steam flows (>60% power). Thus, the SG NR water level-low low setpoint is believed to be non-conservative during certain transients." "In response, operators declared all SG NR water level-low low channels inoperable and entered TS Action 3.0.3. At 1700 [PST], both units began reducing power to approximately 60 percent, where Westinghouse indicates this condition will no longer result in a non-conservative setpoint." "In accordance with 10 CFR 50.72(b)(2)(i), PG&E is reporting this as the initiation of a TS required shutdown. It is also being reported under 10 CFR 50.72(b)(3)(v)(A) as condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition." The licensee notified the Salem facility and the NRC resident inspector. The licensee also plans to notify the local Advisory of the County. (Refer to event #38687 for additional information.) | 90 | 89 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) |  |  | 0 | 2002-02-14
38696 | 0 | POWER RESOURCES |  |  |  |  | 2002-02-14 13:30 | 2002-02-14 18:19 | 2002-02-14 | POWER RESOURCES HIGHLAND URANIUM PROJECT (AN IN-SITU URANIUM MINE LOCATED IN A RURAL AREA APPROXIMATELY 30 MILES NORTH OF DOUGLAS, WYOMING) REPORTED A MINOR RELEASE OF RADIOACTIVE MATERIAL. At 1330 MST, while personnel were moving a trailer-mounted 1,000-gallon tank full of water from a well, they forgot to close a valve, and approximately 20 to 25 gallons of water containing uranium drained onto a county road. The spill was cleaned up by approximately 1530 MST. Original contamination levels were between 1,000 and 5,000 cpm, however, alpha scans of the area currently meet the NRC unrestricted release standard of 1,000 cpm. A sample of the water from the trailer is being analyzed to determine the actual activity levels. There were no personnel contaminations or injuries associated with this event. The licensee notified the Department of Transportation and plans to notify the local sheriff's office. The NRC Region 4 office plans to notify the State of Wyoming. The NRC mining experts assessed this event and stated that no adverse impact is anticipated and no response is required. (Call the NRC operations officer for licensee contact telephone numbers.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MINING EVENT | [9 empty] | NON EMERGENCY | 4 | WY | MAT | [5 empty] | 0 | 2002-02-14
38695 | 0 | ENG. RESEARCH & DEVELOPMENT CENTER |  |  |  |  | 2002-02-14 | 2002-02-14 13:52 | 2002-02-14 | POTENTIAL OVEREXPOSURE AT ENGINEER RESEARCH & DEVELOPMENT CENTER IN HANOVER, NEW HAMPSHIRE On 02/04/02, the licensee received a telephone notification that an individual's badge had an exposure of 16 Rem during a 3-month period. After further investigation on 02/05/02, the licensee determined that the individual had lost the badge while packing a moisture density gauge for storage. Approximately 4 weeks later, the badge was discovered when the device was being prepared to be sent for recalibration. On 02/08/02, the licensee received a telex identifying what the exposures were in writing. The licensee notified the NRC Region 1 office (Betsy Ullrich) on 02/14/02. The licensee currently believes that the 16-Rem exposure was an exposure to the badge and not to the individual. NOTE: The licensee stated that Engineer Research & Development Center is a research portion of the Core of Engineers and that it was previously know as the U.S. Army Cold Regions Research & Engineering Laboratory. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | NH | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2002-02-14
38694 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2002-02-14 01:03 | 2002-02-14 04:18 | 2002-02-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "This ENS notification is made to report initiation of a plant shutdown required by the Columbia Generating Station Technical Specifications pursuant to 10 CFR 50.72(b)(2)(i). This plant shutdown is initiated due to the expected inability to restore the Division II Emergency Diesel Generator (DG) to Operable status prior to exceeding the expiration of the Completion Time of Tech Spec LCO 3.8 1 Required Action B.4. The expected inability to restore the DG to operable status is due to a mechanical problem in the DG output breaker. The breaker is capable of closing and connecting the DG to its safety bus however, Mechanically Operated Contacts that are actuated by the breaker have failed to actuate, Although the Completion time of Technical Specification LCO 3 8.1 Required Acton B.4 expires at 0315, February 14, 2002, plant shutdown will commence prior to that time in order to fully evaluate the breaker anomaly." The NRC resident inspector has been informed of this notification by the licensee. | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-02-14
38693 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-02-13 21:08 | 2002-02-13 22:17 | 2002-02-13 | LOSS OF EMERGENCY SIREN EQUIPMENT GREATER THAN ONE HOUR "We have a simultaneous inoperability of the Massachusetts Emergency Management Agency (MEMA) Framingham and the MEMA Area 1 siren activation equipment for greater than one hour. This condition was discovered during the performance of a routine silent activation test that is conducted approximately every two weeks. We verified the state has implemented their contingency plan to be able to activate the sirens locally if needed. Twenty-seven sirens are affected by the problem. The sirens for the state of New Hampshire were verified to be working correctly." The NRC Resident Inspector was notified of this event by the license. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-02-13
38692 | 0 | C.F.MARTIN & CO. INC. |  |  |  |  | 2002-02-13 16:28 | 2002-02-13 16:28 | 2002-02-13 | MISSING STATIC ELIMINATOR GUN Mr. Whalen of C.F.Martin & Co. Inc. reported that they are missing a static eliminator gun. The static eliminator gun model number is P2021 which originally contained 10 millicuries of Po-210. The static eliminator gun was made by NRD LLC, located in Grand Island N.Y., on August 16, 2000. The licensee thinks that they have misplaced the static eliminator gun. Serial number of the gun is A2AC914. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-02-13
38691 | 0 | THOMAS G. FARIA CO. |  |  |  |  | 2002-02-13 14:56 | 2002-02-13 14:56 | 2002-02-13 | STATIC ELIMINATOR MISSING SINCE 1992 Thomas G. Faria Co., located in Uncasville, CT, received an invoice from the state of CT requesting a $100 fee for a static eliminator. Nobody in the company knew anything about the static eliminator. Research by company officials found that they did have a static eliminator at one time. The static eliminator was made NRD LLC located in Grand Island, NY. NRD records indicated that they had sent a static eliminator to Thomas G. Faria Co. on 12/13/91. The static eliminator contained 20 millicuries of Po-210 and the Model # of the static eliminator was P-2031. Serial number of the static eliminator was 46218. Everybody associated with the static eliminator retired several years ago. Thomas G. Faria Co. no longer uses a static eliminator. The halflife of Po-210 is 138.4 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-02-13
38690 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2002-02-13 04:34 | 2002-02-13 13:11 | 2002-02-13 | VALID REACTOR PROTECTION SYSTEM ACTUATION. At 0434, 2/13/02, Callaway Plant experienced a valid Reactor Protection System (RPS) actuation. The plant was in Mode 4 with the primary system at 330 degrees F and 395 PSIG. The Reactor Trip breakers were closed to facilitate Main Turbine shell and chest warming. Secondary plant manipulations, which included securing Steam Generator Blowdown and conducting Auxiliary Feedwater flow testing, caused a reduction in condensate flow through feedwater preheaters. This reduction in flow through the preheaters caused steam pressure inside the Main Turbine to increase above a permissive (P13) setpoint normally activated at 10 % reactor power. This P13 permissive in turn enabled a Reactor Trip permissive (P7) for a low Pressurizer pressure reactor trip which has a setpoint of 1885 PSIG. Since primary pressure was below the 1885 PSIG setpoint, a Reactor Protection System signal was generated and caused the Reactor Trip breakers to open. Although pressure measured within the Main Turbine increased, primary system temperature and pressure never increased above the limits for Mode 4. All systems actuated as expected. Main Turbine warming was secured and an Event Review Team was assembled to determine the cause of the event. Operating instructions are being modified to address this situation and prevent future actuations related to these conditions. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-02-13
38689 | 0 | PALISADES | 1 |  |  | [1] CE | 2002-02-12 10:45 | 2002-02-12 22:00 | 2002-02-12 | OFFSITE NOTIFICATION MADE TO THE MICHIGAN POLLUTION EMERGENCY ALERT SYSTEM At 1045 ET the following report was made to the Michigan Pollution Emergency Alert System, Operator number 30. At 0900 ET 02/12/02 an estimated 300 gallons of liquefied sewage (visually free of solids) spill occurred to Lake Michigan beach. The source of the spill was an overflow of the support building sewage system to the plant storm drain system. The source of the spill was immediately isolated. It is believed that the spill did not reach Lake Michigan due to absorption in the sand and the approximate 100 feet distance to the waters edge. A written report will follow to the Michigan Department of Environmental Quality. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-12
38688 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2002-02-11 15:38 | 2002-02-11 18:26 | 2002-02-11 | OFFSITE NOTIFICATION - INJURED SECURITY GUARD At 1538 CT, 02/11/02 Control Room received a phone call from security that a guard had received a laceration and needed medical attention. Site emergency medical technicians were paged to respond and offsite ambulance and rescue personnel were notified to respond. A security sergeant and one site EMT accompanied the injured guard to Blair Memorial Hospital, leaving the site at 1601CT. The injured guard was closing a security gate when high winds caused him to lose control of the gate. The razorwire attached to the gate struck the guard on the back of his head behind his left ear. The cut turned out to be minor (requiring only several stitches) however the razor wire had nicked a small artery causing larger amounts of blood flow that otherwise would have occurred. The NRC Resident Inspector was notified of this event by the licensee. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-11
38687 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-02-09 03:37 | 2002-02-09 10:09 | 2002-02-09 | MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER TO A STEAM GENERATOR "At 0337, on 2/9/2002, Unit 2 reactor was manually tripped due to a failure of feedwater regulating valve FW-2-FCV-540. The valve failed closed isolating feedwater to steam generator 2-4. The reason for the failure is currently unknown, investigation continues. All safety systems responded as required. [All control rods fully inserted]. Auxiliary feedwater pumps 2-1, 2-2, 2-3 started as required in response to low steam generator water levels. "DCPP unit 2 is stable in Mode 3, heat removal is via steam dumping to the normal condenser, auxiliary feedwater continues to supply the steam generators." The unit will remain in Mode 3 until repairs are made. The unit 2 steam generator 4 has had a long term tube leak (about 2 years) on the order of about 3.82 gpd (TS limit 150 gpd) by most recent calculation. Secondary activity is less than detectable and only a count rate on steam jet air ejector is positive indication. Primary activity pretrip was 3.47E-3 µCi/ml. The licensee notified the NRC Resident Inspector and will make a normal press release. (Refer to event #38697 for additional information.) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-02-09
38686 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-02-08 22:52 | 2002-02-09 00:30 | 2002-02-09 | MANUAL REACTOR SCRAM - DEGRADED VACUUM DUE TO ACTIONS FOR HIGH OFFGAS HYDROGEN "Plant Hatch Unit 1 was SCRAMMED at 2252 EST on 02-08-2002. The Reactor was SCRAMMED from approximately 27% RTP and the Main Turbine subsequently tripped. Degraded function of the Main Condenser Offgas Recombiner system had resulted in high Hydrogen in the Offgas. The 'Failure of Recombiner' Abnormal Operating procedure (AOP) had been entered at approximately 2100 and a power reduction begun from 100% RTP at about 2105. Per the AOP, the inservice Steam jet Air Ejector was removed from service at 2220 (due to the Offgas Hydrogen concentration reaching approximately 4%). Hatch Unit 1 was subsequently scrammed due to degrading Condenser Vacuum. The mechanical vacuum pump was placed in service after the SCRAM to maintain Condenser Vacuum as the heat sink. The lowest Reactor Water Level noted during the SCRAM (approximately 7" above Instrument zero) was above any ESF actuation settings, so no ESFs were required or received. No Reactor Pressure increase was noted during the SCRAM. At this time plans are to proceed to Cold Shutdown for repairs to the Offgas Recombiner system and other maintenance. Air purge had been placed inservice to purge the Hydrogen from the Offgas system at around 2230, and remains inservice to reduce Hydrogen concentrations." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-02-09
38685 | 0 | BRIGHAM YOUNG UNIVERSITY |  |  |  |  | 2002-01-01 | 2002-02-08 16:15 | 2002-02-08 | SELF-POWERED TRITIUM EXIT SIGNS DISCOVERED MISSING FOLLOWING FACILITY RENOVATION The auditorium at the Brigham Young University Campus in Laie, HI underwent renovation between 6/2000 and 1/2002. The contractor removed nine (9) self-powered tritium exit signs for storage and reinstallation following completion of the work. After work was completed the signs could not be located. The Safety Officer (SO) at the University believes that the signs may have been installed at another business location. Based on other self-powered exit signs currently in possession, the SO feels the missing signs contained 10 Curie tritium sources each and were manufactured by SRB Technologies, Inc. located in Winston-Salem, NC between 1992 and 1993. A written report will be submitted for the loss of this general licensed material in accordance with NUREG-1556. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-02-08
38684 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2002-02-04 15:00 | 2002-02-08 15:36 | 2002-02-08 | AGREEMENT STATE REPORT INVOLVING POTENTIAL PERSONNEL EXPOSURES On 2/4/02 at 1500EST a female patient undergoing treatment for thyroid cancer received 250 millicuries I-131 at the Holy Cross Hospital located at 1500 Forest Glen Road in Silver Springs, MD 20910. The patient subsequently expired on 2/5/02 at 0630EST. The body was released by the hospital to the Metropolitan Funeral Home located at 5517 Vine Street in Alexandria, VA for cremation. Due to the relatively short period of time between administration of the I-131 dose and the patient's demise radiation levels were measured 67 mR/hr @ 1 meter. The decedent was transferred back to Holy Cross Hospital and is in an area away from the general public awaiting final disposition. Both NRC Region I (Duncan White) and NRC Region II are aware of this event. Contamination surveys were performed at the Funeral Home with negative results. An investigation is ongoing to determine any personnel exposures associated with this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2002-02-08
38683 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2002-01-29 | 2002-02-08 13:43 | 2002-02-08 | AGREEMENT STATE EVENT The licensee reported the loss of a internally contaminated duct. The duct is 13-feet long and 4-inches in diameter and contaminated with U-234, U-235, and U-238, with the highest concentration being U-234. The licensee estimates that 1.5 microcuries of U-234 is in the duct. The duct was sent to a construction debris landfill in Franklin County, Ohio along with other construction debris. Source/Material: Unsealed Material, Other Radionuclide: U-234 Activity (Curies): 0.0000015 Agreement State Item number: OH-02-021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2002-02-08
38682 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-02-06 | 2002-02-07 17:29 | 2002-02-07 | AGREEMENT STATE REPORT INVOLVING POTENTIAL PERSONNEL OVEREXPOSURE This is notification of an event in Washington state as investigated by the WA Department of Health, Division of Radiation Protection. STATUS: new Licensee: TRANSALTA MINING CENTRALIA City and state: CENTRALIA, WA License number: WN-10241-1 Type of license: FIXED GAUGE Date of event: February 6, 2002 Location of Event: Centralia, WA ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) The licensee reported a serious mechanical failure of a Ronan Engineering Company model SA-4 gauging device. This is the same device which previously experienced several failures of the source rod becoming disconnected from the source. This failure is the most serious to date. The operator pulled the source rod, complete with source, entirely out of the shield while conducting a routine end-of-shift securing of the source. The RSO was informed and, while moving what he thought was just the source rod to a separate storage area, decided to check whether the source was still connected. An old CDV instrument had been provided to the licensee following the previous failures. This instrument confirmed that significant radiation exposure was occurring. The RSO acted quickly to isolate the source and notify the state. The state Division of Radiation Protection arrived within several hours and assisted the licensee in assessing the need for additional shielding. Initial readings with minimal shielding in place indicated a surface dose rate that was "off scale" (greater than 5000 mrem/hour) and about 3000 mrem/hour at 6 inches. Bags of lead shot were obtained and the maximum dose rate on the exterior of the storage building went from 50 mrem/hour to 0.25 mrem/hour. State staff are on-site February 7 to conduct interviews, time-motion studies, and additional exposure measurements to assess personnel exposure. What is the notification or reporting criteria involved? WAC 246-221-250 Notification of incidents (equipment malfunction; personnel exposure) Activity and Isotope(s) involved: 1.7 Ci Cesium-137 Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) Two workers exposed. Doses unknown at this time. Lost, Stolen or Damaged? (mfg., model, serial number) Ronan Engineering Company Model SA-4 gauging device, serial number 0973GK, with Amersham Model CDC.711M source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-02-07
38681 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2002-02-07 15:00 | 2002-02-07 17:26 | 2002-02-07 | OFFSITE NOTIFICATION TO THE STATE OF MICHIGAN DUE TO A CHEMICAL SPILL ONSITE "At 1500 on 2/7/02 a spill of Sodium Hypochlorite occurred at the circulating water pump house while unloading the product into the storage tank. The cause of the spill was from a rupture disc located high on the supply truck tank rupturing. The release quantity was estimated at ~20 gallons of 15% concentration of Sodium Hypochlorite. The spill landed on the gravel and dirt located near the Sodium Hypochlorite storage tank. The source of the spill was stopped. There were no personnel injuries as a result of this spill. No Sodium Hypochlorite reached navigable waters. Communication was made with the site environmental group and it was determined that this event is reportable to the State of Michigan. "The Michigan Department of Environmental Quality was notified at 1550 EDT. "There were no puddles on the gravel to clean up with absorbant material. The ground is currently being washed with potable water which is being pumped to the containment dike for the Sodium Hypochlorite storage tank. Ground excavation will occur once ground cleaning is complete. "This report is being made in accordance with 10CFR 50.72(b)(2)(xi) Any event or situation, related to the health arid safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-07
38680 | -1 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2002-02-07 16:00 | 2002-02-07 16:52 | 2002-03-19 | 1-HOUR SECURITY REPORT INVOLVING THE POTENTIAL LOSS OF SAFEGUARDS INFORMATION Discovery of loss of classified document/safeguards information. No compensatory measures available. Licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Center for additional details. ***RETRACTED ON 3/19/02 AT 1110 EST FROM BRIAN ROKES TO RICH LAURA*** The licensee is retracting this event after completing their investigation. The licensee informed the Resident Inspector. Notified the RIDO (R. Conte). Contact the HOO for details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-02-07
38679 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2002-02-07 12:35 | 2002-02-07 14:26 | 2002-02-08 | HPCI DECLARED INOPERABLE FOLLOWING DISCOVERY OF UNKNOWN CONTAMINANT IN OIL "Declared High Pressure Coolant Injection System (HPCI) INOP due to unknown contaminants in the oil system. Plant formulated an action plan to resample the sump, identify the particles, and identify the source of the contaminants. Entered 7 day LCO per Tech Spec 3.5.C.1.a." The licensee informed the NRC Resident Inspector. * * * UPDATE 1620EST ON 2/8/02 FROM ANDY HALLIDAY TO S. SANDIN * * * The licensee is retracting this report based on the following: "Further analysis has shown that the foreign material found in the HPCI lube oil sample taken 2/7/2002 did not cause HPCI to become inoperable, it could have performed its design function before, during and after the time it was declared inoperable. "This is based on determination through engineering review that the type and size of material found in the sample would not have prevented any part of HPCI from failing to operate as required. "Preliminary cause determination is that 4 liters of unfiltered oil were added to the 150 gallon lube oil system during the previous monthly sample evolution. "For these reasons. JAF is concluding that HPCI remained operable from the original LCO entry of 12:15; 2/7/02. and is retracting notification #38679." The licensee informed the NRC Resident Inspector. Notified R1DO(Doerflein). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-02-07
38678 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-02-07 | 2002-02-07 13:33 | 2002-02-07 | AGREEMENT STATE REPORT INVOLVING RADIOACTIVE MEDICAL BYPRODUCT MATERIAL This is notification of an event in Washington state as investigated by the WA Department of Health, Division of Radiation Protection. STATUS: new NON-Licensee: Stericycle City and state: Morton, WA License number: NOT APPLICABLE Type of license: NOT APPLICABLE Date of event: January 23, 2002 Location of Event: Morton, WA ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) A package of medical waste sent to Stericycle for treatment set off the radiation alarm. Stericycle is not permitted to receive or treat radioactive waste. The package was pulled from the conveyor line and measured at 2.5 mrem/hour at one spot on the surface. The package indicated it was from Northwest Prostate Institute in Seattle. Stericycle held the package in cold storage until February 4 when a re-survey indicated the dose rate had not diminished. A Division of Radiation Protection inspector was dispatched to verify the dose rate and check the gamma spectrum. The gamma energies are consistent with an I-125 source. The state of Washington issued DOT exemption 11406 (approval number WA-WA-02-01) allowing return shipment. The package will be received by the licensee (Northwest Hospital, Seattle) which handles implant procedures for patients of the Northwest Prostate Institute. It is believed an I-125 seed was passed in a urine sample during a post-implant follow-up visit at the Institute. What is the notification or reporting criteria involved? WAC 246-221-260 Reports of overexposures and excessive levels and concentrations. Activity and Isotope(s) involved: unknown quantity of I-125 Event Report #WA-02-005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-02-07
38677 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-02-07 09:45 | 2002-02-07 12:46 | 2002-02-07 | OFFSITE NOTIFICATION INVOLVING QUARANTINE OF CAFETERIA "Today (02/07/02) @ 09:45 AM the Shift Manager was informed of a incident that occurred in the plant cafeteria, which required notifications to other government agencies( New Jersey State Police, the local Police Department). 10CFR 50.72(b)(2)(xi) notification "The incident that occurred in the cafeteria (which is located within the Owner Controlled Area but outside the Protected Area) was the discovery of a white powder substance in a roll of quarters. A worker who was opening the roll to place the quarters in a cash register made the discovery of the white powder. The area was secured and the security department was contacted, the State Police and local Police Departments were contacted. "The substance is being collected and will be tested by the appropriate off-site agencies. The Plant cafeteria remains closed until further information is known. There are no other areas of the station that are closed down or were impacted." The licensee anticipates making a press release and informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-02-07
38676 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2002-02-06 17:22 | 2002-02-06 22:37 | 2002-02-08 | HPCI DECLARED INOPERABLE "During the completion of scheduled testing on the Unit 1 High Pressure Coolant injection (HPCI) system, a valve designed to provide minimum flow protection for the associated pump did not automatically open in the time frame expected during pump shutdown. The valve did respond correctly to Operator action. "HPCI was declared inoperable as of 1722 hours on February 6th, 2002. Troubleshooting on the minimum flow protection circuitry is currently in progress. "This report is being made in pursuant to 10CFR50.72(b)(3)(V)(D) for failure of a single train accident mitigation system." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE 1508EST ON 2/8/02 FROM STAN GAMBLE TO S. SANDIN * * * The licensee is retracting this report based on the following: "This is a retraction of the event notification made on 2/6/02 at 22:37 hours. This event (#38676) was initially reported as a safety system functional failure under the requirement of 10CFR50.72(b)(3)(v)(D), after the Unit 1 High Pressure Coolant Injection (HPCI) minimum flow valve did not automatically open during system testing. "Subsequent testing verified that the valve would have opened automatically without operator action following the low flow alarm actuation. A delay in response is expected when system flow is reduced to a value within the range of the flow transmitter. This delay in response, and the short duration of pump operation at a no flow condition is not detrimental to the HPCI pump. "The system response was verified to be as designed considering the test conditions. A condition did not exist at the time of discovery that could have prevented the fulfillment of the safety function." The licensee informed the NRC Resident Inspector. Notified R1DO(Doerflein). | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-02-06
38675 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-02-06 19:19 | 2002-02-06 20:51 | 2002-02-06 | OFFSITE NOTIFICATION OF OPACITY EXCEEDANCE "On 2/6/02, while placing X-600 Steam Plant #2 boiler in service, two opacity readings (six minute average) were above 20% within one hour. This requires a verbal notification to the Ohio Environmental Protection Agency (OEPA). "At 1919 hours, the Plant Shift Superintendent notified OEPA of the X-600 Steam Plant opacity exceedance. UE2-RA-RE1030, App. D, section P requires a four hour NRC event when other government agencies are notified." The NRC resident inspector has been informed of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-02-06
38674 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2002-02-05 19:00 | 2002-02-06 11:46 | 2002-02-06 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following is taken from a faxed report: "Event Report ID No. TN-02-024 "License No.: R-05018 "Licensee: S & ME. inc. "Event date and time: February 5,2002, between 1900 CST and 2100 CST "Event location: Old Hickory, TN "Event type: Stolen moisture density gauge "Notifications: US NRC Region II, Metro Davidson Police Department "Event description: S & ME, Inc., reported a Troxler moisture density gauge, Model 3401B SN 13284, containing 8 millicuries of Cesium-137 and 40 millicuries of Americium 241:Beryllium was stolen from the bed of a pickup truck on the night of February 5, 2002. The gauge was chained in the back of the truck parked at YMCA parking lot. Thieves cut the padlock and removed the locked container. State DRH inspectors are onsite investigating at this time. "Media attention: None-at this time. A press release is being issued by TDEC." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2002-02-06
38673 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-01-29 00:30 | 2002-02-06 09:52 | 2002-02-06 | STUCK WELL LOGGING TOOL The licensee notified the State on 2/5/2002 that a well logging source became stuck at 10,565'. The device was a NSR-F serial # 2437 containing Am-241/Be @ 16 curies. The tool became stuck on the third descent into the well. Five attempts at "fishing" the tool were unsuccessful. The cause of the incident is believed to be overbalanced sand. The licensee will abandoned the source at 10,565'. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-02-06
38672 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2002-01-31 | 2002-02-05 19:26 | 2002-02-05 | AGREEMENT STATE REPORT ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) A sealed source was discovered to be leaking and contamination was found on one researcher and at several locations within the researcher's lab. The contamination from a custom-made sodium-22 source was discovered during a routine survey of the lab. The WSU Radiation Safety Office (RSO) continues to oversee clean-up of the lab. The WSU researcher was contaminated on the inside of a knuckle of one hand. The WSU RSO staff estimated about 2 nCi of Na-22 in a 0.5 centimeter wide spot on the contaminated finger. This was about 10,000 cpm when first measured and immediately cleaned to 3000 cpm (0.04 mR/hr) by simple washing. The researcher was taken to the Pullman Hospital for additional cleaning and an X-ray of the finger to rule out the possibility of a metal sliver or other removable contamination. RSO staff were at the hospital to oversee activities. Contamination was only found in the lab, including on a jacket and the floor. No contamination was found outside the lab. Staff and others who had access to the lab are being checked to see if any contamination was carried out of the lab on shoes or clothing. What is the notification or reporting criteria involved? WAC 246-221-265 (Special Reports...Leaking Sources) Activity and Isotope(s) involved: 18 millicuries Na-22 Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) One individual was known to have some contamination on a finger but the dose is unknown at this time. Lost, Stolen or Damaged? (mfg., model, serial number) The Na-22 source was made by Brookhaven National Labs in December 2000. Model and serial number unknown at present. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2002-02-05
38671 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-01-14 | 2002-02-05 17:45 | 2002-02-05 | AGREEMENT STATE REPORT - OVEREXPOSURE The following is text of a TX licensee report regarding the event: "In reviewing our quarterly dosimetry reports for the first three quarters of 2001, we find that the employee identified on the attachment has exceeded the annual TEDE for occupational]y exposed workers. The fourth quarter report will not be available from our TLD supplier until sometime in February. "However, in compliance with TRCR 289.202(yy)(1)(B)(i) we are reporting this overexposure as soon as known. "In discussing this overexposure with the individual, he indicated it was due to the quantity of work performed. No procedures or license conditions were violated. Upon receipt of our fourth quarter report, we will advise you of any addition exposure to this individual." The Quarterly doses were First Quarter - 574 mrem Second Quarter - 1868 mrem Third Quarter - 4847 mrem The State of Texas is investigating the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-02-05
38670 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2002-02-05 09:12 | 2002-02-05 11:20 | 2002-02-05 | MANUAL REACTOR TRIP DUE TO LOSS OF A MAIN CIRCULATING WATER PUMP The licensee initiated a manual reactor trip per procedure due to the loss of a main circulating water pump for an unknown reason. All plant systems functioned properly and all rods fully inserted. The plant is stable in Hot Standby with auxiliary feedwater supplying the steam generators and the atmospheric reliefs removing excess heat. The licensee is investigating the cause of the main circulating water pump trip. The licensee notified the NRC Resident Inspector, State and Local authorities and the Public Service Commission. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-02-05
38669 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2002-01-10 | 2002-02-04 16:48 | 2002-02-04 | SMALL QUANTITY OF RADIOACTIVE WASTE MISSING The licensee reported that a bag of radioactive waste containing 132 microcuries of I-125 was misplaced between 12/27/01 and 1/10/02. The licensee believes that the waste may have been inadvertently disposed of as biohazardous waste. In this case, the material would have been biologically decontaminated and then sent to a sanitary landfill for disposal. Due to the low penetrating nature of the radioactivity, the licensee does not believe that a search of the landfill would be of much benefit. A calculation of the possible dose resulting from the handling of this material indicated that an individual would not receive a dose in excess of 1 mrem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-02-04
38668 | 0 | UNIV OF MICHIGAN |  |  |  | 2000 KW POOL | 2002-02-01 | 2002-02-04 15:57 | 2002-02-04 | POSSIBLE OVEREXPOSURE BASED ON DOSIMETRY READING On 2/1/2002, the University Radiation Safety Officer received the 10/15-11/14/2001 TLD results from their dosimetry processor (Landauer), which indicated that an individual had received an extremity dose of 72.6 rem to the hand. This result was based on readings from a ring dosimeter. However, based upon results from another ring dosimeter worn by the individual during the period (114 mrem) , the individual's whole body dosimetery (33 mrem), and the individual's work duties, the RSO believes that this result may be in error. The RSO has been in contact with NRC Region III regarding this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | NPR |  | 20.1906(d)(2) |  |  |  | 0 | 2002-02-04
38667 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-02-03 09:20 | 2002-02-04 09:44 | 2002-02-21 | AGREEMENT STATE REPORT REGARDING GAUGES STOLEN FROM KCCS, INC., IN KISSIMMEE, FLORIDA The following text is a portion of a facsimile received from the state: "Abnormal Occurrence: No" "Followup Report: No" "Allegation: No" "Incident Date: 03-Feb-02" "Licensee or Owner: KCCS, Inc." "[...]" "City, State, and Zip Code: Lauderdale Lakes, FL 33319" "License #: 3087-1" "License Type, Category: Specific, 3L(1)" "[...]" "Isotope(s): Cs-137, Am-241" "Activity(s): CPN 10/50 each, Troxler 9/44" "Material Form; Chemical Form; physical Form: Solid, Special Form, By-product" "Probable Disposition of Material: Unknown" "Exposure? No" "Number: N/A" "Type of Individual(s): N/A" "Exposure Source: N/A" "Dose Delivered to: N/A" "Maximum Dose Received: N/A" "Incident Category: Loss of Control - Lost, Abandoned, or Stolen Materials" "Incident Location: [...], Kissimmee FL 34744" "Location Classification: Temporary Work Site" "Incident Description: [The] licensee discovered at 0920 hours on 2-3-02 that a trailer and shed had been vandalized. This occurred sometime between the evening of 2-1 and the morning of 2-3. The locks were cut, and everything of value [was] taken. The locks on the gauge cases had also been cut. The keys were locked in a desk drawer with other keys, [and] all were taken. [The] City of Kissimmee PD and the Florida Bureau of Radiation Control are investigating. The licensee has been strongly urged to post a reward and is considering it. This office was notified of this event on 2-4-02." "Device Type (Quantity): 1 - Moisture/Density Gauge (1)" "Manufacturer: CPN" "Model Number: MC-3" "Serial Number(s): M3707771" "Device Type (Quantity): 2 - Moisture/Density Gauge (1)" "Manufacturer: CPN" "Model Number: MC-3" "Serial Number(s): M34002262" "Device Type (Quantity): 3 - Moisture/Density Gauge (1)" "Manufacturer: Troxler" "Model Number: 3450" "Serial Number(s): 278" "Emergency Groups at Scene: City of Kissimmee PD (Report # 01-02-000928)" "Organizations Notified: NRC, SWP" "Media Contacted: None" "[...]" "Date; Time Investigated: 04-Feb-02; (//)" "Region II, Dick Woodruff, has been notified. If you have any questions, contact [the] Florida BRC." (Call the NRC Operations Center for licensee contact information, the incident location, and state contact information.) ***UPDATE 1229EST 2/21/02*** The following was received by facsimile from State of Florida, Bureau of Radiation Control "Items were discovered by construction workers in the woods adjacent to new road construction on McCoy Road near SR 528, about 0.25 miles west of SR 15 in SE Orange County. Area is about 2 miles NE of the Orlando International Airport. Items were abandoned along with other items which had been stolen and vandalized. Gauges were undamaged, intact in the transportation boxes with the gauges in the stowed position. Survey readings were normal and sources appeared intact with no removable contamination. Gauges were released to the FBI who will release them to the owners when the crime scene investigation is finished. Numerous news organizations were on the scene and flights were even diverted to different runways at the airport to avoid over flight of the area before investigators were notified and arrived at the scene. No further action will be taken on this incident." Notified R2DO (Modes) and NMSS (Fred Brown) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-02-04
38666 | -1 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2002-02-02 02:42 | 2002-02-02 04:47 | 2002-02-06 | AUTOMATIC EMERGENCY DIESEL GENERATOR START FOR UNKNOWN REASONS The following text is a portion of a facsimile received from the licensee: "Vogtle Electric Generating Plant Unit 1 experienced an emergency start of the 1A emergency diesel generator at 0242 on 02/02/2002. The diesel generator emergency started without a safety injection or [loss of offsite power (LOSP)] signal present. Operators attempted to reset the emergency start signal without success. The diesel started and ran unloaded for approximately 1 hour and then was emergency stopped by control room operators and declared inoperable. An investigation for the cause for the start is underway at this time." The licensee stated that there were no maintenance or surveillance activities ongoing at the time of the event. The licensee also stated that there was no one present in the emergency diesel generator room at the time of the event. The licensee notified the NRC resident inspector. * * * UPDATE ON 2/5/02 @ 1103 BY WILLIAMS TO GOULD * * * RETRACTION An investigation has determined that the event represents an invalid ESF actuation which is not reportable per 10 CFR 50.72. The local EDG manual emergency start handswitch leaked control air pressure resulting in the pressurization of two sensors which generated an emergency start condition. Since a valid ESF actuation signal was not generated by the Solid State Protection System or the ESF actuation system sequencer, the subsequent EDG start represents an invalid actuation of an ESF system. The NCR Resident Inspector was notified. Reg 2 RDO (Fredrickson) was notified | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-02-02
38665 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-01-31 13:45 | 2002-01-31 17:56 | 2002-02-07 | LOSS OF 6 EMERGENCY SIRENS DUE TO ICE STORMS AT 1345 it was determined that six of their eleven emergency plant sirens were not operational. An ice storm caused the loss of power to the sirens. The county sheriffs office was contacted and in the event of an actual emergency they will contact personnel in these areas directly (route alerting). The remaining five sirens will alert a majority of the population in the effective ten mile zone. The total ten mile zone is approx. 6099 persons. The remote telemetry system used to identify siren failures did not function correctly. We determined that at least one siren was unavailable and this information was unavailable from the normal monitoring method. A backup method was used to determine the extent of the problem. A news statement was issued to the public at approximately 1600 hours, 01/31/02, discusses the loss of the six emergency sirens. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1408EST ON 2/7/02 FROM RICK HUBBARD TO S. SANDIN * * * The licensee provided the following information as an update: "On 1/31/2002 @ 1656CST, the NRC Operations Center was contacted, EN #38665, concerning a loss of E-Plan Sirens. As of 1233CST 2/7/2002, all sirens have been restored to operable status. A news release has been prepared and will be made following this notification." The licensee informed state/local agencies, FEMA and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) | 50.72(b)(2)(xi) |  |  | 0 | 2002-01-31
38664 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2001-10-01 12:00 | 2002-01-31 16:06 | 2002-01-31 | OVEREXPOSURE The film badges of two radiographers working for H& H X-Ray Services were processed for the month of October, 2001. The readings of the film badges for the month of October were 7909 mrem and 3825 mrem. H & H X-Ray Services individuals were using a 68 curie (Iridium-192) radiography camera in Monroe, LA. The State of Mississippi Division of Radiation Health is following up on this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0 | 2002-01-31
38663 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-01-30 12:00 | 2002-01-31 13:30 | 2002-02-21 | LEGACY ISSUE NRC BULLETIN 91-01 24 HOUR NOTIFICATION "AT 1313 CST, on 1-30-02 the Plant Shift Superintendent (PSS) was notified of uncharacterized legacy process equipment which was not stored in accordance with an approved Nuclear Criticality Safety Approval (NCSA). The mass of fissile material was less than a safe mass and at an assay of less than 2.0 Wt. %. This is in violation of the NCS program requirements of SAR, Section 5.2 which requires fissile material operations to be controlled by approved NCSA's. "The PSS determined that this event is a 24 Hour Event Report due to the failure to maintain double contingency controls. SAFETY SIGNIFICANCE OF EVENTS: "This material is in a stable condition and double contingency has been established using approved procedures. Once the material was characterized, it was determined that proper spacing had been maintained. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "In order for criticality to be possible more than a critical mass would need to be accumulated in an unsafe geometry. The storage containers are safe by geometry and the fissile material is less than a safe mass. Therefore, it is not possible for this barrier material to result in a criticality accident. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Mass ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "Less than 10 pounds at an enrichment of less than 2.0 Wt. % NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Since no NCS controls were applied to the material, double contingency cannot be demonstrated. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "The material is controlled in accordance with procedure CP-2-TS-TS2030. The material has been characterized." The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1845EST ON 2/21/02 FROM CALVIN PITTMAN TO S. SANDIN * * * The following information is provided as an update: "After discovery, further characterization of the material was performed. Independent assay smears and direct surveys by health physics personnel confirmed that several pieces of the material were <1% assay and not fissile. The remaining material was weighed, on a NMC&A balance, and found to have a total mass of <15 grams U-235. Therefore, this material stored in this room of C-710 does not meet the conditions of a fissile operation. "SAFETY SIGNIFICANCE OF EVENTS: Further analysis revealed this material does not meet the conditions of a fissile operation; therefore, no further actions are required. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Further analysis revealed that less than 15 grams of total mass of U-235 were involved. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Further analysis revealed this material does not meet the conditions of a fissile operation. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Further analysis revealed this material does not meet the conditions of a fissile operation; therefore, no further actions are required." The NRC Resident Inspector was notified of this event by the licensee. Notified R3DO(Jorgensen) and NMSS(Brach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-01-31
38662 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2002-01-30 12:30 | 2002-01-30 15:46 | 2002-01-30 | OFFSITE NOTIFICATION TO STATE POLICE OF ACCIDENT INVOLVING A RADIOACTIVE SHIPMENT. At 12:30 on 1/30/02, the NC State Police Department was notified that a radioactive shipment (OC-9004-02) was involved in an accident. The shipment enroute from Oyster Creek to Oak, Ridge TN for disposal, was involved in a vehicular accident in North Carolina on Route 40. The shipment was an empty office trailer which contained some fixed contamination on the inside. The trailer struck a bridge on Route 40 at approximate mile marker 116. The roof of the trailer peeled back about 15' to 30'. There was no spread of contamination and the trailer was taken to the side of the road. Additional vehicles have been dispatched for assistance. The trailer will be torn down a bit, covered with tarps and the continue to TN. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-01-30
38661 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2002-01-30 10:54 | 2002-01-30 13:09 | 2002-01-30 | PLANT MADE AN OFFSITE NOTIFICATION OF AN OIL SPILL On 1/30/02, at 1054, the Beaver Valley Control Room received notification of a fuel oil spill from a tractor trailer truck outside the owner controlled protected area, at the basin of the Unit 2 cooling tower. At 1056, the control room staff entered abnormal operating procedure 1/2AOP-75.6, "Oil Spill Response." Assessment by the Beaver Valley response personnel determined that the fuel oil side saddle tank of the tractor trailer had ruptured. Approximately 100 gallons of diesel fuel oil was released down a storm sewer. An unknown quantity of oil entered the Ohio River. The remaining oil is being contained and removed from the "Peggs Run" area. Offsite notifications have been made to the Pennsylvania Department of Environmental Protection (DEP), the Pennsylvania Emergency Management Agency, and downstream Public Water Authorities. Weavertown Environmental Services has been contacted and is assisting in clean-up activities. The NRC resident has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-01-30
38660 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-01-29 12:00 | 2002-01-30 11:12 | 2002-01-30 | AGREEMENT STATE REPORT - RECEIPT OF PACKAGES EXCEEDING SURFACE RADIATION LIMIT "AEA Technology QSA, Inc., license number 12-8361, reported that on January 29, 2002 they received nine Type A packages that exceeded the external surface radiation regulatory limit and exceeded their labeled Transport Indexes (T.I.). All of the packages originated from Russia and were shipped to the U.S. by Reviss Services of the U.K. using Federal Express as the carrier. "Each package contained 1.4 to 2.4 TBq of Selenium 75 and had surface external radiation measurements of up to 577 mR/hr and 1 meter measurements of up to 6.0 mR/hr. All the highest readings were found at the bottom of each package. "Preliminary investigation of the Type A packages indicate they may be missing an inner shield which affected the bottom area dose rates. "The dose to the shippers is not expected to be greater that normal because all of the highest readings were found at the bottom of the packages and all the TI's were below the regulatory limits." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2002-01-30
38659 | 0 | EARTH ENGINEERING |  |  |  |  | 2002-01-30 | 2002-01-30 07:08 | 2002-01-30 | STOLEN TROXLER DENSITY GAUGE A Troxler density gauge was stolen from the technician's car. A report has been made to the Philadelphia Police Department. More information to follow from the company. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-01-30
38658 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2002-01-28 12:45 | 2002-01-29 10:19 | 2002-01-29 | FITNESS FOR DUTY REPORT A Supervisor tested positive for marijuana during a random test. The individual's access has been suspended. The licensee will conduct a work review. The licensee will inform the NRC Resident Inspector. Contact the Headquarters Operations Center for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.73 |  |  |  | 1 | 2002-01-29
38657 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2002-01-28 16:00 | 2002-01-28 17:39 | 2002-01-28 | OFFSITE NOTIFICATION OF AN OIL SPILL A spill of approximately 40 gallons of turbine lube oil in the turbine hall occurred with no release to the environment. This amount was in excess of the reportable quantity of 10 gallons, so notification was made to the Connecticut Department of Environmental Protection of the spill. This incident occurred during a decommissioning activities in the turbine hall. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-01-28
38656 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-01-27 21:15 | 2002-01-28 15:45 | 2002-01-28 | 24 HOUR 91-01 BULLETIN RESPONSE Reason for Notification At the time of the event, the Team Leader of the Burnable Absorber Expansion System called the cognizant Nuclear Criticality Safety (NCS) engineer to inform him that 113.5 kg of uranium oxide powder had spilled from process equipment into the granulator hood. Summary of Process Dry UO2 powder blended with U3O6 and erbium oxide is processed in a favorable geometry, gravity fed, vertical pipe from a roll compactor down to a granulator. Inside a hood, the granulator feeds down through a flexible tube into a polypak. As Found Condition A summary of the as found conditions is as follows: It had been determined that the granulator screen needed to be replaced, and operations were stopped. When the granulator screen was removed, material in the vertical pipe spilled down onto the bottom of the hood, remaining contained within the hood. The spill was immediately placed into polypaks and telephone notification was made to Nuclear Criticality Safety. Double Contingency Protection Double contingency protection for this situation, which is classified as a spill, is based on control of mass and moderation, and assumes a hemispherical configuration. The mass limit is 50.3 kgU or 57.1 kg UO2; the moderator limit is 32.1 liters of water. It was determined that double contingency protection was lost because the amount of material spilled exceeded the mass limit. Moderation controls remained intact. Double contingency protection was restored in approximately 30 minutes. Therefore the incident requires notification in accordance with Westinghouse Operating License (SNM-107), paragraph 3.7.3 (c.5), in which greater than safe mass is involved, but controls are restored within four hours. Summary of Activity Nuclear Criticality Safety gave permission to resume operations because double contingency protection had been restored. On January 28, 2002, written instructions were issued to erbia operations personnel and training conducted reinforcing that before removal of the screen from the granulator, the material in the vertical process pipe is to be processed into polypaks. Long term corrective actions to prevent the possibility of recurrence will be evaluated as part of apparent cause analysis. Conclusions Loss of double contingency protection did occur, but was restored within approximately 30 minutes. At no time was criticality possible because there was no moderator present. At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. It has been determined that this is a safety significant incident in accordance with governing procedures. An apparent cause analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-01-28
38655 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2002-01-27 15:50 | 2002-01-28 13:55 | 2002-01-28 | TRANSPORTATION OF A CONTAMINATED INDIVIDUAL TO THE HOSPITAL At 1515 hours on Sunday, January 27, 2002, an employee performing the routine task of cleaning out piping was struck on the left upper arm by a flange and/or packing material. The employee was unaware that the piping was overpressurized at 13.7 psig when he released the clamp on the flange. The operator received minor skin contamination when one of the unused gloves in the glove box in which he was working separated from the box, releasing contamination to the work area. The contaminated operator was transported to the local hospital emergency room for treatment. Maximum skin contamination was less than 17,000 dpm/100 cm². A Radiation Technician accompanied the injured employee to monitor contamination levels. After treatment the employee returned to the plant and was decontaminated to less than 200 dpm/100 cm². Hospital emergency facilities, the emergency vehicle, and attending personnel were surveyed and no contamination was found. The Licensee continues to investigate the incident. The NRC resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(3) |  |  |  | 1 | 2002-01-28
38654 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2002-01-26 21:00 | 2002-01-26 18:03 | 2002-01-27 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS Unit 2 will be shut down in accordance with plant Technical Specifications because the 2A EDG has been declared inoperable due to worn engine drive gears and repairs cannot be completed within the 72 hour TS LCO time. The worn gears were discovered during a routine maintenance inspection. The licensee will commence the shutdown at 2100 EST. The licensee will inform the NRC resident inspector of this shutdown. * * * UPDATE 0120EST ON 1/27/02 FROM DAVE LYNCH TO S. SANDIN * * * An NOED (Notice of Enforcement Discretion) conference call was held following which Unit 2 was granted a six day extension until shutdown is required, i.e., 0300EST on 2/2/02. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-01-26
38653 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-11-07 | 2002-01-25 18:15 | 2002-01-25 | AGREEMENT STATE REPORT "A truck caught fire and burned. A S.P.E.C. camera, serial # 98, source serial # HS1210 containing Ir-192 was on board. The source remained intact and was not leaking. The device and source were returned to the manufacturer. "We have no additional information. We have contacted the Licensee to obtain more details." Texas Incident No.: I-7848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-01-25
38652 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-01-25 12:00 | 2002-01-25 18:05 | 2002-01-25 | 24-HOUR NRC BULLETIN 91-01 REPORT "The Plant Shift Superintendent (PSS) was notified of an employee entering an inadvertent container area with a camera inside a plastic bag. During an investigation requiring pictures, the camera was removed from the plastic bag. When the employee was taking pictures the plastic bag was left unattended. This is a violation of NCSA-705076.A03 control #3 and #5. #3 When unattended, all potential inadvertent containers shall be modified to prevent an unsafe accumulation in the container. #5 If flexible material is utilized, it shall be configured or secured such that it cannot be deformed into an inadvertent container with an unsafe accumulation potential. "The plastic bag was removed from the area. "SAFETY SIGNIFICANCE OF EVENTS: "LOW, There was no leak of uranium bearing material in the vicinity of the unattended plastic bag. The uranium recovery system was not in operation however solution was in the system. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "The recovery system would have to be in operation bearing solution with an unknown or high quantity of uranium. A leak from the system would occur such that an unsafe amount of liquid would spray into the plastic bag. The liquid would then have to collect 2.5 liters and deform the plastic bag to a depth of greater then 1.5 inches and an unsafe geometry. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY. CONCENTRATION, ETC.): "Volume 2.5 liters or Geometry 1.5 inches in depth or 4 inches in diameter "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "No uranium bearing material was involved in this event "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "An unattended plastic bag in an inadvertent container area was not configured or secured such that it could not be filled or deformed into an inadvertent container with an unsafe accumulation potential. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "The plastic bag was removed from the area." The NRC resident inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-01-25
38651 | 0 | AUTOMATIC VALVE |  |  |  |  | 2002-01-25 | 2002-01-25 16:25 | 2002-01-25 | PART 21 REPORT "On 11-14-2001 [an employee] of Exelon Power Labs called and reported that (2) U0203FBBR-AA valves had been sent to their lab from Exelon - Limerick for evaluation with the complaint that the valves were leaking in the energized position. The valve is being used in the normally closed mode at an inlet pressure of 74 psig. Further, according to [the employee], there are additional U0203FBBR-AA valves at Limerick that are exhibiting the same problem. "On 11-29-2001 one valve was returned to Automatic Valve for further evaluation. At inlet pressures of 74 & 125 PSIG it was determined that the valve did not reset after the solenoid was de-energized. It did not reset until the inlet pressure was reduced to approximately 40 psig respectively. "When tested in the normally open mode - pressure to port 1 [...], there was leakage at exhaust port 3 when the solenoid was energized but the valve immediately reset at its maximum rated inlet pressure of 125 psig when the solenoid was de-energized. "When the valve was disassembled a permanent set in the rubber in the top plunger seal was found that conformed to the shape of the top seat in the solenoid plunger guide. This deformation is normal and is not a concern. "The plunger was then dissected for additional analysis. It was determined that the top seat was 0.020" below the top surface of the plunger or 0.007" below the maximum design standard of 0.013". "With the top seat 0.020 below the top surface of the plunger, the top seal was touching the top orifice but was not compressing the internal spring and hence not creating a good seal. Consequently, there was severe leakage out of exhaust port 3 which is 0.125 in diameter. This severe leakage created a pressure differential across the top of the plunger, and thus a force tending to hold the plunger in place. This force could not be overcome by the external spring until the inlet pressure was reduced to approximately 40 psig. "It was observed that all parts of the dissected plunger were present and in their proper location. Further, it was noted that the tested leak rates and performance characteristics of the valve prior to the plunger being dissected did not match field reports from Exelon. Consequently, Exelon was contacted and additional samples were requested. "On January 3, 2002 a second U0203FBBR-AA valve was returned to Automatic direct from Exelon - Limerick by [...]. This valve exhibited the same operational characteristics in the normally closed mode as did the valve returned on November 29, 2001. That is, it leaked excessively when energized. And, as with the previous valve examined by Automatic Valve, the inlet pressure at port 1 had to be reduced to approximately 54 psig after the solenoid was de-energized before the valve returned to its normally closed position. "A second test was run on the valve returned on January 3, 2002. Previously both returned valves were tested 'cold.' That is, they had been at room temperature for a number of hours or days. When tested, pressurized air was plumbed to port 1 and the solenoid was energized only long enough to confirm that there was leakage out of port 3. Then the solenoid was de-energized and the inlet pressure reduced to a value that the plunger would return to its normally closed position. With the second valve, the solenoid was left energized with 125 psig of air to port 1. After a period of approximately 60 minutes, the leak at port 3 greatly diminished and, when the solenoid was de-energized, the valve immediately returned to its closed position. This test was repeated three (3) times with the same results. "In summary, evaluation of the (2) valves resulted in the following symptoms and concerns: "1. A faulty valve will leak out of port 3 when the valve is used in its normally closed mode [...] or leak out of port 1 when the valve is used in its normally open mode [...] "2. There is no concern that U0203FBBR-** valves used in the normally open mode (pressure at port 3) will return to their de-actuated position (port 3 open to port 2 and port 1 blocked) when the solenoid is do-energized. In this mode both the internal spring, the external spring, and inlet pressure at port 1 act to return the plunger to its normal do-actuated position. "3. There does not seem to be a concern, based on field experience, that U0203FBBR-** valves used in the normally closed mode (pressure at port 1) will return to their de-actuated position (port 2 open to port 3 and port 1 blocked) when the solenoid is de-energized provided the solenoid has been energized for an extended period of time. Test on the valve returned on January 3rd indicate that this period of time is approximately 15 minutes at 80 psig inlet pressure and approximately 60 minutes at 125 psig. However, the impact of further degradation of the shell relative to the seal, when the valve has been energized over an extended period of time is unknown. "4. There would not seem to be a concern in applications where the U0203FBBR-** valve is used in the normally closed mode (air at port 1) and the valve is normally de-energized provided that, when energized, it is not energized for a total period of time exceeding 6 months. "5. There is a concern that U0203FBBR-** valves used in the normally closed mode will not return to their de-actuated position if the valve has been in its de-energized position for a sufficient amount of time for the valve and the internal top seal to cool down. If the valve is energized then is de-energized, within a period of approximately 60 minutes with 125 psig at port 1, or 15 minutes with 80 psig at port 1 there is a high probability that the valve will not return to its de-energized condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MI | OTH | PAR | 21.21 |  |  |  | 0 | 2002-01-25
38650 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-12-28 17:01 | 2002-01-25 15:36 | 2002-01-25 | 60-DAY OPTIONAL REPORT PURSUANT TO 10CFR50.73(a)(1) "On 12/28/01, the plant was in a cold shutdown condition with the RHR system in the shutdown cooling mode. The reactor head vent valves were open. "At 1701 hours a reactor water level indication spike (notching) occurred on the 'B' narrow range reactor water level instrumentation (e.g. instrument rack C-2206). The event occurred when Reactor Recirculation Pump 'B' was started. This resulted in Reactor Pressure Vessel pressure lowering due to condensing of vapor in the Reactor Vessel. The spiking was due to gasses coming out of solution in the reference leg associated with the 'B' narrow range instruments. The specific source of the gas is still under investigation. No spike was noted on the 'A' narrow range reactor water level instrumentation (e.g. instrument rack C-2205). The Group I isolation resulted in the closure of the Reactor Water Sample valves (AQ-44 and AQ-45). The Main Steam Isolation Valves (MSIV's) were already closed due to plant conditions. "The Group I isolation was the result of a false high water level signal(s) from analog trip system trip units LS-263-58A-2 (to PCIS Channel A2) and LS-263-58B-2 (to PCIS Channel B2) while the reactor mode switch was in the REFUEL position (not RUN). A Group I isolation is designed to occur if a high water level condition occurs when the reactor mode switch is not in the RUN position. These trip units receive signals from reactor water level transmitters LT-263-58A (instrument rack 2206A) and LT-263-58B (instrument rack 2206A) that are associated with condensing chamber 12B. "The Group I isolation signal was not valid because a reactor water level increase of about 20" did not actually occur. Thus, even though the Group I isolation signal was not planned, the isolation signal was invalid." The NRC resident inspector has been informed of this report by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-01-25
38649 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2002-01-25 08:54 | 2002-01-25 13:06 | 2002-01-25 | FITNESS FOR DUTY REPORT A non-licensed supervisor tested above the limit for blood alcohol content during a random test. The individual's site access has been suspended and the licensee is conducting a review of the individual's recent work. The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.73 |  |  |  | 0 | 2002-01-25
38648 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2002-01-24 11:00 | 2002-01-24 18:20 | 2002-03-07 | FAILURE OF REACTOR VESSEL WATER LEVEL SWITCH "At 11:00 EST, during performance of the 24 Month Calibration of Reactor Vessel Water Level Channels on Unit 2, Level Indicating Switch LIS-B21-2N031C would not properly relock following calibration. As a result of this, the switch was declared inoperable. A review of the design drawings revealed that this switch provides inputs (through relays) that affect the reset logic for the 'A' and 'C' ESW pumps and the trips for the 'A' Reactor and Turbine Building Chillers on a Low Reactor Water Level signal. Without this switch functioning properly, the listed ESW pump start timers would not reset as required and the listed chillers would not trip as required on the Low Reactor Water signal. The Tech Spec Basis for this instrumentation indicates that without these features, both offsite circuits and the associated Diesel Generators would be inoperable. Given this, both offsite sources and two (2) Diesel Generators were declared inoperable. SSES safety analysis requires three Operable Diesel Generators to safely shutdown the plant. Given this, this condition requires an 8 hour ENS notification in accordance with 10CFR50.72(b)(3)(v). "As a result of this condition, LCO 3.0.3 was entered on both Unit 1 and Unit 2 (in addition to other applicable LCO's). As of 13:00 on 01/24/02, the switch was repaired and declared operable (and the associated LCO's were cleared). "There were no Diesel Generators, ECCS, or Tech Spec Electrical Distribution systems out of service at the time of the event." The NRC resident inspector has been informed of this notification by the licensee. * * * EVENT RETRACTED AT 1743 EST 3/7/02 BY GRANT FERNSLER TO GERRY WAIG * * * "A subsequent evaluation of the inoperable level switch determined that the impact, under worst case conditions, would have resulted in only one inoperable Emergency Diesel Generator. Both offsite power sources and the remaining three aligned Emergency Diesel Generators would remain operable. This is within the design basis of the plant and therefore the condition would not have resulted in a complete loss of a safety function. Based on that evaluation, ENS notification EN#38648 is retracted." The NRC Resident has been notified of the retraction by the licensee. Notified the R1DO (Mohamed Shanbaky). | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2002-01-24
38647 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2002-01-21 | 2002-01-23 14:23 | 2002-01-23 | AGREEMENT STATE REPORT INVOLVING UNPLANNED CONTAMINATION On 1/21/02 a patient undergoing a cardiac stress test at the St. Alexius Medical Center located in Hoffman Estates, IL, had the IV needle inadvertently pulled from his arm resulting in a 20mCi Technetium-99m spill. The licensee washed the patient's hand which was potentially contaminated and isolated the room to allow for decay. Survey readings using a Ludlum, model 14C survey meter, ranged between 17mr/hr and 35 mr/hr. Twenty-four hours after the spill the highest rad reading was 5mr/hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2002-01-23
38646 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2002-01-18 17:30 | 2002-01-22 15:49 | 2002-01-22 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "...A Troxler Electronics Model 3430, Serial Number 30208 gauge had been stolen between 5:00 pm and 5:30 pm on Friday, January 18, 2002. "On Friday evening January 18, 2002, two Bhate employees stopped after work for dinner at Nifflers Restaurant in Auburn, Alabama. At approximately 5:30 pm they came out of Nifflers and discovered the nuclear gauge. which had been chained to the bed of the truck was gone. Someone had cut the chain and taken the gauge, which was locked inside the transportation case. "The device was found either Friday night or Saturday morning by the Auburn Police Department where it had been abandoned on Spring Hill Road in Auburn, Alabama. "On Saturday afternoon, January 19, 2002, the Auburn Police Department contacted Dr. Charles Ray of Auburn University, who serves as an advisor to their local Haz-Mat team. Later that same afternoon, the Auburn Police Dept delivered to device to Auburn University, who placed the device, still inside the locked case, in their radioactive materials storage area. At approximately 8:00 am on the morning of Tuesday January 22, 2002, a representative of Bhate picked up the device from Auburn University. The case was still locked and the 'trigger lock' was also still in place. "Several employees of the Alabama Office of Radiation Control were available and on pager at all times during this holiday weekend. It appears no one from the Agency was notified. The Agency plans to cite the licensee for failure to make immediate notification of the stolen device as required by 420-3-26-.03(51)(a) of the Alabama Administrative Code. A fax sent to the Agency's offices after hours does not constitute immediate notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2002-01-22
38645 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2002-01-17 08:00 | 2002-01-22 12:10 | 2002-01-22 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The licensee reported the theft of a Troxler moisture density gauge (model 3411, serial #16098) containing two sealed sources (40 mCi Am-Be and 8 mCi Cs-137). The gauge was stolen from the back of a truck parked at an employee's residence in Park Hills, KY. The Park Hills police department and the Commonwealth of Kentucky were notified. On 1/18/02 the gauge was recovered behind a convenience store in Covington, KY. The licensee has possession of the gauge which was not damaged. Ohio reference #OH 02-009. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2002-01-22
38644 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2002-01-21 11:11 | 2002-01-22 11:17 | 2002-01-22 | FAILURE OF 23 OUT OF 24 EMERGENCY SIRENS IN MONROE COUNTY At 0851, January 22, 2002, Ginna Station Emergency Planning received the weekly Siren Silent Test results from Monroe County 911 center. Results indicated a 96% failure (23 out of 24) of the Monroe County sirens on 01-21-02 at 11:11 AM. On 1-21-02 at 11:11AM, RG&E technician was notified by Monroe County of the failure and responded to the 911 center to investigate. The 911 center representative gave the siren test results to the technician. The technician then performed a successful silent test from the central control unit located at RG&E's West Avenue location, however, Monroe County plans do not include the RG&E West Avenue location as an activation or test location. Due to a holiday on 01-21-02, the Monroe County Cobbs Hill location was not staffed and therefore a silent test was not performed from that location. Ginna Station Emergency planning personnel were not notified of the Siren Test failure on 01-21-02, or the retest performed immediately following. Guidelines of EPG-2 specify that Emergency Planning be immediately notified of siren failures greater than 25% in one county. Wayne County has 72 sirens and Monroe County has 24 sirens. On 12-12-01, communications from Monroe County 911 Center to the transmitter on Cobbs Hill was moved from a leased telephone line to the Monroe County microwave system. Since 12-12-01, test performed from this location have been successful. The recent test on 01-21-02 indicates possible interference on the microwave system appears to cause obstruction with siren communication. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-01-22
38642 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2002-01-21 17:35 | 2002-01-21 19:50 | 2002-01-21 | AUTOMATIC REACTOR SCRAM ON TURBINE GENERATOR LOAD REJECT The licensee reported receiving a turbine generator load reject scram, cause unknown at this time. Generator lockout started the event. A Group 2 isolation occurred at +9" reactor water level. All systems functioned as designed. The scram and Group 2 have been reset and the plant will remain shutdown until further investigation is complete. The licensee notified the NRC Resident Inspector, as well as the State and Local Governments. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2002-01-21
38640 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-01-19 00:05 | 2002-01-19 07:56 | 2002-01-19 | UNEXPECTED AUTOMATIC START OF TURBINE DRIVEN AUXILIARY FEEDWATER PUMP (TDAFW) AFTER PLANT SHUTDOWN. After the scheduled reactor trip from 20% power in preparation for a refueling outage the steam generator water level lowered to approximately 17%. This was lower than anticipated on the trip resulting in the Turbine Driven Auxiliary Feedwater Pump autostarting as a function of the steam generator's water level. Both Motor Driven Auxiliary Feedwater (MDAFW) pumps had already been started. Steam generator water levels rapidly recovered and the reactor coolant system cooled below 547 degrees F, which is the normal no load temperature, to 540 degrees F. The 7 degree cooldown below the Tave No Load Condition resulted in Pressurizer Water Level shrink and a letdown isolation. The operators secured the TDAFW pump and throttled the flows from the MDAFW pumps and restored reactor coolant system temperature and pressurizer inventory. The reactor coolant system cooldown and depressurization proceeded normally from that point on. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2002-01-19
38639 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-01-18 21:23 | 2002-01-19 00:47 | 2002-01-19 | THREE OUT OF FOUR TIME DELAY SETTINGS FOR THE REACTOR HIGH PRESSURE ISOLATION CONDENSER INITIATION SWITCHES FOUND OUT OF CALIBRATION. During performance of DIS 1300-01, Sustained High Reactor Pressure Calibration, three of the four time delay settings for the reactor high pressure Isolation Condenser initiation switches were found to be out of Technical Specification tolerance. The maximum time delay allowed per Technical Specification Surveillance Requirement 3.3.5.2.3 is 15 seconds. The time delays for high pressure switches 2-263-53A, 53A, and 53C were 15.6, 15.4, and 15.4 seconds respectively. The 2-263-53D switch was found in tolerance at 14.8 seconds. Each time delay was adjusted to be back in tolerance. This combination of three out-of-tolerance time delays could have prevented the Isolation Condenser from receiving an initiation signal within the 15 second Technical Specification required time limit. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2002-01-19
38638 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2002-01-18 11:00 | 2002-01-18 12:39 | 2002-01-18 | INDUSTRIAL RADIOGRAPHY ACCIDENT WITH POSSIBLE CONTAMINATION Louisiana state licensee Owensby and Kritikos had an industrial radiography accident at the Citgo refinery in Lake Charles , La. It appears that the source drive cable crossed an electric line and a spark exploded the Iridium-192 source. They believe the source is in a safe condition, but there was considerable contamination outside the device. They also believe some people may have contamination on their clothing which may have been tracked to other areas. A health physicist has been dispatched to the scene. The state also told the licensee to isolate the area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-01-18
38637 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-08-03 | 2002-01-17 18:23 | 2002-01-17 | OCCUPATIONAL EXPOSURE INCIDENT On August 3, 2001, Littleton Radiation Oncology called to report error codes 4 and 20. Upon inspection, the Field Service Engineer (FSE) identified a loop in the source cable at the top of the source drum. The FSE removed the loop in the cable; however, the source motor would not drive the source out. The source exchange tool was connected to the service port of the emergency container and the source was driven out manually. The emergency container was used to house the source instead of the source shipping pig since the motor would not drive the source. Per the FSE, the lead technologist was informed of the source status within the room and that the source would need to be moved to a secure storage area. The FSE then left the treatment room to discuss the situation with the physician when the lead technologist interrupted indicating that the source had been pulled out of the container. The FSE secured the source in the emergency container. Parts to make the appropriate repairs were sent immediately and the afterloader was restored to proper working condition. In order to identify the problem, secure the source, and make repairs, the FSE handled a partially shielded to unshielded source on three occasions: i. manually driving the source into the emergency container, ii. securing the source back into the emergency container after it been pulled out by ancillary staff, iii. moving the source from the emergency container to the shipping pig. The FSE wore a self-reading dosimeter along with body and extremity badges provided by Landauer. The occupational exposure reported by Landauer for the period during which the exposure incident occurred is as follows: Deep Dose (DDE) 447 mrem Extremity (SDE) 760 mrem The year to date (1/15/01-8/14/01) total for the individual is 487 mrem (DDE). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2002-01-17
38636 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2002-01-13 | 2002-01-17 18:14 | 2002-01-17 | OKLAHOMA LICENSEE REPORTED A MISSING SHIPMENT IODINE-125 BRACHYTHERAPY SEEDS Mills Biopharmaceutical Co reported that a shipment which left 1/11 via FedEx did not reach its destination, the Palisades Medical Center in New Jersey, on the expected date 1/14/02. The shipment consisted of brachytherapy seeds containing 13.3 millicuries of I-125. The biopharmaceutical company was notified by FedEx on 1/13 that the shipment had experienced a processing delay in Memphis, TN. and now FedEx can not locate the shipment. FedEx is currently looking for it. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2002-01-17
38635 | 0 | STORA ENSO NORTH AMERICA CORP |  |  |  |  | 2002-01-15 15:00 | 2002-01-17 17:11 | 2002-01-17 | MISSING EXIT SIGN The licensee reported that during inventory check a Evanlite model LE exit sign that was installed in their facility was missing. They believed the sign, with a 20,000 millicurie H-3 source, was removed during ongoing remodeling. They are still searching for the sign. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2002-01-17
38634 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2002-01-17 11:45 | 2002-01-17 13:07 | 2002-05-27 | OFFSITE NOTIFICATION INVOLVING RECOVERED SEA TURTLE FROM INTAKE CANAL At approximately 1130 EST on 01/17/02, a green sea turtle was retrieved from the intake canal and a determination was made that it was in need of rehabilitation. As required by the Plant's Sea Turtle Permit, the Florida Fish and Wildlife Conservation Commission (FFWCC) was notified at 1145 EST. The licensee notified the NRC Resident Inspector. See EN #38513 for 2001 occurrences. * * * UPDATE ON 1/28/02 @ 1243 BY KORTH TO GOULD * * * At approximately 1115 on 1/28/02 a loggerhead turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. Per the licensee's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1125. The NRC Resident Inspector was notified. Notified Reg 2 RDO (Ninh) * * * UPDATE ON 2/6/02 @ 0853 BY MERRILL TO GOULD * * * At approximately 0745 on 2/6/02 an injured green sea turtle was rescued from the plant's intake canal. The turtle was alive, but in need of rehabilitation. The turtle will be transported to a facility in Clearwater for treatment. The Florida Department of Environmental Protection has been notified of the event. The NRC Resident Inspector was notified. Notified Reg 2 RDO(Fredrickson) * * * UPDATE 1025 3/2/2002 BY R. DIEHL TAKEN BY R. STRANSKY * * * "At approximately 0830 3/2/02 a Loggerhead turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 0845." The NRC resident inspector has been informed of this report. HOO notified R2DO (Julian). * * * UPDATE 1040EST ON 3/5/02 FROM GEORGE TULLIDGE TO S. SANDIN * * * "At Approximately 1000 on 3/5/02, a Loggerhead turtle was retrieved from the plant intake canal. The turtle was determined to be in need of rehabilitation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified." The NRC resident inspector has been informed of this report. HOO notified R2DO (Julian). * * * UPDATE 1047EST ON 3/6/02 FROM D. EMLING TO M.NORRIS * * * "At Approximately 1000 on 3/6/02, a Loggerhead turtle was retrieved from the plant intake canal. The turtle was determined to be in need of rehabilitation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified." The NRC resident inspector has been informed of this report. HOO notified R2DO (Henson). * * * UPDATE ON 3/10/02 @ 1740 BY KORTH TO GOULD * * * The Florida Department of Environmental protection was notified of a loggerhead sea turtle requiring off-site rehabilitation. The turtle was recovered live from the plant's intake canal. The NRC Resident Inspector was notified. Notified Reg @ RDO (Henson) * * * UPDATE ON 5/27/02 AT 1012 BY RUSSELL SCOT TO FANGIE JONES * * * The Florida Department of Environmental protection was notified of a sick underweight loggerhead sea turtle requiring off-site rehabilitation. The turtle was recovered live from the plant's intake canal at 0915 EST on 5/27/02. The NRC Resident Inspector will be notified. Notified R2DO (Thomas Decker). * * * UPDATE AT 1938EDT ON 5/27/02 FROM ELLIOT SUMNER TO S. SANDIN * * * "A dead Sea Turtle was recovered from the St. Lucie Plant Intake Canal at approx. 1600 [on] 05/27/02. The FL. Dept. of Envir. Protection was notified (1615 [on] 05/27/02) as required by the St. Lucie Plant - Sea Turtle Permit. This notification to a state government agency requires a four (4) hr non-emergency notification to the NRC per 10 CFR 50.72(b)(2)(xi). There were no unusual evolutions in progress beyond normal operations which would have contributed to this event." The NRC Resident Inspector will be informed. Notified R2DO(Decker). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-01-17
38633 | 0 | WASHINGTON STATE UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2002-01-17 08:22 | 2002-01-17 12:22 | 2002-01-17 | WASHINGTON STATE UNIVERSITY REPORTED AN ALERT CONDITION AT THEIR REACTOR The university reported they had a rod stuck 2" out of the core but the reactor is well shut down and they expect no radiological problems. They did evacuate the building and notified their emergency organization, but did not require the police or fire departments. They will troubleshoot to determine the cause of the problem. * * * UPDATE ON 1/17/02 @ 1747 BY TRIPARD TO GOULD * * * Alert terminated at 1449 PST due to the rod being fully inserted and the reactor being in a safe and stable condition. They will make an inspection to determine the problem. Notified Mendonca(NRR), Lyons(EO), Powers(Reg 4 RDO), Sweetser(FEMA) OTHER AGENCIES by fax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EMERGENCY DECLARED | [9 empty] | ALERT | 4 | WA | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-01-17
38632 | 0 | US ARMY |  |  |  |  | 2002-01-16 13:45 | 2002-01-16 16:06 | 2002-01-16 | SAFETY EQUIPMENT FAILURE INVOLVING A RADIOGRAPHY CAMERA SHUTTER On 1/16/02 during an NRC inspection the shutter on a Cyclops Camera Unit failed to close. The licensee manually cranked the shutter to the closed position and locked/tagged the device to prevent operation. The licensed maintenance technician was notified to initiate repairs. The Camera is used by the Crane Army Munitions Activity at the Naval Surface Warfare Center located in Crane, IN. The Cyclops Camera, S/N 105 is a model 590 manufactured by Picker Corp. The source is 1930 Curies of Cobalt-60, S/N T1520, manufactured by Neutron Products. There was no personnel exposure associated with this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2002-01-16
38631 | 0 | STORA ENSO NORTH AMERICA CORP. |  |  |  |  | 2002-01-15 15:00 | 2002-01-16 09:56 | 2002-01-18 | DISCOVERY OF A MISSING CESIUM-137 SOURCE AT A PAPER MILL (STORA ENSO NORTH AMERICA CORP.) LOCATED IN WISCONSIN RAPIDS, WISCONSIN During performance of a quarterly inventory on 01/15/02, the licensee discovered that a 200-millicurie cesium-137 source was missing. It was used as part of a fixed volume/density gauge which was mounted on a pipe. Apparently, the unit had been stored in the locked position on the pipe. The licensee reported that a paper machine dismantling project was ongoing near the previous location of the unit. It is currently believed that the unit may either have been moved or dismantled and shipped somewhere. The licensee's investigation is still in progress. (Call the NRC operations officer for a licensee contact telephone number.) * * * UPDATE ON 1/17/02 @ 1711 BY CHAPMAN TO GOULD * * * After further investigation the licensee has determined the source may have been stolen from the site. The licensee has notified the police and Region 3. The device manufacturer will be notified. Notified RDO 3 (Vegel), NMSS EO(Frant) * * * UPDATE ON 1/17/02 @ 1843 BY BREWSTER TO GOULD * * * The licensee reported that they had been advised that an individual working for a contractor took the missing device. They are further investigating the incident. Notified RDO 3 (Vegel), NMSS EO(Frant) * * * UPDATE ON 1/18/02 @ 1513 BY CHAPMAN TO GOULD * * * The licensee after further investigation and coordination with the local police have determined the the missing device was stolen. Continuing investigation is ongoing. Notified Reg 3 RDO (Vegel) and NMSS EO(Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-01-16
38630 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-01-15 09:55 | 2002-01-15 10:14 | 2002-01-15 | UNUSUAL EVENT DECLARED AND EXITED The licensee entered and exited an Unusual Event due to a leak from the Chemical and Volume Control System (CVCS) that was caused by the lifting of a relief valve. During valve maintenance on a line tagged out as isolated, the opening of a valve caused pressure in the line to exceed that of a relief valve, causing flow to the Unit 1 Boric Acid Storage Tank (BAST). The licensee is sampling the tank to ensure operability of the tank. The NRC resident inspector has been informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2002-01-15
38628 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2002-01-10 17:30 | 2002-01-14 08:26 | 2002-01-14 | AGREEMENT STATE REPORT "Troxler Model 3411, Serial No. 9260 with two sealed sources: 8.3 millicurie Cs-137, Serial No. 47-5771; and 40 millicurie Am-241/Be, Serial No. 40-6575, was stolen from a company pickup truck parked in a public parking lot in downtown San Antonio. The gauge had last been used at approximately 12:30 pm and was secured in the bed of the pickup. The operator/driver proceeded to several other jobs during the afternoon. When returning to the truck, parked in a Public Parking Lot, the operator/driver noticed the tailgate in the down position and the gauge case open. The gauge was not in use on this job and was still secured by chain in the rear of the truck. The gauge was stolen by cutting the lock on the transport case and removing the gauge from the case. The gauge's paperwork and standard block were not stolen. A Police Report has been filed with the San Antonio Police Department. The gauge has not been located. A copy of the police report is not yet available. The gauge was recovered by the San Antonio Police Department, who report that they broke up a fight between two men over the gauge on the side of a San Antonio street. The men report that they saw the gauge thrown from the rear of a van traveling down the street. The police notice the radiation symbol on the gauge during the recovery, which occurred during the morning of 01/11/02. Exact time of recovery is not known. Gauge is packaged and being readied by Licensee for shipment to the manufacturer (Troxler - Arlington, Texas) for leak testing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2002-01-14
38627 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-01-11 18:07 | 2002-01-11 23:03 | 2002-01-30 | 24 HOUR REPORT - VALID ACTIVATION OF A TSR REQUIRED SAFETY SYSTEM "At 1807 CST, on 1-11-02 the Plant Shift Superintendent (PSS) was notified of an activation of the Water Inventory Control System (WICS) on #4 autoclave In the C-360 building. Approximately seven minutes into the heat cycle the Hi Primary and HI Secondary Condensate alarms were received, and the autoclave went into containment as designed. The operators investigated the alarm with assistance from the Shift Engineer. Due to the alarm being received on the redundant Primary and Secondary probes at a point in the heat cycle when there is a high steam demand. Engineering determined this to be a valid activation of the system. The autoclave was removed from service and the WICS was declared inoperable. Further investigation will be performed by the System Engineer and Instrument Maintenance to determine the exact cause of the alarm. The purpose of the WICS is to limit the amount of water In the autoclave and is a safety system required by TSR 2.1.4.3. "The PSS determined that this event is a 24 Hour Event Report due to the valid activation of a TSR required safety system. "The NRC Senior Resident Inspector has been notified of this event." * * * UPDATE ON 1/30/02 @ 1357 BY BEASLEY TO GOULD * * * RETRACTION UPDATE 1-30-02: THIS EVENT HAS BEEN RETRACTED. Subsequent troubleshooting and analysis, led by the system engineer concluded that the WICS activation was initiated by an invalid signal (electrical short), and therefore the reporting criteria is not met. During troubleshooting It was discovered that the shielding on the primary probe's wire connector was worn. This allowed the wire to come into contact with the side of the connector causing it to short and actuate the WICS alarm. The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2002-01-11
38626 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2002-01-04 09:32 | 2002-01-11 18:14 | 2002-01-11 | INVALID ACTUATION OF PARTIAL GROUP II ISOLATION "While performing Post Maintenance Testing (PMT) on Primary Containment Isolation Valve (PCIV) 2-9208A (Unit 2 Drywell Air Sample Valve) a fuse in the control circuit blew when the 2-9208A valve was given an open signal. This caused a partial Group II Isolation (Invalid Actuation) consisting of a loss of indication to 14 PCIVs and the automatic closure of 11 PCIVs. Additionally the Traversing In-Core Probes (TIP) automatically retracted and the 5 associated ball valves closed. "All plant systems responded as expected for the fuse opening. The fuse was replaced and the PCIVs that repositioned were returned to their normal position. The 2-9208A was removed from service. TIP runs were restarted. This event did not have any adverse effect on plant operation. "Troubleshooting found a shorted wire connection in the junction box for the 2-9208A solenoid. The wire connection was repaired and the 2-9208A valve PMT was performed satisfactorily." The licensee notified the NRC Resident Inspector. | 0 | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-01-11
38625 | 0 | U.S. AIR FORCE |  |  |  |  | 2002-01-10 | 2002-01-11 15:50 | 2002-01-11 | UNKNOWN CONDITION OF SOURCES ON HELICOPTER THAT CRASHED On 1/10/02 a H-60 US Air Force helicopter crashed north of Santa Fe, NM during a rescue effort. The helicopter has 6 IBIS (In-flight Blade Inspection System) indicators, each containing 500 microcuries of Sr-90. The condition and actual location of the sources is unknown at this time. Teams will be out this weekend to access the crash site and try to locate the sources as part of the recovery efforts. The NRC Region 4 contact (Tony Gains) will be notified by the US Air Force. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2002-01-11
38623 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2002-01-11 09:15 | 2002-01-11 11:23 | 2002-01-11 | OFF-SITE SIRENS INOPERABLE IN YORK COUNTY "TMI is notifying the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(xiii) that a major loss of emergency preparedness capabilities for TMI has occurred. At 9:15 AM on Friday, January 11, 2001 during a test of all of the emergency sirens for the five (5) risk counties around TMI, it was determined that the public emergency sirens for York County did not activate. Attempts to return the sirens to an operable status within 1 hour were unsuccessful. The sirens are currently inoperable. "The apparent cause of the siren failure was a serial port failure on the computer that activates the York County signal transmitter. Therefore, no signal was transmitted to the 34 sirens for York County. Troubleshooting is in process to determine the exact cause of the failure. "The siren test covered all of the five (5) risk counties around TMI. All of the public emergency sirens for the other four risk counties for TMI (Cumberland, Dauphin, Lancaster and Lebanon) activated with the exception of a single siren in Lancaster County. The inoperability of sirens for one-(1) of the five (5) risk counties around TMI impacts a large segment of the population. (continued on next page) "This event meets the criteria set forth in NUREG 1022 for a major loss of emergency offsite communications capability. The site Sr. Resident Inspector has been informed of the event and the 8-hour report. The Pennsylvania Emergency Management Agency (PEMA) has been notified of the event. York County Emergency Management is aware of the event and has contacted the siren vendor. The siren failure event is being entered into the TMI-1 corrective action program." The licensee notified the NRC Resident Inspector as well as state and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-01-11
38622 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2002-01-11 04:00 | 2002-01-11 05:12 | 2002-01-11 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO # 2A EMERGENCY DIESEL GENERATOR NOT OPERATING PROPERLY. "A unit shutdown was initiated at 0400 on 01/11/02 as required by Technical Specifications. Technical Specification Action Statement 3.8.1.1.b action b was entered at 0303 on 01/08/02 for scheduled maintenance on the 2A emergency diesel generator. During post maintenance testing, oscillations associated with the generator voltage control system were observed. The cause of the voltage oscillations has not been identified or corrected. Troubleshooting activities are on-going in an attempt to identify the cause. "The 2B and 2C emergency diesel generator surveillance tests were performed within 24 hours to evaluate for common cause failures. A Common Cause Failure was not identified and the 2B and 2C surveillance tests were performed satisfactorily. "Salem Unit Two will be in Mode 3 by 0930 on 01/11/02 and in Mode 5 by 1503 on 01/12/02 as required by Technical Specifications. "Salem Unit one is not affected by this event and remains in Mode 1 at 100%" The NRC Resident Inspector was notified of this event notification by the licensee. | 0 | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2002-01-11
38621 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2002-01-10 12:30 | 2002-01-10 16:01 | 2002-01-10 | 'B' COMPONENT COOLING WATER (CCW) PUMP DECLARED INOPERABLE On 1/9/02 during the shift of CCW pumps from train 'B' to train 'A', the operator noted that the casing temperature on the 'B' CCW pump increased after the 'A' CCW pump was started. Engineering evaluation and testing on 1/10/02 led to the conclusion that the 'A' CCW pump overpowers the 'B' CCW pump when they are run in parallel. The 'B' CCW pump is in effect "dead-headed" when the pumps are operated in parallel, which would lead to failure during extended operation. The 'B' CCW pump control switch has been placed in pull-to-lock to make it inoperable. Consequently, the plant is in the technical specifications limiting condition for operation for an inoperable CCW pump. This condition is reported due to the potential for a complete loss of CCW, an engineered safeguards feature. This is based on the assumption that the "dead-headed" pump would eventually fail and the subsequent failure of the only available CCW pump, resulting in a complete loss of CCW. These assumptions are consistent with the Kewaunee's design basis. "Additionally, this report is also being used to notify NRC that Kewaunee submittal according to the requirements of NRC Bulletin 88-04, "Potential Safety Related Pump Loss." Kewaunee's submittal indicated the CCW system was not vulnerable to this particular type of system failure." The plant's engineering and management staff are continuing to review the event and determine what corrective actions will be necessary to support continued plant operation. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-01-10
38620 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2002-01-09 14:12 | 2002-01-09 18:08 | 2002-01-09 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO POTENTIAL JET PUMP FAILURE The following text is a portion of a facsimile received from the licensee: "At 1412 [CST], Unit 1 experienced indication of Jet Pump #19/20 failure based on the following plant indications: a) Gross Megawatt Electric decrease[,] b) Reactor Pressure decrease[,] c) Total Core Flow Indication increase[, and] d) Core Plate dP decrease[.]" "At 1442 [CST], the 1B Recirculation Pump tripped - the cause of this trip is unknown at this time. Based on indication of Jet Pump [#]19/20 failure, the plant entered Tech Spec 3.4.2, Condition A, at 1521 [CST], requiring the unit to be placed in Mode 3 within 12 hours. A plant shutdown is in progress. No other related surveillances were in progress at the time. All other equipment is operating as expected with all ECCS equipment available on Unit 1." "Unit 1 has been operating with a minor fuel leak, which has been suppressed, since December 22, 2001. Steam line radiation levels increased and subsequently decreased, and the SJAE Radiation Monitors show a minor spike and return to near pre-event values. Main Chimney Radiation Monitors show no change in station effluent release rate to the environment. No estimate of return to service for the unit is available at this time." The licensee notified the NRC resident inspector. | 15 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2002-01-09
38618 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-01-08 09:08 | 2002-01-08 17:25 | 2002-01-17 | DISCOVERY OF A POTENTIAL UNANALYZED CONDITION INVOLVING AN APPENDIX R SAFE SHUTDOWN FIRE ANALYSIS The following text is a portion of a facsimile received from the licensee: "While investigating fire risk scenarios associated with the auxiliary feedwater system (see EN #38541), a potential unanalyzed condition involving an Appendix R safe shutdown fire analysis was discovered. The problem involves the availability of sufficient AFW flow capacity for a fire in the Central 26' and 46' areas of the Primary Auxiliary Building (Fire Area A01-B/Fire Zones 187 [and] 237)." "Cables and equipment associated with all [four] AFW pumps (both turbine- and motor-driven pumps) are located in this fire area. A fire in this area could potentially cause a loss of normal Steam Generator instrumentation for both units. This would require shutdown of both units. An alternate cable routing is available for only the Red channel of instrumentation. This channel is only available for the 'B' train steam generators. Therefore, the present Appendix R Safe Shutdown Analysis assumes this shutdown would be accomplished using the 'B' steam generators for each unit and the P38B motor-driven AFW pump, which feeds the 'B' steam generator in each unit, along with the use of manual actions to mitigate the fire damage to cables associated with valves and instruments. The nominal capacity of this AFW pump is 200 GPM." "An Appendix R calculation shows that approximately 200 gal/min is required during the initial start-up of AFW flow to maintain sufficient heat removal capability for one unit. Under the current conditions with procedural controls, only the one motor-driven AFW pump is made available, [and] there may not be enough capacity to provide adequate decay heat removal for both units. Without sufficient AFW flow, the Appendix R performance requirement of 10 CFR [Part] 50, Appendix R III.G.L.2.c, which requires the reactor heat removal function shall be capable of achieving and maintaining decay heat removal, may not be met. This condition is potentially an unanalyzed Appendix R situation." "As a compensatory measure, fire rounds are being conducted in the fire areas affected." The licensee notified the NRC resident inspector. * * * UPDATE @ 1349 ON 1/17/02 BY RODE TO GOULD * * * RETRACTION At 1625 CST on January 8, 2002, ENS Event Notification #38618 was made in accordance with 10 CFR 50.72(b)(3)(ii)(B) for identification of a potential unanalyzed condition involving the Appendix R safe shutdown fire analysis. The notification involved a concern with the availability of sufficient auxiliary feedwater (AFW) flow capacity for a fire in the Central 26' and 46' areas of the Primary Auxiliary Building (Fire Area A01 -B/ Fire Zones 187 & 237). The information documented in the SSAMS (Safe Shutdown Analysis Management System) database, indicated that the Appendix R fire scenario for Fire Area A01-B relies on the use of a single motor driven AFW pump (P-038B) to provide RCS decay heat removal for both units. The design capacity of P-038B is approximately 200 gpm @ 1,300 psi. An Appendix R Calculation demonstrates that approximately 200 gal/min is initially required during fire safe shutdown to maintain sufficient heat removal capability for each Unit. Therefore, P-038B, alone, does not provide sufficient decay heat removal capacity for both units. Upon closer examination of the analyses and documentation supporting the SSAMS, we have identified that this was not an unanalyzed condition but was due to a SSAMS documentation error. A PBNP Manual Action Feasibility Report (FPTE-012) had evaluated the feasibility of the use of two separate sets of aux. feed water pumps for fires in different areas of Fire Area A01-B. That report documented the capability for manually operating the steam supply valves to start the turbine driven pumps (each with a capacity in excess of 400 gpm which can be aligned to the unit's B' steam generators) for a fire in Fire Zones 187-199. For the fire in Fire Zone 237, the electric driven pumps can be manually aligned to the 'B' steam generators using the available cross-connect (i.e., opening valves AF-30 and AF-43). The two electric pumps provide a total capacity of 400 gpm, which is sufficient decay heat removal capacity for both units. This information was inadvertently omitted from the SSAMS database. Based on this more complete information, we have concluded that an unanalyzed condition did not exist and are retracting our event notification. The NRC Resident Inspector was notified. Region 3 RDO (Vegel) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-01-08
38617 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2002-01-08 13:05 | 2002-01-08 14:47 | 2002-02-21 | SLOW RESPONSE TIME DURING A HIGH PRESSURE COOLANT INJECTION (HPCI) PUMP TIME RESPONSE SURVEILLANCE The following text is a portion of a facsimile received from the licensee: "On 01/08/02 at 1305 hrs, while performing a HPCI pump time response surveillance, the HPCI pump achieved rated pressure and flow in 31.5 seconds. This exceeded the acceptance criteria of <29 seconds. HPCI was declared inoperable due to this surveillance failure. Plant personnel are evaluating the data to determine the cause of the failure. All other [emergency core cooling system (ECCS)] equipment and [reactor core isolation cooling (RCIC)] are operable. This is being reported under 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC resident inspector. * * * UPDATE 1235EST ON 2/21/02 FROM PATRICK FALLON TO S. SANDIN * * * The licensee is retracting this report based on the following: "Upon further evaluation, it has been determined that the apparent slow HPCI response time obtained on 1/8/02 is not reportable. No specific equipment degradations or system malfunctions were identified that could have led to the delay in the system response time obtained on 1/8/02. Following additional testing and discussions with an outside equipment expert it was concluded that the HPCI system response time is a function of the time that the HPCI combined hydraulic and lubricating oil system has been in standby. Specifically, the time for the ramp generator to start, allowing steam admission to the turbine, is dependent on oil system pressurization, and is a function of the time that the oil system has been in standby. This is due to oil system drain down during system inactivity, the bulk of which occurs in the first few days. "The response time of 31.5 seconds obtained on 1/8/02 followed approximately 41 days of oil system inactivity. Subsequent runs on 1/10/02 and 1/12/02 resulted in response times of 25.7 and 24.7 seconds, respectively. The period of oil system inactivity prior to these two runs was very short, resulting in quicker oil system pressurization, and thus a shorter delay in the start of the ramp generator. "Although the acceptance criteria for this test specified in the Technical Requirements Manual (TRM) and in plant procedures was 29 seconds, the analyzed limit for HPCI injection to the vessel is actually 60 seconds. Thus, the response time of 31 .5 seconds obtained on 1/8/02 was well within the analyzed limit (60 seconds), less an allowance for instrument and sensor response time (5 second). Therefore, the high pressure injection safety function was maintained and this event is not reportable. Consequently, this notification is being retracted. " The licensee informed the NRC Resident Inspector. Notified R3DO(Jorgensen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-01-08
38616 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2002-01-08 12:55 | 2002-01-08 13:08 | 2002-01-08 | POSITIVE RANDOM FITNESS-FOR-DUTY TEST A contract supervisor tested positive for cocaine during a random fitness-for-duty test. The individual's site access has been denied, and a review of the individual's work activities is underway. (Contact the NRC operations officer for additional event details and for a site contact telephone number.) The licensee notified the NRC Region 1 office (John Ray) and the State Department of Environmental Protection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0 | 2002-01-08
38615 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2001-12-17 | 2002-01-08 12:10 | 2002-01-08 | AGREEMENT STATE REPORT "Event Report ID No.; LA010019 "License No.: LA-4440-L01 "Licensee: Holden X-Ray Service "Event date and Time: 12/17/01 at 14:27. Report faxed to Holden "Event Location: NA "Event type: Excessive-exposure to Industrial Radiographer "Notifications: Holden X-Ray notified the Department. The letter is dated December 26, 2001. The Department received the letter on January 3, 2002. I received a copy of the letter on January 7, 2002. "Event description; [individual] received a Deep dose of 6873 mrem, Lens dose of 6873 mrem, and a shallow dose of 6629 mrem as of November 9, 2001 for the 2001 year. He was using Iridium 192 with source strengths up to 93 Curies. [Individual] was working a lot towards the end of the year." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2002-01-08
38614 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2002-01-04 | 2002-01-08 10:09 | 2002-01-08 | AGREEMENT STATE - MEDICAL MISADMINISTRATION Patient was undergoing a Pterygium treatment to the eye lid on January 4, 2002. This was the 3rd session and it was to be a 44 second session delivering a dose of 1,000 rad. A nurse, who was timing the exposure using a stop watch, was distracted by all the activity going on in the area and the exposure actually lasted one minute and 49 seconds. A dose of 2,480 rads was delivered a 148% overexposure. The patient and the physician have been notified. Worst case is that the patient's eye may have some scar tissue form. Licensee is buying new stop watches with audio alarms and is giving in-service training to nurses. This office was notified the on January 4, 2002 by phone. Licensee will submit a written report within 15 days. Further action is referred to Radioactive Materials. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-01-08
38613 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2002-01-08 01:20 | 2002-01-08 03:15 | 2002-01-08 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO AN AREA DOOR. A safeguards system degradation related to an area door was discovered. Compensatory measures were put in place within 10 minutes. (Contact the HOO for additional information.) The NRC Resident Inspector will be notified. ***** RETRACTION FROM ANDREW OHRABLO TO LEIGH TROCINE AT 1727 EST ON 01/08/02 ***** The licensee is retracting this event notification because it was determined to be loggable only. (Contact the NRC operations officer for additional details.) The following text is a portion of a facsimile received from the licensee: "Additionally, the power level stated on the original event notification was 100%. Power level both before and after was 94%." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Chuck Cain). | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0 | 2002-01-08
38612 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2002-01-06 13:45 | 2002-01-07 11:52 | 2002-01-07 | 24-HOUR NRC BULLETIN 91-01 REPORT (VOLUNTARY) "Water Leak in Burnable Absorber Expansion System Modcon Area January 6, 2002 "Reason for Notification At the time of the event, the Team Leader of the Burnable Absorber Expansion System called the cognizant Nuclear Criticality Safety (NCS) engineer to inform that the roofs over the moderation control (Modcon) area in the erbia blending area had developed a small water leak. "As Found Condition A summary of the as found conditions is as follows: * No operations were being performed in the erbia blending area. * The leak was small trickle of water that ran down a structural I-beam and puddled onto the floor. * The water was not dripping onto any process equipment. * The erbia blender was empty (contained no SNM), and the blender and all bulk containers were tightly closed. * The leak stopped by approx. 17:00 hours. * The total amount of leakage was approx. 2 gallons (7.6 liters)of water over approx. 5 hours. "Double Contingency Protection Double contingency protection for the erbia blender and bulk containers is based on moderation control (prevent greater than 20.48 liters of water equivalent from entering blender/container). It was determined that double contingency protection remained for the system. It is also noted that at no time was greater than the safety limit of moderator involved. Therefore the incident does not technically require notification in accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3. However, the decision was made to provide this notification since it was considered to be a serious 'near miss'. "Summary of Activity * The incident was discussed thoroughly between the Team Manager and thc NCS engineer by phone as soon as the leak was discovered. * The NCS engineer made the preliminary determination that double contingency protection remained. * The NCS engineer then came to the plant, inspected the area of the leak with Operations, applied the incident to the previously documented fault tree analysis of the system, and confirmed that double contingency remained. "Conclusions * Loss of double contingency protection did not occur. * Partial degradation of the controls did occur. * Detection and corrective actions were effective in preventing ~y water from becoming available to the blender or bulk containers. * At no time was greater than a safe limit of moderator involved. * At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. * The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. An apparent cause analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2002-01-07
38611 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2002-01-06 14:10 | 2002-01-06 21:42 | 2002-03-01 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE During the performance of the quarterly valve surveillance test for the HPCI system, a testable check valve, 1FD-V032, related to the HPCI Barometric Condenser Discharge Line, failed. This failure rendered the HPCI system inoperable at 1410 EST on 01/06/02. The licensee entered an active 14 day Limiting Condition of Operation that expires on 01/20/02 at 1410 EST. All other safety systems are operable. Current plans to return plant to normal configuration include the development of corrective maintenance work package. The NRC Resident Inspector will be notified of this event by the licensee. ***3/1/02 0952 Event was retracted by Licensee; Jim Priest to Mike Norris.*** "PSEG Nuclear retracts the event notification made on 1/6/02 (event number 38611). "Barometric condenser condensate pump discharge check valve 1 FD-V032 was opened and inspected. The valve internals were cleaned and the valve was reassembled and retested satisfactorily. "Subsequent evaluation determined that failure of 1 FD-V032 to close would not have prevented the HPCI system from performing its safety function. Reverse flow through 1 FD-V032 would not degrade the flow that HPCI supplies the reactor vessel during a postulated accident. "Since the HPCI system remained capable of performing its safety function, this event is not reportable. "The NRC Resident Inspector has been notified of this event by the licensee." Notified R1DO (Linville) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-01-06
38610 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-01-06 05:15 | 2002-01-06 08:43 | 2002-03-05 | EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE At 1347 on 1/4/2002, the "A" emergency diesel generator (EDG) was declared inoperable due to tube degradation identified in the lube oil, intercooler and jacket water heat exchangers. Technical Specification 3.8.1 was entered, the affected heat exchanger tubes were plugged and the "A" EDG was restored to operable status at 1134 on 1/5/2002. At 1301 on 1/5/2002, the "B" EDG was taken out of service to perform inspections of its lube oil, intercooler, and jacket water heat exchangers. Inspection of the heat exchanger tubes and analysis of the inspection data found similar results, subsequently resulting in the need to plug heat exchanger tubes to restore the "B" EDG to operable status. Based upon the similarity and extent of the tube degradation in both the "A" and "B" EDG heat exchangers, prior to implanting the tube plugging corrective action, the possibility exists that the degradation of the EDG heat exchangers' tubes could have prevented the fulfillment of the safety function of the onsite standby class 1E power source following a design basis earthquake. The NRC Resident Inspector was notified. * * * UPDATE ON 01/06/02 AT 1927 EST BY HUBBARD TAKEN BY MACKINNON * * * "B" EDG was restored to operable status. R4DO (B. Spitzberg) notified. The NRC Resident Inspector was notified. * * * RETRACTED AT 1826 EST ON 3/5/02 BY STEVE HENRY TO FANGIE JONES * * * Subsequent evaluation of the heat exchangers by the licensee determined that the degradation was not severe enough to interfere with the proper operation of the EDGs. The licensee is retracting the event notification, as the EDGs were operational and fully available. The licensee notified the NRC Resident Inspector. The R4DO (Linda Smith) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-01-06
38609 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2002-01-05 17:50 | 2002-01-05 23:33 | 2002-01-22 | DISCOVERY THAT PROPANE TANKS ON SITE EXCEEDED THE VOLUME ASSUMED IN THE CONTROL ROOM HABITABILITY TOXIC GAS ANALYSIS The following text is a portion of a facsimile received from the licensee: "Propane tanks on site exceeded the volume assumed in the toxic gas analysis for control room habitability. The analysis assumes 1,000 gallons were available for release. Instead, there were two locations were two 1,000-gallon tanks were available for release (filled with propane on January 4th and then emptied on January 4th). Upon determination that the 1,000-gallon limit was exceeded, the control room outside air intake dampers were closed and remained closed until the tanks were emptied. Reanalysis (completed today) assuming a release of 2,000 gallons results in the calculated concentration of propane in the control room exceeding the acceptance criteria." The licensee stated that there was nothing unusual or misunderstood and that all systems functioned as required. The licensee plans to notify the NRC resident inspector. * * * RETRACTED AT 1636 EST ON 1/22/02 BY ANDREWS TO FANGIE JONES * * * "The event reported on January 5, 2002 (Propane tanks on-site exceeded the volume assumed in the toxic gas analysis for the control room. NRC Event Number 38609) is hereby retracted. "Subsequent analysis (via updated methodology, consistent with the guidance in the proposed Revision 1 to Reg Guide 1.78, 'EVALUATING THE HABITABILITY OF A NUCLEAR POWER PLANT CONTROL ROOM DURING A POSTULATED HAZARDOUS CHEMICAL RELEASE') has demonstrated that the maximum propane concentration in the control room would be well below the acceptable level. "Thus, although the plant had been in an unanalyzed condition, that condition has now been shown to have not significantly degraded plant safety and is, therefore, not reportable under the requirements 10 CFR 50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. The R3DO (Sonia Burgess) has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2002-01-05
38608 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-11-05 02:47 | 2002-01-04 16:12 | 2002-01-04 | GROUP SIX ISOLATION (60-Day Report) The following text is a portion of a facsimile received from the licensee: "Event Date: 5 Nov 2001" "Event Time: 0247 CST" "Description:" "a. This telephone report is being made under 10CFR50.73(a)(2)(iv)(A)." "While performing installation work inside an energized isolation relay cabinet in the cable spreading room, a wire was accidentally grounded and the power supply fuse blew causing [an] inadvertent Group Six isolation." "b. A Group Six isolation actuation was received consisting of the following systems[:] * Isolation of Primary Containment Vent and Purge system[,] * Tripped Reactor Building Ventilation Fans[,] * Isolation of Reactor Building Ventilation system[,] * Isolation of Recirculation MG Set Ventilation system[,] * Started Standby Gas Treatment system[, and] * Open Reactor Equipment Cooling system Critical Loop Isolation Valves[.]" "c. The train actuations were [partial. The] position of seven ventilation system valves associated with Reactor Building Ventilation and Recirculation MG Set Ventilation were not verified due to a loss of position indication resulting from the blown fuse. Primary and Secondary Containment were not required for the plant conditions." "d. All systems operated as expected for a loss of power event." "The following also occurred due to the loss of electrical power[:] * Division two valves associated with a Group Two isolation of the Drywell Ventilation Radiation Monitoring sample supply and return failed closed due to the loss of electrical power. There was no Group Two actuation signal." "These are expected actions for the loss of power event that occurred." The licensee plans to notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2002-01-04
38607 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2002-01-02 12:30 | 2002-01-02 21:34 | 2002-01-04 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM (SPDS) At 1230CST SPDS was lost for reasons unknown. Troubleshooting is currently in progress. The licensee informed the NRC Resident Inspector. * * * Update on 01/04/02 at 1118EST by Rick Hubbard taken by S. SANDIN * * * SPDS was restored to service at 2229CST on 01/03/02. R4DO (B. Spitzberg) notified. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-01-02
38606 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-01-02 11:52 | 2002-01-02 12:47 | 2002-01-02 | 4-HOUR REPORT DUE TO EPA NOTIFICATION REGARDING AN OPACITY VIOLATION The #3 High Pressure Blower on Boiler #3 tripped due to a suspected equipment malfunction causing a pollutant discharge exceeding the 20% opacity limit in any one hour period specified by EPA to occur between 0915 and 0921EST. Operations notified the NRC Resident Inspector and the Ohio Environmental Protection Agency (OEPA) of the violation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-01-02
38605 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2002-01-02 01:50 | 2002-01-02 09:48 | 2002-01-02 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) IS OUT OF SERVICE The SPDS has not been functioning since 01:50. It has been operable for about one hour, but they are still monitoring it before they determine it to be completely operable. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-01-02
38604 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2002-01-02 03:05 | 2002-01-02 04:56 | 2002-01-02 | MANUAL REACTOR TRIP DUE TO DECREASING STEAM GENERATOR WATER LEVEL. During a plant start-up at 7% reactor power, feedwater oscillations occurred on all three steam generators. At 0215 on 01/02/02 the main feedwater regulator bypass valves were placed in manual control to stabilize level. The bypass valves were then returned to automatic control at 0245 on 01/02/02, and the oscillations continued within the normal operating band of 52-62%. At 0300 0n 01/02/02. The Control Operator noted lowering level on the "C" steam generator at approximately 55% with indication that the "C" main feedwater regulator bypass valve was shut. The operator placed the "C" bypass valve in manual control and attempted to open the valve with no response noted in valve position indication. At 30% indicated level in the "C" steam generator and a lowering trend, the Unit Shift Control Operator ordered a manual reactor trip prior to receipt of a steam generator low water level trip signal at 25%. All safety systems functioned as expected. Both Motor Driven Auxiliary Feedwater Pumps automatically actuated on the subsequent 'C" steam generator low water level signal. All rods fully inserted into the core and the electrical grid is stable. An investigation into what caused this event is in progress. The NRC resident inspector was notified of this event by the licensee. | 0 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2002-01-02
38603 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2002-01-01 21:32 | 2002-01-01 22:36 | 2002-01-01 | 4-HOUR REPORT DUE TO EPA NOTIFICATION REGARDING AN OPACITY VIOLATION The M4 electrical feeder was lost causing instrumentation associated with Boiler #3 control to deenergize. This resulted in pollutant discharge exceeding the 60% opacity limit specified by EPA to occur between 1620 and 1720EST. Operations notified the Ohio Environmental Protection Agency (OEPA) of the violation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2002-01-01
38602 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2002-01-01 09:19 | 2002-01-01 10:08 | 2002-09-19 | OFFSITE NOTIFICATION DUE RESCUED SEA TURTLE EN #37902 started the biennial report period. On January 1, 2002 at 0919, a rescued sea turtle was identified as a green sea turtle. This is the 62nd rescue of a live sea turtle at Crystal River Unit 3 (CR-3) in this biennial period. Notification to the National Marine Fisheries Service and the Florida Fish and Wildlife Conservation Commission. The licensee intends to notify the NRC Resident Inspector. * * * UPDATE ON 1/05/02 @ 1002 BY RAWLS TO GOULD * * * On January 5, 2002, at 0720, a rescued sea turtle was identified as a Loggerhead Sea Turtle. This is the 63rd rescue of a live sea turtle at Crystal River Unit 3 (CR3) in this biennial period. This is reportable as a 4-hour report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. The NRC Resident Inspector was notified. Reg 2 RDO (Decker) was notified. * * * UPDATE ON 01/09/02 @ 1107 EST BY ANDY BARNES TAKEN BY MACKINNON * * * On January 9, 2002, at 0838, a rescued sea turtle was identified as a Kemp's Ridley Sea Turtle. This is the 64th rescue of a live turtle at Crystal River Unit 3 (CR-3) in this biennial period. This is reportable as a 4-hour 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. The NRC Resident Inspector was notified. Reg 2 (Brian Bonser) was notified. * * * UPDATE ON 02/17/02 at 0940 EST BY RICKY RAWLS TO FANGIE JONES * * * "On February 17, 2002 at 0820, a rescued injured sea turtle was identified as a Kemp's Ridley Sea Turtle. The injury will require transportation to Clearwater Marine Science Center or Florida Fish and Wildlife Conservation Refuge. The Injury appears to be from a boat propeller. This is the 65th rescue of a live sea turtle at Crystal River Unit 3 (CR-3) in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This Is an update to event 38602." The NRC Resident Inspector will be notified. R2DO (Stephen Cahill) has been notified. * * * UPDATE ON 03/01/02 AT 1122 EST BY RICKY RAWLS TO GERRY WAIG * * * "On March 1, 2002 at 0952, a healthy rescued sea turtle was identified as a Green Sea Turtle. This is the 66th rescue of a live sea turtle at Crystal River Unit 3 (CR-3) in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The NRC Resident Inspector was notified. R2DO (Julian) was notified. * * * UPDATE ON 03/07/02 AT 1114 EST BY CHUCK MORRIS TO MIKE NORRIS * * * "On March 7, 2002 at 0835, two healthy sea turtles rescued at CR#3 were identified as Green Sea Turtles. These are the 67th and 68th live sea turtle rescues at the Crystal River Energy Complex in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The NRC Resident Inspector was notified. R2DO (Henson) was notified. * * * UPDATE ON 04/02/02 at 0408 EST BY RICKY RAWLS TO FANGIE JONES * * * "On April 2, 2002 at 0236, two sea turtles previously rescued at CR#3 intake area were identified by FPC Mariculture staff as Kemp Ridley Sea Turtles. One of the turtles appears to be in distress and may require transportation to Clearwater Marine Science Center of Florida Fish and Wildlife Conservation Refuge. These are the 69th and 70th live sea turtle rescues at the Crystal River Energy Complex in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The NRC Resident Inspector will be notified. The R2DO (Carolyn Evans) was notified. ***** UPDATE AT 1023 EDT ON 05/19/02 FROM PELLERIN TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "On May 19, 2002, at 0916, a sea turtle previously rescued at CR#3 intake area was identified by FPC Mariculture staff as Green Sea Turtle. This is the 71st live sea turtle rescue at the Crystal River Energy Complex in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The licensee plans to notify the National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission and the NRC resident inspector. The NRC operations officer notified the R2DO (Paul Fredrickson). * * * UPDATE 1816 EDT ON 5/28/02 FROM BERRY FOSTER TO S. SANDIN * * * "On May 28, 2002 at 1700, a sea turtle previously rescued at CR#3 intake area was identified by FPC Mariculture staff as a Green Sea Turtle. This is the 72nd live sea turtle rescue at the Crystal River Energy Complex in this biennial period. The turtle is being transported to the Clearwater Marine Science Center. This is Reportable as a 4-Hour Report under 10 CFR 50.72 (b) (2) (xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The licensee will inform the NRC Resident Inspector. Notified R2DO(Landis). * * * UPDATE 1602 EDT ON 5/31/02 FROM BILL BANDHAUER TO MIKE NORRIS * * * "On May 30, 2002 at 1323, a sea turtle previously rescued at CR#3 intake area was identified by FPC Mariculture staff as a Kemp's Ridley Sea Turtle. This is the 72nd live sea turtle rescue at the Crystal River Energy Complex in this biennial period. (Note: The sequential numbering of the live sea turtle takes has been modified to reflect the actual live sea turtle takes, On 4/02/02, a live rescue of two turtles was reported, however, one of the turtles died and was reclassified as a non-causal mortality, which is non-reportable). This event is Reportable as a 4-Hour Report under 10 CFR 50.72(b) (2) (xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The NRC Resident Inspector has been notified. Notified R2DO (Landis). *****UPDATE AT 13:58 EDT ON 7/18/02 FROM SWEENEY TO LAURA***** An offsite notification to the State regarding a green sea turtle that was rescued from the CR#3 intake area by the FPC Mariculture staff. The NRC resident inspector was notified. Notified R2DO (C. Payne). * * * UPDATE 1126 EDT ON 8/1/02 FROM BILL BANDHAUER TO FANGIE JONES * * * "At 0915 on August 1,2002, a dead sea turtle recovered at the CR#3 intake area was identified by FPC Mariculture staff as a Kemps Ridley Turtle. FPC determined that the cause of death was non-causally related to the operation of CR3. This is the 7th dead Kemps Ridley Turtle recovery at the Crystal River Energy Complex in this biennial period. The threshold for reporting non-causal sea turtle deaths is 6 in a biennial period. This event is Reportable as a 4-Hour Report under 10 CFR 50.72 (b) (2) (xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) will be made. This is an update to event 38602." The licensee intends to notify the NRC Resident Inspector. The R2DO (Mike Ernstes) has been notified. * * * UPDATE 1529 EDT ON 8/8/02 FROM DAN DeBOER TO GERRY WAIG * * * "At 1234 on August 8, 2002, FPC determined that the dead Kemps-Ridley sea turtle recovered at 1930 on May 11, 2002, at the Crystal River Unit 3 intake area was reportable as a 4-Hour Report under 10 CFR 50.72 (b) (2) (xi). This event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been made. At 1347 on May 13, 2002 the FPC Mariculture Center determined that the cause of death was non-causally related to the operation of Crystal River Unit 3. This was the 6th non-causal dead turtle recovery at the Crystal River Energy Complex in this biennial period. The threshold for reporting non-causal sea turtle deaths is 6 in a biennial period. This is an update to event 38602." The licensee notified the NRC Resident Inspector. The R2DO (Claude Julian) has been notified. ***UPDATE 11:10 EDT ON 8/20/02 FROM McCallum to LAURA*** "On August 20, 2002 at 0932, a sea turtle previously rescued at CR#3 intake area was identified by FPC Mariculture staff as a Kemp's Ridley Sea Turtle. This is the 74th live sea turtle rescue at the Crystal River Energy Complex in this biennial period. This event is Reportable as a 4-Hour Report under 10 CFR 50.72(b) (2) (xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The licensee notified the NRC Resident Inspector. The R2DO (M. LESSER) has been notified. * * * UPDATE 1449 EDT ON 09/10/02 FROM BILL BANDHAUER TO G. WAIG * * * "On September 10, 2002 at 1328, a sea turtle previously rescued at CR#3 intake area was identified by FPC Mariculture staff as a Kemp's Ridley Sea Turtle. This is the 75th live sea turtle rescue at the Crystal River Energy Complex in this biennial period. This event is Reportable as a 4-Hour Report under 10 CFR 50.72 (b) (2) (xi) as this event is related to the protection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The licensee will notify the NRC Resident Inspector. The R2DO (Jack Whitten) was notified by the Hq Ops Officer. ****UPDATE 18:35 EDT on 9/19/02 FROM SWEENEY TO LAURA**** "On September 19, 2002 at 1730, a sea turtle was rescued at CR#3 intake area and identified by FPC Mariculture as a Green Sea Turtle. This is the 76th live sea turtle resue at the Crystal River Energy Complex in this biennial period. The event is reportable as a 4-Hour Report under 10 CFR 50.72 (b) (2) (xi) as this event is related to the proptection of the environment for which a notification to other government agencies (National Marine Fisheries Service and Florida Fish and Wildlife Conservation Commission) has been or will be made. This is an update to event 38602." The licensee intends to notify the NRC Resident Inspector. Notified R2DO (Fredrickson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2002-01-01
38601 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2002-01-01 00:42 | 2002-01-01 09:41 | 2002-01-21 | HIGH PRESSURE COOLANT INJECTION (HPCI) TURBINE DETERMINED TO BE INOPERABLE The licensee determined during surveillance testing that the HPCI turbine was inoperable due to the minimum flow valve cycling open and closed due to problem with the associated flow switch. The problem is being worked on. The licensee intends to notify the NRC Resident Inspector. * * * RETRACTED AT 1736 EST ON 1/21/02 BY DAVID MADSEN TO FANGIE JONES * * * "Event Number 38601 reported a condition at Cooper Nuclear Station (CNS) where the High Pressure Coolant Injection (HPCI) was declared inoperable due the minimum flow valve cycling open and closed. This condition occurred during surveillance testing of the HPCI turbine. "This event was reported per 10CFR50.72(b)(3)(v)(D), Accident Mitigation, on the basis that the cycling of the minimum flow valve (when HPCI injection is required) could have resulted in injection flow below that required to maintain fuel integrity during certain transients or accidents. Subsequent investigation found the instrumentation initiating a signal to open the MOV would not reset. The requirement for the minimum flow to open for pump protection was always met. Existing analyses have determined that sufficient margin exists to achieve adequate system flow even if the minimum flow valve is in the full-open position. Also, the additional flow demands on the HPCI pump would not have resulted in a large enough increase in turbine speed that would have resulted in a turbine trip. For the scenario where the valve may have cycled between open and closed position, the HPCI pump control system is capable of handling the change in flow without resulting in a turbine trip. Should HPCI have received a isolation signal or if the turbine was manually tripped, the minimum flow valve would have closed. "Therefore, the above described condition did not result in a loss of safety function for HPCI. Nebraska Public Power District has determined that this event is not reportable under the requirements of 10CFR50.72(b)(3)(v)(D), and as such, Event 38601 is retracted." The licensee intends to notify the NRC Resident Inspection. The R4DO (Dale Powers) has been notified. | 10 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2002-01-01
38600 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2001-12-31 19:22 | 2002-01-01 03:19 | 2002-01-01 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) INOPERABLE The licensee reported that the SPDS display screens were locked up and thus unavailable for use in case of an incident. Several procedures including the Emergency Operating Procedures refer to the displays for information. With the system unavailable for greater than 8 hours a report under loss of assessment capabilities was made. The SPDS is being worked on at this time and is expected back in service in a short period of time. The licensee intends to notify the NRC Resident Inspector. * * * UPDATE 1622EST ON 1/1/02 FROM TOM COBBLEDICK TO S. SANDIN * * * The SPDS was restored to service as of 1615EST. The licensee will inform the NRC Resident Inspector. Notified R3DO(Shear). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2002-01-01
38599 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-12-31 00:10 | 2001-12-31 02:00 | 2001-12-31 | REACTOR TRIP AND SAFETY INJECTION DUE TO SPRAY VALVE FAILING OPEN The unit experienced a reactor trip and safety injection as a result of a pressurizer spray valve (2PS3) failing open. This caused a reactor trip on Overtemperature DeltaT and a safety injection on low reactor coolant system pressure. All emergency equipment responded properly, all safety injection pumps started and all control rods fully inserted. The emergency diesels started, but were not required to load. The auxiliary feedwater pumps started on low steam generator level. The pressurizer spray valve closed when the valve's operating air was isolated. The unit is stable in Mode 3 (Hot Standby) at normal temperature and pressure. Auxiliary feedwater and steam dumps are in use to maintain steam generator level and remove excess heat. An investigation of the failure is underway. The licensee intends to notify the NRC Resident Inspector and the local Township. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2001-12-31
38598 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-12-27 13:21 | 2001-12-27 16:03 | 2001-12-29 | REACTOR SCRAM AFTER TWO RECIRCULATION MOTOR-GENERATOR (MG) SETS TRIPPED DURING THE PERFORMANCE OF ANTICIPATED TRANSIENT WITHOUT SCRAM (ATWS) LOGIC TESTING The following text is a portion of a facsimile received from the licensee: "While performing ATWS logic testing, both [the] 'A' [and] 'B' [recirculation] MG sets tripped, and the reactor was scrammed. The cause of the scram is being determined at this time. All control rods fully inserted on the scram. All safety systems functioned properly during the transient. The plant is in the process of being maneuvered to Cold Shutdown." The licensee stated that the main steam isolation valves remained open and that none of the safety relief valves lifted. In addition, there were no emergency core cooling system actuations, and none were required. The reported engineered safety feature actuation was the actuation of the reactor protection system. The unit is currently stable in Hot Shutdown. Normal condensate and feedwater is being utilized to supply water to the reactor vessel, and the condenser is being utilized as a heat sink. Containment parameters are normal, offsite power is available, and the electrical grid is stable. The emergency diesel generators and engineered safety feature systems are available if needed. The licensee stated that the ATWS logic test procedure was not new and that it had been performed on several occasions in the past. The ATWS logic test was successfully completed for the 'A' side earlier today, and the plant transient occurred during the performance of the ATWS logic test for the 'B' side. The cause of the recirculation MG set trips is currently under investigation. The licensee notified the NRC resident inspector. * * * UPDATED AT 0023 ON 12/29/01 BY ERIC OLSON TO FANGIE JONES * * * The licensee reported the cause of the scram as Average Power Range (APR) Hi-Hi trip caused by a flow control trip reference card signal from the low flow due the trip of both recirc pumps. The NRC Resident Inspector has been informed by the licensee. The R1DO (Michele Evans) has been informed. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-12-27
38597 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-12-16 00:18 | 2001-12-27 14:10 | 2001-12-27 | INVALID PRIMARY AND SECONDARY CONTAINMENT ISOLATION DUE TO A SPURIOUS UPSCALE SPIKE OF REACTOR BUILDING VENTILATION RADIATION MONITOR B (60-Day Report) The following text is a portion of a facsimile received from the licensee: "Event Description" "At 0018 hours on December 16, 2001, with the plant operating at 100 percent of rated thermal power, Reactor Building (Secondary Containment) Ventilation Exhaust Radiation Monitor B spiked upscale and immediately returned to normal." "The radiation monitor upscale spike (trip) resulted in automatic closure of outboard isolation valves and therefore isolation of the following systems or functions: * Primary Containment Drywell and Suppression Chamber pressure sensing for alarm and indication functions only, * Primary Containment Continuous Atmosphere Monitoring (CAM) for particulate and gaseous radioactivity monitoring, and * Primary Containment Hydrogen and Oxygen Analyzer B." "The trip signal also resulted in automatic isolation of the Reactor Building (Secondary Containment) Ventilation system and starting of Standby Gas Treatment subsystem B to maintain the reactor building atmosphere at a slightly negative pressure." "System performance was in accordance with the design. Examination of operating records indicated that the redundant radiation monitor, other monitoring systems, and the plant computer system did not detect any abnormal radioactivity. Shift operating and radiation protection personnel investigated and did not detect any abnormal radiological conditions. Examination of the radiation monitor did not reveal any indication of abnormal operation, and it was concluded that the trip signal had been a spurious invalid signal." "Shift operating personnel completed restoration of the affected systems to normal at 0104 hours, 46 minutes after the event start." "Actions Taken" "1. Verified system response was in accordance with the design. 2. Investigated radiological conditions and determined they were normal. 3. Restored the affected systems to normal." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-12-27
38596 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2001-12-21 20:25 | 2001-12-26 15:39 | 2002-01-17 | INDETERMINATE IF HIGH PRESSURE CORE SPRAY (HPCS) EMERGENCY DIESEL GENERATOR (DG) COULD FULFILL ITS REQUIRED SAFETY FUNCTION. "On 12/21/01, Condition Report 01-4350 was initiated to document the failure of Div . 3 DG to pass SVI-E22-T1319. Specifically, the DG did not come up to frequency/voltage within the required 13 seconds (TS 3.8.1.7.b.2). The DG was declared inoperable and an immediate investigation was requested. The immediate investigation indicated that the cause of the SVI failure was due to the DG governor control switch not being properly set during shutdown on the DG on 12/16/01. In analyzing the shutdown data from the 12/21/01 DG surveillance testing, it was determined that the situation had been corrected, and that the next DG start, the DG would satisfy the TS SR. The DG was started on 12/22/01 and satisfied the SR. The DG was then declared operable. "During this time, it is indeterminate if the HPCS DG could fulfill its required safety function. The immediate investigation infers that an operator error occurred when shutting down the DG on 12/16/01. This error, the mis-operation of the DG governor control switch, prevented the DG from properly coming up to the required frequency/voltage within 13 seconds as identified on 12/21/01. Hence, it is conservative to assume that the capability to perform the safety function was not maintained. This condition is an 8-hour report pursuant to 50.72(b)(3)(v) and (vi). It should be noted that HPCS is a single train system and there are no redundant features within the same system to perform the safety function." The NRC resident inspector will be notified of this event by the licensee. * * * UPDATE ON 1/17/02 @ 1204 BY RUSSELL TO GOULD * * * RETRACTION On 12/26/01, a report was made per 10CFR50.72(b)(3)(v)(D) for the Loss of Safety Function of the High Pressure Core Spray pump, a single train safety system. The cause of the loss of the HPCS pump was the failure of the DIVISION 3 diesel generator to achieve the required frequency. Subsequently, it was determined by further engineering evaluation that the HPCS pump and its supporting systems had sufficient margins available to perform the required safety functions at the reduced frequency. Therefore, no loss of safety function occurred and therefore event notification 38596 is retracted accordingly. The NRC Resident Inspector was notified. The Region 3 RDO (Vegel) was notified. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-12-26
38595 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-12-26 10:16 | 2001-12-26 14:10 | 2001-12-26 | PLANT EMPLOYEE TESTED POSITIVE FOR ILLEGAL DRUGS An electrical licensee tested positive for marijuana during a random drug test. The employee's access to the plant has been pulled and his past work is being reviewed. Call the Headquarters Operation Officer for further details. The NRC resident inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.73 |  |  |  | 0 | 2001-12-26
38594 | 0 | CBC ENGINEERS AND ASSOCIATES |  |  |  |  | 2001-12-26 | 2001-12-26 11:52 | 2001-12-26 | TROXLER GAUGE STOLEN FROM CBC ENGINEERS AND ASSOCIATES OF DAYTON, OHIO A Troxler gauge model #3430 serial # 29017 which was locked in a truck was stolen along with the truck from the driver's residence in Whitesville, West Virginia. The gauge contained 8 mCi of Cs-137 and 40 mCi of Am-241/Be. The W Va State Police were notified and the licensee will contact the local fire department along with the media to offer a reward. * * * UPDATE ON 12/26/01 @ 1237 BY BANNER TO GOULD * * * The vehicle was found in West Virginia with Troxler gauge intact. Notified Reg 2 (Boland), Reg 3 (Clayton) and NMSS (Brown) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | WV | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-12-26
38593 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-12-26 07:20 | 2001-12-26 08:52 | 2001-12-26 | REACTOR TRIP FROM 100% POWER DUE TO TURBINE TRIP The plant had an auto stop oil pressure trip on the main turbine followed by a reactor trip from 100% power. The plant went into natural circulation for 1 hour at which time the #24 reactor coolant pump was put in service. Auxiliary feedwater was placed in service. Partial offsite power was lost and the three EDG's auto started and powered buses "2A" and "3A". The cause of the trip is being investigated. All rods fully inserted, no ECCS was initiated and no safety relief valves lifted, however, the atmospheric dump valves were opened to vent steam from the system. The plant is stable and in hot shutdown. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-12-26
38592 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-12-25 18:19 | 2001-12-25 20:40 | 2001-12-27 | AUTOMATIC REACTOR SCRAM DUE TO 'A' RECIRCULATION PUMP SPEED UNEXPECTEDLY INCREASING "At 18:19 Eastern on 12/25/01, Hatch Nuclear Plant Unit 2 reactor tripped. The cause is presently under investigation. Preliminary indications are that the 'A' Recirculation Pump speed increased. Reactor power increased causing the all four channels in the Neutron Monitoring System to trip. Group 2 Primary Containment isolation occurred. All group 2 isolated as expected. No other group isolations were required. RFPTs were used to maintain reactor water level, and Main Turbine Bypass valves maintained reactor pressure. No initiation signals required ECCS or RCIC to initiate." On the automatic reactor scram, one control rod inserted to the 01 position and drifted to the 00 position. The swing Emergency Diesel Generator, 1B, is degraded but fully operable. The only other problem was that the Main Generator Output breakers did not automatically open but were manually opened from the control room. This problem has occurred before, and the control room operators are watching the output breakers. The NRC resident inspector was notified of this event by the licensee. ***** UPDATE FROM GUY S. GRIFFIS TO LEIGH TROCINE AT 1217 ON 12/27/01 ***** This update was made to correct/clarify the cause of the automatic reactor scram from 100% power and to provide additional information. It was initially reported that 'A' recirculation pump speed increased and caused all four channels in the neutron monitoring system to trip. However, further review determined that decreased main steam line 'B' flow caused the neutron monitoring system trip due to increased flux. Initial diagnostics indicate the 2B21-F028B main steam isolation valve as the failure. The licensee's investigation is still ongoing. The licensee plans to provide additional detailed information in a Licensee Event Report. NOTE: Cold Shutdown was achieved at 0255 on 12/27/01 in compliance with Technical Specification 3.6.1.3.e. The licensee notified the NRC resident inspector. The NRC operations officer notified the R2DO (Boland) and IRO (Holonich). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-12-25
38591 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2001-12-24 07:22 | 2001-12-24 09:39 | 2001-12-24 | SECURITY REPORT Unaccounted for security weapon, immediate compensatory measures taken on discovery. The licensee intends to notify the NRC Resident Inspector. Refer to the HOO Log for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-12-24
38590 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-12-22 15:42 | 2001-12-22 19:20 | 2001-12-22 | UNIT 2 EXPERIENCED A REACTOR TRIP/TURBINE TRIP DUE TO EHC SYSTEM LOSS OF POWER SUPPLY The Unit 2 electro-hydraulic control (EHC) system power supply failed, causing a loss of electrical load. The resulting shrink in steam generator water level tripped the reactor on steam generator "1A" Lo-Lo level ("first out alarm indication"). A turbine trip on reactor trip occurred, as expected. All control rods fully inserted. Both AMSAC and the auxiliary feedwater (AFW) system actuated ( 2 motor-driven and the turbine-driven pump). However, normal feedwater remained in service and the AFW pumps have subsequently been returned to standby. Unit 2 is currently stable in mode 3 with decay heat removal to the main condenser. No secondary safeties/atmospheric relief valves lifted. Abnormal indications during the transient included reactor coolant pump (RCP) "A" vibration alarm (cleared during transient), pressurizer power-operated relief valve (PORV) lifted/reseated and one Individual rod position indication (IRPI) indicator malfunctioned. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-12-22
38589 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2001-12-20 08:00 | 2001-12-21 11:33 | 2001-12-21 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE On 12/20/01 a Standard Testing employee on his way to a jobsite stopped at a McDonalds located at I-35 and South 29th Street in Oklahoma City, between 0725 and 0800CST for breakfast. Later in the day the employee noticed that the soil moisture density gauge was missing. The device was properly secured/blocked and braced for transport. The chain securing the transport case was cut and the case containing the gauge missing. The licensee informed both the Oklahoma DEQ Rad Management office and the Oklahoma City Police Department. A press release will be issued offering a $500.00 reward. The stolen device is a Troxler Moisture Density Gauge Model #3430, S/N 25733, containing an 8 millicurie Cs-137 source, S/N 75-8614, and a 40 millicurie Am241/Be source, S/N 47-22109. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2001-12-21
38588 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2001-12-19 14:00 | 2001-12-20 11:12 | 2001-12-20 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER DENSITY GAUGE "Angelo Iafrate was using a Troxler Nuclear Density Gauge to measure the density of back fill dirt on a construction site on Napoleon Avenue in New Orleans, LA. Between 12:00PM and 2:00PM the Density gauge was discovered missing. The Density gauge was a Troxler Model 3450 and the serial number is 180. It has a 8.0 mCi source of Cs-137 and a 40.0 mCi source of Am-241Be. The last leak test was performed on July 17, 2001. The facility called the New Orleans Police Department on December 19. 2001, after discovering the gauge was missing. "Louisiana Department of Environmental Quality Event Report ID No.: LA010018" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2001-12-20
38587 | 0 | PARK VIEW HOSPITAL |  |  |  |  | 2001-12-19 | 2001-12-20 11:09 | 2001-12-28 | POSSIBLE MEDICAL MISADMINISTRATIONS COULD HAVE OCCURRED DURING THERAPEUTIC TREATMENTS IN 1998. A radiopharmacy (Spectrum Co.) supplied the hospital with incorrectly calibrated doses of samarium-153 which were used in 1998 during three (04/15/98, 06/03/98, and 06/10/98) therapeutic treatments for bone pain. The supplier believes the doses may be 20-30% less than what was calculated. They are currently performing calculations to determine what the doses were and have already reported this problem to the NRC. The hospital was notified on 12/19/01 of this calculation error. ***** UPDATE RECEIVED AT 1437 EST ON 12/28/01 FROM JOHN AGNEW TO LEIGH TROCINE ***** The licensee is updating this event notification to provide the actual doses received during the treatments in question. The written directive for the 04/15/98 treatment was 90 millicuries of samarium-153, and the radiopharmacy recalculated the actual dose to be 67.18 millicuries. The written directive for the 06/03/98 treatment was 54 millicuries of samarium-153, and the radiopharmacy recalculated the actual dose to be 42.44 millicuries. The written directive for the 06/10/98 treatment was 54 millicuries of samarium-153, and the radiopharmacy recalculated the actual dose to be 41.14 millicuries. The NRC operations officer notified the R3DO (Brent Clayton) and NMSS EO (Fred Brown). (Call the NRC operations officer to obtain contact telephone numbers for John Agnew and for Spectrum.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-20
38586 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-12-19 23:19 | 2001-12-20 02:15 | 2001-12-20 | REACTOR AUTO TRIP FROM 100% POWER ON AMSAC(ATWS MITIGATING SYSTEM ACTUATION CIRCUITRY) SIGNAL While operating at 100% power, the Watts Bar Unit 1 reactor automatically tripped at 2319 EST on December 19, 2001, due to an AMSAC signal which resulted in a turbine/reactor trip. All control rods fully inserted properly and the Auxiliary Feedwater (AFW) System started, as required, in response to the AMSAC signal and the reactor trip. The steam generator levels were at normal levels prior to the trip. No ECCS actuation occurred and no relief valves lifted. The cause of the AMSAC signal is under investigation. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-12-20
38585 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-12-19 16:00 | 2001-12-19 19:12 | 2002-02-15 | EVENT OR CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "The Callaway Plant Final Safety Analysis-Site Addenda, Chapter 2.4 specifies controls to ensure site drainage paths are maintained to prevent flooding of the safety related facilities during postulated design basis precipitation events. Controls are specifically established to ensure modifications to site grading and roadway elevations are evaluated to ensure the Probable Maximum Precipitation (PMP) design basis is not adversely affected and the safety-related structures are protected from flooding. "During installation of highway barriers at the site perimeter on December 19, 2001, it was determined that the barrier installation had not been properly evaluated to ensure the PMP design basis was not adversely impacted. "It was concluded this event was reportable per 10 CFR 50.72(b)(3)(v) because the barrier configuration, in conjunction with PMP conditions could have prevented the fulfillment of the safety function of structures or systems due to flooding. "Immediate actions have been initiated to remove the barriers, thus restoring site grading and road elevations. These actions are targeted for completion within the next twelve-hour shift. In addition, current weather conditions are clear, with no precipitation forecast for the next 24 hours. "The NRC Resident Inspector was notified of this event by the licensee." *** RETRACTION FROM PATRICK McKENNA TO LEIGH TROCINE RECEIVED AT 1650 EST ON 02/15/02 *** The following text is a portion of a facsimile received from the licensee: "On December 19, 2001, Callaway Plant filed Event Notification 33585 to report that concrete security barriers had been installed along the Plant North perimeter and this installation had the potential to violate the Probable Maximum Precipitation (PMP) design basis analysis. Calculations have since been performed to verify current drainage areas and slopes and the potential water surface elevations due to the concrete security barriers. These calculations verify that the potential water surface elevations do not exceed the power block weir and, therefore, do not impact the Operability of the power block buildings." "The Operability Determination is based on the FSAR-SA pg. 2.5-15, which states that the ponding elevation during the site PMP rainfall must be maintained less than elevation 840.5 MSL. As shown in Calculation SPA-18, Addenda 4, the maximum water surface elevation is calculated at 839.4 MSL, an increase of 0.3 feet, and the plant was Operable with the security barriers installed. Since these calculations prove that there was no Operability concern, Callaway Plant is retracting Event Notification 38585." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Linda Smith). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2001-12-19
38584 | 0 | US ARMY |  |  |  |  | 2001-12-19 | 2001-12-19 16:33 | 2001-12-19 | CHEMICAL AGENT MONITOR FAILED ANNUAL LEAK TEST A Chemical Agent Monitor containing a 15 millicurie Ni-63 source failed the annual leak test. The swipe analyzed at the laboratory in Maryland measured .006 microcuries which exceeds the .005 microcurie limit. The device was manufactured by Environmental Technology Group, serial number 316-C-Q-2205, and is currently in Pirmasens, Germany. Corrective action will be to double bag and dispose of it as radwaste. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-12-19
38583 | 0 | CENTRAL SOYA COMPANY |  |  |  |  | 2001-12-14 | 2001-12-19 12:15 | 2001-12-19 | NUMEROUS GENERAL LICENSE TRITIUM EXIT SIGNS FOUND MISSING During a review of tritium exit signs on hand, the licensee discovered that 28 of the 33 were missing. The 33 tritium signs shown in possession include 24 manufactured by Self Powered, Inc (Qty 8 - Model 700C with 4700 millicuries activity/each received on 2/15/89 and Qty 16 - Model 710 with 25,000 millicuries activity/each received on 5/15/88) and 9 manufactured by NRD LLC (Model T4001 with 8400 millicuries activity/each received on 5/15/93). The missing signs include 19 Self Powered units (specific models not identified at time of report) and all 9 NRD units. The facility in Indianapolis where these signs were installed experienced an explosion and fire in 1993 and was subsequently demolitioned in 1996. The licensee contacted NRC Region 3(Andrea Cook) and was advised to submit a written report. * * * UPDATE 1459EST ON 12/19/01 FROM TOM ANDORFER TO S. SANDIN * * * The licensee updated their notification to identify that the 5 exit signs in possession are the model 710. Notified R3DO(Phillips) and NMSS(Turner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-12-19
38582 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-12-13 | 2001-12-19 10:36 | 2001-12-19 | THE COLORADO DEPARTMENT OF PUBLIC HEALTH AND ENVIRONMENT REPORTED A POSSIBLE MEDICAL MISADMINISTRATION BY ONE OF THEIR LICENSEES This occurred during a therapeutic administration of strontium - 90 when the catheter being used shifted about 15 mm and ended up in the aorta instead of a blood vessel. When the catheter was initially placed and the sources were driven out, on the initial 30 second check everything was ok, but on the second 30 second check, the catheter looked like it had moved, so the source was retracted and the catheter repositioned. The source was out for approximately 1 minute 15 seconds. After the repositioning the full treatment(23 gray) was given to the patient. The patient was notified through the referring physician. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-12-19
38581 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2001-12-19 02:50 | 2001-12-19 04:47 | 2001-12-19 | LOCAL FIRE DEPARTMENT NOTIFIED OF A FIRE ONSITE A fire alarm was received @ 0248 CST on 12/19/01 for room-22 safety injection pump room. An inspection showed heavy smoke at entrance to room. The plant fire brigade was manned and personnel entered the room. The fire source was an extension cord, connected to some heaters, which started some anti-contamination clothing on fire. The fire was identified @ 0306 CST and declared out @ 0308 CST. The Blair Fire Department was notified @ 0250 CST and responded to the site. No entry was made to the Protected Area, as the fire was out upon their arrival. The licensee is still investigating the cause. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-12-19
38580 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2001-12-17 12:05 | 2001-12-18 09:13 | 2001-12-18 | FAILURE OF THE STANDBY GENERATOR TO START ON AUTOMATIC DUE TO A PARTIAL POWER OUTAGE AND RELAY FAILURE Moisture in a substation resulted in a partial power outage, and a faulty relay resulted in a failure to switch over to an automatic start on the standby generator. The failure of the standby generator to start on automatic occurred at 1205 CST on 12/17/01. The facility was shut down until the generator was restored and the relay was fixed. The system was restored to service at approximately 1930 CST on 12/17/01. The licensee reported that there was no loss of source material related to this event. In addition, there were no personnel radiation exposures or contaminations. The licensee reported this event in accordance with 10CFR40.60(b)(2)(iii) because there was no redundant equipment available to operate and perform the required safety function. The licensee notified the NRC resident inspector (Bruce Bartlett) for Paducah and plans to submit a written report. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2001-12-18
38579 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-12-17 15:30 | 2001-12-17 16:17 | 2001-12-17 | 24-HOUR REPORT DUE TO POTENTIAL OPERATION IN EXCESS OF OPERATING LICENSE CONDITION 2.C(1) "After restart of Hope Creek from RF10, analysis of plant parameters indicated that changes occurred in the final feedwater temperature since the previous operating cycle. The temperatures as indicated by temperature loops 1AETE-N041A/B/C/D, were approximately 3 degrees lower than when operating at 100 percent power prior to the outage. This indicates that actual power may have been below 100 percent of last cycle operation. Other parameters, such as First Stage pressure, main turbine control valve position, #6 Feedwater Heater shell pressure, feed pump discharge flow, condensate pump flow, were also lower, substantiating that power was lower than previous cycle. Performance Engineering notified Design Engineering of this condition. Design Engineering then initiated a complete review of related documentation. "During Hope Creek RF9 (May 2000), the main feedwater temperature loops required recalibration to support power up-rate. The traditional method to determine the RTD curve introduced a +1 degree F bias. This was non-conservative, in that power level was higher than calculated by the plant computer. In January of 2001, crossflow was implemented to correct for fouling of the venturis. In October 2001, a non-conservative moisture carryover fraction was used in the core thermal power calculation as reported in Hope Creek Special Report 354/2001-003-00. As a result of these conditions, Hope Creek Generating Station has potentially operated at power levels in excess of Operating License Condition 2.C(1), which requires that the facility be operated at reactor core power levels not in excess of 3339 MWt. The upper limit may have been exceeded by significantly less than 0.1%. This potential overpower condition existed between the time of crossflow implementation and RF10. "This notification is being made in accordance with Hope Creek Operating License Condition 2.F, as a potential violation of Hope Creek Operating License Condition 2.C(1). "The moisture carryover fraction was corrected during RF10. During the recent forced outage, the 4 RTDs were checked and all four loops were calibrated, therefore, eliminating the potential for operating above 100% power." The period of time during which the unit may have operated in this condition occurred between August 1, 2001, and October 10, 2001. The corrective action involving calibration of the 4 RTDs was completed last week. The licensee informed the NRC Resident Inspector. | 10 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2001-12-17
38578 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-12-17 08:00 | 2001-12-17 10:39 | 2001-12-17 | SIGNIFICANT FITNESS-FOR-DUTY EVENT UNDER BRAIDWOOD PROGRAM SEC-1.10 A non-licensed supervisor tested positive based on a for-cause test due to the odor of alcohol. The individual was immediately escorted out of the Protected Area, and the individual's access has been suspended. (Call the NRC operations officer for additional details and for the Security Manager's telephone number.) The licensee notified the NRC resident inspector. | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2001-12-17
38577 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-11-20 03:25 | 2001-12-17 09:58 | 2001-12-17 | INADVERTENT START OF A MOTOR-DRIVEN EMERGENCY FEEDWATER PUMP (60-Day Report) The following text is a portion of a facsimile received from the licensee: "During the performance of a surveillance test, the 'B' Motor-Driven Emergency Feedwater (EFW) pump was inadvertently started from the Main Control Board when the intended action was to place the control switch in the pull-to-lock position. The plant was preparing to test the function of the solid state output relay K633 as it pertains to sending an open signal to the EFW flow control valves IFV03531, IFV03541, and IFV03551. To prevent actually injecting EFW into the [steam generators (S/G)], the pump for the train whose relay is being tested (in this case 'B') must be placed in pull-to-lock since the same relay which opens the IFVs also starts the pump." "When the BOP operator attempted to place the pump in P-T-L the pump started. This was immediately recognized as an unexpected response, and the pump was shut off within a second. Due to the start of the EFW pump, S/G blowdown isolated as per design and had to be subsequently realigned. [Data from the] plant computer and alarm printers [was] reviewed by the Shift Supervisor and [Shift Engineer] to determine if any cold EFW actually entered the S/Gs. The alarm printer showed 1 second between pump start and pump stop, which is consistent with the prompt error recognition observed by the crew. The plant computer data showed no increase in EFW flow during the time period in question. It is believed from this investigation that the pump never came up to speed to the point where sufficient pressure was developed to swing open the discharge check valves, thus no EFW injection occurred. The cause of this event is attributed to human performance error." "This event does not require a telephone notification under 10CFR50.72(b)(3)(iv)(A) because this is being reported as an invalid ECCS actuation of an Emergency Feedwater Pump. However, the plant is making this call under the criteria of 10CFR50.73(a)(1) in lieu of submitting an LER under 10CFR50.73(a)(2)(iv)." The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-12-17
38576 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2001-12-16 16:45 | 2001-12-16 21:39 | 2002-02-05 | BOTH HIGH FLOW INSTRUMENTATION FOR REACTOR WATER CLEANUP (RWCU) FOUND INOPERABLE. During performance of routine surveillance testing on the PBAPS Unit 3 RWCU system high flow isolation instrumentation, it was discovered that both channels of isolation instrumentation were simultaneously inoperable. Both affected instruments were returned to operable status by 1828 hours on 12/16/01. The RWCU system is designed to automatically isolate upon detection of a high flow condition. This isolation detection system utilizes two channels of differential pressure instrumentation for high flow detection. An isolation of the RWCU system can be accomplished by actuation of either channel of the logic. A single channel trip would result in either an inboard or outboard isolation. A failure of both channels would result in a failure of the system to isolate as required. On 12/16/01 at 1111 hours, surveillance testing of the "A" channel high flow instrument (DPIS 3-12-124A) determined that this instrument failed to trip due to entrapped air in the sensing line. DPIS 3-12-124A was vented, retested, and returned to operable status at 1536 on 12/16/01. At 1645 hours, surveillance testing of the "B" channel RWCU high flow instrument (DPIS 3-12-124B) determined that this instrument failed to trip due to entrapped air in the sensing line. DPIS 3-12-124B was vented, retested, and returned to operable status at 1828 on 12/16/01. At 1645 on 12/16/01, it was determined that both channels of Unit 3 RWCU system high flow isolation instrumentation were simultaneously inoperable since the system had been placed in service during refueling outage 3R13. Unit 3 entered Mode 2 on 10/08/01 at 2221 hours, requiring the Primary Containment Isolation (PCIS) function to be operable. Based on the above, this event is reportable under 10 CFR 50.72(b)(3)(v)(C). The systems affected were the RWCU system isolation logic instruments, DPIS 3-12-124A and DPIS 3-12-124B. These instruments actuate on high system flow of 125%. No plant effects or transient occurred as a result of this event. The RWCU system isolation capability, on high system flow, was inoperable. This isolation capability is required whenever the RWCU system is in service with the reactor in Modes 1, 2, or 3. DPISs 3-12-124A and 3-12-124B were filled, vented, tested satisfactorily, and returned to operable status. A station investigation to determine the cause of the air entrapment is in progress. The NRC resident inspector was notified of this event by the licensee. * * * RETRACTION 1413 2/5/2002 FROM KOVALCHICK TAKEN BY STRANSKY * * * "This notification is a retraction of Event Number (EN) 38576 which reported a loss of safety function of thc RWCU primary containment isolation valves due to entrapped air in the instrument sensing lines for the high flow isolation for both isolation valves. "On December 16, 2001, the Reactor Water Cleanup (RWCU) system high flow isolation instrumentation routine surveillance was performed. During the routine surveillance, it was discovered that both high flow isolation instruments tripped outside their Technical Specification Allowable Value due to entrapped air in the system. resulting in both instruments being declared inoperable. "An engineering evaluation determined that the test failure was caused by the testing methodology and concluded that both instruments were operable and the safety function was not impacted. Specifically, the evaluation determined that the entrapped air existed in the test lines only, which are isolated during normal plant operations. "Therefore, because the safety function of the RWCU automatic isolation on high flow was maintained, this issue is not reportable under 10 CFR 50.72(b)(3)(v)(C). "The NRC resident has been notified." Notified R1DO (Doerflein). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2001-12-16
38575 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-12-15 22:28 | 2001-12-16 00:30 | 2001-12-17 | THE REACTOR RECIRCULATION PUMPS DOWN SHIFTED TO SLOW SPEED FOR UNKNOWN REASONS RESULTING IN AN AUTOMATIC REACTOR SCRAM, BALANCE-OF-PLANT ISOLATIONS, AND EMERGENCY CORE COOLING SYSTEM ACTUATIONS. At 2228 EST on 12/15/01, the reactor recirculation pumps down shifted to slow speed for unknown reasons. This caused reactor pressure vessel (RPV) water level to swell, and an automatic reactor scram from 100% power occurred when Level 8 was reached. All control rods fully inserted. Following the scram, RPV water level started to decrease because the feedwater pumps also tripped (as designed) when Level 8 was reached. When RPV water level dropped to Level 2 (130 inches), balance-of-plant isolations occurred, and all of the applicable valves properly isolated. In addition, the high pressure core spray (HPCS) and reactor core isolation cooling (RCIC) systems automatically actuated when Level 2 was reached. The HPCS and RCIC systems were utilized to restore RPV water level to the normal range. The unit is currently stable in Mode 3 with RPV pressure at 900 psi and RPV water level at 210 inches. Normal feedwater is being utilized to maintain RPV water level within the proper band, and the HPCS and RCIC systems have been secured. The main steam isolation valves remained open, and the condenser is being utilized as the heat sink. Containment parameters are currently normal, the electrical grid is stable, and the emergency diesel generators are available. The licensee stated that all systems functioned as required and that there was nothing unusual or misunderstood other than the cause of the initiating event (the recirculation pumps down shifting to slow speed). The licensee's investigation is underway. The licensee notified the NRC resident inspector. * * * UPDATE AT 1844 EST ON 12/17/01 FROM DAVID GUDGER TO S. SANDIN * * * "This notification is a follow-up to the notification provided on 12/16/01." "The following is a description of the sequence of plant events that occurred as determined by the failure analysis." "Initial conditions: Feedwater level control was on Master Level controller selected to the 'B' narrow range channel and the plant was operating at 100% power. Due to the level summer card 1C34K657 failure, the level signal from the selected channel rapidly decreased to less than 178 inches, Level 3 (L3) signal, which caused the reactor recirculation pumps to receive a fast-to-slow speed downshift. Simultaneously, feedwater flow rapidly increased in response to the low level on the 'B' channel. The feedwater pumps tripped at 219 inches, Level 8 (L8), which occurred due to swell from the recirculation pumps downshift and increased feedwater flow. The [motor feed pump (MFP)] did not automatically start due to the L8 signal (as designed) and level decreased to 130 inches, Level 2 (L2). The recirculation pumps tripped, and [the] HPCS and RCIC systems [automatically] started and restored level. The MFP L8 signals were reset, and level was controlled on the startup controller." "The Reactor Water Cleanup Inboard Containment Isolation Valve failed to close as designed upon [the] L2 isolation signal. The valve was manually closed during containment valve isolation verification following the scram. The cause of the failure to close was determined to be relay failure. Two relays were subsequently replaced and retested satisfactorily." The licensee informed the NRC resident inspector. The NRC operations officer notified the R3DO (Phillips). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2001-12-16
38574 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-12-15 19:00 | 2001-12-15 23:00 | 2001-12-15 | MANUAL REACTOR SCRAM FROM 60% POWER DUE TO UNIDENTIFIED LEAK RATE EXCEEDING 5 GPM At 0431 on December 15, 2001, Unit 2 noted a step increase in unidentified drywell leakage from 0.2 gpm (normal) to 0.4 gpm. Coincident with this step increase, containment atmosphere radiation levels rose and alarmed on the particulate channels. Throughout the day, investigation continued into possible causes, and the trend in leakage showed no appreciable increase. At 1658, containment atmosphere radiation levels rose again, and a large step increase in leakage was noted from approximately 0.5 gpm to 1.7 gpm. The technical specification limit is less than 5 gpm unidentified leakage and less than a 2-gpm rise in unidentified leakage during the previous the 24 hours. At 1745, plant management ordered an orderly plant shutdown to identify the source of leakage in the drywell. At 1900, a normal reactor shutdown was commenced, original reactor power was 100%, in preparation for repairing the leak in the drywell. At 1919, drywell unidentified leakage rose to 2.27 gpm, and the technical specification action statement was entered for greater than a 2-gpm rise in unidentified leakage during the previous 24 hours. At 2040, the drywell unidentified leak rate exceeded 5 gpm (5.87 gpm), and the decision was made to scram the plant. At 2046, the reactor mode switch was placed in shutdown, all systems functioned as required, all rods fully inserted into the core. The scram signal received was Average Power Range Monitor (APRM) neutron upscale due to setpoint setdown with the mode switch out of run. A secondary scram signal was received when reactor water level dropped to less than 159.3" (Level 3) (expected due to level shrink on the scram). Level 3 also provided a Primary Containment Isolation System (PCIS) signal to group 4 (Residual Heat Removal System, [RHS] sampling valves) and group 5 (RHS shutdown cooling valves). At the time of the signal, all group 4 and 5 valves were closed. At 2043, technical specification action statement associated with exceeding 5 gpm was exited. At 2149, technical specification action statement associated with greater than 2 gpm rise over the previous 24 hours was exited. At this time, drywell unidentified leakage 1.5 gpm and lowering, plant pressure is being reduced. Reactor water level is being maintained with condensate/feedwater. Reactor pressure control is being maintained via turbine bypass valves with cooldown in progress. All Emergency Core Cooling Systems and the Emergency Diesel Generator are fully operable, and the electrical grid is stable. The NRC resident inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2001-12-15
38573 | 0 | MEMORIAL HOSPITAL |  |  |  |  | 2001-12-14 | 2001-12-14 15:43 | 2001-12-14 | POTENTIAL MEDICAL MISADMINISTRATIONS: UNDERDOSES OF SAMARIUM-153 The licensee was notified today by the RSO of Spectrum Pharmaceuticals that the total activity of Sa-153 quadramet does may be approximately 20-30% less than labeled due to an error in the attenuation calculation for beta factor in the Sa-153 total activity. The licensee believes that he has treated two patients since 1998 with Sa-153. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38572 | 0 | ST. JOSEPH'S HOSPITAL |  |  |  |  | 2001-12-14 | 2001-12-14 15:27 | 2001-12-14 | POTENTIAL MEDICAL MISADMINISTRATION: UNDERDOSE OF SAMARIUM-153 The licensee was notified today by the RSO for Spectrum Pharmaceuticals that the total activity of Sa-153 quadramet doses may be approximately 20-30% less than labeled due to an error in the attenuation calculation for the beta factor in the Sa-153 total activity calculation. This condition may have existed for greater than 1 year. The licensee found one patient who was treated with Sa-153 and that was on 10/05/00. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38571 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2001-12-12 | 2001-12-14 15:20 | 2001-12-14 | EXCESSIVE EXPOSURE "The monthly personnel badges showed an excessive exposure for three employees. [One individual] had 5136 mRem, [another individual] had 5095 mRem, and [a third individual] had 5200 mRem for the year as of November 10, 2001. Once the facility received the badge report, the facility notified [the] DEQ. The facility is also sending a written report to [the] DEQ. These three individuals have been removed from radiation work." Event Report No.: LA010017 (Call the NRC operation officer for contact information and for the names of the individuals involved.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2001-12-14
38570 | 0 | ST. LUKES HOSPITAL |  |  |  |  | 2001-12-12 07:00 | 2001-12-14 15:07 | 2001-12-14 | SURFACE CONTAMINATION IBA out of New Jersey delivered a metal case, ammo case, which contained less than 21 millicuries of fluorine-18, to St. Lukes North outpatient facility on 12/12/01 before 0700 hours. Swipes taken of the outside and inside of the ammo case found technetium-99m contamination. Outside and inside swipes both indicated contamination level around 6800 cpm. The ammo case was decontaminated and placed in St. Lukes Hot Lab. St. Lukes contacted IBA and informed them of the contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2001-12-14
38569 | 0 | BRONSON METHODIST HOSPITAL |  |  |  |  | 2001-12-14 | 2001-12-14 14:48 | 2001-12-14 | POSSIBLE MEDICAL MISADMINISTRATION: UNDERDOSE OF SAMARIUM-153 The licensee was notified today by the RSO for Spectrum Pharmaceuticals that the total activity of Sa-153 quadramet doses may be approximately 20-30% less than labeled due to an error in the attenuation calculation for the beta factor in the Sa-153 total activity calculation. This calculation error may have existed for greater than 6 months. The licensee is aware of one patient treated in the last year. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38568 | 0 | BORGESS MEDICAL CENTER |  |  |  |  | 2001-12-14 | 2001-12-14 14:44 | 2001-12-14 | POSSIBLE MEDICAL MISADMINISTRATION: UNDERDOSE OF SAMARIUM-153 The licensee was notified today by the RSO for Spectrum Pharmaceuticals that the total activity of Sa-153 quadramet doses may be approximately 20-30% less than labeled due to an error in the attenuation calculation for the beta factor in the Sa-153 total activity calculation. This calculation error may have existed for greater than 6 months. The licensee does not know how many patients have been treated and is looking through records to determine number of patients treated with Sa-153. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38567 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-12-14 11:27 | 2001-12-14 14:30 | 2001-12-14 | FITNESS-FOR-DUTY REPORT A contract supervisor tested positive for illegal drug use during a random test. The individual did not have access to vital areas, and his site access has been terminated. The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2001-12-14
38566 | 0 | ST. JOSEPH'S REGIONAL MEDICAL CENTR |  |  |  |  | 2001-12-14 | 2001-12-14 14:13 | 2001-12-14 | POTENTIAL MEDICAL MISADMINISTRATIONS: UNDERDOSES OF SAMARIUM-153 The licensee was notified today by the RSO for Spectrum Pharmaceuticals that the total activity of Sa-153 quadramet doses may be approximately 20-30% less than labeled due to an error in the attenuation calculation for the beta factor in the Sa-153 total activity calculation. This calculation error may have existed greater than 6 months. The licensee is aware of two patients who were treated during this period. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38565 | 0 | HOME HOSPITAL |  |  |  |  | 2001-12-14 | 2001-12-14 13:17 | 2001-12-14 | POTENTIAL MEDICAL MISADMINISTRATION: UNDERDOSE OF SAMARIUM-153 The licensee was notified today by the RSO for Spectrum Pharmaceuticals that the total activity of Sa-153 quadramet doses may be approximately 20-30% less than labeled due to an error in the attenuation calculation for the beta factor in the Sa-153 total activity calculation. This calculation error may have existed for greater than 6 months. The licensee is aware of one patient who was treated during this period and is reviewing treatment records to determine whether any others may be affected. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38564 | 0 | GOSHEN GENERAL HOSPITAL |  |  |  |  | 2001-12-14 | 2001-12-14 12:18 | 2001-12-14 | POSSIBLE MEDICAL MISADMINISTRATIONS: UNDERDOSES OF SAMARIUM-153 Goshen General Hospital was notified today by the RSO for Spectrum Pharmaceuticals that Sa-153 quadramet, used for pain relief in bone cancer patients, beta attenuation were incorrectly calculated. This attenuation calculation error made by Spectrum Pharmaceuticals has resulted in patient's given Sa-153 at Goshen General Hospital being underdosed between 20 to 30%. The attenuation error may have existed for greater than 6 months. Three patients have been given a possible underdose of Sa-153. NRC Region 3 personnel have been notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38563 | 0 | ELKHART HOSPITAL |  |  |  |  | 2001-12-14 | 2001-12-14 12:17 | 2001-12-14 | POSSIBLE MEDICAL MISADMINISTRATIONS: UNDERDOSES OF SAMARIUM-153 Elkhart Hospital was notified today by the RSO for Spectrum Pharmaceuticals that Sa-153 quadramet doses total activity shipped to them was incorrectly calibrated. Spectrum Pharmaceuticals informed the Hospital that they had made an error in the attenuation calculation for the beta factor in the samarium-153 total activity and that this error may have been made more than 6 months ago. Spectrum Pharmaceuticals believes that the Sa-153 total activity is actually less by 20 to 30%. At this time, Elkhart Hospital does not know how many patients have received an underdose of Sa-153. NRC Region 3 has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-12-14
38562 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-12-14 06:45 | 2001-12-14 08:57 | 2001-12-14 | PLANT COMPUTER AND SAFETY PARAMETERS DISPLAY SYSTEM INOPERABLE The unit suffered a failure of the plant computer at 1452 CST on 12/13/01 and repairs are ongoing. The plant computer is expected to be down greater than 24 hours. The plant computer feeds the Safety Parameter Display System (SPDS), which is inoperable also. The licensee has made a decision to make this report under a major loss of emergency assessment capabilities per 10 CFR 50.72(b)(3)(xiii) as a conservative measure. The control board indicators are operable and are used by the operators normally in an emergency. The Shift Technical Advisor will perform a manual review of safety parameters in the case of an emergency, using the control board indications. The licensee notified the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-12-14
38561 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-12-09 | 2001-12-13 17:00 | 2001-12-13 | LOST RADIOACTIVE SEALED SOURCE Hospital had a package of 94 I-125 seeds at 310 microcuries each delivered on December 9, 2001. Package was delivered to the nuclear medicine department and left on top of boxes that the person delivering thought would be seen by nuclear medicine personnel. The package was not accepted by an individual in nuclear medicine. At the time of the scheduled treatment, December 11, 2001, nuclear medicine called to see where the seeds were and were told that they had arrived on the 9th and had been delivered to nuclear medicine. The seeds were packaged and the seeds cannot be found. Texas Incident No. I-7839. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-12-13
38560 | 0 | CARBOLINE COMPANY |  |  |  |  | 2001-12-13 12:00 | 2001-12-13 16:06 | 2001-12-13 | CARBOZINC 11 SG HAS BEEN DETERMINED TO HAVE A REPORTABLE DEFECT. Carboline has been notified of stability problems with some Carbozinc 11 SG product over the last year. The material is exhibiting premature gellation or thickening prior to the end of the published shelf life expiration date. Carbozinc 11 SG that is gelled or exhibiting significant thickening will not atomize or spray properly, resulting in poor adhesion to the substrate. When this occurs the coating cracks during the spray process and the coating process and the coating flakes off the substrate. On December 14, 2001, Carboline will send by register mail to all purchasers of Carbozinc 11 SG reporting Part 21 Reporting of Defect. See event number 38408, reported 10/19/2001 for background information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MO | OTH | PAR | 21.21 |  |  |  | 0 | 2001-12-13
38559 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2001-10-15 00:01 | 2001-12-12 15:58 | 2001-12-12 | ISOLATION OF DIVISION I CONTAINMENT ISOLATION VALVES DUE TO THE UNEXPECTED TRIP OF THE FEEDER BREAKER FOR A NON-SAFETY 480-VOLT AC SWITCHGEAR (60-Day Report) The following text is a portion of a facsimile received from the licensee: "On October 15, 2001, at approximately 12:01 a.m., with the plant at approximately 80% power, an isolation of Division I containment isolation valves occurred. This event was caused by the unexpected trip of the feeder breaker for one of the plant's non-safety 480-volt AC switchgears. In addition, five manual breakers on the same switchgear opened. This deenergized the normal power supply to the Division I reactor protection system (RPS), which caused the actuation of Division I containment isolation valves. This event is being reported in accordance with the 60-day telephone notification provision in 10CFR50.73(a)(2)(iv)(A) as an invalid general containment isolation signal." "Division I containment isolation valves automatically closed, and the Division I annulus mixing and standby gas treatment systems received an automatic start signal. Consistent with plant design, isolation of the annulus pressure control system subsequently caused the Division II annulus mixing and standby gas treatment systems to start. However, the Division II annulus mixing fan breaker tripped open after receiving a close signal. Both divisions of the fuel building charcoal filter trains started. The Division I containment atmosphere hydrogen analyzer automatically started." "After an initial assessment, operators implemented abnormal operating procedures and restored systems in containment to their normal alignment. Plant operation was not interrupted. Except for the trip of the Division II annulus mixing fan, all plant systems responded as designed to the event. The fan trip is being addressed within the stations corrective action program." "The investigation of the spurious breaker trips is still in progress. Tests completed thus far have not determined the cause of the trip, and switchgear inspections performed during a brief plant outage in the interim found no hardware deficiencies. The Division I RPS system remains powered from its alternate source, which will prevent its loss should the switchgear again be de-energized. The switchgear has been instrumented in order to collect transient data in the event the trips recur." The licensee notified the NRC resident inspector. | 80 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-12-12
38558 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-12-12 08:20 | 2001-12-12 11:32 | 2001-12-12 | OFFSITE NOTIFICATION REGARDING NPDES PERMIT VIOLATION "This 4-hour call is being made to the NRC based on the requirements of 10CFR50.72(b)(2)(xi). A written report was submitted to the Missouri Department of Natural Resources concerning the discharge of plant processed water to a storm water runoff outfall inconsistent with the terms and conditions of Callaway Plant's NPDES permit. This written report was submitted on December 12, 2001, and addresses a discharge of water from the plant circulating water system that occurred on December 7, 2001. "On December 12, 2001, the Missouri Department of Natural Resources (Mo. DNR) was notified that a discharge of plant processed water from our circulating water system, occurred. This event occurred on December 7, 2001 and was the result of a minor leak that developed at a caulked construction joint in our cooling tower basin. "This event resulted in a notification to the Mo. DNR on 12/12/01. It was concluded this event is reportable per 10CFR50.72(b)(2)(xi) since it represents a notification to a government agency relating to the protection of the environment." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-12-12
38557 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-10-17 10:39 | 2001-12-11 17:16 | 2001-12-11 | INVALID ACTUATION OF THE REACTOR PROTECTION SYSTEM WHILE THE UNIT WAS IN COLD SHUTDOWN (60-Day Report) The following text is a portion of a facsimile received from the licensee: "This 60-day optional report, as allowed by 10CFR50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the reactor protection system (RPS). On October 17, 2001, at 1039 with Unit 2 in MODE 5 with a boron concentration of 2531 ppm, an invalid reactor trip signal was generated from 2 out of 4 logic for overtemperature delta-T. The reactor trip breakers opened as designed upon receipt of the invalid reactor trip signal. All control rods and shutdown rods were already fully inserted before the invalid reactor trip signal trip signal was generated. At the time of the invalid reactor trip signal, reactor protection channel III had been properly removed from service for maintenance testing. Other maintenance technicians were in the process of setting up test equipment in reactor protection channel I for upcoming resistance temperature detector cross calibrations. The technicians thought that the place where they were connecting the test equipment was isolated from the circuit and would have no effect on the plant. During the connections, a momentary spike occurred on reactor protection channel I. This completed the 2 out of 4 logic for an overtemperature delta-T reactor trip, and a reactor trip occurred. The control room operators entered appropriate procedures and verified proper equipment operation for the existing plant conditions. Both trains A [and] B of the reactor protection system actuated. This was a complete actuation, and the system performed as designed for the existing plant conditions. This event has been entered into the site-specific corrective action program for resolution." The licensee notified the NRC resident inspector and plans to notify applicable state, county, and local agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-12-11
38556 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2001-12-10 12:00 | 2001-12-10 18:49 | 2001-12-10 | DISCOVERY THAT STANDBY LIQUID CONTROL SYSTEM RELIEF VALVES ON UNIT 3 MAY INTERMITTENTLY LIFT DURING THE MOST LIMITING ATWS TRANSIENTS (Refer to event #38555 for a similar notification received from Quad Cities.) The following text is a portion of a facsimile received from the licensee: "While performing calculations associated with the power uprate project, Dresden Nuclear Power Station determined that the Standby Liquid Control (SLC) system relief valves on Unit 3 may intermittently lift during the most limiting ATWS [transients. (The] specific scenario evaluated is a Main Steam Line isolation at rated power with failure of the normal, backup, and alternate rod insertion (ARI) scram functions.) This issue also applies to the current rated power level during two pump SLC operation. Title 10 of the Code of Federal Regulations, subpart 50.62, requires the SLC system to inject the equivalent of 86 gpm of 13-weight percent sodium pentaborate solution. While the relief valve was lifted, the system flow rate would not meet the required equivalent flow rate into the vessel. Therefore, this condition is not in direct compliance with 10 CFR 50.62. The NRC communicated a similar industry issue in Information Notice 2001-13" "Further plant specific analysis has demonstrated that an adequate volume of boron would be injected to shut down the reactor and meet the appropriate acceptance criteria including reactor pressure, peak cladding temperature, peak suppression pool temperature, and peak containment pressure. For these reasons, the safety significance of this event is minimal." "This phone call is being made as an informational call. Written communications, as appropriate, will be submitted to provide additional detail. The station will continue to communicate additional information with the NRC resident inspectors and with [NRC] Region Ill as it is identified." The licensee stated that although Dresden Units 2 and 3 are similar vintage boiling water reactors, this issue does not apply to Dresden Unit 2 because the piping runs are different. The licensee notified the NRC resident inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2001-12-10
38555 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2001-12-10 12:00 | 2001-12-10 18:40 | 2001-12-10 | DISCOVERY THAT STANDBY LIQUID CONTROL SYSTEM RELIEF VALVES MAY INTERMITTENTLY LIFT DURING THE MOST LIMITING ATWS TRANSIENTS (Refer to event #38556 for a similar notification received from Dresden Unit 3.) The following text is a portion of a facsimile received from the licensee: "While performing calculations associated with the power uprate project, Quad Cities Nuclear Power Station determined that the Standby Liquid Control (SLC) system relief valves on Unit 1 and Unit 2 may intermittently lift during the most limiting ATWS [transients. (The] specific scenario evaluated is a Main Steam Line isolation at rated power with failure of the normal, backup, and alternate rod insertion (ARI) scram functions.) This issue also applies to the current rated power level during two-pump SLC operation. Title 10 of the Code of Federal Regulations, subpart 50.62, requires the SLC system to inject the equivalent of 86 gpm of 13-weight percent sodium pentaborate solution. While the relief valve was lifted, the system flow rate would not meet the required equivalent flow rate into the vessel. Therefore, this condition is not in direct compliance with 10 CFR 50.62. The NRC communicated a similar industry issue in Information Notice 2001-13." "Further plant specific analysis has demonstrated that an adequate volume of boron would be injected to shut down the reactor and meet the appropriate acceptance criteria including reactor pressure, peak cladding temperature, peak suppression pool temperature, and peak containment pressure. For these reasons, the safety significance of this event is minimal." "This phone call is being made as an informational call. Written communications, as appropriate, will be submitted to provide additional detail. The station will continue to communicate additional information with the NRC resident inspectors and with Region Ill as it is identified." The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2001-12-10
38554 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-10-29 01:21 | 2001-12-10 11:58 | 2001-12-10 | INVALID PRIMARY AND SECONDARY CONTAINMENT ISOLATION DUE TO LOSS OF POWER TO A REACTOR PROTECTION SYSTEM POWER DISTRIBUTION BUS (60-Day Report in Accordance with 10CFR50.73(a)(1)) The following text is a portion of a facsimile received from the licensee: "Event Description" "At 0121 hours on October 29, 2001, with the plant operating at 66 percent of rated thermal power, power was lost to Reactor Protection System (RPS) power distribution bus B as a result of an Electrical Protective Assembly (EPA) logic card failure." "The power sources for the RPS provide power to both the RPS and the Primary Containment Isolation System (PCIS) logic circuits. Loss of power to RPS power distribution bus B resulted in invalid actuation of RPS trip system B and [PCIS] trip system B. The RPS trip was a partial actuation (a 'half scram'), and the PCIS trip was also a partial actuation (a 'half isolation')." "The portions of PCIS logic that are designed with separate 'inboard' and 'outboard' logic had the 'outboard' logic de-energized due to the power loss. This resulted in the automatic closure of the outboard primary containment isolation valves [...] for the: drywell pressure sensing line, pressure suppression chamber pressure sensing line, Reactor Water Cleanup system pump suction line, Reactor Water Cleanup system return line, and reactor water sample line." "The de-energized PCIS logic circuits also initiated automatic closure of Reactor Building (Secondary Containment) ventilation system outboard supply and exhaust isolation valves and automatically started Standby Gas Treatment (SGT) subsystem B, as designed, to maintain the reactor building atmosphere at a slightly negative pressure." "Operating personnel restored power to RPS power distribution bus B by transferring to the alternate power source. The invalid PCIS and RPS trip signals that were caused by the loss of power were reset, systems that isolated were restored to service, reactor building ventilation was restored to normal, and SGT subsystem B was restored to a normal standby status." "Actions Taken" "1. RPS power distribution bus B was energized from the alternate power source." "2. RPS and PCIS logic systems were reset." "3. The affected systems were restored to normal." "4. Troubleshooting of a logic card associated with the tripped EPA circuit breaker revealed a failed capacitor. The failed logic card was replaced with a refurbished logic card from stock." "5. Power to RPS power distribution bus B was transferred back to the normal (motor generator) source." "6. New capacitors will be installed on the logic cards, or refurbished logic cards will be installed, in the subject EPAs during the next available maintenance window." The licensee notified the NRC resident inspector. | 66 | 0 | 0 | 66 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-12-10
38553 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-12-10 03:48 | 2001-12-10 11:53 | 2001-12-10 | INADVERTENT LOSS OF POWER TO THE C-315 TAILS WITHDRAWAL BUILDING DURING AN IMPROPERLY PERFORMED POWER SWITCHING EVOLUTION (24-Hour Report) The following text is a portion of a facsimile received from the Paducah: "At 0348 CST on 12-10-01, 480-volt power was inadvertently lost to the C-315 tails withdrawal building during an improperly performed power switching evolution. As a result of the power loss, the high voltage UF6 release detection system for the UF6 condensers, accumulators, and heated housings was rendered inoperable for approximately 10 minutes. The high voltage UF6 release detection system is required to be operable per TSR 2.3.4.4. The function of the high voltage UF6 release detection system is to detect UF6 releases and to sound an alarm in the local control room. The power loss also caused the withdrawal systems to shut down and automatically isolate as designed. No UF6 releases occurred as a result of this evolution. Power was restored and the building was returned to normal operation." "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed." Paducah personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2001-12-10
38551 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-12-09 15:40 | 2001-12-09 17:44 | 2001-12-09 | OFFSITE MEDICAL TRANSPORT An individual working in a contaminated area fell approximately five feet from some scaffolding and sustained an apparent hip injury. The victim was transported by ambulance to the Monticello-Big Lake Hospital. The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTION 2215 12/9/2001 FROM McKAY TAKEN BY STRANSKY * * * "On 12/9/01, event number 38551 was called in as an offsite medical, 10 CFR 50.72, 8 hour notification. A worker in a contaminated area fell approximately 5 ft and was transported via ambulance to the Monticello-Big Lake Hospital. The individual was transported as a contaminated person. Subsequently, it has been determined that the individual was NOT contaminated. The individual, ambulance and hospital were surveyed and found to be free of contamination. Therefore, we wish to retract event number 38551." The NRC resident inspector has been informed of this retraction by the licensee. Notified R3DO(Hiland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2001-12-09
38550 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-12-07 23:50 | 2001-12-08 01:52 | 2001-12-08 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO LOW REACTOR COOLANT SYSTEM FLOW "Relay actuation on 6.9KV Breaker 2TD-3 caused a loss of Reactor Coolant Pump 2D resulting in a reactor trip and emergency feedwater auto start. 2TD-4 Breaker also tripped resulting in a loss of normal power to essential bus 2ETB. 2B Emergency Diesel Generator auto started and loaded as appropriate. The unit is currently stable in mode 3. Efforts to establish normal feedwater and power are in progress." All systems functioned as required. Unit 2 is currently supplying emergency feedwater to the steam generator using both motor-driven Emergency Feedwater Pumps and discharging steam to the main condenser for decay heat removal. The licensee will inform both the states of NC and SC as well as local authorities and has informed the NRC resident inspector. * * * UPDATE 0420EST ON 12/8/01 FROM DON BRADLEY TO S. SANDIN * * * The licensee has reestablished normal feedwater supply and secured the operating emergency feedwater pumps. Also, 2B Emergency Diesel Generator has been returned to standby after essential bus 2ETB was realigned to the preferred alternate power source. Notified R2DO(Lesser). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-12-08
38549 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-12-07 | 2001-12-07 18:21 | 2001-12-07 | AGREEMENT STATE REPORT L.A. County Radiation Management reported that a package containing a Mo-99 generator had excessive external dose readings when received by a CA State Licensee. When the package was surveyed before shipping, it was measured to have a surface dose reading of 100 mR/hr (transport index of 2); however, it was reading 400-450 mR/hr (T.I. 16) upon arrival at the Medi-Physics facility. No surface contamination was detected. The package had been shipped from Amersham in Chicago, IL via FedEx. The licensee is still trying to determine the cause of the elevated dose rate from the package. Amersham has proposed that approximately 800 microcuries may have migrated into an unshielded part of the Mo-99 generator. The States of California and Illinois, as well as FedEx, have been contacted regarding this event. CA NMED # XCA102 HOO note: This report was made on behalf of the CA Radiation Control Program by L.A. County Radiation Management. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-12-07
38548 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-12-07 14:01 | 2001-12-07 16:23 | 2001-12-07 | MANUAL REACTOR TRIP DUE TO LOSS OF STATION AIR COMPRESSOR "During steady state power operation, Beaver Valley Unit 1 experienced a loss of station air compressor SA-C-IA. The opposing compressor SA-C-1B was out of service for maintenance. The operating crew entered the Loss of Station Air Abnormal Operating Procedure (AOP) and started the backup diesel driven air compressor. The reactor was manually tripped in accordance with the AOP due to decreasing station instrument air pressure. The crew entered the Emergency Operating Procedures and stabilized the plant in Mode 3. Station air was restored using the diesel driven backup air compressor. The plant responded normally. "The plant is currently stable in Mode 3. Steam Generator feed is via the Main Feed Water System. The auxiliary feed water system was in service and has been secured. Cooling is via the condenser steam dump system. "Station Air Compressor SA-C-1A was found to have a blown control circuit fuse. The fuse was replaced and the compressor returned to service. "There were no radiological releases in progress as a result of this event." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-12-07
38547 | 0 | PHILLIP MORRIS USA |  |  |  |  | 2001-12-04 09:10 | 2001-12-07 14:26 | 2001-12-07 | INFORMATION REPORT "Equipment:: Maid N Scanning Head (Beta Gauge) "Equipment NRC Registration: # NR-462-D-1 02-B "Equipment Registered to: Molins Richmond 3900 Carolina Avenue P.O. Box 6159 Richmond, VA 23222-0159 "Radioactive Material: strontium-90, 0.025 curies, sealed source "Nature of Failure: On Tuesday. December 4, 2001, an Authorized User was conducting routine leak-tests and shutter-checks. While conducting tests, he noticed cigarette maker machine 2A4, which was shutdown for routine maintenance, had a shutter indicator denoting the shutter in the open position. In this machine state, this shutter should have been closed. He used a survey meter to verify the shutter was open. He immediately inserted a cigarette rod in the pass tube to simulate normal operating conditions and radioed another Authorized User to bring another scanning head to the maker. Together they dismounted the scanning head and removed the source at 09:20 a.m. A beta shield was used during the source removal and the source was placed into a lead container. The other scanning head was placed on the maker and a survey was made. The source and malfunctioning scanning head were taken to the radiation shop and the source was placed into a locked storage sate. "The Molins Maid N scanning head is a fixed gauge. During operation, it is bolted to a cigarette-making machine. The Maid N scanning head is used to measure the density of tobacco in a continuous, paper-wrapped. cylindrical rod that passes through this gauge en route to being sectioned into individual cigarette lengths in another part of the machine. The Maid N is shielded except for a 9-mm diameter pass tube through which the continuous tobacco rod passes. The Strontium 90 source is situated at the rear of the gauge and the detector tube at the front. The direct beam of radiation is wholly contained within the gauge and is aligned perpendicular to the pass tube. During normal operation, the pass tube is filled by a cigarette rod. When the gauge is turned off, the pass tube is clear and the shutter is closed. "Date/Time of Event: Tuesday, December 4, 2001, 09:10 a.m.. "Date/Time Initially Reported to NRC: Tuesday, December 4, 2001 4:50 p.m.. "Name or Individual Reporting: Mr. Chuck L. Stiff, Safety Director Mr. Joe Tenhet, RSO "Location: Philip Morris USA Richmond Manufacturing Center 3601 Commerce Road P.O. Box 26603 Richmond, VA 23261 "License # 45-00385-06 "Corrective Actions: The scanning head was completely disassembled, checked and repaired. The repair technician found no reason for the shutter to fail to close and was not able to reproduce the problem. A new shutter assembly was installed in the scanning head as a precaution." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | VA | OTH | GEN |  |  |  |  | 0 | 2001-12-07
38545 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-12-06 10:20 | 2001-12-06 13:52 | 2001-12-06 | FITNESS FOR DUTY A licensed operator (currently inactive) tested positive for illegal drug use under the licensee's fitness-for-duty (FFD) program. The individual was not on shift assignment, nor had the individual performed on-shift activities during the past year. The individual's site access has been terminated. The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2001-12-06
38544 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-12-06 09:05 | 2001-12-06 11:34 | 2001-12-06 | THE LICENSEE MADE AN OFFSITE NOTIFICATION TO THE MISSOURI PUBLIC SERVICE COMMISSION The following is a report to the Missouri Public Service Commission (MPSC) to notify them of a forced outage at the Callaway Nuclear Plant. This notification is reportable under 4CSR240-20.080(3)(B) because the outage is expected to last longer than 72 hours. At 2248 CST, December 3, 2001, Callaway Plant shut down to effect repairs on the Main Generator. A leak had developed on a Main Generator cooling system requiring repairs which could only be made with the unit off-line. Initially, the Plant was expected to return to service within 72 hours, but due to the complexity of the repairs, the unit is now expected to return to service after the 72-hour deadline has expired. Expectations are to return to service by December 7, 2001. The Licensee has informed the NRC Resident Inspector of the MPSC notification. | 1 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Startup | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-12-06
38543 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2001-12-05 14:30 | 2001-12-06 09:39 | 2001-12-06 | DISCOVERY OF A SHALLOW MONITOR WELL IN EXCURSION FOR SULFATE At approximately 1430 CST on 12/05/01, the licensee received second confirmation of well #SM723 being in excursion for sulfate. Sulfate was discovered to be at a concentration of 68 mg/l which exceeded the upper control limit of 65 mg/l. This excursion is believed to be naturally occurring, and the licensee has submitted a license amendment request to change the upper control limit. The licensee also plans to maintain an increased monitoring frequency. The licensee stated that well #SM723 is located within a controlled well field with a shallow aquifer and that there was no adverse impact expected on individuals or the environment. (Call the NRC operations officer for licensee contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0 | 2001-12-06
38542 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-12-06 03:50 | 2001-12-06 04:55 | 2001-12-06 | MANUAL REACTOR SCRAM DUE TO A LOSS OF STATOR WATER COOLING The following text is a portion of a facsimile received from the licensee: "At 0350 on 12/6/01 with the reactor at 100%, a manual reactor scram was inserted due to the loss of stator water cooling. All control rods fully inserted into the core. While taking a stator water sample, the heat exchanger vent line broke off the heat exchanger losing stator water from the system. A reactor scram was inserted prior to an [imminent] turbine generator trip." "Following the reactor scram, water level dropped to approximately 120". Reactor water level is being maintained in the normal level band (197") with feedwater/condensate. The following 'Level 3' isolations occurred as expected:" "Group 4 - RHR Shutdown Cooling and Head Spray" "Group 13 - Drywell Sumps" "Group 15 - Traversing Incore Probe Systems" "All valves in [Groups] 4 and 15 were closed prior to the event. Group 13 valves closed as designed. No ECCS systems initiated, and no SRVs lifted. All Emergency Diesel Generators are operable." The licensee stated that the main steam isolation valves remained open and that the main condenser is being used as the heat sink. Containment parameters are normal, and the grid is stable. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-12-06
38541 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-12-05 18:00 | 2001-12-05 20:26 | 2001-12-05 | APPENDIX R REVIEW REVEALED A POTENTIAL FAILURE OF THE MOTOR DRIVEN AUXILIARY FEEDWATER PUMPS The licensee was conducting an Appendix R review and made the following discovery. "Review of the Motor Driven Aux. Feed Pump (MDAFP) response to an Appendix R fire with a coincident loss of off-site power and instrument air indicates an Appendix R concern in Fire Areas A01-B, A02, A23N and A23S, which are the Central Area of the 26' PAB, SI/CS Pump Room, North Aux. Feed Pump Room and South Aux. Feed Pump Room, respectively. In each of these areas, a MDAFP is relied upon as the means of getting Aux Feedwater to at least one Steam Generator for at least one of the Units and both Units for Fire Area A01-B, to support heat removal from the RCS. The review performed, revealed that an Appendix R fire in these fire areas could potentially result in an auto-start of the credited MDAFP, due to fire damage initiating the start signal or trip of the Main Feedwater Pumps. This auto-start signal also opens the mini-recirc. valve for the MDAFP and motor driven discharge valve(s) for the steam generator to be supplied Aux. Feedwater. Due to fire damage, the motor driven discharge valve may fail to open and the mini-recirc valve may fail closed due to a loss of instrument air supply. This could potentially result in dead heading the pump and subsequent damage to the pump. "In response to the discovery of this issue, hourly fire rounds have been initiated in the fire areas affected. With the establishment of this compensatory measure in conjunction with existing guidance contained in operations procedures, the MDAFPs are considered operable." The licensee notified the NRC Resident Inspector. (Refer to event #38618 for additional information.) | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-12-05
38540 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-12-05 10:00 | 2001-12-05 16:25 | 2001-12-05 | EMERGENCY RESPONSE DATA SYSTEM FOUND INOPERABLE The licensee was conducting their quarterly functional test of the Emergency Response Data System (ERDS) and found it to be inoperable. The problem with ERDS is being investigated at this time. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-12-05
38539 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-12-04 18:24 | 2001-12-04 21:58 | 2001-12-04 | 24-HOUR REPORT REGARDING AN OPERATING LICENSE CONDITION VIOLATION (GGNS LICENSE CONDITION F) The licensee discovered an error in the thermal power calculation during an ongoing review previously reported under LER 2001-004-00, Docket #50-416 Thermal Calculation Error. There is an additional error of 5.5 MWth in the calculation due to the original use of the 1936 Steam Tables versus the updated 1969 version. The licensee has reduced reactor thermal power by the 5.5 MWth and is maintaining 3827 MWth for an 8 hour average. The licensee notified the NRC Resident Inspector. See Event #38344 from Grand Gulf. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW | [5 empty] | 0 | 2001-12-04
38538 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-12-04 16:30 | 2001-12-04 17:18 | 2001-12-04 | LICENSEE NOTIFIED THE BETHAL FIRE DEPARTMENT The licensee called on the Bethal Fire Department for help in clean-up of a lift station spill (sewage). Fire header water will be used to flush spill area to yard drains and catch basin for later release in accordance with procedures. No sewage reached the lake. The licensee intends to notify the NRC Resident Inspector, the states of South Carolina and North Carolina, and local counties. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-12-04
38537 | -1 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2001-12-04 12:00 | 2001-12-04 16:03 | 2001-12-21 | FAILURE OF PART OF THE OFF-SITE NOTIFICATION SIRENS TO OPERATE WHEN TESTED The licensee was performing their semi-annual off-site notification siren operational test and found that only 147 of 154 sirens operated properly. The remaining 7 sirens are being investigated for the cause of their failure. The licensee will use the Emergency Plan alternate means of informing the public, including route alerting and public announcements in the event of an accident. The licensee notified the NRC Resident Inspector. * * * UPDATE 1200EST ON 12/21/01 FROM JIM READY TO S. SANDIN * * * The licensee is retracting this report based on the following: "Indian Point Units 1,2 and 3 is retracting the eight (8) hour non-emergency notification made in accordance with 10 CFR 50.72(b)(3)(xiii) on December 4, 2001, at 1603 hours (EN # 38537). The notification reported the loss of a portion of the offsite communication capability due to a failure of 5 of 16 sirens in Orange County to actuate during the semi-annual siren test. The notification was a result of less than a 90% response rate of sirens in one county (Orange). At the time, 5 sirens in Orange County were being investigated for the cause of failure. "Upon subsequent investigation and testing, which was completed on December 13, Entergy determined that this condition was not reportable because the 5 Orange County sirens were acceptable and operable and thereby did not exceed the threshold for notification. The cause of the sirens to appear to have failed was attributed to a discrepancy in test coordination which occurred during the conduct of the siren test. The licensee informed the NRC Resident Inspector. Notified R1DO(Kinneman). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-12-04
38536 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2001-11-30 | 2001-12-04 15:46 | 2001-12-04 | AGREEMENT STATE REPORT - RELEASE OF 5 SOURCES The following is taken from a faxed report: This First Notice constitutes early notice of events of possible safety or public interest significance. The information is as initially received without verification or evaluation, and is basically all that is known by the Agency Staff at this time. Date: December 4, 2001, Time: 12:30 PM (MST), First Notice 01-11 Arizona Licensee: Good Samaritan Regional Medical Center, License No. 07-478 On November 30, 2001 the Arizona Radiation Regulatory Agency was notified of a release of 5 sources of Strontium 90. The Licensee was utilizing a Novoste Beta-Cath system model A1732 with a BEBIG, model No. SrO.SO3 with 12 sources and 60 millicuries in the train. As apart of the Licensee's preparation, the source train was being test run in the device. The Licensee noted the sterile water was less resistant to injection and found a leak. He then retrieved the sources and heard the solenoid click indicating the sources were back in a safe position. The catheter was removed. While checking the system to determine the cause of the leak, the Licensee noted 5 sources were on the floor. The Licensee instituted an inventory and could clearly identify 11 sources with a possible location of the 12th. The Agency assisted the Licensee and determined that all sources were accounted for and approved the return of the device to the manufacturer. The manufacturer is to determine why the device signaled all sources had returned and why one source was trapped within the device. The State of Georgia has been notified of the details of this incident. Agency continues to investigate this event. The State of Georgia,, together with the U.S. NRC, are being notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2001-12-04
38535 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-12-04 11:00 | 2001-12-04 14:57 | 2001-12-04 | EMERGENCY RESPONSE DATA SYSTEM FOUND INOPERABLE The licensee was conducting their quarterly functional test of the Emergency Response Data System (ERDS) and found it to be inoperable. The ERDS was restored to service at 1405 EST on 12/4/01. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-12-04
38534 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-12-03 22:56 | 2001-12-04 04:58 | 2001-12-04 | AUXILIARY FEEDWATER ACTUATION During a controlled plant shutdown, a vibration problem occurred on the Main Turbine that required breaking condenser vacuum. Since breaking condenser vacuum would cause a loss of the operating Main Feedwater pump and generate an Auxiliary Feedwater Actuation signal, both "A" and "B" Motor Driven Auxiliary Feedwater pumps were manually started prior to breaking condenser vacuum. "A" Motor Driven Auxiliary Feedwater pump failed to develop proper flow, so the Turbine Driven Feedwater pump was placed in service. The "A" Motor Driven Auxiliary Feedwater pump was subsequently secured and declared inoperable. A plan of action is being developed to troubleshoot and repair the inoperable "A" Motor Driven Auxiliary Feedwater pump. Initially, Steam Generator Atmospheric Power Operated Relief Valves were being used to control Reactor Coolant System temperature. Condenser vacuum has been restored and currently, Steam Generator water levels are being maintained using the Turbine Driven Auxiliary Feedwater pump with condenser steam dumps maintaining Reactor Coolant System temperature. The NRC Resident Inspector was notified of this event by the licensee. | 1 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Startup | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-12-04
38533 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-12-03 17:34 | 2001-12-03 23:13 | 2001-12-03 | SAFETY EQUIPMENT FAILURE "At 1734 CST, on 12/3/2001, the Plant Shift Superintendent was notified that the C-337 High Pressure Fire Water (HPFW) Sprinkler System 8-14 had been inspected and 4 sprinkler heads had visible corrosion on them. The system configuration and building configuration were evaluated using EN-C-822-99-047. Effects of impaired Sprinkler Heads on System Operability, and determined that with these heads impaired, a portion of the building would not have sprinkler coverage. The sprinkler system is required to be operable according to TSR LCO 2.4.4.5. HPFW Sprinkler System B-14 was declared inoperable and TSR LCO 2.4.4.5 Required Action B was implemented for the area without sprinkler coverage. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2001-12-03
38532 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-12-02 17:21 | 2001-12-02 20:40 | 2001-12-02 | PLANT RECEIVED A SECOND SCRAM WHILE IN MODE 3 Following the manual scram at 1448 the plant had a second scram at 1721 which was an automatic scram on low water level (Level 3 - 159.3") when lowering reactor pressure to inject with the booster pumps at 1721. The scram was reset and plant shutdown and cooldown is continuing. The NRC Resident Inspector was notified. HOO NOTE: see event #38531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-12-02
38531 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-12-02 14:48 | 2001-12-02 18:17 | 2001-12-03 | MANUAL REACTOR SCRAM FROM 75% POWER On December 2, 2001 at 1448, Unit 2 manually scrammed from approximately 75% reactor power due to a low water level trip (159.3" - Level 3). Preliminary indications are an electrical fault/trip on feedwater Pump "A" was the cause of the reactor low level condition. The "A" Recirculation Flow Control Valve (FCV) ran back to minimum position as required on the low level alarm at 178.3" - Level 4. The "B" FCV failed to fully run back as required due to the electrical transient and the subsequent loss of hydraulic control units. The "B" FCV stabilized at 50% open. The Operators were inserting cram rods in an attempt to lower power further when the low water level trip alarm came in for Division 1. The Control Room Supervisor (CRS) ordered the mode switch to shutdown. All Control Rods inserted as required. Reactor water level is being controlled in the normal level band with Condensate Booster pumps. Reactor pressure is being reduced to place the shutdown cooling system in service by the use of the turbine bypass valves. Additionally, indications show that the Neutron Monitoring System (NMS) scram setpoints were exceeded for the Average Power Range Monitoring (APRM) thermal power trip. This trip signal was in close sequence to the mode switch being placed in the shutdown position. The NRC Resident Inspector was notified. HOO NOTE: see event # 38532 * * * UPDATED AT 1734 EST ON 12/3/01 BY TOM RESTUCCIO TO FANGIE JONES * * * "The purpose of this notification is to provide an update to Event #38531. From reviews of plant computer data and alarm printouts, it was determined that the Average Power Range Monitoring (APRM) Thermal Power trip was NOT exceeded. The only APRM scram signal received was the expected APRM neutron monitoring scram which occurred when the mode switch was taken out of the run position. With the mode switch not in run, the APRM neutron monitoring scram setpoint is 15% which was exceeded due to power being at 75%." The licensee notified the NRC Resident Inspector. The R1DO (John Rogge) has been notified. | 0 | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-12-02
38530 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-11-29 | 2001-11-30 14:32 | 2001-11-30 | LEAKING PROMETHIUM SOURCE AT WEYERHAEUSER TECH CENTER The licensee provided notification to the State of Washington that leakage was discovered when a 3 millicurie Promethium-147 source was about to be re-installed in an AMBERTEC Oy model BET- 1 formation tester. At this time it appears that the radioactive source was removed from the formation tester by licensee personnel in mid 1999. The source was placed into a storage container kept under the licensee's control. The un-sourced device was subsequently shipped to the manufacturer in Finland for repair. The device was recently returned to the licensee facility. A Finnish technician accompanying the device tested the source prior to installation and discovered contamination on the source and in the storage container. No contamination was detected on the outside of the container, in the storage location or at the work bench where the device is presumed to have been disassembled two years ago. Other details are unclear at this time and a Division of Radiation Protection staff will be on-site today to investigate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2001-11-30
38529 | 0 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2001-11-29 17:00 | 2001-11-30 14:28 | 2001-11-30 | MEDICAL MISADMINISTRATION AT THE WILLIAM BEAUMONT HOSPITAL A patient was prescribed a total dose of 2,800 centigrays of Ir - 192 given in seven fractions for treatment of recurring cancer. However, the standard fraction dose for 7 fractions @ 500 centigrays/fractions was administered resulting in a total dose of 3,500 centigrays. This misadministration resulted when the authorizing physician initially prescribed seven standard fraction doses(500 centigrays/fraction), but then changed his mind and prescribed seven fractions @ 400 centigrays/fraction which would have resulted in the total prescribed dose of 2,800 centigrays. These treatments took place between 09/27/01 and 11/02/09, but the mistake was not discovered until 11/20/01 @ 1700 during an audit. The error was made when the authorizing physicist did not transcribe from the treatment plan onto the worksheet the correct information used to program the HDR device and put in the 500 centigrays instead of the 400 centigrays. The patient and the referring physician were notified. No adverse affects to the patient are expected. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0 | 2001-11-30
38528 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-11-28 11:00 | 2001-11-30 12:48 | 2001-11-30 | AGREEMENT STATE REPORT - LOST SOURCE A patient receiving palliative treatment for lung cancer had six seeds implanted in the lungs. Each seed contained 0.4 mCi of I-125. After about 2 hours, an x-ray of the lungs was performed to verify positioning of the seeds and 3 of the seeds were missing. A search/survey of the area did not find the missing seeds. It is unknown where the seeds are, it is possible the patient coughed up the seeds and swallowed them. The patient was released later that day. There is minimal threat to any member of the public. California Radiation Control Program office contacted NRC State Programs (Pat Larkin). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-11-30
38527 | 0 | GENESYS REGIONAL MEDICAL CENTER |  |  |  |  | 2001-11-30 09:30 | 2001-11-30 12:03 | 2001-11-30 | INCORRECT SHIPPING PACKAGE USED FOR SHIPPING I-133 TO THE MEDICAL FACILITY The Genesys Regional Medical Center received a shipment of 156 millicuries of I-133 from Syncor International in Flint, Mi. that was packaged in a Yellow - 2 package. Yellow - 2 packages have a 50 mr/hr limit for transporting radiological materials. Syncor had monitored the shipment as 80 mr/hr and the medical facility monitored it at 100 mr/hr. Therefore, it should have been shipped in another type of package(possibly a Yellow - 3). There was no contamination measured. Syncor was notified of this error by the medical center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.1906(d)(2) |  |  |  | 0 | 2001-11-30
38526 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2001-11-29 13:00 | 2001-11-30 10:37 | 2001-11-30 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED EMPLOYEE'S USE OF A CONTROLLED SUBSTANCE A non-licensed employee (supervisor) was determined to be under the influence of a controlled substance. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2001-11-30
38525 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-11-29 15:38 | 2001-11-29 18:07 | 2001-11-30 | A LOSS OF INSTRUMENT AIR MAY CAUSE A POTENTIAL COMMON MODE FAILURE FOR ALL AUXILIARY FEEDWATER PUMPS. Instrument Air (IA) can be lost primarily by two failure mechanisms. The first, and most likely, is a loss of off-site power where the IA and Service Air (SA) compressors are stripped from the bus and not automatically re-loaded. The second less likely scenario is a random loss of the instrument air system due to equipment failure without potential for short term recovery. When IA is lost, the minimum flow recirculation valves for AFW fail closed. During these two transients, the AFW pumps will start injecting into the steam generators. Early in the EOP's, the operator is directed to control flow to the steam generators to maintain desired level. This may include shutting off flow to one or both steam generators if level is above the desired band. If flow from any auxiliary feed pump is reduced too low (as would occur if the auxiliary feed regulating valves are closed) without functional recirculation valves, the pump will fail in a very short period of time. This common mode of failure (common loss of instrument air and common response to high steam generator level) could result in simultaneous failure of all AFW pumps. The Auxiliary Feedwater system has passed all required testing and is currently fully operable and capable of performing its safety function. It is only under the specific circumstances outlined above that a failure of Auxiliary Feedwater may occur. The licensee is taking interim corrective actions in the form of Operating Crew briefs to ensure Auxiliary Feedwater is not damaged under Loss of Air conditions and is evaluating procedural and equipment design changes to provide a permanent correction to Aux. Feedwater. The NRC Resident Inspector will be notified. * * * UPDATE ON 11/30/01 @ 1849 BY RAASCH TO GOULD * * * The purpose of this supplement is to clarify the discussion of the potential failure of one or more Auxiliary Feedwater (AFW) pumps as described in Event Notification #38525. The potential failure is limited to only the minimum recirculation flow control valves for the AFW pumps. These recirculation valves function automatically to provide recirculation flow during periods of low Steam Generator (SG) demand from the AFW pumps. This potential failure mode would manifest itself during a loss of offsite power, with an attendant loss of instrument air, if the operator, while reducing AFW flow to a SG after satisfactory initial filling, fails to recognize that the recirculation valves do not open while reducing AFW flow to the steam generators. This action would have to be done individually to each of the running AFW pumps for multiple failures to occur. The air operated valves for controlling AFW pump output flowrate are safety-related and are not susceptible to this condition since the instrument air supply to these valves is backed up by a safety-related Nitrogen backup system. These valves would continue to be capable of supplying and controlling the required AFW flow to the steam generators. As an interim corrective action, operating personnel were provided a briefing on this potential failure mechanism to ensure the AFW pumps are not damaged under a Loss of Instrument Air condition. Additionally, temporary information tags have been hung to ensure continued awareness until an evaluation of potential procedural and equipment design changes can be completed. The NRC Resident Inspector was notified. The Reg 3 RDO(Jorgensen) was informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-11-29
38524 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-11-29 06:50 | 2001-11-29 16:48 | 2001-11-29 | TRANSPORTATION INCIDENT INVOLVING A TEXAS STATE LICENSEE Ice on bridge caused car in left lane to loose control. Car following swerved into right lane in front of wireline truck traveling approximately 30 mph. Truck could have hit car or move to edge of road, which it did and ended up in the ditch. The truck laid over on it's right side with minor damage to right side of the vehicle - mirror and glass. No damage to sources which were secured in Pigs welded to the floor and wall of the vehicle. The vehicle is to be up-righted and towed to Houston for repairs. RSO for Licensee is on-site and has assessed sources as un-damaged and secure in their storage Pigs. The sources carried by the truck are a Well logging calibration stick(Ra-226), calibration bar(Am-241/Be/Cs-137), a Cs-137 well logging source and a Am-241/Be well logging source. Only minor injuries were received by the two occupants of the truck. Activity readings were normal for the truck. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-11-29
38523 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2001-11-28 | 2001-11-29 16:45 | 2001-11-29 | STATE LICENSEE REPORTED A MEDICAL MISADMINISTRATION A patient was being treated with a brachytherapy dose of Ir-192. The Ir-192 was 6.6 Ci. The facility was performing multiple fractions. Each fraction was supposed to be 440 centigray. Fraction 5 of 6 was 269 centigray, which is more than a 20% difference. The individual making the notification stated that another directive would be written for the sixth fraction so that the patient receives the full 2640 centigray dose. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2001-11-29
38522 | 0 | US GEOLOGICAL SURVEY |  |  |  |  | 2001-11-19 | 2001-11-29 11:00 | 2001-11-29 | RADIOACTIVE SHIPMENT SHIPPED AS EXCEPTED PACKAGE - LIMITED QUANTITY INSTEAD OF DOT 7A YELLOW II The following text describes a mislabeled package shipped via FedEx: "Summary of Incident: 11/19/2001: Samples were irradiated for McCrone & Associates Inc. by the US Geological Survey TRIGA Reactor staff. (Facility license R-1 13, docket 50-274). After irradiation, the samples were surveyed with an ion chamber and analyzed with a germanium detector for nuclide determination. The ion chamber had been response checked that morning. The samples were packaged in Type A shipping container (juice can) that was placed inside a cardboard box. Radiation surveys on the package were conducted using the same ion chamber as before, and contamination surveys were also conducted. All radiation/contamination surveys and isotope activities indicated an excepted package-limited quantity radioactive shipment. These readings were consistent with prior sample irradiations performed for McCrone & Associates. The package, reading 0.42 mr/hr on the surface was sent from Denver, CO to McCrone and Associates Inc (in a Chicago suburb) via FedEx overnight. 11/20/2001: McCrone's Radiation Safety Officer notified USGS Reactor staff that the package containing the samples had been received and the surface of the box read 4 mr/hr with their Geiger-Mueller pancake detector. No contamination was found on the package. The package was opened only to remove the paperwork and then was placed behind lead shielding. The calibration of the USGS meter that was used to survey the outgoing package was checked and the meter was found to be defective. A good USGS ion chamber was sent via FedEx overnight to McCrone to get comparison readings. 11/21/2001: Radiation readings were taken on top of the Type A container (inner package) with McCrone's detector (3.0 mr/hr) and with USGS detector (1.8 mr/hr). Calculations were performed to estimate the radiation levels on the surface of the package and the transport index when it was shipped. These calculations were based on the half-life of Na-24, the predominant isotope, and the readings taken by McCrone & Associates approximately 19 hours after the package was shipped by USGS. These calculations indicate the package read approximately 5.8 mr/hr on the surface and had a transport index of 0.1 at the time of shipment. With a transport index of 0.1 and shipment time of 19 hours (allowing 5 hours for flight) a person at one meter from the package the total 14 hours would receive 1.4 mrem. We believe this calculation represents a very conservative maximum exposure received from the package by any one individual during the shipment. FedEx was notified of the mislabeled package (Harold Brooks with the Dangerous Goods Department). The State of Illinois has also been notified by McCrone and Associates personnel. The shipping department of the USGS at the Denver Federal Center has also been notified of the incident. Conclusions: No radioactivity was released from the package. FedEx workers received an estimated 1.4 person-mrems during shipment of this package. Follow-up: Further investigations will be performed to determine actions that can be taken to prevent similar incidents from occurring in the future. A comprehensive written report will be submitted by December 3, 2001." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | CO | MAT | [5 empty] | 0 | 2001-11-29
38521 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-11-28 18:20 | 2001-11-28 20:00 | 2001-11-28 | CONFIRMATION OF A LOOSE PART IN THE REACTOR SYSTEM (DISCOVERY OF AN OBSTRUCTION IN A JET PUMP NOZZLE) During a daily jet pump surveillance test at approximately 1800 CST on 11/27/01, the licensee discovered that the flow through reactor recirculation jet pump #13 was reduced. Although one of three surveillance criteria was not met, the jet pump and recirculation system remained operable because at least two of the three criteria were met. The surveillance criteria that was not met involved a deviation of jet pump flows from one jet pump to the other jet pumps (i.e., flow not being within 10% of an established pattern). The licensee reported that the loose parts detection system was not working and was undergoing a review for potential removal. However, further analysis today (11/28/01) confirmed that one nozzle of jet pump #13 is obstructed by a loose part. The obstruction size and type have not yet been determined. Additional investigations are ongoing. The licensee stated that confirmation of a loose part in the reactor system constitutes a 1-hour reportable event in accordance with procedure 01S065. This was also reported to be a commitment in the Final Safety Analysis Report. The licensee contacted General Electric and the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW | [5 empty] | 0 | 2001-11-28
38520 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2001-11-28 06:00 | 2001-11-28 11:50 | 2001-11-28 | AGREEMENT STATE REPORT REGARDING A TRI-STATE TESTING AND DRILLING, INC. TROXLER MOISTURE DENSITY GAUGE STOLEN IN CHATTANOOGA, TENNESSEE The following text is a portion of a facsimile received from the State of Tennessee, Department of Environment and Conservation, Division of Radiological Health: "Event Report ID No.: TN-01-217" "License Number: R-33105" "Licensee: Tri-State Testing and Drilling, Inc." "Event date and time: November 28, 2001, approx. 0600 EST" "Event location: Chattanooga, TN" "Event type: Stolen moisture density gauge" "Notifications: Tennessee Emergency Management Agency, USNRC Region II, Alabama Office of Radiation Control, Georgia Radioactive Materials Program, Chattanooga Police Department" "Media interest: None at this time. A press release is being issued by TDEC." "Event description: Tri-State Testing and Drilling, Inc. reported a Troxler moisture density gauge, Model 3440, SN 17252, containing 8 millicuries of Cesium-137 and 40 millicuries of Americium-241:Beryllium, was stolen from the bed of a pickup truck early this morning. The gauge was chained in the back of the truck parked at an employees residence. Thieves cut the chain and removed the locked container. State DRH inspectors are onsite investigating at this time." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2001-11-30
38519 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2001-11-26 18:15 | 2001-11-26 18:43 | 2001-11-26 | UNUSUAL EVENT DECLARED DUE TO A SMALL FIRE LASTING GREATER THAN 15 MINUTES At approximately 1745, the control room was notified of heavy smoke. At 1815, the licensee declared an Unusual Event based on a small fire in the industrial area of the plant lasting greater than 15 minutes. Preliminary indications revealed that the incident may have been related to an electrical fire involving the heating element or switch of a drum dryer located in the old chemistry lab. There was no release of radiological or hazardous materials, and there were no personnel injuries. The Fire Department is currently on site, and the fire is believed to be under control. The control room is currently waiting for confirmation that the fire is out in order to terminate the Unusual Event. The licensee notified the State Police and Fire Department. ***** UPDATE FROM RONALD HOWARD TO LEIGH TROCINE AT 1918 ON 11/26/01 ***** The licensee terminated the Unusual Event at 1900. The fire is out, and it is currently believed that the fire was cause by a short in the drum dryer's electrical system. The licensee notified the State Police and plans to notify the Fire Department. The NRC operations officer notified the R1DO (Ruland), NRR EO (Adensam), IRO (Mamish), and FEMA (Gene Kanupp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 1 | ME | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-11-26
38518 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-11-26 12:32 | 2001-11-26 13:37 | 2002-03-01 | ERDS INOPERABLE DUE TO PLANNED OUTAGE OF THE PLANT PROCESS COMPUTER SYSTEM (PPCS) AT 1232 CT, the Point Beach Nuclear Plant ERDS became inoperable as a result of modifications to change out the plant process computer system (PPCS). This is a planned evolution. ERDS will remain inoperable until approximately, December 18, 2001. This information was verbally provided to a representative of NRR during the week of 10/15/2001. The senior resident inspector has also been briefed on the modifications and schedule. NMC to NRC letter (NRC 01-0080) dated 11/21/2001 stated we would be submitting this Non-Emergency report. ***** UPDATE FROM RICK ROBBINS TO LEIGH TROCINE AT 2006 EST ON 11/27/01 ***** The following additional information is a portion of a facsimile received from the licensee: "As part of the PPCS modification, several inputs to the SPDS monitor were also made unavailable. Any out-of-service indications on the SPDS can be obtained by control room control board indications." The licensee notified the NRC resident inspector. The NRC operations center notified the R3DO (Bruce Jorgensen). * * * UPDATE 1259EST ON 12/22/01 FROM RYAN RODE TO S. SANDIN * * * The licensee provided the following information as an update: "On 11/26/01 at 12:32, the PBNP ERDS and SPDS were declared out of service for the PPCS upgrade project. EN #38518 indicated to the NRC that the systems would remain unavailable until approximately December 18, 2001. Due to reliability issues with the newly installed PPCS, that expected date has been delayed to approximately January 3, 2002." The licensee informed the NRC Resident Inspector. Notified R3DO(Phillips). * * * UPDATE ON 01/03/02 @1430 BY MEYER TO GOULD * * * During the installation of the new PPCS, issues were identified which need to be resolved to allow SPDS and ERDS to be placed back in service fully. Currently, the new PPCS is only partially operable. Work is continuing on the new PPCS to allow full operability. The current estimate for return to service of SPDS and ERDS is 01/19/02. This date may need to be extended again due to parts availability. The NRC Resident Inspector was notified. Notified Reg 3 RDO(Shear) * * * UPDATE ON 1/17/02 @ 1855 BY HARRSCH TO GOULD * * * Update to 1/3/02 update (see below). Work continues on the Plant Process Computer System (PPCS) to allow full operability. The Safety Parameter Display System (SPDS) is still out of service, however the Emergency Response Data System (ERDS) is now available. As mentioned in the 1/3/02 update, parts availability has been a problem and the date for returning SPDS to service is now estimated to be 2/16/02. The NRC Resident Inspector was notified. Reg 3 RDO(Vegel) was informed ***UPDATE ON 2/15/02 @ 1323 EST BY ADAMS TO NORRIS*** Update to 1/17/02 update. Work continues on the Plant Process Computer System (PPCS) to allow full operability. The Safety Parameter Display System (SPDS) is still out of service. Due to parts availabilty, the date for returning SPDS to service is now estimated to be 3/09/02. The NRC Resident Inspector was notified. Reg 3 RDO(Vegel) was informed. ***UPDATE ON 3/1/02 @ 1145 EST BY MILLEN TO NORRIS*** Update to 1/17/02 event notification. As part of the upgade to the Plant Process Comuter System (PPCS), the Safety Parameter Display System (SPDS) has been accepted for use and is considered fully operational. The NRC Resident Inspector was notified. Reg 3 RDO (Lipa) was informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW | [5 empty] | 0 | 2001-11-26
38517 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2001-11-26 06:18 | 2001-11-26 06:42 | 2001-11-26 | UNUSUAL EVENT DECLARED DUE TO REACTOR COOLANT LEAKAGE GREATER THAN 10 GALLONS PER MINUTE, EMERGENCY ACTION LEVEL (EAL) 1A. "Reactor Coolant System leakage greater than 10 gpm while placing the Shutdown Cooling System in service during a planned unit shutdown for refueling. Leak has been isolated. Event has been terminated. "Relief valve 3483 lifted while placing the SDC system in service. Relief valve setpoint is 350 psia. RCS pressure at the time of event was 268 psia. Relief valve lifted when the Hot Leg Suction Valve from RCS to the SDC system was opened. Leak was isolated & event terminated by closing the Hot Leg Suction Valve. Leakage from the relief valve was directed to the Chemical & Volume Control System Hold Up Tank" Unusual event was declared and terminated at the same time (0618). State and local officials were notified of this event by the licensee. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-11-26
38516 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-11-25 16:20 | 2001-11-26 06:24 | 2001-11-26 | 24-HOUR NRC BULLETIN 91-01 REPORT "During an NCS annual assessment by operations personnel, two cardboard boxes with unfavorable geometry were found inside an area controlled by NCSA-326_014 A02. This Is a violation of control #17 of the NCSA that requires unfavorable items capable of holding solution shall have holes to provide drainage such that no more than one inch of solution can accumulate in them. "This resulted in a violation of the double contingency principle where control was reestablished and is reportable under NRC BL 91-01. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is low. The open cardboard box was not under any overflow line or seal exhaust lines and the seal exhaust station is not operating. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "During operation of the seal exhaust station the contents of the seal exhaust lines could have sprayed in to the box to cause a criticality. "CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION, ETC.): "The first control was the requirement to have drainage holes in unfavorable geometry containers. The second control was that it was unlikely an unfavorable geometry container would be positioned in a location that seal exhaust oil would spray into the container. "ESTIMATED AMOUNT. ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "The licensed material would be UF4 in oil with a maximum enrichment of 20% U-235 "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Control #17 of the NCSA that requires unfavorable items capable of holding solution shall have holes to provide drainage such that no more than one inch of solution can accumulate in them. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "The cardboard boxes were removed from the area controlled by NCSA-326_014.A.02" The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-11-26
38515 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-11-24 03:30 | 2001-11-24 11:00 | 2001-11-24 | OFFSITE NOTIFICATION REGARDING RELEASE OF NONRADIOACTIVE CHEMICALLY TREATED WATER "During routine surveillance run of Fire Protection Pump X-05, the shutdown of the pump caused a momentary drop in system pressure resulting in the autostart of Fire Protection Pump X-04. The start of the second pump resulted in a momentary pressure surge that caused a pipe cap to separate releasing approximately 6,500 gallons of nonradioactive, chemically treated water to the environment and Squaw Creek Reservoir. "Fire protection water is treated with Bulab 6002. This spill is reportable to the Texas Natural Resource Conservation Commission (TNRCC). TNRCC was notified at 0815 CST on 11/24/01. "Actions taken to contain/control the spill were adequate. Monitoring for fish kill is ongoing. No evidence of fish kill is evident to date." The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-24
38514 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-11-23 18:00 | 2001-11-23 19:38 | 2001-11-23 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED OPERATOR A licensed employee was determined to be under the influence of alcohol during a random test. The licensee took the employee home. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2001-11-23
38513 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-11-23 12:10 | 2001-11-23 12:30 | 2003-03-16 | OFFSITE NOTIFICATION TO FLORIDA STATE INVOLVING RECOVERED SEA TURTLE FROM UNIT 1 INTAKE STRUCTURE "A sea turtle with no external injuries but appearing to be distressed was recovered from the Unit 1 Intake Structure. The State Stranding Coordinator for sea turtles has been contacted." * * * UPDATE 11/23/01 AT 1255EST FROM CHARLIE PIKE TO S. SANDIN * * * "Turtle has died." The licensee informed both the State of Florida and the NRC Resident Inspector. * * * UPDATE 1413EST ON 12/3/01 FROM JACK BREEN TO FANGIE JONES * * * At approximately 1215 EST on 12/3/01, a report was made to the Florida Department of Fish and Wildlife concerning the recovery of an injured sea turtle from the plant's intake canal. The turtle was a green sea turtle in the intake canal that appeared distressed and looked to have a wound from a boat motor on its back. It will be transferred to the State for rehabilitation. The licensee plans to notify the NRC resident inspector. Notified R2DO(MacAlpine). * * * UPDATE 1333EST ON 12/15/01 FROM JACK BREEN TO JOHN MACKINNON * * * At approximately 1215 EST on 12/15/01, a report was made to the Florida Department of Fish and Wildlife Conservation Commission to pick up a Green Turtle for rehabilitation. The Green Turtle was taken from the plant's intake canal, and the turtle appears to have shark bites. The licensee plans to notify the NRC resident inspector. Notified R2DO (Chuck Ogle). * * * UPDATE 1450EST ON 01/06/02 FROM TULLIDGE TO JOHN MACKINNON * * * At 1350EST, a notification to the State of Florida Department of Fish and Wildlife Conservation Commission was made due to finding an injured Loggerhead sea turtle in Unit 1 intake. The sea turtle was transported offsite for rehabilitation. R2DO (Tom Decker) notified. The licensee notified the NRC Resident Inspector. ***UPDATE 1330EST ON 4/23/02 FROM JACK BREEN TO RICH LAURA*** The licensee rescued a Loggerhead sea turtle from the intake canal. The Florida Fish and Wildlife Conservation Commission was notified, and the turtle was turned over for rehabilitation. The NRC Resident Inspector was informed. Notified R2DO (B. Bonser). ***UPDATE 1241EDT ON 5/29/02 FROM DAVE WILLIAMS TO RICHARD LAURA*** The licensee reported that an offsite notification was made to the Florida Fish and Wildlife Conservation Commission concerning the discovery of a live loggerhead sea turtle found in the plant's intake canal. The turtle was lethargic and was sent for rehabilitation. The NRC Resident Inspector was informed. Notified R2DO (K. Landis). ***** UPDATE AT 1125 EDT ON 06/01/02 FROM CHARLES MARPLE TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "At 1020 on 06/01/02, a notification was made to the Florida Fish and Wildlife Conservation Commission regarding a weak and emaciated Loggerhead turtle found in the plant intake barrier net. The turtle will be sent off-site to the Marine Life Center for Rehabilitation." The licensee notified the NRC resident inspector. The NRC operations officer notified the R2DO (Kerry Landis). *****UPDATE AT 11:53 EDT ON 6/2/02 FROM MARPLE TO LAURA****** "A notification was made to the Florida Fish and Wildlife Conservation Commission regarding a dead small green sea turtle found in the tangle net. The turtle will be maintained on ice for a postmortem examination." The NRC resident inspector was notified. Notified R2DO (K. Landis) *****UPDATE AT 12:45 EDT ON 7/18/02 FROM BREEN TO LAURA****** A notification was made to the State regarding a dead green sea turtle that was removed from the intake canal. The NRC resident inspector will be notified. Notified R2DO (C. Payne ***UPDATE AT 1045 EDT ON 10/20/02 FROM KORTH TO NORRIS*** A Loggerhead turtle was retrieved from the plant's intake canal. The turtle was in need of rehabilitation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 0927 EDT. The NRC Resident Inspector has been notified. Notified R2DO (Barr) * * * UPDATE AT 1338 EDT ON 10/22/02 FROM KELLY KORTH TO GERRY WAIG * * * A Loggerhead turtle was retrieved from the plant's intake canal. The turtle was in need of rehabilitation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1250 EDT. The NRC Resident Inspector will be notified by the licensee. Notified R2DO (Bob Haag) * * * UPDATE ON 11/22/2002 @ 1821 BY FIELDS TO GOULD * * * The licensee notified the Florida Department of Environmental Protection of the recovery of a distressed loggerhead sea turtle from their intake canal. The turtle was taken to a rehabilitation facility. The NRC Resident inspector will be notified. Notified R2DO (David Ayres). * * * UPDATE AT 1320 EST ON 12/16/02 FROM BILL PARKS TO GERRY WAIG * * * "On 12-16-02, two loggerhead turtles were retrieved from the plant's intake canal. The turtles were determined to be in need of rehabilitation. The injuries to the turtles are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1230 EST. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC." The NRC Resident inspector will be notified. Notified R2DO (Mike Ernstes). * * * UPDATE AT 1350 EST ON 1/25/03 FROM DAVE FIELDS TO MIKE RIPLEY * * * "The State of Florida Department of Environmental Protection was notified that an injured juvenile loggerhead sea turtle was retrieved from the plant intake canal. The turtle was sent to a rehabilitation facility." The NRC Resident inspector will be notified. Notified R2DO (Ken Barr). * * * * UPDATE AT 1140 EST ON 2/12/03 FROM ALAN HALL TO MIKE RIPLEY * * * * On 02/12/03 (approximately 1030 hrs), one loggerhead turtle was retrieved from the plant's intake canal. The turtle was determined to be in need of rehabilitation. The injury to the turtle is not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1040 EST. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC." The licensee notified the NRC Resident Inspector. Notified R2 DO (C. Ogle). * * * UPDATE AT 1313 ON 3/16/03 FROM TEREZAKIS TO GOULD * * * On 3-16-03, a loggerhead sea turtle was retrieved from the plants intake canal. The turtle was determined to be in need of rehabilitation. The injuries to the turtle are not causal to plant operation. Per the plant's turtle permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1140 EST. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of FWCC. The NRC Resident inspector will be informed Notfied Reg 2 RDO(Ayers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-23
38512 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-09-30 | 2001-11-20 17:07 | 2001-11-20 | INVALID PCIS GROUP 3 ISOLATION - ALTERNATE LER REPORT "This notification is being made in accordance with 10CFR50.73 (a) (2) (iv) (A), which provides for an optional telephone notification, instead of submitting an LER. "The purpose of this communication is to provide notification pertaining to the invalid actuation of the PCIS Group 3 isolation signals which affected containment isolation valves in more than one system. "On September 30, 2001, with the reactor at full power, an invalid actuation of a Refuel Floor High Radiation Monitor caused a Group 3 isolation to occur. A spike due to electronic noise invoked the High Level Trip to this monitor (RM-17-453B), which resulted in a trip to PCIS logic Channel B1. "The system started and functioned successfully since either Channel A1 or Channel B1 provides for a complete group 3 isolation. "The train actuation was complete. The PCIS Group 3 isolation occurred and both trains of the Standby Gas Treatment System started as designed. "It was determined that the Group 3 isolation was invalid, due the Refuel Floor High Radiation Level Trip occurring at 35 mR/hr. General area radiation levels on the refuel floor were 10 mR/hr. The prescribed set point of 70 mR/hr had drifted to 35 mR/hr. " The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-11-20
38511 | 0 | EDWARDS PIPELINE SERVICES |  |  |  |  | 2001-11-20 08:00 | 2001-11-20 09:43 | 2001-11-20 | LICENSEE REPORTED A STOLEN RADIOGRAPHY CAMERA A Spec 150 radiography camera serial # 446 was stolen from a mobile darkroom in Mobile, Alabama. The camera contained 58 curies of Iridium-192 serial # HI1815. The individual, however, did not take the controls for the camera. The licensee's technicians chased the thief, but he escaped in a car. The Mobile Police were notified along with the State of Alabama and the licensee will notify the State of Oklahoma. The licensee's Alabama license number is 1333 and the Oklahoma license number is 23193-02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | OK | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-11-20
38509 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2001-11-16 12:30 | 2001-11-16 17:53 | 2001-11-16 | DISCOVERY THAT CERTAIN SAFETY-RELATED COMPONENTS COULD BECOME SUBMERGED DURING A POTENTIAL FLOODING SCENARIO The following text is a portion of a facsimile received from the licensee: "The Wolf Creek Nuclear Operating Corporation (WCNOC) is reviewing calculations and assumptions regarding its flooding analysis. Internal room flooding calculation FL-04 for Auxiliary Building Rooms 1206 and 1207 is based on a maximum flood rate of 3500 gpm. Research into this maximum flood rate indicates the value was based upon the required flow rate to the Condensate Hotwell from the Condensate Storage Tank (CST). The non-safety related 10" pipe which is routed through rooms 1206 [and] 1207 provides water at a flow rate greater than 3500 gpm from the CST to the Condensate Hotwell. Engineering review found that the subject rooms (1206 [and] 1207 are connected) could flood given a Safe Shutdown Earthquake and a subsequent double guillotine break of the non-safety related 10" line within the room. Multiple trains of safety related equipment exist in this room, and are at an elevation such that these components could become submerged during the flooding. Subsequently, WCNOC is reporting this issue as an event or condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident." "Upon discovery, WCNOC has throttled valve AP-V012 Condensate Storage Tank Outlet Isolation to one-third open, thereby eliminating the potential of flooding in excess of the capability of the floor drain system in the subject rooms given a Safe Shutdown Earthquake." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-11-16
38508 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2001-11-15 21:30 | 2001-11-16 14:39 | 2001-11-16 | AGREEMENT STATE REPORT REGARDING A TRANSPORTATION ACCIDENT INVOLVING A RADIOGRAPHIC CAMERA IN SPANISH FORK CANYON, UTAH The following text is a portion of a facsimile received from the Utah Department of Environmental Quality, Division of Radiation Control: "Event Report ID No.: UT-01-0004" "License No.: 17-19236-02 (Reciprocity)" "Licensee: H&H X-Ray Services, Inc. d.b.a. H&H X-Ray Services, Inc.; Monroe X-Ray Co., Inc.; [...] Mississippi X-Ray Service; Waggoner & Associates West Monroe, Louisiana [...]" "Event Date and Time: Date: 09/15/01 Time: Prior to 9:30 p.m. MST" "Event Location: Spanish Fork Canyon near Spanish Fork, Utah" "Event Type: Transportation Accident involving a Radiographic Camera" "Notifications: The Utah Division of Radiation Control was notified by a Utah licensee (Quality Testing and Inspection) on 09/16/01 at approximately 9:00 a.m. MST. The Radiation Safety Officer for Quality Testing and Inspection indicated that he was contacted on 09/15/01 by the Spanish Fork City Fire Department and asked to assist with an accident involving radioactive material. He assisted in surveying the radiographic exposure device and then took possession of the device." "[...]" "Event Description: H & H X-Ray Services, Inc. was approved to work in Utah under the provisions of reciprocity. The licensee's radiography truck was transporting a radiographic exposure device (Amersham Corporation Model 660 B, serial number B2521 containing 61 curies of iridium-192, sealed source model number 424-9, serial number 01453B). The licensee's truck was involved in a one-car rollover accident. The radiographic camera and radioactive source were observed to be undamaged. However, the lid to the steel drum that the exposure device was packaged for transport in came off as a result of the accident. The reciprocity licensee is making arrangements for the exposure device to be leak tested and transferred to Diamond H. Testing in Idaho, [...]. The individual driving the licensee's vehicle was unharmed, and no significant radiation doses resulted from this incident." "Transport Vehicle Description: H&H X-Ray Services, Inc., radiography truck." "Media Attention: None" (Call the NRC operations officer for contact information for the State Department of Environmental Quality, Division of Radiation Control; H&H X-Ray Services, Inc.; Quality Testing and Inspection; and Diamond H. Testing.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2001-11-20
38507 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2001-11-16 11:30 | 2001-11-16 12:31 | 2001-11-16 | AGREEMENT STATE REPORT A vial containing approximately 6.64 mCi of S-35 was discovered to be missing from a laboratory refrigerator. The material had last been handled on 10/31/01 when a researcher removed 0.36 mCi of the material for an experiment. The university is currently investigating this issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2001-11-20
38506 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-11-16 10:15 | 2001-11-16 12:09 | 2001-11-16 | DISCOVERY OF A COMPROMISE OF SAFEGUARDS INFORMATION The licensee reported the discovery of a compromise of safeguards information in accordance with 10CFR73.71(b)(1). Immediate compensatory measures were taken upon discovery. (Contact the NRC operations officer for additional details). The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-11-16
38505 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-11-11 18:00 | 2001-11-16 10:57 | 2001-11-16 | DELIVERED RADIOACTIVE MATERIAL LEFT OUTSIDE UNATTENDED FOR SEVERAL HOURS. DelMed Courier delivered a package containing 19.5 millicuries of Iodine-125 from Syncor located in Golden, Co to Syncor located in Stanford, CT on November 11, 2001. DelMed Courier arrived after closing hours for Syncor. The DelMed Courier delivery person did not have the key to open a door to place the package inside the Syncor building. Therefore the delivery person placed the package containing the radioactive material inside a unmarked box and left it outside by the delivery door. Several hours later the licensee arrived and found the unmarked box containing the radioactive material inside. The box had not been tampered with or opened. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-11-20
38504 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-11-14 | 2001-11-14 17:53 | 2001-11-14 | SPDS/ERIS TURNED OFF DUE TO REFUEL OUTAGE WORK "On November 14, 2001, both SPDS/ERIS systems were turned off due to refuel outage work. Power to these systems will remain off for approximately 36 hours. "This report is being made in accordance to 10CFR50.72(b)(3)(xiii). "Loss of Emergency preparedness Capabilities -Safety Parameter Display System (SPDS) "Loss of Communications Capability - ERDS modem will be out of service "All other capabilities and communications are available." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-11-14
38503 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-11-14 09:00 | 2001-11-14 10:05 | 2001-11-14 | OFFSITE NOTIFICATION REGARDING THE RECOVERY OF AN INJURED SEA TURTLE The following text is a portion of a facsimile received from the licensee: "At approximately 0900 on 11/14/01, a report was made to the Florida Department of Fish and Wildlife concerning the recovery of an injured sea turtle from the plant's intake canal. The turtle was a loggerhead found impinged at the top of the barrier net. It will be transferred to the turtle hospital in Marathon, Florida, for rehabilitation." The licensee plans to notify the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-14
38502 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2001-11-14 08:45 | 2001-11-14 09:59 | 2001-11-14 | OFFSITE NOTIFICATION MADE TO LOCAL FIRE DEPARTMENT Portable propane cylinder (100 lbs) found to be leaking inside the Turbine Building which is currently under demolition. Estimate approximately 60 lbs of propane released. 19 people evacuated from the Turbine Building at 0855ET. Local Fire Department was called to the site and is investigating the reason why the propane cylinder leaked. Nobody was injured. NRC Region 1 (John Wray) notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-14
38501 | 0 | US ARMY |  |  |  |  | 2001-10-25 | 2001-11-13 15:35 | 2001-11-13 | CHEMICAL AGENT DETECTOR CONTAINING AN AMERICIUM-241 SOURCE DETERMINED MISSING An M43A1 Chemical Agent Detector (S/N Z03D23750/C24967) was assigned to the "A" Company 70th Engineer Battalion located at Ft. Riley, KS for use in a training exercise conducted at Ft. Irwin, CA between 9/18 - 9/23/01. During an inventory conducted on 10/25, it was determined that the 250 microcurie Americium-241 source was missing. An extensive search was conducted, however, the source could not be located. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-11-13
38500 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-11-09 | 2001-11-13 15:21 | 2001-11-13 | AGREEMENT STATE REPORT INVOLVING A TROXLER GAUGE STOLEN FROM A TxDOT FIELD OFFICE "The gauge is suspected of being stolen during the hours of darkness on the evening of November 9, 2001. The site was discovered vandalized by a contractor on the morning of November 10, 2001. However, it was thought that only the contractors equipment had been broken into. A portable generator was stolen, as was a water truck which had been driven through the front (locked) gate. The truck was found abandoned approximately 2 to 2 ½ miles from the site abandoned in a field. When TxDOT personnel arrived on site Monday November 12, 2001, they discovered that their site trailer had also been broken into. The door lock and knob were broken as was a rear window to the trailer. Inside, the locked closet had it's hasp and lock pried from the door. The only thing missing was the gauge and it's transportation case, although other high dollar equipment was also locked in the closet and computers/printer, etc were located in the trailer. The gauge was in a locked trailer, locked in it's transportation container and had the control rod locked. A police report was filed with the Denton County Sheriff's Office. This gauge was ... transferred to TxDOT under contract September 12, 2001. The gauge has been maintain at the temporary job site since that date." "Texas Incident No.: I-7827 "Licensee: Texas Department of Transportation, McKinney Area Office "Event Location: 12000 Highway 380, Crossroads, Texas 76227 (TxDOT - Field Office) a locked Field Office Trailer "Event Type: Stolen Radioactive Material - Troxler Nuclear Gauge "Notifications: CRCPD, surrounding states, Troxler R.S.O., Texas Public Health Region #3 (Arlington)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-11-15
38499 | 0 | NTH CONSULTANTS |  |  |  |  | 2001-11-13 08:30 | 2001-11-13 12:07 | 2001-11-13 | LICENSEE REPORTED A STOLEN TROXLER MOISTURE DENSITY GAUGE A Troxler gauge model 3401B serial # 14234 containing 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be was stolen from the back of a pickup truck with a cap sometime between 11/7 and 11/13. The cap was still locked and the case was still in the truck, but the device had been removed. The lock on the case was removed, but had not been cut. Both the Detroit and Warren, Mi. police Departments have been notified. A press release may be issued. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-11-13
38498 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-11-13 06:03 | 2001-11-13 08:59 | 2001-11-13 | REACTOR VESSEL HEAD PENETRATION THROUGH WALL LEAK DISCOVERED "North Anna Unit 2 Reactor Vessel head has an apparent through wall leak on penetration number 63. Engineering decided to treat this penetration as a through-wall leak based on the qualified visual inspection results and liquid penetrant examination of an excavated finding. "A portion of the weld around penetration 63, approximately 2.75" long, has been excavated to a depth of approximately 1" of weld material. The liquid penetrant exam of this excavation shows there is an indication located in the outside edge of the weld almost the full length of the excavation, and which turns into the weld at the uphill and downhill ends of the excavation. "Further evaluation will continue. Unit 2 was in a shutdown mode to perform reactor vessel head penetration inspections per NRC Bulletin 2001-01." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | RESPONSE-BULLETIN |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-11-13
38497 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2001-11-12 21:00 | 2001-11-13 02:16 | 2001-11-13 | ERDS DISCOVERED INOPERABLE "...This report is being made pursuant to 10 CFR 50.72(b)(3)(xiii) and Exelon Reportability Manual SAF 1.10. At 2100 hours on 11/12/01, it was discovered that the Emergency Response Data System (ERDS) was not operational. This system provides a data link between the LaSalle onsite computer system and the NRC Headquarters Operational Center when activated during emergency situations. The ERDS system was restored to an operable status at 2320 hours on 11/12/01 after resolving a computer system software issue. The NRC resident inspector has been notified of this event." The discovery was made while conducting training of a new candidate. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-11-13
38496 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-11-08 20:57 | 2001-11-12 12:37 | 2001-11-12 | INVALID RPS ACTUATION DURING STARTUP DUE TO A BLOWN FUSE "Beaver Valley Power Station is retracting its previous 10 CFR 50.72(b)(3)(iv) notification from 11/9/2001, EN# 38486. The automatic Reactor Protection System (RPS) actuation that occurred on 11/8/2001 was initiated by a blown fuse in the N36 intermediate range nuclear flux instrument causing a high intermediate range reactor trip signal to be generated. The blown fuse was not in response to actual plant conditions and is not a parameter satisfying the requirements for initiation of the safety function of the system. Hence this RPS actuation was not a valid actuation since there was no actual high flux condition within the reactor. Therefore, this event is not reportable pursuant to 10 CFR 50.72(b)(3)(iv)(A) since the automatic trip was not generated by a valid actuation. "This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since this event involved an automatic actuation of the Reactor Protection System which was not part of a pre-planned sequence, did not occur with the RPS properly removed from service, and did not occur after the safety function of dropping the control rods had already been completed. "However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification instead of submitting a written LER since the automatic reactor trip occurred with the reactor subcritical, and was not generated by a valid actuation. On 11/8/2001, all control rods inserted due to the blown fuse initiating a reactor trip on a one out of two high intermediate range high power. All required safety systems operated as designed and the plant was stabilized in Mode 3." The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A/R | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-11-12
38495 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-11-12 10:45 | 2001-11-12 12:28 | 2001-11-12 | LARGE FISHKILL REPORTED TO THE STATE OF NEW JERSEY The New Jersey Department of Environmental Protection was notified of a large fishkill(approximately several hundred fish) in their discharge canal. Most of the fish were Jack fish, but there were also other species. The cause is from the unplanned unit shutdown on 11/11/01. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-12
38494 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-11-10 03:14 | 2001-11-12 11:20 | 2001-11-12 | DETERMINATION MADE THAT A PREVIOUSLY TERMINATED EVENT MET THE CRITERIA FOR EMERGENCY PLAN ENTRY "This report is being made due to the determination that a previously terminated event had met the criteria for emergency plan entry. "At approximately 03:14 on 11/10/01, St. Lucie Unit 1 was operating in Mode 4. The Shutdown Cooling System had been secured for approximately 15 minutes when a realignment sequence was initiated to place the system back in service. During the performance of this evolution, thermal relief valve V3431 lifted and did not immediately reseat. The event was terminated when the 1B Low Pressure Safety Injection Pump was secured and the relief valve reseated. "Initial assessment of the leakage rate, while the relief valve was open, concluded that the flow rate was less than 10 gpm and therefore did not meet the threshold for Emergency Plan entry. A Condition Report was initiated to perform a more in depth analysis of the event. "Subsequent, detailed analysis of the event has determined that the flow rate from the relief valve did exceed the 10 gpm criteria for Emergency Plan implementation." The licensee notified the NRC Resident Inspector and intends to notify the State and Local Authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2001-11-12
38493 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-11-12 03:35 | 2001-11-12 04:59 | 2001-11-12 | INDICATION OF PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING VISUAL INSPECTION OF HEAD The licensee was conducting visual inspection of the reactor vessel control rod drive mechanism (CRDM) nozzles in response to the NRC Bulletin 2001-01. They discovered indications of leakage evidenced by minor boric acid buildup around 4 CRDM nozzles. There is potential for 3 additional nozzles leaking that will require further inspections. Additional inspections and repairs will be conducted in accordance with NRC Bulletin 2001-01. The plant will remain at or below Cold Shutdown until repairs are completed. The licensee notified the NRC Resident Inspector. (Note: See similar events #38416, 38365, 38169) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | RESPONSE-BULLETIN |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-11-12
38492 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-11-11 17:45 | 2001-11-11 22:23 | 2001-11-11 | HPCI SYSTEM DECLARED INOPERABLE "At 1727 EST, Unit 1 received a 'high level' alarm for the HPCI Turbine Steam Supply line Drain Pot. Investigation revealed that power was lost to the solenoid on one of the steam line drain valves causing it to fail closed. In this configuration, condensate is no longer drained from the HPCI Steam Supply line so there would be a potential for water to enter the turbine upon a HPCI initiation. Given this concern, the HPCI system was declared inoperable at 1745 EST when actions were taken to align the system in a configuration to prevent an automatic initiation (breaker was opened for the Aux Oil Pump and the Flow Controller was placed to Manual/Minimum). Because HPCI is a single train ECCS safety system, this event results in the loss of an entire safety function which requires an 8 hour ENS notification in accordance with 10CFR50.72(b)(3)(v) and the guidance provided under NUREG-1022, rev. 2. "There are no other ECCS systems presently out of service." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2001-11-11
38491 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-11-11 09:36 | 2001-11-11 10:44 | 2001-11-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF SUBSTATION The licensee reported that at 0610 EST on 11/11/2001 that the 1B2 Unit Substation was lost on a ground fault on the 4160 side. The actual cause of the ground fault is unknown and is being investigated. The licensee has entered multiple LCOs due to loss of other vital equipment and the most limiting is due to the inoperability of containment isolation valves, which is a requirement to be in Cold Shutdown in 24 hours. The licensee expects the plant to shutdown completely within the 24 hour window. The licensee notified the NRC Resident Inspector. | 88 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-11-11
38490 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-11-09 15:34 | 2001-11-09 21:28 | 2001-11-09 | CONTAINMENT PATHWAY DECLARED INOPERABLE FOLLOWING LLRT TESTING "This condition is being reported in accordance with the requirements of 10CFR50.72(b)(3)(ii) as an event or condition that results in: (A) The condition of the nuclear power plant. including its principal safety barriers, being seriously degraded. "During local leak rate testing (LLRT) being performed on the 'B' reactor feed line to the reactor, both primary containment boundary check valves (RF-CV-13CV and RF-CV-14CV) failed LLRT. Efforts to quantify the leak rate were unsuccessful. The maximum leakage indicated on the test equipment used is 424 Standard Cubic Feet Hour (SCFH). The allowable leakage (La) for Primary Containment is 317.41 SCFH. Subsequently this primary containment pathway was declared inoperable. CNS is in MODE 5 for refueling with vessel level >23 feet above the flange and the spent fuel pool gates removed. No fuel movements or operations with the potential to drain the reactor vessel were in progress. Primary containment is not required per CNS Technical Specifications in this mode of operation." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-11-09
38489 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-11-09 11:13 | 2001-11-09 17:05 | 2001-11-09 | FITNESS FOR DUTY REPORT An employee acting in a supervisory position failed a random alcohol test. Access was immediately revoked and EAP assistance was sought by the individual. A supervisor will review work performed by the individual for impact on quality and safety. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2001-11-09
38488 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-11-09 11:00 | 2001-11-09 12:31 | 2001-11-09 | SAFETY SYSTEM ACTUATION DURING TESTING OF THE EHC SYSTEM "At 1859 on October 30, 2001, during performance of Electro-Hydraulic Control (EHC) testing, a Nuclear Steam Supply Shutoff System isolation actuation occurred. The plant was in operational condition 4, mode switch locked in refuel, all control rods inserted and reactor pressure vessel level and temperature were within the appropriate band, at the time of the event. "The cause of the actuation was due to the impact of test setup conditions established to perform EHC testing being performed concurrent with reactor vessel cold hydrostatic testing, which effectively un-bypassed a low vacuum trip input signal. "The NRC Resident is fully aware of the event. "This notification is being made in accordance with 10CFR50.72(b)(3)(iv)(A). "PSE&G Nuclear is continuing to evaluate this condition to determine other possible causes and corrective actions." This event was identified as reportable as part of the licensee's corrective action program review. The licensee will also inform the Lower Alloways Creek Township (LAC). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-11-09
38487 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2001-11-08 14:00 | 2001-11-09 08:27 | 2001-11-09 | STATE OF NC REPORTED THAT ONE OF THEIR LICENSEES MISPLACED/LOST A BETA THICKNESS GAUGE The Guilford Mills textile plant is in the process of being decommissioned and disposing of 4 gauges when it was discovered that one gauge could not be located. The gauge that is missing is a Mahlo America model FMIR-7AK-6271-12-1400 beta thickness gauge. It contained 100 millicuries of Krypton-85 source serial # 1603BX and was last inventoried in 1997. The licensee is continuing to look for the device. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0 | 2001-11-09
38486 | -1 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-11-08 20:57 | 2001-11-09 01:08 | 2001-11-12 | AUTOMATIC REACTOR TRIP DURING UNIT STARTUP "During a reactor start up, BVPS Unit One Reactor tripped prior to reaching criticality. The apparent cause of the trip is a blown control power fuse on Intermediate Range Nuclear Instrument channel N36. The blown fuse caused actuation of the Intermediate Range high level trip. All control rods fully inserted. All equipment properly functioned. Unit One is presently in mode three at normal temperature and pressure. Decay heat removal is through the steam bypass valves to the main condenser as it was throughout the event. A main feed pump is supplying feedwater through the bypass feedwater regulating valves." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE 1237 EST ON 11/12/01 FROM MIKE KOGELSCHATZ TO S. SANDIN * * * The licensee is retracting this report based on the following: "Beaver Valley Power Station is retracting its previous 10 CFR 50.72(b)(3)(iv) notification from 11/9/2001, EN #38486. The automatic Reactor Protection System (RPS) actuation that occurred on 11/8/2001 was initiated by a blown fuse in the N36 intermediate range nuclear flux instrument causing a high intermediate range reactor trip signal to be generated. The blown fuse was not in response to actual plant conditions and is not a parameter satisfying the requirements for initiation of the safety function of the system. Hence this RPS actuation was not a valid actuation since there was no actual high flux condition within the reactor. Therefore, this event is not reportable pursuant to 10 CFR 50.72(b)(3)(iv)(A) since the automatic trip was not generated by a valid actuation. "This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since this event involved an automatic actuation of the Reactor Protection System which was not part of a pre-planned sequence, did not occur with the RPS properly removed from service, and did not occur after the safety function of dropping the control rods had already been completed. "However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification instead of submitting a written LER since the automatic reactor trip occurred with the reactor subcritical, and was not generated by a valid actuation. On 11/8/2001, all control rods inserted due to the blown fuse initiating a reactor trip on a one out of two high intermediate range high power. All required safety systems operated as designed and the plant was stabilized in Mode 3." The licensee will inform the NRC Resident Inspector. Notified R1 IRC. HOO Note: See EN #38496. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-11-09
38485 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-11-08 10:45 | 2001-11-08 22:35 | 2001-11-08 | SAFETY SYSTEM DISCOVERED INOPERABLE DURING SURVEILLANCE TEST "At 1045 hours maintenance personnel identified the failure of the safety system component in the X-760 building. During the scheduled TSR surveillance, maintenance on the X-760 Criticality Accident Alarm System (CAAS), maintenance personnel identified that the associated nitrogen horns would not have functioned as designed. Post maintenance testing of the associated nitrogen horn identified that the horns would not sound as required due to a gross leak at the block manifold. Repairs and a successful post maintenance test were completed under the direction of the System Engineer. The Plant Shift Superintendent (PSS) has directed a random check of the site CAAS facilities be conducted to ensure this condition does not exist elsewhere. The X-760 CAAS remains inoperable pending the completion of the requested engineering evaluation to address the gross leak condition causing the safety system failure." Operations informed both the NRC Resident Inspector and the DOE Site Representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2001-11-08
38484 | 0 | CONAM |  |  |  |  | 2001-11-08 09:35 | 2001-11-08 16:52 | 2001-11-08 | THE CONAM COMPANY REPORTED THAT ONE OF THEIR RADIOGRAPH CAMERAS HAD A SOURCE THAT BECAME STUCK An Iridium - 192 AEA model 660B radiography camera in use at the Sunoco refinery at Gerard Pt. Philadelphia, Pa. had the source get stuck while the licensee was retracting it into the camera. The source was moved in and out of the camera a few times before it finally was fully retracted into the camera. No one was overexposed and the camera will be returned to the manufacturer for inspection and repair. They believe the cause was due to a locking problem in the camera. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | [10 empty] | NON EMERGENCY | 3 | IL | OTH | GEN |  |  |  |  | 0 | 2001-11-08
38483 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-11-08 12:40 | 2001-11-08 16:30 | 2001-11-08 | INFORMATION REPORT INVOLVING A CONTROLLED PLANT SHUTDOWN FOR REPAIRS "A controlled plant shutdown was performed due to a small (1 inch or less) steam leak on 'B' main steam header. The leak originated from a 1 inch drain line located upstream of the 'B' MSIV. The Unit was shutdown in accordance with plant procedures. A plant cooldown to mode 5 is in progress to affect repairs." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2001-11-08
38482 | 0 | UNIVERSITY OF PENNSYLVANIA |  |  |  |  | 2001-11-08 15:15 | 2001-11-08 16:05 | 2001-11-08 | THE LICENSEE REPORTED A MEDICAL MISADMINISTRATION OCCURRED DURING THERAPEUTIC TREATMENT At approximately 2:45 pm on November 7, 2001, a physician, an authorized user in Nuclear Medicine, began administration of a Y-90 therapeutic radiopharmaceutical dose in accordance with the written directive for the treatment. The administration system used a saline flush followed by an air flush to administer the radiopharmaceutical. During the air flush at approximately 3:15 pm, fluid was observed on the top of the second dose vial. To avoid infusing a potentially non-sterile dose, the doctor stopped the dose administration before the entire dose was infused. Based on post infusion measurements of the dose vials, the patient received approximately 80 mCi instead of the prescribed 120 mCi. The administrating physician informed the patient on November 7, 2001 that because of the administration problem, the total prescribed dose was not administered. The referring physician will be notified. There are no expected harmful effects as a result of this treatment. The treatment protocol requires the subject to receive three separate 120 mCi doses of the Y-90 radiopharmaceutical. This was the patient's second treatment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0 | 2001-11-08
38480 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-11-08 13:05 | 2001-11-08 14:00 | 2001-11-08 | THE LICENSEE NOTIFIED THE STATE OF A DEAD SEA TURTLE DISCOVERED IN THE INTAKE CANAL "At approximately 1230, one dead sea turtle was recovered from the St. Lucie Intake Canal. Pursuant to the sea turtle permit the Florida Department of Environmental Protection (FDEP) was notified at 1305. The notification of FDEP necessitates a four (4) hour non-emergency notification of [the] NRC per 10CFR50.72(b)(2)(xi)." The licensee informed the State of Florida and will inform the NRC Resident Inspector. HOO Note: See previous event #38479. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-08
38479 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-11-08 10:39 | 2001-11-08 10:39 | 2001-11-08 | THE LICENSEE NOTIFIED THE STATE THAT TWO DEAD SEA TURTLES WERE DISCOVERED IN THE INTAKE CANAL At approximately 0800 on 11/8/01 two dead sea turtles(one green and one loggerhead) were recovered from the licensee's intake canal. Pursuant to the sea turtle permit, the Florida Department of Environmental Protection(FDEP) was notified at approximately 0845. Both turtles apparently drowned below the surface of the 5" mesh barrier net. The carcasses will be turned over to the FWCC. The NRC Resident Inspector and the FDEP were notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-08
38478 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2001-11-07 20:04 | 2001-11-07 21:31 | 2001-11-07 | AUTOMATIC REACTOR SCRAM Reactor power level was at 8% after coming out of a refueling outage when a 1/2 scram signal was received. Approximately 2 minutes after receiving the 1/2 scram signal, while investigating the cause of the 1/2 scram signal, another 1/2 scram signal was received which initiated a fully reactor scram from 8% reactor power. All rods fully inserted into the core. The initial shrink of reactor vessel water level from plus 30 inches to plus 10 inches was due to the reactor scram. Group 2, drywell isolation valves, and Group 3, reactor water cleanup, isolations were caused by reactor vessel water level decreasing. Main Steam Isolation Valves were closed to maintain control of reactor vessel pressure, very little decay heat in the core. Reactor pressure is currently 562psi and reactor feed pumps are maintaining proper reactor vessel water level. All emergency core cooling systems are fully operable if needed. The emergency diesel generators are fully operable if needed and the electrical grid is stable. The licensee at this time does not know what signal initiated the 1/2 scram signals. Investigation is in progress. The NRC Resident Inspector will be notified by the licensee of this event. | 0 | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-11-07
38477 | -1 | PALISADES | 1 |  |  | [1] CE | 2001-11-07 14:14 | 2001-11-07 19:47 | 2002-03-04 | HEAD LOSS CHARACTERISTICS OF CHECK VALVES GREATER THAN PREVIOUSLY ASSUMED. On November 7, 2001, at approximately 1414 hours, with the plant in mode 5 (cold shutdown), evaluation of preliminary results from mock-up testing of containment sump check valves determined that the head loss characteristics of the check valves are greater than previously assumed by calculations that support the safety analyses. The result of increased head loss through the containment sump check valves is reduced available net positive suction head (NPSH) for the safety injection and containment spray pumps during recirculation mode following a loss of coolant accident (LOCA). The reduced available NPSH may have effected the ability of the pumps to satisfy their required design safety function during previous periods of plant operation. Recirculation mode operation of these pumps is required by Technical Specifications in Mode 3 (hot standby) and above. Therefore, this condition has no adverse implications for the present plant condition at Mode 5. Evaluation of test results is continuing. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1450 EST ON 03/04/02 BY DAN MALONE TO GERRY WAIG* * * "Subsequent evaluation of the past operability of the pumps with the reduced NPSH condition was concluded that the pumps were nonconforming but operable. This conclusion was reached by crediting containment overpressure and actual plant parameters, which increase available NPSH above that required for all pumps considering the most limiting postulated conditions. "Since a determination of nonconforming but operable was reached for past operating conditions, there was no loss of a required safety function and no significant impact on plant safety this condition was originally discovered and reported with the plant in Mode 5; and was corrected prior to plant restart by modifying plant equipment and procedures without further reliance on crediting containment overpressure." Licensee notified the NRC Resident Inspector. Notified R3DO (John Madera). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-11-07
38476 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2001-11-07 | 2001-11-07 17:00 | 2001-11-07 | THE STATE OF ILLINOIS REPORTED A SOURCE BEING FOUND AT A SCRAPYARD The source of the elevated readings was traced to a metallic right circular cylinder, approximately 1 inch long and 1/8 inch in diameter. There were no visible markings, color codings, or other identifications on this object. Measured exposure rates were 110 mR/hour at 3" and 13 mR/hour at 12". The object was placed into the finger of a nitrile glove and further surveys were performed. Mr. Labkon's(the individual who recovered the scrap metal) hands and gloves were surveyed and were found to be free of contamination. The Styrofoam cup which had held the source and the storage room were also surveyed and found to be free of contamination. A gamma spectrum was obtained using the Microspec-2 portable multichannel analyzer, serial number 94006. The spectrum showed no discernible photopeak. Spectral data are included with this report. The source/nitrile glove finger were placed into a Syncor threaded pig. The exposure rate at near contact with the pig was measured at 25 µRem/hour. Based on the data available, this source would be either a strong beta emitter, or a very low energy gamma emitter, such as 241-Am. In order to determine whether this source may have been manufactured as a neutron source, a neutron measurement was performed on November 1, 2001. Using a Health Physics Instruments Model REM 500 neutron meter, serial number 00203, and taking a standard one minute count for each determination, the following readings were obtained: Configuration Reading (mRem/hour) Reading(neutrons/minute) Background 0.000 0 4" from unshielded source 3.21 330 at near contact with the stainless steel shield with the source inside 0.448 2 Based on the available data, considering the possibilities of an 241-Am-Be source, a 239-Pu-Be source, or a 226-Ra-Be source, the most likely possibility is an 241-Am-Be source, with a calculated activity of 4 mCi. The source was returned to a safe shielded position and locked within their source storage room. Pending satisfactory disposal of this source, this matter may be considered closed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2001-11-07
38475 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-11-07 09:00 | 2001-11-07 10:32 | 2001-11-07 | NOTIFICATION OF THE RECOVERY OF A DEAD GREEN TURTLE FROM THE PLANT'S INTAKE CANAL A dead green turtle was recovered from the plants intake canal where it apparently drowned near the 5" barrier net. The licensee notified the Florida Department of Environmental Protection as required by the plant's sea turtle permit. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-11-07
38472 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-11-06 14:16 | 2001-11-06 15:38 | 2001-11-06 | AUTOMATIC REACTOR TRIP ON LOW-LOW STEAM GENERATOR WATER LEVEL. "At 14:16 Unit One Reactor automatically tripped due to low-low level in the 1C Steam Generator. Feed Water Control Valve (FCV-FW-498) failed closed causing the 1C steam generator level to rapidly drop and reach the low-low level trip setpoint. All Control Rods fully inserted and all required equipment functioned properly. The plant is currently stable in mode 3 at normal pressure and temperature. Decay Heat removal is via the Steam Bypass valves. Normal and Auxiliary Feed Water systems are in service. Cause of the failure under investigation" Emergency Core Cooling Systems, Emergency Diesel Generators are fully operable if needed and the electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-11-06
38471 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-11-06 11:32 | 2001-11-06 14:01 | 2001-11-06 | 24-HOUR REPORT IN ACCORDANCE WITH OPERATING LICENSE DUE TO POTENTIAL MAXIMUM POWER LEVEL VIOLATION. "This report is being made in accordance with Nine Mile Point Nuclear Station, Unit 2 Operating license No. NPF-69 Section 2.F, which in part states the following; "... shall report any violations of the requirements contained in section 2.C of this license in the following manner: initial notification shall be made within 24 hours to the NRC Operations Center via the Emergency Notification System, with written follow-up within 30 days in accordance with the procedures described in 10CFR 50.73 (b), (c), and (e)." "The following text is an excerpt of a facsimile received by the licensee: "General Electric (GE) report titled, Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculation , September 2001, documents a non-conservative constant for moisture carryover fraction in the equation used to calculate plant heat balance. The report states that a number of later model GE BWR plants have moisture carryover fractions of less than 0.003%. Nine Mile Point Unit 2's heat balance assumed a 0.003% moisture carryover factor. "Based on the above report from GE, on October 1, 2001 at 1926 hours Nine Mile Point Unit 2 implemented an Interim administrative power level limit of 3465 MWt (2 MWt less than the license limit of 3467 MWt) to conservatively account for a potential lower moisture carry over factor. in addition, a sample time period was reviewed to determine whether the Maximum Power level was exceeded while the non-conservative constant was in place. This review determined that on August 20, 2001 from 12:03 to 23:59 hours the Maximum Power Level Limit (3467 MWt) was exceeded by approximately 2 MWt. The time that Maximum Power Level was exceeded was previous to he date that NMP 2 was notified by GE of the potential non-conservative moisture carryover factor. Since the interim administrative limit has been implemented NMP 2 has not exceeded its Maximum Power Level. Additionally, the method used to calculate NMP 2's heat balance has been revised to eliminate the non-conservative moisture carryover factor." The NRC Resident Inspector was notified of this event by the Licensee. (Refer to event numbers 38330, 38337, 38340, 38344, 38445, 38347, 38349, and 38357 for similar events at Fermi, Perry, Hope Creek, Grand Gulf, Columbia Generating Station, Limerick 2, River Bend, and Limerick 1.) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2001-11-06
38469 | 0 | MALLINCKRODT |  |  |  |  | 2001-11-06 09:15 | 2001-11-06 10:50 | 2001-11-06 | ALERT DECLARED DUE TO FIRE IN DECON AREA An Alert was declared at 0915 CST due to a fire in Decon Area 2 in Building 600. The fire was smoke only, from an autoclave where a process of depyrogeneration of Mo-99 glassware was taking place. There was a piece of tygon tubing in the autoclave which became involved, producing the smoke. The Alert was exited at 0940 CST when the fire was out. There was no release to the environment and air samples taken in the laboratory showed no detectable activity. The Maryland Heights Fire Department responded to the site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EMERGENCY DECLARED | [9 empty] | ALERT | 3 | MO | MAT |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-11-06
38466 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-11-05 12:15 | 2001-11-05 14:51 | 2001-11-05 | ALL EMERGENCY SIRENS FAIL TO RESPOND DURING ANNUAL FULL CYCLE TEST. During the performance of the annual full cycle siren test 49 out of 49 sirens in Calvert County failed to respond. Licensee believes sirens failed due to a transmission problem. Technicians will be sent out to investigate problem. Calvert County if needed will perform routing alert. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-11-05
38465 | 0 | REVISS SERVICES INC. |  |  |  |  | 2001-11-05 12:00 | 2001-11-05 13:05 | 2001-11-05 | MISSING CLASS 7 COBALT-60 A representative of Reviss Services, Inc. made the following report: Today, FedEx was supposed to pickup a shipment of Cobalt-60 from the United Kingdom at Port Elizabeth, NJ. When FedEx arrived at approximately 1200 noon they were informed that the shipment had been picked up by Select Cargo at 0621. The shipment was supposed to be shipped to Northborough, Mass. The total curie content of the cobalt-60 irradiator shipment from the United Kingdom was 382,000. The 382,000 curies of cobalt-60 were packed in 2 class B containers. Each container is approximately 3 cubic feet in volume. Each one of these containers were placed in a 20 foot isolation container. The TI index on contact of the cage of the isolation container is 3. Reviss Services, Inc. informed Mass Radiation Control Program and Ill Department of Safeguards of this event. ****UPDATE ON 11/05/01 AT 1600 HOUR BY MACKINNON ***** NRC, with the assistance of the U.S. Customs Service, has investigated this incident and determined that the shipment had been moved to another location at the terminal by Select Cargo Services. The shipment remains under the control of the U.S. Customs Service. NRC is following up to understand the circumstances of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-11-05
38464 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2001-11-02 14:00 | 2001-11-05 08:49 | 2001-11-05 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE A Troxler moisture density gauge, model 3440 with 8 mCi Cs-137 and 40 mCi Am-241:Be, was damage when a roller backed over it. This took place in the Blair, MD area at a new housing development area. The gauge was severely damaged, however the sources appear to be intact. The gauge will be sent to Troxler for further examination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2001-11-05
38463 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-11-04 11:42 | 2001-11-04 13:44 | 2001-12-20 | LOSS OF CONTAINMENT INTEGRITY "At 0525[EST] the Control Room received a low flow alarm as a result of a leaking 1/4 inch fitting on the 'B' Hydrogen/Oxygen analyzer. At 1142[EST] it was determined, as a result of a leak rate test, that the maximum allowable test leak rate (La) was potentially exceeded. The system was isolated within 5 minutes of receiving the alarm. A 24 hour hour shutdown LCO (TS 3.7.A.8) was entered at 0525[EST] and exited at 0530[EST]." The licensee will inform both the State of Vermont and the NRC Resident Inspector. Hoo Note: A similar problem related to this particular monitor was reported on 10/30/01 - see event #38444. * * * UPDATE 1317EST ON 12/20/01 FROM KELLY ROBINSON TO S. SANDIN * * * The licensee is retracting this report based on the following: "Systems Engineering completed a Technical Evaluation (2001-061) on November 20, 2001 which concluded, 'When the combined minimum pathway flow (89 scfh) is added to the resultant, the value is less than 0.6La (193 .674 scfh). The condition that existed (i.e., the crack before tightening, the discovered condition) did not compromise Primary Containment Integrity. The results are conservative.' "This Technical Evaluation demonstrates that the Technical Specification for system leakage and combined minimum pathway were not exceeded. Primary Containment was capable of performing and fulfilling its specified safety function, without operator intervention. "Therefore, ENS Event Number 38463, made on 11/04/01, is being retracted." The licensee will inform the NRC Resident Inspector. Notified R1DO(Kinneman). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2001-11-04
38459 | 0 | NTH CONSULTANTS |  |  |  |  | 2001-11-02 | 2001-11-02 15:07 | 2001-11-13 | TROXLER GAUGE DISCOVERED MISSING DURING ROUTINE INVENTORY During a routine physical inventory, a Troxler Model 3411B (upgraded 3401B), S/N 16990, was discovered missing from the Farmington Hills, MI, main office. The gauge which contains 8 millicuries Cs-137 and 40 millicuries Americium-241/Be, was logged out from the Grand Rapids office on 8/31/01 as a return to the main office for repairs. The main office has no record of the shipment. The local police department in Grand Rapids has been informed of the missing gauge. The licensee is continuing their investigation. * * * UPDATE ON 11/13/01 @ 1240 BY PARSONS TO GOULD * * * The device was found at the house of a former employee on 11/3/01. Notified John Hickey and Anita Turner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-11-02
38458 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-11-02 03:25 | 2001-11-02 09:54 | 2001-11-02 | BOTH REACTOR BUILDING TO TORUS VACUUM BREAKERS WERE PREVENTED FROM RESPONDING TO A REACTOR BUILDING TO TORUS DIFFERENTIAL PRESSURE At 0325 CST, it was identified that the switches for TORUS VACUUM RELIEF valves PC-AOV-243AV and PC-AOV-244AV were in the closed position. With the switches in the closed position, the valves would not respond to a differential pressure between the Reactor Building and Torus as required by SR 3.6.1.7.3. The switches had been placed in the closed position for performance of LLRT on penetration X-205. The valves were declared inoperable and LCO 3.6.1.7 Condition D was entered. The required action for this condition is to restore all vacuum breakers in one line to operable status within 1 hour. If the valves are not restored to operable, Action E is entered, which requires the plant to be in Mode 3 in 12 hours and Mode 4 in 36 hours. The valve switches had been placed in this position as part of a clearance order issued at 2357. At 0342 CST, the switches for the Torus Vacuum Relief valves were returned to the Auto position, and the valves were declared operable as vacuum breakers. The LCO 3.6.1.7 Condition D was exited. The function of the Reactor building to Torus vacuum breakers is to relieve vacuum when primary containment depressurizes below Reactor Building pressure. With the switches in the closed position, the valves would not respond to a situation where a significant negative pressure existed between the Reactor Building and Torus. A negative differential pressure is caused by rapid depressurization of the drywell. Events that cause this rapid depressurization are cooling cycles, primary containment spray actuation, and steam condensation in the event of a primary system rupture. The Reactor building to Torus vacuum breakers prevent an excessive negative differential pressure across the primary containment boundary. This event was determined to be reportable on 11-2-01 at 0430 CST after review of NUREG 1022 and design basis information. The NRC Resident Inspector was notified. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-11-02
38457 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2001-11-01 12:30 | 2001-11-01 15:13 | 2001-11-01 | AUTOMATIC REACTOR TRIP DURING CEA TROUBLESHOOTING FOR REASONS UNKNOWN "While operating at full power at approximately 1010 CST on 11/01/2001, Control Element Assembly (CEA) 43 dropped into the core for unknown reasons. Reduction of reactor power began at approximately 1017. With reactor power stable at approximately 22 percent, troubleshooting of the cause of the CEA-43 drop was in progress at approximately 1230 CST when an automatic reactor trip occurred. The reason for the trip is unknown. Plant response to the trip was normal and uncomplicated. All CEAs fully inserted. There were no ESF system actuations. The plant is stable in Hot Standby (Mode 3) conditions with decay heat being removed via the Steam Generators to the Main Condenser. No radiation releases occurred." The licensee informed the state and NRC Resident Inspector. | 0 | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-11-01
38454 | 0 | ST BARNABAS MEDICAL CENTER |  |  |  |  | 2001-10-26 | 2001-11-01 10:36 | 2001-11-01 | MEDICAL MISADMINISTRATION DURING THERAPEUTIC TREATMENT REPORTED BY ST BARNABAS MEDICAL CENTER A patient undergoing the third therapeutic treatment received a dose to an unintended treatment site due to an incorrect step size on a High Rate Remote After Loader which was used in the treatment. This was the result of human error. It was determined there will be no medical implications and the patient will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.33 |  |  |  | 0 | 2001-11-01
38453 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-10-31 | 2001-11-01 09:47 | 2001-11-01 | CONTROL RODS DID NOT FULLY INSERT DURING CONTROL ROD TEST On October 31 and November 1, 2001 following reactor vessel assembly and heat up, control rod drop testing was performed in mode 3. Rods N-9 and C-9 did not fully insert into the dashpot region (24 steps) following operability and trip testing. Rod J-13 exhibited similar characteristics following operability and trip testing but shortly after trip testing it fully inserted. Four other rods fully inserted but were slower than normal in the dashpot region. All other control rods tested fully acceptable. The Unit is currently cooling down and plans are under way to replace unacceptable control rods as necessary. The Unit has remained borated above the all rods out critical boron concentration since core reload and adequate SDM exits. On October 06, 2001 Farley Unit 1 commenced a normal Unit shutdown to start its 17th refueling outage. All control rods were fully inserted with no problems. During insert and control rod changeout in the Unit 1 fuel pool several control rods not scheduled to go back into the core experienced binding in older fuel assemblies that prevented the rods from fully inserting in the dashpot region of assemblies. Upon investigation of the old control rods scheduled to be replaced axial cracks were observed by visual exmination in several assemblies near the rod ends but above the rod tips. This resulted in an inspection program for 18 older control rods scheduled to go back into the core to confirm the acceptability for continued use in cycle 18. Visual inspection and drag testing was performed in the Unit 1 Spent Fuel. Westinghouse reviewed the test results and confirmed the acceptability of 18 control rods for Cycle 18 use. The NRC Resident was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW | [5 empty] | 0 | 2001-11-01
38452 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2001-10-31 14:23 | 2001-10-31 18:44 | 2001-10-31 | OFFSITE NOTIFICATION REGARDING HYDRAULIC OIL SPILL "At 1423 hours CST Wednesday October 31, 2001 LaSalle control room received notification of an oil sheen at the Illinois River intake structure for LaSalle County Nuclear Stations Unit 1 and 2. Station procedures and the Spill Prevention Control and Counter Measures Plan was entered and the station Environmental Specialist and HAZMAT qualified personnel were dispatched to the scene. The Environmental Specialist notified the Main Control room that hydraulic fluid from the River intake structure equipment had leaked into the screenhouse inlet and due to a gap between in the floating boom and the concrete structure some hydraulic fluid had been released to the Illinois River. Current estimate is that approximately 5 gals of hydraulic fluid entered the inlet and approximately 100 milliliters was released into the Illinois River. Per the Exelon Reportability Manual ENV 3.19, and 40 CFR 110.10 Discharge of Oil into or upon Navigable Waters or Adjoining Shorelines the release of oil into the Illinois River is reportable to the National Response Center and Illinois Emergency Management Agency (IEMA) with in 1 hour. The National Response Center was notified at 1448 CST and the Illinois Emergency Management Agency was notified at 1505 CST. Pursuant to Exelon Reportability Manual SAP 1.9, and 10 CFR 50.72(b)(2)(xi) notification to the NRC is required to be notified within 4 hours, this notification is being made to address this requirement. "Currently, the HAZMAT team is at the scene and the oil release to the river has been stopped. Cleanup efforts are underway using oil booms and oil soak rags." The NRC resident inspector has been notified of this event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-10-31
38451 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-10-31 13:20 | 2001-10-31 18:33 | 2001-10-31 | FIRE WATER SYSTEM ISOLATION VALVE FOUND CLOSED "DURING PERFORMANCE OF PROCEDURE XP4-CU-UG6206 'HIGH PRESSURE FIRE WATER SYSTEM (HPFW) UNDERGROUND DISTRIBUTION LOOP TESTING,' UTILITY OPERATIONS AND FIRE FIGHTING PERSONAL DISCOVERED A SECTIONAL ISOLATION VALVE, THAT WAS EXPECTED TO BE OPEN, WAS RESTRICTING FLOW TO THE PORTION OF THE LOOP BEING TESTED. THIS RESTRICTION IN THE LOOP CAUSED A PORTION OF THE HPFW SPRINKLER SYSTEM FOR THE X-326 BUILDING TO FAIL TO PERFORM ITS INTENDED SAFETY FUNCTION (FIRE SUPPRESSION). UPON IDENTIFYING THE PROBLEM THE FIRE DEPARTMENT NOTIFIED THE PLANT SHIFT SUPERINTENDENT (PSS) WHO IMMEDIATELY DECLARED THE HPFW SPRINKLERS SYSTEMS IN THE X-326 BUILDING INOPERABLE, AND DIRECTED THE REQUIRED TSR ACTIONS TO BE PERFORMED. UTILITY OPERATIONS PERSONNEL SECURED THE TEST AND REOPENED ALL SECTIONAL ISOLATION VALVES THAT WERE SHUT FOR THE TEST. AT 1345 HOURS HPFW WAS RESTORED TO THE ISOLATED PORTION OF THE LOOP. "ENTIRE EVOLUTION IS UNDER INVESTIGATION AT THIS TIME." The NRC resident inspector has been informed of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2001-10-31
38450 | 0 | GEO ENGINEERING |  |  |  |  | 2001-10-31 | 2001-10-31 18:06 | 2001-10-31 | DAMAGED MOISTURE/DENSITY GAUGE A CPN model MC-1 moisture/density gauge (S/N M15076270) was damaged when it was run over. The source rod was not exposed at the time of the event. The Puerto Rico Health Department responded to the scene and surveyed the gauge, but found no evidence of contamination. The gauge has been secured pending further action by the licensee. The licensee has contacted an NRC inspector in Puerto Rico, who is going to respond to the scene tomorrow. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | PR | MAT | [5 empty] | 0 | 2001-10-31
38448 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-10-31 14:09 | 2001-10-31 16:59 | 2001-10-31 | MANUAL TURBINE/REACTOR TRIP "Unit 2 Turbine Condenser Air Ejector was isolated for a potential steam leak. After the condenser air ejector was isolated, the A/B condenser differential reached 2.5" Hg vacuum. This is a procedural requirement to trip the turbine. Operators initiated a manual reactor/turbine trip at 1409. The main steam isolation valves were manually closed to ensure air ejector isolation. Steam generator (S/G) power operated relief valves (PORVs) are controlling RCS temperature at 547 degrees F. "Both auxiliary feedwater pumps auto started on low S/G levels. N35 NIS intermediate range detector failed to reach the source range setpoint. Source range detectors were manually reenergized." The NRC resident inspector has been informed of this event by the licensee. The licensee plans to issue a press release regarding this event. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-10-31
38447 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2001-10-30 19:00 | 2001-10-31 14:55 | 2001-11-23 | 24-HOUR REPORT DUE TO VIOLATION OF LICENSE CONDITION "On 10/30/2001 at 1900 hours, during a walkdown of approximately 600 fire barrier penetrations which had been mistakenly excluded from the Fermi 2 fire barrier penetration seal inspection program, 11 penetrations were found to have no seal material installed. To date, over 350 of the approximately 600 fire barrier penetrations not included in the program have been inspected. The lack of seal material in these penetrations constitutes an inoperable 10 CFR 50, Appendix R fire rated barrier and is reportable under License Condition 2.F as a violation of License Condition 2.C (9), 'Modifications for Fire Protection.' The plant is currently shut down for refueling. Hourly fire watches have been established in the affected areas as required by the Technical Requirements Manual. Detroit Edison will report any further missing seals that are identified as part of this inspection." The NRC resident inspector has been informed of this report by the licensee. * * * UPDATE 11/23/01 AT 1805EST FROM KEVIN DAHM TO S. SANDIN * * * The licensee is retracting this report based on the following: "The 600 (approximately) fire barrier penetration seals which had been mistakenly excluded from the Fermi 2 fire barrier penetration seal inspection program have now all been inspected. Fifteen (15) of these penetrations were found to have not been sealed. These 15 penetrations are all in the same fire barrier. This fire barrier has been evaluated in accordance with Generic Letter 86-10, and it has been determined that the as found configuration is adequate to ensure the capability to achieve and maintain safe shutdown in the event of a fire. Therefore, this condition does not constitute a violation of License Condition 2.C.(9) and is not reportable." The licensee informed the NRC Resident Inspector. Notified R3DO(Lipa). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2001-10-31
38446 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-10-30 18:20 | 2001-10-30 22:30 | 2001-10-30 | HPCI DECLARED INOPERABLE "On 10/30/2001 with DAEC operating in Mode 1 at 100% power, the plant was in the following LCOs for preplanned maintenance on the 'A' Loop of RHR and RHRSW subsystems: Day 1 of 7 for the LPCI system; Day 1 of 7 for the 'A' Loop of RHRSW; Day 1 of 7 for the 'A' Loop of Torus Cooling; Day 1 of 30 for the 'A' Loop of Drywell Sprays; Day 1 of 30 for the 'A' Loop of Torus Sprays. "At 1820, the HPCI system was declared inoperable due to a Oil leak on the HPCI oil system. A 14 day, 7 day, and 72 hour LCOs were entered per Technical Specifications conditions 3.5.1.F, 3.5.1.G and 3.5.1.H. "The unplanned HPCI system inoperability is reportable under 50.72(b)(3)(v)(D) and 50.73(a)(2)(v)(D) as a failure of a single train of equipment required to mitigate the consequence of an accident. "On 10/29/2001, system engineering personnel discovered a small oil leak on the HPCI oil system. During work planning walkdowns with maintenance personnel on 10/30/2001, the leak located under insulation lagging on the 38 psig portion of the HPCI oil system at 3/4" swagelock fitting was determined to be 90 drops per minute. HPCI was declared inoperable at 1820 on 10/30/2001. Maintenance is in progress to repair the 3/4" fitting. "The DAEC PSA computer model Sentinel was used to determine the risk significance of having the 'A' RHR, 'A' RHRSW and HPCI systems inoperable at the same time. The initial CDF for having the 'A' Loop of RHR and RHRSW inoperable was 1.602E-5. With the HPCI, RHR and RHRSW systems inoperable, the CDF value was determined to increase to 2.390E-5 which would still be considered a green status." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-10-30
38445 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2001-10-30 15:30 | 2001-10-30 18:56 | 2001-10-30 | STATE ISSUES PRESS RELEASE REGARDING NATIONAL GUARD DEPLOYMENT "The Governor's Office of the State of Arizona issued the attached press release regarding National Guard deployment at the Palo Verde Nuclear Generating Station (PVNGS). The press release was issued at 15:30 MST. The Palo Verde Nuclear Generating Station has no plans to issue a press release at this time. "The NRC Resident Inspector has been notified of the State press release and provided a copy." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown | Cold Shutdown | Power Operation | Cold Shutdown | Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-10-30
38444 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-10-30 13:15 | 2001-10-30 16:10 | 2001-10-30 | LOSS OF CONTAINMENT INTEGRITY It has been determined that a loss of containment occurred on 10/25/01 when a tube broke on the discharge of the "B" Hydrogen/Oxygen Monitor sample pump. The monitor was secured and isolated within 25 minutes of the break. Engineering review has determined that under accident conditions, leakage from this break would have exceeded allowable containment leakage limits. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(C) |  |  | 0 | 2001-10-30
38441 | -1 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-10-30 08:50 | 2001-10-30 09:30 | 2001-10-31 | UNUSUAL EVENT DECLARED DUE TO AN UNPLANNED RADIOLOGICAL RELEASE, EMERGENCY ACTION LEVEL 7.2 (LIQUID EFFLUENT). "At 0850 on 10/30/2001 a Notification of Unusual Event (NOUE) was declared and terminated at 0910 on 10/30/2001 at Sequoyah Nuclear Plant due to an unplanned radiological release. At 0640 on 10/30/2001 count rate on 0-RM-90-212, the Station Discharge Rad Monitor, reached the alarm setpoint of 600 CPM. An initial Chem Lab sample taken at 0720 indicated no abnormal activity. A followup sample completed at 0802 confirmed activity in the Turbine Building Sump. The Chem Lab samples confirmed the validity of this alarm and the REP declaration requirements were met. At 0810 the release was terminated by isolating the station sump and realigning to the Low Volume Waste Treatment Pond. Readings on 0-RM-90-212 are slowly trending up at present 39000 CPM. Investigation is in progress to determine and correct the source. Detailed sample analysis are also in progress to identify the magnitude and nuclides involved in this release. Followup information will be provided when available." State and Local officials were notified of this event by the licensee. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1627EST ON 10/31/01 FROM CALVIN FIELDS TO S. SANDIN * * * The licensee is retracting this report based on the following: "This is an update to the October 30, 2001, notification. Subsequent analysis show that the total activity in the TB Sump was less than 35% of the ODCM limit. No release limits were exceeded and, therefore, the NOUE criteria of 2 times the ODCM limits did not exist. In accordance with NUREG-1022, Rev. 2, Section 2.8, TVA is retracting the previous notification via this follow-up telephone call." The licensee informed the NRC Resident Inspector and will inform both state and local agencies. Notified R2IRC. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Refueling Shutdown | Power Operation |  | Refueling Shutdown | Power Operation |  | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-10-30
38436 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-10-26 | 2001-10-29 16:32 | 2001-11-02 | SPDS UNAVAILABLE AT EOF The licensee reported that a computer system upgrade performed on 10/26/01 rendered the SPDS (safety parameter display system) inaccessible from the EOF. The condition was discovered on 10/29/01. The condition has since been repaired. The NRC resident inspector has been informed of this condition by the licensee. * * * UPDATE 1431EST ON 11/2/01 FROM JOHN TWAROG TO S. SANDIN * * * The licensee is retracting this report based on the following: "On Oct. 29, 2001 Vermont Yankee reported to the NRC, via Event Number 38436, the loss of the EOF SPDS computers since Oct. 25, 2001. Preliminary investigation identified the loss of the computers was due to an upgrade to the company's computer network performed on Oct. 25. Further investigation on Oct. 30 revealed the EOF SPDS was only unavailable for approximately 3 hours while the actual upgrade was being performed. This notification serves as retraction of a prior 10 CFR 50.72 notification regarding the loss of the EOF SPDS computers." The licensee informed the NRC Resident Inspector. Notified R1IRC. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-10-29
38435 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-10-28 00:15 | 2001-10-28 01:05 | 2001-11-02 | DISCOVERY OF APPARENT THROUGH-WALL INDICATIONS ON CONTROL ROD DRIVE MECHANISM PENETRATIONS The following text is a portion of a facsimile received from the licensee: "Following shutdown for a scheduled refueling outage, Surry Unit 1 performed a visual inspection of the reactor vessel control rod drive mechanism (CRDM) penetrations per NRC Bulletin 2001-01." "At approximately 0015 on October 28, 2001, apparent through-wall indications were identified on CRDM penetrations 27 and 40. The inspection is not yet complete. This condition did not pose a significant safety risk during plant operation. This is being reported as a non-emergency (8-hour report in accordance with 10 CFR 50.72(b)(3)(ii)(A) and 50.73(a)(2)(ii)(A)." The licensee stated that the unit is currently defueled. The licensee notified the NRC resident inspector. * * * UPDATE ON 11/2/01 @ 0338 BY HILBERT-SEMMES TO GOULD * * * UPDATE At approximately 0220 hours on November 2, 2001, additional indications were identified as having flaws that are not acceptable under ASME Section XI IWB-3600 on penetrations 65, 47, and 69. Two previously identified indications were previously reported in this event. The inspection of all CRDM penetrations is now complete with disposition of one penetration still underway. This condition did not pose a significant safety risk during plant operation. This is being reported as an update. The NRC Resident Inspector was notified. The Reg 2 IRC Manager was notified. ***** UPDATE FROM LISA HILBERT-SEMMES TO LEIGH TROCINE AT 2357 ON 11/02/01 ***** The following text is a portion of a facsimile received from the licensee: "At approximately 2250 hours on November 2, 2001, an additional CRDM penetration (location number 18) was identified as having flaws that are not acceptable under ASME Section XI IWB-3600. Five previously identified penetrations were reported [...]. This condition did not pose a significant safety risk during plant operation. This is being reported as a non-emergency 8-hour report in accordance with 10 CFR 50.72(b)(3)(ii)(A) and 50.73(a)(2)(ii)(A), a condition that results in a principal safety barrier being seriously degraded." The licensee notified the NRC resident inspector. The NRC operations officer notified the Region 2 Incident Response Center (Steve Rudisail) and NRR EO (John Zwolinski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-28
38434 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-10-27 08:50 | 2001-10-27 15:25 | 2001-10-28 | PARTIAL LOSS OF ONE CONTROL USED FOR DOUBLE CONTINGENCY (IN-LINE MONITOR). NRC BULLETIN 91-01 24 HOUR NOTIFICATION. On the evening of 10/26/01, low level waste solution from raffinate was recirculated, sampled, and analyzed for uranium content (0.0116gU/l and 0.0125gU/l). Authorization was then given to discharge the solution to the waste tank WD01. During the discharge to the waste tank, the in-line monitor was activated and the valves on the in-let line (to the waste tanks) were closed. An attempt was made to sample the solution in the waste tank; however, due to the low volume of solution in the waste tank, it was not possible to re-circulate the solution and obtain a sample. A non-destructive assay (NDA) of the tank was then performed. The scan results indicated approximately 55.7 grams of U-235 in the tank (This is below the tank limit). On the morning of 10/27/01, an NDA specialist evaluated the event. The NDA specialist determined that the peak for the solution had drifted outside the region of interest for the system. (I.e., 185 Kev peak for U-235). The NDA specialist then adjusted the gain on the monitoring system's electronics. The event is continuing to be evaluated. BACKGROUND: Low-level waste streams are discharged to Waste Tanks WD01 and WD02 from various sources (The solution from WD01/WD02 is then transferred to the Waste Water Treatment Facility). Multiple controls on these sources prevent significant accumulations of U-235 in the waste tanks WD01/WD02. These controls include dual sampling, filtration, visual inspections, and the use of an in-line monitor (Cambarra System). The in-line monitor activates and closes two (2) valves on the inlet line to the waste tanks when the monitor detects a uranium concentration above the action level. Based on process knowledge and the known history of the operation, a major process upset , in addition to failure of these controls, would have to occur before the uranium mass limit in Waste Tank WD01 or WD02 could be exceeded. WHAT IS THE CONTROL(S) OR CONTROL SYSTEM(S) AND THE FAILURE (S) OR DEFICIENCIES: Partial loss of one (1) control used for double contingency (in-line monitor). Concentration is used to control mass. When the in-line monitor detects a uranium concentration above the action limit, the monitor actuates and closes two (2) valves on the in-let line to two (2) waste tanks. It was determined that the peak for the solution had drifted outside the region of interest for the system (I.e., 185 Kev peak for U-235). WHAT ARE THE CORRECTIVE ACTIONS TAKEN AND WHEN WAS EACH IMPLEMENTED: Upon observation of the situation, discharge to Waste Tanks WD01/WD02 were immediately suspended (No other discharges were being made at the time). An attempt was made to sample the solution in the waste tank. Due to the low volume of solution in the waste tank, it was not possible to re-circulate the solution and obtain a sample. A non-destructive assay (NDA) of the tank was then performed. The scan results indicated approximately 55.7 grams U-235 in the tank. The solution in the transfer line was also sampled and analyzed for uranium content (0.248 gU/l) and 0.239gU/l). On the morning of 10/27/01, the gain on the in-line monitor system was readjusted. The valves remain closed until authorization to open the valves is given. WHAT IS THE SAFETY SIGNIFICANCE OF THE EVENT: Low safety significance due to defense-in-depth associated with the waste tanks. The NRC Resident Inspector was notified of this event. * * * RETRACTION ON 10/28/01 AT 1148ET BY RANDY SHACKELFORD TAKEN BY MACKINNON * * * After further investigation it was discovered that there was no drift problem or equipment problem with the in-line monitor. Double contingency control was always maintained. Therefore, this event is being retracted. R2DO (V. McCree) & NMSS EO (Bill Brach) notified. The NRC Resident Inspector will be notified of this retraction. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 1 | 2001-10-27
38433 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-10-27 02:08 | 2001-10-27 04:24 | 2001-11-05 | TWO OF THREE AUXILIARY FEEDWATER PUMPS DECLARED INOPERABLE The licensee reported that the auxiliary boiler (steam generator) feedwater pump 21 was declared inoperable at 0021 EDT due to high packing temperature during the planned plant shutdown. Later at 0208 EDT, the second pump, 23, was declared inoperable because the outboard bearing could not be kept below 200°F without the use of city water. City water is not seismically qualified leading to the declaration of pump 23 being inoperable. Pump 23 is functional and able to provide feedwater. Pump 22 is being used and is fully operational. The plant is being cooled down as planned and due to the pump problems has until 1400 EDT today, 10/27/01, to cool down to less than 350°F in accordance with technical specifications. The licensee expects to meet the requirement with no trouble. The licensee has notified the NRC Resident Inspector. ***** UPDATE FROM DENNIS CORNAX TO JOHN MACKINNON AT 2353 ON 10/28/01 ***** The following text is a portion of a facsimile received from the licensee: "On October 27, 2001, at 0452, Indian Point Unit 2 exited the 12-hour action statement of Technical Specification 3.4.B(1)b by achieving Hot Shutdown conditions with RCS temperature below 350°F. 23AFP remained in service for secondary side steam generator heat removal with City Water providing cooling to 23AFP's outboard bearing for the duration of the cooldown. Cold Shutdown was achieved on October 27, 2001, at 1215." "Although declared inoperable, preliminary evaluations by Engineering conclude that 21AFP would have been able to perform its safety function notwithstanding the high packing temperatures." "A test of 23AFP was completed with preliminary indications that it too would have been able to perform its safety function without City Water cooling to the outboard bearing jacket cooler." The licensee notified the NRC resident inspector. The NRC operations officer notified the Region I Incident Response Center (Neil Perry) and NRR EO (William Beckner). * * * RETRACTED AT 1342 EST ON 11/5/01 BY MARK LEONE TO FANGIE JONES * * * The licensee determined that the operators made a conservative call declaring auxiliary feedwater pump 21 inoperable due to higher than expected packing temperature and auxiliary feedwater pump 23 inoperable due to higher than expected outer bearing temperature. The pumps have been determined to have been able to perform their intended safety functions and the licensee is retracting this event notification. The licensee intends to notify the NRC Resident Inspector. The R1DO (James Linville) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-10-27
38432 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-10-26 19:17 | 2001-10-26 23:03 | 2001-10-26 | AUTOMATIC REACTOR SCRAM. ALL RODS FULLY INSERT INTO THE CORE. Unit Two reactor scram. The cause is presently under investigation. Preliminary indications are that the "B" Recirculation pump experienced a runback which was immediately followed by an increase to its previous speed, resulting in a rapid reactor power increase causing the neutron monitoring system (Average Power Range Monitors) to trip and cause a reactor scram. All rods fully inserted into the core. The following isolations occurred: Primary Containment isolated (Group 2 isolation), Secondary Containment isolation which started the Standby Gas Treatment System, and Reactor Water Clean-up isolated (Group 5 isoaltion). HPCI and RCIC system initiated on low low reactor vessel water level, but did not inject into the reactor due to the feedwater system recovering reactor pressure vessel water level. All Emergency Core Cooling systems and the Emergency Diesel Generators are fully operable if needed and the electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-10-26
38431 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2001-10-26 16:00 | 2001-10-26 18:44 | 2001-10-26 | FITNESS FOR DUTY A non-licensed supervisor employee was confirmed positive during a random drug test. The employee's badge has been blocked. Contact the HOO for further details. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2001-10-26
38430 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-10-26 11:39 | 2001-10-26 12:46 | 2001-10-26 | OFFSITE NOTIFICATION MADE TO FLORIDA FISH AND WILDLIFE CONSERVATION COMMISSION. A dead American crocodile hatchling discovered by plant access road, just outside employee parking lot. The hatchling appears to have been struck by a vehicle. State of Florida Fish and Wildlife Conservation Commission has been notified. The NRC Resident Inspector will be informed of this event notification by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-10-26
38429 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-10-26 | 2001-10-26 08:55 | 2001-10-26 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE A Troxler gauge was stored in an approved temporary storage site at a construction facility. Overnight, several storage containers and offices were broken into. The hasp of the storage container was broken and an additional door inside the container was forced and one of three gauges was stolen. The police have been notified and a press release will be issued. The keys to the gauge were not at the temporary site and were not taken with the gauge. The gauge is a Troxler model 3440, serial number 21218, with 8 mCi Cs-137 and 40 mCi Am-241:Be sources. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2001-10-26
38428 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-10-25 15:30 | 2001-10-25 23:24 | 2002-02-21 | NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 1530, on 10/25/01, the Plant Shift Superintendent (PSS) was notified that the 70-foot stack in the C-310 building was discovered to contain a deposit of fissile material. There is no NCSE/A which covers operation, maintenance, storage, etc. of this equipment. The presence of a deposit in the stack was not expected. A single NDA has been performed and indicates a deposit of less than 61 lbs.(U). Assay smears taken on the stack previously indicated an assay of approximately 1.6%. SAFETY SIGNIFICANCE OF THE EVENTS: For the assay of the deposit, the piping geometry and deposit mass are not sufficient to support a criticality. However, no NCSA controls have been established to address this fissile material operation. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: Based on the assay and geometry of the piping it is not feasible for a criticality to occur in the pipe. Additionally, the pipe located approximately 8 feet above the floor and is therefore not feasible to have spacing violations. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Since this equipment does not have an NCSA for it, there is no controlled parameter. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): 61 lbs. U with an enrichment of 1.6% U-235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTIONS OF THE FAILURES OR DEFICIENCIES: The 70-foot discharge stack has been abandoned in place since the 200-foot stack was placed into service in the early 1980s. The 70-foot stack was last used briefly in the 1996 timeframe. The 70-foot stack has not been previously identified as a fissile material operation. This operation has not been evaluated for nuclear criticality safety. Therefore, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Characterize the remaining sections of the 70-foot stack system. Control the are around the stack and post as required by CP2-EG-NS1031. The NRC Resident Inspector was notified of this event by the certificate holder. * * * UPDATE 1845EST ON 2/21/02 FROM CALVIN PITTMAN TO S. SANDIN * * * The following information is provided as an update: "Further walk downs identified exhaust oil filters (located near the C-335 Seal Exhaust/Wet Air Station) as potentially fissile material operation without an approved NCS evaluation. "SAFETY SIGNIFICANCE OF THE EVENTS: The oil filters are of favorable geometry for the plant maximum assay at the time the filters were cut from the seal exhaust system. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: The oil filters are separated from the seal exhaust system by air gaps. The use of the filters had been discontinued, therefore there is no potential for fissile material to be added to the filters. In order for a criticality to be possible, a spacing violation would have to occur. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The amount of material in the oil filters is unknown at this time but activity levels in the filters indicates less than a safe mass. Further analysis will be performed in accordance with the approved remediation plan. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTIONS OF THE FAILURES OR DEFICIENCIES: The seal exhaust oil filters have not been previously identified as a fissile material operation. This operation has not been evaluated for nuclear criticality safety. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The filters will be characterized in accordance with NCS guidance, which will be provided in a remediation guide." The NRC Resident Inspector was notified of this event by the certificate holder. Notified R3DO(Jorgensen and NMSS(Brach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-10-25
38427 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-10-25 10:00 | 2001-10-25 23:19 | 2001-10-25 | NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 1000, on 10/25/01, the Plant Superintendent (PSS) was notified that the independent verification for selecting the correct cylinder for washing was performed by the same operator, violating NCSA 400-002. This NCSA states that a second person, independent of the first person, verify that the correct cylinder is being washed. The purpose of this requirement is to preclude washing an unintended cylinder. The cylinder which was being washed was a non-fissile cylinder. SAFETY SIGNIFICANCE OF EVENTS: Double contingency for cylinder was operation is based on selecting the correct cylinder to wash. A cylinder was on the washstand that was not verified, by two independent people, to be an approved cylinder. The cylinder was subsequently verified independently to be non-fissile. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, a cylinder would have to be washed which contained greater than a critical mass of fissile material. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Independent verification of correct cylinder. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): This cylinder contained non-fissile material. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Double contingency is maintained by implementing two controls to ensure the correct cylinder is washed. The first leg of double contingency is based on ensuring that the cylinder selected for washing has been approved. The cylinder met the criteria and was approved for washing. This control was not violated. The second leg of double contingency is based on independent verification that the cylinder, after being put on the washstand but prior to being washed, is an approved cylinder. Since the independent verification was done incorrectly the control was violated and double contingency was not maintained. Since double contingency is based on two controls on one parameter, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Continue processing the cylinder according to CP4-CU-CH2110. (A second person has independently verified that the cylinder washed was an approved cylinder according to step 8.4.3, of procedure CP4-CU-CH2110.) The NRC Senior Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-10-25
38426 | 0 | TRAP ROCK INDUSTRIES |  |  |  |  | 2001-10-24 22:30 | 2001-10-25 12:16 | 2001-10-28 | STOLEN TROXLER ASPHALT DENSITY GAUGE CONTAINING 10 MILLICURIES OF CESIUM-137 Prap Industries was performing work on a newly paved road which was closed to traffic at the intersection of Interstate 95 and Route 31 located in Ewing, NJ. A Prap Rock Industries employee placed the Troxler gauge, Model # 4640B, in a cart and moved the cart next to a tree and went off to perform other duties. When the person returned, time unknown how long the person was away from the unattained gauge, he discovered that the gauge and cart were missing. This individual immediately notified the onsite New Jersey State Troopers that the gauge was missing. A search of the area was conducted with not results in finding either the gauge or the cart. NRC Region 1 individual was notified of this event by the licensee. ***** UPDATE AT 0740 ON 10/28/01 FROM NRR (KATHY GRAY) TO LEIGH TROCINE ***** This event is being updated to correct the licensee's name. It should have been Trap Rock Industries in lieu of Prap Rock Industries. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-10-25
38425 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-10-25 00:25 | 2001-10-25 02:07 | 2001-10-25 | WORKER OVERCOME BY HEAT TAKEN TO LOCAL MEDICAL FACILITY The licensee evacuated a worker who was working in containment and was overcome by the heat. The worker was transported using the utility's emergency vehicle. There was a small area of contamination on the worker's neck which was decontaminated during the trip to the hospital. The worker was not contaminated when admitted to the hospital. The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2001-10-25
38424 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-10-24 16:25 | 2001-10-24 19:09 | 2001-12-18 | PROCEDURE USED FOR INSTALLATION OF TEMPORARY FIRE SEALS WAS NOT IN COMPLIANCE WITH THE CALCULATION QUALIFYING THE TEMPORARY FIRE SEALS During an internal review of the fire protection program at Point Beach Nuclear Power Plant, it was determined that the procedure used for the installation of temporary fire seals was not in compliance with the calculation qualifying the temporary fire seals. The procedure called for 4 inches of Kaowool while the calculation demonstrated the 5 inches would ensure adequate fire protection. Out of the 9 barriers that were identified, 4 of them are required to provide train separation for safe shut down equipment. Due to the identified condition, these penetrations may not have adequately provided such separation as required by our safe shutdown analysis. Immediate actions taken included: 1) Affected penetrations were identified and declared out of service. 2) Appropriate fire rounds were commenced. 3) Installed the required 5 inches of Kaowool in the identified barriers and returned the barriers back to service. Pending corrective actions: Although the calculation determined 5 inches of Kaowool provides an adequate fire barrier, engineering will perform an additional evaluation to determine if 4 inches of Kaowool would suffice. The NRC Resident Inspector was notified. * * * UPDATE 1409EST ON 12/18/2001 FROM RYAN RODE TO S. SANDIN * * * The licensee is retracting this report based on the following: "Subsequent to this notification our Engineering Staff has prepared and approved, a Fire Protection Engineering Evaluation (FPEE 2001-003) of the as-found condition for these temporary fire seals following the guidelines of Generic Letter 86-10. This analysis demonstrates that a 4 inch temporary penetration seal constructed of 8 pounds per cubic feet ceramic fiber material satisfies the time function of a 3 hour rated seal by preventing fire propagation across the barrier. Accordingly, we have concluded that the presence of temporary fire seals with 4 inches of seal material did not significantly compromise plant safety with respect to separation of the safe shutdown equipment and this event notification should be retracted. The licensee informed the NRC Resident Inspector. Notified R3DO(Phillips). | 63 | 100 | 0 | 63 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-10-24
38423 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2001-10-24 17:40 | 2001-10-24 18:41 | 2001-10-24 | GREATER THAN 25% OF THE OFFSITE EMERGENCY SIRENS WERE OUT OF SERVICE At 1523 on 10/24/01 16 of 44 emergency sirens were determined to be inoperable for greater than one hour due to a storm causing power outages. At 1620 six of the original non-functioning sirens were returned to service, leaving a total of ten sirens out of service which is less than 25% being out of service The remaining out of service sirens are expected to be returned to service on 10/25/01 as power is restored to these areas. The NRC Resident Inspector and local agencies were notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-10-24
38422 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2001-10-24 10:00 | 2001-10-24 13:41 | 2001-10-24 | ACTUATION OF THE EMERGENCY FEEDWATER SYSTEM At 1000 on October 24, 2001, Crystal River Unit 3 (CR-3) was in MODE 3 withdrawing Safety Rod Group 2 in preparation for Reactor Startup following a refueling outage. In-plant Auxiliary Steam loads were being supplied from Crystal River Unit 1 (CR-1). Auxiliary Steam (AS) loads are normally supplied from CR-1 or Crystal River Unit 2 (CR-2) (sister fossil units) when Unit 3 is not operating at high power. CR-2 was off-line at the time and CR-1 tripped, resulting in a complete loss of Auxiliary Steam (AS) to Unit 3. Motive steam was lost for the running Main Feed Pump and Main Condenser vacuum lowered. Both Once Thru Steam Generator (OTSG) levels lowered resulting in an Emergency Feedwater System (EFW) actuation on low OTSG level. The OTSG levels were restored to normal by EFW. OTSG levels remained on scale throughout the transient. Safety Rod Group 2 was fully inserted and Reactor Startup preparations were suspended. The AS header was repressurized from the Main Steam System and Main Condenser vacuum was restored. Reactor Coolant System (RCS) temperature and pressure are stable at normal hot standby values and plant startup will continue once AS is restored from CR-1. This event was an event or condition that resulted in a valid actuation of the Emergency Feedwater System and is thus reportable as an eight hour report. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-10-24
38421 | 0 | DRESSER-RAND |  |  |  |  | 2001-10-22 | 2001-10-24 05:05 | 2001-10-24 | 10 CFR PART 21 REPORT CONCERNING TERRY TURBINE TRIP & THROTTLE VALVE SCREW SPINDLE The following is from a facsimile report: DESCRIPTION OF DEFECT: Material substitution of grade 1212 Steel in place of grade 1018 carbon steel specified by design. ENGINEERING EVALUATION & RECOMMENDATIONS: Following the failure of an installed Trip/Throttle valve screw spindle on the Catawba unit #2 AFW Pump Turbine (Terry Turbine S/N 40096A or B) on May 25, 2000, the material of the failed screw was analyzed and found to be Grade 1212 steel. Gimpel gave verbal confirmation that the screw material was incorrect (Grade 1213 and 1215 steel) at the Terry Turbine Users Group meeting on July 18, 2001 Gimpel has traced the supplied material to a single lot of approximately 50 original screw spindles manufactured in 1974, and has identified the originally affected Trip & Throttle valve serial numbers as 74-12201-01 to 74-12244-02, 78-13136-01, 78-13215-01, and 78-13091-01. Written confirmation of this defect and a listing of affected valves was received by Dresser-Rand 10/11/01. Following this incident, additional information was received indicating that a screw spindle installed in Palo Verde Unit 1 was found cracked In 1992, and was determined to be grade 1213 steel. Dresser-Rand tested the material of a functional screw spindle removed from an in-house test valve (Gimpel serial number 74-12243) and determined the material was grade 1212. It is unknown whether the material substitution was a contributing factor in the failures of the screw spindles at these sites. The trip valves in question have been in operation for many years, and although the material used is less desirable in this application than the design specified material, the limited number of failures indicates that the immediate risk of continued operation is minimal. It is acknowledged however, that a substantial safety hazard may exist due to this defect in that failure of this component can result in steam isolation preventing the emergency feedwater turbine from performing its safety-related function. Recommendations: 1) Units using Gimpel T&T valves in the serial number series listed above which may have the original Screw spindle installed should replace their screw spindles at the next maintenance opportunity. The original spindles should be destroyed. 2) It is additionally recommended that any Gimpel screw spindles in-stock or in-service which may have been manufactured in the 1974-75 timeframe be treated as suspect and be tested to confirm that the material is correct (Grade 1018 carbon steel). A written Final Report will be submitted no later than 11/21/01. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2001-10-24
38420 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-10-23 17:12 | 2001-10-23 19:40 | 2001-10-23 | THE PLANT HAD A REACTOR SCRAM FROM 98% POWER DUE TO A GROUP 1 ISOLATION The group 1 MSIV isolation instrumentation was bumped in the plant causing an inadvertent group 1 isolation which resulted in a reactor scram. Group 2 and 3 isolations also occurred on low reactor level (+9") during the reactor scram. The low-low set controlled reactor pressure while the MSIV's were closed. The "H" SRV cycled approximately 6 times and fully reseated. All rods fully inserted and no ECCS actuation occurred. The NRC Resident Inspector, the state, and local agencies were notified. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-10-23
38419 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2001-10-23 11:02 | 2001-10-23 14:57 | 2001-10-23 | REACTOR SCRAMMED FROM 100% POWER DUE TO TURBINE VALVE FAST CLOSURE SIGNAL Unit 2 was operating at 100% power when a Main Generator Lockout resulted in a Reactor SCRAM from a Turbine Control Valve Fast Closure Signal. Reactor Pressure peaked at 1125 psig causing 5 Safety Relief Valves to open, and an automatic ARI (Alternate Rod Insertion) initiation on high reactor pressure. The SCRAM transient also caused an expected reactor low level condition of minus seven inches (-7 inches) resulting in PCIS (Primary Containment Isolation System) Group II and III Isolations and SBGTS (Standby Gas Treatment System) initiation. All plant systems operated as expected with all rods being fully inserted and all relief valves fully reseating. The Unit 2 Reactor is shutdown, and cause of the Generator Lockout is being investigated. Reactor level is 23 inches, and a controlled reactor cool down is in progress. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-10-23
38418 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-10-23 | 2001-10-23 14:54 | 2001-10-23 | THE EMERGENCY NOTIFICATION NETWORK WAS INOPERABLE The licensee reported that their Emergency Notification Network(ENN) was declared inoperable due to an on site switching problem. Three channel banks went down and did not automatically transfer to backup source. The problem has been identified and was restored(test satisfactory) at 1324 CDT. The problem with the automatic transfer is still being investigated. The licensee uses the Southern Line System as a backup for the ENN. The NRC Resident inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-10-23
38417 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-10-23 | 2001-10-23 12:59 | 2001-10-23 | THE CITY OF COLORADO SPRINGS REPORTED A MISSING Ni-63 RADIATION SOURCE The wastewater treatment plant has gas chromatography equipment that uses electron capture detectors containing 8-15 mCi Ni-63. For as long as anyone now present can remember, the instruments in use there have been made by Hewlett Packard. There have been 4 detectors made by Varian in a box in storage on a shelf in a cabinet in the lab. Those detector cells did not fit on the HP GCs. The lab manager discovered another laboratory that wanted the detectors that were in storage. They solicited and received a copy of that laboratories license to possess radioactive material (as well as the license for CJ Bruyn, a detector maintenance facility). The 4 detectors were sent to C.J. Bruyn of Bellingham Washington, who upon receiving the detectors and opening the cases for cleaning reported that one of them did not contain the radioactive source. An exhaustive search of the lab, concentrating on the cabinet area where the sources were stored revealed no hint of the source. The emissions or Ni-63 are of such energy that external readings with a survey instrument would never indicate the presence of such a source. Areas of the laboratory have been wipe tested for contamination from the time that sources have been in use there, and no lost source has been so revealed. The source housings for the Varian sources have not been opened at the Laboratory, to the best of anyone's knowledge. In the past, the HP sources were opened for cleaning and maintenance, but never the Varian sources. No one now at the lab can remember using Varian GCs and so cannot remember that one of those detectors did not work (possibly indicating a missing source). The only scenarios that make any sense is that either 1. The detector cell was received without the radioactive source from the original vendor or a facility that cleaned it. 2. The source inadvertently fell out of the detector cell when it was opened at CJ Bruyn and was not detected. The individual involved at CJ Bruyn denies this possibility. Ni-63 is a beta emitter with 67 keV electron energy and approximately 100y half-life. The range of the emissions in air is ~10 inches, if the source was in contact with an individuals skin the electrons would penetrate ~0.35mm. A significant radiological hazard is hard to imagine unless the source was ingested, inhaled, or held against the skin for a protracted period. It has been discussed with the department that ingesting Ni-63 is not even a hazard of significance. Nickel is not absorbed by the body and the beta particles are absorbed by the fecal matter. Modifying the procedures to avoid a future occurrence of a similar instance is not indicated due to the extremely unlikely probability. We no longer have EC detectors that are in long-term storage and use the ones that we have on a regular rotation, so we will know if the source is not present. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-10-23
38416 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2001-10-22 13:57 | 2001-10-22 18:48 | 2001-10-24 | DISCOVERY OF A THROUGH-WALL LEAK AROUND 3 (THREE) CONTROL ROD DRIVE MECHANISM NOZZLES (REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAK) On October 11 and 12, 2001, following shutdown for a scheduled refueling outage, Three Mile Island Unit 1 (TMI-1) performed a visual inspection of the Reactor Vessel (RV) Control Rod Drive Mechanism (CRDM) nozzles per NRC Bulletin 2001-01. The inspection revealed evidence of boric acid buildup around 12 CRDM nozzles. No other CRDM nozzles showed similar boron buildup. After the RV head was removed and placed on the storage stand, additional inspections were performed. At approximately 1357 on October 22, 2001, Engineering evaluation of the visual inspection, Liquid Penetrant Test (PT) data and Ultrasonic Test (UT) data identified through-wall indications on three CRDM nozzles. This engineering evaluation concluded that the visual indications around CRDMs 44, 35, and 37 indicate a Reactor Coolant System (RCS) pressure boundary leak. The inspection is not yet completed, thus additional CRDM through-wall indications may be identified. This condition is consistent with industry experience with Primary Water Stress Corrosion Cracking (PWSCC) in similar components that have been evaluated as part of the NRC Generic Letter 97-01 and NRC Bulletin 2001-01. Additional nozzles may be examined by UT in accordance with TMl-1's response to NRC Bulletin 2001-01. This condition did not pose a significant safety risk during plant operation. TMl-1 plans to perform CRDM nozzle repairs during the current refueling outage. Since the condition resulted in leakage through the RCS pressure boundary, it is being reported as a non-emergency [8-hour] report in accordance with 10 CFR 50.72(b)(3) (ii)(A) and 50.73(a)(2)(ii) (A). The NRC resident inspector has been notified. * * * UPDATED AT 1015 EDT ON 10/24/01 BY ADAM MILLER TO FANGIE JONES * * * Two additional CRDMs (29 and 64) indicate a RCS pressure boundary leak. This brings the total to 5 CRDM nozzles showing through-wall leaks. The licensee notified the NRC Resident Inspector. The R1DO (John Kinneman) and the NRR EO (William Beckner) have been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-22
38415 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2001-10-22 | 2001-10-22 12:02 | 2003-09-16 | THE STATE REPORTED A STOLEN TROXLER MOISTURE/DENSITY GAUGE FROM ONE OF THEIR LICENSEES Bowser-Morner, Inc (State of Ohio licensee) reported the theft of a Troxler moisture/density gauge (model 3430, serial 31270) containing a 1.44 GBq (38.9 mCi Am-Be sealed source and a 0.28 GBq (7.7 mCi) Cs-137 sealed source. The gauge was stolen from the back of a truck parked at an employee's residence in Toledo, Ohio. The gauge was stolen in the time period between the evening of 10/20/01 and the morning of 10/22/01. The handle of the gauge case had been pried off, leaving the handle and locked chain. The licensee notified the Toledo and Oregon, Ohio police departments. * * * UPDATE ON 09/16/2003 AT 1110 EDT BY MIKE SNEE TO MACKINNON * * * On 09/12/2003, the Troxler moisture density gauge was found in an abandoned building in Toledo, Ohio by the police. It has been returned to the licensee. The gauge was still inside the case and locked. The licensee will perform a leak test of the gauge then will start using it again. Mike Snee is with the Ohio Bureau of Radiation Protection. R3DO (Lanksbury) & NMSS EO (Doug Broaddus). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2001-10-22
38414 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-09-29 08:30 | 2001-10-22 12:00 | 2001-10-22 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE The following is a portion of a fax received from the Texas Department of Health: "On the morning of September 29, 2001, [a] QTE technician picked up Troxler Gauge [Model 3440] SN:30229 from office to perform test on a project in Garland at 8:30 a.m. On his way to project he realized that he forgot his wallet and returned home to pick it up. After returning to his pickup (1998 Chevy S-10 - Silver), he noticed that the lock was cut and the gauge had been stolen (approximately 8:00 a.m.). Source numbers are (CS-137: 750-4377) and (AM-241: 47-27208)." The licensee notified the City of Garland Police Department (Report Number R028859) and the Texas Department of Health (Texas Incident Number I-7816). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-10-24
38413 | 0 | UNDERWOOD ENGINEERING |  |  |  |  | 2001-10-22 07:45 | 2001-10-22 11:10 | 2001-10-22 | REPORT INVOLVING A STOLEN TROXLER GAUGE A Troxler Gauge, Model 3430 S/N 31156, containing 8 millicuries Cs-137 and 40 millicuries Am-241/Be was stolen from the bed of a company truck at a construction site on Ruan Street, off of Frankfurt, in the northeast District of Philadelphia, PA. The employee parked the truck at approximately 0730EDT and discovered both the gauge and it's case missing at 0745EDT when he returned. The device was properly stowed for transport with indication of forcible removal. The licensee notified both Troxler and the Philadelphia Police Department. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-10-22
38412 | -1 | CABELL HUNTINGTON HOSPITAL |  |  |  |  | 2001-10-22 | 2001-10-22 08:16 | 2001-10-22 | MEDICAL MISADMINISTRATION INVOLVING A DIAGNOSTIC GIVEN TO THE WRONG PATIENT At approximately 1400EDT on Friday,10/19/01, a 12.2 millicurie Tc-99m cardiolite dose for a resting cardiolite study was administered to a 70-year old female patient. The technologist administering the diagnostic dose relied on oral confirmation as to the patient's identity since the patient's wristband was missing. The patient responded "right" several times when asked if she was patient "x." When she was taken to the treadmill area she identified herself as patient "y." The Director of Nuclear Medicine was informed this morning when he returned to work of the error and has informed the referring physician. The patient will be notified later today. There are no adverse effects anticipated from this incident. Corrective action includes verification of identity using wristbands. * * * UPDATE 1205EDT ON 10/22/01 FROM PEATROSS TO S. SANDIN * * * The licensee is retracting this report in that it does not meet the criteria for reporting as a misadministration. Notified R2IRC and NMSS(Frant). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 2 | WV | HOS |  | 35.33 |  |  |  | 0 | 2001-10-22
38411 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-10-21 18:20 | 2001-10-21 19:41 | 2001-10-22 | LOSS OF SOME OFFSITE COMMUNICATIONS The licensee reported that the Emergency Notification Network, used to contact state and local government agencies, is currently inoperable. The licensee has confirmed that commercial telephone communication with these agencies is still possible. The NRC resident inspector will be informed of this condition by the licensee. * * * UPDATE 0139EDT ON 10/22/01 FROM ROBERT FUCICH TO S. SANDIN * * * The licensee restored the Emergency Notification Network to service at 0039CDT. Notified R2IRC. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-10-21
38410 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2001-10-20 16:00 | 2001-10-20 19:25 | 2001-10-20 | DEGRADED STEAM GENERATOR TUBE FOUND DURING EDDY-CURRENT INSPECTION "At 1600 hours on Saturday, October 20, 2001 as a result of tube eddy current inspections performed during the 1R14 outage, TMI-1 determined that at least one tube in the 'B' OTSG was seriously degraded. Inspection of the tube found that the tube had been mechanically damaged to the extent of approximately 90% through wall thickness by an adjacent plugged tube that had apparently severed during the last operating cycle. "Primary to Secondary leakage was very low throughout the last operating cycle, well below Technical Specification limits. The current condition of the tube is such that engineering judgment is that the tube would not have had sufficient strength to meet all of the structural integrity criteria described in NUREG 1022, Rev. 2. "The 'B' OTSG is currently inoperable with both the upper and lower primary manways removed. OTSG tube inspections are in progress. Additional testing and inspection will be conducted. Structural integrity of the inservice OTSG tubes will be confirmed prior to restart. The extent of the condition discovered and the cause of the condition will be addressed in the followup licensee event report that will be submitted in accordance with 10 CFR 50.73(a)(2)(ii)." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-20
38408 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-10-19 | 2001-10-19 16:39 | 2001-10-19 | 10 CFR PART 21 REPORT "During RFO-22, Carboline Carbozine CX-11SG paint primer was applied to the drywell shell (inner wall) to the floor joint as part of a qualified seal design. The purpose of this seal is to provide a moisture barrier to mitigate water entering the shell to concrete interface. In preparation for and during subsequent applications of the primer, significant gelling/premature set-up of the paint was exhibited (ref. ER20011169, dated 5/11/01). Within 24 hours of the paint application, the paint began to lift and blister. This paint was supplied under an Appendix B Vendor QA Program in accordance with VY PO 011040. Failure analysis received from Carboline and an independent test lab indicated the paint was defective. Carboline indicates the failure was most likely due to a moisture problem during manufacture. The problem was with part 'A' of the two-part paint. The impact of the failed paint applied in the drywell during the outage was evaluated under ER 20011169. The seal was then coated with a single coat of Carboline 890. Carboline Corporation has verified this to be an acceptable application until a permanent remedy is achieved." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 21.21 |  |  |  | 0 | 2001-10-19
38407 | 0 | EASTERN ISOTOPES INC |  |  |  |  | 2001-10-19 15:19 | 2001-10-19 16:31 | 2001-10-19 | POSSIBLE OVEREXPOSURE TO AN EMPLOYEE'S EXTREMITIES Eastern Isotopes Inc. was notified by the Landauer Company of Chicago, IL that an employee had a reading from her plastic TLD ring for the month of September of 56,350 millirem. From the first of the year to the end of August she already had 15,570 millirem. The employee works in PET Imaging where the suspected isotope is fluorine-18(F-18). However, for one week in September she was operating their dose drawing robot. Normally the operators of that device get about 10-12 millirem/dose, but she may have gotten up to 110 millirem/dose. They are continuing to investigate to determine if overexposure occurred during that one week period or over the whole month period. They will remove the employee from all duties until the investigation is complete. The licensee will notify the State of Virginia. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2001-10-19
38406 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-09-20 09:30 | 2001-10-19 10:50 | 2001-11-30 | DISCOVERY OF MISSING SHIPMENTS (30-DAY REPORT) The following text is a portion of a facsimile received from the licensee: "On September 12, 2001, NFS provided two packages to Airborne Express, Inc. for delivery. On September 20, 2001, NFS was advised by Airborne Express that both of these packages were lost. Airborne Express continued to search for these packages and found the following:" "* The tracking system shows that the packages were picked up at NFS on 9/12/01. Due to the grounding of all aircraft after the events of September 11, 2001, the packages were delivered by truck to Airborne's facility at Knoxville, TN." "* The tracking system shows the receipt of the packages at the Knoxville terminal on September 12, 2001. The packages were loaded onto a contract trucking company's truck for transport to Airborne's Facility in Wilmington, OH. An Airborne employee and the contract truck driver recall this loading, but arrival of the packages at the Wilmington, OH facility is not shown by the tracking system." "* Airborne also checked all Airborne truck hubs in the United States, and performed an all-station trace with no results." "* The addresses were contacted (also by NFS) to ensure that the packages bad not been received." "* The loading/receipt areas at NFS, and the facilities of Airborne in Blountville, TN, Knoxville, TN, and Wilmington. OH have been inspected two times (spaced a week apart) for these packages." "* The manufacturer of the pail (FBF Nuclear Containers), whose Knoxville, TN address was on the pail, was contacted." "* Airborne Express believes that these packages are in an overpack container. Due to the light weight of the radioactive material packages, this overpack container probably appears to be empty. Also, the black pails would be hard to see inside of the overpack." "* A radiation survey was conducted unsuccessfully at Airborne's Wilmington, OH facility, but was unsuccessful due to the low level of radiation from these packages." "Since both packages are expected to be together, the data for both is provided; however, the radioactive materials are licensed by different government agencies:" "Thorium Package" "1. Licensed by: State of Tennessee" "2. Airborne Express Airbill: # 477 138 3784" "3. Shipping Classification: Radioactive Material, LSA, 7, UN2912" "4. Additional Shipping Information: LSA-I, Yellow II Label, T.I. <0.8, Cargo Aircraft Only" "5. Material: 4.9 kgs Thorium (natural) metal, solid" "6. Activity: 39.96 MBq (1.08 mCi)" "7. Package: Black 5-gallon pail (12" dia x 14"), DOT Spec 7A, Type A package" "8. [Addressed]: APL Engineered Materials, [...], Urbana, IL, [...]" "Uranium Package" "1. Licensed by: U.S. NRC" "2. Airborne Express Airbill: #477 137 3784" "3. Shipping Classification: Radioactive Material, LSA, 7, UN2912" "4. Additional Shipping Information: Fissile Excepted, LSA-II, White I label, T.I. = 0.1" "5. Material: 1 g highly-enriched U samples, containing 1 g U-235, solid, [uranium dioxide, decommissioning sample from 200 complex]" "6. Activity: 3.37 MBq (0.091 mCi)" "7. Package: Black 5-gallon pail (12" dia x 14"), DOT Spec 7A, Type A package" "8. Addressed: O'Brien & Gere Laboratory, ATTN: Mr. Mike Gerber, [...] Syracuse, NY, [...]" The licensee notified NRC Region 2 (Bill Gloersen) and the State of Tennessee. (Call the NRC operations officer for contact information.) * * * UPDATE ON 11/30/01 @ 1514 BY ROSENBERGER TO GOULD * * * The material was found today intact at the Airborne Express facility in Wilmington, Oh. It was in an unmarked container back in a corner of the facility. It will be forwarded to Nuclear Fuel Services. NFS has notified the FBI that the material was found. Notified Reg 2 Rdo(Mcalpine), NMSS EO(Fred Brown), IRO(Mamish) and SGT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 20.2201(a)(1)(ii) |  |  |  | 1 | 2001-10-19
38405 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-10-18 15:10 | 2001-10-18 16:08 | 2001-10-18 | SECURITY EVENT Unescorted access granted inappropriately. Immediate compensatory actions taken upon discovery. The licensee will inform the NRC resident inspector. Contact the NRC Operations Center for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-10-18
38402 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-10-17 14:02 | 2001-10-17 17:56 | 2001-10-17 | HPSI SYSTEM DECLARED INOPERABLE. "At 1415 on 10/17/01, the HPCI steam stop valve did not reopen upon release of the local turbine trip knob. This condition was discovered during surveillance testing. The surveillance procedure directs declaring the HPCI system inoperable if this condition occurs. The HPCI system was originally declared inoperable at 1402 on 10/17/01 for surveillance testing. This is being reported as a failure of a single train system such that it cannot perform its safety function of mitigating the consequences of an accident. All other Emergency Core Cooling Systems are operable. This event is being entered into the corrective action and work control programs for investigation and resolution." The licensee notified the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-10-17
38401 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-10-03 05:00 | 2001-10-17 17:06 | 2001-10-17 | AGREEMENT STATE REPORT - STOLEN GAUGE The following is from a faxed report: This is notification of a Campbell Pacific Nuclear Density Gauge (MC-2), Serial Number M20013097 that was stolen on 10/03/2001. The gauge was stolen at a Stop-N-Go at 702 Mason Rd. in Katy, Texas. The gauge was chained in the back of a pick-up truck with the chain through the top handle and one side handle, with an additional lock on one of the hinges. The hinge was broken off and there was just enough slack in the chain to remove the gauge. The theft occurred at approximately 5:00 am. ... reported the theft to your office around 7:15 a.m. the morning of the theft. The theft was also reported to the Harris County Sheriffs Department and was assigned a case number (01110031145). Since this event occurred as the result of an illegal act, we are unable to guarantee such occurrence will not be repeated. However, I've issued a memo and instructions to all employees that gauges must be chained through all three handles and that the chain shall be taught so that entry can only be obtained by unlocking the chain or cutting the chain. It is possible that the gauge might not have been stolen if this procedure had been followed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-10-19
38400 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-10-17 06:50 | 2001-10-17 15:05 | 2001-10-17 | OFFSITE NOTIFICATION DUE TO SMALL OIL SPILL The licensee notified the New Hampshire Environmental Services of an oil spill of less than or equal to 25 gallons. There was no oil discharged from the site nor did any enter a waterway. Also, no impact to groundwater was observed. The licensee is removing the contaminated soil. The licensee is in the process of replacing some oil bearing piping. A section of that piping contained residue of oil, which was washed out by heavy rains yesterday. The amount of oil is small and this notification is conservative based on the fact that it was not possible to accurately determine the quantity. Oil was observed in the rainwater inside an excavation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-10-17
38399 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2001-10-17 02:48 | 2001-10-17 11:10 | 2001-10-17 | UNEXPECTED LOSS OF POWER TO A SAFETY-RELATED SWITCHGEAR The following text is a portion of a facsimile received from the licensee: "At approximately 2:48 am CDT, the normal supply breaker to the Division 2 4160-volt safety-related switchgear opened unexpectedly, causing a loss of power to the Division 2 electrical systems. This event is being reported in accordance with 10CFR50.72(b)(3)(iv)(A) as a valid actuation of safety systems." "The Division 2 diesel generator responded as expected by automatically starting and restoring power to the Division 2 switchgear. Also, containment isolation valves actuated as expected in the following systems due to the loss of power: reactor water cleanup, reactor building floor and equipment drains, reactor coolant sampling, containment airlock air supply, and containment ventilation systems. Automatic actuations occurred as expected in the following systems: standby gas control, annulus mixing, control building ventilation, and fuel building ventilation." "Following the event, the containment isolation logic was reset and ventilation systems were returned to their normal configuration." "The Division 2 diesel generator remains in service supplying the Division 2 switchgear. The cause of the trip of the normal supply breaker to the 4160[-volt] standby switchgear is being investigated." The licensee notified the NRC resident inspector. | 80 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-10-17
38398 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-10-17 06:11 | 2001-10-17 10:44 | 2001-10-17 | REACTOR WAS MANUALLY SCRAMMED FROM 100% POWER. At approximately 0610 on October 17, Instrument AC bus 1Y11 failed due to an inverter failure. One of the two reactor feed pumps tripped due to a low suction pressure caused by its minimum flow valve failing open on the loss of instrument power. The Reactor was then manually scrammed in anticipation of a Reactor low level trip. All rods were inserted, no relief valves lifted and the plant response was as designed with the exception that one main generator breaker failed to trip (the transmission system isolated the generator as designed). Containment isolation Groups 2 through 4 were initiated when reactor level decreased below 170 above top of active fuel and a Group 5 isolation was initiated by the loss of instrument power. Reactor level was restored and maintained using the RCIC system initially (auto initiation) and subsequently the reactor feed system. The plant is currently in Mode 3 with plans to go to Mode 4. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-10-17
38396 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-10-12 | 2001-10-16 16:54 | 2001-10-16 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "A gauge was stolen on Sunday night, October 12, 2001. The RSO learned of the theft today. The gauge was a Troxler Model 3430, serial number 28502. The sealed sources were as follows: a 40 millicurie Am-241/Be, serial number 4725568 and an 8 millicurie Cs-137 source, serial number 7502724. "The gauge was taken from the back of a truck at a residence. It was in its case which was stolen along with other equipment on the back of the truck. The case was probably not secured or locked to the truck. The source rod was probably locked. A police report is being made. Also DOT is being contacted by the Licensee. "The Licensee will submit a written report within thirty days". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-10-19
38395 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2001-10-16 | 2001-10-16 16:18 | 2001-10-16 | NRC BULLETIN 91-01 REPORT - 24 HOUR The following is from a faxed report: At approximately 1630 on October 15, 2001 following an automatic shutdown of Dry Conversion Process Line 2, a higher than normal moisture analytical result was identified on Line 2A powder outlet cooling hopper. Manual moisture sample results indicated free moisture content in the U02 powder averaged 1.2% which is above the operational limit of 0.4% but well below the safety limit of 11 .2%. The associated outlet hatch valve control valve seats were subsequently determined to be leaking, leading to material with a higher than normal moisture content in the cooling hopper. The associated active engineered control (AEC) interlocks functioned as designed, the cooling hoppers were isolated, and the conversion process was automatically shutdown, thus no unsafe condition existed. The affected material has been transferred to favorable geometry containers per procedure. Controls were reestablished within 4 hours by proper function of the redundant dewpoint probe interlocks and automatic system shutdown. This event is reported pursuant to NRC Bulletin 91-01 (within 24 hours) due to loss of one of two independent moderation controls. Line 2 conversion remains shutdown pending investigation and implementation of corrective actions. SAFETY SIGNIFICANCE OF EVENTS: Low safety significance - actual moisture content averaged 1.2% (12,200 ppm H20) within the established uniform moderation limit of 11.2% for (112,000 ppm H20) for the cooling hopper. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Multiple failure modes required before a criticality accident could occur. CONTROLLED PARAMETER(S) (MASS. MODERATION. GEOMETRY. CONCENTRATION. ETC): Moderation ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Net U02 inside cooling hopper A was ~50 kgs (4.95 % enriched) with 1.22% H20 (12,200 ppm H20). Uniform moderation limit for cooling hopper is 11.2% (112,000 ppm H20) assuming 5% enriched U02. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Upstream moderation control on outlet hatch control system partially failed due to valve seat. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Conversion Line 2 shutdown. 2. Outlet hatch valve being replaced. 3. Investigation and implementation of additional corrective actions pending. The licensee intends to notify the local and state authorities and NRC Region 2 (David Ayres) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2001-10-16
38391 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-10-15 10:30 | 2001-10-15 16:34 | 2001-10-15 | 24 HOUR REPORT - NRC BULLETIN 91-01 The following is a faxed report of finding in building X-330: During a building walk down, contaminated items in a category II staging area were observed to be closer than the NCSA plant-048 allowed. The PSS entered an anomalous condition. The items were moved to the appropriate spacing requirements. The anomalous condition was exited. SAFETY SIGNIFICANCE OF EVENTS: The safety significance is low, The safe mass quantity is less than half of the minimum critical mass, in a spherical geometry. and with optimum moderation. The NCSE evaluated two items touching, these items were still separated, had little moderation present, and are not spherical. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): In order for a criticality to occur more spacing violations, to increase mass would have had to occur and additional moderating material would be required. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Mass and spacing are controlled. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Items involved were less than safe mass and enriched to 10% or less. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The controls were mass and spacing. Spacing was the control violated. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The items observed inside the spacing requirements were moved to required spacing requirements. The licensee notified the NRC Resident Inspector and the DOE representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-10-15
38390 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-10-15 13:07 | 2001-10-15 14:31 | 2001-10-15 | AUTOMATIC REACTOR TRIP DURING PERFORMANCE OF QUARTERLY ROD OPERABILITY SURVEILLANCE The licensee reported that during a normal quarterly rod operability surveillance an automatic reactor trip occurred, all rods fully inserted. Preliminary investigation indicates that one rod dropped during rod motion causing a negative rate trip to occur. The Emergency Feedwater system actuated, as expected on a reactor trip, and is providing feedwater to the steam generators. Excess heat is being rejected to the main condensers via the steam dumps. No safety or relief valves opened during the transient. The plant is stable in Mode 3 and an investigation into the event is underway. The licensee notified the NRC Resident Inspector and will issue a media release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-10-15
38389 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-10-15 09:59 | 2001-10-15 13:16 | 2001-10-15 | AUTOMATIC REACTOR SCRAM DUE TO MAIN STEAM ISOLATION FOR UNKNOWN CAUSE Unit 2 was operating at 100% power, steady state, when the Main Steam Isolation Valves (MSIVs) fast closed causing a Reactor Protection System (RPS) full scram, all rods fully inserted. The reactor feedwater pumps tripped on Reactor Vessel Water Level 8 due to controlling reactor pressure with Safety Relief Valves. After the feedwater trip, reactor pressure was reduced to 550-650 psig so condensate booster pumps could inject to the Reactor Pressure Vessel (RPV). At 1043 the Reactor Vessel Water Level 2 was reached on the shrink from closure of the Safety Relief Valves. This in turn caused a valid initiation and injection of the High Pressure Core Spray (HPCS) and isolation of various containment isolation valves. Reactor vessel water level and pressure has been stabilized. HPCS has been restored to standby. The plant is stable in Mode 3. The cause of the MSIV isolation is still under investigation and a normal post scram review is underway. The licensee notified the NRC Resident Inspector and will issue a media release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2001-10-15
38388 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-10-11 | 2001-10-15 13:02 | 2001-10-15 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "Thursday, 10/11/01 a Krazan and Associates employee, after working late took his portable moisture density gauge to his residence on Floyd Road in Modesto, California. The gauge was reportedly locked and chained to the rear of his pickup truck , but was not covered. The gauge chain was reportedly cut and the gauge was stolen sometime between 9:00 PM and 6:00 AM on October 12, 2001 by unknown persons. The gauge was a Troxler 3440 Serial Number 231711 containing approximately 10 millicuries of cesium 137 and 40 millicuries of americium 241. The RSO indicated he will be placing an ad in the local newspaper offering a reward for the gauge. The RSO indicated that he has counseled his employee for breaking company rules by taking the gauge to his residence which is against company policy and California regulations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-10-15
38386 | -1 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-10-14 11:45 | 2001-10-14 12:27 | 2001-11-20 | REACTOR COOLANT SYSTEM BOUNDARY LEAKAGE During an inspection, while the plant was in intermediate shutdown (2235 lbs. pressure), an unisolable leak at the "A" loop hot leg temperature element was detected (at 0530 hrs) measuring 3 drops/min. On the second entry (at 0940 hrs) when pressure was 400 lbs. no active leak was detected. The plant entered an NOUE at 1145 and TS action statement to be in cold shutdown within 30 hours was initiated. Since the plant was already in intermediate shutdown, it should be in cold shutdown within 2-3 hours. The NRC Resident Inspector was notified along with State and local agencies. * * * UPDATE ON 10/14/01@ 1621 FROM LOCASCIO TO GOULD * * * The plant went to below cold shutdown at 1620 at which time the NOUE was terminated. The NRC Resident Inspector was notified. State and local agencies will be notified. Notified Reg 2 IRC Team manager, EO(Imbro) and FEMA(Ciboch) * * * RETRACTED AT 1715 EST ON 11/20/01 BY GROVER WEEDZELL TO FANGIE JONES * * * "On 10/14/01 during containment walkdowns for Surry Unit I Refueling Outage, it was reported that a non-isolable fault existed on the 'A' loop hot leg temperature element, TE1413. A 4 hour Event Notification (#38386) was made pursuant to 10CFR50.72 (b)(2)(i), a Non-Emergency Technical Specification Required Shutdown. "Subsequent NDE inspections of the RCS pressure boundary components following unit shutdown identified that a non-isolable fault did not exist. The most probable leakage path was through mechanical pipe threads of the temperature element thermowell. "Based on the inspection results, NRC Event Notification #38386 is being retracted because a non-isolable fault did not exist in the RCS. "Repairs on TE 1413 are complete." The licensee notified the NRC Resident Inspector. The R2DO (Caudle Julian), NRR EO (Elinor Adensm) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) |  |  | 0 | 2001-10-14
38385 | -1 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2001-10-14 01:59 | 2001-10-14 12:14 | 2001-10-31 | POSSIBLE REACTOR COOLANT SYSTEM LEAKAGE During an inspection, while the plant was in shutdown mode 3, a dry white residue was discovered on a loop 2 hot leg spare thermowell plug. Being conservative they looked at this condition as a possible RCS pressure boundary leakage while in an operating mode. However, there was no active leak from the spare thermowell plug. The plant has 36 hours to be in mode 5. They will determine the type of repair work necessary to remedy the problem. The NRC Resident Inspector was notified. * * * RETRACTION 1623 10/31/2001 FROM RODRIGUEZ TAKEN BY STRANSKY * * * "On October 14, 2001, at 0914 PDT, Southern California Edison (SCE) made a 4-hour telephone notification in accordance with 10CFR50.72(b)(2)(i) for the initiation of a nuclear plant shutdown required by Technical Specification (TS). The purpose of this call is to retract that notification. "On October 14 2001, Unit 2 was being shutdown to Mode 5 to begin secondary plant equipment repairs. While in Mode 3, plant personnel discovered a white powdery substance on an RCS thermowell and considered that this could be dried boric acid and evidence of an RCS boundary leak. SCE logged entry into TS 3.4.13, action 'B' to be in Mode 3 within 6 hours and Mode 5 within 36 hours after discovery of RCS pressure boundary leakage. Even though the plant was shutdown and on its way to mode 5, because TS 3.4.13, action 'B' also required a reduction in plant mode, SCE conservatively considered this to be a 'shutdown required by the TS and made the phone report to the NRC in accordance with 10CFR50.72(b)(2)(I) "To investigate this finding, SCE: 1. Removed the thermowell threaded plug and the threads were found clean and dry with no evidence of an RCS pressure boundary leak. 2. Inspected the thermowell with a fiber-optic scope and found it clean and dry with no evidence of an RCS pressure boundary leak, 3. Inspected the thermowell-to-nozlle weld and found no indications (i.e., weld cracks or defects) present. 4. Analyzed the white powder and concluded it was not boric acid crystals. "Based on this evidence, SCE concluded that an RCS pressure boundary leak did not exist. Therefore, entry into TS 3.4.13, action 'B' was not required and a phone-report to the NRC for 'initiation of a plant shutdown required by the TS' was not required and is now being retracted. "At the time of the initial report Unit 2 was shutdown in mode 3, and Unit 3 was operating at about 100 percent power. The NRC Resident Inspectors will be notified of this occurrence and will be provided with a copy of this report." HOO Notified R4DO (Spitzberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-10-14
38384 | 0 | PARK VIEW HOSPITAL |  |  |  |  | 2001-10-11 16:45 | 2001-10-12 17:37 | 2001-10-12 | PARK VIEW HOSPITAL REPORTED A MEDICAL MISADMINISTRATION During an intravascular bracytherapy treatment with strontium-90 to a heart artery, a possible medical misadministration occurred at the completion of the treatment. At the conclusion of this treatment, not all the sources returned to the Novoste applicator. The sources were seen to have left the vessel and heart within the appropriate time(5 sec), but they did not all return to the device. Another attempt to remove the sources was made, but was unsuccessful, so the entire treatment catheter was removed(within 18 secs) from the patient as per their emergency procedures. The physician and manufacturer of the device did not consider this as a medical misadministration, however an NRC inspector felt that it was for that additional 18 secs to remove the treatment catheter. This incident occurred 8/27/01. It was decided not to notify the patient because of the patient's condition. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0 | 2001-10-12
38383 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2001-10-12 12:30 | 2001-10-12 16:32 | 2001-10-12 | DISCOVERY OF A THROUGH-WALL LEAK AROUND 8 THERMOCOUPLE NOZZLES (REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAK) On October 11 and 12, 2001, following shutdown for a scheduled refueling outage, three Mile Island Unit 1 (TMI-1) performed a visual inspection of the Reactor Vessel (RV) Thermocouple (TC) nozzles per NRC Bulletin 2001-01. The inspection revealed evidence of boric acid buildup around all eight (8) TCs nozzles. At approximately 1230 on October 12, 2001, Engineering evaluation of the visual inspection results confirmed that the boron deposits around the eight TCs indicate a Reactor Coolant System (RCS) pressure boundary leak. This condition is consistent with industry experience with Primary Water Stress Corrosion Cracking (PWSCC) in reactor vessel head nozzles that have been evaluated as part of the NRC Generic Letter 97-01 and NRC Bulletin 2001-01. TMI-1 plans to perform repairs during the current refueling outage. Since the condition resulted in leakage through the RCS pressure boundary, it is being reported as a non-emergency [8-hour] report in accordance with 10 CFR 50.72(b)(3)(ii)(A) and 50.73(a)(2)(ii)(A). Results from the CRDM nozzle inspection have not yet been submitted. The NRC resident inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-12
38382 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-10-11 14:44 | 2001-10-12 15:32 | 2001-10-12 | 24 HOUR 91-01 BULLETIN RESPONSE Four waste drums were discovered to be incorrectly characterized based on incorrect laboratory analysis results. The incorrect analysis resulted from failure to follow a step in the procedure and violated the single point failure prevention arguments for sample characterization in NCSA 1493-33. The purpose of preventing a single point failure is to maintain double contingency for the case in which independent sample results are used to characterize and classify waste drums as "NCS Spacing Exempt." The samples were later re-analyzed for both assay and U-235 content. The re-analysis results demonstrated that three of the four drums in question are in fact non-fissile and have been handled conservatively. The remaining drum is greater than 1%, but the U-235 mass is less than the limit for spacing exemption. NUCLEAR CRITICALITY SAFETY CONTROLS INVOLVED AND THEIR IMPACT ON DOUBLE CONTINGENCY Double contingency is maintained by implementing controls to ensure the samples are analyzed correctly, without common mode failures. The first leg of double contingency is based on correctly analyzing the sample for U-235 loading. Since the procedure was violated the analysis result should not have been relied upon for NCS purposes. The control was violated. Since there are two controls on one parameter, double contingency was not maintained. The second leg of double contingency is based on independently analyzing the sample correctly for U-235 loading. Since the procedure was violated the independent analysis result should not have been relied upon for NCS purposes. The control was violated. Since there are two controls on one parameter, double contingency was not maintained. Since double contingency is based on two controls on one parameter, double contingency was not maintained. Potential Critical Pathways: In order for a criticality to be possible, the mass in multiple waste drums would each have to be greater than the safe mass determined for that container size and these waste drums would have to be stored together or re-containerized into unfavorable geometry drums. Safety Significance: Double contingency for characterizing and storing "NCS Spacing Exempt" waste are based on determination of U-235 mass in the drum. Both of these controls were lost. However, based on re-analysis results the drums are in fact non-fissile or spacing exempt. EXCLUSION ZONE AND POSTiNG: Control the area around the drum and post as follows according to CP2-EG-N51031; Do not move fissile/potentially fissile material into or within this area without NCS and PSS approval. NCS-INC-01 -025 CORRECTIVE ACTIONS: 1. Re-characterize the drum according to CP4-EW-WM2100 based upon the re-analysis results. 2. Remove the ropes and postings The NRC Resident Inspector was informed and the DOE Representative will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-10-12
38381 | 0 | WASHINGTON HOSPITAL CENTER |  |  |  |  | 2001-10-12 12:30 | 2001-10-12 14:45 | 2001-10-12 | PACKAGE CONTAINING PHOSPHOROUS-32 WITH EXTERNAL RAD LEVELS GREATER THAN LIMITS The Washington Hospital Center received a package from Isotex Diagnostics Incorporated(Texas lic # L02999) of Friendswood, Texas that measured on surface contact 48 Rads/hr using an ion chamber with the beta shield off. This was over a small area of the package. At one meter with the beta shield off it measured 77 millirads/hr. Both the shipper and the carrier(FedEx) have been notified. The package contained 92.8 millicuries of phosphorous-32 with packing label yellow-2 and transport index 0.6. There was no contamination detected. They are holding the package for inspection by the shipper. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 20.1906(d)(2) |  |  |  | 0 | 2001-10-12
38380 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2001-10-11 14:20 | 2001-10-11 17:56 | 2001-10-26 | CONDITION OF LICENSE REPORT DUE TO UNAVAILABLE EMERGENCY LIGHTING On October 11, 2001, following a fire protection program self assessment, it was determined that emergency lighting was unavailable in two required locations. Actions in these areas are required steps of procedure 20.000.18 "Control of Plant from Dedicated Shutdown Panel." The inability to perform steps in 20.000.18 constitutes a reportable condition under Fermi 2 License Condition 2.F as a violation of "Modifications for Fire Protection" as described in License Condition 2.C(9). Short term corrective action is to revise the procedure steps to obtain portable lighting prior to exiting the plant. Long term corrective actions are being evaluated. The NRC Resident Inspector was notified. * * * RETRACTION ON 10/26/01 AT 1315 ET REPORTED BY KEVIN DAHM TAKEN BY MACKINNON * * * Upon further evaluation, it has been determined that License Condition 2.C (9) was not violated. The steps in question in the CTG 11-1 Control Building and in the EDG-11 Switchgear Room can be completed successfully with the current lighting configuration; and therefore, there is no adverse affect on the ability to achieve and maintain safe shutdown. License Condition 2.C (9) is thus met, and this condition is not reportable under License Condition 2.F. The original notification, Event Number 38380, is retracted. R3DO (Brent Clayton) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2001-10-11
38378 | 0 | US ARMY |  |  |  |  | 2001-09-13 | 2001-10-11 14:49 | 2001-10-11 | WIPE TEST LIMITS EXCEEDED LIMITS FOR CHEMICAL AGENT DETECTORS Wipe test on a Ni -63 chemical agent detector measured 17,931 DPM(equivalent to .007 microcuries). This was way above their action level guide lines of 1,000 DPM. They are in the process of disposing of the device. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2001-10-11
38377 | 0 | US ARMY |  |  |  |  | 2001-10-10 18:45 | 2001-10-11 14:49 | 2001-10-11 | LOST CHEMICAL AGENT DETECTOR (CAD) The US Army reported that during inventory check in Vilseck, Germany at the 529th Ordinance, one CAD containing 15 millicuries Ni-63 was not accountable. A search was conducted with no success in finding it, so it was presumed to be lost. This discovery was made on 7/15/01. They are still investigating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-10-11
38376 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-10-10 | 2001-10-10 17:29 | 2001-10-10 | AGREEMENT STATE REPORT REGARDING DISCOVERY OF A LAW ENGINEERING AND ENVIRONMENTAL SERVICES GAUGE ON A RESIDENTIAL STREET BY AN EMPLOYEE OF ANOTHER COMPANY The following text is a portion of a facsimile received from the Texas Department of Health, Bureau of Radiation Control: "Texas Incident No.: I-7810" "License No.: L02453" "Licensee: Law Engineering and Environmental Services, Houston, Texas (Fort Worth Subsite)" "Event date and time: 10/10/01 a.m." "Event location: Dallas, Texas (exact location unknown at this time - gauge was transported to 10722 North Stemmons Freeway, Dallas, Texas 75220[)]" "Event type: Found Nuclear Density Gauge, Troxler 3411 B, Serial #11251" "Notifications: Notified Troxler Electronic Labs, TDH Public Health Region 3 to pickup gauge and have leak tested." "Event description: Gauge found in the middle of a residential street by an employee of Giles Engineering, Texas License L04919-001. Gauge was found to be un-locked - both case and control rod. The gauge was reported to be in the 'On' position. No shipping papers were found in the case. No warning stickers were reported to be on the exterior of the case. Troxler Labs reports that the gauge was last seen by them over 2-years ago and was then owned by Austin Testing Engineers - no evidence of Licensure through this Agency. Gauge was tracked to Law Engineering in Fort Worth. TDH is holding the gauge. Will have leak test performed. Licensee was unaware that the gauge was missing and could not immediately find if the gauge was assigned on a job for 10/10/01." "Transport vehicle description: None available at this time." "Media attention: None" (Contact the NRC operations officer for an agreement state point of contact.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-10-16
38375 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2001-10-10 12:30 | 2001-10-10 15:38 | 2001-11-20 | HPCI INOPERABLE "On 10/10/01 at 12:30, while performing surveillance 24.202.01 'HPCI Pump Time Response and Operability Test at 1025 psi', HPCI pump flow reached 5000 gpm in 35 seconds (<29 seconds is acceptance criteria). HPCI was declared INOPERABLE due to the surveillance failure. Plant personnel are evaluating trend data to determine the cause of the failure. "All other ECCS systems and RCIC are OPERABLE. This is being reported under 10CFR50.72(b)(3)(v)(D)." The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTED AT 1257 EST ON 11/20/01 BY JERRY FLINT TO ROBERT STRANSKY * * * "Upon further evaluation, it has been determined that the HPCI failure to reach rated flow is not reportable. An extensive investigation was performed to determine the cause of the failure of HPCI to reach rated flow in the required time. The failure was attributed to two root causes: System configuration changes made since 1994 reduced available margin to the 29 second acceptance criteria and a decrease in opening stroke position of the HPCI test line throttle valve resulted in a change to the HPCI system test characteristic. "Adjustments to the HPCI test line throttle valve opening were performed. A subsequent HPCI surveillance run was performed on 10/18/2001. Rated flow was reached within the surveillance acceptance criteria. No changes were made to the HPCI system acceptance criteria or to HPCI components that would impact actual injection to the reactor pressure vessel. The changes to the testing method remain conservative with respect to an actual vessel injection. "Therefore, HPCI remained fully capable of reaching rated flow in the required time during the 10/10/2001 surveillance run; and therefore, HPCI was Operable. and this condition is not reportable under 10CFR50.72(b)(3)(v)(d). The original notification. Event Number 38375, is retracted." The licensee notified the NRC Resident Inspector. The R3DO (Christine Lipa) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-10-10
38373 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2001-10-10 07:45 | 2001-10-10 11:23 | 2001-10-10 | UNIT 2 COMMENCED A TECH SPEC REQUIRED SHUTDOWN BASED ON ASSUMED CEA DEGRADATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 10, 2001, at approximately 07:45 MST, Palo Verde Nuclear Generating Station (PVNGS) Unit 2 commenced a reactor shutdown required by Technical Specification 3.0.3. "CEA degradation was observed during refueling of PVNGS Unit 3 and is assumed to be transportable to Unit 2. As discussed in the Technical Specification 3.1.5 Bases, mechanical failures may cause a CEA to become inoperable. There were no reactivity anomalies in Unit 2 (or Unit 3) indicating CEA degradation prior to this discovery. The condition is not transportable to PVNGS Unit 1 CEAs because they were replaced during its last refueling outage. "Preliminary investigation indicates the cause to be aging. "Limiting Condition for Operability (LCO) 3.1 .5 requires 'All full length CEAs shall be OPERABLE..' No associated action in Technical Specification 3.1.5 applies to the CEA degradation, therefore Unit 2 entered LCO 3.0.3. "No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified." | 0 | 75 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-10-10
38372 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-10-08 | 2001-10-10 11:19 | 2001-10-25 | AGREEMENT STATE REPORT "Licensee reported that a Troxler 3440 portable gauge containing 10 mCi of cesium-137 and 50 mCi of americium-241:beryllium, in sealed sources, was stolen from one of their technician's pick-up while being kept overnight at the technician's home in Hemet. The gauge was in its transport case, locked down in the bed of the vehicle with a 'shell.' "The gauge was stolen sometime after being parked at the technician' s home on the evening of 10-8-01. "The stolen gauge was a Troxler 3440, S/N 14409." * * * * UPDATE ON 10/25/01 AT 1520 ET BY ROBERT GREGER TAKEN BY MACKINNON * * * * The gauge was recovered on 10/23/01 after a reward was offered for the recovery of the gauge. No damage to the gauge. R4DO (Bill Johnson) and NMSS (Brian Smith) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-10-10
38371 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-10-10 03:32 | 2001-10-10 08:44 | 2001-10-10 | RCS PRESSURE BOUNDARY LEAKAGE IDENTIFIED DURING CONTAINMENT WALK DOWN "During a Primary Containment walk down at the beginning of the Hope Creek 10th Refueling Outage, inspection crews identified a cracked weld on the 'A' Reactor Recirculation Loop elbow tap instrument piping, which is part of the Reactor Coolant Pressure Boundary. The cracked weld is located where a 1" tap connects to the 28" recirculation loop piping, and constitutes a part of the Reactor Coolant Pressure Boundary. The unit was in Hot Shutdown Operational Condition 3 at the time of discovery. "Technical Specification LCO 3.4.3.2.a has been entered due to leakage from the Reactor Coolant Pressure Boundary, which requires the unit be in Cold Shutdown by 03:32am on October 11, 2001. Cooldown to Operational Condition 4 is in progress. "PSEG Nuclear is developing plans to repair the leak." The licensee described the leak as a fine spray which is much less than the 10gpm averaged over a 10 minute period required to declare an Unusual Event (ECG 2.1.1a, 2.1.1b). The licensee will inform the Lower Alloways Creek Township and the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-10
38370 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-10-10 02:53 | 2001-10-10 08:44 | 2001-10-10 | AUTOMATIC RPS ACTUATION ON LOW REACTOR VESSEL WATER LEVEL FOLLOWING UNIT SHUTDOWN "Following the shutdown of Hope Creek Generating Station at the beginning of the 10th Refueling Outage, a subsequent low reactor water level condition occurred which resulted in actuation of the Reactor Protection System (RPS). The low level occurred when reactor depressurization was terminated. The unit was in Hot Shutdown at the time of the RPS actuation with all control rods fully inserted. "Cooldown to Operational Condition 4 is in progress." The licensee will inform the Lower Alloways Creek Township and the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-10-10
38369 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2001-10-09 18:20 | 2001-10-09 21:27 | 2001-10-09 | TRANSPORT OF A RADIOACTIVELY CONTAMINATED PERSON TO AN OFFSITE MEDICAL FACILITY FOR TREATMENT The following text is a portion of a facsimile received from the licensee: "On October 09, 2001, a contract worker injured his leg while working in the Reactor Building at Crystal River Unit 3. The injury required the worker to be transported offsite to a local medical facility. A Health Physics technician accompanied the individual to the medical facility since he was potentially contaminated. The subsequent survey found radioactive contamination on the individual's clothing and on the backboard used for transport. The Health Physics technician took custody of the contaminated material and returned it to Crystal River Unit 3." "This is reportable as an 8-hour report under 10 CFR 50.72(b)(3)(xii), 'any event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment.' " The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2001-10-09
38368 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-10-09 13:15 | 2001-10-09 15:25 | 2001-10-09 | OFFSITE NOTIFICATION DUE TO GASOLINE SPILL OUTSIDE THE PROTECTED AREA The licensee was filling a company minivan with gasoline when the automatic shut-off valve stuck and an uncontained spill occurred of greater than 5 gallons and less than 50 gallons. This occurred outside of the protected area. The licensee is conducting cleaning efforts in accordance with proper procedures. The licensee notified the state and local authorities concerning the spill, making this notification necessary. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-10-09
38367 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-10-09 09:00 | 2001-10-09 14:42 | 2001-10-09 | DISCOVERY THAT ANTICIPATED FLOW MAY RESULT IN ENGINEERED SAFETY FEATURE EQUIPMENT BEING INCAPABLE OF PERFORMING DESIGN FUNCTIONS The following text is a portion of a facsimile received from the licensee: "Prior to entering the scheduled refueling outage and while the plant was removed from service on 09/23/01, operating flow and temperature data for the Turbine Building Service Water (SW) system header was obtained. The Turbine Building SW header is a branch connection off the Engineered Safeguards (ESF) SW header, which is manually selected to either 'A' or 'B' train ESF SW header. Preliminary reviews of the data indicate that anticipated flows under accident conditions, using existing analysis limits, result in ESF equipment being incapable of performing design functions. The current accident analyses for the SW ESF equipment only assumes a Turbine Building demand on the selected ESF header of 2000 gallons per minute (gpm). The gathered data, when projected to accident temperature limits for design basis cooling requirements, shows the Turbine Building header flow to be significantly greater than 2000 gpm. The data indicates that a lake water temperature of 55 degrees F would be the maximum that would support the previously assumed ESF operation Turbine Building header flow at 2000 gpm. Current accident analysis assumes that ESF equipment will remain operable up to 80 degrees F lake water while supplying the Turbine Building header." "Kewaunee will continue to review available and previously assumed analytical data to determine what plant operational limitations may apply and or what changes may be necessary to support a return to power operation. The current schedule for the refueling outage includes a return to power operation on December 5, 2001." The licensee stated that the unit is currently defueled as part of the ongoing refueling outage. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-09
38366 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2001-10-09 11:30 | 2001-10-09 12:22 | 2001-10-10 | LANCASTER COUNTY EMERGENCY SIRENS WERE FOUND INOPERABLE "At 11:30 AM on 10/9/01, TMI determined that the apparent inoperability of emergency sirens in Lancaster County, Pennsylvania for approximately 3 days met the criteria set forth in NUREG 1022, Rev. 2 for a major loss of emergency offsite communications capability and that an immediate 8 hour notification in accordance with 10 CFR 50.72(b)(3)(xiii) was required. "At approximately 8:55 am on Tuesday, October 9, 2001 the emergency sirens in Lancaster County were inadvertently activated during routine maintenance by Capitol Area Communications, the siren vendor. During the weekly evaluation of system electronics on Tuesday, October 9, 2001, Capitol Area Communications had discovered an anomaly with the system communications with Lancaster County. Capitol Area Communications called Lancaster County and it was found that apparently the transmitter for Lancaster County had been incorrectly left turned off following recent maintenance performed on Saturday, October 6, 2001 that occurred in the vicinity of the transmitter. "The transmitter was turned back on at approximately 8:55 am on Tuesday, October 9, 2001. When the transmitter was turned on, a signal that had been sent on Saturday, October 6, 2001 for the monthly Saturday test of the sirens that had been received but not acted upon, was acted upon by the transmitter which then activated the sirens. The sirens were silenced upon recognition of the inadvertent actuation. Lancaster County is notifying local media of the cause of the inadvertent siren actuation. "Subsequent discussions between Exelon Emergency Management personnel and the siren vendor determined that the sirens for Lancaster County had apparently been inoperable from sometime on Saturday, October 6 until today, Tuesday, October 9. "The sirens in Lancaster County were reactivated when the transmitter [was turned] back on. "The Lancaster County 911 dispatcher number 41 called the TMI Control Room at approximately 9:00 AM. The Control notified a duty public information representative of the siren malfunction. The duty Public Information Representative spoke with Lancaster County Emergency Management at 9:13 am who confirmed the information received from the 911 dispatcher. Subsequently, at 9:15 am Exelon emergency management reconfirmed the information received. "The site Sr. Resident Inspector has been informed of the event and the 8 hour report. TMI Communications contacted the Lancaster County Commissioners and PEMA to inform them of the event." * * * UPDATE 1423 10/10/2001 FROM SCHORK TAKEN BY STRANSKY * * * "This is a revision of the initial 8 hour notification made by TMI-1 per Event Notification 38366 on October 9, 2001 at 1222 hours. The revised notification is being submitted to document that the sirens in question were out of service for approximately 4 days instead of the initial report of 3 days and that a contributing cause to the event may be the software that is used in performing the test. "Additional discussions between TMI Emergency Preparedness, Exelon Emergency Preparedness, Lancaster County Emergency Management and Capitol Area Communications that took place on Wednesday, October 10, 2001 determined that the siren transmitter was out of service from Friday, October 5 to Tuesday, October 9. In addition, a functional test of the computer software used to perform the weekly test in Lancaster County found that the software did not detect a failure of the sirens to actuate when the transmitter is de-energized. The software does detect siren failures when the transmitter is energized. Exelon Emergency Preparedness is contacting the software vendor to obtain additional information. The software in question was provided by AmerGen to the 5 risk counties for Three Mile Island Nuclear Power Station." The NRC resident inspector has been informed of this update by the licensee. Notified R1 IRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-10-09
38365 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2001-10-08 16:30 | 2001-10-08 17:48 | 2001-10-08 | DISCOVERY OF A THROUGH-WALL LEAK AROUND ONE CONTROL ROD DRIVE MECHANISM NOZZLE (REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAK) The following text is a portion of a facsimile received from the licensee: "On October 1, 2001, following shutdown for a scheduled refueling outage, Crystal River Unit 3 (CR-3) performed a visual inspection of the Reactor Vessel (RV) Control Rod Drive Mechanism (CRDM) nozzles per NRC Bulletin 2001-01. The inspection revealed evidence of boric acid buildup around one CRDM nozzle (#32). No other CRDM nozzle showed similar boron buildup. After the RV head was removed and placed on the storage stand, additional inspections were performed. At approximately 1610 on October 8, 2001, Ultrasonic Test (UT) revealed a through-wall indication. This confirms that the boron deposits around CRDM #32 indicate a Reactor Coolant System (RCS) pressure boundary leak. This condition is consistent with industry experience with Primary Water Stress Corrosion Cracking (PWSCC) in similar components that have been evaluated as part of the NRC Generic Letter 97-01 and NRC Bulletin 2001-01. Additional nozzles are being examined by UT in accordance with CR-3's response to NRC Bulletin 2001-01. This condition did not pose a significant safety risk during plant operation. CR-3 plans to perform repairs during the current refueling outage. Since the condition resulted in leakage through the RCS pressure boundary, it is being reported as a non-emergency [8-hour] report in accordance with 10 CFR 50.72(b)(3)(ii)(A) and 50.73(A)(2)(II)." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-08
38364 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-10-08 01:10 | 2001-10-08 08:33 | 2001-10-08 | SECONDARY CONTAINMENT DECLARED INOPERABLE DURING SURVEILLANCE TESTING "During performance of the secondary containment drawdown test, reactor building vacuum fluctuated between 0.49 and 0.50 inches wg. The acceptance criterion for the test is greater than or equal to 0.50 inches wg vacuum. Secondary Containment was therefore declared inoperable at 01:10. Surveillance Requirement (SR) 4.6.5.1.c requires verification that the FRVS will draw down the secondary containment to greater than or equal to 0.25 inches wg vacuum. The test acceptance criterion ensures that vacuum throughout the reactor building meets the SR acceptance criterion. Hope Creek entered Technical Specification action statement 3.6.5.1 .a which requires SECONDARY CONTAINMENT INTEGRITY to be restored within 4 hours or the plant to be in HOT SHUTDOWN within the next 12 hours. "The FRVS reactor building pressure controller setpoint was found to be incorrectly set. The controller was returned to the required setpoint and reperformance of the test is in progress. "PSEG Nuclear is evaluating the test acceptance criterion and the instrumentation used for the test." The licensee will inform the Lower Alloways Creek Township and the NRC resident inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2001-10-08
38363 | 0 | STERIGENICS |  |  |  |  | 2001-10-06 10:15 | 2001-10-07 17:38 | 2001-10-07 | COMMERCIAL IRRADIATOR FACILITY REPORT REGARDING A SOURCE HANG UP Sterigenics is a panoramic, wet-source storage, commercial, irradiator facility. At approximately 2215 EDT on 10/07/01, a 2.6-megacurie cobalt-60 source got stuck in the unshielded position. The licensee attempted to lift the source rack and had to release the ear out of the cylinder in the cell to free it. The source rack was successfully returned it to its shielded position within approximately 1 hour. There were no personnel radiation exposures or injuries as a result of this event, and there was no source leakage. The licensee is still investigating the cause of this event and has ceased operations until engineering personnel can complete their evaluation. (Call the NRC operations officer for a site contact telephone number and street address.) (Refer to event #38342 for a similar event at Sterigenics on 10/07/01.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSHIELD STUCK SOURCE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 36.83(a)(1) |  |  |  | 0 | 2001-10-07
38362 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-10-07 09:50 | 2001-10-07 13:02 | 2001-10-10 | UNEXPECTED REACTOR TRIP DURING PLANT STARTUP OPERATIONS ". . . . This event occurred at 0950 hours this morning (10-7-01). Currently the Unit is in Mode 3 with all systems normal. At the time of the trip the unit was at approximately 8 % power (by RCS AT indication, about 6 to 7 % on Power Range Nuclear Instrumentation) in power ascension and was just preparing to roll the main turbine. "RCS Tavg was noted to decrease below the normal 547 °F no-load post-trip value to about 535 °F by the Reactor Operator monitoring the temperature. At the time of the trip one main feedwater pump was supplying the Steam Generators (SG), with low-flow feedwater pre-heating in service. Main feedwater isolated on the trip with the SGs being supplied post trip by the motor driven Auxiliary Feedwater (AFW) Pumps. The RCS cooldown was attributed to the #4 SG AFW flow control valve not closing as expected on high flow thus allowing too much flow to #4 SG, as well as steam that was still being supplied to low flow feedwater preheating. Operator actions taken in response to the cooldown were to close the main steam stop valves, and review AFW valve positions so as to limit steam flow from, and feed flow to, the SGs. These actions were completed by 0959 hours, and were sufficient to maintain temperature control. RCS temperature shortly recovered to 547 °F at about 1032 hours, 10-7-01. No other significant abnormalities were noted, pressurizer pressure decreased in response to the temperature transient, and the subsequent RCS shrink caused RCS letdown to isolate on low pressurizer level. The plant is presently stable in Mode 3. No other RPS or SI setpoints were exceeded due to the trip and subsequent temperature transient. All other systems and equipment functioned normally. "The initiating RPS signal was a high Power Range Nuclear Instrument Rate Trip on 2 out of 4 channels. Cause of this rate trip is not definitively known at this time, rapid event teams to investigate and evaluate the trip have been initiated. Suspected cause is a Rod Control System problem." The licensee notified the NRC Resident Inspector. * * * UPDATE 0353EDT ON 10/10/01 FROM DALE TURINETTI TO S. SANDIN * * * The following information was received as an update to this report: "The cause of the Unit 2 reactor trip was a negative rate trip as a result of a loss of Rod Control Motor Generator set voltage. The loss of voltage was attributed to a failed open resistor on the North motor generator set which caused a loss of voltage regulation. It is believed this loss of voltage caused the north motor generator set to act as a load; and the south motor generator set could not maintain the output voltage. The reduction in voltage caused a collapse of field and the subsequent release of control rods and resultant negative rate trip. "The motor generator set resistors have been replaced and associated relays have been tested to ensure proper operation of the motor generator sets. Plant power ascension is in progress with the unit in mode 1 and at 25%." The licensee informed the NRC resident inspector. Notified R3DO(Parker). | 0 | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-10-07
38361 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-10-07 04:59 | 2001-10-07 06:11 | 2001-10-07 | EMERGENCY OPERATIONS CENTER WITHOUT ELECTRICAL POWER FOR SCHEDULED MAINTENANCE The licensee reported that the Emergency Operations Facility (EOF) will be without power for approximately eight hours so that preplanned maintenance can be performed. The NRC resident inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-10-07
38360 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-10-07 | 2001-10-07 03:13 | 2001-10-07 | MANUAL REACTOR TRIP DURING TESTING "On 10/06/01, testing personnel and the Control Room crew were performing 1BVT-1 .1.7, 'Rod Position Indication System Calibration Verification' and 1BVT-1.1.1, 'Rod Drop Testing' in preparation for reactor startup after Unit 1's 14th Refueling Outage. At 1959 hours, the Control Room operators observed indications of 2 dropped control rods (rod position indication reading zero steps and rod bottom lights on), and entered 1AOP-1.1.8 (Abnormal Operating Procedure - Rod Inoperability). The Reactor Operator opened the reactor trip breakers in accordance with the Abnormal Operating Procedure and the Reactivity Management Plan that included reactivity limits and recommended contingency actions. It was subsequently discovered that the indications were caused by the test crew repositioning knife switches to place the rod drop computer in service. The action and resulting indications were not communicated to the Control Room crew. This event is being reported under 10CFR 50.72(b)(3)(iv)(A), as a Specified System Actuation (RPS), because a valid manual RPS signal (opening the reactor trip breakers from the Control Room) was initiated which was not part of the pre-planned testing in progress. All equipment functioned as expected, and no additional failures or equipment challenges occurred as a result of this event. There were no radiological releases associated with this event." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-10-07
38359 | 0 | RESEARCH MEDICAL CENTER |  |  |  |  | 2001-10-05 10:30 | 2001-10-05 17:34 | 2001-10-05 | MEDICAL MISADMINISTRATION INVOLVING A MISSING IRIDIUM-192 SEED At 0830 CDT on 10/05/01, the licensee discovered that 1 of 71 iridium-192 seeds was missing following a brachytherapy treatment involving both cesium-137 tubes and iridium-192 ribbons. The licensee's investigation revealed that the missing iridium-192 seed remained inside the patient. The licensee determined that this event was reportable at 1030 CDT on 10/05/01. The patient was in surgery at the time of this event notification. As a result, the total dose the patient has not yet been determined. The missing iridium-192 seed had an activity of 0.89 millicuries. ***** UPDATE FROM STEVEN SLACK TO LEIGH TROCINE AT 1819 EDT ON 10/05/01 ***** The missing iridium-129 seed was successfully recovered at 1645 CDT on 10/05/01. The NRC operations officer notified the R3DO (David Hills) and NMSS EO (Patricia Holahan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.33 |  |  |  | 0 | 2001-10-05
38358 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-10-04 | 2001-10-05 17:31 | 2001-10-05 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following is the faxed report: City and state: Spokane, WA License number: WN-l093-1 Type of license: Portable Gauge Date of event: October 4, 2001 Location of Event: University Place, WA ABSTRACT: A Troxler portable gauge was stolen from a pick-up parked at a residence. An authorized user was returning home late from a job site and knowing he had to go back early the next morning requested permission from the licensee's Radiation Safety Officer to take the gauge home and secure it there. The authorized user's home was closer than the licensee's storage location. Permission was given and the gauge, a Troxler model 3440, serial number 31199, was locked and chained in the bed of the pick-up. The pick-up, which did not have a canopy, was parked in the residence's drive way on the evening of October 4. The authorized user discovered early the next morning that the chain had been cut and the gauge stolen. Neighbors reported hearing noises about 11:45 PM that night. The theft was reported to the local police, the licensee's corporate RSO and to the Department. A reward is being offered for the gauge which contains 10 millicuries of cesium 137 and 50 millicuries of americium 241/beryllium. What is the notification or reporting criteria involved? WAC 246-221-240 (Reports of stolen, lost or missing radiation sources.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2001-10-05
38357 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-10-05 11:15 | 2001-10-05 17:10 | 2001-10-05 | 24-HOUR REPORT IN ACCORDANCE WITH OPERATING LICENSE DUE TO POTENTIAL MAXIMUM POWER LEVEL VIOLATION The following text is a portion of a facsimile received from the licensee. "This report is being made in accordance with Limerick Generating Station Unit 1 Operating License Condition 2.F as a potential violation of License Condition 2.C(1), Maximum Power Level." "GE Report titled, 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations,' September 2001, documents a non-conservative assumption for the moisture carryover fraction used in the calculation of core thermal power. The assumed carryover fraction of 0.1% was discovered to be potentially closer to zero and therefore non-conservative in later model GE BWRs." "A review of Limerick Unit 1 moisture carryover test data performed in September of 1999 found a moisture carryover value of 0.1%. However, it is believed that the results of the test may be more in line with the Limerick Unit 2 data of 0.0277%. This results in an estimated bias of approximately 2.8 MWth Based on this potential non-conservatism on Unit 1, an input parameter of the Process Computer has been changed to eliminate this bias." 'Exelon staff is continuing to evaluate the effect of the moisture carryover term in the heat balance calculation." The licensee plans to notify the NRC resident inspector. (Refer to event numbers 38330, 38337, 38340, 38344, 38445, 38347, 38349, and 38356 for similar events at Fermi, Perry, Hope Creek, Grand Gulf, Columbia Generating Station, Limerick 2, River Bend, and Clinton.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2001-10-05
38356 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2001-10-05 | 2001-10-05 17:11 | 2001-10-05 | 24-HOUR REPORT IN ACCORDANCE WITH OPERATING LICENSE DUE TO POTENTIAL MAXIMUM POWER LEVEL VIOLATION "This report is being made in accordance with Clinton Power Station Unit #1 Operating License Condition #2.G as a potential violation of License Condition #2.C(1), Maximum Power Level. "GE Report titled 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations', September 2001, documents a non-conservative assumption for the moisture carryover fraction used in the calculation of core thermal power. The assumed carryover fraction of 0.1 % was discovered to be potentially closer to zero and therefore non-conservative in later model GE BWRs. "A review of Clinton Power Station Unit #1 moisture carryover test data performed on May 21 2001 found a moisture carryover value of 0.0046% and on October 4, 2001 found a moisture carryover value of 0.0020% inducing an estimated bias of approximately 2.4 MWth. Based on this potential non-conservatism on Unit #1 indicated Maximum Power Level shift average is being administratively controlled 4 MWth below the licensed power level of 2894 MWth. "Exelon staff is continuing to evaluate the effect of the moisture carryover term in the heat balance calculation. The NRC resident has been notified." (Refer to event numbers 38330, 38337, 38340, 38344, 38445, 38347, 38349, and 38357 for similar events at Fermi, Perry, Hope Creek, Grand Gulf, Columbia Generating Station, Limerick 2, River Bend, and Limerick 1.) | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2001-10-05
38355 | 0 | AVERA McKENNAN HOSPITAL |  |  |  |  | 2001-10-04 | 2001-10-05 16:50 | 2001-10-05 | SPILL OF TECHNETIUM IN PUBLIC AREA The mobile lab of Avera McKennan Hospital was on site at the Freeman Hospital, Freeman, S.D. when a cracked vial containing 250 mCi of Technetium leaked on to the floor of the kitchen. The area was secured and the only exposure/contamination was the shoes of the medical technician transporting the vial. A containment area was established and gross cleanup was completed on 10/4/01. The area was checked again this morning and further evaluation will be taken tomorrow, 10/6/01, after 8:00 PM, which will be greater than ten half-lives. NRC Region 4 (Bob Brown) has been notified by the hospital chief technician. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 4 | SD | HOS |  | 30.50(b)(1) |  |  |  | 0 | 2001-10-05
38354 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-10-05 14:00 | 2001-10-05 15:35 | 2001-10-05 | POTENTIAL PERSONNEL OVEREXPOSURE The licensee discovered a positive indication on a routine bioassay sample for uranium uptake in an operator. The first backup sample confirmed the potential for an uptake. All other samples from other individuals are negative. Initial calculation indicates a potential dose that could exceed 25 rem total dose equivalent. The incident is believed to occurred in building 302 area E. An investigation is underway to determine exactly what occurred. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 20.2202(a)(1) |  |  |  | 1 | 2001-10-05
38353 | 0 | ABB INC. |  |  |  |  | 2001-10-05 | 2001-10-05 14:26 | 2001-10-05 | 10 CFR PART 21 REPORT CONCERNING A CLASS 1E RELAY The following is the faxed report: Subject: Initial Notification of Potential Defect per 10 CFR Part 21 Type CVE/CVE-1 Relays Provided By: ABB Inc., Substation Automation & Protection Division This letter is the initial notification of a deviation concerning our Class 1E relay type CVE/CVE-1. The deviation concerns the difference between the original zero period acceleration value and the recent zero period acceleration value as reported to us by an independent dedicating entity. Details will be provided in our written notification forthcoming within the next thirty days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2001-10-05
38352 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-10-05 00:26 | 2001-10-05 04:30 | 2001-12-05 | UNIT 2 ENTERED TECH SPEC 3.0.3 DUE TO TWO TRAINS OF SERVICE WATER DECLARED INOPERABLE "At 0026 hrs on October 5, 2001, Beaver Valley Power Station Unit 2 experienced a trip of the 'A' Train Service Water (SWS) Pump. 2SWS-P21 C was operating on the 'A' SWS header when the pump tripped on Motor Ground Over Current. Both A and B Train Emergency Service Water Pumps (SWE) auto started as designed and Service Water header pressure returned to normal values. Due to a piping class break, safety/non-safety, between the SWS and SWE systems, the unit entered Technical Specification 3.0.3 due to two trains of Service Water being Inoperable. The unit entered and completed the Abnormal Operating Procedure for Loss of Service Water, and the Bravo Train of Service Water was restored Operable when 2SWE-P21 B was secured and isolated from the 'B' SWS header. 25W5-P21 B continued to operate normally during this event. Technical Specification 3.0.3 was exited at 0037 hrs. The plant is currently stable and operating at 100% power. Technical Specification 3.7.4.1 for Service Water (72-hour action) is applicable, as the only operating pump on the 'A' SWS header is 2SWE-P21A. The Alpha Service Water Pump, 2SWS-P21 A is unavailable due to Intake Structure Bay cleaning. Currently efforts are under way to recover the Intake Bay and restore 2SWS-P21A Operable. It is expected that both trains of Service Water will be Operable within 12 hours. The Non Safety Related Chiller units tripped due to the SWS low pressure conditions, and were recovered shortly there after. No additional failures or equipment challenges occurred as a result of this event." The licensee informed the NRC resident inspector. * * * RETRACTED AT 1907 EST ON 12/5/01 BY J. A. WITTER TO FANGIE JONES * * * "At 0430 hours on October 5, 2001 Beaver Valley Power Station Unit 2 reported entry into Technical Specification 3.0.3, due to two trains of the Service Water System being inoperable (Event Notification #38352). The declaration of the loss of both trains of the Service Water System was a conservative action taken by the operating personnel at that time. This notification is a retraction of the 10 CFR 50.72(b)(3)(v)(B) event on October 5, 2001 at 0026 hours. Subsequent investigation of the event and engineering assessment of operability concluded that one train of the Service Water System remained operable throughout the time period of this event. Therefore, Technical Specification 3.0.3 was not applicable and Technical Specification 3.7.4.1 was applicable for the loss of one train of Service Water, which was subsequently properly exited 6 hours later." The licensee notified the NRC Resident Inspector. The R1DO (John Rogge) has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2001-10-05
38351 | 0 | US AIR FORCE |  |  |  |  | 2001-10-04 | 2001-10-04 18:09 | 2001-10-04 | REPORT OF 2 MISSING EXIT SIGNS CONTAINING TRITIUM AT CANNON AFB Two exit signs containing 20 curies of tritium each were discovered missing from building 1258 at Cannon Air Force Base, New Mexico. The signs were in place on 9/26/01 during a previous inspection. The signs are manufactured by SRB Technologies and the serial numbers are 192167 and 192168. There will be a formal investigation conducted. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-10-04
38350 | 0 | RAPID CITY REGIONAL HOSPITAL |  |  |  |  | 2001-10-04 | 2001-10-04 16:58 | 2001-10-04 | MEDICAL MISADMINISTRATION - UNDERDOSE Today, 10/4/01, when the dose for a second treatment was being prepared, it was discovered that the first dose was not as large as prescribed. The first dose administered on 9/27/01 should have been 750 centigray and was only 400 to 500 centigray. The attending physician has been notified and the patient will be notified. A correcting dose, an additional fraction, will be given to correct the underdose. No adverse affects are expected by this misadministration. The dosage is administered with a high dose rate machine, Nucletron Microselectron. The Radiation Safety Officer contacted NRC Region 4 (Richard Leonardi). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | SD | HOS |  | 35.33 |  |  |  | 0 | 2001-10-04
38349 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2001-10-04 09:13 | 2001-10-04 16:10 | 2001-10-04 | OPERATING LICENSE CONDITION VIOLATION (POTENTIAL MAXIMUM POWER LEVEL VIOLATION) "This report is being made as required by River Bend Station license condition 2.E. River Bend is reporting a potential violation of the maximum power level as authorized in license condition 2.C.1. "This event is similar to event numbers 38337 and 38340 reported by two other BWR plants Based on the General Electric (GE) report titled, 'Impact of Steam Generator Carryover Fraction on Process Computer Heat Balance Calculations, September 2001.' It is possible that River Bend may have exceeded the maximum power level on some occasions in the past by approximately three megawatts thermal. "River Bend Station is currently in a refueling outage, so no immediate actions are necessary. This condition has been entered into the station's corrective action program to further evaluate the applicability of this condition and to develop an appropriate response before returning to power operations. "The licensee notified the NRC resident inspector." (Refer to event numbers 38330, 38337, 38340, 38344, 38445, 38347, 38356, and 38357 for similar events at Fermi, Perry, Hope Creek, Grand Gulf, Columbia Generating Station, Limerick 2, Clinton, and Limerick 1.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2001-10-04
38348 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2001-10-04 | 2001-10-04 15:59 | 2001-10-04 | SMALL PRESSURE BOUNDARY LEAK IDENTIFIED WHILE SHUTDOWN "At 0809 on October 4, 2001, Crystal River Unit 3 (CR-3) was in MODE 6 shutdown for refueling operation. CR-3 has identified a small defect in the reactor coolant system (RCS) pressure boundary. An RCS leak was suspected due to elevated radioactivity levels detected in the nuclear services closed cycle cooling water (SW) system since June 2001. Testing was conducted on-line in MODE 1 and could not determine the source of the leakage. Additional testing in MODE 6 has identified the seal area heat exchanger on the 1B reactor coolant pump (RCP-1B) as the most likely source of the leakage. The defect allowed a small amount of leakage to occur from the RCS to the SW system during the previous operating cycle. A definitive leak location could not be identified due to the extremely small size of the leak. However, since all components in the RCP heat exchanger are included as part of the class 1 RCS pressure boundary, this defect is reportable under 10 CFR 50.72(b)(3)(ii)(A). CR-3 was shutdown in MODE 6 at the time of the discovery. The RCP heat exchanger will be repaired prior to returning to power operation." The leak rate has been determined to be 0.02 gpm which exceeds the Technical Specification limit of 'No Pressure Boundary Leakage' and it appears to be a long term development. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-10-04
38347 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-10-03 23:28 | 2001-10-04 14:23 | 2001-10-04 | 24-HOUR REPORT IN ACCORDANCE WITH OPERATING LICENSE DUE TO POTENTIAL MAXIMUM POWER LEVEL VIOLATION "This report is being made in accordance with Limerick Generating Station Unit 2 Operating License Condition 2.E. as a potential violation of License Condition 2.C(1), Maximum Power Level "GE Report titled 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations', September 2001, documents a non-conservative assumption for the moisture carryover fraction used in the calculation of core thermal power. The assumed carryover fraction of 0.1% was discovered to be potentially closer to zero and therefore non-conservative in later model GE BWRs. "A review of Limerick Unit 2 moisture carryover data from an ASME PTC 6 test performed in October of 1999 found a moisture carryover value of 0.0277%, inducing an estimated bias of approximately 2.8 MWth. Similar testing on Limerick Unit 1 found a value of greater than 0.1%. Based on this data Limerick Unit 1 is not considered affected at this time. "Based on this potential non-conservatism on Unit 2, indicated Maximum Power Level shift average is being administratively controlled 3 MWth below the licensed power level of 3458 MWth. "Exelon staff is continuing to evaluate the effect of the moisture carryover term in the heat balance calculation." The NRC resident has been notified. (Refer to event numbers 38330, 38337, 38340, 38344, 38445, 38349, 38356, and 38357 for similar events at Fermi, Perry, Hope Creek, Grand Gulf, Columbia Generating Station, River Bend, Clinton, and Limerick 1.) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2001-10-04
38346 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2001-10-04 | 2001-10-04 14:11 | 2001-10-04 | AGREEMENT STATE REPORT - DAMAGED GAUGE 1. Event Report ID No.: NV-01-006 2. License No.: 00-11-0196-01 3. Licensee: Las Valley Water District 4. Event time, date, location: Las Vegas, NV, October 1, 2001 5. Event type (e.g. misadministration, lost source, overexposure, etc.): Slightly damaged portable gauge. Cause of the incident was lack of attention to detail. 6. Any notifications i.e. other agencies, patient, press release, FBI, etc.: N/A 7. Event description: release, isotope, activity, exposure(s), dose, contamination level, equipment malfunction model, serial No., etc.: A portable gauge fell off the bed of a slow moving transporting pickup and was slightly damaged. The gauge was not carried in it's shipping container at the time of the incident, The source was in the safe, shielded position at the time of the incident. The gauge has been surveyed and leak tested and has been shipped to the manufacturer for repair. The gauge was a Troxler Model 3440, s/n 22284 containing 10 mCi of Cs-137 and 40 mCi of Am-241 :Be. 8. Transport vehicle description, if known: Company pickup. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2001-10-04
38345 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-10-02 16:37 | 2001-10-03 18:50 | 2001-10-03 | 24-HOUR REPORT REGARDING AN OPERATING LICENSE CONDITION VIOLATION (POTENTIAL MAXIMUM POWER LEVEL VIOLATION The following text is a portion of a facsimile received from the licensee: "General Electric (GE) report titled, 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculation, September 2001,' documents a non-conservative constant for moisture carryover fraction in the equation used to calculate plant heat balance. The report states that a number of later model GE BWR plants report carryover fractions of less than 0.003%. Currently, Columbia Generating Station uses 0.1% for the carryover term in the calculation as directed by the GE design specifications. Use of the 0.1% term in the heat balance calculation may have resulted in Columbia Generating Station exceeding the maximum core thermal power value of 3486 MWt specified in license condition 2.C(1) by approximately 2.83 MWt or 0.08% Rated Thermal Power. As a compensatory measure until this issue is resolved, Columbia Generating Station will adopt a conservative value of 0.0% for the moisture carryover term in the plant heat balance calculation. Consequently, the Plant Process Computer eight hour average core thermal power is currently being administratively controlled at less than or equal to 3482 MWt." "The Columbia Generating Station Operating License (NPF-21) contains a requirement to report a violation of this license condition to the NRC Regional Administrator or the Administrators designee. The NRC Region IV Regional Administrator's designee, Mr. William Jones, has been informed of this condition." The licensee notified the NRC resident inspector. (Refer to event numbers 38330, 38337, 38340, 38344, 38347, 38349, 38356, and 38357 for similar events at Fermi, Perry, Hope Creek, Grand Gulf, Limerick 2, River Bend, Clinton, and Limerick 1.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW | [5 empty] | 0 | 2001-10-03
38344 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-10-03 13:00 | 2001-10-03 16:28 | 2001-10-03 | 24-HOUR REPORT REGARDING AN OPERATING LICENSE CONDITION VIOLATION (POTENTIAL MAXIMUM POWER LEVEL VIOLATION) The following text is a portion of a facsimile received from the licensee: "This report is made as required by Grand Gulf Nuclear Station License Condition 2F. Grand Gulf is reporting a potential violation of the maximum power level of 3833 MWT as stated in Licensee Condition 2.C.1." "This event is similar to event number 38337 and 38340 called in by two other BWR plants. Based on the General Electric (GE) report titled, 'Impact of Steam Generator Carryover Fraction on Process Computer Heat Balance Calculations, September 2001.' It is possible that Grand Gulf [may] have exceeded the maximum power level on some occasions in the past by about 3 MWT. The plant has reduced the 100% power limit by 3 MWT until the Heat Balance Equation can be corrected." The licensee notified the NRC resident inspector. (Refer to event numbers 38330, 38337, 38340, 38445, 38347, 38349, 38356, and 38357 for similar events at Fermi, Perry, Hope Creek, Columbia Generating Station, Limerick 2, River Bend, Clinton, and Limerick 1.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW | [5 empty] | 0 | 2001-10-03
38343 | 0 | SORRENTO ELECTRONICS |  |  |  |  | 2001-10-03 | 2001-10-03 16:12 | 2001-10-03 | 10 CFR PART 21 NOTIFICATION REGARDING MICROPROCESSOR BASED RADIATION MONITOR RM-2000 The following text is portion of a facsimile received from Sorrento Electronics: "The information following is in accordance with the reporting requirements of 10 CFR 21.21(d)(4):" "ii) Identification of the basic component which contains the defect: The basic component which contains the defect is software version 16.0 and higher of the microprocessor based radiation monitor, RM-2000, with the 'SAVE MASTER DATABASE' function, where the master database has been restored at least once." "iii) Identification of the firm supplying the basic component: Sorrento Electronics, Inc. [...]" "iv) Nature of the defect and the safety hazard which is created by the defect: The defect was noted at Sorrento Electronics following a power up on a RM-2000 skid, where the detectors had been detached while the monitor was powered down. When the monitor was powered up, the channels associated with the detectors continued to indicate a green operate status rather than indicating a NO PULSES operate failure condition. Further interrogation of the database revealed the monitor was not responding to taking the channel in and out of service or to changing the alarm status. The monitor showed a constant radiation on the channel display. The affected channels would not return to a normal operating condition until the detector was reconnected." "This failure will cause the RM-2000 to not process the following tasks associated with the affected channel: 1. Temperature correction 2. Tracking algorithm 3. No pulses 4. Display checksource value 5. Over range 6. Background subtract 7. Pressure correction 8. Limit to minimum value 9. Display current count rate 10. Limit to maximum value 11. Perform checksource 12. Channel in service 13. Check alarms 14. Reset alarms after power failure" "v) Date on which the information was obtained: The information was noted on software discrepancy notice, (SDN 545), on August 14, 2001, for review of possible 10 CFR [Part] 21 implications. Evaluation by [Sorrento Electronics'] engineering of the problem for 10 CFR [Part] 21 applicability was immediately begun. The evaluation was completed and declared reportable on October 1, 2001." "vi) The number and location of the components subject to the regulations per 10 CFR [Part] 21: The following safety-related equipment is affected: PLANT RADIATION MONITOR ASSEMBLY NUMBER RM-2000 VERSION Salem (PG & E) 04231701-001, S/N: 001 (Gas Monitor) 16.6 Salem (PG & E) 04233101-001, S/N: 001 (Duct Monitor) 16.6 Salem (PG & E) 04231201-001, S/N: 001 (Particulate Iodine Gas Monitor) 16.6 "vii) Name of the implementing organization and time frame for implementing the corrective action: The responsibility for the implementing the corrective action has been delegated to [...] RMS Engineering. Sorrento Electronics will make the individual purchasers aware of this possible problem. Further, the RM-2000 operating code will be revised to correct the deficiency. The new corrected version of the RM-2000 code will be available to customers after November 1, 2001." "viii) Advise related to the defect that will be given to the purchasers: While this defect is not likely to occur during normal operation at a nuclear power plant, it is possible. Therefore, Sorrento Electronics will advise the affected purchasers via a Quality Bulletin of the following interim test procedure to verify operability of the affected RM-2000:" "There are two methods to verify that a RM-2000 has not failed after a power fail sequence. First, if the radiation value being displayed is changing, the monitor is operating correctly. Second, if the radiation value is not changing, then the user should remove the monitor from operation by taking a channel out of service by database manipulation. If the channel goes into a operate fail condition, the RM-2000 is working correctly and the channel can be returned to service. If the monitor does not go into an operate fail condition, the monitor has failed and is not receiving any pulses from the associated detector." (Call the NRC operations officer for reporting organization contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2001-10-03
38342 | 0 | STERIGENICS |  |  |  |  | 2001-10-02 23:59 | 2001-10-03 13:10 | 2001-10-03 | COMMERCIAL IRRADIATOR FACILITY REPORT REGARDING A SOURCE HANG UP Sterigenics is a panoramic, wet-source storage, commercial, irradiator facility. At approximately midnight on 10/02/01, a 2.6-megacurie cobalt-60 source got stuck in the unshielded position for approximately 1 hour. Because the source got stuck on the way down, the licensee lifted the source rack, freed it, and successfully returned it to the shielded position. The licensee is still investigating the cause of this event but stated that there were no obvious reasons at this time. There were no personnel radiation exposures or injuries as a result of this event, and there was no source leakage. (Call the NRC operations officer for a site contact telephone number.) (Refer to event #38363 for a similar event at Sterigenics on 10/07/01.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSHIELD STUCK SOURCE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 36.83(a)(1) |  |  |  | 0 | 2001-10-03
38340 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-10-02 15:57 | 2001-10-02 16:20 | 2001-10-02 | 24-HOUR REPORT REGARDING AN OPERATING LICENSE CONDITION VIOLATION (POTENTIAL MAXIMUM POWER LEVEL VIOLATION) The following text is a portion of a facsimile received from the licensee. "General Electric (GE) report titled, 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations, September 2001,' documents a non-conservative assumption for moisture carryover used in the calculation of core thermal power. The assumed carryover fraction of 0.1% was discovered to be closer to 0.0% (non-conservative) in later model GE BWRs. Hope Creek Generating Station may be affected by the non-conservative core thermal power calculation with an estimated bias of less than 4 MWt. As a result, there is a potential that Hope Creek Generating Station has operated at power levels in excess of Operating License condition 2.C(1) which requires that the facility be operated at reactor core power levels not in excess of 3339 MWt." "This notification is being made in accordance with Hope Creek Operating License Condition 2.F, as a potential violation of Hope Creek Operating License Condition 2.C(1)." "An administrative shift average power limit of 3335 MWt has been implemented when the Crossflow ultrasonic flow measurement system is available. If Crossflow is unavailable, shift average power will be administratively limited to 3289 MWt." "PSEG Nuclear is continuing to evaluate the effect of the moisture carryover term on the heat balance calculation." The licensee notified the NRC resident inspector. (Refer to event numbers 38330, 38337, 38344, 38445, 38347, 38349, 38356, and 38357 for similar events at Fermi, Perry, Grand Gulf, Columbia Generating Station, Limerick 2, River Bend, Clinton, and Limerick 1.) | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2001-10-02
38339 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-09-25 09:16 | 2001-10-02 11:44 | 2001-10-02 | AGREEMENT STATE REPORT REGARDING A RADIOGRAPHY CAMERA THAT WAS LOST AND FOUND IN LONGVIEW, TEXAS (Texas Incident #7806) A logging source was found at the intersection of Eastman Road and Cotton Street in Longview, Texas. The Longview Fire Department responded to the scene, and the licensee, Hi-Tech Testing Service, Inc., was contacted. A licensee representative also responded to the site and performed a complete survey of the exposure device using a calibrated survey meter. There were no abnormally high readings observed during this survey. The IR100 exposure device was also visually examined for any damage to the body, locking mechanism, and outlet port. There was no physical damage seen during this examination. The exposure device was returned to the licensee's shop, thoroughly inspected, and locked inside a radioactive storage area. This subsequent detailed inspection revealed that all mechanical components were functioning properly, and there was no apparent damage to the exposure device body. One transport label was replaced because some of the information was illegible. It was later determined that the exposure device had unknowingly fallen onto the highway from the bumper of a pickup truck. NOTE: Exposure Device S/N 4573, Source S/N 00564B, Type and Activity of Source Material - Not Reported | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-10-02
38337 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-10-01 15:30 | 2001-10-01 19:14 | 2001-10-01 | 24-HOUR REPORT REGARDING AN OPERATING LICENSE CONDITION VIOLATION (POTENTIAL MAXIMUM POWER LEVEL VIOLATION) The following text is a portion of a facsimile received from the licensee. "This report is being made in accordance with Perry Nuclear Power Plant (PNPP) Unit 1 Operating License Condition 2.F, as a potential violation of the Maximum Power Level of 3758 [MWth] as described in License Condition 2.C(1)." "General Electric (GE) report titled, 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations, September 2001,' documents a non-conservative assumption for moisture (carryover) used in the calculation of core thermal power. The assumed carryover fraction of 0.1% was discovered to be closer to 0.0% (non-conservative) in later model GE BWRs." "Following initial review by PNPP staff, moisture carryover has not been tested at Perry since the initial startup test program, and the plant was potentially affected by the non-conservative core thermal power calculation results presented by GE. The plant is unable to perform carryover testing at this time to provide a more accurate MWth bias; therefore, until testing can be accomplished a conservative 3 MWth bias is suspected. Additionally, the plant staff continues to investigate the overall effect of the moisture carryover term within the Heat Balance equation." "PNPP Unit 1 has an administrative 8-hour average power limit of 3754 MWth (reactor power reduction of 4 MWth) that was conservatively implemented on 09/20/01 when the plant initially identified the potential concern in the corrective action program." The licensee notified the NRC resident inspector. (Refer to event numbers 38330, 38340, 38344, 38445, 38347, 38349, 38356, and 38357 for similar events at Fermi, Hope Creek, Grand Gulf, Columbia Generating Station, Limerick 2, River Bend, Clinton, and Limerick 1.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0 | 2001-10-01
38336 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-10-01 16:00 | 2001-10-01 19:14 | 2001-10-01 | OFFSITE NOTIFICATION REGARDING OUTFALL STRUCTURE SAMPLES IN EXCESS OF RELEASE LIMITS The following text is a portion of a facsimile received from the licensee. "Injection of [a] microbiological agent commenced at 1140 hours to treat the station raw water systems for Zebra Mussel infestation. [The] agent used was Spectrus CT-1300 (Clamtrol). Injection was being made at the station intake structure, and [a] detoxification agent was being added at the outfall structure prior to returning to Lake Erie. At 1600 hours, it was discovered that samples taken at the outfall structure indicated concentration of this chemical of 0.35 ppm which is in excess of the release limit of 0.04 ppm contained in the Chemical Permit. This event requires notification of the US EPA. [The] feed rate of the Clamtrol was decreased, and [the] feed rate of the detoxification agent was increased. Injection of the chemical was terminated at approximately 1740 hours. Sampling is continuing to determine when compliance with the Chemical Permit is reestablished." The licensee notified the NRC resident inspector and plans to notify the US EPA. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-10-01
38335 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-10-01 02:00 | 2001-10-01 12:59 | 2001-10-01 | ACTIVATION OF THE HIGH VOLTAGE UF6 RELEASE DETECTION SYSTEM DUE TO A UF6 LEAK TO ATMOSPHERE The following text is a portion of a facsimile received from Paducah personnel: "At 0200 CDT, on 10-01-01, the Plant Shift Superintendent was notified of an activation of the High Voltage UF6 Release Detection System at the C-315 Tails Withdrawal Building. Two UF6 detector heads had alarmed due to a UF6 leak to atmosphere from the rupture disc assembly for the 'B' UF6 accumulator. Operations isolated and pulled down the affected system. The Plant Emergency Squad responded and closed the rupture disc isolation valves. High volume air samples were taken with negative results. Health Physics surveyed the area in C-315 and determined that contamination was limited to the housing near the accumulator. The C-315 building was then released to operations with controls on the area of contamination." "This event is reportable to the NRC per the Safety Analysis Report, section 6.9, table 1, criteria J.2, safety system actuation due to a valid signal as a 24-hour event notification." "The NRC Senior Resident Inspector has been notified of this event." "PGDP Problem Report No. ATR-01-5077; PGDP Event Report No. PAD-2001-040; Event Worksheet: [38335] Responsible Division; Operation." ***** UPDATE FROM KEVIN BEASLEY TO LEIGH TROCINE AT 2105 EDT ON 10/01/01 ***** The following text is a portion of a facsimile received from Paducah personnel: "Further investigation determined that the UF6 was released from a tube that connected the rupture disc assembly to a calibration buggy. The connection tube had come in contact with a heater that melted a section of the tube allowing the UF6 release." Paducah personnel notified the NRC resident inspector. The NRC operations officer notified the R3DO (David Hills) and NMSS EO (Patricia Holahan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-10-01
38334 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-09-28 11:30 | 2001-10-01 09:07 | 2001-10-01 | TROXLER GAUGE WAS STOLEN FROM STATE OF FLORIDA LICENSEE A truck with a Troxler gauge (8mCi Cs-137 and 40mCi Be:Am-241) in a transport case chained to the bed was left unattended in the parking lot. When an employee returned at 11:30 a.m., the gauge was missing. The padlock on the transport case had been cut and the gauge was gone. The transport case and the keys were not taken. Law enforcement and the Florida Bureau of Radiation Control are investigating. NRC Region II has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2001-10-01
38333 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2001-09-28 | 2001-10-01 08:41 | 2001-10-01 | PART 21 INVOLVING UNACCEPTABLE INSPECTION SERVICES On August 24, 2001, FPC personnel performed a water test on spare safety-related Decay Heat Raw Water System pump RWP-3A to determine whether the lip seal was installed correctly. This test was not part of an FPC receipt inspection. No bearing flush/lubricating water flow was observed coming from the pump. Upon disassembly of the pump bowl, FPC personnel confirmed that the lip seal was installed incorrectly. In 1999, spare RWP-3A pump was rebuilt by Tampa Armature Works under Purchase Order No. F742538K. FPC contracted Raytheon (Contract Number NO1067AD) to oversee the RWP-3A rebuilding activities and ensure, through inspection, that the work was performed in accordance with the Raytheon 10 CFR Part 50, Appendix B, QA Program. The shop traveler provided to Tampa Armature Works by FPC included a detailed sketch and specific guidance with respect to the orientation of the pump lip seal. In February 2000, Tampa Armature Works signed off on and Raytheon Inspector 21 stamped Shop Traveler Line Item #30A attesting to the correct orientation of the lip seal even though the lip seal was not installed correctly. The rebuilt pump was subsequently delivered to FPC. FPC considers the above condition to be reportable pursuant to 10 CFR 21.21 as a defect associated with a substantial safety hazard. 10 CFR 21.3 states, in part, that a defect means a deviation in a basic component delivered to a purchaser for use in a facility or activity subject to 10 CFR Part 21 if, on the basis of an evaluation, the deviation could create a substantial safety hazard. The NRC Resident Inspector and the vendor were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 21.21 |  |  |  | 0 | 2001-10-01
38332 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2001-09-30 14:00 | 2001-09-30 20:28 | 2001-10-02 | EVIDENCE OF REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE DISCOVERED WHILE IN COLD SHUTDOWN. The following text is a portion of a facsimile received from the licensee: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73." "On September 30, 2001, at approximately 1400 MST, Palo Verde Nuclear Generating Station (PVNGS) Unit 3 discovered evidence of reactor coolant system (RCS) pressure boundary leakage. PVNGS Unit 3 was shut down in Mode 5 conducting cooldown and depressurization in its [ninth] refueling outage at the time of discovery. Current RCS temperature is approximately 135 degrees Fahrenheit and RCS pressure is approximately 20 psia." "The leakage was discovered at two [Inconel] alloy 600 nozzle locations during inservice inspection (ISI); one in a RCS hot leg temperature detector nozzle and another in a pressurizer heater sleeve. The RCS hot leg leakage is located in the RTD nozzle for an inservice temperature [detector] (Loop #1, Equipment ID: 3JRCETW112HD). The pressurizer heater sleeve leakage is located at pressurizer heater B17. The leakage was identified in the form of small deposits of boron accumulation around the circumferences of the hot leg nozzle and that of the pressurizer sleeve. PVNGS has conducted inspections of these nozzles [and] sleeves during each refueling outage since the discovery that Inconel alloy 600 nozzles are susceptible to axial cracking. No evidence of leakage was identified when inspected during the last refueling outage approximately 18 months ago." "The timing of this ENS report was based on the determination at 14:00 MST on September 30, 2001, that the boron accumulation represented a serious of a principle safety barrier. PVNGS Unit 3 Technical Specification Limiting Condition for Operation (LCO) 3.4.14 (RCS Operational Leakage) permits no reactor coolant system pressure boundary leakage. It was therefore conservatively concluded that any evidence of pressure boundary leakage, regardless of magnitude, represents serious degradation of a principle safety barrier. Technical Specification [LCO] 3.4.14 is applicable in Modes 1, 2, 3, and 4. Unit 3 was in Mode 5 in a planned refueling outage at the time of discovery; therefore, LCO 3.4.14 is currently not applicable. The-hot leg nozzle and pressurizer sleeve will be repaired prior to re-entering Mode 4. It is anticipated that the repair will be utilizing the Mechanical Nozzle Seal Assembly (MNSA). No ESF actuations occurred and none were required. No structures systems or components were inoperable that contributed to this event particularly the fuel cladding and the containment fission product barriers. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee notified the NRC resident inspector. ***** UPDATE FROM DAN MARKS TO LEIGH TROCINE AT 1304 EDT ON 10/02/01 ***** The following text is a portion of a facsimile received from the licensee: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73." "This is a follow-up notification from the Palo Verde Nuclear Generating Station (PVNGS) Unit 3 to remove the references to reactor coolant system (RCS) pressure boundary leakage at a pressurizer heater sleeve. The notification of pressure boundary leakage from a Resistance Temperature Detector (RTD) nozzle remains as identified in the original ENS report #38332 of September 30, 2001 at 1728 ET. Chemistry and radiological analysis of the residue located in the vicinity of the pressurizer heater sleeve and engineering personnel review of the analysis results determined the residue was not evidence of pressure boundary leakage." "On September 30, 2001, at approximately 1400 MST, Palo Verde Nuclear Generating Station Unit 3 discovered evidence of RCS pressure boundary leakage. PVNGS Unit 3 was shut down in Mode 5 conducting cooldown and depressurization in its ninth refueling outage at the time of discovery. Current RCS temperature is approximately 100 degrees Fahrenheit and RCS pressure is approximately 18 psia." "The leakage was discovered at one Inconel alloy 600 nozzle location during inservice inspection (ISI), in a RCS hot leg temperature detector nozzle. The RCS hot leg leakage is located in the RTD nozzle for an inservice temperature [detector] (Loop #1 Equipment ID: 3JRCETW112HD). The leakage was identified in the form of small deposits of boron accumulation around the circumference of the hot leg nozzle. PVNGS has conducted inspections of these nozzles during each refueling outage since the discovery that Inconel alloy 600 nozzles are susceptible to axial cracking. No evidence of leakage was identified when inspected during the last refueling outage approximately 18 months ago." "The timing of the Initial ENS #38332 report at 1428 MST (1728 ET) on September 30, 2001, was based on the determination at 1400 MST that the boron accumulation represented a serious degradation of a principal safety barrier. PVNGS Unit 3 Technical Specification Limiting Condition for Operation (LCO) 3.4.14 (RCS Operational Leakage) permits no reactor coolant system pressure boundary leakage." "It was therefore conservatively concluded that any evidence of pressure boundary leakage, regardless of magnitude, represents serious degradation of a principle safety barrier. Technical Specification [LCO] 3.4.14 is applicable in Modes 1, 2, 3, and 4. Unit 3 was in Mode 5 in a planned refueling outage at the time of discovery; therefore, LCO 3.4.14 is currently not applicable. The hot leg nozzle will be repaired prior to re-entering Mode 4." "No ESF actuations occurred and none were required. No structures systems or components were inoperable that contributed to this event, particularly the fuel cladding and the containment fission product barriers. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Claude Johnson) and NRR EO (Tad Marsh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-09-30
38330 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-09-28 16:25 | 2001-09-28 18:39 | 2001-09-28 | 24-HOUR REPORT REGARDING AN OPERATING LICENSE CONDITION VIOLATION (POTENTIAL MAXIMUM POWER LEVEL VIOLATION) The following text is a portion of a facsimile received from the licensee: "This report is being made in accordance with Fermi 2 License Condition 2.F, as a potential violation of the Maximum Power Level of 3430 MWth as described in License Condition 2.C(1)." "GE report titled, 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations, September 2001,' documents a non-conservative assumption for moisture [carryover] used in the calculation of core thermal power. The assumed carryover fraction of .1% was discovered to be closer to 0.0% (non-conservative) in later model GE BWRs." "An initial review at Fermi 2 was completed at 1625 on 09/28/01. The initial review indicated that Fermi is susceptible to the non-conservative core thermal power calculation, with an estimated bias of 1.64 MWth. This initial analysis was based on a carryover test performed in 1996 at Fermi 2." "Fermi 2 has an administrative 8-hour average power limit of 3428.8 MWth. Given the 1.64 MWth bias, it is possible that the license limit of 3430 MWth has been exceeded in the past. Fermi 2 took immediate action to reduce the administrative power limit to 3427 MWth. Reactor power was reduced by 3 MWth." The licensee notified the NRC resident inspector. (Refer to event numbers 38337, 38340, 38344, 38445, 38347, 38349, 38356, and 38357 for similar events at Perry, Hope Creek, Grand Gulf, Columbia Generating Station, Limerick 2, River Bend, Clinton, and Limerick 1.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2001-09-28
38329 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-28 15:20 | 2001-09-28 17:11 | 2001-09-28 | OFFSITE NOTIFICATION REGARDING AN OPACITY VIOLATION (4-hour Report) The following text is a portion of a facsimile received from Portsmouth personnel: "At 1520 hours [on] 09/28/01, the Ohio Environmental Protection Agency (OEPA) was notified per Ohio Administrative Code (OAC) 3745-15-06(B) that an opacity exceedance had occurred at the X-600 Steam Plant. The opacity violation occurred on [the] #2 Boiler when our #2A Precipitator voltages began to fluctuate. Operators adjusted load/air requirements on the #2 Boiler in an effort to prevent further exceedances. [The] cause of the voltage fluctuations has not been determined at this time." "This is reportable as a 4-hour NRC Event due to notification to an outside agency (OEPA) being made per Nuclear Regulatory Reporting Procedure UE2-RA-RE1030, Appendix D, Criteria P (Miscellaneous)." Portsmouth personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-28
38328 | 0 | US ARMY |  |  |  |  | 2001-09-28 12:07 | 2001-09-28 13:34 | 2001-09-28 | MISSING CHEMICAL AGENT DETECTOR CONTAINING 30 MICROCURIES OF AMERICIUM-241 A chemical agent detector (CAD) containing 30 microcuries of americium-241 was discovered to be missing during a physical inventory conducted during 08/01. A search was performed at all units, and the US Army Aberdeen Proving Ground in Maryland was notified of the missing CAD at 1207 on 09/28/01. It is believed that the CAD may have been last used by the Wisconsin Army National Guard located in Black River Falls during nuclear biological chemical (NBC) training. (Call the NRC operations officer for licensee contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-09-28
38326 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2001-09-27 13:00 | 2001-09-28 11:43 | 2001-09-28 | DENSITY GAUGE SOURCE ROD BROKEN OFF A Humboldt Model # 5001gauge was run over by a 50-ton blader vehicle. The density gauge source rod was broken off, and the gauge itself was flattened. The blader vehicle ran over the density gauge in a landfill while the person who was assigned to guard the gauge had his back turned. The source was in its stored position when it was run over by the blader vehicle. There was no contamination on the blader vehicle and no radioactive release from the gauge. The Humboldt Model # 5001 has 8 mCi of cesium-137 and 40 mCi of americium-241/beryllium. The owner of the gauge is Thompson Dreessen Dorner Inc., which is located in Omaha. (Call the NRC operations officer for State contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2001-09-28
38325 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-09-27 08:00 | 2001-09-27 19:47 | 2001-09-27 | AGREEMENT STATE REPORT REGARDING A STOLEN NITON GAUGE The following text is a portion of a facsimile received from the California Radiologic Health Branch, Department of Health Services: "This is 24-hour report [in accordance with] 10CFR20.2201(a)(1)(i) from State of California Radiologic Health Branch." "This is to report that an x-ray fluorescence device has been stolen. [The] company is Geotechnical Services [in] Tustin, CA." "[The] device is a Niton S/N U2387NR1222. The operator's car was broken into some time between 7PM (9-26) and 8AM (9-27) in Long Beach. [A] police report [is] being filed, and [the] facility will run an add describing the device and offering a reward for its return." "These devices typically contain up to 50 mCi of Cd-109." (Call the NRC operations officer for state and licensee contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-09-27
38324 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-09-27 18:34 | 2001-09-27 19:39 | 2001-09-27 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO A LEAK IN A COMMON SAFETY INJECTION SUCTION HEADER The following text is a portion of a facsimile received from the licensee: "Unit 1 is required to shut down due to entry into Tech Spec 3.0.3 for both trains of SI (safety injection) pumps being inoperable (Tech Spec 3.5.2). The cause of both Unit 1 SI pump inoperability is due to a leak in the common suction header at a vent line on the common header." The licensee notified the NRC resident inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-09-27
38323 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2001-09-27 | 2001-09-27 13:58 | 2001-09-27 | AGREEMENT STATE REPORT REGARDING AN OVEREXPOSURE DURING A RADIOGRAPHY EVENT On an unknown date, a Longview Inspection employee received an exposure of 4,500 mrem during a radiography event in Pascagoula, Mississippi. As a result, the individual's annual exposure increased to 5,270 mrem, which exceeded the annual limit of 5,000 mrem. The second radiographer at the scene of the event received approximately 300 mrem. An inspection is planned for next week. The Mississippi State Health Department notified the NRC Region 2 Office (Dick Woodruff). (Call the NRC operations officer for a State contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0 | 2001-09-27
38322 | 0 | UNIVERSITY OF WISCONSIN |  |  |  |  | 2001-09-09 | 2001-09-27 09:58 | 2001-09-27 | MISSING AM-241 SOURCES During renovation work in a laboratory, a contractor moved a workbench upon which five americium-241 anti-static sources were being stored. The sources were individually contained in tubes, which apparently broke open upon striking the laboratory floor. Two of the five sources were recovered, but since the sources are extremely small (approximately 1 mm x 3 mm) and the contractor and custodial staff were unaware of their presence, the licensee believes that the three other sources were discarded in a sanitary landfill. The licensee estimates the activity of each source to be between 0.4 and 4 microCuries, and does not believe that these sources present a health risk to the general population. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-09-27
38321 | 0 | UNIVERSITY OF PENNSYLVANIA |  |  |  |  | 2001-08-29 12:00 | 2001-09-27 08:27 | 2001-09-27 | MISSING 21 MICROCURIE COBALT-60 TESTING SOURCE. On 08/29/01 it was discovered at the University of Pennsylvania Physics Department that a 21 microcurie cobalt-60 source was missing. An extensive survey and search of the Physics Department building was performed and the source was not found. All persons who had access to the source were questioned. The Radiation Safety Officer for the University of Pennsylvania notified NRC Region 1 office of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-09-27
38320 | 0 | QUEENS MEDICAL CENTER |  |  |  |  | 2001-09-26 09:00 | 2001-09-26 22:07 | 2001-09-26 | MEDICAL MISADMINISTRATION INVOLVING DELIVERY OF TREATMENT TO THE WRONG SITE At approximately 0900HST on 9/26, a patient undergoing treatment for restenosis of a cardiac vessel received a 23 gray dose using a Sr-90 source via intravascular brachytherapy. The error occurred due to difficulty in resolving the correct vessel segment location using fluoroscopy imaging. The attending radiologist and cardiologist reviewed film concluding that the wrong segment had been treated. The prescribed dose was then delivered to the correct site. The patient has not been informed and there are no adverse effects anticipated. The licensee will meet with the vendor to discuss appropriate corrective actions in use of the equipment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 35.33 |  |  |  | 0 | 2001-09-26
38319 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2001-09-25 | 2001-09-26 17:45 | 2001-09-26 | AGREEMENT STATE REPORT INVOLVING POTENTIAL DAMAGE TO A PORTABLE GAUGE DURING TRANSPORT "A portable gauge fell off the bed of the transporting pickup and was slightly damaged. The gauge was not carried in it's shipping container at the time of the incident. The guide rod (as opposed to the source rod) broke near the base of the gauge. The source was in the safe, shielded position at the time of the incident. The gauge has been surveyed and leak tested and has been shipped to an authorized repair facility. The gauge was a Humboldt 5001, s/n 400 containing 8 mCi of Cs-137 and 40 mCi of Am-241:Be. "Cause of the incident was lack of attention to detail. Event Report ID No. NV-01-005." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2001-09-26
38316 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-25 09:30 | 2001-09-25 13:28 | 2002-02-05 | 4-HOUR 91-01 BULLETIN RESPONSE The following text is a portion of a facsimile received from Portsmouth personnel: "At 0930, uranium bearing material was observed in the interior spaces of a block wall in the X-705 recovery area the openings leading to the interior spaces of the block wall is a violation of administrative control #3 of NCSA 0705_076.A03 because the exact geometry or volume of the potential collection area is unknown. This is a loss of one leg of double contingency as defined in NCSE 0705_076.E03. The presence of an unknown (at this time) amount of uranium bearing material that was spilled (at some time in the facility's past) is a potential violation of passive design feature one of NCSA 0705_076.A03 which credits the physical integrity of X-705 system piping this would represent a loss of the second leg as defined in NCSE 0705_076.E03." "Measurements are being conducted and are ongoing to determine amount of material, which may affect this report." "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is potentially high (at this time) because the exact amount of Uranium bearing material that could have entered the opening in the block wall is unknown. Measurements to quantify the material are in progress. The apparent block wall construction (as evidenced by visual inspection of wall openings in the other areas of Recovery) indicates the potential for the presence of unfavorable geometry voids within and between the blocks compromising the exterior building wall." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): If 1) a significant amount of uranium bearing material entered the void spaces of the block wall, 2) the material has collected in the multiple voids resulting in a single unfavorable geometry configuration, 3) the material has a high enrichment and uranium concentration, and 4) the material would become sufficiently moderated, then a potentially critical configuration could result. Note that no spills or leaks of uranium bearing material from present X-705 systems has occurred at this time. The material in question has apparently been there for some time." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for inadvertent containers relies upon the physical integrity of X-705 piping to prevent a spill of an unsafe amount of material. An unsafe amount is defined by the concentration and enrichment of the material. Double contingency also relies upon administrative controls limiting the presence of unfavorable geometry or unsafe volume containers that could collect a spill or leak." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Unknown at this time. Enrichment could be greater than 90% based upon historical operations. The form is most likely uranyl nitrate or UO2F2. Measurements for determination of mass and assay are currently in progress." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The openings leading to the interior spaces of the block wall is a violation of administrative control #3 of NCSA.705_076.A03 because the exact geometry or volume of the potential collection area is unknown. This is a loss of one leg of double contingency as defined in NCSE-0705_076.E03. The presence of an unknown (at this time) amount of uranium bearing material that has spilled (at some time in the facility's past) is a potential violation of passive design feature 1 of NCSA-0705_076.A03 which credits the physical integrity of X-705 system piping. This would represent a loss of the second leg of double contingency as defined in NCSE-0705_076.E03." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Samples of the material have been taken and DNA measurements will be taken to determine amounts of material and assay." The NRC Resident Inspector was notified and the DOE Representative will be notified. ***** UPDATE FROM JIM McCLEERY TO LEIGH TROCINE AT 1942 ON 09/27/01 ***** The following text is a portion of a facsimile received from Portsmouth personnel: "Update #1 - Conservative NDA analysis of the area near column A-16 indicates a total maximum mass of 225+/-113 grams 235U with an enrichment of 8.2% is present (preliminary NDA analysis reported less conservative values), which is less than the safe mass limit for uranium. Investigations to determine the extent of condition have identified three additional areas of potential concern in X-705 Recovery. These areas are: the wall near the A-loop overflow column, the wall adjacent to the Calciner system, and the wall near the top of the B-38 storage columns. Each of these areas has received preliminary scans via NDA analysis to determine the potential for uranium material holdup in the block walls. Preliminary results indicate that the amount of material, if any, in the wall near the A-loop overflow and near the Calciner are bounded by the amount quantified near column A-6. More detailed [quantitative] NDA scans for these two locations (to differentiate between surface contamination, uranium holdup, and background) are currently in progress and will be reported when available. Preliminary results indicate that no material is suspect in the wall near the B-38 storage column (near background readings). Additional NDA scans are currently in progress to locate any other potential areas of concern in the Recovery Area. "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is now low because the amount of uranium bearing material that entered the openings in the block wall is known to be less that 338 grams 235U which is less than the safe mass limit for uranium." Portsmouth personnel plan to notify the NRC resident inspector. The NRC operations officer notified the R3DO (Phillips) and NMSS EO (Holahan). ***** UPDATE FROM MIKE RITCHIE TO LEIGH TROCINE AT 1626 ON 10/01/01 ***** The following text is a portion of a facsimile received from Portsmouth personnel: "Update #2 - More detailed quantitative NDA scans for the wall near the A-loop overflow column indicate a total maximum mass of 92+/-46 grams 235U with an enrichment of 86% is present (less than a safe mass). Quantitative NDA scans for the wall adjacent to the Calciner system indicate a total maximum mass of 201+/-101 grams 235U with an enrichment of 5.3% (also less than a safe mass). It should be noted that these results incorporate conservative assumptions about the distribution of uranium bearing material in the wall matrix, and total amount of uranium present may be found to be much less upon final disposition." "Preliminary results indicate that no material is suspected in the wall near the B-38 storage column (near background readings): therefore, quantification was not performed in this area." "[...]" Portsmouth personnel plan to notify the NRC resident inspector. The NRC operations officer notified the R3DO (Hills) and NMSS EO (Brown). (Call the NRC operations officer for additional details.) ***** UPDATE FROM CURT SISLER TO LEIGH TROCINE AT 0408 ON 02/05/02 ***** The following text is a portion of a facsimile received from Portsmouth personnel: "Update #3 - To reestablish compliance, an approximately 24" X 80" section of block wall was removed in accordance with NCSA-0705_135. Following removal of the primary area, five locations around the perimeter were then subjected to additional NDA analysis. Conservative NDA analysis indicated less than 306 grams U235 total spread over the five additional locations. In a second removal operation, additional blocks were removed at four locations adjacent to the primary area where greater than 15 grams U235 was indicated. When combining all NDA estimates which make conservative assumptions about the distribution of uranium-bearing material in the wall matrix, up to 705 [grams] U235 may have been distributed in this area. If the mass were concentrated in one location, it would still be less than the maximum subcritical mass [...] given in ANSI/ANS-8.1-1983." Portsmouth personnel plan to notify the NRC resident inspector. The NRC operations officer notified the R3DO (Tom Kozak) and NMSS EO (John Hickey). (Call the NRC operations officer for additional details.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-25
38315 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2001-09-22 | 2001-09-25 10:25 | 2001-09-25 | BAKER HUGHES OIL FIELD OPERATIONS INC. REPORTED A STUCK WELL LOGGING SOURCE New Mexico state licensee Baker Hughes Oil Field Operations Inc. has a stuck source 2018 ft below the surface which they are currently fishing for retrieval. It contains 2 curies of Cesium-137, 18 curies Americium-241/Beryllium and 0.8 microcuries Cesium-137. The location is between Hobbs and Artesia, NM east of Loco Hills. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2001-09-25
38314 | 0 | DEFENSE MICROELECTRONICS ACTIVITY |  |  |  |  | 2001-09-25 | 2001-09-25 09:22 | 2001-09-25 | INCORRECT ACTIVITY SOURCE PROVIDED BY VENDOR The licensee called to report that a sealed source installed in their irradiator facility does not have the source activity specified. The source is supposed to contain 200 Ci, but the licensee estimates the actual activity at approximately 100 Ci. The source was installed by GE Vallecito within the past several weeks. The licensee has contacted GE regarding the apparent discrepancy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | CA | OTH | GEN |  |  |  |  | 0 | 2001-09-25
38313 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-09-24 23:51 | 2001-09-25 03:39 | 2001-09-25 | MANUAL REACTOR TRIP DUE TO LOSS OF CIRCULATING WATER PUMPS The licensee reported that Salem Unit 1 manually tripped the reactor due to a loss of circulating water pumps, caused by a fault on the #2 station power transformer. The fault isolation caused loss of one of the required two off-site power sources to both Salem units. Auxiliary feedwater started on low steam generator level after isolation of main feedwater due to the reactor trip. All system functioned as required. The unit is stable in Hot Standby and an investigation into the cause of the electrical disturbance is underway. Two of four reactor coolant pumps tripped when the unit was tripped, which is expected with the partial loss of off-site power. Presently, the only major secondary equipment that is unavailable is associated with the loss of power to two of four non-vital 4 Kv buses. There is one shutdown Technical Specification in effect and that is associated with having only one off-site power source. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-09-25
38312 | 0 | RUTGERS UNIVERSITY |  |  |  |  | 2001-09-24 | 2001-09-24 16:40 | 2001-09-24 | POTENTIALLY MISSING/UNACCOUNTED FOR TRITIUM EXIT SIGN Rutgers University located in New Brunswick, NJ is conducting an investigation to determine whether a general license exit sign containing between 20-30 curies tritium was installed in the Chapel and, if so, is missing. Interviews of several individuals has provided conflicting information. A records search is in progress. The licensee informed NRC Region I (Ruland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | GEN |  |  |  |  | 0 | 2001-09-24
38311 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-09-24 12:30 | 2001-09-24 15:33 | 2001-09-24 | OFFSITE NOTIFICATIONS TO VARIOUS AGENCIES DUE TO A SPILL OF SULFURIC ACID ONSITE "This 4-hour call is being made to the NRC based on the requirements of 10CFR50.72(b)(2)(xi). This is due to a chemical spill at the Callaway Plant requiring notification of the Environmental Protection Agency (EPA), the United States Coast Guard National Response Center (USCGNRC) and Department of Natural Resources (DNR). "On 9/24/01, a sulfuric acid spill was discovered on the plant site. Initial estimates place the spill volume at two hundred gallons and requires notification of the EPA, USCGNRC, and DNR. It was concluded this event is reportable per 10CFR50.72(b)(2)(xi) due to notifications made to various governmental agencies. "The NRC Resident Inspector was notified of this event by the licensee." The sulfuric acid is 93% concentration and is used for treating cooling tower basin water. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-24
38310 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2001-09-24 11:35 | 2001-09-24 15:16 | 2001-09-24 | COURTESY CALL INVOLVING INDICATION OF A LEAKING FUEL ELEMENT A particulate airborne monitor measured Cs-137 and Rb-88 which is indication of a leaking fuel element. The reactor is currently shutdown. The licensee will identify which fuel element is leaking and remove it from service before restarting. The offsite dose consequence is minimal since the airborne activity is less than 10(E-12) microcuries/ml. The licensee will inform the NRR project manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2001-09-24
38309 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-09-24 03:55 | 2001-09-24 10:03 | 2001-09-24 | LOSS OF PROMPT NOTIFICATION TONE ALERT RADIO FOR GREATER THAN 1 HOUR At 0504 the licensee received notification that Oswego County Prompt Notification System Tone Alert Radio was out of service at 0355 and remained out of service for>1 hour from 0455 onward. The Sheriff department was contacted by Oswego County Emergency Operations Center for alternate alerting methods. The National Weather Service is addressing the reason for the Tone Alert Radios being out of service and will provide a return to service time to the Oswego County EOC. The NRC Resident Inspector was notified. See event #38309 * * * UPDATE 1235EDT ON 9/24/01 FROM DAVE POULAN TO S. SANDIN * * * The Tone Alert Radio was restored to service at 1200EDT. The licensee will inform the NRC resident inspector. Notified R1DO(Costello). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-09-24
38308 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2001-09-24 04:55 | 2001-09-24 05:55 | 2001-09-24 | LOSS OF PROMPT NOTIFICATION TONE ALERT RADIO FOR GREATER THAN 1 HOUR The licensee received a call at 0504 EDT from the Oswego County Warning Point that the Oswego County Prompt Notification Tone Alert Radio had been out-of-service for greater than 1 hour as of 0455 EDT. The cause of the outage is unknown and is being investigated. The licensee notified the NRC Resident Inspector. See event #38309 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-09-24
38307 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-09-23 18:34 | 2001-09-23 18:45 | 2001-09-23 | CONDITION FOR AN UNUSUAL EVENT REPORTED BUT NOT DECLARED. At 1755ET the sensing line to the "B" Centrifugal Charging Pump (CCP) local discharge pressure gage broke. The operator noticed that the Volume Control Tank level was decreasing, Reactor Coolant System Pressurizer level did not change, but the VCT low level alarm was never reached. The leak was from the sensing line for "B" CCP local discharge pressure gage which is located in the Auxiliary Building. The leak rate was determined to be approximately 25 gpm by using the plant computer monitor to determine the rate of change of the Volume Control Tank level. All the water issuing from the sensing line drained into the Auxiliary Building drain system which drained into the radwaste system. No release offsite. The licensee is not in any Limiting Condition of Operation at this time. "B" CCP is fully operable because it's discharge pressure can be read from several locations, "A" CCP is fully operable. All other emergency core cooling systems, emergency diesel generators are fully operable if needed. State and Local officials were notified of this event. The time between 1801 hours and 1834 hours were used to determine the size of the leak from the Volume Control Tank. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2001-09-23
38306 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-09-23 05:42 | 2001-09-23 07:03 | 2001-09-23 | 1 HOUR SECURITY REPORT Safeguards system degradation related to power supply functions. Immediate compensatory measures were taken upon discovery. NRC Region 2 (Al Gooden) has been informed by the licensee. Refer to the HOO for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2001-09-23
38305 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-22 02:25 | 2001-09-22 06:21 | 2001-09-22 | 4 HOUR REPORT - NRC BULLETIN 91-01 On 9/22/01 at 0225 hrs., operations personnel in the X-330 process building discovered that a UO2F2 deposit with "Greater Than Safe Mass" (GSM) was no longer being buffered with dry air or N2, to greater than or equal to 14 psia. The deposit was located at 31-5, cell 6/8 drop. The buffer pressure had been monitored from an adjacent cell 31-5-8. Block valves marked as open on a pin chart, were found to be closed, thus isolating the deposit from the monitoring cell. The GSM deposit pressure was verified to be 5.81 psia with Maintenance and Test Equipment (M&TE). NCSA-0330_004.A06 requirement #8a states in part, "If there is a deposit greater than a safe mass for systems conditions in the equipment, the pressure in the equipment shall monitored each shift and if the pressure is less than 14 psia it shall be adjusted with dry air or N2 to greater than 14 psia within 12 hours." Buffer pressure was increased to greater than 14 psia at 0425 hours. Remaining areas of the plant with similar conditions were checked and verified to be compliant with the 14 psia Buffer pressure requirement. SAFETY SIGNIFICANCE OF EVENTS: MODERATE, in this event the equipment was potentially without a buffer for 5 months which is insufficient time to allow enough water to enter the pipe and moderate the deposit to the level required to support a criticality. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): Sufficient moderation must be added to a deposit at > safe mass to potentially create a critical configuration. This is highly dependent on geometry and reflection conditions. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, FTC.): In this event, moderation is the only available control, and it was not maintained. Other parameters, like geometry and reflection, are assumed to be optimum. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Worst case 1549 pounds U02F2 +/- 50% (max. 2323 pounds) at 2.26% based on available Non-Destructive analysis Measurements. This mass is above the minimum critical mass (690 pounds U02F2 at optimum conditions) for this enrichment level. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Moderation Control was not maintained for up to 5 months, change in system configuration unknowingly isolated the deposit from pressure monitoring point. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: 0425 hours required buffer re-established, the valves involved were opened and tagged to remain open, verified remaining 4 like conditions were buffered as required. Investigation in progress. The licensee notified the NRC Resident Inspector and the on-site DOE representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-22
38304 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-09-22 00:39 | 2001-09-22 03:48 | 2001-09-22 | OFFSITE NOTIFICATION TO THE LOCAL AUTHORITIES DUE TO AN INCIDENT IN FRONT OF THE PLANT The licensee's security department contacted the local police department about an incident just outside the plant at the highway entrance about a quarter mile from the protected area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-22
38303 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2001-09-21 | 2001-09-21 17:25 | 2001-09-21 | AGREEMENT STATE REPORT INVOLVING POTENTIAL MEDICAL MISADMINISTRATION "Malfunction of Leksell Gamma Knife patient table. Possible misadministration to patient. Licensee is preparing a written report with more detail, corrective action, etc. "Patient being treated in a Gamma Knife unit rolled up against the table and table was unable to automatically retract from the Gamma Knife 'cave.' Licensee personnel were able to enter the room and manually remove the patient and table from the 'cave.' Personnel exposure estimated to be between 3 mr and 20 mr. Gamma Knife manufacturer (Leksell) has also been notified." Event Report ID No. NV-01-004. Event location Las Vegas, NV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2001-09-21
38302 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-09-21 11:00 | 2001-09-21 15:30 | 2001-09-21 | AGREEMENT STATE REPORT INVOLVING RAD CONTAMINATION DURING TRANSPORT "On August 24th at approximately 9:00 a.m. at the Medi-Physics facility located at 4877 Mercury Street. "A courier for Medi-Physics brought back some empty ammo containers from the morning deliveries. The containers were wiped upon receipt and it was discovered that one of the containers had removable contamination on the top of the container. From our phone conversation it appears that the level of removable contamination was approximately 300,000 DPM/ 100 cm2. The material was identified as Technetium-99. Medi-Physics will be submitting a letter with the details to my attention. The RSO at the hospital was contacted and he completed a survey to check for contamination at their facility. It is not known at this time the results of that survey. The courier's feet and the pedals of the vehicle also showed elevated levels of contamination." This information was reported to the San Diego Office on 9/21/01 at approximately 1100PDT. CA Event Report Identification XCA 85. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-09-21
38300 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-09-19 16:30 | 2001-09-20 15:15 | 2001-09-20 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER GAUGE "A Troxler model 3401B moisture density gauge (serial #016692) was run over by earth moving/compacting equipment while the gauge was in use (i.e., the source rod was extended). The source rod was bent such that the source could not be retracted into the shielded position. The unshielded source contained nominally 10 mCi of Cs-137. The source rod was cut by the fire department with the source in a lead 'pig' provided by the UC Santa Cruz health physics program. The source and the gauge housing will be sent to Troxler for repairs." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-09-20
38299 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-09-19 20:15 | 2001-09-19 22:12 | 2001-09-19 | BORIC RESIDUE BUILDUP Visual inspection of the Unit 2 Steam Generator 2B (SG 2B) lower head bowl drain during the current refueling outage indicated boron residue buildup on the 0.5" piping immediately below the SG. The total volume of residue was approximately 1 cubic inch. The origin appears to be the partial penetration of a weld between the reducing coupling and the lower head shell. Exact location could not be conclusively determined at this time and additional inspection using NDE will be conducted. Visual inspection of the other three SG's was also conducted and no indications of leakage were identified. State and Local officials will be given a courtesy call. The NRC Resident Inspector will be notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-09-19
38298 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-19 10:06 | 2001-09-19 18:36 | 2001-09-19 | NRC BULLETIN 91-01 24 NOTIFICATION During a meeting to discuss compensatory actions for PR-PTS-01-04202, additional concerns were raised regarding compliance with the requirements of NCSA-705-076. Specifically, exterior walls have openings (windows and gaps) which could allow uranium bearing solution to spray outside the facility and collect in an unfavorable geometry inadvertent container. A walk down was performed. The findings resulted in a violation of control # 3 of NCSA 705-76, inadvertent containers. Compliance with NCSA was reestablished with the closure of windows, caulking of identified openings and continued shutdown of system involved. SAFETY SIGNIFICANCE OF EVENTS: The safety significance is low because there was no leak of uranium bearing material! near the identified openings in the walls of the X-705. The two areas in question are designated as "Inadvertent Container Area" due to the presence of the Recovery System and Microfiltration, neither of which are currently in operation due to a stand down of all X-705 operations. The presence of an inadvertent container in the area is a violation of NCS controls and one leg of the double contingency principle as described in NCSE-0705 _076.E.03. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events would be required: The recovery system or Microfiltration would have to be operating and processing uranium bearing liquid with a high concentration of uranium. Then a leak in this system must occur such that an unsafe amount of liquid sprays from the system directly through an open window or through another penetration in the building wall. The liquid would then have to flow or drip into a potentially unfavorable geometry that may be present immediately adjacent to the outside building wall. Depending on the volume collected, some reflection would also be required to sustain a critical chain reaction The Recovery and Microfiltration systems are not currently in operation. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION. ETC.): Inadvertent containers are controlled based upon volume (2.5 liters maximum) or geometry (1.5 inches in depth or 4 inches in diameter). The exact potential collection volume for this event is unknown. Although analyzed for 100% enriched materials, the Recovery System would Currently process materiel with less than or equal to 5% enrichment ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium bearing material was involved in this event. There were no leaks of uranium bearing materiel in the area during this event. The event involves the presence of an unsafe geometry (via an opening in the building block wall) that could collect solution in the event of a spill. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The presence of holes in the exterior building walls could lead to the collection of a spill or leak in the unfavorable geometry space. This is a violation of control #3 of NCSA-0705_076, Inadvertent Containers, which specifically evaluates this event. Compliance with inadvertent container controls was reestablished for a shutdown Recovery system and for the Microfiltration system (running or shutdown) within four hours of discovery. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Compliance with the NCSA was reestablished with the closure of windows, caulking of identified openings and continued shutdown of Systems involved. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-19
38297 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-19 12:45 | 2001-09-19 15:04 | 2001-09-19 | AUTOCLAVE ISOLATION OTHER NON-CFR REQUIREMENT - 24 HOUR NOTIFICATION At 1245 hours on 09/19/01, both the "A" and "B" High Level Condensate probes activated on Autoclave # 3 in the X-334 uranium hexafluoride Sampling Facility causing a High Condensate Alarm. The activation of either of these probes will cause the autoclave steam supply valves ("Q" components) to actuate (close). The steam supply valves closed, as designed, autoclave # 3 was in TSR Mode 2 (Heating) at the time of the alarm activation. Operations personnel immediately responded to the alarm in accordance with the approved Alarm Response Procedures. The alarm reset when operations personnel drained excess condensate from autoclave drain line, and then acknowledged the alarm at the local autoclave control panel. All autoclave (and cylinder) operating parameters were determined to be within normal ranges. Autoclave # 3 was placed in TSR mode 7 (Shutdown) by operations personnel and declared inoperable by the Plant Shift Superintendent. Based on the actuation of both High Level Condensate probes, this event is being reported as a valid safety system actuation, a 24-hour NRC event. An Engineering Evaluation has been requested to investigate the circumstances surrounding this safety system actuation. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-19
38296 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2001-09-19 09:05 | 2001-09-19 10:16 | 2001-09-19 | STANDBY DIESEL GENERATOR FAILED TO START AND IS UNAVAILABLE The licensee reported that a standby diesel generator failed to start in manual and automatic during a test. The generator is unavailable as redundant for required safety function. The generator is being worked on. The plant is shutting down their processing until repairs are made. The licensee will submit a 30-day written report and is notifying NRC Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2001-09-19
38295 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-19 08:13 | 2001-09-19 09:00 | 2001-09-19 | OFFSITE NOTIFICATION REGARDING AN OPACITY VIOLATION (4-hour Report) The following text is a portion of a facsimile received from Portsmouth personnel: "At 0813 hours [on] 09/19/01, the Ohio Environmental Protection Agency (OEPA) was notified per Ohio Administrative Code (OAC) 3745-15-06(B) that an opacity exceedance had occurred at the X-600 Steam Plant. The opacity violation occurred on [the] #2 Boiler when our #2A Precipitator voltages began to fluctuate. Operators adjusted load/air requirements on the #2 Boiler in an effort to prevent further exceedances. [The] cause of the voltage fluctuations has not been determined at this time." "This is reportable as a 4-hour NRC Event due to notification to an outside agency (OEPA) being made per Nuclear Regulatory Reporting Procedure UE2-PAE1030, Appendix D, Criteria P (Miscellaneous)." Portsmouth personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-19
38294 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-18 14:04 | 2001-09-18 17:58 | 2001-09-18 | LOSS OF DOUBLE CONTINGENCY. NRC BULLETIN 91-01 4 HOUR NOTIFICATION At 1404 during facility stand down recovery efforts, a wall penetration for conduit lines above the A-loop concentrate slab was questioned as a possible violation on NCSA-0705_076, Inadvertent Containers. The concrete blocks used in the construction of the wall have internal void spaces which could accumulate an unsafe amount of material in the event of a spill or leak. The edges of the penetration were not sealed or covered to prevent solution from entering. If the feed pump for the A-loop concentrate slab were operating (X-705 operations are currently in stand-down mode), solution could potentially spray onto the conduit and run into the openings. The feed pump will remain administratively tagged out of service until the potential spray path is mitigated. Repairs are in progress. Following identification of the above event, a walkdown was conducted in all inadvertent Container Areas to locate any similar problems. Numerous cracks, holes, and penetrations were identified in the block walls of the Recovery Area. Small cracks and joints in the walls are not considered a violation of the NCSA controls because it is not credible that an unsafe amount of material could seep through a crack in a (vertical) wall and collect in an unsafe geometry. However, many holes were observed that could potentially collect an NCS significant amount of material if a spray or leak stream were to be aimed directly at the hole. This is a violation of the administrative controls of NCSA-0705_076 for Inadvertent Containers. Due to the number of penetrations/holes identified by subsequent walkdowns of the Recovery Area, compliance with NCSA controls could not be reestablished within 4 hours. Thus making this event a criticality control 4-hour 91-01 bulletin event. The safety significance is low because there was no leak of uranium bearing material near the identified openings in the walls of the Recovery Area. A walkdown of the Microfiltration Area and Tunnel Basement Area (also subject to Inadvertent Container controls) did not find any violations of NCS controls. SAFETY SIGNIFICANCE OF EVENTS: The safety significance is low because there was no leak of uranium bearing material near the identified openings in the walls of the Recovery Area. The area in question is designated an "Inadvertent Container Area" due to the presence of the Recovery System, which is not currently in operation due to a stand down of all X-705 operations. The presence of an inadvertent container in the are is a violation of NCS controls and one leg of the double contingency principle as described in NCSE-705_076.E03. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(s) OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events would be required: The recovery system would have to be operating and processing uranium bearing liquid with a high concentration of uranium. Then a leak in the system must occur such that an unsafe amount of liquid sprays from the system directly into one of the identified openings in the block wall. The liquid would then have to flow through the small opening and collect in the internal void spaces of the block wall forming an unsafe geometry. Depending on the volume collected, some reflection would also be required to sustain a critical chain reaction. The Recovery System is not currently an operation, and will remain shutdown until the holes/penetrations are mitigated. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Inadvertent containers are controlled based upon volume (2.5 liters maximum) or geometry (1.5 inches in depth or 4 inches in diameter). The exact potential collection volume inside the block wall is unknown. Although analyzed for 100% enriched materials. The Recovery System would currently process material with less than or equal to 5% enrichment. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium bearing material was involved in this event. There was no leaks of uranium bearing material in the area while the opening in the walls were present. The event involves the presence of an unsafe geometry (the inside of the block wall) that could collect solution in the event of a spill. NUCLEAR CRITICALITY SAFETY CONTROL(s) OR CONTROL SYSTEM(s) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The presence of holes in the block walls could lead to the collection of a spill or leak on the unfavorable geometry void spaces. This is a violation of control # 3 of NCSA-0705_076, Inadvertent Containers, which specifically evaluates this event. Note that it was not possible to mitigate all of the holes in the Recovery Area walls; therefore, Recovery operations remain shutdown until expedited repairs can be completed. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Feed pump for the A-loop concentration slab will remain tagged out of service until the potential path is mitigated. The NRC Resident Inspector was notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-09-18
38293 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-09-18 09:50 | 2001-09-18 15:13 | 2001-10-18 | LOCAL LEAK RATE TESTING (LLRT) OF MAIN STEAM ISOLATION VALVE (MSIV) "2B" LIMITS EXCEEDED. During LLRT of MSIV's per appendix J of 10CFR50 the "2B" 21F022A and "2B" 21F028A were found to be leaking 192 scfh (standard cubic feet per hour); diagnostic testing determined that "2B" 21F022A is leaking at approximately 130 scfh. (Technical Specification Surveillance requirement limit is 100 scfh). The "2B" 21F022B was found to be leaking above 100 scfh and above the maximum pathway allowable leakage of 250 scfh for all four lines. The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTION 2203 10/18/2001 FROM WATTS TAKEN BY STRANSKY * * * "On 9/18/01 at 15:13 EDT Plant Hatch made a Notification of Significant Event Report number 01-12 to the NRC (Mr. MacKinnon). The 50.72(b)(3)(ii)(A) report was made for failure of the MSIVs to pass Local Leak Rate Testing (LLRT). The initial test of the penetration 2B21F022A and penetration 2B21F022B leaked greater than the Technical Specification Surveillance Requirement 3.6.1.3.11 of 100 SCFH. Also, the leakage through the 2B21F022B was sufficient to be greater than the same Technical Specification Surveillance Requirement 3.6.1.3.11 of 250 SCFH for all four Main Steam lines. At the time of this notification the actual as found leakage through each penetration pathway could not be determined because the test is conducted between the valves in each penetration. "Per the Event Report Guidelines in NUREG-1022, the containment leak tests where the total containment as found, minimum-pathway leak rate exceeds the LCO in the facilities Technical Specifications would be reportable. The minimum-pathway leak rate means the minimum leak rate that can be attributed to a penetration leakage path. The NUREG-1022 explains for example, the smaller of either the inboard or outboard valve's individual leak rates. Therefore, after repairing the 2B21F022B and the 2B21F028A and before the repair of the other valves (one inboard and one outboard) another LLRT was performed for each penetration pathway. These LLRT results showed that the minimum-pathway leak rate did not exceed the Technical Specification Surveillance Requirement 3.6.1.3.11 of 100 SCFH for either penetration pathway. Also, the minimum-pathway leak rate for all four Main Steam lines did not exceed the Technical Specification Surveillance Requirement 3.6.1.3.11 of 250 SCFH." The NRC resident inspector has been informed of this retraction. Notified R2 IRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-09-18
38292 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2001-09-10 16:16 | 2001-09-18 10:22 | 2001-09-18 | INADVERTENT ACTUATION OF SPECIFIED SYSTEM - SECONDARY CONTAINMENT ISOLATION AND STANDBY GAS TREATMENT SYSTEM "This 60-day optional report. as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically Secondary Containment Isolation and Standby Gas Treatment System. "On September 10, 2001, a lightning storm struck the Peach Bottom Atomic Power Station and resulted in a trip of the 2B Reactor Protection System (RPS) Motor Generator (MG) set due to a blown fuse. As a result of the loss of the 2B RPS power supply, the Secondary Containment outboard isolation valves closed and the Standby Gas Treatment system automatically started. "The Secondary Containment outboard isolation valves and the Standby Gas Treatment responded as expected for the given conditions. Both systems were subsequently returned to their normal configuration per plant procedures. No deficiencies were noted during actuation of either system. "This event has been entered into the site-specific corrective action program for resolution. "The NRC resident has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-09-18
38291 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-09-17 12:05 | 2001-09-17 19:05 | 2001-09-17 | LOSS OF NON-SAFETY RELATED 125 VOLT DC BUS RESULTED IN BOTH MOTOR DRIVEN AUXILIARY FEEDWATER PUMPS STARTING. During routine scheduled maintenance activities, power was lost to a non-safety related 125 volt DC bus. Loss of power to the bus resulted in loss of oil pressure indication on 1 of 2 channels on both main feedwater pumps, which in turn resulted in the actuation of both motor driven auxiliary feedwater pumps. The motor driven auxiliary feedwater pumps ran for approximately 3 minutes. Reactor power increased but no over power event occurred. Power has been restored to the non-safety related 125 volt bus and the motor driven auxiliary feedwater pumps have been secured. The licensee is looking into that maybe when cross connecting the 125 volt DC buses that one of the two fuse disconnect switches might have had a blown fuse which would have resulted in the above event. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-09-17
38290 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-09-16 19:00 | 2001-09-16 23:15 | 2001-09-16 | OFFSITE NOTIFICATION DUE TO EXCEEDING NPDES PERMIT LIMIT FOR CHLORINE DISCHARGE At approximately 1100EDT on 9/16/01 a grab sample of the plant effluent cooling water was taken and analyzed. The overboard concentration of chlorine which is added as a antifouling agent was measured at .21 mg/l which is .01 higher than the allowed National Pollution Discharge Elimination System (NPDES) permit limit of .2 mg/l. The discharge occurred between 1118EDT and 1144EDT on 9/16/01. Steps were taken to adjust chlorine levels to .03 mg/l. This violation was reported by the licensee to the NJ DEP. The licensee will inform the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-16
38289 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-09-16 09:05 | 2001-09-16 18:20 | 2001-09-16 | 24-HOUR FITNESS-FOR-DUTY REPORT A non-licensed supervisor was determined to be under the influence of alcohol during a for cause test. The employee's access to the plant has been suspended. The licensee informed the NRC resident inspector. Contact the Headquarters Operation Center for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2001-09-16
38287 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2001-09-13 10:45 | 2001-09-14 16:06 | 2001-09-14 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER GAUGE "On 9/13/01 at 1045MST, a smooth barrel compactor ran over a Troxler Electronic Laboratories Incorporated Model 4640-B thin layer density gauge (serial number 1580, containing 8 millicuries of Cesium-137). As a result, the source rod was damaged (bent) and could not be returned to the safe shielded position. The event location was 7765 Highway 89, Willard, Utah. "The Utah Division of Radiation Control was notified by the licensee on 9/13/01 at 1100MST. A Utah Division of Radiation Control inspector was sent to investigate the incident (Utah Event Report ID No. UT-01-0003)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2001-09-14
38286 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2001-09-13 17:48 | 2001-09-13 19:11 | 2001-09-13 | PRESS RELEASE INVOLVING AN INJURED CONSTRUCTION WORKER "The following is a press release issued by a construction company that is working on a construction project at Wolf Creek Generating Station. The project is associated with a training center outside the protected area but inside the owner controlled area. The Senior Resident has been notified. This four-hour notification is being made pursuant to 10CFR50.72(b)(2)(xi). " 'BURLINGTON, Kan.--A workman performing metal building erection on a training center renovation located just outside the Wolf Creek Generating Station fell 20 feet to the ground sustaining multiple injuries. The workman, who worked for Total Construction Enterprises located in St. Louis, Mo., was flown out via Life Star to a Topeka hospital for treatment. The name of the workman is not being released nor is his medical status known at this time.' " | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-13
38285 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2001-09-13 12:45 | 2001-09-13 14:17 | 2001-09-13 | OFFSITE NOTIFICATION INVOLVING CONTAMINATED SCAFFOLD KNUCKLES "While performing incoming routine surveys, Turkey Point Health Physics personnel discovered low levels of radioactivity on several pieces of scaffolding knuckles and elbows received from a vendor. The knuckles never entered the site's radiation controlled area. These items were counted in a Small Articles Monitor (SAM) and indicated low level contamination was present. In total 3 out of approximately 2700 items surveyed indicated the presence of low level fixed activity. The highest level measured was 9,800 disintegrations per minute (dpm) when counted in the SAM and non-detectable using a standard HP-210 (pancake GM) probe. Isotopic analysis indicates Cobalt-60 and Cesium-137. No loose surface contamination was found. The items identified with low level fixed contamination are now being held inside the Turkey Point radiation controlled area. "Florida Power & Light Company has notified the owner of the scaffolding and the State of Florida (Department of Health, Bureau of Radiation Control) of this matter." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-13
38284 | 0 | BATTELLE MEMORIAL INSTITUTE |  |  |  | ADVANCED FUEL R&D AND PILOT PLANTS | 2001-09-13 09:25 | 2001-09-13 09:39 | 2001-09-13 | UNUSUAL EVENT DECLARED DUE TO CONTAINED FIRE. Unusual event was declared because of a small contained fire, now out, in High Energy Cell (HEC) lasting less than 10 minutes. A "berry can" was being ground open in order to dispose of some combustible material. The grinding caused the contents inside the can to catch fire. The fire remained within the can until it burnt itself out. First water was sprayed into the can to extinguish the fire but the flames got larger so the licensee let the fire burn itself out. The max. flame height was approximately 18 inches. The "berry can", which looks like a one gallon paint can, was located in a 20 foot high hot cell located in building JN-1B. There was no release and nobody was injured. Smears taken detected no radioactivity except for radon which was caused by an atmospheric inversion. Any gases released within the hot cell must go through a HEPA filter. The licensee notified NRC Region 3, the DOE Project Manager, and local officials of this event. * * * UPDATE ON 09/13/01 AT 1026 ET BY C. JENSEN TAKEN BY MACKINNON * * * Unusual event terminated at 0957 ET based on negative air samples. R3DO (Sonia Burgess), NMSS (Fred Brown) and FEMA (Barden) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 3 | OH | FUE |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-09-13
38282 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-09-13 | 2001-09-13 02:00 | 2001-09-13 | INFORMATION REPORT IN ACCORDANCE WITH NRC INFORMATION NOTICE 98-35 A suspicious vehicle was noted in area around the plant site. Immediate compensatory actions were taken upon discovery. Contact HOO for further details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW | [5 empty] | 0 | 2001-09-13
38281 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-09-12 18:13 | 2001-09-12 20:53 | 2001-09-12 | AUTOMATIC REACTOR TRIP DUE TO TURBINE/GENERATOR TRIP The plant sustained a turbine/generator trip resulting in a reactor trip, all rods inserted fully, all systems functioned as required unless otherwise noted, and the plant is stable in MODE 3 (Hot Standby). Main feedwater was lost due to a loss of power to the secondary pumps. Power is being supplied from the startup transformer, reactor coolant system is in forced circulation, emergency feedwater is supplying the steam generators, and turbine bypass valves to the condensers are providing a heat sink. The licensee is investigating the cause of the turbine/generator trip and the loss of power to the secondary pumps. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-09-12
38280 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-09-12 08:17 | 2001-09-12 19:57 | 2001-09-12 | FITNESS FOR DUTY REPORT A licensed employee was determined to be under the influence of alcohol during a for-cause test. The employee's access to the plant has been terminated. The NRC resident inspector has been informed of this event by the licensee. Contact the NRC Operations Center for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.73 |  |  |  | 0 | 2001-09-12
38279 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-09-12 08:00 | 2001-09-12 16:36 | 2001-09-12 | ACCESS DENIED A contract employee was determined to be under the influence of alcohol during a for-cause test. The employee's access to the plant has been denied. The NRC Resident Inspector was notified of this event by the licensee. Contact the Headquarters Operation Center for further details. | 90 | 96 | 0 | 90 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2001-09-12
38278 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-09-11 16:30 | 2001-09-11 20:09 | 2001-09-11 | PRESS RELEASE MADE CONCERNING THE HEIGHTENED STATE OF SECURITY AT THE SITE The licensee made a press release concerning the heightened state of security at the site as directed by the NRC. There has been no credible general or specific threats to Plant Farley. The press release also related that security is normally very tight and drills are regularly conducted to insure the security of the plant. They went on to inform the public that the visitors would be restricted from the plant site until further notice. The licensee notified the state and the NRC Resident Inspector that a press release had been made. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-11
38277 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2001-09-11 13:00 | 2001-09-11 19:40 | 2001-09-11 | INFORMATION REPORT IN ACCORDANCE WITH NRC INFORMATION NOTICE 98-35 The licensee reported the finding of a body at a state park near the licensee's location, but outside the owner controlled area. There is no indication of a connection to ongoing events in the nation. The licensee notified the NRC Resident Inspector. Contact the HOO for further information. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2001-09-11
38276 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-09-11 15:30 | 2001-09-11 16:15 | 2001-09-11 | SUSPICIOUS PERSONS IN AREA AROUND PLANT SITE. IMMEDIATE COMPENSATORY ACTIONS TAKEN UPON DISCOVERY. CONTACT HEADQUARTERS OPERATION OFFICER FOR FURTHER DETAILS. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-09-11
38275 | -1 | CLARK MEMORIAL HOSPITAL |  |  |  |  | 2001-09-11 07:00 | 2001-09-11 15:17 | 2001-09-12 | MISSING 94 PALLADIUM SEEDS. Licensee received, in the mail, a box containing 94 palladium seeds with a total activity of 119.14 millicuries on Friday, 09/0701 at approximately 1200 ET. The box containing the seeds was locked in the Hot Lab at approximately 1700 hours on 09/07/01. Saturday morning it was noticed that the box containing the palladium seeds was missing. It was assumed that the box of seeds had been picked up. Today, 09/11/01, at 0700 hours a Radiation Physicist came to pick up the box of palladium seeds. At this time it was realized that the seeds were missing. A search of the hospital areas, trash, etc., was performed and the seeds were not found. The hospital security and the Jeffersonville Police department were notified of the missing palladium seeds. * * RETRACTION ON 09/12/01 AT 0943ET BY TRINNA WALKER TAKEN BY MACKINNON * * * This event is being retracted since a cyclotron was used to irradiate the palladium seeds. R3DO (Sonia Burgess) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-09-11
38274 | 0 | PRIVATE CITIZEN |  |  |  |  | 2001-09-10 17:00 | 2001-09-11 07:47 | 2001-09-11 | AN UNATTENDED TRUCK HAULING A NUCLEAR WASTE CONTAINER WAS PARKED ON A SERVICE ROAD OVERNIGHT. A concerned citizen notified the NRC of a truck owned by Hittman Trucking Co that has been parked on a service road at the intersection of Suitland, Rd. and Route 4 in Prince George's County, Md. The truck had been left unattended since at least 1700 on 9/10/01. The caller noticed the radiation placards on the container, but did not identify any readings on the placards. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | MD | TRA | [5 empty] | 0 | 2001-09-11
38273 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-09-07 17:54 | 2001-09-10 23:13 | 2001-09-10 | LOSS OF OFFSITE POWER SOURCES DUE TO LIGHTNING "On 9/7/01 at 1750 CDT the Startup Transformer was de-energized due to a lightning strike on the transmission system. This deenergized one of the two off-site circuits. This trip resulted in the trip of 'A' Recirculation M/G set and subsequent single loop operations. Shortly after this at 1754 CDT the Emergency Transformer was declared inoperable due to degraded voltage and the plant entered the Limiting Condition for Operations for loss of both off-site power circuits. Both Emergency Diesels remained available and the unit remained on line. All plant equipment responded as expected. At 1932 CDT the Emergency Transformer was returned to operable status. Two loop operations were restored at 0521 CDT on 9/8/01. The Startup Transformer was restored to operable at 1045 CDT on 9/8/01. Full power operation was restored at 2100 CDT on 9/8/01. The NRC Senior Resident Inspector has been notified. This event is reportable in accordance with NUREG 1022 Rev. 2 and 10 CFR 50.72(b)(3)(v). Staff review of the event and NUREG 1022 Rev. 2 on 9/10/01 identified the need to make a report under 10 CFR 50.72." | 62 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-09-10
38272 | 0 | U.S. DEPARTMENT OF AGRICULTURE |  |  |  |  | 2001-09-06 11:00 | 2001-09-10 16:48 | 2001-09-10 | STUCK SOURCE The licensee reported that a 15 mCi Am-241 source, used for soil moisture measurements, had become stuck within a 6 foot length of tubing. Attempts to retrieve it using the attached cable were unsuccessful. The source was retrieved by digging up the tubing, cutting off the bottom portion and pushing the source back up through the tube. The source was returned to its shipping container. The dosimetry of the individual who performed the retrieval has been sent to the vendor for analysis. An inspector from NRC Region I is currently performing a site visit to the USDA office in Beltsville, MD, from where this report originated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | OR | MAT | [5 empty] | 0 | 2001-09-10
38271 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2001-09-06 11:00 | 2001-09-07 18:31 | 2001-09-12 | MISSING TROXLER DENSITY GAUGE. Western Technologies, out of Albuquerque, accidentally left a 3430 Troxler moisture density gauge at mile marker 49 on US highway 550. The moisture density gauge was out of its transport case laying on the side of the highway when the it was left behind. The driver immediately, within an hour, returned to the location and discovered that the gauge was missing. State of New Mexico has recommended to the licensee that they offer a reward for the missing gauge. * * * UPDATE 1851 9/12/2001 FROM MILLER TAKEN BY STRANSKY * * * The state reported that the missing gauge has been recovered. Notified R4DO (Shaffer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2001-09-07
38270 | 0 | MADISION MEMORIAL HOSPITAL |  |  |  |  | 2001-09-06 13:30 | 2001-09-07 18:03 | 2001-09-07 | PATIENT GIVEN TECHNETIUM-99 MDP INSTEAD OF MYOVIEW. Nuclear Medicine Technologist placed a vial that he thought contained technetium-99 myoview into a carrier and took it across the hallway. He administered 32.2 millicuries of technetium-99 MDP instead of 32.2 millicuries of technetium-99 myoview to a patient walking on a tread mill. The nuclear Medicine Technologist discovered that the patient received the incorrect technetium while imaging the patient. The Nuclear Medicine technologist notified the radiologist of the error but has not contacted the patient or the patients physician. The patient's physician left for the weekend after the technetium-99 myoview had been administered to the patient. No harm to the patient due to incorrect technetium given to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 35.33 |  |  |  | 0 | 2001-09-07
38269 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2001-09-07 00:24 | 2001-09-07 03:30 | 2001-09-07 | MANUAL REACTOR SCRAM DUE TO 2 LOW PRESSURE HEATER STRINGS ISOLATING The following is taken from a facsimile report: This report is being made per 10CFR50.72(b)(2)(iv)(B) RPS actuation (scram) (4 hour notification for U-2). At 12:24 AM CDT, Friday 9/7/01, U-2 was manually scrammed. The initiating event was a loss of 2 of 3 Low Pressure Feedwater Heater Strings. A high level condition was initially received in the 21A Low Pressure Heater, which caused the Condensate System inlet and outlet isolation valves to the 2A Low Pressure Heater String to close. Subsequently, a high level condition was also received in the 21C Low Pressure Heater, which caused the Condensate System inlet and outlet isolation valves to the 2C Low Pressure Heater String to close. With a second Low Pressure Heater String isolated, Unit 2 was manually scrammed in accordance with LaSalle Procedure LOA-HD-201, "Heater Drain System Trouble". All systems operated as designed. There were no ECCS actuations or Primary Containment isolations. The lowest Reactor level reached was minus 20 inches (141 inches above the top of active fuel) and was recovered to normal level using feedwater. Reactor pressure responded normally. No Safety Relief Valves actuated. All Control Rods fully inserted. The NRC Resident Inspector has been notified. The cause of the Low Pressure Heater String loss is being investigated at this time. | 0 | 0 | 0 | 0 | 72 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-09-07
38268 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-09-06 17:38 | 2001-09-07 00:47 | 2001-11-05 | REACTOR CORE ISOLATION COOLING SYSTEM MADE INOPERABLE "Columbia Generating Station Reactor Core Isolation Cooing (RCIC) system has been isolated and made inoperable per Technical Specification 3.5.3 and unavailable due to manual closure of the RCIC turbine trip valve. The manual closure of the RCIC turbine trip valve was required due to the loss of automatic trip capability of the turbine trip valve [due to a solenoid failure]. This loss of automatic trip capability under postulated conditions could cause a water hammer event significant enough to threaten primary containment. "The RCIC system is a single train system and is listed in plant procedures as an Engineered Safety Feature (ESF). "The RCIC system will function automatically or manually to inject water into the RPV if manually returned to service." The licensee notified the NRC Resident Inspector. * * * RETRACTED AT 1635 EST ON 11/5/01 BY ROBERT SHERMAN TO FANGIE JONES * * * "Retraction for EN #38268, Regarding Closure of RCIC System Trip and Throttle Valve RCIC-V-1, November 5, 2001 "Automatic closure of the RCIC trip and throttle valve (RCIC-V-I) on low pressure in the RCIC pump discharge piping (i.e.., conditions in which voiding could be present in the RCIC pump discharge piping) prevents waterhammer by preventing automatic start or restart of RCIC. The closure of RCIC-V-1 under these conditions serves as a redundant and diverse backup to the closure of the RCIC pump discharge check valve RCIC-V-90. When it was discovered that RCIC-V-1 failed to close upon receipt of a system trip or valve close signal, system check valve RCIC-V-90 was determined to be operable thereby preventing conditions that could potentially result in waterhammer. Therefore, the condition of RCIC-V-1 failure to close upon receipt of a trip or close signal did not create a condition that could have resulted in potential waterhammer damaged to RCIC piping and containment." The licensee notified the NRC Resident Inspector. The R4DO (Linda Smith) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-09-07
38267 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-08-29 12:00 | 2001-09-06 15:15 | 2001-09-06 | AGREEMENT STATE REPORT: MISSING NDC DENSITY GAUGE Today Smurfit-Stone Container Corporation faxed a copy of a letter to the State of Florida Bureau of Radiation Control stating that a device was missing; NDC, Mass Monitor, Model # 104. The former Florida Coast Paper facility had several fixed radioactive sources when it went bankrupt in 1998. It was purchased by Smurfit-Stone and the radioactive sources have all been removed with the exception of this source. It was a portable device that had been kept in a locked steel toolbox within a locked laboratory. It was last seen in late June. Numerous contractors have been on site engaged in the removal of equipment prior to mill demolition. Mill personnel have searched the mill repeatedly and now suspect that the device was removed by one of the contractors. All facilities that have received equipment from the mill have been asked to search for the device. Florida is investigating this incident. Florida incident number for this event is FL01-095. The NDC Mass Monitor contained 30 millicuries of americium-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2001-09-06
38266 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-06 06:00 | 2001-09-06 10:52 | 2001-09-06 | 4 HOUR REPORT - NRC BULLETIN 91-01 The following is taken from a facsimile report: At 0600, on 9-06-01, the Plant Shift Superintendent (PSS) was notified that moisture sampling results on Unit 1 Cell 2 even R-114 system in building C-337 were above allowable limits of NCSA CAS-011. NCSA CAS-011 sets the limit for moisture content in R-114 at 1760 ppm. The sample results showed that the actual moisture content in C-337 Unit 1 Cell 2 even R-114 system was 2100 ppm. Set point calculations for the R-114 moisture meters used by Cascade personnel to determine the moisture content of R-114 for Cascade coolant systems was found biased low with respect to moisture content. The meters are used to detect high moisture levels in the R-114. An R-114 system containing a high moisture content is required to be independently verified drained prior to removing the fluorinating process environment. Since the setpoint calculation was potentially in error, R-114 with a potentially high moisture content was not immediately drained according to NCSA CAS-002. This control prevents a moderating environment within the process gas system from exceeding 50% relative humidity at 70 degrees F. The NRC Acting Senior Resident has been notified of this event. SAFETY SIGNIFICANCE OF EVENTS: The final determination of whether the moisture content limit has been exceeded cannot be made until the moisture meter "as-found" calibration data can be reviewed. This data a not currently available. However, the plant is pro-actively taking the compensatory actions as though the moisture meter were in error until such time as the calibration data can be reviewed as a final determination made. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible a fissile deposit containing greater than a critical mass would have to absorb greater than 10 kg of water. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC: Two controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): No known deposits of concern at this time. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Double contingency for this scenario is established by implementing two controls on moderation. The first leg of double contingency is based on immediately draining the R-114 upon determination that it contains a high moisture content. The set point calculation derived for the R-114 moisture meter was biased low with respect to moisture content. Due to the set point calculation error the R-114 system was not immediately drained as required by the NCSA which may have allowed an unknown quantity of water to enter the process system. Since the quantity of water in-leakage to the process system cannot be quantified the process condition was exceeded and double contingency was not maintained. The second leg of double contingency is based on independently verifying the immediate draining of the R-114 upon determining that it contains a high moisture content. The set point calculation derived for the independent R-114 moisture meter was biased low with respect to moisture content. Due to the set point calculation error the R-114 system was not independently verified as being immediately drained as required by the NCSA which may have allowed an unknown quantity of water to enter the process system. Since the quantity of water in-leakage to the process system cannot be quantified the process condition was exceeded and double contingency was not maintained. Since double contingency is based on two controls on moderation, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The R-114 system is in the process of being drained. The process system will then be sampled for R-114 per CP3-CO-C02029 and appropriate actions contained therein will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-09-06
38265 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-09-04 14:00 | 2001-09-04 18:09 | 2001-09-12 | 24-HOUR 91-01 BULLETIN RESPONSE At 1400, on 9/4/01, the Plant Shift Superintendent (PSS) was notified of an NCSA violation that had occurred at the C-355 air plant. Immediately after switching drying units at the air plant, a high-high moisture alarm was received. The alarm indicated air moisture content greater than 1300 ppm water, violating NCSA GEN-10-01. NCSA GEN-010 credits the dry air system for producing dry air with moisture content of less than 1300 ppm. The purpose of this requirement is to prevent exposure of fissile uranium deposits to a moderating environment. No equipment containing fissile material was exposed to high moisture content plant air at the time of the alarm or following receipt of the alarm. Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hr. event report. SAFETY SIGNIFICANCE OF EVENTS: There was no purging of equipment containing fissile material in progress at the time of the moisture excursion. Although a parameter was exceeded, the proper response to the alarm was taken prior to resuming buffering of purging equipment containing fissile material. POTENTIAL CRITICALITY PATHWAYS INVOLVED(BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible. Operations personnel would have had to fail to respond to the alarm. In addition, a fissile deposit containing greater than a critical mass and absorbing greater than 10 kg of water would have had to be present. CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION. ETC: Double contingency for this scenario is established by implementing two controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): n/a NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Double contingency for this scenario is established by implementing two controls on moderation. The first leg of double contingency Is based on receiving a high-high moisture alarm indicating a moisture content greater than 1300 ppm water and ceasing buffering and purging operations in response to the alarm. This control was not violated. The second leg of double contingency is based on the dry air system producing plant air with a moisture content less than 1300 ppm water. Since the moisture content was confirmed to be greater than 1300 ppm, this process condition was exceeded and double contingency was not maintained. Since double contingency is based on two controls on moderation, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: No corrective actions implemented. Proper procedure response was performed. The NRC Resident Inspector was notified. * * * UPDATE ON 09/12/01 AT 1455 ET BY PITTMAN TAKEN BY MACKINNON * * * Criticality Safety Incident Report NCS-INC-01-022 has been revised to include information from EN-C-826-01-039 that documented that the moisture content did not exceed the NCS limit of 1300 ppm. Since the moisture limit for the plant air system was not exceeded, no violation occurred. R3DO (Sonia Burgess) notified. The NRC Resident Inspector was notified of this update by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-09-04
38264 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-09-04 15:00 | 2001-09-04 17:00 | 2001-09-04 | FAILURE OF 17 OUT OF THE 49 EMERGENCY NOTIFICATION SYSTEM SIRENS FOR CALVERT COUNTY The licensee reported that 17 out of 49 sirens in Calvert County failed to respond to the scheduled county test.. However, all sirens did respond to a mobile siren test kit which is used locally at the siren. Calvert County Emergency Management was notified to perform route alerting in the affected areas in the event of an emergency. The cause is believed to be a transmission problem. The NRC Resident Inspector will be notified. The county has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-09-04
38263 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-09-04 13:04 | 2001-09-04 16:54 | 2001-09-20 | REACTOR MANUALLY TRIPPED FROM 100% POWER DUE TO STEAM GENERATOR LEVEL APPROACHING THE LO-LO LEVEL SETPOINT While operating at 100% power, the Watts Bar Unit 1 reactor was manually tripped at approximately 1304 EDT on September 4, 2001 due to steam generator (SG) level approaching the Lo-Lo level setpoint. Just prior to the manual trip of the reactor, an abnormal voltage alarm was received on 125V Vital Battery Board 1-1. The immediate cause of the trip is considered to be the loss of the 1-1 Vital AC Inverter which caused a feedwater regulating valve to close. Subsequently, the maintenance power supply was used to restore power to the 1-1 vital AC bus. All control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated as expected. However, subsequent to the initial actuation signal, additional operator action was required to[manually] start 1B motor driven pump. After the 1B pump was successfully started, the motor driven AFW pump 1A was secured based on instrument indications available to the operating staff. After power was restored to the vital AC bus, the 1A pump was subsequently started and performed properly. Inspections are currently underway to determine the exact cause of the loss of the 1-1 Vital Inverter and basis for the 1B pump failing to [auto] start. No ECCS injection occurred, but the steam generator atmospheric relief valves lifted and fully reseated. The manual actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv). The actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv). The plant is stable in mode 3. The NRC Resident Inspector was notified. * * * UPDATE 1244EDT ON 9/20/01 FROM CHARLES TOUCHSTONE TO S. SANDIN * * * The following information was received as an update: "This report supplements the report made by TVA at approximately 1654 on September 4, 2001 - NRC Event Report 38263. "Description of Event: "While operating at 100% power, the Watts Bar Unit 1 reactor was manually tripped at approximately 1305 EDT on September 4, 2001, due to the level of Steam Generator (SG) Number 1 approaching the low-low level setpoint. The immediate cause of the trip is considered to be the loss of the 1-I Vital AC Inverter which caused the Number 1 SG feedwater regulating valve to close. Subsequently, the maintenance power supply was used to restore power to the 1-I Vital AC board. "10 CFR 50.72 Notification: "Initial notification to NRC of the reactor trip was made by WBN Operations at 1654 EDT The manual actuation of the Reactor Protection System (RPS) was reported as a four hour report under 10 CFR 50.72 (b)(2)(iv). The actuation of the Auxiliary Feedwater System (an engineered safety feature) was reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv). This report supplements the initial report and is being reported under the same criteria. "Cause of the Event: "The root cause of the reactor trip was the failure of the sensing/current limiting card installed in vital battery charger 6-S or its associated edge connector. The failure of the component resulted in the DC output of the charger rising to 209V. The high DC output voltage resulted in a high input to inverters 1-I and 2-I. Inverter 1-I input and output fuses were blown, while inverter 2-I continued without failure. This occurred because inverter 1-I is equipped with parallel 5 and 15 KVA constant voltage transformers (CVTs), which are more sensitive to high input voltage than the type used in inverter 2-1 which utilizes a single 20 KVA CVT. The inverters are rated for a maximum input of 140 volts. "Equipment Response: "All control rods inserted properly in response to the reactor trip. For WBN, the AFW system consist of a turbine driven AFW (TDAFW) pump and two trains (Train A and Train B) of motor driven AFW (MDAFW) pumps. The design calls for the MDAFW arid TDAFW pumps to start due to the loss of both Main Feedwater (MFW) pumps or an AMSAC actuation, In addition, the MDAFW pumps will actuate on low-low S/G level in any S/G and the TDAFW pump will actuate on low-low level in any two S/Gs. For this event, actuation of the TDAFW pump resulted from the required logic being met for SGs Number 1 and 4. Based on data obtained subsequent to the reactor trip, an auto start for the TDAFW train was initiated immediately after S/G low-low level setpoints were met. "Subsequent to the initial AFW actuation signal, additional operator action was required to start the 1A-A and 1B-B motor driven pumps. For the Train A MDAFW, the pump did not receive an auto start signal due to the loss of Vital Board 1-I. This resulted from the power for the signal generating circuit being lost with the Vital Board. The evaluation performed to establish the cause for the Train B MDAFW not starting found that the breaker for the pump did not close as a result of the automatic signal initiated by the low SG level. The breaker was subsequently tested and performed as designed and therefore, no conclusive cause was found for the breaker not closing. However, it was established that the most likely cause of the problem was dirty relay contacts on the 1X and 30RX relays." The licensee informed the NRC resident inspector. Notified R2DO(Sparks). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-09-04
38262 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2001-09-03 17:28 | 2001-09-03 22:02 | 2001-09-03 | REACTOR MANUALLY SCRAMMED FROM 100% DUE TO LOW VESSEL LEVEL This report is being made per 10CFR50.72(b)(2)(iv)(B) RPS actuation (4 hour notification for U-2), 10CFR50.72(b)(2)(iv)(A) ECCS Injection/Actuation (4 hour notification for Unit 2), and 10CFR50.72(b)(3)(iv)(A) System Actuation not including RPS (8 hour notification for Unit 1 and 2). At 1728 CST. Monday, 9-3-01,U-2 was manually scrammed. Initiating event appears to be a loss of Bus 241Y, which resulted in a loss of feedwater. The reactor was manually scrammed at approximately 20 inches before the automatic scram setpoint for low vessel water level. All rods fully inserted. The Reactor Core Isolation Cooling (RCIC) and High-Pressure Core Spray (HPCS) systems automatically started and injected and restored Reactor Pressure Vessel (RPV) level. A primary containment-level 2 isolation occurred and the Reactor Recirculation pumps tripped at minus 50 inches as expected. Unit 1 was affected due to standby gas treatment auto start and the reactor building vent system isolation. The lowest Reactor water level reached was minus 55 inches (106 inches above the top of active fuel) as indicated by the Division 2 instrumentation and was recovered to normal level with RCIC and HPCS within a few minutes. Approximately 10,000 gallons of water was injected. Bus 241Y was automatically re-energized from the (0) Common Diesel Generator. Dry-well pressure increased due to the expected loss of primary containment cooling. The highest pressure reached was approximately (1) one psig. Primary Containment Cooling has been restored. There are no indications of a leak inside the primary containment. RPV pressure is being controlled at 800 to 1000 psig by the use of RCIC. Main Steam Line drains, and manual operation of Safety Relief Valve (as necessary). RPV level has been restored to normal and feedwater is being used. Subsequent in the Reactor Scram, the 2A RHR Pump failed to start when manually initiating from the Main Control Room (for suppression pool cooling). System isolations have been restored with exception of reactor water cleanup and the Reactor Recirculation Hydraulic Power Units on U-2. The station is taking action to investigate the cause of the initial loss of 241Y and the unrelated failure to start of the 2A RHR pump. At this time, there appears to be a blown fuse for the 241Y bus Under Voltage logic which prevented the 2A RHR pump from starting. The plant is stable. The NRC resident inspector has been notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2001-09-03
38261 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-09-02 13:08 | 2001-09-02 17:52 | 2001-09-02 | HPCI SYSTEM DECLARED INOPERABLE "The High Pressure Coolant Injection (HPCI) steam supply line drain trap developed a steam leak that required the drain trap to be manually isolated. "At 1308, shortly after isolating the steam trap, the HPCI steam supply drain pot high level alarm was received; the HPCI system was declared inoperable and a 14-day LCO was entered per Technical Specification 3.5.1 Condition F. "At 1326, the HPCI turbine auto start feature was defeated to mitigate the potential damage to the turbine and other components from water in the steam supply line. "Unplanned HPCI system inoperability is reportable under 50.72(b)(3)(v)(D) as a single train failure that could have prevented the fulfillment of a safety function of structures or systems to mitigate the consequences of an accident." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-09-02
38260 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-09-01 08:15 | 2001-09-01 08:45 | 2001-09-01 | OFFSITE NOTIFICATION TO FLORIDA STATE AND WILDLIFE INVOLVING INJURED TURTLE "Notification being made due to a State Notification (Florida State and Wildlife) at 0815. "Notification made due to injured immature Loggerhead sea turtle being transported offsite for rehabilitation. "Notification to offsite agency requires NRC notification pursuant to 10CFR50.72(b)(2)(xi)." The licensee will inform the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-09-01
38259 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2001-08-31 23:08 | 2001-09-01 00:05 | 2001-09-27 | 1-HOUR SECURITY REPORT INVOLVED SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to detection of area boundary. Immediate compensatory measures taken upon discovery. The licensee will inform the NRC resident inspector. Contact the Headquarters Operations Center for additional details. ***** RETRACTION FROM JOHN WARNER TO LEIGH TROCINE AT 1419 ON 09/27/01 ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "This condition was promptly compensated for upon discovery. Harris Nuclear Plant performed a 1-hour notification due to this condition. Site personnel have determined that this issue is not reportable in accordance with NRC Generic Letter 91-03. As specified in Generic Letter 91-03, if these events are properly compensated upon discovery in accordance with Regulatory Guide 5.62 and NUREG-1304, they need only be logged. Therefore, Harris Nuclear Plant is retracting EN #38259 due to promptly compensating the condition in accordance with Regulatory Guide 5.62 and NUREG-1304." (Contact the NRC operations officer for additional information.) The licensee notified the NRC resident inspector. The NRC operations officer notified the Region 2 Incident Response Center (Jay Henson) and IAT (Roberta Warren). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-09-01
38258 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-08-30 12:15 | 2001-08-31 17:15 | 2001-08-31 | AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGE FOUND "A yellow box with a Yellow II label was found and Hazmat responded to the scene. The box was found abandoned in a dumpster at an apartment building. Hazmat's radiation survey meters indicated the presence of radioactive material. However, the radiation levels indicated were inconsistent with readings expected from a gauge. It was later determined the Hazmat team had confused µR with mR and the readings were much lower than earlier believed. "The city requested assistance to identify the owner of the gauge and possibly to take possession of the gauge. Because Houston was recently flooded, the city's basement area (with a lead lined vault was severely damaged and could not be used to temporarily secure the gauge. "It was determined that the gauge belonged to ATSER Corporation (L04741). A former employee reported carrying it in his vehicle and it was stolen along with the vehicle. The company is still investigating. The gauge is a Humboldt, s/n 3612. The source serial number of the Cs-137 source is 9842GQ and the Am-241/Be source is NJ03905." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-08-31
38257 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2001-08-31 | 2001-08-31 16:10 | 2001-08-31 | AGREEMENT STATE REPORT "The licensee called to report that 105 iodine-125 seeds totaling 336 millicuries were missing. The seeds were delivered to the hospital by Airborne Express on 8/29/01 and records indicate they were received by a purchasing clerk at approximately 2:00 p.m.. A prostate implant was scheduled for the morning of 8/31/01. When the radiation therapy technologist went to retrieve the seeds from the nuclear medicine department. the nuclear medicine technologist was unaware that any seeds had been delivered to the hospital. The clerk who signed for the seeds is not at the hospital today and on vacation until Tuesday. The housekeeping staff member who cleaned the area on 8/29/01 does not recall seeing any container fitting the description of the one in which the seeds were packaged and delivered. The Nuclear Medicine Department and the Radiology Department have been searched and the package not located. The dumpsters were emptied and sent to the landfill prior to discovery of the missing sources. An investigation is underway at the hospital. State radiation control personnel will conduct an onsite investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2001-08-31
38256 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2001-08-31 | 2001-08-31 13:30 | 2001-08-31 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The wrong radiopharmaceutical was administered to a patient, resulting in a dose of 9 rem (90 mSv) to the lower large intestine. A technician had picked up two doses: one Tc-99m dose (prescribed for the patient) and one Ga-67 dose. The technician then engaged in a conversation with another individual, became distracted and inadvertently administered the Ga-67 dose to the patient. The hospital will be submitting a written report to the state within 15 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2001-08-31
38255 | 0 | MAYO CLINIC |  |  |  |  | 2001-08-30 08:55 | 2001-08-31 09:19 | 2001-08-31 | MEDICAL MISADMINISTRATION DURING THE USE OF A GAMMA STEREO TACTIC UNIT A CANCER PATIENT WAS UNDERGOING THERAPEUTIC TREATMENTS AND RECEIVED A COBALT-60 DOSE GREATER THAN 39% OF THE PRESCRIBED DOSE. THE PRESCRIBED DOSE WAS 20 GRAYS AND THE ACTUAL DOSE WAS 27.8 GRAYS. CAUSE OF THE MISADMINISTRATION WAS DUE TO THE TIME OF TREATMENT BEING INCORRECTLY ENTERED IN THE TREATMENT UNIT. THE PATIENT AND PHYSICIAN WERE NOTIFIED. THERE IS NO ANTICIPATION OF ANY ADVERSE AFFECT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MN | HOS |  | 35.33 |  |  |  | 0 | 2001-08-31
38254 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-08-31 04:55 | 2001-08-31 08:35 | 2001-08-31 | NATIONAL MARINE FISHERIES SERVICE NOTIFIED OF THE RECOVERY OF A DEAD LOGGERHEAD TURTLE A deceased endangered loggerhead turtle was recovered from the circulating water intake trash bars. Based on the condition of the turtle, it was determined to have been deceased for some time and the cause was not directly related to being impinged on the circulating water (cw) trash bars. The NRC Resident Inspector will be notified along with the National Marine Fisheries Service | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-31
38253 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-08-30 12:48 | 2001-08-30 14:09 | 2001-08-30 | INDIVIDUAL ROD POSITION INDICATORS(IRPI) BECAME UNRELIABLE AND INOPERABLE As the unit was shutting down per management direction from problems encountered with the ESW system (Refer to event #38249 for additional information.), several Individual Rod Position Indicators became unreliable and inoperable as a result of changing RCS temperatures. At 1248 on 8/30/01, more than one IRPI per group became inoperable which is beyond Cook TS 3.1.3.2. Action statement. This would require entry into TS 3.0.3 which requires initiating action within one hour to place the unit in a mode in which the specification does not apply. At that time Unit 2 was in mode 2@3.3% power and was expected to enter mode 3 at which time 3.1.3.2 would no longer be applicable. At 1347 the unit was shut down in mode 3 and exited both TS 3.1.3.2 and 3.0.3. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-08-30
38252 | 0 | DOMINION |  |  |  |  | 2001-08-03 | 2001-08-30 11:55 | 2001-08-30 | MISSING NUCLEAR GAUGE A Texas Nuclear gauge, Model 5197 (S/N B847), has been discovered to be missing from the Mt. Storm coal generating station. The gauge contains 100 mCi of Cs-137 and was purchased under a general license. The vendor notified the Mt. Storm facility on 8/3/2001 that the gauge had never been returned. The gauge was last inventoried in August of 1982. All attempts to locate the gauge have been unsuccessful. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | WV | MAT | [5 empty] | 0 | 2001-08-30
38251 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-08-30 09:58 | 2001-08-30 11:50 | 2001-08-30 | LOSS OF OFFSITE RESPONSE CAPABILITY The loss of the Public Prompt Notification System(PANS) was discovered during the performance of a surveillance test. The Wright County Civil Defense was notified and is standing by to perform route alert if necessary. The NRC Resident Inspector will be notified along with state and local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-30
38250 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-08-23 | 2001-08-30 10:34 | 2001-08-30 | AGREEMENT STATE REPORT REGARDING A DAMAGED RADIOGRAPHY CAMERA AT WASHINGTON GROUP INTERNATIONAL, INC., IN HOUSTON, TEXAS The following text is a portion of a facsimile received from the Texas Department of Health: "Damaged Equipment - 30 Day Report[ - ]August 30, 2001" "1. Event Report Identification No.[:] Incident 7793" "2. License Number[:] Texas License 02662-004" "3. Licensee[:] Washington Group International, Inc." "4. Event time, date, location[:] 5:00 a.m., July 26, 2001, Job Site - Cvaerner Calpine, 8605 FM 1405, Baytown, Texas 77520" "5. Event Type[:] Damaged Equipment - Radiographic camera (Exposure device)" "6. Notification[:] 30-day report" "7. Event Description[: ...] On August 23, 2001, the licensee notified the Agency of a damaged radiographic camera which occurred on July 26, 2001. The device, containing 43 curies of Iridium-192, was damaged by a radiographer applying excessive force to the selector ring while attempting to connect the drive assembly. The device was returned to [its] transportation overpack and returned to storage as damaged. After disassembly, cleaning, and inspection, no visual signs of damage were detected and the gauge was reassembled. Upon reassembly, it was noted that there was play in the selector ring. A new storage cover was installed and the camera was returned to service. To prevent a recurrence: the radiographer involved was retrained on the equipment and informed to immediately notify the radiation safety officer of damaged equipment; both radiographers were reprimanded for failure to follow company Operating, Safety, and Emergency Procedures; all other exposure devices were inspected to see if the same problem existed - none exhibited this problem; this incident was discussed at the licensee's biweekly safety meeting; and the 'old' device cover was sent for evaluation. No abnormal exposures were detected as a result of this incident." (Call the NRC operations officer for state contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-08-30
38249 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-08-29 22:55 | 2001-08-30 06:23 | 2001-08-30 | DISCOVERY OF ABNORMALLY LOW ESSENTIAL SERVICE WATER FLOW TO DIESEL GENERATORS The following text is a portion of a facsimile received from the licensee: "This is Scott Richardson calling from the DC Cook Nuclear Plant with an [8]-hour non-emergency notification in accordance with 10CFR50.72(b)(3)(v) for 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition . . . . . . ' " "While performing an Essential Service Water (ESW) surveillance test on Unit 2, it was noted that the ESW flow to each Diesel Generator was abnormally low. This condition could have prevented the Diesel Generators from fulfilling their safety function. This condition was caused by sand and sediment in the ESW system and impacted both units." "Subsequent system flushes and valve cycling [have] eliminated the low flow condition in both Unit 1 and 2 Diesel Generators." "We will continue to monitor ESW system performance. Further investigation of this event is in progress to determine the root cause of the low flow anomaly." "Unit 2 will be [shutting] down [and] going to [Cold Shutdown] beginning in the next 3 hours." (Refer to event #38253 for additional information.) The licensee plans to notify the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-08-30
38248 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-07-28 | 2001-08-29 12:53 | 2001-08-29 | AGREEMENT STATE REPORT - ABANDONED WELL LOGGING SOURCE The following is taken from a facsimile from Texas Department of Health Bureau of Radiation Control for Incident 7794: Date of Occurrence: 7/28/2001 Source Identification: 1.7 Ci, Cs-137, Density Source, serial # A1884 16 Ci, Am-241:Be, Neutron Source, serial #A3001 Well Identification: Blackstone Energy Well: Carpenter Corp #1 Field: Wildcat, Hardin County Texas Seal Results: 500 ft. of cement on top of the tool at 10,700 ft. A deflection device and another 50 ft. of cement to be added at a later date when the well is completed. Recovery Attempts: Multiple attempts from 8/22/2000 to 8/25/2000 Depth of Sources: 1.7 Ci, Cs-137, Density Source, serial # A1884 @ 10,732 ft., 16 Ci, Am-241:Be, Neutron Source, serial #A3001 @10,714 ft. Depth of Well: 12,000 ft Identification: Plaque as required by Part 39 ordered and will be attached to the well. Initial Telephone Contact: Ruben Cortez, Texas Bureau of Radiation Control at 4:51 PM CDT on July 27, 2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-08-29
38247 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-08-29 10:04 | 2001-08-29 11:02 | 2001-09-10 | OFFSITE NOTIFICATION REGARDING A 30-GALLON DIESEL OIL SPILL FROM A FREIGHT TRAIN WHICH DERAILED AND BREACHED THE PROTECTED AREA BOUNDARY A freight train derailed and breached the protected area boundary. There were no personnel injuries as a result of this event. However, 30 gallons of diesel oil spilled from the train. The oil was contained by trap rocks and did not reach receiving waters. Security personnel have been posted as a result of the protected area boundary breach, and fire protection personnel are currently on scene cleaning up the diesel oil spill. The licensee is in the process of notifying the Connecticut Department of Environmental Protection of the oil spill. The licensee also requested that local police investigate the cause of the train derailment. In addition to the initial 4-hour event report for the offsite notification, the licensee plans to call back with an update to include the reporting criterion for the breach in the protected area boundary. The licensee notified the NRC resident inspector and plans to notify applicable state and local officials. ***** UPDATE FROM MIKE GOBELI TO LEIGH TROCINE AT 1115 ON 08/29/01 ***** The licensee provided this update to include an additional 1-hour security reporting criterion to the initial 4-hour event report for the offsite notification. The licensee determined that this event was also reportable in accordance with 10 CFR 73.71(b)(1), Appendix G, I(1)(c), for a degradation or discovered vulnerability in a safeguards system that could allow unauthorized or undetected access to a protected area, controlled access area, or vital area. The NRC operations officer notified the R1DO (David Lew), NRR EO (John Tappert), IRO (Nader Mamish), NRR IAT (Richard Rosano), NMSS IAT (Aaron Danis), Region 1 IAT (Greg Smith), Region 1 (Curtis Cowgill), Headquarters OPA (Beth Hayden), and Region 1 OPA (Neil Sheehan). * * * PARTIAL RETRACTION 1350 9/10/2001 FROM SMITH TAKEN BY STRANSKY * * * The licensee has determined that this incident is not reportable pursuant to 10 CFR 73.71 (b)(1) as a one hour report. The NRC resident inspector has been informed. Notified R1DO (Barr). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | SAFEGUARDS REPORTS |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) | 73.71(b)(1) |  |  | 0 | 2001-08-29
38246 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-08-29 04:04 | 2001-08-29 06:25 | 2001-08-29 | PLANNED MANUAL REACTOR SCRAM TO REPAIR A REACTOR RECIRCULATION PUMP FLOW CONTROL VALVE The following text is a portion of a facsimile received from the licensee: "Grand Gulf Nuclear Station manually scrammed from 27% [core thermal power] in preparation to repair reactor recirculation pump 'A' flow control valve B33F060A. All control rods fully inserted, and all other safety systems responded as designed. Condensate booster pump 'A' tripped for no apparent reason. Investigation into why the 'A' condensate booster pump tripped is underway." The licensee notified the NRC resident inspector. * * * RETRACTED AT 1305 EDT ON 8/29/01 BY DAVID HANKS TO FANGIE JONES * * * The licensee is retracting this event notification. After further review, the licensee determined that the manual reactor scram was part of a pre-planned sequence of events and as such was not reportable under 10 CFR 50.72(b)(3)(iv)(A). The licensee notified the NRC Resident Inspector. The R4DO (Gail Good) has been notified. | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-08-29
38245 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2001-08-28 20:23 | 2001-08-28 21:26 | 2001-08-28 | LOSS OF OFFSITE COMMUNICATIONS The licensee reported that ENS and local phone service was lost at 2023 EDT when a thunder storm went through the area. Communications are available via cellular service and radio communications with the state police. * * * UPDATED AT 2342 EDT ON 8/28/01 BY MIKE HEYL TO FANGIE JONES * * * The phone services have been restored. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-28
38244 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2001-08-28 14:00 | 2001-08-28 19:53 | 2001-08-28 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "At approximately 2:00 PM, August 28, 2001, the Agency received a report advising that a Troxler Model 3411B moisture/density gauge was missing. This information was supplied by the LICENSEE Radiation Safety Officer. The information supplied indicated that the LICENSEE was unsure when the gauge was taken. It was last seen on August 28, 2001 at approximately 3:00AM in a pickup truck at 1976 North Lemontree, Chandler, AZ. The gauge contained [an 8-millicurie cesium-137] source and a [44-millicurie americium-241:berylium] source. The serial number for the gauge is 17677. The retaining cable in the truck had been cut. Phoenix PD is investigating this matter, report # 0176390. The LICENSEE is offering a $500.00 reward. The LICENSEE will be issuing a press release. "The LICENSEE and the Agency continue to investigate this event. "The states of Utah, California, Colorado, New Mexico, and Nevada together with the U.S. NRC, the U.S. FBI, and Mexico are being notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2001-08-28
38243 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-08-28 12:02 | 2001-08-28 17:42 | 2001-08-28 | POSITIVE TEST ON RANDOM DRUG TEST FOR CODEINE A non-licensed supervisor tested positive on a random test for codeine. The employee's access to the plant and clearance was suspended for a minimum of 14 days. The employee is being referred to the Employee Assistance Program. The licensee has notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2001-08-28
38242 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2001-08-21 | 2001-08-28 15:27 | 2001-08-28 | AGREEMENT STATE REPORT - GAUGES CONTAINING Cs-137 DAMAGED IN FIRE A fire occurred late on 8/22/2001 at the Crompton Corp. facility at Mapleton, IL potentially involving 17 gauges containing from 50 to 1200 mCi of Cs-137. The fire involved Aluminum Alkyl which is used as a catalyst and burns (at 1800 °F) when exposed to air and can explode when exposed to water. This type of fire is typically allowed to burn itself out, but can be contained with dry chemical agents. After the fire was out, the gauges were surveyed for damage and leakage. Seven of the 17 gauges were damaged, but there was no indication of leakage. The damage was mainly to the lead shielding. The 7 gauges were removed and shielded, then shipped to the manufacturer (Ohmart/Vega) for examination. The manufacturers examination found that none of the sealed sources were damaged. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2001-08-28
38241 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2001-08-04 23:47 | 2001-08-28 13:14 | 2001-08-28 | 60 DAY REPORT - PCIV OUTBOARD ISOLATION VALVE CLOSURE "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of a specified system, specifically Primary Containment Isolation Valve (PCIV) Group 2 outboard valves. "On August 04, 2001, a spurious audio tone transfer trip caused a loss of an offsite electrical source which resulted in 4KV emergency buses automatically transferring to their respective alternate power supply. During the power transfer, the PCIV Group 2 outboard valves isolated due to a momentary loss of power to the valve logic. "The PCIVs isolated as expected for the given conditions and the valves were subsequently reopened when power was restored. No deficiencies or abnormalities were noted during valve operation. "This event has been entered into the site-specific corrective action program for resolution. "The resident has been informed." | 42 | 0 | 0 | 42 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-08-28
38240 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-08-28 01:50 | 2001-08-28 02:10 | 2001-08-28 | OCEAN COUNTY SHERIFF'S DEPARTMENT NOTIFIED Oyster Creek Generating Station notified the Ocean County Sheriff's Department of a failure of six (6) out of 42 emergency notification sirens. Repairs to the sirens are underway. A thunderstorm passed through their area before the emergency sirens were found to be inoperable. The NRC Resident Inspector will be notified of this event by the licensee. * * * UPDATED AT 1306 EDT ON 8/28/01 BY DAVID PIETRUSKI TO FANGIE JONES * * * The licensee has restored all sirens to operable. The NRC Resident Inspector will be informed. The R1DO (David Lew) has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-28
38239 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-08-27 18:10 | 2001-08-27 23:34 | 2001-08-27 | 24 HOUR REPORT - 'Q' COMPONENT ACTUATION "At 1810 hours on 08/27/01, Autoclave #1 in the X-344 facility experienced a UF6 Cylinder High Pressure Alarm. The alarm indicated a high cylinder pressure condition had occurred and the 'UF6 Cylinder High Pressure Autoclave Steam Shutoff System' actuated, which caused the autoclave steam containment valves ('Q' components) to close. The autoclave was in TSR Operational Mode II (Heating) at the time of the alarm actuation. Operations personnel immediately responded to the alarm in accordance with the approved Alarm Response Procedures and confirmed no release of UF6 had occurred. Autoclave #1 was placed in TSR Operational Mode VII (Shutdown) by operations personnel and declared inoperable by the Plant Shift Superintendent. "Instrument Maintenance was requested to perform 'as founds' on the system instrumentation. An Engineering Evaluation has been requested to investigate the circumstances surrounding the safety system actuation. "This event is reportable as a valid Safety System Actuation, a 24 hr. NRC Event Notification." The licensee notified the NRC Resident Inspector and the DOE representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-08-27
38238 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2001-08-27 08:35 | 2001-08-27 16:05 | 2001-08-27 | POSITIVE TEST ON RANDOM TEST FOR ALCOHOL A supervisor tested positive on a random test for alcohol. The employee's access to the plant and clearance was suspended for a minimum of 14 days. The employee is being referred to the Employee Assistance Program. A review of the employee's work is being performed. The licensee has notified NRC Region 2 (Jon Wallo) and intends to notify the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2001-08-27
38237 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-08-27 14:30 | 2001-08-27 14:53 | 2001-08-27 | SECURITY REPORT Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the NRC Operations Center for additional details. | 82 | 100 | 0 | 82 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-08-27
38236 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-08-27 09:41 | 2001-08-27 14:49 | 2001-08-27 | POSITIVE FOR-CAUSE TEST FOR ALCOHOL A licensed operator supervisor tested positive on a for-cause test for alcohol. The operator's access to the plant was suspended. A review of work performed found no threat to plant safety. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2001-08-27
38235 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-08-27 12:33 | 2001-08-27 14:20 | 2001-08-27 | OFFSITE NOTIFICATION FOR FISH KILL IN COOLING LAKE This notification is being made pursuant to 10CFR50.72(B)(2)(xi), Braidwood Station Technical Specification Appendix B 4.1 and Exelon Reportability manual section SAF 1.9. At 1233CT on 08/27/01, it was communicated to the Illinois Department of Natural Resources that a large number of primarily Gizzard Shad perished in a fish kill in Braidwood Nuclear Station's cooling lake, due to increased temperature (current lake temperature of 89 degrees with a 3 degree increase in a relatively short period of time on 8/26/01). The licensee notified the NRC Resident Inspector. | 97 | 97 | 0 | 97 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-27
38234 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-08-24 23:07 | 2001-08-25 00:34 | 2001-08-25 | LOSS OF EXCITATION TO THE MAIN GENERATOR RESULTS IN A REACTOR TRIP. Unit 1 was operating at approximately 100% power. While the main generator rectifier bank # 1 was being placed back in service after repairs when the main generator had a loss of excitation to the generator resulting in a generator trip, turbine trip and reactor trip. All rods fully inserted into the core. An investigation is in progress to determine when excitation was lost when attempting to place main generator rectifier bank # 1 back in service. An Auxiliary Feedwater Actuation Signal was generated on Lo-Lo Steam Generator Water Levels and AMSAC. Both Motor Driven Feedwater Pumps and the Turbine Driven Auxiliary Feedwater Pump started. The plant is currently stable in mode 3 (Hot Standby). An evaluation is in progress to determine what work will be done with the unit shut down and to develop a schedule for returning to power operation. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-08-25
38233 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-08-24 13:05 | 2001-08-24 17:05 | 2001-09-17 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO AREA BOUNDARY IMMEDIATE COMPENSATORY MEASURES TAKEN UPON TO DISCOVERY THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED CONTACT THE HEADQUARTERS OPERATION CENTER FOR ADDITIONAL DETAILS. * * * RETRACTED AT 1407 EDT ON 9/17/2001 BY MICHAEL FERRY TO FANGIE JONES * * * The licensee retracted this notification after further review of the event particulars. The licensee notified the NRC Resident Inspector. The R4DO (John Pellet) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-08-24
38232 | 0 | PROVIDENCE HOSPITAL |  |  |  |  | 2001-08-24 | 2001-08-24 15:03 | 2001-08-24 | PROVIDENCE HOSPITAL REPORTED MEDICAL MISADMINISTRATIONS OCCURRING BETWEEN 1996 AND 2000 The hospital reported that during the period from 8/7/96 to 10/18/00 fourteen medical misadministrations of strontium-90 occurred during clinical procedures using a strontium-90 eye applicator. The same ophthalmologist was the operator of the applicator during all fourteen incidences. It appears that there was a misinterpretation of what the affect the shield had on the radiation reaching the eye. There was a supposition that the use of the shield reduced the radiation to the eye by a minimum of 50% and up to 80%. Therefore, the amount of administration time for the procedures was doubled. The amount of radiation given(in the range of 3,000 rads) was well within the therapeutic range for the procedure, but it was not what the physician had written. The amount of rads given was doubled of what was prescribed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.33 |  |  |  | 0 | 2001-08-24
38231 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS INC |  |  |  |  | 2001-08-24 | 2001-08-24 12:46 | 2001-08-24 | PART 21 FOR A POTENTIAL NONCONFORMANCE RELATED TO REMOTE DIAPHRAGM SEALS Pursuant to 10CFR Part 21 Paragraph 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you of a potential nonconformance related to two model 1159 remote diaphragm seals. The two remote diaphragm seals are connected to a single Rosemount nuclear qualified transmitter with serial number 0521038. The two remote diaphragm seals are used to measure differential process pressure or liquid level while preventing the process fluid from contacting the transmitter diaphragm. The remote seals contain discrepant fill fluid screws. The fill fluid screws are part of the pressure boundary of the remote seal system. The nonconformance was due to an oversight during assembly, which has been corrected. The material specification for the qualified fill screws is 416 SST. The unqualified fill screws are 416 SST with a ball tip that is AISA E52100. The ball tip allows multiple insertions. The qualified screw does not possess the bearing feature. 1.0 Affected customer - Grand Gulf 2.0 Identification of items supplied - Model 1159 Remote Diaphragm Seals 3.0 Identification of firm supplying the Item - Rosemount Nuclear Instruments, Inc. 4.0 Nature of the failure and potential safety hazard: This notification relates to two Model 1159 Remote Diaphragm Seals, which contain discrepant fill fluid seal screws. These screws are part of the pressure boundary of the remote diaphragm seal system. This notification is not applicable to other remote diaphragm seal systems. RNII has determined that there is no safety impact related to plant applications. RNII does not feel Licensees with installed Model 1159 Remote Diaphragm Seals need to address this issue. 5.0 The corrective action which is taken, the name of the individual or organization responsible for that action and the length of time taken to complete that action: RNII immediately contacted the affected customer, and the nonconforming seals were returned to RNII prior to installation into the customer's facility. The unit will be reworked to conform to the qualification requirements. RNII internal corrective actions: 1. Revised the non-standard filling procedure for remote seals to ensure that qualified fill screws are installed during the filling process. 2. Training of engineering, manufacturing and quality personnel involved in the preparation, review and approval of non-standard procedures and processes to reemphasize the need to specifically address the material requirements. 6.0 Any advice related to the potential failure of the item: This notification applies to a single transmitter with two Model 1159C20A Remote Diaphragm Seals. This unit was returned to RNII prior to installation; therefore, does not pose a potential failure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2001-08-24
38230 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2001-08-23 21:43 | 2001-08-24 02:29 | 2001-08-24 | LOSS OF ELECTRICAL POWER TO THE TECHNICAL SUPPORT CENTER An unexpected electrical breaker trip has caused a loss of power to the Technical Support Center (TSC). On 08/23/01 at 21:43 the main control room was notified that the TSC, which is located in a building adjacent to the protected area, was without power. Communications were verified available from the TSC. An investigation revealed that an offsite breaker controlled by the power system director had tripped. Further investigation is in progress to identify and repair any deficiencies. The station procedures for contingency actions were put in place if an event requiring the TSC were to occur during the loss of power. Power was restored to the TSC at 0130 EDT on 08/24/01 from an alternate offsite source. The licensee notified the NRC Resident Inspector. | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-24
38229 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-08-23 16:21 | 2001-08-23 16:53 | 2001-08-23 | SUSPECTED INTRUSION ON THE SITE IMMEDIATE COMPENSATORY MEASURES TAKEN ON DISCOVERY THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR, STATE, LOCAL AND OTHER GOVT. AGENCIES A PRESS RELEASE WILL BE ISSUED. CONTACT HOO FOR ADDITIONAL DETAILS * * * UPDATE ON 8/23/01 @ 2009 BY WOZINSKI TO GOULD * * * THE NOUE WAS TERMINATED AT 1952 THE RESIDENT INSPECTOR WAS NOTIFIED REG 1 RDO(NOGGLE), EO(ADENSAM), FEMA(CANUPP), IAT(ROSANO), IAT(WARREN) WERE INFORMED | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | SAFEGUARDS REPORTS |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 73.71(b)(1) |  |  | 0 | 2001-08-23
38228 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-08-08 22:43 | 2001-08-23 13:05 | 2001-08-23 | AUTOMATIC START OF AN EMERGENCY DIESEL GENERATOR The following information is provided as a 60 day telephone notification to NRC in accordance with 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of WBN Emergency Diesel Generator (EDG) 2B-B. NUREG 1022, Rev 2, identifies the information that needs to be reported as discussed: (a)The specific train(s) and system(s) that were actuated. On August 8, 2001, at 2243 hours, Train B, Emergency Diesel Generator 2B-B (System 82) actuated (automatically started). The cause of the start is under evaluation, but was not in response to actual plant conditions or an ESF signal. No loss of essential board voltage was observed, no emergency start signal initiated (manually or automatically), and no other initiating signal such as an SI occurred. (b) Whether each train actuation was complete or partial. The actuation is considered complete. EDG 2B-B automatically started and accelerated to rated speed of 900 RPM. As there was no loss of essential board voltage, no load shedding occurred and the diesel generator output breaker remained disconnected from its respective shutdown board. (c) Whether or not the system started and functioned successfully. EDG 2B-B automatically started and functioned successfully. As discussed above, the EDG accelerated to rated speed of 900 RPM. Since there was no loss of essential board voltage, the diesel remained disconnected from its respective shutdown board and available to perform its safety function in the event of a loss of offsite power. No complications were observed. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-08-23
38227 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2001-07-27 | 2001-08-22 11:43 | 2001-08-23 | MISSING SHIPMENT OF CaF SETTLING POND CLEANUP WASTE A shipment of CaF settling pond waste left the site on July 25, 2001 and apparently did not arrive on July 27, 2001 at the Andrews County WCS in Texas. The shipment, one of several, consisted of 44,480 pounds of 80% CaF and 20% lime with less than 500 ppm natural uranium contained in it. The natural uranium is calculated at about 19 pounds total contained in the shipment. The driver reported that the shipment was delivered, but there is no paperwork to support the delivery. The licensee notified NRC Region 3 (Monte Phillips), the EPA, and the Illinois State Police, who are investigating. * * * UPDATE ON 8/23/01 @ 1425 BY ROBERTS TO GOULD * * * Wills Trucking found the material intact on the ground on 8/22/01 north of Dallas, Tx. and they are responding with the Texas EPA and other regulatory agencies. Notified Reg 3 RDO(Gardner), Brown(NMSS), Reg 3 IAT(Creed) and NMSS(Davidson) by e-mail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-08-22
38226 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2001-08-20 12:30 | 2001-08-22 08:30 | 2001-08-22 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The licensee is licensed out of North Carolina working under reciprocity in South Carolina. A Troxler Model 3430 moisture density gauge was stolen from the back of the company pickup truck while working at the North Auxiliary Air Force Base in North, South Carolina. The gauge was not secured or chained down when stolen. The gauge contains 40 mCi Am-241:Be and 8 mCi Cs-137. The North Police Department has been notified and is investigating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0 | 2001-08-22
38225 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2001-08-22 05:08 | 2001-08-22 08:07 | 2001-08-22 | AUTOMATIC REACTOR SCRAM ON TURBINE TRIP DUE TO A LOAD REJECT "In accordance with 10 CFR 50.72 b (2) iv (B) a RPS actuation occurred following a generator load reject. Reactor Scram occurred at 0508 August 22, 2001 due to a turbine trip signal generated from the load reject. All six ERVs opened to control reactor pressure due to the initial load reject. A negative phase sequence was experience on 345 kV lines resulting in a trip of generator 86 G1& G2 relays. All control rods fully inserted following the automatic reactor scram. "Also, in accordance with 10 CFR 50.72 b (3) iv (A) an MSIV isolation was experienced when reactor pressure reached 850 psig with the mode switch in RUN as expected. The operator was in the process of taking the mode switch to SHUTDOWN but before this action was complete the MSIV isolation signal was generated as pressure dropped below 850 psig. High Pressure Coolant Injection initiated due to vessel level <53 inches as expected. Vessel level dropped to approximately 43 inches. Following the MSIV isolation level increased to the high-level trip setpoint as expected and was returned to the normal band. MSIVs were reopened for pressure control and a feedwater pump was restarted to augment vessel level control. "SOPs and EOPs were entered to stabilize the plant and control reactor pressure and level in normal bands. Cooldown to cold shutdown is in progress. Current reactor temperature is 439 degrees F with reactor pressure 361 psig. "All containment parameters are normal and offsite power is available. No maintenance or surveillance activities were occurring at the time of the Reactor Scram." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-08-22
38224 | 0 | WYOMING MEDICAL CENTER |  |  |  |  | 2001-08-20 11:00 | 2001-08-21 15:56 | 2001-08-21 | MEDICAL MISADMINISTRATION INVOLVING AN UNDERDOSE DUE TO PERSONNEL ERROR On July 10, 2001 and elderly female patient received approximately 250 instead of the 500 centigray prescribed as a boost dose for urinary cancer. The device involved was a Wang applicator 3 centimeter in diameter with a hemispherical head containing a Cs-137 source. This was an adjunct procedure to surgery. The patient will be informed and there is no remedial treatment necessary or planned. The licensee discovered this error on 8/20/01 in a review while planning similar treatment for another patient. The following actions have been taken to preclude recurrence: all point dose calculations done by hand will include the dose prescription point and a planned treatment will include a review of previous treatments utilizing this particular applicator. The licensee attributes the underdose to personnel error and has discussed this report with the NRC Region 4 office (Whitten). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | WY | HOS |  | 35.33 |  |  |  | 0 | 2001-08-21
38223 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-08-20 08:10 | 2001-08-20 11:51 | 2001-08-20 | MISSOURI DEPARTMENT OF NATURAL RESOURCES (DNR) NOTIFIED OF MINOR OIL SPILL TO MISSOURI RIVER On 8/16/01 the Missouri DNR was notified of an unmonitored oil discharge to the Missouri River. The release, approximately 19 gallons of hydraulic oil from the Intake Structure, occurred over a 14 day period. The licensee determined that the offsite notification to the state was reportable at 0810CDT on 8/20/01. The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-20
38222 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2001-08-19 | 2001-08-20 10:29 | 2001-08-20 | AGREEMENT STATE REPORT "The licensee reported irretrievable sealed radiation sources in a well. Permission was granted to begin abandonment procedures. The well is located in Tuscarawas County, Ohio and was drilled for Belden & Blake Corp. The sources are a 2 Ci Cs-137 sealed source and a 3 Ci Am-Be sealed source. The depth of the well is 5915 feet and the sources are located at a depth of 4920 feet." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2001-08-20
38221 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-08-18 05:30 | 2001-08-18 08:23 | 2001-08-18 | TECHNICAL SUPPORT CENTER UNAVAILABLE The licensee deenergized electrical buses supplying the Technical Support Center in order to perform regularly scheduled maintenance to a circuit breaker and transformer. Contingency plans are in place in the event that the TSC becomes necessary to support onsite activities. The licensee estimates that power will be restored to the facility within 12 hours. The NRC resident inspector has been informed of this notification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-18
38220 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2001-08-17 16:45 | 2001-08-17 21:19 | 2001-10-16 | TECH SPEC REQUIRED SHUTDOWN DUE A LEAK FROM THE FUEL POOL INTO CONTAINMENT "On August 17, 2001 at approximately 1245 MST, Palo Verde Unit 3 was at approximately 97 percent power and at normal RCS temperature and pressure, when operations personnel detected an increase in containment sump level. Subsequent investigation revealed the quick operating closure device (QOCD) (EQID #PCE-M01) that isolates the containment from the fuel transfer tube was leaking by borated water from the fuel transfer canal at approximately 1 gallon per minute. Operations personnel entered TS LCO 3.6.1 Containment, Required Action A. This action requires the containment be restored to an operable status within one hour. "Since containment integrity was uncertain, and compliance with LCO 3.6 1 Required Action A could not be met within one hour, operations personnel entered LCO 3.6.1, Required Action 8.1 at 1345 MST. Required Action B.1 requires the unit be placed in Mode 3 in 6 hours, and Required Action 8.2 requires the unit be placed in Mode 5 within 36 hours, Following operations briefings, shutdown was commenced at approximately 1645 MST. At this time, Palo Verde Unit 3 is continuing to reduce power in an orderly manner and anticipates being in Mode 3 (Hot Standby) by approximately 1845 MST. "There were no other component failures, testing or work in progress that contributed to this event. The QOCD leak is allowing 4400 part per million borated water into the containment. There has been no release of radioactivity to the environment and no impact to the health and safety of the public has occurred or is anticipated. There is no elevated RCS activity and heat removal is via normal steaming to the main turbine condenser. The electric grid is stable." The licensee informed the NRC Resident Inspector. * * * RETRACTED AT 1257 EDT ON 10/16/01 BY DANIEL HAUTALA TO FANGIE JONES * * * "This notification is a retraction to the August 17, 2001, ENS #38220 which reported a Palo Verde Nuclear Generating Station Unit 3 shutdown required by Technical Specification 3.6.1. In the condition described by this ENS, the failure, a loss of containment integrity, never existed. Although personnel conservatively declared containment inoperable, plant engineers have since determined that containment integrity per Technical Specification 3.6.1 was maintained. The water leakage into containment via the Quick Operating Closure Device (QOCD) 0-rings did not constitute or create a potential accident leakage path out of containment. Therefore, the subsequent plant shutdown was not required by a Technical Specification action. "The NRC Resident Inspector has been notified." The Region 4 Duty Officer (Bill Jones) has been notified. | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-08-17
38219 | 0 | McMINN'S ASPHALT CO., INC. |  |  |  |  | 2001-08-17 00:30 | 2001-08-17 04:59 | 2001-08-17 | TROXLER GAUGE DAMAGED BY VEHICLE AT CONSTRUCTION SITE At 0030EDT on 8/17/01 a light pickup truck struck a Troxler gauge at a road construction project on State Road 340 in Lancaster, PA. The East Lampeter Police Department responded (Incident # 01-414) briefly closing traffic. The RSO surveyed the device and confirmed that the sealed source was intact prior to removal. The Troxler is a model 4640B containing an 8-millicurie Cs-137 source. The licensee is returning the device to the manufacturer's service center in Timonium, MD for inspection and repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2001-08-17
38218 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2001-08-16 23:25 | 2001-08-17 00:31 | 2001-08-17 | LOSS OF EMERGENCY SIREN REMOTE ACTUATION CAPABILITY "Omni phone system was lost resulting in a loss of Emergency Siren remote actuation control. Power was lost 8/16/01 22:25 EDT and restored 8/16/01 23:55 EDT. Per reportability manual ID# E-02 and Event# SAF 1.10, loss of assessment capability is reportable after 8 hours, but loss of greater than 25% of the sirens for more than one hour constitutes immediate notification. "The omni phone system was lost due to the associated battery voltage becoming too low to support system operation. This was caused by a temporary battery charger installed in place of the normal charger (due to a failed transformer) not maintaining the battery adequately charged. Immediate omni system recovery was effected using available AC power from an alternate source to power up the equipment. Long term plans are to replace the failed transformer and return the normal charger to service." The licensee informed the NRC resident inspector and will inform state/local agencies. | 100 | 82 | 0 | 100 | 82 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-17
38217 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-08-14 13:40 | 2001-08-16 19:00 | 2001-08-16 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE "At approximately 1:40 PM on August 14, 2001 an unidentified person in a private automobile ran over a Troxler nuclear density gauge while this gauge was being used by a trained technician at a work site southwest Denver. The technician narrowly escaped being stuck by the vehicle, but the vehicle did strike the gauge. The exterior casing of the gauge was damaged and broken into numerous pieces as a result of the collision. However the sealed source and shielding assembly remained intact. Following the incident the source was able to be retracted into the shielding and the shutter closed." Denver Police were notified immediately following the incident. The site and the gauge with the sealed source were surveyed and no leakage was found. The Troxler gauge involved is a model 4640B (serial number 841) containing a single, 8-millicurie, Cs-137, sealed source (serial number 50-7987). The gauge will be shipped back to Troxler. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-08-16
38216 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-08-16 13:55 | 2001-08-16 16:19 | 2001-08-16 | OFFSITE NOTIFICATION DUE TO OIL SPILL AT ASSOCIATED HYDRO UNIT The licensee was performing work on the pier at the Keowee Hydro Intake structure when about 1 gallon of Mobil EAL 224H (biodegradable) oil spilled into Lake Keowee. A boom had previously been installed and contained the oil in a 50 foot by 50 foot area. The spill was a result of a hydraulic hose leak. The clean-up was nearly complete at the time of the report. There was no effect on plant operations or any safety significance. The licensee notified the National Response Center, the South Carolina Department of Health and Environmental Control, and the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-16
38215 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-08-15 15:45 | 2001-08-16 12:23 | 2001-08-16 | 24-HOUR NRC BULLETIN 91-01 REPORT The licensee has notified the NRC Resident Inspector and the DOE representative. The following text is a portion of a facsimile received from Portsmouth personnel: During a walk through of the X-705 Decontamination Facility a hole was discovered on the top of the Calciner glove box. The hole could have allowed uranium bearing solution to accumulate in the bottom of the glove box [in] the unlikely event of a leak. This is in violation of the analysis of NCSA-705_024.E02 "Calciner Solution Recovery" which specifically evaluates this event. The PSS entered an anomalous condition. Tape was placed over the hole on the top of the Calciner glove box. The PSS exited the anomalous condition. This event is reportable per NRC BL 91-01 as a loss of one control of the double contingency principle. SAFETY SIGNIFICANCE OF EVENTS: low There was no leak of uranium bearing material in the vicinity of the Calciner glove box. Also, the opening on the glove box is very small. This would require a significant amount of time for the solution to accumulate in the glove [box] had a leak occurred at that exact location. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events would be required: The recovery system would have to be operating and processing uranium bearing liquid with a high concentration of uranium. Then the leak in this system must occur such that solution sprays onto the glove box. The liquid would then have to flow through the small opening on the top of the glove box and accumulate to a depth of >1.5 inches. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): volume, geometry The unlikely event supporting double contingency credits the integrity of the glove box for preventing solution from collecting in an unsafe geometry/volume. The hole on the top of the glove box could potentially allow solution to enter the glove box. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium material was involved in this event. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The hole could have allowed uranium bearing solution to accumulate in the bottom of the glove box in the unlikely event of a leak. This is in violation of the analysis of NCSA-705_024.E02 "Calciner Solution Recovery" which specifically evaluates this event. The presence of the opening undermines the basis of an unlikely event credited for double contingency. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Tape was [placed] on the hole on top of the glove box. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-08-16
38214 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-08-16 09:25 | 2001-08-16 11:40 | 2001-08-17 | ALL EMERGENCY OFFSITE SIRENS INOPERABLE The licensee determined that all 16 Emergency Offsite Sirens were inoperable. The exact cause of the failure is unknown and a plan is being developed to repair the sirens. The licensee notified the NRC Resident Inspector and intends to notify the state and local authorities. * * * UPDATED AT 1735 EDT ON 8/16/2001 BY PETER ORPHANOS TO FANGIE JONES * * * "As of 1300 August 16, 2001 163 of 165 Limerick Generating Station Emergency Offsite Sirens are determined to be functional. "A plan has been developed and investigation continues into the cause of the inoperability of the sirens." The licensee notified the NRC Resident Inspector. The R1DO (William Ruland) has been notified. * * * UPDATED AT 1751 EDT ON 8/17/2001 BY GREG SOSSON TO FANGIE JONES * * * "As of 17:30, August 17, 2001 163 of 165 Limerick Generating Station Emergency Offsite Sirens remain fully functional. The status of the sirens is being continuously monitored as part of the troubleshooting plan. "There was one 20 minute interruption of the siren system early this morning. Since then, the sirens have continued to function properly. "The investigation and troubleshooting will continue through the weekend. "Contingency public notification plans have been confirmed to be in place with the counties." The licensee notified the NRC Resident Inspector. The R1DO (Ronald Bellamy) has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-16
38213 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2001-08-16 08:25 | 2001-08-16 11:14 | 2001-08-16 | FITNESS FOR DUTY REPORT INVOLVING CONTRACTOR FOREMAN A contractor foreman was determined to be under the influence of alcohol during a random test. The contractor's access to the plant has been terminated. The licensee informed the NRC Region 2 Office (Wallow) and the Resident Inspector. Contact the Headquarters Operation Officer for details. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2001-08-16
38212 | 0 | MALLINCKRODT INC. |  |  |  | NUCLEAR PHARMACY | 2001-08-16 08:45 | 2001-08-16 10:00 | 2001-08-16 | PERSONNEL OVEREXPOSURES INVOLVING TWO WORKERS BETWEEN 1995 AND 1999 An on-going dose reconstruction in response to Confirmatory Action Letter EA-00-143, dated June 22, 2000, identified two (2) workers who received more than 250 Rem to their extremities, specifically less than one (1) square centimeter of the fingertips. The overexposures occurred between 1995 and 1999 on seven (7) occurrences during the manufacturing process involving P-32. The licensee will inform the two individuals involved and offer medical services, if requested. The licensee discussed this incident with NRC Region 3 (Cameron). * * * UPDATED AT 1532 EDT ON 8/16/2001 BY JAMES SCHUH TO FANGIE JONES * * * The on-going review has identified a total of 4 workers in 10 occurrences with overexposures. All have occurred in similar activities except for 1 person in 2 events doing a different process. NRC Region 3 (Bob Gatone) has been contacted by the licensee. The R3DO (Thomas Kozak) and NMSS (Brian Smith) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 3 | MO | FUE |  | 20.2202(a)(1) |  |  |  | 0 | 2001-08-16
38211 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2001-08-15 05:50 | 2001-08-15 13:12 | 2001-08-15 | UNEXPECTED LOSS OF POWER TO THE TECHNICAL SUPPORT CENTER The following text is a portion of a facsimile received from the licensee: "An unexpected electrical breaker trip has caused a loss of power to the Technical Support Center (TSC). On 08/15/01 at 0550, the Main Control Room was notified that the TSC, which is located in a building adjacent to the protected area, was without power." "Subsequent investigation revealed that the feed breakers supplying power to the affected bus had tripped. Further investigation is in progress to identify and repair any deficiencies. In accordance with station procedures, contingency actions are in place should an event occur which required the use of the TSC. Communication remains available from the TSC." The licensee notified the NRC resident inspector. | 100 | 82 | 0 | 100 | 82 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-15
38210 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-08-14 16:44 | 2001-08-15 12:04 | 2001-08-15 | POSITIVE, FOR-CAUSE, FITNESS-FOR-DUTY TEST The following text is a portion of a facsimile received from the licensee: "On August 14, 2001, at 1655 hours, a [non-licensed contract] supervisor tested positive for an illegal substance as a result of a for-cause test. Access to the protected area was suspended at 1659 hours on August 14, 2001. A review of the individual's work activities was performed, and no deficient work practices which could impact safety-related equipment/systems were identified. The employee has been denied further access to the Fermi Energy Center." Call the NRC operations officer for additional details. The licensee notified the NRC resident inspector and NRC Region 3 office (Gary Pirtle). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2001-08-15
38209 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2001-08-15 04:49 | 2001-08-15 06:30 | 2001-08-15 | UNIT 3 WAS MANUALLY TRIPPED DURING A LOAD REDUCTION DUE TO A LOSS OF CONDENSER VACUUM. "During a Unit 3 load reduction, a manual reactor trip was initiated. Plant documents provide guidance for manually tripping the reactor. "If reactor power is greater than 10% and condenser vacuum decreases below 24.5" Hg with generator load less than 531 MWe, then the reactor is manually tripped. "The balance-of-plant operator noted condenser vacuum at 24.2" Hg with reactor power at 15% and generator load at 30 MWe. The Unit RCO with SRO concurrence manually tripped the reactor. "Systems which did not function as required: a. N-35 Intermediate Range; High Level Trip did not clear as expected. b. N-36 Intermediate Range; Spiking indication following reactor trip. c. Rod Position Indicator E-9 indicates mid-scale approximately 117 steps (Rod Bottom light on)." The licensee has the cause for the loss of condenser vacuum under investigation. The licensee will inform the NRC resident inspector. | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-08-15
38208 | 0 | BIG ROCK POINT | 1 |  |  | [1] GE-1 | 2001-08-14 19:20 | 2001-08-14 20:16 | 2001-08-14 | SECURITY EVENT Security Officer's unescorted access was revoked. Compensatory action was immediately taken upon discovery. Licensee is reviewing person's previous work. Licensee will notify NRC Region 3 of this event. Contact the NRC Operation Center for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-08-14
38207 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-08-14 03:34 | 2001-08-14 12:07 | 2001-08-14 | DEAD SEA TURTLE FOUND. A dead Kemp's Ridley sea turtle was found in the intake canal of Oyster Creek early this morning. No tags present or obvious boat propeller wounds on the sea turtle but it has several scutes with superficial scrapes near carapace centerline and posterior notch. National Marine Fisheries Service Northeast Region was notified. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2001-08-14
38206 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-08-13 17:53 | 2001-08-13 21:31 | 2001-08-15 | UNEXPECTED REACTOR SCRAM DURING LOGIC SYSTEM TESTING OF EMERGENCY BUS A5. Pilgrim Unit 1 scrammed from 100% during performance of Logic System Testing of Emergency Bus A5. This is the first time that the Logic System Testing of Emergency Bus A5 had been performed at power. The test is performed once every 24 months and had just been rewritten to be performed at power. The cause of the scram is under investigation at this time but the initiating transient was the loss of Emergency Bus A5. All rods fully inserted into the core. The plant is at 700 lbs. and a controlled depressurization is in progress. Plans are to cool down to less than or equal to 150 lbs. and repair the outboard RCIC steam isolation valve. Due to deenergization of Emergency Bus A5, Recirculation Pump A tripped and there was a fast transfer of the swing bus (this was expected). The licensee is looking into the transfer of the swing bus causing the trip of Recirculation Pump B. Loss of both operating Recirculation Pumps at power will cause a reactor scram. All systems operated properly. The electrical grid is stable and all Emergency Core Cooling systems are fully operable if needed. The Recirculation pumps will be restarted when the differential temperature between the top and bottom head are within specification. The NRC Resident Inspector was notified of this event by the licensee. **** UPDATE ON 08/14/01 AT 1338ET BY V. FALLACARA TAKEN BY MACKINNON **** This is a supplement report to detail additional information on the scram a Pilgrim, Unit 1 on 08/13/01. Upon further evaluation of the event and the requirements of 10CFR50.72 and NUREG-1022, Pilgrim is reporting the valid actuation of the following containment isolation groups immediately following the scram: Group 2 (Secondary Isolations), Group 6 (Reactor Water Cleanup), and Reactor Building Isolation with initiation of Standby Gas Treatment Systems. These are expected occurrences in a post-scram transient due to reactor water level shrink below the Reactor Level Setpoint of + 12". Further plant response issues which are currently under investigation include: Finalizing the cause of the "B" side RPS actuation. Determining the cause of the loss of "B" Recirculation Pump. Resolving a falsely pegged level indication on the "A" Reactor Water Level Indication. Determining the cause of the loss of 120 VAC bus Y-4. An event analysis team has been formed to drive out all of these issues. R1DO (Ron Bellamy) notified. The NRC Resident Inspector was notified of this event by the licensee. ***** UPDATE FROM VINCENT FALLACARA TO LEIGH TROCINE RECEIVED AT 1420 ON 08/15/01 ***** The following text is a portion of a facsimile received from the licensee: "This is a supplemental report to further clarify information initially provided concerning logic system testing of the Division 1 Emergency Bus as it related to the 08/13/01 automatic shutdown." "The initial information indicated that this was the first time this testing had been performed at power and that the test had been rewritten to be performed at power." "This initial information did not clearly describe the situation concerning this testing. Emergency Bus Relay testing has been successfully performed at power in the past. This test procedure was reformatted to delineate Tech Spec required testing from non-Tech Spec required testing to reduce the unnecessary Diesel Generator unavailability time. During reformatting, an error was introduced which left out a needed prerequisite to successfully complete the Tech Spec required testing of the A-EDG output breaker. This is currently believed to be an initiating event that contributed to the 08/13/01 automatic shutdown." "At this time, Pilgrim is in Cold Shutdown. The Events Analysis Team continues to investigate previously identified plant issues related to this shutdown." The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R1DO (Bellamy). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-08-13
38205 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-08-13 14:15 | 2001-08-13 20:40 | 2001-08-13 | LOSS OF ONE CONTROL OF THE DOUBLE CONTINGENCY PRINCIPLE NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 1415 8/13/01 loose plastic wrap was discovered on a storage shelf in an inadvertent container area and was not configured or secured such that it cannot be deformed into an inadvertent container with an unsafe accumulation potential. This is a violation of control # 5 of NCSA705_076.A03, "Use Of Inadvertent Containers". A pump located on a lower shelf apparently had a pump flange cover dislodged, uncovering a potential inadvertent container. This is a violation of control # 3 of the same NCSA. The PSS entered an anomalous condition. The plastic wrap and pump were removed from the inadvertent Container area. The PSS exited the anomalous condition. SAFETY SIGNIFICANCE OF THE EVENTS: LOW There was no leak of uranium bearing material in the vicinity of the plastic or the uncovered pump. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events would be required: The microfiltration system would have to be processing uranium bearing liquid with an unknown or high concentration of uranium. Then a leak in this system must occur such that an unsafe amount of liquid sprays from the system onto the plastic wrap or uncovered pump. The plastic would then have to deform or the pump would have to fill such that 2.5 liters collects to a depth of greater than 1.5 inches. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): volume, geometry Inadvertent containers are controlled based upon volume (2.5 liter) or geometry (1.5" or 4" diameter). Flexible material is specifically controlled such that solution cannot pool to a depth greater than 1.5 inches. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): No uranium material was involved in this event. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES Loose plastic wrap was not configured or secured to prevent deformation into an inadvertent container. The pump flange cover was dislodged. The pump was located on a lower shelf in the same area. This is a violation as control # 5 and # 3 respectively of NCSA-705_076.A.03. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The plastic wrap and pump were removed from the inadvertent container area. The NRC Resident Inspector was notified of this event report by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-08-13
38204 | 0 | SCIENTECH, INC. |  |  |  |  | 2001-08-07 | 2001-08-13 17:14 | 2001-08-13 | POTENTIAL DEFECT SCIENTECH, Inc.'s subsidiary NUS Instruments, Inc. (NUSI) has determined that a Basic Component, supplied to Rochester Gas and Electric Ginna Station Nuclear Plant under RG&E purchase order 5000002014, contains a potential defect that is reportable under 10CFR21. NUSI determined that the potential defect was reportable under the provisions of 10CFR21 on August 07, 2001. SCIENTECH, Inc. President was informed August 13, 2001. RG&E is aware of this problem and the affected component is being modified to restore this item to an acceptable status by August 17. A formal written report will be provided within 30 days of this notification. The component, delta T Time Domain Module, M/N: TMD500-08/08/08/08-08-08-1/2, P/N: MBA-E063PA-1, Rev. 0 (1ea.), S/N:9800771, was originally manufactured as P/N: MBA-E062PA-1 (voltage output) by NUSI. NUSI performed a conversion of this item to P/N: MBA-E063PA-1 (current output) resulting in a defect. A total of six items were converted under this purchase order for use in Safety Related Systems. NUSI has opened a 10CFR21 file concerning this component and has numbered it as 21-01-01. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MD | OTH | PAR | 21.21 |  |  |  | 0 | 2001-08-13
38203 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-08-13 13:10 | 2001-08-13 15:04 | 2001-08-13 | OFFSITE NOTIFICATION TO THE FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION An immature green sea turtle was rescued from the plant's intake canal. The turtle is alive but in need of rehabilitation. As required by the plant's sea turtle permit, the Florida Department of Environmental Protection (Florida Fish and Wildlife) was notified of this event. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-13
38202 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-08-12 07:46 | 2001-08-12 12:16 | 2001-08-12 | MANUAL REACTOR SCRAM DUE TO DECREASING REACTOR WATER LEVEL AND GROUP 1 ISOLATION DUE TO LOW REACTOR PRESSURE WHILE IN RUN The following text is a portion of a facsimile received from the licensee: "At 07:46:00 [CDT], a reactor water low-level alarm was received. The reactor operator verified the low-level condition and took manual control of feedwater level control. The operator matched feedwater and steam flow. At 07:46:28 [CDT], the 'B' feedwater pump tripped on low suction pressure. A manual scram was inserted at 07:46:42 [CDT] due to lowering reactor water level. Level dropped below 170 [inches] on the reactor scram [as expected], and [Group 2, 3, and 4 isolations] were received. All isolations went to completion. At 07:47:48 [CDT], a Group 1 isolation was received on the 850 psig low reactor pressure in Run isolation signal. The operator was in the process of [taking] the mode switch [out of] Run, but the isolation occurred before this action could be completed. All [main steam isolation valves] closed on the Group 1 isolation signal. Reactor level increased to the high level trip following the reactor scram, as expected, and the 'A' feedwater pump tripped. Due to the Group 1 isolation, the operating crew elected to manually initiate Low Low Set pressure control using the safety relief valves. A relief valve was opened, arming Low Low Set, and the two valves lowered reactor pressure to 900 psig. The Group 1 was reset, and main steam line drains to the condenser are being used to control pressure. The 'A' feedwater pump high level trip has been reset and is maintaining level." "All systems responded as expected. The plant is currently in Hot Shutdown at 800 psig. Plans are being reviewed to determine the length of the forced outage. Preliminary investigations indicate that the 'B' feedwater pump minimum flow valve may have failed open to initiate the event." The licensee stated that there were no maintenance or surveillance activities ongoing at the time of the event. All control rods fully inserted following the manual reactor scram. All containment parameters are currently normal, and offsite power is available. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-08-12
38201 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-08-10 21:15 | 2001-08-10 23:02 | 2001-08-16 | UNPLANNED REACTOR PROTECTION SYSTEM (RPS) SYSTEM/SAFETY SYSTEM ACTUATIONS WHILE CRITICAL The following text is a portion of a facsimile received from the licensee: "[The unit] received [an] isolation of the [transverse incore probe (TIP)] purge system and the offgas system during [an] electrical transient on the 230kV distribution system. [The licensee believes] the isolations were caused by the voltage fluctuations felt in the plant from the grid. Since the TIP purge isolation is processed through [the reactor protection system (RPS)] and offgas from the offgas [radiation] monitors, this falls under actuation of a safety system while critical." "[The licensee] reset isolations and restored systems to normal." The licensee stated that the isolation signals that were processed did not show up on any alarms. Alarms were received but nothing specific to indicate the isolations. This may have been due to voltage fluctuations/losses as a result of power/instrument panels that transferred to their alternate power supplies. The voltage fluctuations on the in-house 4160V buses were attributed to the electrical transient on the 230kV distribution system. There was severe weather in the area at the time of this event. As a result, one of two 230kV outgoing power lines and both 34.5kV feed lines were lost. All of these lines have since been returned to service. The licensee stated that offsite power was never lost because one 230kV line remained available to backfeed/supply the 34.5kV buses. The licensee notified the NRC resident inspector. * * * RETRACTED AT 1840 EDT ON 8/16/2001 BY JERE FREEMAN TO FANGIE JONES * * * The licensee, after review of the event, determined that the actuation of a single component due to a power panel transfer on a voltage transient did not meet the requirement of an actuation of the containment isolation system for reportability. Per NUREG 1022 Rev 2, this event was not reportable and is retracted. The licensee notified the NRC Resident Inspector. The R1DO (William Ruland) has been notified. | 84 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-08-10
38200 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2001-08-10 18:10 | 2001-08-10 19:52 | 2001-08-10 | LOSS OF GREATER THAN 25% OF THE EMERGENCY PREPAREDNESS SIRENS DUE TO POWER OUTAGES FROM ELECTRICAL STORMS The following text is a portion of a facsimile received from the licensee: "[A total of 26 out of] 97 emergency preparedness sirens (>25%) are out of service due to power outages from electrical storms. [This includes 20 out of] 27 in York County, 2 in Herford County, 2 in Lancaster County, 1 in Cecil County, and 1 in Chester County. Plans are in progress to restore power." The licensee reported that all systems functioned as required and that there was nothing unusual or misunderstood. The licensee also reported that there was no loss of offsite power. The licensee notified the NRC resident inspector. ***** UPDATE FROM JACK POPIELARSKI TO LEIGH TROCINE RECEIVED AT 2101 ON 08/10/01 ***** The licensee also notified York County. The NRC operations officer notified the R1DO (Holody). | 100 | 84 | 0 | 100 | 84 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-10
38199 | 0 | MILLSTONE | 1 | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-08-10 10:15 | 2001-08-10 13:18 | 2001-08-10 | PLANNED OFFSITE NOTIFICATION REGARDING A FISH KILL IN THE DISCHARGE QUARRY DUE TO A RECENT SUSTAINED HEAT WAVE IN THE NORTHEAST The following text is a portion of a facsimile received from the licensee: "A visual inspection by Millstone [station biologists] on August 10, 2001, revealed approximately 50 dead [Tautog] (blackfish) in the discharge quarry by the fish barrier. A subsequent dive into the quarry by station biologists [revealed] 2 additional dead Tautog along the fish barrier. No additional [mortalities] or other species were found on the bottom of the quarry." "The fish most likely died as a result of the sustained elevated temperatures during the week of August 6, 2001, experienced throughout New England and Connecticut. Intake water temperatures have risen above 70 degrees F with discharge temperatures about 98 degree F. Water temperatures in the quarry have climbed to above 90 degrees F at times during the week. Tautog are known to have decreased resistant when water temperatures are above 90 degrees F." "Station [biologists] continue to monitor fish in the quarry." The licensee stated that there was nothing unusual about the temperature deltas across the condensers and that discharge temperatures are normal. The licensee also stated that load has been reduced on Unit 2 in order to keep condenser pressure below the condenser low pressure alarm setpoint and to maintain discharge temperatures within acceptable limits. The discharge temperatures for Unit 3 were reported to be normal with the unit at full power. The licensee plans to notify the NRC resident inspector and the State Department of Environmental Protection. | 0 | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-10
38198 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2001-08-10 09:45 | 2001-08-10 11:24 | 2001-08-10 | SMALL URANIUM HEXAFLUORIDE RELEASE ONSITE The licensee reported that from 0945 to 0950 CDT, a small UF6 release occurred in the feeds material building. No material left the site, nor did the licensee declare an Alert. Two individuals were exposed to fumes from the leak. Those individuals were treated with oxygen at the facility and transported to a local hospital. The UF6 leak has been stopped. The exact quantity of material released has yet to be determined. The licensee is currently conducting an investigation of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | IL | FUE | [5 empty] | 0 | 2001-08-10
38197 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-08-10 11:15 | 2001-08-10 11:21 | 2001-08-10 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO TWO AUXILIARY FEEDWATER PUMPS BEING INOPERABLE. Commenced Unit 2 plant shutdown to comply with Technical Specification 3.7.1.2.b: Two Auxiliary Feedwater pumps inoperable. Unit 2 Turbine Driven Auxiliary Feedwater pump was inoperable due to scheduled maintenance. Unit 2 "2 East" Motor Driven Auxiliary Feedwater pump was declared inoperable due to a failure of associated room cooling (room cooler inoperable) required by administrative procedure PMP 4030.001.001, Impact of Safety Related Ventilation on the Operability of Technical Specification Equipment. All other systems fully are operable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-08-10
38196 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-08-09 | 2001-08-10 09:25 | 2001-08-10 | STOLEN HUMBOLDT 5001C NUCLEAR GAUGE The gauge was lost during the hours of darkness July 15-16, 2001, from the back of a truck that was parked overnight at the home of the driver. The gauge and it's transport case were removed from a parked pickup truck by cutting the chain securing the gauge to the bed of the truck. Also stolen during this incident was the operator's toolbox and assorted hand tools. The gauge is a Humboldt Model 5001C, Serial # 2606, containing two radioactive sources: 10 millicuries of cesium-137, Serial #6171GQ; and 40 millicuries of americium-241;Be, Serial # NJ02767. A police report was filed on July 16, 2001, with the Dallas Police Department (Report # 0551265-K). A press release offering a $250 reward for the return of the gauge was run in the Dallas Morning News for two days. The gauge has not been recovered as of this date. The licensee has been cited for failure to maintain the gauge under constant surveillance. The state of Texas has informed the Radiation Control authorities in Mexico, Arizona, New Mexico, Arkansas, and Louisiana, as well as the Humboldt Radiation Safety Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-08-10
38195 | -1 | PALISADES | 1 |  |  | [1] CE | 2001-08-09 20:00 | 2001-08-09 21:37 | 2001-11-19 | DISCOVERY THAT SUPPORTS MAY NOT BE CAPABLE OF PROPERLY RESTRAINING THE MISSILE SHIELD DURING A DESIGN BASIS SEISMIC EVENT The following text is a portion of a facsimile received from the licensee: "Evaluation of the Missile Shield, over the Reactor Vessel Head, has revealed that the supports for the Missile Shield may not be capable of properly restraining the Missile [Shield] in the horizontal direction during a Design Basis Seismic Event. Consequently the Missile Shield is considered inoperable pending further evaluation. This is being reported as an unanalyzed condition that could significantly degrade Plant safety." The licensee notified the NRC resident inspector. * * * RETRACTED AT 1602 EST ON 11/19/01 BY DAN MALONE TO FANGIE JONES * * * The licensee is retracting this event after further evaluation determined that the supports for the Missile Shield are adequate to restrain it during a Design Basis Seismic Event. The shield has been determined to be Operable, but degraded. The licensee notified the NRC Resident Inspector. The R3DO (Christine Lipa) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-08-09
38194 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-08-09 16:01 | 2001-08-09 18:18 | 2001-08-09 | OFFSITE NOTIFICATION REGARDING APPROVAL TO EXCEED THE NORMAL OPERATING DISCHARGE TEMPERATURE PERMIT LIMIT DUE TO THE EMERGENCY NEED FOR POWER AND CONDITIONS ON THE GRID At approximately 1500, the licensee began to reduce reactor power from 100% because main condenser discharge temperature began to approach the discharge permit temperature limit of 106°F. At 1601, the system dispatcher notified the licensee of an emergency need for power and informed the licensee that the criteria to exceed the discharge permit temperature limit was authorized. In this condition, a discharge temperature of 110°F is allowed. As a result, the licensee ceased the power reduction with the unit at approximately 98% reactor power and returned reactor power to 100%. The emergency need for power was cancelled at 1612. As a result, the licensee commenced another power reduction in order to reduce the main condenser discharge temperature and comply with the 106°F discharge permit limit. The highest main condenser discharge temperature attained was 106.36°F. Reactor power is currently stable at 93%. The licensee notified the New Jersey Department of Environmental Protection and plans to notify the NRC resident inspector. | 93 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-08-09
38193 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-08-07 | 2001-08-09 14:22 | 2001-08-09 | AGREEMENT STATE REPORT REGARDING A DAMAGED NDC GAUGE CONTAINING AMERICIUM-241 AT GREEN BAY PACKAGING IN MORRILTON, ARKANSAS The following text is a portion of a facsimile received from the Arkansas Department of Health: "The Department received notified on August 8, 2001, that a gauge containing radioactive material was damaged during maintenance operations at Green Bay Packaging in Morrilton, Arkansas. The gauge is licensed under Arkansas Radioactive Material License Number ARK-197-BP-01-98." "The incident occurred on August 7, 2001, when the gauge became caught in the conveyor wire and was pulled away from the mounting bracket, falling and striking a roller. The impact tore the shutter from the gauge. The gauge was retrieved without exposure to personnel. Temporary shielding was added to the gauge, and the gauge was placed in storage by the Radiation Safety Officer." "It was determined that the source was intact, and a leak test was performed. The gauge is to be returned to the manufacturer." "The gauge is [an] NDC Model Number 104F, Serial Number 12605, containing 0.93 gBq (21 mCi) of Americium-241." "The Department is conducting an investigation of the incident." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2001-08-09
38192 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-08-08 19:00 | 2001-08-08 22:42 | 2001-09-05 | STARTUP TRANSFORMER (SUT) AND 4A EMERGENCY DIESEL GENERATOR (EDG) BOTH INOPERABLE Unit 4 Startup Transformer (SUT) and 4A EDG were both inoperable for 3 hours, 40 minutes on 08/08/01. This was discovered after the fact at 1900 hours on 08/08/01 while investigating a failure of the 4A EDG ventilation system. The 4A EDG was restored to operable status at 1920 hours on 08/08/01. The Unit 4 SUT was taken out of service at 0800 0n 08/08/01 for planned maintenance. The SUT on Unit 4 was returned to operable status at 1140 hours on 08/08/01. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 9/5/01 @ 1734 BY MORRIS TO GOULD * * * RETRACTION The licensee is retracting the notification made on August 8, 2001, in which it was reported that the Unit 4 Startup Transformer and the 4A Emergency Diesel Generator (EDG) were both inoperable (NRC Event Report 38192). The licensee has determined that the failure of the 4A EDG ventilation system did not make the 4A EDG inoperable. Therefore, there was no time during which the 4A EDG and the Unit 4 Startup Transformer were simultaneously inoperable. The NRC Resident Inspector will be notified. Notified Reg 2 RDO(Monninger) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2001-08-08
38191 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-08-08 09:15 | 2001-08-08 21:20 | 2001-08-08 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING VIOLATION OF CRITICALITY CONTROLS "At 0915, on 8-8-01, the Plant Shift Superintendent (PSS) was notified of an NCSA violation that had occurred in the C-335 building. While a Waste Management operator was transporting a potentially fissile 5.5 gallon waste drum on the ground floor of C-335, the operator momentarily set down the drum being transported closer than 2 feet from another potentially fissile drum in violation of the spacing requirements in NCSA GEN-15. The operator them continued the task, and transported the container to its desired location. The requirement states that a minimum 2 foot edge-to edge spacing is required between fissile/potentially fissile waste containers. This requirement is used as an interaction control. "Since one leg of double contingency was lost this is being reported to the NRC as a 24-hr. Event report. "The NRC Acting Senior Resident has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: "While a control was violated, concurrent violations of the same control would have to occur for a criticality to be possible. NCSA GEN-15 limits the movement of fissile/potentially fissile waste to one container at a time, limiting the possibility of concurrent violations of the spacing control. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: "In order for a criticality to be possible, additional concurrent spacing violations would have to occur. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Double contingency for this scenario is established by Implementing a control for geometry and a control for interaction. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND %WORST CASE CRITICAL MASS): "Less than 240 grams U-235 . "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Double contingency for this scenario is established by implementing a control for geometry and a control for interaction. "The first leg of double contingency is based on geometry. Specific dimensions for the 5.5 gallon waste drums are used in the calculation analysis. The drum used was an AQ-NCS approved container. This control was not violated. "The second leg of double contingency is based on interaction. NCSA GEN-15 requires fissile/potentially fissile waste container be maintained a minimum of 2 foot edge-to edge from other fissile/potentially fissile material. By placing the drum less than 2 feet from another fissile/potentially fissile waste container, the control was violated and the process condition limit was exceeded. "Since the interaction process condition limit was exceeded, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AN WHEN EACH WAS IMPLEMENTED: "The drum was placed in a safe configuration immediately following the incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-08-08
38190 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-08-07 18:10 | 2001-08-08 11:37 | 2001-08-08 | POTENTIAL OPERATION OUTSIDE OF LICENSE LIMITS On 8/7/2001, with Unit 1 and Unit 2 operating in Mode 1 at 100% power, during a review of the Core Thermal Power calculation, Engineering discovered that a constant for the Moisture Fraction input into the calculation was non-conservative. Due to the identified non-conservatism in the constant, actual core thermal power could have been as much as 6 MWth higher than indicated (~0.2% of Rated Thermal Power). This condition resulted in both Units having potentially operated above their Maximum Power Level License Limits (Reference NPF-14, 2.C(1) and NPF-22, 2.C(1)). Both Units have been administratively de-rated 7 MWth until this issue is resolved. There is a potential that this condition has existed since the startup of both Units. This event meets the License Conditions requiring a 24 Hour report in accordance with 10CFR50.72. The NRC Resident Inspector was notified. | 99 | 99 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2001-08-08
38189 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-08-07 20:15 | 2001-08-07 23:11 | 2001-08-08 | UNIT 1 EXPERIENCED AN AUTOMATIC REACTOR SCRAM FOR REASONS UNKNOWN "At 2015, Grand Gulf Unit 1 had an automatic RPS actuation. This is a 4-hour notification per 10 CFR 50.72 (b)(2)(iv)(B). All systems performed as expected, except that Feedwater/Condensate were not available due to hotwell level problems. RCIC was manually started for level control. At the time of the scram, a local generating station was experiencing switchyard problems (Baxter Wilson Electric Station). Also at the time, significant lightning strikes were noticed in the area. Scram initiation event analysis is in progress." All rods fully inserted. The licensee is in the process of restoring the condensate system. Offsite power is stable and available. All safety equipment is available. The main condenser is available for decay heat removal. The licensee informed the NRC resident inspector. * * * UPDATE 1756EDT ON 8/8/01 FROM WALTER CADE TO S. SANDIN * * * "This is supplemental to event number 38189 reported on 8/7/01. " During Post Trip analysis of Reactor Scram, it was determined that the EOC-RPT circuits required by GGNS Technical Specifications did not function as expected. There were no consequences to the failure as a non-tech spec vendor supplied load reject circuit operated properly. This is being reported per 10 CFR 50.72 (b)(3)(v)(A). Details will be available in the LER to follow. This circuit [is] not required below 40% Reactor Power." The unit is currently in mode 3 making preparations for restart. Corrective actions will be determined following completion of a fuels analysis. This issue and a possible TS change request has been discussed with NRR. The licensee informed the NRC resident inspector. Notified R4DO(Marschall). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2001-08-07
38188 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2001-08-03 | 2001-08-07 13:53 | 2001-08-07 | STATE OF SOUTH CAROLINA WAS NOTIFIED BY ONE OF THEIR LICENSEES OF A HIGH FILM BADGE READING GME Engineering, which uses moisture density gauges, received a second quarter film badge reading for one of its employees that measured 33.5 Rem. The employee had been terminated in mid May for vandalizing company property. It is believed that the employee intentionally exposed his badge so that he would not have to work with a moisture density gauge any more. The licensee has not been able to locate the individual. The State was notified on 8/7/01. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0 | 2001-08-07
38187 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-08-05 21:30 | 2001-08-05 22:25 | 2001-08-05 | NOAA WEATHER RADIO SYSTEM INOPERABLE The NOAA weather radio system was determined to be inoperable at 2130 EDT. The radio system is used as part of the licensee's prompt notification system. The licensee has contacted state and local government agencies. The NRC resident inspector will be informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-08-05
38186 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-08-04 15:22 | 2001-08-04 19:55 | 2001-08-09 | AUTOMATIC START OF BOTH UNITS DIESEL GENERATORS DUE TO A LOSS OF START-UP POWER "Electrical fault caused loss of Start-up Power to both units. This caused all six [6] diesel generators on both units to automatically start." Circuit breaker CB212 which supplies 230KV start-up power to both units opened due to an unidentified electrical fault. Initial indication was a loss of power to outbuildings onsite followed about twenty-two (22) minutes later with a loss of power to the Start-up transformers. Investigation found the grounding fuses on the Unit 1 side open. Should a unit trip occur while in this condition, RCS cooldown by natural circulation would be required. Both units are in Tech Spec LCO 3.8.1 Condition 'A' which requires restoration of start-up power within 72-hours or unit shutdown; mode 3 (hot standby) in the following 6-hours followed by mode 5 (cold shutdown) 36-hours later. The licensee is performing a maintenance and engineering evaluation to determine if start-up can be restored by closing a cross-tie breaker from Unit 2. None of the diesel generators loaded and all have been secured and returned to standby. The licensee informed the NRC resident inspector. ***** UPDATE FROM JEFF KNISLEY TO LEIGH TROCINE RECEIVED AT 1759 EDT ON 08/09/01 ***** The following text is a portion of a facsimile received from the licensee: "[...] FOLLOW-UP INFORMATION" "The event, as described in the original event notification number 38186, caused all six diesel generators on both units to automatically start. The diesel generators started, as designed, upon receiving an anticipatory signal due to the loss of Start-Up Power; and the diesel generators did not load, as designed, because vital and non vital power was still available from the Auxiliary Transformers, back-fed from the generator output of each unit." "As stated in the original event notification, the grounding fuses for the Unit 1 Start-Up Transformer were found open. The immediate cause of the event was a fault in the 12kV Fuse Cabinet for the Unit 1 Start-Up Transformer ground resistor. The ground resistor was observed to be radiating heat just prior to the event witnessed by the damage to the Fuse Cabinet. The cause of this failure is being investigated within the corrective action program." "As stated in the original event notification, there was a loss of power to outbuildings onsite. The 12kV underground distribution breaker tripped [on 08/04/01 at] 1500 PDT, causing the loss of non-essential site loads; such as the Administration, Training and Maintenance Buildings, and support facilities -supporting power production including water treatment for Condensate make-up, back-up Service Air Compressors, and Radwaste Laundry Building." "Start-Up power to Unit 2 was restored [on 08/05/01 at] 0513 PDT. After assuring there was no damage to the Unit 1 Start-Up Bus, power was restored to the Unit 1 Start-Up Bus [on 08/06/01 at] 1122 PDT, via a cross-tie breaker from the Unit 2 Start-Up Transformer. The 12kV underground loop was reenergized [on 08/07/01], thus restoring power to the non-essential site loads. Repair of the Fuse Cabinet is in progress." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Charles Marschall). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-08-04
38185 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-08-03 20:40 | 2001-08-03 22:56 | 2001-08-04 | UNIT 1 DECLARED AN UNUSUAL EVENT DUE TO A FIRE LASTING GREATER THAN 10 MINUTES A fire occurred in the 4KV Bus 12 while realigning the electrical power supplies from the 1 Reserve Transformer to the 1 Main Transformer during power ascension. Bus 12 supplies both the 12 Reactor Coolant Pump and the 12 Feedwater Pump which were secured. The 11 Reactor Coolant Pump was also secured placing the unit in natural circulation. Auxiliary Feedwater Pumps 11 and 12 are in service (autostarted on lo-lo SG level) supplying both Steam Generators (SG) as normal for a reactor trip. The Main Condenser is in-service for decay heat removal. The licensee is in the process of electrically isolating Bus 12. The Red Wing Fire Department is onsite responding to the fire which has not been confirmed extinguished at the time of this report. The cause of the reactor trip and the fire is unknown. The licensee informed state/local agencies and the NRC resident inspector. * * * UPDATED AT 0016 EDT ON 8/4/2001 BY SCOTT WHITSON TO FANGIE JONES * * * The licensee reported that 2 employees were treated for heat exhaustion on site and another employee was transported to a local hospital at 2255 CDT for the same reason. All were part of the onsite fire brigade. * * * UPDATED AT 0115 EDT ON 8/4/2001 BY DENNIS CARLSON TO FANGIE JONES * * * The licensee exited the Unusual Event at 0012 CDT on 8/4/2001. The plant is stable in natural circulation and all safeguards buses are energized by offsite power. The licensee notified the NRC Resident Inspector. The R3DO (John Madera), NRR EO (Herb Berkow), and FEMA (Zapata) have been notified. * * * UPDATED AT 0325 EDT ON 8/4/2001 BY MIKE SLEIGH TO FANGIE JONES * * * The licensee reported that at the beginning of the Unusual Event a safeguards degradation related to the area boundary took place. Compensatory measures were taken upon discovery. The licensee notified the NRC Resident Inspector and intends to notify R3 IAT (James Creed). The R3DO (John Madera) was notified. Refer to the HOO Log for details. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | SAFEGUARDS REPORTS | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 73.71(b)(1) | 0 | 2001-08-03
38184 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-08-03 16:42 | 2001-08-03 20:33 | 2001-08-03 | 4-HOUR REPORT INVOLVING NOTIFICATION TO OTHER GOVERNMENT AGENCIES "On 8/3/01 at 1642 the Plant Shift Superintendent received a 911 emergency response notification of a vehicle accident on perimeter road, which is included in the Department Of Energy (DOE) reservation. There was one (1) fatality and three (3) injuries which required hospitalization. Notifications of the vehicle accident were made to Pike County (Ohio) Sheriff's Office. Once it was determined that the accident involved a fatality DOE-OROC, and DOE-HQ were also notified. "This PORTS notification to 'other government agencies' requires notification to the NRC as a 4-hour NRC Event Report." The NRC resident inspector was informed of this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-08-03
38183 | -1 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2001-08-02 15:00 | 2001-08-02 19:17 | 2001-09-28 | UNANALYZED CONDITION INVOLVING SEISMIC EVENT DISCOVERED DURING ENGINEERING REVIEW "On August 2, 2001, at approximately 1500 hours, Engineering notified operations that the Service Water (SW) System may not meet analyzed flow requirements after a seismic event as a result of a system re-alignment change implemented June 4, 2001. The SWS re-alignment change placed an 8 inch non-seismic SW line on the essential SW header. The SWS was originally analyzed for a seismic event with the break of a 10 inch non-seismic SW line. The change evaluation concluded that this configuration was bounding for the alignment. The assessment of the alignment change did not adequately consider the effects of the seismic event. After a review of the change, Engineering judged that the SWS would not meet system design flow requirement after a seismic event with two out of three pumps due to the failure of both non-seismic lines that were aligned as a result of the change. Operations initiated realignment of the 8 inch SW line back to the non-essential header which was completed at 1640 hours. Engineering is performing evaluations but judged that the SWS would have met flow requirements for plant shutdown with three SW pumps operable after a seismic event with no random single failure (three pumps operable)." The licensee will inform the NRC resident inspector. **** RETRACTION ON 09/28/01 AT 1002 HOURS BY TIM RIEGER TAKEN BY MACKINNON **** Upon further assessment, the re-alignment condition is not considered reportable. Additional engineering reviews showed that the alignment to the non-seismic SW lines to the Essential header was not risk significant. Engineering judgement and analysis concluded that the plant design basis events, including the seismic event, would not cause a consequential loss of the non-seismic lines aligned to the Essential header. Therefore, the condition did not significantly degrade plant safety and although at the time was unanalyzed, the condition does not meet reporting requirements. As part of Indian Point 3's corrective action program, the cause and extent of condition of the event is being evaluated and identified corrective actions will be performed. R3DO (John Kinneman) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-08-02
38182 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-08-02 12:38 | 2001-08-02 18:10 | 2001-08-02 | 24-HOUR REPORT INVOLVING A SAFETY SYSTEM ACTUATION DUE TO A VALID SIGNAL "At 1250 on 08/02/01, the PSS office was notified that a High Autoclave Steam Pressure alarm was received on the C-337A autoclave position 2 west Autoclave Steam Pressure Control System (SPCS). The SPCS system is required to be operable while feeding in mode 5 according to TSR 2.2.3.3. The autoclave was in Mode 5 at the time of the actuation. The indications were checked according to the alarm response procedure and the alarm was determined to be a valid signal. The autoclave was removed from service and the Steam Pressure Control System was declared inoperable by the Plant Shift Superintendent. "This safety system actuation is reportable to the NRC as required by Safety Analysis Report, section 6.9, table 1, criteria J.2, Safety System actuation due to a valid signal as a 24-hour event notification. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-08-02
38181 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2001-08-02 08:23 | 2001-08-02 10:07 | 2001-08-02 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER FOLLOWING LIGHTNING STRIKE At 0823 CDT, the licensee declared an Unusual Event due to a lightning strike on or near the Unit 2 main transformer which caused a fire in the transformer and a loss of offsite power to the unit. Both emergency diesel generators (the Unit 2 and swing EDGs) started and loaded. An automatic reactor scram occurred and all control rods inserted following the scram. The unit is currently in Hot Shutdown with decay heat being removed via the safety/relief valves and reactor vessel water level control being maintained using the safe shutdown makeup pump and the reactor core isolation cooling (RCIC) system. Offsite firefighting assistance was requested to combat the fire, which has since been extinguished. The licensee is currently in the process of restoring offsite power to the unit. The electrical transient did not significantly affect the operation of Unit 1. The NRC resident inspector has been informed by the licensee. HOO NOTE: The NRC senior resident inspector notified the NRC Operations Center of this event at 0933 EDT. The agency entered the monitoring phase of normal mode at 1003 EDT. * * * UPDATE 1220EDT ON 8/2/01 FROM FOSTER (REGION 3 IRC) TO S. SANDIN * * * Region 3 has secured from Monitoring at 1120CDT based on current plant conditions and the licensee's on-going restoration of offsite power. Notified IRO(Holonich). * * * UPDATE 1253EDT ON 8/2/01 FROM CHRISSOTIMOS TO S. SANDIN * * * Unit 2 exited the Unusual Event at 1147CDT. The following information was provided via fax: "The Unit 2 and 1/2 [Swing] Emergency Diesel Generators Auto Started on the ESF signal. Group II and III isolations were received as expected. Local Fire Department assisted in fire activities and extinguished transformer fire. RCIC and the Safe Shutdown Makeup Pump were manually initiated to provide level control. Relief valves were manually operated to control pressure. At 1048 CDT Transformer 22 power was restored and is providing loads to Unit 2. Both EDG's have been shutdown. The Illinois Emergency Management Agency has been notified of the Hazmat spill from the transformer fire. "A courtesy call was also made to the National Response Center for a potential of a Hazmat spill into the Mississippi River [NRC Incident Report # 575186]. "The Unusual Event was terminated at 1147 CDT." The licensee is in the process of informing state/local agencies and has informed the NRC resident inspector. Notified R3DO(Madera), EO(Madden), IRO(Holonich), EDO(Bergman) and FEMA(Caldwell). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2001-08-02
38180 | 0 | NTH CONSULTANTS |  |  |  |  | 2001-08-02 07:50 | 2001-08-02 08:49 | 2001-08-02 | STOLEN TROXLER MOISTURE DENSITY GAUGE The licensee reported a missing (presumed stolen) Troxler moisture density gauge, model #3401 serial #14236. The gauge was discovered missing from the bed of a pickup where it had been locked in its case and the case cabled to the truck. The gauge contains 2 sources, one of approximately 8 mCi Cs-137 and the other 40 mCi Am-241:Be. The licensee intends to make a police report and is retracing the trucks route from the work site back to the driver's home located in Farmington Hills, MI. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-08-02
38179 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-08-01 07:01 | 2001-08-01 09:05 | 2001-08-02 | AUTOMATIC REACTOR TRIP DUE TO NEGATIVE FLUX RATE The unit automatically tripped from 100%; the first out annunciator was Flux Rate Reactor Trip. Immediately following the trip, the rod position indicator showed that five control rods did not insert completely. The stuck control rods indicated 15-20 steps out from bottom. Operators entered their reactor trip/safety injection emergency procedure (1E0), but were able to transition to the trip recovery procedure (1ES0.1). One of the stuck control rods subsequently indicated full insertion. The unit is currently stable in Mode 3. Operators are emergency borating the reactor per 1ES0.1 a total of 1000 gallons (250 gallons per stuck rod). The licensee is continuing their trip recovery. Preliminary investigation indicates a problem with the rod control system may have led to one or more dropped control rods. The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE 1025 EDT 8/1/01 FROM DAMMANN TAKEN BY JONES * * * The licensee reported that the auxiliary feedwater (AFW) system (pumps 11 and 12) automatically actuated on steam generator low-low level following the trip, as expected. In addition, two of the stuck rods are now indicating full insertion. The NRC resident inspector has been informed of this update. * * * UPDATE 1624 EDT 08/01/01 FROM GOSMAN TAKEN BY MACKINNON * * * After interviewing the Reactor Operators it was determined that 6 rod bottom lights did not immediately come on after the reactor trip. Also a media press release will be made concerning this event. R3DO (John Madera) notified. The NRC resident inspector was notified of this update by the licensee. * * * UPDATE 0431 EDT 8/2/01 FROM IRVIN TAKEN BY STRANSKY * * * "Investigation into the cause of the reactor trip has determined that control rods associated with Rod Control Power Cabinet 2AC began to insert into the core. As designed, the reactor protection system actuated to insert the remaining control rods. "In accordance with procedures, operators verified the reactor had safely shutdown. However, indicator lights for six of twenty-nine individual control rods did not indicate that the rods had fully inserted. This situation is addressed in the reactor trip procedure and the operators responded appropriately by borating to compensate. "Control rod drop testing has been performed and has verified that all control rods fully inserted. Individual rod position indication calibration check is in progress." The NRC resident inspector will be informed of this update by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-08-01
38178 | 0 | PALMERTON PARRISH INC. |  |  |  |  | 2001-07-31 12:00 | 2001-07-31 16:26 | 2001-07-31 | TROXLER MOISTURE DENSITY GAUGE MISSING. A 3440 Troxler Moisture Density gauge, serial number 23967, containing 10mCi's of Cesium-137 (source serial # 75-5945) and 40mCi's of Am-241/Be (source serial # 47-19997) fell out of back of pickup truck at the corner of Farm roads 182 and 139. The moisture density gauge was out of its container and in the back of an open bed pickup truck with its tail gate down when it fell from the back of the truck. The driver of the truck did not notice that the moisture density gauge was missing until he arrived at his destination which was 5 miles after the corner of Farm roads 182 and 139. The driver drove back searching for the gauge when he met a farmer who said that he had seem the gauge laying in the road at the corner of Farm roads 182 and 139 around 1200 CT. Palmerton Parrish Incorporated sent 4 or 5 people out to search the area, tall vegetation and a river by the road side. A search of the area did not find the gauge. The licensee notified the Green County Sheriffs department of the missing gauge, sheriff report number is 01-6085. A bulletin will be release by the sheriff's department later today informing people of the missing moisture density gauge. The sheriff's department will also notify the local police, local fire departments, and surrounding counties of the missing moisture gauge. The gauge was bought new by the licensee back in November 1994. NRC Region 3, D. Wiedeman was notified of this event by the licensee. * * * UPDATE ON 07/31/01 AT 2002 ET BY PALMERTON TAKEN BY MACKINNON * * * The gauge was recovered after a $500 reward was offered for the recovery of the gauge. Radiation survey of the gauge found were within normal readings. R3DO (Pat Hiland) & NMSS EO (Camper) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-07-31
38177 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2001-07-30 14:45 | 2001-07-30 17:52 | 2001-07-31 | ONE SPECIAL NUCLEAR MATERIAL CONTAINER UNEXPECTEDLY RETURNED TO BWXT. Westinghouse Electric Company received a telephone call from BWXT stating they had received one 3-gallon container of uranyl nitrate crystals from Westinghouse in a SNM shipping container labeled as empty. This container was originally shipped from BWXT to Westinghouse on 07/17/01 for processing and was documented by a 741 form. Ninety-six containers were indicated on the 741, but one was inadvertently left in the outer shipping container or put back into the shipping container and returned to BWXT for the next shipment. BWXT stated that the original inner container Tamper Indicating Device was still on the container and intact. After discussion and clarification of the incident with BWXT personnel, Westinghouse Electric Company personnel determined at 1700 hours that this incident was reportable to the NRC Operation Center. ***** UPDATE FROM DAN COLWELL TO LEIGH TROCINE RECEIVED AT 1000 ON 07/31/01 ***** The licensee provided this update to correct the initial discovery date. It should have been 07/30/01 in lieu of 07/29/01. The NRC operations officer notified the R2DO (Widmann), NMSS EO (Brach), NMSS IAT (Warren), and IRO (Holonich). (Contact the NRC operations officer for licensee contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OF SNM/CRIT | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.52(a) |  |  |  | 0 | 2001-07-30
38176 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-07-30 11:10 | 2001-07-30 15:33 | 2001-07-30 | NOTIFICATION OF MISSISSIPPI DEPARTMENT OF ENVIRONMENTAL QUALITY DUE TO A CHEMICAL SPILL. Mississippi Department of Environmental Quality was notified of a minor chemical spill, fire fighting foam, on site that entered the storm drain system. The source of the spill is isolated. The spill is contained and all effects are expected to remain on site. The licensee continues to monitor the situation. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-30
38175 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2001-07-24 | 2001-07-26 14:29 | 2001-07-26 | AGREEMENT STATE REPORT INVOLVING MISSING SR-90 SOURCES "Event description: The licensee called the Division to report the loss of 997 mCi of Sr-90 sealed sources. The licensee's records indicate there were 14 individual sources received as brokered material from Stan A. Hauber Consultants, Inc., New Lenox. IL. These sources were received at the facility on June 26, 2000. Physical inventories have been performed and the sources have not been located. It is unknown whether the sources were encapsulated and sent for burial at a licensed disposal facility. This event is reportable under SRPAR 1200-2-5-.140 (1)(a).1.(i)." TN Event Report ID No.: TN-01-137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0 | 2001-07-26
38174 | 0 | WASHINGTON HOSPITAL CENTER |  |  |  |  | 2001-07-25 17:00 | 2001-07-26 14:11 | 2001-07-26 | MEDICAL MISADMINISTRATION REPORT INVOLVING ADMINISTERED DOSAGE > PRESCRIBED DOSAGE At 1700EDT on 7/25/01 a patient undergoing treatment for hyperthyroidism received a 25.7 millicurie dose of I-131 instead of the 20 millicuries prescribed (28% greater than prescribed). The licensee attributes the error to inattention to detail on the part of the technologist involved, i.e., the prescribed dosage was specified on the form. Both the patient's mother and the referring physician have been informed. Since the administered dosage is within the normal range allowed for this treatment, no adverse effects are anticipated. The licensee will determine appropriate corrective actions. Call the NRC Operations Center for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.33 |  |  |  | 0 | 2001-07-26
38173 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-07-25 10:11 | 2001-07-25 19:02 | 2001-08-09 | POTENTIAL TO DRAIN AFW STORAGE TANK DURING PLANT FLOODING SCENARIO "STPNOC Engineering identified a condition outside the station's design basis that has been determined to be reportable under 10CFR50.73(a)(2)(ii) as an unanalyzed condition that significantly degraded plant safety. Notification is required by 10CFR50.72(b)(3)(ii)(B). "During review of design calculations, a new internal flooding condition was identified that could have resulted in depletion of the AFW Storage Tank to the point where the plant would not be able to transition from AFW to RHR as designed. Each of STP's four trains of AFW is enclosed in its own water-tight compartment directly beneath its associated MFW line RCB penetration. Operator response to a main feedline break includes isolation of the faulted steam generator, including AFW. If the MFW break is postulated to occur in the MFW penetration area above AFW, the AFW cubicle beneath the break will flood. In the case of the D train steam-driven AFW, the water level will submerge the turbine-driven AFW pump, its trip/throttle valve and AFW isolation valves in about 6 to 30 minutes, depending on break size. As a consequence of the accident, the submerged motor-operated valves are assumed to fail as-is, supplying steam to the turbine-driven pump and allowing AFW flow. In addition, the analysis assumes the single failure of one unsubmerged steam supply isolation valve. The steam-driven pump will continue to function while submerged and continue to take suction from the AFWST and expel it out the break. Unless the pump is secured, its continued operation could accelerate the depletion of the AFWST to the point that the plant would not be able to transition from AFW to RHR as designed. This condition affects only the D train steam-driven AFW. Trains A, B, and C are motor driven and can be readily secured at their power source if necessary. "Compensatory action is being taken to implement a temporary modification to allow operator action to isolate the AFW supply to the steam-driven AFW pump at the AFWST." The NRC resident inspector has been informed of this condition by the licensee. ***** RETRACTION FROM WAYNE HARRISON TO L. TROCINE RECEIVED AT 1507 EDT ON 08/09/01 ***** The following text is a portion of a facsimile received from the licensee: "[...] This notification is RETRACTED. The break described above is in a break exclusion zone and is the non-mechanistic break required by the Standard Review Plan to be postulated for the purpose of defining the environmental conditions for qualification of equipment. Consideration of a single failure with this non-mechanistic break is not required. Consequently, the unsubmerged steam supply valve may be assumed to function to isolate steam to the turbine-driven AFW pump and there is not a condition that significantly degrades plant safety." The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R4DO (Charles Marschall). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-07-25
38172 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2001-07-25 15:24 | 2001-07-25 17:59 | 2001-07-25 | HPCI SYSTEM DECLARED INOPERABLE "Unit 3 high pressure coolant injection (HPCI) system inoperable. This constitutes an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(v) and 10 CFR 50.36(c)(1)(ii)(A). The unit 3 HPCI system was considered inoperable while aligned to the suppression pool. This condition was determined during the performance of an approved system operating procedure that would ensure the suction line of the HPCI system is filled and vented while aligned to the suppression pool. Adequate suction pressure could not be developed during the performance of the procedure, therefore Operations placed the auxiliary oil pump in pull-to-lock to prevent automatic starts of the system. "Unit 3 HPCI was aligned to the suppression pool in order to comply with Technical Specification Section 3.3.5.1, Required Action D.2.2. Required Action D.2.2 was performed due to a failure of the condensate storage tank (CST) level switches. The failed CST level switches caused an unplanned automatic swap of the HPCI suction line from the CST to the suppression pool. "The problem is being investigated and the cause is unknown at this time." The NRC resident inspector has been informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-07-25
38171 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2001-07-25 10:46 | 2001-07-25 15:31 | 2001-07-25 | AUTOMATIC TURBINE TRIP/REACTOR SCRAM DURING TESTING "During performance of CIV [combined intercept valve] testing per 2-OI-47 section 6.7, the unit 2 reactor scrammed due to Turbine Generator Load reject. Emergency control procedure EOI-1 was entered due to low reactor water level and high reactor pressure. PCIS [primary containment isolation system] groups 2,3, 6 and 8 were received, A, B and C SBGT [standby gas treatment] trains started and A CREV [control room emergency ventilation] started as expected. Initial indications show that some Safety Relief Valves (SRVs) momentarily opened during the pressure spike following closure of the main turbine control and stop valves. The unit remains in hot shutdown (mode 3) to continue troubleshooting the exact cause of the EHC [electrohydraulic control] logic control system causing the main turbine trip. "This event is reportable as a 4 hour ENS report per 10CFR50.72(b)(2)(iv)(B) as 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor Operation.' And an 8 hour report per 10CFR50.72(b)(3)(iv)(A) as 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(8), ie: RPS'. "This is also reportable per 10CFR50.73 (a)(2)(iv)(A) for the above conditions as a 60 day written report." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-07-25
38170 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-07-25 11:16 | 2001-07-25 13:12 | 2001-07-25 | OFFSITE NOTIFICATION REGARDING ACTUATION OF THE CIVIL DEFENSE SIRENS WHEN NO ACTUAL EMERGENCY EXISTED The following text is a portion of a facsimile received from the licensee: "During an emergency preparedness drill, a local agency (Claiborne County Civil Defense) activated the civil defense sirens. The sirens should not have been sounded for the drill. This report is being made as an event that for which notification to other agencies has been or will be made (50.72(b)(2)(xi)). Plant operation was not affected, and no release of radioactivity occurred." The licensee stated that the sirens sounded briefly (for probably less than 1 minute). At the time of this event notification, the site had not received any calls from the public. It was reported that Claiborne County Civil Defense notified local radio stations and requested them to make an announcement stating that the actuation of the sirens was unintentional and that there was no emergency. Claiborne County Civil Defense also plans to issue a press release. Applicable State, local, and other government agencies were involved in the exercise and are aware of the event. The licensee notified the acting NRC resident inspector (Peter Alter). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-25
38169 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-07-25 08:31 | 2001-07-25 11:51 | 2001-07-25 | ADDITIONAL INDICATIONS DISCOVERED ON CRDM HOUSINGS "Nondestructive examination of welds on control rod drive mechanism pressure housings has resulted in the discovery of additional indications to those reported earlier (reference event notification numbers 38083, 38103 and 38111). The weld examinations are being conducted as part of an extent-of-condition evaluation resulting from a discovery on June 21, 2001 of a through-wall indication on CRDM 21. Extent-of-condition and cause evaluation is ongoing. Regular updates with NRC Region III and NRR will continue." The licensee stated that no further notifications will be made to the NRC Operations Center regarding this issue. The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-07-25
38168 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-07-24 12:30 | 2001-07-25 05:28 | 2001-07-25 | 24 - HOUR 91-01 BULLETIN - LOSS OF ONE CONTROL OF THE DOUBLE CONTINGENCY PRINCIPLE On 7-24-01 at 1230 hours, a process operator in the X-330 Building discovered a NCSA-0330_004.A05 noncompliance with cell 29-4-6. Cell 29-4-6 is a shutdown cell at a UF6 negative and was buffered above 14 psia. Over time the pressure decrease to 13.96 psia. This violated NCSA-0330_004.A05 requirement #8 resulting in a loss of one control (moderation) of the double contingency principle. Mass (second control) was maintained throughout the event. NCSA-0330_004.A05 requirement #8 states in part, "Within 8 hours after cascade equipment shutdown (motor turned off) and with the system at a UF6 negative, the system shall be pressurized with plant air or N2 buffer at > 14 psia, unless the equipment is undergoing maintenance, pre and post maintenance troubleshooting, being evacuated or treated." Buffer pressure was increased to greater than 14 psia at 1300 hours. Moderation control was re-established for cell 29-4-6. The safety significance of this event is low. There is no deposit in this cell. The worst case would be contamination on process surfaces exposed to process gas prior to shutdown and buffering. This event is reportable per NRC BL 91-01 as a loss of one control of the double contingency principle. SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is low. There is no deposit in the cell (thus is less than a safe mass for an H/U=4 and the cell is isolated from the cascade. The mass in the cell is controlled by virtue of the fact that the shutdown cell is isolated from the cascade which is also shutdown. If the unbuffered condition were permitted to continue for a long period of time, the H/U could eventually reach a maximum of 4. However, since any material in the cell is less than the safe mass H/U ratio, a criticality would not occur even if the H/U reached the maximum through the loss of a buffer. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): The cell would need to be unisolated and UF6 introduced to create a deposit. That deposit would then have to become sufficiently moderated in order for a criticality to occur. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The parameters controlled are mass and moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): There is no deposit in this cell. Worst case would be contamination on process surfaces exposed to process gas prior to shutdown and buffering. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The NCS control is a dry air buffer >14 psia. Over time the pressure decreased to 13.96 psia. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Buffer pressure was increased to greater than 14 psia at 1300 hours. Control was re-established. The NRC Resident Inspector was notified along with the DOE Representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-07-25
38167 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-07-24 15:50 | 2001-07-24 17:35 | 2001-07-24 | OFFSITE NOTIFICATION DUE TO EXCEEDING NPDES PERMIT LIMITS "The EPA and NH Department of Environmental Services (NHDES) were notified this afternoon of a daily maximum exceedence of the NPDES Permit limit for oil and grease at Outfall 025 (Waste Test Tank). The discharge occurred on July 3, 2001. The amount of the exceedence is minor but the significance is still being evaluated so this report is being made as a conservative decision." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-24
38166 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-07-23 14:30 | 2001-07-24 13:25 | 2001-07-24 | 24-HOUR NRC BULLETIN 91-01 REPORT "Background "Various waste streams are discharged to Waste Tanks WD01 and WD02 from various sources. Various controls on these sources prevent significant accumulations of U-235 in the tanks. These controls include dual sampling, filtration, visual inspections, and the use of an in-line monitor. In addition, significant process knowledge and history is available for the systems and a major process upset, in addition to failure of these controls, would have to occur in order for significant accumulations of U-235 to occur. The in-line monitor is located on the 'P-Trap' portion of the line. "Event "As a result of recent modifications associated with the discharge line to Waste Storage Tanks WD01 and WD02, it was determined that some discharge solution being discharged to the Storage Tanks may not be monitored effectively by the in-line monitor located on the discharge line to the waste tanks. Recent modifications to the discharge line included the relocation of the in-line monitor, the installation of a drain line on the discharge line's 'P-Trap,' and the use of clear PVC pipe on the 'P-Trap' so that the line's contents could be observed. The modifications were completed over the weekend of 7/21/2001 and the discharge line was first put into operation on 7/23/2001. "During observation of discharges from Area 800 to the Storage Tanks on 7/23/2001, it was observed that the discharge line 'P-Trap' was not completely full of solution. In other words, solution was slowly trickling into the 'P-Trap' and air was observed in the line. The in-line monitor is most effective when the line is completely full of solution and it was determined that the Area 800 pumps, when operated in continuous mode, pumped air into the line such that the line was only partially filled with solution. "Compensatory Measures "Discharges to the waste tanks were immediately suspended. Discharges from Area 800 to Storage Tanks WD01 and WD02 were then placed in 'manual mode.' In other words, the pumps used to make discharges from Area 800 were placed (operated) in a manual mode as opposed to continuous mode. Discharges are made as needed; however, when air is observed in the discharge line near the in-line monitor, the discharge is suspended. Additional long-term engineering modifications are being planned. "The solution in Waste Tank WD01 (collected on 7/23/20011 was also measured (0.0098 gU/l and 0.0108 gU/l). The tank contained a total of approximately 400 gallons or approximately 16.5 grams U-235. "What is the safety significance of the event? "Low safety significance due to defense-in-depth associated with the waste tanks. "Brief scenario(s) of how criticality could occur: "Major process upset combined with failure of controls associated with the particular discharge stream (filters, sampling, visual inspections). "Controlled parameter(s): "Mass. "Estimated mass: 16.5 g U-235, Enrichment: 97.3 wt.% U-235 "Form of licensed material: low level waste solution, Process limit: 476 g U-235 "Percent of worst case critical mass: 2.0% "What is the control(s) or control system(s) and the failure(s) or deficiencies? "Partial loss of one control (in-line monitor). Concentration is used to control mass. Monitor is most effective when discharge line (near detector) is full. Air in line (created by Area 800 discharge pump) caused 'trickling effect' through the line past the detector when Area 800 solution is being discharged. "What are the corrective actions taken and when was each implemented? "Upon immediate observation of situation, discharge to WD01/WD02 was suspended (Area 800 was only stream being discharged) ~2:30 p.m. on 7/23/01. Suspected situation was caused by Area 800 discharge pump. Pumps were running in continuous mode and putting air in line. Pumps were placed in manual mode (~3:00 p.m.) which minimized air effects." The licensee has contacted NRC Region II (McAlpine) regarding this issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 1 | 2001-07-24
38165 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2001-07-24 06:39 | 2001-07-24 10:00 | 2001-07-24 | AUTOMATIC REACTOR TRIP ON HIGH REACTOR COOLANT SYSTEM PRESSURE The unit received an automatic reactor trip on high reactor coolant system pressure due to a problem with the main turbine control valves. There were no ESF actuations and all rods fully inserted. Steam generator safeties opened for a short period as expected. The plant is stable in hot shutdown with excess heat being controlled by condenser bypass valves with main feedwater system controlling steam generator level. The problem is being investigated and the cause is unknown at this time. The licensee notified the NRC Resident Inspector and state agencies. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-07-24
38164 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2001-07-24 02:51 | 2001-07-24 05:59 | 2001-07-24 | AUTOMATIC REACTOR SCRAM ON HIGH REACTOR VESSEL LEVEL The reactor scrammed at 0251 CDT on 7/24/20001 on a level 8 signal, a high reactor vessel level. All rods fully inserted and all systems functioned properly. At the time of the scram there was a surveillance being performed on a level transmitter that feeds the feedwater level control system. Exactly what happened is not known at this time, but an investigation is ongoing. The plant is stable using the bypass valves to the condenser and level is being maintained with motor driven feedwater pump. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-07-24
38163 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-07-23 21:36 | 2001-07-23 22:19 | 2001-07-23 | UNUSUAL EVENT DECLARED DUE TO LOW SERVICE WATER INTAKE LEVEL At 2136, the licensee declared an Unusual Event due to service water intake pump well level less than 60.7' MSL (mean sea level). The licensee determined that one of the intake traveling water screens had become clogged with debris, cleared the screen, and terminated the UE at 2137 when normal pump well level was restored. Reactor power of both units was reduced as a result of the event. The licensee's preliminary investigation indicates that the upstream traveling water screen did not automatically enter a backwash cycle as designed in response to increased differential pressure. The downstream screen was tagged out of service for a planned design modification. The NRC resident inspector has been informed of this event by the licensee. | 85 | 90 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-07-23
38162 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-07-23 17:45 | 2001-07-23 18:34 | 2001-07-23 | SECURITY REPORT Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. The NRC resident inspector will be informed. Contact the NRC Operations Center for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-07-23
38161 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-07-23 12:55 | 2001-07-23 17:27 | 2001-08-07 | 4-HOUR NRC BULLETIN 91-01 REPORT The following text is a portion of a facsimile received from Paducah personnel: "At 1255, on 7-23-01, the Plant Shift Superintendent (PSS) was notified that checks required to meet the requirements of NCSA CAS-011 were not performed during replacement of the C-337 Unit 5 Cell 10 RCW [recirculating cooling water] spool piece. NCSA CAS-011 requires a line clarity check on the peak reading pressure gauges prior to connecting the spool piece. This check was not performed. The purpose of this requirement is to ensure the RCW pressure in the condenser does not exceed 35.5 PSIA. "The NRC Acting Senior Resident has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: "While a control was violated, insufficient time existed for moisture from the RCW system to enter the process gas system. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "In order for a criticality to be possible, the following conditions must exist. With the condenser RCW supply and return valves closed, the supply or return valve must be leaking to allow the condenser pressure to exceed the minimum coolant pressure of 35.5 PSIA. The process gas equipment must contain a UO2F2 deposit greater than a critical mass. The condenser must have a leak of sufficient rate and duration to allow enough water to overcome the down corner allowing liquid water to enter the cooler. The cooler must also have a simultaneous leak which would allow wet coolant to leak into the process gas side of the equipment at a location which would allow a moderation of the deposit. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): "Two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "No known deposits of concern at this time.. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Double contingency for this scenario is established by implementing two controls on moderation. "The first leg of double contingency is based on preventing moderation of a deposit by maintaining the RCW pressure in a condenser below 35.5 PSIA. Pressure gauges are installed and checked for clarity whenever the RCW return valve is closed on a cell without a fluorinating environment. Since clarity of the pressure reading instrument was not verified, the functionality of the pressure reading instrument cannot be assured, violating the control. "The second leg of double contingency is based upon independent verification that the RCW pressure gauges are reading correctly. Since clarity of the pressure reading instrument was not independently verified, this control was violated. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Upon discovery of the failure to perform the requirement, the coolant system was sampled for moisture and verified to be dry." * * * UPDATE AT 1623EDT ON 8/7/01 FROM MIKE UNDERWOOD TO S. SANDIN * * * This report is retracted based on the following: "UPDATE 8-7-01: THIS EVENT HAS BEEN RETRACTED. Additional information was discovered which changes the initial evaluation of the violation. In preparation for maintenance, the peak reading pressure gauges were adequately installed on the condenser head and clarity verified prior to isolating the condenser. Since the maintenance involved the RCW control valve, it was not necessary to remove the pressure gauges. The normal course of events would be to remove the pressure gauges after the condenser is drained. However, in this case, the maintenance evolution was limited and Cascade Operations decided to leave the pressure gauges installed on the condenser head. If the pressure gauges had been removed while the RCW system was drained the gauges would have been required to be reinstalled and clarity verified prior to reestablishing system integrity. Once system integrity is reestablished, the pressure gauges are used to ensure the RCW pressure in the condenser does not exceed 35.5 psia. The clarity check supports the double contingency principle by ensuring the common instrument line to the gauges is not blocked. However, in this case, the gauges were not removed and the instrument isolation valves were not manipulated. Therefore, clarity was maintained. "After the maintenance had been performed, Operations realized the second clarity check had not been performed. At this point, NCS was contacted and direction was given to perform the remedial actions as if the pressure limit were exceeded according to NCSA CAS-011. These actions included opening the RCW return valve and sampling the coolant system for moisture, which was found to be below the moisture limits, These actions were performed within the NCSA CAS-011 required inspection frequency of 12 hours. "After the incident report was competed, it was discovered that the pressure gauges had not been removed from the condenser head. Therefore, the requirement for the reinstallation and clarity check of the pressure gauges had already been performed. Since the requirement of NCSA CAS-011 to perform a clarity check was met and the system conditions were clearly bounded by the analysis of NCSA CAS-011, no violation occurred. "The NRC Acting Senior Resident has been notified of this event." Notified R3DO(Stone) and NMSS(Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-07-23
38160 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-07-22 17:44 | 2001-07-22 19:08 | 2001-07-22 | CALLED IN AS A 24 HOUR NOTIFICATION A dead sea turtle, species unknown, was discovered in dilution intake structure bay # 5. The sea turtle has a gash in the back of the head which may have been caused by a boat propeller. National Marine Fisheries was notified. The licensee will notify the New Jersey Department of Environmental Protection. The licensee will contact the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2001-07-22
38159 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-07-22 13:30 | 2001-07-22 15:15 | 2001-07-22 | OFFSITE NOTIFICATION REGARDING A MINOR FISH KILL This notification was being made pursuant to 10CFR50.72(b)(2)(xi), Braidwood Station Technical Specification Appendix B 4.1, and Exelon Reportability Manual Section SAF 1.9. At 1330 CDT on 07/22/01, it was communicated to the Illinois Department of Natural Resources that approximately 700 fish had perished in a minor fish kill in Braidwood Nuclear Station cooling lake due to increased temperature. As summer air temperature increased, the cooling lake temperature increased to above 97 degrees F, beyond the threshold at which point species susceptible increased temperature begin to perish. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-22
38158 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2001-07-21 15:28 | 2001-07-21 18:26 | 2001-07-21 | OFFSITE NOTIFICATION REGARDING A MINOR FISH KILL IN THE COOLING LAKE DUE TO INCREASING SUMMER TEMPERATURES The following text is a portion of a facsimile received from the licensee: "... this notification is being made pursuant to 10CFR50.72(b)(2)(xi) and Exelon Reportability Manual Section SAF 1.9. At 1528 CST on 07/21/01, it was discovered that a minor fish kill took place in LaSalle County Nuclear Station's cooling lake due to increased temperature. As summer air temperatures increase, the cooling lake temperature increased to 97°F, beyond the threshold at which point species susceptible to increased temperature begin to perish. It was communicated to the Illinois Department of Natural Resources that approximately 2,000 fish, mainly Gizzard Shad, had perished." The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-21
38157 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-07-20 14:50 | 2001-07-20 21:57 | 2001-07-20 | DISCOVERY OF THE POTENTIAL FOR A LOSS OF REACTOR CORE ISOLATION COOLING (RCIC) REMOTE SHUTDOWN PANEL CAPABILITY DURING A POSTULATED MAIN CONTROL ROOM FIRE The following text is a portion of a facsimile received from the licensee: "A review of the Limerick fire safe shutdown analysis identified that during a fire in the control room, RCIC system operation from the remote shutdown panel (RSP) may not be available for safe shutdown of the unit. A postulated fire that results in a short of the Division 1 DC distribution system to ground causes a voltage control device to fail integral to [an RSP] instrument power supply inverter. This ground, potentially caused by a fire that affects Division 1 DC in the control room, results in failure of the fused instrument power supply to the RCIC RSP inverter." "The current fire safe shutdown analysis credits only one safe shutdown method as being analyzed as acceptable during a worst case main control room fire. This analysis requires RCIC to be operational from the RSP to support acceptability of the method. With this loss of RCIC RSP capability during a [main control room] fire, this event is reportable under 10CFR50.72(b)(3)(ii)." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-07-20
38156 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-07-20 16:15 | 2001-07-20 17:06 | 2001-07-20 | OFFSITE NOTIFICATION REGARDING A SODIUM NITRITE CHEMICAL RELEASE The following text is a portion of a facsimile received from the licensee: "Notification is being made for exceeding the reportable quantity for release of sodium nitrite from a closed cycle cooling system to the outfalls discharging effluents from the V.C. Summer Nuclear Station to the environment (Lake Monticello). A drain valve was left open during maintenance on an instrument air compressor at approximately 1600 hours on 7/19/01. The drain line discharged effluent from a closed cycle coolant system containing sodium nitrite to the plant sumps for approximately 16.5 hours. Following isolation of the line, a review of flow rates and discharge paths found (completed at 1615 hours on 7/20/01) that approximately 16,000 gallons of effluent had been discharged from the plant to the environment." "It has been determined that approximately 135 pounds of sodium nitrite was discharged from the plant during this period. The reportable quantity for release is 100 pounds in a 24-hour period." "The hazard from sodium nitrite is from the pH level of 10.5. A daily check of pH at the plant outfall that received this discharge found the pH to be 9.0; therefore, there is no hazard to the environment from this release since this is the normal pH at this sample point. Plant personnel will continue to check the pH level of this discharge point each day." The licensee reported that they have not observed any environmental impacts and that there was no release of radioactive materials. The licensee notified the Environmental Protection Agency via the National Response Center at 1650 hours, and the National Response Center is documenting this event under report #573719. Because the site is located in an Agreement State, the licensee also notified the South Carolina Department of Health and Environmental Control at 1700 hours. In addition, the licensee notified the Local Planning Committee and the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-20
38155 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-07-19 17:10 | 2001-07-19 21:57 | 2001-07-19 | BULLETIN 91-01 RESPONSE (4-Hour Report) - LOSS OF ALL DOUBLE CONTINGENCY CONTROLS APPLICABLE TO A FISSILE MATERIAL OPERATION DUE TO AN INADEQUATE NCS EVALUATION The following text is a portion of a facsimile received from Paducah personnel: "DESCRIPTION OF OCCURRENCE:" "Neither NCSA GEN-010 [which deals with equipment removal and replacement] nor NCSA CAS-011 [which deals with cell shutdown and the controls for equipment moderation control] establish necessary moderation controls to ensure double contingency is maintained for the transition between equipment removal and cell shutdown. [Essentially, if a cell is taken out of service and a piece of equipment is removed, there are no controls in place to ensure that the equipment that goes back in has met the requirements of control 3.3.6 of CAS-011, and the purpose of this control is to prevent moderation by heating the equipment up to 140°F for 60 hours.] Control 3.3.6 of NCSA CAS-011 establishes a baseline hydration level for maintaining double contingency on shutdown process equipment." "NUCLEAR CRITICALITY SAFETY CONTROLS INVOLVED AND THEIR IMPACT ON DOUBLE CONTINGENCY:" "NCSE 039 establishes double contingency based on two controls on moderation." "Controls have not been established to ensure moderation control is maintained during the transition from equipment installation activities performed under NCSA GEN-010 and cell shutdown approved under NCSA CAS-011. Therefore, double contingency was not maintained." "Potential Critical Pathways:" "In order for a criticality to be possible, an equipment item containing a hydrated UH by mass deposit would have to be installed in the cascade. Following installation, normal equipment treatment activities would have to fail to dehydrate the deposit. Following startup, the equipment would have to fail to operate at or above 140 F for 60 hrs. The deposit would then have to more than double in size and achieve a total of at least 10 kg of water hydration in a geometry favorable to result in a critical configuration." "Safety Significance:" "No NCSA controls have been established to address the currently allowed transition from equipment installation to cell shutdown." "EXCLUSION ZONE AND POSTINGS:" "None." "CORRECTIVE ACTIONS:" "1. Areas of the cascade containing equipment that was installed following implementation of NCSA CAS-011 should be reviewed to determine if the drying requirements established in NCSA CAS-011 have been met." "2. Discontinue installation of process gas equipment containing fissile deposits until adequate controls have been established for this transition." "3. Include work packages related to GEN-010 equipment installation on Work Control Functional Directive WC-99-001." Paducah personnel plan to ensure that these requirements are addressed in the procedures in addition to following up on equipment that could potentially have been installed that was not addressed under these requirements. Paducah personnel notified the NRC resident inspector (Rob Krsek). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-07-19
38154 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-07-19 16:30 | 2001-07-19 17:10 | 2001-07-19 | SECURITY REPORT Unescorted access was granted inappropriately to an NRC employee and two NRC contractors. Immediate compensatory were measures taken upon discovery. (Call the NRC operations officer for additional details.) The licensee plans to notify the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-07-19
38153 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2001-05-14 | 2001-07-19 10:34 | 2001-07-19 | 10 CFR 21 REPORT - POTENTIAL FOR MAJOR DEGRADATION OF SAFETY EQUIPMENT The following is from a faxed report: "Basic component: Safety-related terminal block (symbol #95-10-077) "Supplier: Systems Control of Iron Mountain, Michigan [manufacturer is General Electric, both supplier and manufacturer have been contacted by NMP.] "Nature of defect: While installing a new terminal block in the emergency diesel generator panels, a mounting screw for terminal points was found to be loose. Contrary to general quality requirements stated in the Purchase Order, this screw was not fully threaded during manufacture. As a result, if installed, the screw could potentially have fallen into safety-related equipment located below thereby potentially affecting the function of the emergency diesels. Thus, a major degradation of essential safety-related equipment ,i.e., a substantial safety hazard, could have occurred. "Number of terminal blocks initially estimated to be affected at Nine Mile Point Units 1 and 2: Several hundred (including 169 in stock) "Corrective actions taken: The defective terminal block was discarded, A 20 percent sample inspection of the terminal blocks remaining in stock at NMP was performed. No other loose screws were identified. These terminal blocks were supplied in the 1980s and no plant operational problems due to a loose screw in a terminal block were previously identified. Therefore, it has been concluded that this is an isolated instance. "Date of discovery: May 14, 2001 "Date on which 10CFR21 evaluation completed: July 12, 2001 "Date on which Vice President Nuclear Generation notified: July 17, 2001 "Date by which written 10CFR21 report will be submitted: August 16, 2001 The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21 |  |  |  | 0 | 2001-07-19
38152 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-07-19 03:00 | 2001-07-19 05:16 | 2001-07-19 | TECH SPEC REQUIRED SHUTDOWN DUE TO TIME LIMIT ON NON-SAFETY POWER TO INSTRUMENT BUS The licensee entered Technical Specification 15.3.7(b)(1)(j) at 1900 CDT on 7/18/2001, which allowed 8 hours to restore electrical power from a safety powered bus to the Unit 1 instrument bus. Non-safety power was provided when a problem caused an automatic transfer. At 0300 CDT on 7/19/2001, a Technical Specification required shutdown was commenced. The plant has 6 hours to reach Hot Shutdown and another 44 hours to reach Cold Shutdown. The licensee has been and continues to research the problem and does not know when safety power will be restored to the instrument bus. The licensee notified the NRC Resident Inspector. * * * UPDATED AT 0936 EDT ON 7/19/2001 BY MIKE MEYER TO FANGIE JONES * * * The licensee restored power from a safety powered bus to the instrument bus and has exited the Tech Spec required shutdown. Plant is being restored to full power. The licensee notified the NRC Resident Inspector. The R3DO (Bruce Jorgensen) has been notified. | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2001-07-19
38151 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-06-09 | 2001-07-18 15:30 | 2001-07-18 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following is taken from a faxed report: "We have recently experienced an incident resulting in the compromising of the shielding around an Iodine-125 prostate implant seed (sealed source). This report is filed per the requirements of RH 458 "On June 5, 2001, during the course of an I-125 seed implant of a patient's prostate gland an Iodine-125 seed which was thought to have been implanted was instead withdrawn with the implant plunger back into a position partly in the implant applicator and partly in the seed cartridge. This seed position will not allow the cartridge to be removed normally from the implant applicator. A GM counter (thin end window) survey was performed over that section of the implant applicator but the presence of the seed was not detected. The cartridge was then forcefully removed from the applicator. The applicator was rinsed into a stainless steel basin to remove blood clots that were present. The routine survey at the end of the procedure indicated that a seed was present in this washbasin. A bent seed was found in a blood clot. When the seed was removed from the basin, a survey of the basin indicated that the water was also contaminated. It was concluded that the shielding around the seed had been compromised. "The contents of the rinse basin were poured into a plastic container that could be sealed. All equipment, which had come in contact with the seeds, was surveyed and cleaned until wipe tests demonstrated that removable contamination had been reduced to less than 200 dpm. The sealed plastic container containing the contaminated liquid, and all of the cleaning materials were placed in our long-term waste storage facility for decay. Absorbent material was added to this container on July 11th to soak up any remaining liquid and eliminate any potential spill hazard over the two years (10 half-lives) this container will be in storage. "The two individuals most closely involved in extracting the seed cartridge and performing the cleanup were given thyroid bioassay exams in the week immediately following the incident. Those exams were negative. The patient was given the same exam approximately one month following the procedure that indicated an uptake of 0.2 ± 0.09 µCi corrected to the day of the implant. If this uptake is real and not the result of radiation scatter from his active prostate seed implant (87 seeds, 22.3 mCi on the day of the thyroid scan), this would result in a radiation dose to the thyroid of not more that 0.8 cGy. This radiation dose has no clinical significance. "Corrective Actions: This incident occurred because the applicator plunger, which most likely had a blood clot adhering at the point normally in contact with the iodine-125 seed, extracted the seed previously pushed into the prostate gland. The seed, believed to have been implanted, instead came to rest across the space between the applicator body and the seed cartridge. A GM survey of the applicator body and cartridge combination failed to detect the presence of the seed. The seed was damaged when the cartridge was forcefully withdrawn. "This incident could have been averted using the following procedure: 1. Assume that any cartridge jam is caused by an unaccounted for I-125 seed. 2. Remove the implant needle from the applicator body. (If there is believed to be only one seed involved in the jam, the applicator body may be surveyed by directing the sensitive portion of the GM detector down the barrel of the applicator previously occupied by the implant needle. The GM detector may not be sensitive enough to detect radiation though the sides of the applicator body.) 3. Place the body of the applicator with the cartridge still in place, into the rinse pan. 4. Advance the plunger slowly through the seed cartridge until the seed is visible and can be rinsed away from the body of the applicator. (This may requite lifting the cartridge plunger to allow the applicator plunger past such that it can traverse the full extent of the cartridge.) If the cartridge is not empty the seed causing the jam will be pushed out by another seed so two seeds will deposit in the rinse basin. 5. Withdraw the applicator plunger completely and remove the seed cartridge normally. 6. NEVER forcefully remove a seed cartridge! "All individuals involved In this incident have reviewed this procedure." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-07-18
38150 | 0 | MATHY CONSTRUCTION CO |  |  |  |  | 2001-07-18 12:00 | 2001-07-18 15:11 | 2001-07-18 | THE LICENSEE REPORTED THEIR TROXLER GAUGE WAS STOLEN The licensee reported that a Troxler moisture density gauge model 3440 serial #26689 containing 8 millicuries of Cs and 40 millicuries of Am/Be was stolen from the back of a truck in Barabo, WI. This occurred within 5-10 minutes when the driver entered a store to use the bathroom and buy some ice. The licensee will notify the local police and the State. * * * UPDATE ON 7/18/01 @ 1553 FROM DUKATZ TO GOULD * * * The local police contacted the licensee @ 1550 to inform them the gauge was located. There was no damage and the gauge was intact. Licensee has sent a technician to retrieve the gauge. Regon 3 (Darrel Wiedeman) and NMSS (Susan Frant) have been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | WI | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-07-18
38149 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-07-17 15:30 | 2001-07-18 13:05 | 2001-08-01 | HIGH PRESSURE FIRE WATER SPRINKLER SYSTEM DECLARED INOPERABLE On 7/17/01 at approximately 1530 hrs, the Plant Shift Superintendent (PSS) was notified that during a Fire Protection Engineering assessment/inspection that High Pressure Fire Water (HPFW) sprinkler system #165 in the X-333 Building contained five adjacent sprinkler heads with visible corrosion deposits. Previous engineering reviews have concluded that the system under this condition would not be capable of meeting the Technical Safety Requirements (TSR) to maintain operability. The PSS declared the affected sprinkler system inoperable and TSR required actions were implemented. The NRC Resident Inspector was notified along with the DOE Representative. * * * RETRACTION ON 08/01/01 AT 1600 ET BY KURT SISLER TAKEN BY MACKINNON * * * This event is being retracted based upon engineering evaluation (EVAL-SE-2001-0321) approved on July 31, 2001. Functional testing of these sprinkler heads was conducted. The results showed that all these sprinkler heads would have operated when needed and performed their intended safety function. R3DO (John Madera) & NMSS EO (Brian Smith) notified. The NRC resident inspector was notified of this retraction by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2001-07-18
38148 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-07-18 07:59 | 2001-07-18 10:42 | 2001-07-18 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP DURING RESTORATION OF AMSAC ALARM "During restoration of AMSAC [Accident Mitigation System Actuation Circuitry] to restore a trouble alarm, a spurious turbine trip signal was generated, causing a reactor trip from 100% power. AFW [Auxiliary Feedwater] actuation followed the reactor trip and the MSIV's [Main Steam Isolation Vales] were closed for temperature control." All control rods fully inserted. Unit 2 is currently stable at normal operating pressure and temperature (NOP, NOT) using the Atmospheric Dumps and both motor-driven AFW pumps for decay heat removal. There is no known primary-to-secondary tube leakage and samples confirm less than minimum detectable activity (<MDA). Operators are in the process of re-opening the MSIV's to place the main condenser back in service. All electrical buses remained energized throughout the event. The licensee notified the NRC resident inspector and does not plan a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-07-18
38147 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-07-17 | 2001-07-17 19:37 | 2001-07-17 | STATE OF CALIFORNIA REPORTED THAT ONE OF THEIR LICENSEES HAS LOST A MOISTURE DENSITY GAUGE During an inventory, the licensee could not locate one of their Troxler moisture density gauges (model 3321B serial #279). The device contained 8-10 millicuries of Cs-137 and 30 millicuries of Am-241. The gauge was last seen 6 months ago. The loss was reported to the police. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2001-07-17
38146 | 0 | TENNESSEE VALLEY AUTHORITY |  |  |  |  | 2001-07-13 | 2001-07-16 16:57 | 2001-07-16 | THE LICENSEE REPORTED THE RELEASE OF CONTAMINATED MATERIAL On 7/13/01 two 30 gallon trash cans containing expendable contaminated lab items such as pipette tips, gloves, empty bottles, beakers, etc. were emptied into a dumpster. These items were at very low levels and had been collected in the two trash cans since January. The typical analysis that is done in the laboratory is on nuclear plant effluent samples from which these items received their contamination. Only the items used to handle the effluent sample material were discarded in the two trash cans. The material itself was not disposed in these trash cans. The dumpster was taken to the Hillsboro landfill in Lawrence County, AL this morning. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | AL | OTH | GEN |  |  |  |  | 0 | 2001-07-16
38145 | 0 | NORTECH ENVIRONMENTAL |  |  |  |  | 2001-07-16 08:00 | 2001-07-16 16:36 | 2001-07-16 | NORTECH ENVIRONMENTAL REPORTED THAT AN X-RAY FLUORESCENCE DEVICE WAS STOLEN FROM THEIR OFFICES The device was stolen sometime this past weekend, but was just discovered this morning at 0800 YDT to be missing. The device was a Niton XL model 309 serial #U1002 containing 14 millicuries of cadmium-109 (serial #NR0853). This device was a hand held device used to analyze for lead in paint. The local police and Niton have been notified. The State will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AK | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-07-16
38144 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-07-16 10:33 | 2001-07-16 14:51 | 2001-07-19 | PLANT HAD A MAJOR LOSS OF OFFSITE PUBLIC ALERTING SIREN SYSTEM While performing the weekly siren test, 35 of 47 sirens failed to respond. The weekly test was performed at 1033 EDT. Preliminary investigation suggests a problem with the sirens electronic memory chip. Troubleshooting and repairs are in progress. The NRC resident inspector has been notified. ***** UPDATE FROM JOHN C. WILLIAMS TO LEIGH TROCINE AT 1621 ON 07/19/01 ***** The following text is a portion of a facsimile received from the licensee: "This is an Information Only follow-up notice to Event Notification #38144, submitted on 7-16-2001, regarding the loss of 35 out of 47 sirens in the Offsite Public Alerting Siren System." "All sirens were tested and returned to service as of 1516 EDT on 7-18-2001. A vendor representative from Whelan Engineering Company has advised that cause of the problem was a software issue with a batch of 2020 logic control boards, revision E or prior, used in the siren controller. He further states that he knows of no other nuclear facilities that have these controller boards at this time." The licensee notified the NRC resident inspector. The NRC operations officer notified the R2DO (Jay Henson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-07-16
38143 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-07-16 09:58 | 2001-07-16 11:20 | 2001-07-16 | AUTOMATIC REACTOR TRIP DURING MAINTENANCE "The channel 2 of the 2B streamline pressure was in test. The channel 3 of the 2B streamline pressure was taken out of service (transmitter). This resulted in meeting the logic for main streamline isolation (2/3). This resulted in a reactor trip on overtemperature delta temperature. Auxiliary feedwater autostarted due to decreasing steam generator water levels. This event started as a result of preventative maintenance of steam generator pressure 2B channel 2." All rods fully inserted. Unit 2 is stable in mode 3 at 2235 psig and 556 degrees F with decay heat removal bypassing the main streamline isolation valves to the main condenser. Efforts are underway to restore main feedwater and secure the operating auxiliary feedwater pumps (both electrical and the turbine driven). During the transient all three primary PORVs lifted and reseated while secondary safety valves also cycled. There is no known primary-to-secondary tube leakage. All emergency equipment is available, if needed. The licensee informed the NRC resident inspector and does not plan a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-07-16
38142 | 0 | WATERFORD | 3 |  |  | [3] CE | 2001-07-15 21:58 | 2001-07-15 23:32 | 2001-07-16 | ALERT DECLARED DUE TO TOXIC GAS RELEASE NEAR PLANT SITE The licensee declared an Alert (EAL EP-4-010 "Toxic Chemical Contingency") due to an anhydrous ammonia release at the Occidental Chemical facility located near the site. The licensee reported that no ammonia has been detected onsite; however, personnel sheltering has been implemented. The release is ongoing and the chemical facility cannot estimate when the release will be secured. The NRC entered Monitoring at 0012EDT on 7/16/01. * * * UPDATE 0300EDT ON 7/16/01 FROM LICENSEE COMMUNICATOR TO S.SANDIN * * * The licensee terminated the Alert at 0200CDT after verifying that all exiting conditions were satisfied. The licensee informed the NRC resident inspector and will inform state/local agencies. The NRC exited Monitoring at 0315EDT on 7/16/01. Notified FEMA(Canupp), DOE(Stambaugh), EPA-DOT(Loreck), USDA(Conley) and HHS-CDC(Cruz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 4 | LA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-07-15
38141 | 0 | McDOWELL AND ASSOCIATES |  |  |  |  | 2001-07-13 07:30 | 2001-07-13 16:24 | 2001-07-13 | STOLEN MOISTURE/DENSITY GAUGE A Troxler Model 3440A moisture/density gauge (S/N 14786) was stolen from its locked storage case. The gauge and case were chained to the bed of a pickup truck that was parked in Shelby Township, MI. The licensee has contacted local law enforcement agencies and has already contacted NRC Region III regarding this matter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-07-13
38140 | 0 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2001-07-12 19:00 | 2001-07-13 15:12 | 2001-07-13 | MEDICAL MISADMINISTRATION An individual prescribed a dose of 2.8 - 3.46 GBq (75.6 - 93.5 mCi) of Y-90 only received 1.1 GBq (29.7 mCi) due to a procedural error. The Y-90 was in the form of insoluble glass microspheres and was being injected into the liver in a saline solution. The procedure was being performed under an FDA approved humanitarian device exemption. During the treatment, the seal on the vial containing the microspheres was not properly pierced, causing backpressure to develop in the delivery lines and forcing some of the microspheres to back up into the treatment device. The licensee is implementing additional controls to prevent recurrence of this type of event. In addition, the device vendor (MDS Nordion) will continue with onsite proctoring of dose administrations until all treatment staff are fully trained. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0 | 2001-07-13
38139 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-07-13 08:55 | 2001-07-13 14:52 | 2001-07-27 | APRM FLOW-BIASED SCRAM SETPOINTS SET NONCONSERVATIVELY "On July 13, 2001 at 0855 hrs, with the reactor at 100% core thermal power, Pilgrim Station determined the Average Power Range Monitoring (APRM) system flow-biased reactor scram setpoints were non-conservative and potentially exceeded Core Operating Limit Report (COLR) analyses. Programmed Flow Control Trip Reference (FCTR) cards establish the APRM flow-biased scram setpoints. The FCTR cards are a plant enhancement in response to the BWR stability issue. During core flow mapping for FCTR card calibration in accordance with station procedure (9.17.1), it was determined by reactor engineering personnel that the input setting for the FCTR card DIP switches was non-conservative. In response to this event, the APRMs were declared inoperable and Technical Specification 3.1 and the Actions of Table 3.1.1 were initiated. TS Table 3.1.1 requires that reactor trip capability for the given trip function be restored within 1 hour or initiate insertion of operable control rods and complete insertion of all operable control rods within 4 hours. However, Instrumentation and Controls personnel completed FCTR card DIP switch adjustments in accordance with station procedure (3.M.2-5.4.s) within approximately 45 minutes. All APRM RPS functions were declared operable at 0946 hours and TS 3.1 was exited. The reactor remained at 100% core thermal power throughout the event and there were no plant transients as a result of the event. "The cause of the event appears to [be] a lack of administrative controls to ensure the FCTR card flow mapping be performed when steady-state 100% core thermal power is achieved following refueling outages or significant power maneuvers." The licensee informed the NRC resident inspector and will inform the Commonwealth of Massachusetts. * * * UPDATE AT 1221EDT ON 7/27/01 FROM OLSON TO S. SANDIN * * * The licensee is retracting this report based on the following: "Pilgrim Station retracts a report made to the NRC Operations Center on July 13, 2001 at 1500 hours. The Event Number was 38139. The report was made pursuant to 10 CFR 50.72(b)(3)(v)(A) when it was determined the Average Power Range Monitoring (APRM) system flow-biased reactor scram setpoints were set non-conservatively. "Subsequent testing has determined that the setpoints were set conservatively and that the APRM flow-biased reactor scram was operable. Therefore, no situation existed which was reportable pursuant 10 CFR 50.72(b)(3)(v)(A). "The NRC resident inspector has been informed of this retraction." Notified R1DO(White). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-07-13
38138 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2001-07-13 08:21 | 2001-07-13 14:51 | 2001-07-13 | AUTOMATIC REACTOR TRIP "On July 13, 2001, at approximately 08:21 MST Palo Verde Unit 2 experienced an automatic reactor trip (RPS actuation) from approximately 100% rated thermal power due to low Departure from Nucleate Boiling Ratio (DNBR) trip generated by the Core Protection Calculators (CPCs). The DNBR trip resulted from the closure of 3 of the 4 main steam isolation valves (MSIVs). Unit 2 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. No ESF actuations occurred and none were required. An investigation of this event has been commenced to determine why the MSIVs closed. "Due to the MSIV closures, two of twenty main steam safety valves (MSSVs) lifted to relieve secondary pressure. Operators restored reactor coolant system heat removal using atmospheric dump valves and feedwater to the steam generators is being supplied by the B train main feedwater pump. "Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 2 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-07-13
38137 | 0 | BURLINGTON INDUSTRIES |  |  |  |  | 2001-07-13 | 2001-07-13 14:07 | 2001-07-13 | LOST AM-241 SOURCE A source purchased from Panametrics (under general license 20-07181-04G) and delivered to the facility in 1977 was inadvertently placed in a scrap metal bin and picked up by a scrap metal dealer in 1997. The device contained a 10 mCi Am-241 source. The scrap metal dealer was contacted, but the whereabouts of the material are unknown. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-07-13
38136 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-07-12 | 2001-07-12 18:33 | 2001-07-12 | AGREEMENT STATE REPORT "The Oregon licensee reported that a Troxler model 3430 portable gauge, serial number 28872, containing 10 mCi of cesium-137 and 50 mCi of americium-241 was stolen from a locked cargotainer at a work site in Washington state. The Oregon Licensee had transported the portable gauge to the work site of a Washington licensee in order to complete a sales transaction. The licensee's employee arrived at approximately 5:30 PM on July 11. Since no one from the Washington licensee was available on site to take possession of the gauge, the licensee's employee locked it in a work site cargotainer. The yellow transport box was reported to be locked. When the licensee's employee came back around 7:00 AM on July 12, the locks had been broken and the gauge and several tools had been stolen. The theft was reported to the City of Issaquah Police. The Washington Radiation control Program has been in contact with the Oregon Radiation control Program to coordinate follow-up." [See related report 38135] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2001-07-12
38135 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2001-07-12 | 2001-07-12 17:58 | 2001-07-12 | AGREEMENT STATE REPORT A Troxler Model 3430 gauge (S/N 28872) was stolen from a storage building in Issaquah, WA. The gauge had been transported to a work site in WA and placed into a locked storage building. The local police department has been notified (Case #01-05791). The licensee is offering a reward for the return of the gauge. [See related report 38136] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2001-07-12
38134 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-07-12 16:17 | 2001-07-12 16:17 | 2001-07-12 | OFFSITE NOTIFICATION The licensee will be notifying the Maryland Department of the Environment (MDE) regarding positive test results for coliform bacteria in drinking water samples taken from the educational center. The NRC resident inspector has been informed of this notification. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-12
38133 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-07-12 10:45 | 2001-07-12 14:21 | 2001-07-12 | UNITS IN POTENTIALLY UNANALYZED CONDITION "On July 12, 2001, Turkey Point determined that a previous failed surveillance may have constituted an unanalyzed condition that significantly degraded plant safety. On June 8, 2001, flow damper D-21 was discovered mispositioned. Damper D-21 controls the amount of recirculation flow in the Control Room Ventilation System (CRVS), when the system is in the emergency (recirculation) mode. "The CRVS is designed such that when it shifts to recirculation mode, the Train B emergency supply fan starts. It draws in a nominal 250 cfm of outside intake air flow, and a nominal 750 cfm of recirculation air flow, for a total of 1000 cfm of flow through the HEPA and charcoal filters. If the Train B fan does not start, the resulting low recirculation flow (less than or equal to 100 cfm) will cause the Train A fan to start. "During the surveillance it was found that, with the damper open too far, the recirculation flow stayed so high (about 250 cfm), that even with no supply fan running, the Train A fan did not receive a low flow start signal. The recirculation flow came from the three running Air Handling Units. As a result, a single failure of the Train B emergency supply fan could have caused a loss of emergency supply air forced flow. "As a result of no forced flow, the outside intake air flow would be reduced, and the recirculation flow from the Air Handling Units would stay at about 250 cfm, as measured. By itself, this situation does not significantly degrade plant safety. If there were no outside air drawn in, the dose to the Control Room operators would be minimal. However, with no filtered outside intake air, Turkey Point cannot assure that the Control Room envelope would be pressurized, the unfiltered inleakage of outside air may be sufficient to increase the dose to operators." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-07-12
38132 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-07-11 23:30 | 2001-07-12 05:21 | 2001-09-06 | DISCOVERY OF AN EXCESSIVE ACCUMULATION OF WATER IN TWO UNDERGROUND FUEL OIL STORAGE TANKS The following text is a portion of a facsimile received from the licensee: "[An] excessive accumulation of water [was] discovered in both [the] D11 and D12 underground fuel oil storage tanks. [There was 33 inches of water in D11 and 22.5 inches of water in D12.] This event would prevent both diesel generators from fulfilling their required safety function. [Technical Specification 3.8.1.1, Actions 'b' and 'e,' were] entered, and reportability manual event SAF 1.8 [was also] entered." "Actions Taken: Water has been removed from both [the] D11 and D12 underground fuel oil storage tanks. [The licensee is] currently performing [an] operability determination." The licensee stated that the unit is remains in the 72-hour limiting condition for operation due to the ongoing operability determination. The licensee notified the NRC resident inspector. * * * RETRACTION ON 09/06/01 AT 1407 ET BY STAN GAMBLE TAKEN BY MACKINNON * * * Subsequent testing verified that the water level in both tanks was below the fuel oil transfer pump suction and that no water was found in the associated Day Tanks. Since no water had been nor would it have been transferred from the Fuel Oil Storage Tanks to the Day Tanks during operation of the Diesel Generators, a condition did not exist at the time of discovery that could have prevented the fulfillment of the safety function. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-07-12
38131 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-07-11 22:27 | 2001-07-12 00:29 | 2001-07-12 | AUTOMATIC REACTOR SCRAM, HPCS/RCIC SYSTEM INJECTION, AND FULL BALANCE-OF-PLANT ISOLATION FOLLOWING AN UNSPECIFIED, INTERNAL, ELECTRICAL TRANSIENT An unspecified, internal, electrical transient affected balance-of-plant (BOP) systems and resulted in a feedwater control circuitry problem. Following this electrical transient, the reactor automatically scrammed from 100% power when reactor vessel water level reached level 3 (178 inches narrow range). All control rods fully inserted. When reactor vessel water level decreased to level 2 (approximately 120 inches narrow range), the high pressure core spray (HPCS) and reactor core isolation cooling (RCIC) systems automatically initiated and injected into the reactor pressure vessel (RPV). A BOP isolation signal was also received on level 2, and a full BOP isolation occurred. In addition, the Division 3 emergency diesel generator (EDG) automatically started on level 2 (in support of HPCS). The EDG did not load, nor was it required to. The lowest reactor vessel water level received was 107 inches narrow range. This was reported to be well above the top of the active full, which is at 0 inches wide range. The licensee stated that all safety systems functioned as required. The extent and cause of the electrical transient are currently under investigation. It was reported that the cause may be related to a possible auctioneered power supply failure which affected BOP systems and the feedwater system control circuitry. The unit is currently in Mode 3 (Hot Shutdown). The RCIC system and the main turbine bypass valves are being utilized for reactor water level control and RPV pressure control, respectively. The main steam isolation valves are open, and the condenser is available as a heat sink. HPCS has been placed in standby. (The quantity of water injected was not available at the time of this event notification.) The full BOP isolation has been reset, and the Division 3 EDG is still running (unloaded). (The licensee needs to load the EDG for 1 hour before securing it.) Containment parameters were reported to be normal, and there were no challenges to offsite power. All emergency core cooling systems and engineered safety feature systems are currently available. The feedwater system remains unavailable pending resolution of the transient's root cause. The licensee notified the NRC resident inspector (who was in the control room at the time of this event notification). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2001-07-12
38130 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-07-11 16:50 | 2001-07-11 23:01 | 2001-08-13 | PRIMARY CONTAINMENT DECLARED INOPERABLE - TECH SPEC REQUIRED SHUTDOWN The licensee found a shipping restraint installed on a drywell-to-torus vent pipe bellows, apparently in place since construction (about 30 years). This device was discovered due to another licensee with similar containment configuration notifying Monticello of their discovery. This device would partially impede axial motion. The primary containment was declared inoperable at 1650 CDT on 07/11/01, and removal was initiated. This is an 8-hour report under 10CFR50.72(b)(3)(ii)(a) as a degraded condition and 10CFR50.72(b)(3)(v)(c and d), control of radiation release and accident mitigation. The licensee initiated a required shutdown at 2050 CDT on 07/11/01 per Technical Specification 3.7.A.2.a, as a result of declaring primary containment inoperable because the drywell-to-torus vent pipe bellows shipping installation attachments were still installed. This is a 4-hour report under 10CFR50.72(b)(2)(i), technical specification required shutdown. The licensee notified the NRC resident inspector and intends to notify state and local agencies. ***** UPDATE FROM DAVE BARNETT RECEIVED BY LEIGH TROCINE AT 0039 EDT ON 07/12/01 ***** The four shipping fasteners have been removed from each of the eight drywell-to-torus vent pipe bellows, and primary containment was declared operable at 2304 CDT on 07/11/01. The technical specification required shutdown was terminated while the reactor was at 90% power. The licensee currently plans to restore reactor power to 100%. The licensee plans to notify the NRC resident inspector as well as the applicable state and county agencies. The NRC operations officer notified the R3DO (Hills). **** RETRACTION ON 08/13/01 AT 1253ET BY D. BARNETT TAKEN BY MACKINNON **** Subsequent evaluation has shown the bellows as well as the drywell and torus attachments capable of performing their design safety functions. Therefore, Primary Containment was considered operable at all times and this event is not considered reportable. The licensee will notify state and local officials of this retraction. R3DO (T. Kozak) notified. The NRC Resident Inspector will be notified of this event by the licensee. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | PLANT S/D REQD BY TS | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 50.72(b)(2)(i) | 0 | 2001-07-11
38129 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-07-10 15:30 | 2001-07-11 14:47 | 2001-07-11 | 16 OF 17 FLOOD PANELS FOUND TO BE NON-FUNCTIONAL "A second quarter 2001 inspection per Procedure PM-3586-10 identified miscellaneous deficiencies (e.g., deteriorated gasket material, obstructions, deficient bolting) with flood panels such that 16 of 17 are considered non-functional. There is no current operability concern due to the river level and the analyzed need for both snow melt and heavy rains to require the use of these panels. We are currently working on a plan to correct deficiencies. Reference: USAR Section 2.4.3.5" The licensee noted that this report was due yesterday. However, the licensee determined this afternoon (7/11/2001) that a report should have been made. The licensee intends to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-07-11
38128 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-07-10 09:10 | 2001-07-10 20:56 | 2001-07-10 | 24 HOUR REPORT - NRC BULLETIN 91-01 The following text is a portion of a facsimile received from PORTSMOUTH: At 0910 on 07/10/2001 it was identified that control #5 of NCSA-0705_076.A03 was not being maintained for two filter press plates covered in plastic. NCSA-0705_076.A03 requires that no inadvertent containers that could contain greater than 2.5 liters of solution be permitted in any areas in which uranium bearing solution could be accumulated in the inadvertent container. The loose plastic wrapped on the filter press plates had the potential to deform into a container that would exceed the maximum criteria identified in the NCSA. This constitutes a loss of one control (geometry) of the double contingency control principle identified in NCSA-0705_076.A03. No fissile material leaked in the area while the plastic wrap was present. NCSA-0705_076.A03 compliance was reported restored at 1010 hours. SAFETY SIGNIFICANCE OF EVENTS: The safety significance is low because at the time of the event there was no uranium bearing material present that could leak into the inadvertent container. The area in question is designated an 'Inadvertent Container Area' due to the presence of the Complexing Hand table. However. the Hand table is not currently in operation. The next nearest fissile material operation is Microfiltration which is currently in operation, but is more than 15 feet from the location of the plastic wrap in question. Nevertheless, the presence of an inadvertent container at that location is a violation of NCS controls and one leg of the double contingency principle described in NCSE-0705_076.E03. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the following events would be required: The complexing Hand table would have to be in operation and be processing uranium bearing liquid with an unknown or high concentration of uranium. Then a leak in this system must occur such that an unsafe amount of liquid sprays (presumably under pressure) from the Hand table system onto the plastic wrap in question. The liquid would then have to collect and deform the plastic wrap such that more than 2.5 liters collects to a depth greater than 1.5 inches forming an unsafe geometry. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Inadvertent containers are controlled based upon volume (2.5 liters maximum) or geometry (1.5 inches in depth or 4 inches in diameter. Flexible material (e.g., plastic wrap) is specifically controlled such that solution cannot pool to a depth grater than 1.5 inches, ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium bearing material was involved in this event. There were no leaks of uranium bearing material in the area while the inadvertent container was present. The event involves the presence of an unsafe geometry container that could collect solution in the event of a spill. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Loose plastic wrap placed over filter press plates in an inadvertent Container Area was not configured or secured such that it cannot be deformed into an inadvertent container with an unsafe accumulation potential. This is a violation of control #5 of NCSA-0705_076.A03. Use of Inadvertent Containers CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Requirements of an NCS Anomalous condition entered. At the direction of an NCS engineer, the condition was corrected. Portsmouth personnel notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-07-10
38127 | 0 | ST. LUKES MEDICAL CENTER |  |  |  |  | 2001-07-10 14:30 | 2001-07-10 17:33 | 2001-07-10 | MEDICAL MISADMINISTRATION INVOLVING TREATMENT TO WRONG SITE There were 2 patients prepared for treatment with a gamma knife. The wrong treatment package was used for the first patient. There were 4 of 8 shots administered to the wrong site before it was discovered that the wrong package was being used. The patient received approximately 13 gray over a short period to a small area. The consequences of the exposure are not known at this time and are being investigated and the patient's progress will be followed for some time. The patient received the correct treatment subsequently. The attending physician has been notified and the patient will be informed tomorrow. There is a review and evaluation of procedures on going to determine how to insure this event is not repeated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 35.33 |  |  |  | 0 | 2001-07-10
38126 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-07-10 16:11 | 2001-07-10 16:47 | 2001-07-10 | PLANT SHUTDOWN REQUIRED DUE TO FAILED CONTAINMENT LEAK RATE TEST The licensee was conducting normal technical specification surveillance of containment leak rate and determined that the personnel access airlock has failed the surveillance. The plant commenced a technical specification required reactor shutdown to Mode 3 at 1611 EDT on 7/10/01. The licensee will remain in Mode 3 until the airlock is repaired. The licensee has notified the NRC Resident Inspector and the State of Connecticut. | 0 | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | OFFSITE NOTIFICATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(xi) |  |  | 0 | 2001-07-10
38125 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-07-09 | 2001-07-10 12:15 | 2001-07-10 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The Colorado Department of Health received a call from CTC-Geotech at approximately 9:30 (AM) on 7/10/01. The call reported a Troxler gauge model 3430 serial #32097 stolen late afternoon on 7/9/01. It was stolen from a job site in Thorton, CO. The gauge was chained to the back of pickup truck and the locks were cut while the user was inside a construction trailer getting work information. A police report and a written report will be sent to Colorado Department of Health. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-07-10
38124 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2001-07-08 14:30 | 2001-07-09 14:12 | 2001-07-09 | OFFSITE NOTIFICATION DUE TO SEA TURTLE CAPTURE The licensee notified the National Marine Fisheries Services of the capture of an endangered non-injured juvenile green sea turtle in the intake structure. The turtle has been released to the Marine Mammal Stranding Center. The licensee intends to notify the NRC Resident Inspector. A written report will be sent to the State with copies to the NRC and National Marine Fisheries Services. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-09
38123 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2001-07-09 09:00 | 2001-07-09 13:07 | 2001-07-13 | CONTROL ROOM VENTILATION SYSTEM DECLARED INOPERABLE The Division 2 Main Control Room Ventilation System was declared inoperable at 0900 CDT on 7/9/2001 because it was not maintaining the required positive pressure while running in the High Radiation Mode of operation. The system was declared operable at 0913 CDT when the required positive pressure was restored. During the 13 minute period Division 2 was inoperable, Division 1 Main Control Room Ventilation System was inoperable due to a scheduled maintenance outage. Therefore, with both systems inoperable, a condition existed which could have prevented the fulfillment of the safety function of the Main Control Room Ventilation System needed to mitigate the consequences of an accident. The cause of the perturbation in control room pressure is being investigated. The licensee notified the NRC Resident Inspector. *** RETRACTION FROM STEVEN STRICKLAN RECEIVED BY LEIGH TROCINE AT 0451 EDT ON 07/13/01 *** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "On 07/09/01, at approximately 0900 [CDT], the Clinton Power Station (CPS) experienced a transient situation where, for a period of 13 minutes, the positive pressure in the Main Control Room (MCR) was compromised. Based on this condition, an ENS notification (#38123) was made in accordance with the requirements of 10CFR50.72(b)(3)(v), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition; (B) remove residual heat; (C) control the release of radioactive material; or (D) mitigate the consequences of an accident." "An evaluation of the conditions present at the time positive pressurization of the MCR was temporarily interrupted has been performed. The evaluation results indicated that the conditions that potentially existed during this event were bounded by the design basis analysis performed for the [MCR]. The calculated MCR operator thyroid dose for this event was determined to be approximately 23.185 Rem, which is less than the USAR calculated dose of 25 Rem. The USAR dose is calculated based on a 20-minute time delay in starting the system in the high radiation mode. For this event, the high radiation mode was already in operation. Whole body and Beta dose for this event are not governing." "It [has] therefore been demonstrated that, in the event of a design basis event, time dose impact of the condition as it existed would be bounded by the current analyses of record. As such, the safety function would be fulfilled, and the ENS notification is retracted." "Although it has been demonstrated that the safety function would be fulfilled, the situation represented a condition prohibited by Technical Specifications, and this event continues to be evaluated for reportability as a Licensee Event Report under 10CFR50.73(a)(2)(i)(B)." The licensee notified the NRC resident inspector. The NRC operations center notified the R3DO (Hills). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-07-09
38122 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-07-09 06:30 | 2001-07-09 07:13 | 2001-07-09 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA BY A LICENSED OPERATOR. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR FURTHER DETAILS. * * * RETRACTED AT 1517 EDT ON 7/9/2001 BY SUSAN REESE TO FANGIE JONES * * * The licensee is retracting this report following further investigation. The licensee notified the NRC Resident Inspector. The R2DO (Edward McAlpine), NRR IAT (Robert Skelton), and NMSS IAT (Aaron Danis) have been notified. Contact the Headquarters Operations Officer for further details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-07-09
38121 | 0 | NATIONAL RESPONSE CENTER |  |  |  |  | 2001-07-06 23:05 | 2001-07-07 00:57 | 2001-07-07 | A STOLEN PICKUP TRUCK CARRYING A MOISTURE DENSITY GAUGE WAS OVERTURNED. National Response Center hooked Headquarters Operation Center up with Jefferson County 911 center. A stolen pickup truck carrying a moisture density gauge was overturned on Hunning road and Elizabeth lane near High Ridge, Mo. Established conference call between the on-scene HAZMAT/EMA responder and R3(Phillips). The on-scene responders requested assistance in determining whether rad material was released due to damage of the moisture density gauge and if it was safe to take the injured driver to the local hospital. An SCI Engineering employee is on-scene and the HAZMAT team will take radiation surveys to make sure that the moisture density gauge is not damaged. * * *UPDATE ON 07/07/01 AT 1031ET BY WILLIAM GUERDAN TAKEN BY MACKINNON * * * William Guerdan, Radiation Safety Officer for SCI Engineering, called in the event for the licensee and gave the following information: The Humboldt Model 5001 moisture density gauge was located in the back of a Ford Ranger pickup truck. The gauge handle was locked, the gauge box was locked, and gauge box was cabled and locked in the open bed of the pickup truck . The RSO had an employee of the company who lived near where the accident occurred retrieve the undamaged moisture density gauge and take it back to SCI Engineering after it was surveyed and released by the HAZMAT team. The moisture density gauge contains less than 11 millicuries of cesium-137 and less than 44 millicuries of americium-241/beryllium. The gauge number of the Humboldt gauge is 1386. R3DO (Tony Vegel) and NMSS EO (Eric Leeds) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-07-07
38120 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-07-06 15:57 | 2001-07-06 17:08 | 2001-07-06 | LICENSEE MADE NOTIFICATION TO THE STATE OF NORTH CAROLINA AS REQUIRED BY THE NATIONAL POLLUTANT DISCHARGE ELIMINATION SYSTEM PERMIT On 7/6/01 an unusually high amount of rain in a very short time has nearly overflowed the Storm Drain Collector Basin. Rain is predicted to continue and conditions are not improving. Two pumps are available for basin pumping with one being a temporary installed engine driven pump. Basin level is now starting to submerge the motor driven pump. Storm water is currently backing up throughout the Turbine Buildings on both Units. This condition is a threat to plant equipment and a potential threat to personnel safety. Overboard Spill valves directly to the discharge canal have been opened to regain control of the Storm Drain Basin level. This release bypasses normal radiological and chemical monitoring and requires North Carolina state notification per the "National Pollutant Discharge Elimination System Permit" permit number NC0007064. INITIAL SAFETY SIGNIFICANCE EVALUATION: None - opening these valves will allow storm water to discharge directly to the discharge canal without radiological and chemical monitoring. The contents of the basin were sampled prior to releasing, and no activity above natural was detected. CORRECTIVE ACTIONS: Regain control of Storm Drain Collector Basin Level as weather conditions permit, and then re-close the Overboard Spill valves. The NRC Resident Inspector was notified along with the State. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-06
38119 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2001-07-05 10:00 | 2001-07-05 16:03 | 2001-08-17 | NON-CONSERVATIVE ANALYSIS FOR OPRM SCRAM SETPOINTS On July 5, 2001, Detroit Edison received confirmation from General Electric of a non-conservative analysis that supports Operation Power Range Monitor (OPRM) scram setpoints. The non-conservative analysis is generic and been determined to affect Fermi 2. The OPRM had been conservatively declared inoperable on June 27, 2001, at 1333 hours as a result of preliminary notification by General Electric. The consequences of the non-conservative analysis are that the associated OPRM Reactor Protective System (RPS) scram setpoints are non-conservative. The non-conservative RPS setpoints may result in violating the Minimum Critical Power Ratio (MCPR) safety limit during a thermal-hydraulic instability. All OPRM channels have been declared inoperable. Technical Specification 3.3.1.1 Action J requires an alternate method of detecting and suppressing thermal-hydraulic instabilities to be implemented within 12 hours. Alternate methods have been established, thus, the Technical Specification required action is satisfied. Fermi 2 has 120 days to restore the OPRMs to an operable condition. This initial report is being made in accordance with 10CFR50.72 (B)(3)(V)(A) as a condition that could have prevented the fulfillment of the safety function of a system needed to shutdown the reactor. See EN #38104, GE Nuclear Energy 10CFR21 report. The NRC Resident Inspector will be notified. * * * RETRACTED AT 1443 EDT ON 8/17/2001 BY PATRICK FALLON TO FANGIE JONES * * * The licensee is retracting the event notification. "Subsequent design calculations have concluded that there was sufficient conservatism in the existing OPRM RPS scram setpoints to accommodate corrections for the non-conservative analysis performed by General Electric, which was the subject of their 10 CFR 21 Notification dated June 29, 2001 (SC01 -01), and still provide protection for the Minimum Critical Power Ratio (MCPR) Safety Limit during a thermal-hydraulic instability throughout the current operating cycle. The OPRM RPS scram function was not required to be operable prior to the current operating cycle. Since the existing OPRM RPS scram setpoints have been shown to be set conservatively, the OPRM system was operable, and therefore no situation existed which was reportable." The licensee has notified the NRC Resident Inspector. The R3DO (Thomas Kozak) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-07-05
38118 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-06-25 06:20 | 2001-07-05 14:50 | 2001-07-05 | STOLEN HUMBOLDT HS-5001P NUCLEAR DENSITY GAUGE A Humboldt Manufacturing Model HS-5001 P, Serial No. 30, containing 10 millicurie Cs-137, Serial No. 400SGF; and 40 millicurie Am-241/Be, Serial No. NJ00026 was stolen. Initial information indicates that the gauge was in the bed of a company pickup truck secured by bungee cords in the gauge's locked transit case when the driver stopped at a convenience store, located at 104 Kaufman Street, Rockwall, Texas. at approximately 6:15 a.m. on June 25, 2001. The operator/driver noticed the gauge was missing when he returned to his truck which was parked immediately in front of the store's front doors. He has estimated that he was in the store for approximately 5 minutes. A police report has been filed with the Rockwall, Texas Police Department. A copy of this report is currently not available. The gauge was enroute to a jobsite when stolen. The owner of the stolen gauge is a Texas Licensee, L03411-000 (Alpha Testing, Inc.. 2209 Wisconsin Street, Suite 100 Dallas, Texas 75229). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-07-05
38117 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-07-05 09:00 | 2001-07-05 12:30 | 2001-07-05 | OFFSITE NOTIFICATION TO MARYLAND DEPARTMENT OF ENVIRONMENT The licensee notified the Maryland Department of Environment due to a positive coliform count in the drinking water at the educational center. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-05
38116 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2001-07-05 10:19 | 2001-07-05 12:15 | 2001-07-05 | THE REACTOR WAS MANUALLY SCRAMMED FROM 100% POWER DUE TO HIGH DRYWELL PRESSURE The plant entered an Alert @ 1019CDT due to drywell pressure rising above the ECCS setpoint(2 psig). The reactor was manually scrammed at 1006 and drywell pressure peaked at 2.3 psig. All rods fully inserted and no safety relief valves lifted. ECCS functioned as required, but no injection initiated. Drywell pressure is currently 2.1 psig and slowly trending down. The NRC Resident Inspector was notified along with state ,local and other Government agencies. Other agencies notified by NRC: Tanner(EPA), Young(DOE), Conley( USDA), Gray(HHS), Robertson(DOT), and Watson(USSS). NRC entered the monitoring mode at 1209 EDT. * * * UPDATE @ 1300EDT COMMISSIONERS ASSISTANT'S BRIEFING * * * Wessman(IRO), Borchardt(NRR), Gagner(PAO), Combs(SP), Hauber(IP), Madden(CO), Bergman(EDO), Paperiello(DEDMRS), Tschiltz(Chairman Assist.), Hiltz(Commissioner Dicus), Beall(Commissioner McGaffigan) Thoma(Commissioner Merrifield), Dyer(Reg 3 Briefer), and Gamberoni(Secy) Monitoring mode was terminated at 1737 EDT. * * * UPDATE AT 1757 ON 7/05/01 BY MOHR TO GOULD * * * Subsequent to earlier notification, information has been obtained that verifies the cause of the high drywell pressure was due to a loss of containment cooling. A redundant cooling water train was placed in service and the drywell temperature and pressure have been trending down to normal ranges. The drywell sump was pumped and confirmed that RCS leak rates have not increased. Drywell radiation levels were verified to be normal. Additionally, drywell atmosphere samples were normal. Drywell pressure is currently .37 PSIG. The plant has been stabilized in accordance with procedures and equipment repairs are being made. Plans are being developed for unit return to service. The Alert was terminated at 1602 CDT. The NRC Resident Inspector and State have been informed. * * * UPDATE AT 1825 ON 7/5/01 BY MOHR TO GOULD * * * The plant also had groups 2 and 3 isolations, low pressure and high pressure ECCS initiation signals and Unit 3 and 2/3 swing emergency diesel generator auto starts. The NRC Resident Inspector was informed. * * * UPDATE 1900 ON 7/05/91 MODIFIED COMMISSIONER ASSISTANT'S BRIEFING * * * Dyer(REG3), Marsh(NRR), Tschiltz(Chairman's Assistants), Thoma(Commissioner Merrifield's Assistant), and Hiltz(Commissioner Dicus' Assistant) Agencies notified by the NRC: Cegielski(FEMA), Poppell(EPA), Morrone(DOE), Conley(USDA), Robertson(DOT), Farrow-Collier(CDC). Notified Beckner(EO), Wessman(IRO), Hayden(PA) and Vegel(REG 3 RDO). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode3: Power Operation; FMode3: Hot Shutdown | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2001-07-05
38115 | 0 | U. S. CUSTOMS SERVICE |  |  |  |  | 2001-07-03 12:30 | 2001-07-05 08:50 | 2001-07-05 | UNMARKED LICENSED RAD MATERIAL RECEIVED AT PORT OF ENTRY A closed intermodal container shipped by Alcan of Kingston, Jamaica to CPN International in California was off loaded and inspected at the Port of Entry in Miami, FL. U.S. Customs alerted local Hazmat personnel after receiving alarms on personnel monitors. Hazmat surveyed both the exterior and interior of the container and found readings of approximately 1 mr/hr and 8 mr/hr, respectively. A followup investigation determined that the container had unmarked density detectors used in mining operations. The shipment has been quarantined and will be returned to the shipper. The National Response Center was informed of this incident by U.S. Customs on 7/3/01 (report #571693). Contact the Headquarters Operations Officer for contact telephone number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | FL | OTH | GEN |  |  |  |  | 0 | 2001-07-05
38114 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-06-29 | 2001-07-03 11:30 | 2001-07-03 | MEDICAL MISADMINISTRATIONS DUE TO INCORRECTLY CALCULATED RADIONUCLIDE ACTIVITIES The Syncor pharmacy in Denver, CO miscalculated the activity in three doses of I-131 due to the use of incorrect settings on the dose calibrator. Of the three doses, two were delivered to a Kaiser Permanente facility and administered. The two doses were as follows: Dose 1 was ordered to be 5 mCi to be used for a whole body scan. Syncor believed that 5.28 mCi had been dispensed; however, the actual activity was 7.97 mCi. Dose 2 was ordered to be 15 mCi to be used for a hyperthyroid treatment. Syncor believed that 15.8 mCi had been dispensed; however, the actual activity was 24 mCi. The state is currently following this issue with the Kaiser Permanente staff. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-07-03
38113 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-07-02 10:00 | 2001-07-02 19:31 | 2001-07-10 | NRC BULLETIN 91-01 RESPONSE - FAILURE TO MAINTAIN THE DOUBLE CONTINGENCY (24-Hour Report) The following text is a portion of a facsimile received from Paducah: "At 1000, on 07/02/01, the Plant Shift Superintendent (PSS) was notified that while approving a cylinder for wash on the C-400 Cylinder Wash stand, an incorrect cylinder number was both entered and independently verified on the UF6 Cylinder Wash Facility Data Sheet violating NCSA 400-002. As a result of these actions, an unapproved cylinder was washed. NCSA 400-002 required the cylinder number be independently verified to be correct on the approval data sheet. The cylinder number is used to prevent misidentification of cylinders. Since the cylinder washed had an unverified UF6 heel (mass control) and independent verification of the cylinder to be washed was incorrectly performed (assay control), double contingency was not maintained." "SAFETY SIGNIFICANCE OF EVENTS: Independent verification required to ensure the correct cylinder be washed was not performed correctly." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, a cylinder containing a critical mass of enriched uranium would need to be washed. The cylinder incorrectly washed had an assay <1.0 WT %235U." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): [The] two process conditions relied on for double contingency for this scenario are assay and mass." "ESTIMATED AMOUNT ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The cylinder washed was <1.0 WT %235U." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on the assay not exceeding 2.0 WT %235U. The cylinder intended for wash and the cylinder actually washed were both 4BHX cylinders, which are limited to a maximum enrichment of 1.0%. While the control was violated, the process condition was maintained." "The second leg of double contingency is based on the heel mass not exceeding 72 pounds. The cylinder actually washed has an unverified heel weight. Therefore, this control was violated, and this leg of double contingency was lost." "Since the process parameter for mass was not independently verified prior to washing the cylinder, double contingency was not maintained." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: This condition was identified while reviewing completed cylinder work records. There is no action that can be performed to resolve this condition and bring the process back into compliance since the cylinder activity has been completed." Paducah personnel notified the NRC resident inspector. * * * UPDATED AT 1535 EDT ON 7/10/01 BY W. F. CAGE TO FANGIE JONES * * * "Nuclear Regulatory Affairs has reviewed the basis for the event report against the NCS reporting position and determined that the NCS violation although serious did not cause either of the two NCS process conditions (assay <2 wt.% or heel mass of 72 pounds) analyzed in NCSA 400-002 to change or to be exceeded. The assay of the material in the cylinder was 0.71 wt. % and the heel mass was 11 pounds. Under the reporting criteria, reporting would only be warranted when the double contingency principal has been violated, but the process conditions cited for double contingency were maintained, i.e., not exceeded. Thus, the double contingency principal, as defined in the SAR and ANSI 8.1 was not violated and the incident is not reportable. Paducah personnel notified the NRC resident inspector. The R3DO (David Hills) and NMSS (Don Cool) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-07-02
38112 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2001-06-05 | 2001-07-02 20:00 | 2001-07-02 | MISLABELED IODINE-125 SEEDS BY NYCOMED AMERSHAM IN ILLINOIS RESULTED IN AN APPARENT MEDICAL MISADMINISTRATION AT FLOWERS HOSPITAL IN DOTHAN, ALABAMA The following text is a portion of a facsimile received from the Alabama Division of Radiation Control: "Alabama Incident #01-11 - I-125 Prostate Seed Implant Misadministration" "On the afternoon of June 29, 2001, the Alabama Office of Radiation Control was notified by [the] Illinois Department of Nuclear Safety that a possible misadministration of an iodine-125 prostate seed implant may have occurred at Flowers Hospital on June 5, 2001. Flowers Hospital is authorized to possess and use the radioactive material under Alabama Radioactive Material License No. 549." "The details of the event are described by [the Illinois Department of Nuclear Safety] in the attached e-mail which was transmitted to this Agency." "Representatives from the Alabama Office of Radiation Control telephoned the medical physicist for Flowers Hospital on the morning of July 2, 2001, to inquire about the possible misadministration. The medical physicist for Flowers Hospital confirmed that a possible misadministration did occur based on the information obtained from the manufacturer[,] but he was in the process of reviewing the records pertaining to the possible misadministration." "The Alabama Office of Radiation Control is presently investigating the details of this apparent misadministration and will be conducting an onsite inspection of licensed activities at Flowers Hospital beginning on July 3, 2001." The following text is a portion of a facsimile received from the Alabama Division of Radiation Control involving an e-mail they received from the Illinois Department of Nuclear Safety at 0421 on June 29, 2001: "SUBJECT: Mislabeled Seeds by Nycomed Amersham Result in an Apparent Medical Misadministration in Alabama" "[A] Nycomed Amersham, RAML No. IL-01044-0l, [representative] called this afternoon and reported the following concerning distribution of their Model 6711 I-125 seeds:" "June 13, 2001 - Nycomed Amersham, while performing a review of their scrapping procedure and inventory of dispensed products noted a discrepancy in a lot consisting of .270 mCi I-125 seeds. The lot was short 110 seeds." "June 14 - Continued review found a discrepancy with a lot consisting of .414 mCi I-125 seeds. This lot was 110 seeds over." "They realized that there was a dispensing error and that 110 seeds of .270 mCi seeds were sent out as .414 mCi seeds." "June 15 - Determined that the seeds in question were transferred to Flowers Hospital in Dothan, Alabama on [May 30, 2001]." "June 16 - Contacted Flowers Hospital and informed the dosimetrist about the problem (Flowers Hospital medical physicist was on vacation until the 18th). The dosimetrist investigated and learned that the seeds had been assayed in a new dose calibrator at their facility and [that] the seeds were implanted in a patient undergoing prostate therapy on June 5, 2001. Apparently[,] the dose calibrator read slightly lower than expected but not enough to stop the use of the seeds in the therapy procedure." "June 18 - Nycomed discussed with the medical physicist at Flowers Hospital. The medical physicist asked Nycomed to send a calibrated seed to his facility so he could check the calibration of the dose calibrator. Nycomed complied with the request." "June 20 - Flowers Hospital medical physicist notified Nycomed that their dose calibrator did not obtain the expected reading using the calibrated seed. The medical physicist requested that Nycomed's physician contact Flowers Hospital attending physician to discuss the matter. The physicians discussed the matter and both concluded that the actual dose delivered from planned was approximately 30% less than that planned. It is believed that the patient also underwent external beam therapy in conjunction with the brachytherapy. The physicians also concluded that the effect on the patient was 'small.'" [An Illinois Department of Nuclear Safety representative] asked if the Alabama program had been notified as this appears to be a misadministration event in Alabama. [The Nycomed Amersham representative] stated that he believed that they had been but did not know for sure as they depend on the licensee to make the necessary reports as they do not want to get in between the licensee and their regulator. [The Nycomed Amersham representative] also stated that the event had been reported to the Chicago District of FDA on a form entitled 'Medical Device Report of Removal.'" "[An Illinois Department of Nuclear Safety representative] then contacted the Alabama State Dept. of Public Health, Office of Radiation Control. [The Illinois Department of Nuclear Safety representative] provided the above information to Kirk Whatley and Jim McNees [of the Alabama Office of Radiation Control]. They stated that this was the first that they had heard about it and that they will follow up on the event. They will notify the NRC Ops Center if in fact a misadministration event actually occurred." "[The Nycomed Amersham representative] will keep us posted on this matter." (Please call the NRC operations center for the Illinois Department of Nuclear Safety and Nycomed Amersham contact names.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0 | 2001-07-02
38111 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-07-01 13:30 | 2001-07-01 17:20 | 2001-07-01 | NON-DESTRUCTIVE EXAMINATION OF CRDM PRESSURE HOUSING FOUND CRACK INDICATION "During non-destructive examination (NDE) of welds on control rod drive mechanism (CRDM) pressure housings, an indication was discovered on CRDM-40. The method being utilized was ultrasonic testing (UT). The indication is axial, approximately 0.7 inches long, located-on the inner surface of the pressure housing. The depth of the indication is approximately 50% through-wall. The indication is located in the top side heat affected zone of an 8 inch butt weld which joins the pressure housing's tubular section to an eccentric reducer. The material of the pressure housing is type 347 stainless steel. "The weld examinations were being conducted as part of an extent of condition evaluation resulting from an earlier discovery, on June 21, 2001, of a through-wall axial indication on CRDM-21. The CRDM-40 indication location corresponds to the location of the earlier discovered indication in CRDM-21(EN #38083) and CRDM-25 (EN #38103). Cause evaluation is ongoing." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-07-01
38110 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-07-01 14:10 | 2001-07-01 15:07 | 2001-07-01 | OFFSITE NOTIFICATION DUE TO INJURED LOGGERHEAD SEA TURTLE The licensee notified the State of Florida Fish and Wildlife Commission about the discovery of an injured loggerhead sea turtle from the intake bay. The turtle is being transported to rehabilitation. The licensee notified the NRC Resident Inspector. | 90 | 100 | 0 | 90 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-07-01
38109 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2001-07-01 02:10 | 2001-07-01 04:35 | 2001-07-01 | AUTOMATIC TURBINE TRIP/REACTOR SCRAM DURING TROUBLESHOOTING "During troubleshooting of Peach Bottom Unit 2 electrohydraulic control (EHC) system, the main turbine control valves fast closed, resulting in an automatic turbine trip, reactor protection system (RPS) trip and reactor scram. "Additionally, as a normal result of the reactor scram, reactor water level lowered below 1 inch, causing a valid automatic group II/III primary containment isolation signal (PCIS) in multiple trains. "The plant responded normally, RPS and PCIS signals were reset and unit 2 is continuing to a cooled-down depressurized condition. No radiological release" The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-07-01
38108 | 0 | JACA & SIERRA TESTING LABS |  |  |  |  | 2001-06-30 | 2001-06-30 15:00 | 2001-06-30 | STOLEN MOISTURE DENSITY GAUGE A pickup truck with a stored and locked Troxler moisture density gauge (serial # M1A03A16A) was stolen sometime this morning (6/30/01) in San Juan, Puerto Rico. The gauge contains sealed sources of Cs-137 (10 mCi) and Am-241/Be (50 mCi). The local police and the Puerto Rico Civil Defense have been notified. There has been a press release and their will be television announcements. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | PR | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-06-30
38107 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-06-29 17:28 | 2001-06-29 21:12 | 2001-06-29 | MANUAL REACTOR TRIP PER PROCEDURE DUE TO INCREASING CONDENSER PRESSURE "Watts Bar Unit 1 was manually tripped when the main condenser backpressure reached limits required by procedure. The rise in the backpressure was caused by a reduced condenser circulating water (CCW) flow which resulted from cooling tower fill material obstructing suction screens to the CCW pumps. All safety systems responded as required during the event. Auxiliary Feedwater initiated due to reactor trip with low Tavg, as required. All control rods inserted properly. Inspections are under way to determine the extent of the debris in the system." The licensee notified the NRC Resident Inspector. They will be notifying the State and Local authorities due to noise from the use of steam generator atmospheric reliefs for excess heat removal while the condenser is not available. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-06-29
38106 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-06-29 17:15 | 2001-06-29 19:19 | 2001-06-29 | NON-CONSERVATIVE ANALYSIS FOR OPRM SCRAM SETPOINTS "On June 29, 2001, General Electric informed Niagara Mohawk Power Corporation of a non-conservative analysis that supports Operation Power Range Monitor (OPRM) scram setpoints. The non-conservative analysis is generic and has the potential to affect all stability option III and I-D plants. "The consequences of the non-conservative analysis are that the associated OPRM Reactor Protection System (RPS) scram setpoints are also non-conservative. The non-conservative RPS setpoints may result in violating the Minimum Critical Power Ratio (MCPR) safety limit during a thermal-hydraulic instability. "All OPRM channels have been declared inoperable. Technical Specification 3.3.1.1 Action F requires an alternate method of detecting and suppressing thermal-hydraulic instabilities to be implemented within 12 hours. Alternate methods are already established in procedures N2-SOP-29 and N2-RESP-12. Therefore, the Technical Specification required action is satisfied. These alternate methods are the same methods used prior to implementation of the OPRM scram function. "Nine Mile Point Unit 2 has 120 days to restore the OPRMs to an operable condition. If the 120 day allowed outage time is exceeded, the Unit must be in at least STARTUP within the following six hours. "This report is being made as required by 10CFR50.72 (B) (3) (V) (A) as condition that could have prevented the fulfillment of the safety function of a system needed to shutdown the reactor." The licensee notified the NRC Resident Inspector. See EN #38104, GE Nuclear Energy 10 CFR 21 report. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-06-29
38105 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2001-06-28 13:30 | 2001-06-29 14:13 | 2001-06-29 | AGREEMENT STATE REPORT: MISSING SHIPMENT OF RADIONUCLIDE Kansas Department of Health (KDHE) was notified that a shipment to Inveresk Research in Scotland was reported missing from the Federal Express at their Memphis, TN hub terminal . The shipment from Chemsyn Science Laboratories of Lenexa, Kansas was 3.5 mCi of radiolabeled (inidazol-2-14C) NED 2000-1 dibenzenesulfonate. The shipment was sent on 6/19/2001 and the search was started on 6/26/2001 when Inveresk contacted Chemsyn about not receiving shipment. Federal Express found the overpack, a dry ice chest (16" x 16" x 23") which originally contained 54 pounds of dry ice and the small Type A Package. The small Type A Package has not been located. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2001-06-29
38104 | 0 | GE NUCLEAR ENERGY |  |  |  |  | 2001-06-29 | 2001-06-29 13:31 | 2001-06-29 | 10 CFR 21 REPORT: STABILITY RELOAD LICENSING CALCULATIONS MAY BE NON-CONSERVATIVE "This letter provides information concerning the potential for non-conservative reload licensing calculations for plants which have implemented stability detect and suppress trip systems. The non-conservatism could result in (1) Option III stability trip system setpoints which do not provide Minimum Critical Power Ratio (MCPR) Safety Limit protection, and (2) inadequate MCPR safety limit protection from the flow-biased Average Power Range Monitor (APRM) flux trip for plants which have implemented Option I-D or Option II. This notification is provided under 10 CFR Part 21(d) as a reportable condition for Hatch Units 1 and 2, and as an interim report per §21.21(a)(2) for the other plants listed in Attachment 1: the full impact of this deviation cannot be completed within 60 days from the date of discovery. Therefore, this notification describes the deviation that is being evaluated by GE Nuclear Energy (GE-NE) for associated safety related reload licensing calculations supplied to licensees by GE-NE and states when the evaluation will be completed. "In addition, GE-NE does not have the capability to perform the evaluation to determine if a defect exists for plants at which GE-NE is not responsible for stability reload licensing calculations. GE-NE has transferred information pursuant to §21.21(b) to those licensees which are known to be potentially affected. "GE-NE has informed all BWR utilities of this issue through the BWROG Potential Issues Response Team (PIRT). All potentially affected utilities have been notified. Compensatory action has been taken at the plants which have been determined to be reportable. Additional information is included in this notification and has been provided to the potentially affected licensees so that they can determine if the concern impacts their stability detect and suppress reload licensing calculations." All GE BWR plants are potentially affected. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2001-06-29
38103 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-06-28 09:30 | 2001-06-28 15:31 | 2001-06-28 | NON-DESTRUCTIVE EXAMINATION OF CRDM PRESSURE HOUSING FOUND CRACK INDICATION "During non-destructive examination (NDE) of welds on control rod drive mechanism (CRDM) pressure housings, an indication was discovered on CRDM-25. The method being utilized was ultrasonic testing (UT). The indication is axial, approximately 0.6 inches long, located-on the inner surface of the pressure housing. The depth of the indication is approximately 25% through-wall. The indication is located in the top side heat affected zone of an 8 inch butt weld which joins the pressure housing's tubular section to an eccentric reducer. The material of the pressure housing is type 347 stainless steel. "The weld examinations were being conducted as part of an extent of condition evaluation resulting from an earlier discovery, on June 21, 2001, of a through-wall axial indication on CRDM-21 [EN #38083]. The CRDM-25 indication location corresponds to the location of the earlier discovered indication in CRDM-21. Cause evaluation is ongoing." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-06-28
38102 | 0 | SHORE MEMORIAL HOSPITAL |  |  |  |  | 2001-06-28 09:15 | 2001-06-28 09:22 | 2001-06-28 | HISTORICAL LOSS OF TWO 0.35-MILLICURIE IODINE-125 SEEDS FROM SHORE MEMORIAL HOSPITAL IN SOMERS POINT, NEW JERSEY On 11/22/99, two iodine-125 seeds were inadvertently flushed into the sewer system, and each seed had an activity of 0.35 millicuries. The seeds in question were used in a MIC applicator as part of a prostate treatment. The licensee stated that when the retractor is removed from the gland, the contents are typically flushed into a bowl and surveyed prior to dumping to ensure that there are no seeds. Apparently, in this instance, two seeds were flushed into the bowl, and the nurse dumped the contents of the bowl before the appropriate surveys were performed. The licensee also stated that individuals were available in the operating room to perform surveys at the time. Surveys of the sink and drain trap were immediately performed, but the seeds were not located. The licensee stated that the fate of the seeds was known and that harm could not come to anyone as a result of the seeds being in the sewer system. This issue was determined to be reportable as a result of a recent NRC inspection and the inspectors (Neelam Bhalla) subsequent discussions with NRC Region 1 office personnel. (Call the NRC operations office for licensee radiation safety officer contact telephone numbers.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2001-06-28
38101 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-06-27 02:00 | 2001-06-27 10:00 | 2001-06-27 | BULLETIN 91-01 24 HOUR REPORT "At 0200 on 6-27-01, the Plant Shift Superintendent (PSS) was notified that during a procedure review for obtaining a UF6 negative on C-335 U/4 C/8, it was discovered that a weekly check for the presence of a fluorinating environment was not performed as required by NCSA CAS.002, Operation of the Uranium Enrichment Cascade, Control 34.11. The purpose of the control is to ensure a fluorinating environment exists without reliance on any administrative controls on the RCW system. Subsequent sampling of the cell determined the presence of UF6." Because the fluorinating environment was not checked on a weekly basis as required, the second leg of the double contingency was violated. The NRC Senior Resident has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-06-27
38100 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-06-27 18:19 | 2001-06-27 21:10 | 2001-06-28 | MANUAL REACTOR TRIP DUE TO LOW PUMP BAY LEVEL "Unit 2 was manually tripped at 1819 due to low pump bay level (-11 feet) in accordance with AOP-13A, Circulating Water System malfunction. The plant is experiencing an alewife fish kill at this time, which is the cause of the circulating water system problems. The unit 2 MSIVs were manually shut per AOP-13A. Decay heat removal is though the atmospheric steam dumps. The auxfeedwater system activated on an AMSAC signal. There is no primary to secondary leakage on unit 2. N-32 source range failed to energize on the reactor trip. Technical specification 15.3.0 was momentarily entered due to a loss of service water pumps to both units. Pump bay level has been restored." All control rods full inserted after the trip. The licensee is investigating the cause of the fish kill and the reason the N-32 source range failed to energize. The licensee notified the NRC resident inspector. * * * UPDATED AT 1518 EDT ON 6/28/01 BY RICK ROBBINS TO FANGIE JONES * * * "This supplemental notification corrects a mischaracterization reported in EN 38100. The reference to a 'fish kill' was misleading. The condition was actually caused by an unusually large influx of small forager fish at the circ water intake that resulted in blockage of the intake travelling screens. "To reiterate, PBNP Unit 2 was manually tripped from about 70% power at 1819 on Wednesday, June 27, following a rapid load reduction from 100%. The operations crew entered our Abnormal Operating Procedure (AOP) in response to the lowering pump bay level that was caused by this unusually large influx of small fish (alewives). This fish influx overloaded our traveling screens and screen wash system, causing the lowering pump bay level. The AOP directs a reactor trip at -11 feet to ensure the service water system is operated within its design basis. Following the trip and after a circ water pump was secured, the pump bay level recovered to its normal level of about -5 feet. "Due to the continuing fish influx on the travelling screens, Unit 1 was also affected and its load was reduced to about 80%. One of the Unit 1 circ water pumps was then secured, allowing pump bay level to be maintained at acceptable values. The unit remains stable." The licensee notified the NRC Resident Inspector. The R3DO (Geoffrey Wright) has been notified. | 0 | 0 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-06-27
38099 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-06-27 11:30 | 2001-06-27 13:39 | 2001-06-27 | OSCILLATION POWER RANGE MONITOR SCRAM SETPOINTS ARE NON-CONSERVATIVE "The Plant Staff was notified by General Electric (GE) via a BWR Owners Group conference call today at approximately 1130 that the Oscillation Power Range Monitor (OPRM) instrumentation SCRAM setpoints are non-conservative due to a non-conservative GE analysis. The OPRM instrumentation is an input to the Reactor Protection System. The OPRM instrument is relied on for providing a safe shutdown safety function when operating during an unstable power to flow condition. The OPRM Instrumentation equipment is therefore considered inoperable and is reportable to the NRC law 10CFR 50.72(b)(3)(v)(A), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to shutdown the reactor and maintain it in a safe shutdown condition. "The plant is currently operating within its Technical Specifications 3.3.1.3 Required Action with Off-Normal Instruction (NO C51) procedure as an alternate method to monitor and suppress thermal hydraulic instability oscillations. GE is currently issuing a 10 CFR Part 21 Interim Report and Transfer of Information to formally notify licensees with an evaluation pending." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2001-06-27
38098 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-06-25 06:00 | 2001-06-27 04:38 | 2001-06-27 | LOSS OF POWER TO EOF WHEN 12.5 KV FEEDER WAS DEENERGIZED DURING ALERT DECLARED ON 6/25/01 "The following is reportable under 10 CFR 50.72(b)(3)(xiii), 'Loss of Emergency Preparedness Capabilities.' "During the ALERT declared on June 25, 2001 (Reference: EN # 38091), there was no AC power in the Emergency Operations Facility (EOF) when the 12.5 KV feeder was lost. This impacted the ability of the EOF personnel to activate the facility in a timely manner and interrupted certain EOF functions such as ventilation, normal lighting, and some AC power outlets supporting computers and other equipment. "The facility is fully functional if the 12.5 KV feeder is available. However, if 12.5 KV power is lost, the system operating procedure limits transfer of all EOF loads to Modes 4 & 5; thus, the facility is considered conditionally functional. The procedural restrictions associated with restoration of power are being investigated. "The Alternate EOF (AEOF) is being setup to be used in the event an emergency is declared requiring activation of the EOF if events associated with the emergency result in the loss of 12.5 KV power. EOF functions would be performed from the AEOF under such circumstances. "This condition was determined to be reportable during the followup evaluations of this event." The licensee will inform state/local agencies and the NRC resident inspector. | 70 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-06-27
38097 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-06-26 13:38 | 2001-06-26 16:59 | 2001-06-26 | TURBINE TRIP - REACTOR SCRAM Unit 2 reactor scram occurred at 1338 on June 26, 2001. The reactor scram occurred as a result of a main turbine trip caused by actuation of unit protection relaying. All systems actuated as designed. The unit is being maintained in hot shutdown at normal reactor vessel water level. The cause of the turbine trip/generator lockout is under investigation. No SRVs lifted and all control rods fully inserted. One reactor recirculation pump has been restarted and the scram has been reset. The licensee notified the State, the surrounding counties and the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-06-26
38096 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-06-12 12:00 | 2001-06-26 12:44 | 2001-06-26 | LOST/STOLEN TROXLER GAUGE Tolunay-Wong Engineers, Inc. reported the loss of a Troxler moisture density gauge, model number 3430 and serial number 27955. The gauge contains 40 mCi of Am 241 and 10 mCi of Cs 137. The gauge was removed from storage along with the yellow type A over pack some point between April 26, 2001 and June 13, 2001. The licensee notified the Houston Police Department. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2001-06-26
38095 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-06-26 06:46 | 2001-06-26 08:10 | 2001-06-26 | REACTOR AUTOMATIC TRIP FROM 100% POWER DUE TO TURBINE TRIP The plant had a reactor trip from 100% power due to a turbine trip. All rods fully inserted, no ECCS actuated or relief valves lifted. The cause of the turbine trip may be due to a problem with the DEH system but they are continuing the investigation. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-06-26
38094 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-06-26 06:09 | 2001-06-26 07:52 | 2001-06-26 | MANUAL REACTOR TRIP FROM 100% POWER DUE TO FEEDWATER REGULATOR VALVE FAILURE Unit 2 was manually tripped from 100% power after the "2D" feedwater regulating valve (2FW540) was found failed closed. The "2A" and "2B" auxiliary feedwater pumps auto started as expected on low 2-steam generator level. All rods fully inserted no ECCS actuation or relief valves lifted. The plant is stable and heat sink is to the condenser through the steam dumps. The cause of the feed reg valve failure is being investigated. The NRC Resident Inspector will be notified. * * * UPDATE on 6/26/01 @ 0839 BY WINTER TO GOULD * * * The plant had a second automatic start (0733CDT) of the "2B" auxiliary feedwater pump on low-2 S/G level. The NRC Resident Inspector was informed. REG 3 RDO (Wright) was notified | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2001-06-26
38093 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-06-25 10:00 | 2001-06-25 13:59 | 2001-06-25 | OFFSITE NOTIFICATION OF AN EMERGENCY SIREN ACTIVATION "An STP Emergency Notification three tone siren was activated for a grass fire near the Tres Palacios Oaks community (located with in the 10 mile Emergency planning Zone) June 24, 2001, at approximately 3:00pm. The local Fire Department used the proper designated fire alarm signal which is separate from the emergency notification signal used in an emergency event at South Texas Project. "Local residents subsequently contacted the Matagorda County Sheriff's Office inquiring about evacuation rumors during the event. The Sheriff's Office contacted South Texas Project personnel to ensure that no emergency situation existed at the Plant. "No formal press release is planned but due to local public interest and county obligations, the County Sheriff and County Emergency Response Director along with STP personnel notified the Matagorda County Commissioner's Court of the situation at 10:00am CDT on June 25, 2001. The local media attended this meeting." The siren in question serves not only as an emergency notification siren for the plant but also for local emergencies such as fires. The sound emitted is different in each case. Since the fire department used the proper alarm the licensee believes the correct sound was emitted. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-25
38092 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-06-25 08:45 | 2001-06-25 09:15 | 2001-06-25 | NOTIFICATION TO THE FLORIDA STATE AND WILDLIFE WAS MADE BY THE LICENSEE This notification was made due to a sick, underweight loggerhead turtle being transported offsite for rehabilitation pursuant to 10 CFR 50.72(b)(2)(xi). The NRC Resident Inspector and the state were notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-25
38091 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-06-25 04:33 | 2001-06-25 06:07 | 2001-06-25 | UNUSUAL EVENT DECLARED DUE TO A FIRE IN THE PROTECTED AREA LASTING 16 MINUTES The licensee fire brigade responded to and extinguished a small oil fire in the Startup Transformer yard after entering EAL 5.1.1. The fire burned for approximately 16 minutes. The plant has reduced power from 100% to 60%. The licensee notified state/local agencies and the NRC resident inspector. At the time of the notification, the Emergency Director had upgraded the event to the Alert declaration. * * * UPDATE 0625EDT FROM CHRISP TO ROBERT STRANSKY * * * At 0455CDT the licensee declared an Alert entering EAL 5.2.1 after determining that the fire has impacted an offsite power source. Unit has entered single loop operations due to the loss of the Startup Transformer. The licensee notified state/local agencies and the NRC resident inspector. At 0619EDT, Region IV RA in consultation with the IRO Manager placed the Agency in Monitoring. Notified FEMA(Sweetzer), DOE(Yates), EPA-NRC(Terry), USDA(Graham) and HHS(Cleveland), EPA-REG(Curry). * * * COMMISSIONERS' ASSISTANTS' BRIEFING AT 0900 6/25/2001 * * * Briefer: K. Brockman (R IV). Participants: Wessman, Holonich (IRO), Thadani (NRR), Hayden, Dricks (OPA), Droggitis (STP), Gerke (OCA), Haag (EDO), Tschiltz (Chm. Meserve), Hiltz (Comm. Dicus), Beall (Comm. McGaffigan), Davis (Comm. Diaz), McCabe (Comm. Merrifield). * * * UPDATE AT 1032 FROM PLETTNER TAKEN BY STRANSKY * * * The Alert was terminated at 0908. The NRC resident inspector has been informed by the licensee. | 60 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-06-25
38090 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2001-06-24 11:03 | 2001-06-24 19:40 | 2001-06-24 | COURTESY NOTIFICATION REGARDING FAILURE OF THE 'A' PHASE BUS POTENTIAL DEVICE IN THE SWITCHYARD [outside the Protected Area but inside the Owner Controlled Area] The following text is a portion of an E-mail received from the licensee following a courtesy telephone call to the NRC Operations Center: "On June 24, 2001, at about 1103 PDT, the 'A' Phase Bus Potential Device failed in the southeast section of the San Onofre switchyard. (This device performs a monitoring function only and plant operations were unaffected). The failure resulted in debris on the road adjacent to the switchyard (old Highway 101). The resulting fire was extinguished by 1140 PDT. One individual was in the switchyard at the time of this occurrence but was not injured. No offsite personnel were injured." "As a precautionary measure, the San Onofre Security force notified the San Diego branch of the FBI and the FBI chose to respond to San Onofre. Before arriving onsite, SCE again contacted the FBI indicating they did not need to respond to this event and they did not." "The NRC Resident Inspectors have been notified of this occurrence and will be provided with a copy of this report. At the time of this occurrence, San Onofre Unit 1 remained permanently shutdown; San Onofre Units 2 and 3 were both at about 100 percent power and remain at about 100 percent power." HOO NOTE: The licensee (Ed Scherer and Clay Williams) stated that the notification to the FBI was not required and that it was only a courtesy notification. The FBI serves as local law enforcement. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2001-06-24
38089 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-06-23 08:57 | 2001-06-23 10:36 | 2001-06-23 | MAIN GENERATOR OVERCURRENT TRIP CAUSES REACTOR TRIP Main Generator overcurrent trip caused a Main Turbine trip/Reactor trip. All rods fully inserted into the core. Both Motor Driven Auxiliary Feedwater Pumps automatically started and are currently maintaining proper steam generator water levels. Reactor Coolant System is being maintained at Normal Operating Temperature and Pressure via the stream dumps to the main condenser. First out annunciator was "2A" low low Steam Generator Water level. Plant computer printout indicated that the initiating event was a Main Generator Overcurrent Trip. No work was being performed on the Main Generator when the overcurrent trip occurred. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-06-23
38088 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-06-23 03:50 | 2001-06-23 06:04 | 2001-07-09 | POWER LOST TO BUILDING BEACON CRITICALITY ACCIDENT ALARM SYSTEM (CAAS). At 0350 hours on 06/23/01, it was discovered that the CAAS beacons for building C-333 were inoperable due to a loss of power. The system is required to be operable according to TSR 2.4.4.2.b for the prescribed modes of operation. Loss of power to the CAAS beacons occurred during the process of returning auxiliary power transformers to service. Power to the beacons was lost for a total of approximately 3 minutes. Normal power was subsequently restored. The building CAAS detectability and horn audibility were not lost due to the power failure. No operations were taking place in building C-333 while the CAAS beacons were inoperable but fissile material is stored in the building. The NRC Resident Inspector has been notified of this event by the certificate holder. * * * RETRACTED AT 1630 EDT ON 7/9/2001 BY J. M. UNDERWOOD TO FANGIE JONES * * * The following is taken from a faxed report: "The PSS's reporting determination was based on the fact that the CAAS lights are mentioned in the CAAS TSR 2.4.4.2b Basis Statement. The Basis includes a paragraph that describes the quarterly surveillance of the CAAS building horns and, in this paragraph, states that the test signal activates the high radiation light and bell in C-300 and activates the building CAAS horns and lights. This is the only mention of CAAS lights in the CAAS TSR. This statement has been interpreted in the past as requiring the CAAS lights to be available and operable and, when inoperable, requiring completion of the TSR 2.4.4.2b LCO actions and reporting to the NRC per 10CFR76.120 (c)(2). "Since the subject event, NRA has reviewed the TSR, SAR. ANSI/ANS8.3, and 10CFR76 and noted the following: [1] CAAS TSR 2.4.4.2b requires the CAAS to be operable (audible) and prescribes the required actions to be taken when the 'area does not have an audible criticality accident alarm'. Audibility is proven by the building CAAS horns which were not affected by the subject power failure. There are no actions required for loss of the building lights. [2] Surveillance requirements 2.4.4.2b-1 and 2.4.4.2b-2 requires quarterly testing of the CAAS horns and verification that the CAAS air accumulator supply pressure to the building horns is adequate to sound the horns for at least 120 seconds. There are no TSR surveillance requirements for the building lights. [3] ANSI/ANS8.3, 'Criticality Accident Alarm System'. Section 4.3 requires audio alarm signals and Section 6.4 requires periodic tests of the signals. ANSI/ANS8.3 does not require or recommend visual alarm signals except in Section 4.3.8, where visual signals are recommended in areas of very high audio background or mandatory hearing protection, neither of which applies to areas outside the buildings with CAAS coverage. [4] PGDP SAR Section 5.2.2.4 states, 'a CAAS is provided to alert personnel if a criticality accident should occur. The system utilizes a distinctive audible signal to notify personnel in the affected area and initiate evacuation...'. There is no mention of the building lights. [5] 10CFR76.89, Criticality Accident Requirements, requires USEC to maintain and operate a criticality monitoring and audible alarm system. There is no mention of building lights, "From the information provided, NRA has concluded that CAAS audibility is provided solely by the CAAS horns and is not affected by the loss of the CAAS lights. Thus, the CAAS building lights are not required to be available and operable by the TSR and CAAS operability is not affected when the lights are not functional. Since the lights are not required to be available and operable by the TSR, the reporting requirement of 10CFR76.120 (c)(2) is not met and reporting is not required. In addition, the TSR LCD actions prescribed by TSR 2.4.4.2b do not apply to the CAAS lights and are not required to be implemented. Based on this information, the subject NRC event notification (PAD.01-023) is being retracted." The licensee notified the NRC Resident Inspector. The R3DO (David Hills) and the NMSS EO (Eric Leeds) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2001-06-23
38087 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-06-22 13:25 | 2001-06-22 21:18 | 2001-06-22 | LIFTING OF AN EMERGENCY DIESEL GENERATOR (EDG) HEAT EXCHANGER COOLING WATER OUTLET RELIEF VALVE DUE TO AN INCORRECT RELIEF SETTING On 06/22/01 at approximately 1325 hours, the 'C' emergency diesel generator (EDG) heat exchanger cooling water outlet relief valve (1EGPSV2409C) opened when two pumps were operating in the 'A' safety auxiliary's cooling system (SACS) loop. The relief valve reseated when one of the 'A' SACS loop pumps was secured. This problem was identified when control room personnel noticed that the indicated 'A' SACS loop head tank level was decreasing, and the leak itself was actually located by an equipment operator in the field walking down his building. The licensee reported that the relief valve was open for 38 minutes and that the estimated amount of leakage was approximately 400 gallons. (This relates to approximately 10% in the indicated level band of the 'A' SACS loop head tank, and the indicated level band was reported to be a small range in the entire tank.) Preliminary investigation indicates that a new relief valve was installed on 06/05/01, and the relief valve installed was set to relieve at 120 pounds instead of the design lift setting of 150 pounds. The initial analysis indicates that following a postulated design basis accident scenario with two SACS pumps operating in the 'A' SACS loop, the 'A' SACS loop could have reached a pressure causing the relief valve to open resulting in draining the 'A' SACS loop head tank and loop inoperability. The inoperability of the 'A' SACS loop would have prevented the 'A' control room emergency filtration unit from performing its design function. At the time of discovery, scheduled maintenance was underway that prevented the 'B' control room emergency filtration unit from performing its design function. This condition is being reported pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident -- specifically, that the operation of systems designed to maintain control room habitability could have been jeopardized. To prevent additional lifting of the relief valve, the 'A' SACS loop has been placed in a configuration that ensures system pressure will not reach a level at which the relief valve will lift (120 pounds). One pump in the loop has been tagged to prevent automatic starting, and certain flow paths were enabled and established such that they will preclude pressure increasing to 120 pounds. The licensee also checked the same relief valves associated with the other three EDGs and confirmed them to be set at the design pressure (150 pounds). The evaluation of the relief valve and its impact on 'A' SACS loop operability is continuing. The licensee plans to complete the maintenance on the 'B' control room ventilation train and return it to an operable condition. Then, the licensee plans to isolate and tag the relief valve in order to facilitate repairs. The licensee notified the NRC resident inspector and plans to notify the Lower Alloways Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-06-22
38086 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-06-22 09:31 | 2001-06-22 11:05 | 2001-06-22 | REACTOR MANUALLY TRIPPED DUE TO DEGRADED INSTRUMENT AIR PRESSURE. The reactor was manually tripped due to degraded Instrument Air pressure resulting in loss of cooling water to the Reactor Coolant pumps. All Reactor Coolant Pumps were secured: Two due to a loss of Component Cooling Water (Supply valves closed) and One due to potential loss of Cooling Water. Natural Circulation has been established with AUX Feed and Main Feed Water available to feed the Steam Generators. Presently the condenser is providing the Heat Sink (steam dumps to the main condenser). Plant is currently stable in Mode 3 (Hot Standby). All rods fully inserted into the core, and all safety systems operated as designed. The cause of degraded Instrument Air pressure is still under investigation. The Instrument Air Header pressure was restored when the Instrument Air dryer was bypassed and isolated. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable. No radiological releases, Reactor Coolant Leaks or steam generator leaks occurred during this event. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 6/22/01 @ 1300 BY SENA TO GOULD * * * The plant is off of natural circulation, the "C" reactor coolant pump was started @ 1120, "A" reactor coolant pump was started @ 1209 and the "B" reactor coolant pump was started @ 1252. The plant is stable and in mode 3. The NRC Resident will be notified. Reg 1 RDO(Trapp) was informed. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-06-22
38085 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-06-21 14:15 | 2001-06-22 10:48 | 2001-06-22 | CONTRACT SUPERVISOR TESTED POSITIVE FOR AN ILLEGAL SUBSTANCE. On 06/18/01 a contract supervisor with unescorted access was given a random drug test. On 06/21/01 at 1415 hours the results of the random drug test was reviewed by the licensee. The contract supervisor tested positive for an illegal substance. The contract supervisor's access and employment were terminated. The licensee is presently reviewing his past work. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 26.73 |  |  |  | 0 | 2001-06-22
38084 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-06-21 18:25 | 2001-06-22 01:07 | 2001-06-22 | DURING MAINTENANCE RESTORATION ELECTRICAL POWER TO THE EMERGENCY OPERATION FACILITY (EOF) WAS LOST. At 1825 CT, on 06/21/01, all electrical power was lost to the EOF. An equipment operator was restoring breaker PPPG16223 from maintenance at the EOF, when all power was lost. Power to the EOF was restored at 2108 CT, 06/21/01. Breaker PPPG16223 remains out of service to troubleshoot the cause of the incident. Breaker PPPG16223 supplies Parking Lot Lights at the EOF. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-06-22
38083 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-06-21 03:20 | 2001-06-21 06:22 | 2001-06-21 | REACTOR COOLANT PRESSURE BOUNDARY LEAKAGE FROM CONTROL ROD DRIVE MECHANISM (CRDM) # 21 The licensee reported the discovery of primary coolant system pressure boundary leakage from the CRDM # 21 lower pressure housing. Visible leakage was observed from an area containing a weld. Primary coolant system leakage is stable at approximately 0.3 gpm. The reactor was shut down earlier to investigate the elevated leak rate noted several days ago. Close inspection of the reactor head area noted the above leakage. The primary coolant system will be placed in mode 5 (cold shutdown) for evaluation and repairs. Leakage from this area is unexpected, and the mechanism for failure is not understood at this time. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2001-06-21
38082 | 0 | US ARMY |  |  |  |  | 2001-06-15 14:18 | 2001-06-20 18:39 | 2001-06-20 | THE ARMY REPORTED THE LOSS OF TWO DEVICES CONTAINING AMERICIUM - 241 The US Army reported that while taking inventory at Fort Bragg, NC, they discovered that a chemical agent detector model M43A1 and the cell assembly for the CAD were missing. Both devices each contained 300 microcuries of Am-241. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-06-20
38081 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-06-20 11:15 | 2001-06-20 11:56 | 2001-06-20 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY. COMPENSATORY MEASURES TAKEN UPON DISCOVERY THE RESIDENT INSPECTOR WAS NOTIFIED CONTACT THE HOO FOR ADDITIONAL INFORMATION | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 73.71(b)(1) |  |  |  | 0 | 2001-06-20
38080 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-06-20 00:11 | 2001-06-20 04:07 | 2001-06-20 | AUTOMATIC REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE FAILING SHUT. At 0011 CDT feedwater regulating valve to steam generator "B" failed to the closed position and manual control was not effective. The reactor/turbine tripped on steam flow greater than feed flow coincident with low steam generator water level. Following the trip, the rod bottom light for rod D4 (interior rod) was off and valve LD-2 indicated mid-position (letdown isolated on low pressurizer water level). Individual Rod Position Indication for rod D4 indicates zero, however, emergency boration was used to inject the required amount of boric acid for one stuck rod. Excess letdown was established at 0028 CDT hours, since normal letdown was not available due to the failure of valve LD-2. All emergency core cooling systems, emergency diesel generators are fully operable if needed and the electrical grid is stable. Both Motor Driven and the Turbine Driven Auxiliary Feedwater Pumps automatically started. The Turbine Driven Auxiliary Feedwater pump was secured per procedure and steam generator water is being maintained by the Motor Driven Auxiliary Feedwater Pumps. At this time the licensee thinks that rod bottom light for rod D4 is burned out. The licensee is also investigating why letdown isolation valve, LD-2, indicates mid-position and the unexpected closure of feedwater regulating valve for steam generator "B". The steam dump bypass control system is operating properly. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2001-06-20
38079 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-06-19 09:15 | 2001-06-19 12:13 | 2001-06-22 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE HPCI system was declared inoperable due to all alarm functions not operating. The local undervoltage alarms did not annunciate in the control room. This condition was discovered during a normal routine test. They were attempting to send a signal from the local HPCI panel in the plant to the control room, but the control room did not receive it. They verified that the local panel is operable. An operator was locally stationed at the subject panel to verify current alarm status and call the control room. Therefore, in this mode of operation, the HPCI system has been declared operable. They are still investigating the problem with signal transmission. The NRC Resident Inspector was notified. The State and local agencies will be informed. * * * RETRACTION CALLED IN AT 1110 ET ON 06/22/01 BY BRETT WELLER TAKEN BY MACKINNON * * This notification retracts the above notification which was made due to HPCI being declared inoperable because of a questionable 250VDC MCC power. This uncertainty was based on control room annunciator that did not operate as expected when alarm checks were performed. After investigation it was determined that there was no degraded power system, nor was there any problem with the voltage sensing circuit, and HPCI was operable at all times during the event. A faulty control room annunciator alarm card caused the confusion regarding the HPCI power source. State and Local authorities were notified of this retraction by the licensee. R3DO (B. Jorgensen) notified. The NRC Resident Inspector will notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-06-19
38078 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-06-18 14:10 | 2001-06-18 14:44 | 2001-06-18 | PLANT DECLARED AN UNUSUAL EVENT DUE TO A TOXIC FUME RELEASE LIMITING ACCESS TO THE AREA During chemical unloading of sulfuric acid from a truck trailer, excessive acid fumes came from the tank, which was located in the turbine building. The chemistry technician supporting the delivery experienced throat and respiratory irritation and was transported to the hospital for examination. The delivery was stopped at the time of discovery and access to the area has been limited. An investigation as to the cause is in progress. The licensee will notify the NRC Resident Inspector and has notified the New Jersey, Delaware and Lower Alloways Creek Township Police Departments. * * * UPDATE ON 6/18/01 @ 1832 BY MCGREGER TO GOULD * * * The NOUE was terminated at 1828 since there no longer is any leakage being detected. They believe the leak was from a vent path, since no breech was detected. The NRC Resident Inspector will be notified. The Reg 1 RDO(Trap), EO(Matthews) and FEMA(Belcher) were notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2001-06-18
38077 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2001-06-18 03:15 | 2001-06-18 11:39 | 2001-06-18 | BREAKER CONTROL SWITCHES NOT PROPERLY ALIGNED "This report is being made under the reporting requirement in 10CFR50.72(b)(3)(vi) to describe an event or condition that could have prevented the fulfillment of a safety function. "On June 18, 2001, at approximately 0315, an offsite power supply to two of four emergency buses on both Units 2 and 3 was lost. All four emergency buses automatically transferred to their respective alternate supply per design. "The restoration procedure subsequently directed the crew to 'green flag' the tripped breakers. The purpose of the procedural step was to align the breaker switch with the actual position of the breaker. The procedure, however, did not direct the crew to 'red flag' the alternate breakers which automatically closed (i.e. match the switch position to the actual breaker position). This created a condition in the electrical logic which would have prevented two of four emergency buses from automatically receiving power from their respective diesel generators in the event of a design basis accident. "Once discovered, the crew 'red flagged' the alternate breakers and restored diesel generator operability. "The restoration procedures have been revised to prevent this condition from reoccurring. "The NRC resident has been informed." The condition existed for about 3 hours, at which time the breaker switches were placed in the 'red flagged' position as required. An investigation is ongoing to determine the cause of the initial power loss. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-06-18
38076 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2001-06-14 11:30 | 2001-06-18 11:37 | 2001-06-18 | ILLINOIS LICENSEE REPORTED TO THE STATE THAT THEY HAD A MEDICAL MISADMINISTRATION The Evanston Northwestern Hospital reported that they had a medical misadministration(while performing an IVB event) when they were unprepared with the second syringe after the primary syringe ran out of water. This resulted in an increase in treatment time by 23% (prescribed treatment time was 206 seconds and actual time was 253.4 seconds). The isotope used was Sr-90 with an activity of 1.2 GBq. The following fax was received after the initial telephone report: "[Northwestern Hospital] called [the Illinois Department of Nuclear Safety] at 11:33 to report that they had an IVB event this morning using the Novoste device. Apparently they ran out of water in the primary syringe and were not prepared with a secondary syringe to replace it. This caused an increase in the treatment time by 23%. The prescribed treatment time was 3 minutes and 26 seconds. [Northwestern Hospital] was unclear if the sources moved during the syringe change-out procedure. He is not on-site but he will call with additional details once he returns to the hospital. The isotope involved is Sr-90 with an activity of 1.2 GBq." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2001-06-18
38075 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-06-18 02:04 | 2001-06-18 10:13 | 2001-06-18 | VITAL BUS SOURCE SEQUENCER ACTIVATED ON LOSS OF NORMAL POWER SUPPLY "This is a notification of an unplanned automatic actuation of the Unit 1 4.16 kV Sfgds Bus 16 (B-train) source sequencer. Severe weather resulted in an electrical grid disturbance which caused 4.16 kV Bkr CT11-1 to open, subsequently rendering the normal Bus 16 offsite 4.16 kV source (CT11) from 345 kV Bus 1 to Unit 1 to be lost. CT11 transformer is a 13.8 to 4.16 kV step-down transformer. Nothing appears to be wrong with the CT11 transformer. The sequencer operated as designed and transferred Bus 16 to its backup 4.16 kV offsite source (1R). "Charging and letdown were lost during this transient, and subsequently restored. Two (2) of the 4 Cooling Tower Pumps and associated Cooling Towers were also lost and remain out of service. B train Sfgds Control Room ventilation was also lost during the transient. This resulted in a temporary dual unit 7 day LCO entry per TS 3.13.A.2, which was subsequently exited when the operability of the ventilation system was restored. "The plant is currently in a Unit 1 7 day LCO per TS 3.7.B2., and investigating the cause of Bkr CT11-1 opening." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-06-18
38074 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-06-15 08:15 | 2001-06-15 11:20 | 2001-06-15 | PRESS RELEASE WILL BE MADE BY THE LICENSEE ABOUT AN ON-SITE FIRE A fire in a non-radiological area (computer UPS inverter cabinet in the turbine building) occurred with no injuries to personnel. The fire was contained and extinguished within 30 mins by off-site fire department. Notification to the NRC was made due to unexpected significant press coverage and subsequent corporate press release to be issued. The NRC resident inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2001-06-15
38073 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-06-15 09:00 | 2001-06-15 11:18 | 2001-06-15 | OFFSITE NOTIFICATION DUE TO ACID SPILL ONSITE "At 0900 hrs Comanche Peak reported a spill of approximately 550 gallons of Hydroxy Ethylidene Diphosphonic Acid (Trade name 'Thru Guard') to the Texas Natural Resource Conservation Committee (TNRCC). The spill occurred at 0030 hrs. on 6/15/01 when a thunderstorm moving through the area caused the level gauge glass of the outside storage tank to separate from the tank. An estimated 20 gal of the spilled acid reached Squaw Creek Reservoir before the spill was contained. "Clean up activities were completed at 0800 hrs on 6/15/01." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-15
38072 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-06-14 10:00 | 2001-06-14 16:09 | 2001-06-18 | AGREEMENT STATE REPORT - MISSING TROXLER SURFACE DENSITY GAUGE The licensee notified the State of Arkansas about 10:00 AM CDT today 6/14/01, that a Troxler Model 4640B surface density gauge, containing 8 mCi of Cs-137, was missing from the back of his truck. The gauge was known to be chained and locked in the back of the truck last night (6/13/01) around 7:00 PM CDT. The chain and lock are still in the truck, undamaged. The Howard County Sheriff's Department and Hope Arkansas Police have been notified of the missing gauge. There will be a press release sent to state police, surrounding states and local authorities. NRC Region 4 (Vivian Campbell) has been notified. * * * UPDATE ON 6/18/01 @1514 BY BRADLEY TO GOULD * * * The licensee reported to the State (6/18/01 @ 0740) that the gauge had been returned early this morning intact and not damaged. The Reg 4 RDO(Loveless) and the NMSS EO(Fred Brown) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2001-06-14
38071 | -1 | VIRGINIA CARDIOVASCULAR SPECIALIST |  |  |  |  | 2001-06-13 14:00 | 2001-06-14 14:59 | 2001-06-15 | MEDICAL MISADMINISTRATION - WRONG PATIENT WAS GIVEN DIAGNOSTIC DOSAGE There were 2 patients in the waiting room with similar names. When the name was called out, the wrong patient answered and was administered the dose of 32.7 mCi of technetium Sestamibi Cardiolyte. Subsequently, it was determined that the wrong patient received the dose. The patient and attending physician have been notified. A written report will follow. * * * RETRACTION 0846 6/15/2001 FROM WEAVER TAKEN BY STRANSKY * * * The licensee is retracting this notification. This event involved a diagnostic dose of technetium and resulted in a dose to the patient which is below the reporting threshold. Notified R2DO (Boland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 2 | VA | HOS |  | 35.33 |  |  |  | 0 | 2001-06-14
38070 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-06-13 19:30 | 2001-06-13 20:12 | 2001-06-13 | A SMALL QUANTITY OF SPECIAL NUCLEAR MATERIAL UNACCOUNTED FOR During the process of investigation of the Transverse In-Core Probe (TIP) detector accountability issue reported on 6/8/01 (EN 38059) it has been discovered that one additional detector cannot be readily accounted for. This was discovered during verification of the detectors installed in the TIP machines. The TIP detector is a fission chamber that utilizes approximately 1 mg of enriched uranium and is therefore considered Special Nuclear Material (SNM). During 1975 to 1986 Pilgrim did not track TIP detectors as SNM due to the detectors containing less than one gram of SNM. It is suspected that during this time frame this detector was changed out. In 1987 a records search was made but did not reveal maintenance performed on this detector. It Is believed that this TIP detector has been properly disposed of as radioactive waste and is not in the public domain. Investigation is continuing. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS OF SNM/CRIT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 70.52(a) |  |  |  | 0 | 2001-06-13
38069 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-06-13 08:39 | 2001-06-13 12:31 | 2001-06-13 | PARTIAL LOSS OFFSITE COMMUNICATIONS On Wednesday, June 13th at 0839, a lightning strike caused a loss of the commercial phone systems at the Monticello Nuclear Plant Site. This affected phones in the control room and Technical Support Center as well as plant paging capabilities. One commercial phone line in the control room, the ENS system, auto-ring hotlines to the State EOC/Duty Officer, fax capabilities and the Radio System to Off-site agencies remained operational. Notification to the State and Local Counties were made informing them of the degraded communication capabilities. The EOF phone system remained operational. All communication systems were restored at approximately 1100 on June 13th. The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-06-13
38068 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-06-13 05:30 | 2001-06-13 11:21 | 2001-06-13 | TRANSPORTATION REPORT INVOLVING RAD WASTE SHIPMENT FROM FERMI TO BARNWELL, SOUTH CAROLINA "Event notification resulting from an offsite notification of a transportation accident involving a radioactive waste shipment from Fermi 2 to Barnwell, South Carolina. NRC reportable under 10CFR50.72(b)(2)(xi) any event or situation for which notification to other government agencies has been made. "At approximately 0530 hours on 06-13-2001, a Hittman Transport vehicle transporting Class 'A' radioactive waste material [proper shipping name: Radioactive Material, Low Specific Activity, n.o.s. 7, UN2912, Fissile Excepted, Compacted Dry Active Waste] from Enrico Fermi 2 facility to Barnwell, SC was involved in a vehicle accident west of Columbia, South Carolina. "Hittman Transport notified the South Carolina Department of Health and Environmental Control at approximately 0805 hours on 06-13-2001 concerning the transportation accident. Hittman Transport also notified Fermi 2 at approximately 0810 hours on 06-13-2001 of the vehicle accident. "The transportation accident was related to rain storm activity in the area and the driver of a passenger vehicle, responsible for the accident, received a traffic citation for speed too fast for conditions. The tractor suffered minor damage, but once released by the South Carolina State Police was able to be driven approximately 6 miles to a repair facility. No damage was noted to the trailer, shipping cask, or cask tie down equipment at the accident scene "At the repair facility, a mechanic evaluated the tractor condition and cleared the tractor and trailer for continued service to the Chem Nuclear Consolidation Facility in Barnwell, SC. The driver of the tractor performed a dose rate survey of the trailer and the dose rates were unchanged from the measured values at the Fermi site. "Fermi 2 does not intend to submit a press release in Michigan since the accident occurred in South Carolina and the proper South Carolina agencies were notified. "A follow up report is not anticipated, since no damage to the waste shipping cask was noted at the repair facility." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-13
38067 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-05-12 16:53 | 2001-06-13 10:57 | 2001-06-13 | 60 DAY OPTIONAL REPORT IN ACCORDANCE WITH 10 CFR 50.73(a)(1) "During performance of a loss of offsite power test with a LOCA, an automatic start of the A and B emergency diesel generators, the A and B core spray systems, and the A, B, C and D low pressure coolant injection pumps occurred. All actuations were complete and functioned as designed. The start was inadvertent and occurred when a 125 VDC knife blade was closed. The switch was installed as part of the procedure and was wired incorrectly such that when it was closed it caused an inadvertent LOCA signal to the affected systems." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-06-13
38066 | 0 | MT DEPARTMENT OF TRANSPORTATION |  |  |  |  | 2001-06-12 08:15 | 2001-06-13 10:02 | 2001-06-13 | DAMAGED MOISTURE/DENSITY GAUGE A Troxler Model 3440 moisture/density gauge (s/n 25332), containing one 8 mCi Cs-137 and one 40 mCi Am-241/Be sources, was slightly damaged when it was struck by a roller. The area surrounding the gauge was immediately roped off until the gauge could be surveyed. The licensee stated that the sources were retracted at the time of the event and results of surveys and wipe tests were negative. The damage appears to be limited to a slight denting of the plastic cover. The licensee has visually inspected the sources but did not observe any damage. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-06-13
38065 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-06-11 14:00 | 2001-06-11 16:50 | 2001-06-11 | GRASS FIRE IN THE OWNER CONTROLLED AREA - OFFSITE NOTIFICATION The licensee called the Bethel Fire Department for help in extinguishing a grass fire on owner controlled property outside of the protected area. No power lines were threatened. The fire was put out in 34 minutes. The licensee also notified the States of North and South Carolina, the Counties of York, Gaston and Mecklenburg as well as the NRC resident inspector. | 100 | 94 | 0 | 100 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-11
38064 | 0 | ION BEAM APPLICATIONS |  |  |  |  | 2001-06-11 12:25 | 2001-06-11 15:48 | 2001-06-11 | IRRADIATOR SOURCE RACK STUCK IN THE UNSHIELDED POSITION While initiating a run, one of two source racks did not fully withdrawal. The system is designed to automatically lower the racks if the full out position is not reached within a set amount of time. This occurred, but the same rack that did not fully withdrawal would not insert. The licensee noted the occurrence and attempted to raise the stuck rack a little, hoping to free it. This worked and then the rack was fully inserted without incident. Upon investigation it was discovered that there was a loose guide cable. This cable was tensioned and the rack was tested several times with no problems. The irradiator was then returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSHIELD STUCK SOURCE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 36.83(a)(1) |  |  |  | 0 | 2001-06-11
38063 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-06-11 13:23 | 2001-06-11 14:04 | 2001-06-11 | OFFSITE NOTIFICATION "At 1323 hrs, the Ohio Environmental Protection Agency (OEPA) was notified per Ohio Administrative Code (OAC) 3745-15-06(B) that an opacity exceedance had occurred at the X-600 Steam Plant. Details are provided below. "At approximately 0500 hrs, Utilities Operations personnel began shutting off the steam flow to the X-333 Process Building in preparation for maintenance and repair work on the steam lines. Total steam demand dropped to approximately 92,000 lb/hr (46,000 lb/hr for each of the two operating boilers). The boilers are difficult to control below approximately 50,000 lb/hr. At approximately 0518 (based on six-minute increments), Boiler #1 reached an opacity of 23% for 6 minutes, then dropped below 20%. At 0530, it rose to 33% for 6 minutes. At 0542, it again rose to 33% for 6 minutes. At 0600, it rose initially to 23%, then to approximately 28%. The Boiler Operators started several steam turbines to increase the load above 50,000 lb/hr each and regained control. "OAC 3745-17-07 limits the boilers to an opacity of 20% as a 6 minute average. One 6 minute average per 60 minute period may exceed 20% but may not exceed 60%. There were four six-minute readings between 20% and 60% in a 60 minute period, therefore, this is reportable to the Ohio EPA. OAC 3745-15-06(B) requires an immediate report in the event that a malfunction causes the emission of contaminants in violation of any applicable law. By reporting such an incident in a timely manner, the incident is not considered a violation. Details of the incident will be included in the next quarterly OEPA opacity report. Site management has taken action to prevent recurrence of any further opacity exceedances related to the above mentioned maintenance evolution. "This is reportable as a 4 hr. Event due to notification to a government agency (OEPA) being made per Nuclear Regulatory Event Reporting Procedure UE2-RA-RE1030 Appendix D Criteria P. (Miscellaneous)." The NRC resident inspector has been informed of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-06-11
38062 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-06-11 11:26 | 2001-06-11 12:34 | 2001-06-11 | FIRE IN AN OFFSITE SUBSTATION - LOCAL FIRE DEPARTMENT CALLED The licensee requested offsite assistance from the Goshen Fire Department because of a fire outside the protected area. The fire is in a substation near the fire training facility and has affected power to the Emergency Operations Facility (EOF). The EOF has an emergency diesel generator, but this tripped when it was brought on line. Plant operations are not affected. The fire department is on scene and has not identified any flames, but smoke is still coming from the substation, the substation is partially underground. The licensee will notify the town of Waterford and the State of Connecticut. The NRC resident has been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-11
38061 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-04-19 23:00 | 2001-06-11 11:44 | 2001-06-11 | 60 DAY REPORT - INVALID ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM "On April 19. 2001, at 2300, during restoration of an out of service which required relanding two leads at Solid State Protection System slave relay K620, one wire came off the screw as it was being relanded to slave relay K620 and made intermittent contact with terminal 8. It was subsequently found the Unit 2 'A' Auxiliary Feedwater pump breaker closed but the pump did not start since the breaker was in the test position and steam generator blowdown containment isolation valve 2SD002H was closed. The Unit 2 'A' Auxiliary Feedwater pump and 2SD002H are both actuated by slave relay K633 which is fed from the same master relay that feeds slave relay K620. It could not be determined how slave relay K633 was actuated during this evolution. This is considered a partial train actuation. Other slave relay components were properly removed from service or in a position such that their safety function had already been completed or were not expected to actuate due to the short duration of the signal. Subsequent slave relay testing verified all slave relays and equipment circuits were operating properly. The event was entered into the Corrective Action Process to initiate corrective actions." The NRC Resident Inspector was notified of this 60 day report by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-06-11
38060 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-06-10 07:15 | 2001-06-10 11:12 | 2001-06-20 | POSSIBLE SPENT FUEL STORAGE CAST DEFECT AND POTENTIAL SIGNIFICANT REDUCTION IN EFFECTIVENESS OF THE SPENT FUEL STORAGE CASK CONFINEMENT SYSTEM DUE TO FAILURE OF MULTI-PURPOSE CANISTER (MPC) VENT AND DRAIN CAPS TO FULLY CLOSE (4-HOUR REPORT) As part of the dry storage project, the licensee has loaded one MPC-68. (This MPC holds 68 fuel bundles.) Subsequent to system vacuum drying and helium backfilling, the vent and drain caps failed to fully close (at 0715). These caps are currently about half closed, and they appear to be stuck in that position. At this time, the licensee is not aware of the loss of any helium. Licensee personnel have snooped for helium in the area and near the fittings. Licensee personnel are also currently in the process of installing pressure gauges to verify that the proper amount of helium remains in the MPC. The licensee plans to place a helium purge on the system if it is determined that helium is being lost. The licensee also notified the cask supplier (Holtec International). The supplier informed the licensee that the presents of helium will keep the system closed. The technical specifications that apply to dry storage state that the MPC shall be dry and helium filled, and a helium backfill density limit is also specified. The licensee stated that this technical specification density requirement was met before the attempt to close the vent and drain caps. At this time, the licensee believes that this limit is still being met. However, the licensee is not positive that this limit is being met with the vent and drain caps in the current position. Therefore, the applicable technical specification limiting condition for operation (LCO) was entered. This LCO requires the licensee to perform an engineering evaluation to determine the impact of helium differential within 72 hours and to develop and initiate corrective actions necessary to return the MPC to an analyzed condition within 14 days. In addition, the applicable technical specifications also specify an MPC helium leak rate limit. The LCO for this specification was also entered. It requires the licensee to perform an engineering evaluation to determine the impact of increased helium leak rate on heat removal capability and offsite dose within 24 hours and to develop and initiate corrective actions necessary to return the MPC to an analyzed condition within 7 days. (The supplier is currently performing an engineering evaluation for the licensee, and the results are expected to be available later today.) The licensee is making this notification as a 4-hour report in accordance with 10 CFR 72.216(a)(1) and (2) for any instance of a defect in any spent fuel storage cask structure, system, or component which is important to safety and for a significant reduction in the effectiveness of any spent fuel storage cask confinement system during use of the storage cask under a general license issued under 10 CFR 72.210. HOO NOTE: In accordance with 65 FR 63788 on 10/25/00, the reporting requirements of 10 CFR 72.216 were revised (effective 01/23/01) to require that licensees make initial and written reports in accordance with 10 CFR 72.74 and 72.75. Therefore, more appropriate reporting requirements for this 4-hour report are believed to be 10 CFR 72.75(b)(2) and (3). The licensee plans to notify the NRC resident inspector. * * * UPDATE ON 6/20/01 @ 1625 BY GORLEY TO GOULD * * * RETRACTION Further review of this event it has determined that there was no defect in the multi-purpose canister(MPC) vent and drain caps. The failure of the vent and drain caps to fully close was due to the procedural process used(no lubrication being applied and no torque requirement was used) and a fault tolerant design basis that was less than adequate(thread design and hole locations in the cap). Therefore, the licensee is retracting this event. NRC Resident Inspector was notified. Reg 2 RDO(Cahill) was informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SPENT FUEL CASK EVENT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 72.75 |  |  |  | 0 | 2001-06-10
38059 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-06-08 16:15 | 2001-06-08 17:12 | 2001-06-08 | SPECIAL NUCLEAR MATERIAL (SNM) REPORT INVOLVING 1 MILLIGRAM U-235 "During [the] process of replacing the 'A' Transverse In-Core Probe (TIP) Detector, the old detector was removed and its serial number recorded. The serial number was not the serial number expected. The expected serial number was 6553444 and the detector that was removed had serial number 6608500. The TIP detector is a fission chamber that utilizes approximately 1 milligram of enriched uranium and is therefore treated as SNM. "During 1975 to 1986, Pilgrim did not track TIP detectors as SNM due to being less than one gram of SNM. It is suspected that during this time frame this detector was changed out. In 1987 a records search was made but did not reveal maintenance performed on this detector. However, an intensive records search will be performed as well as corrective actions yet to be determined." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS OF SNM/CRIT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 70.52(a) |  |  |  | 0 | 2001-06-08
38058 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-06-07 21:33 | 2001-06-08 00:41 | 2001-07-11 | HPCI DECLARED INOPERABLE DUE TO A FAULTY FLOW INDICATING SWITCH With DAEC operating in mode 1, at approximately 47% power, HPCI was declared inoperable due to a faulty flow indicating switch which is utilized to position the minimum flow valve. A 14-day LCO was entered per Technical Specification 3.5.1, condition F, at 2133 on 6/7/01. This condition is reportable under 50.72(b)(3)(v)(D) and 50.73(a)(2)(v)(D) as a failure of a single train of equipment required to mitigate the consequences of an accident. While an in-plant operator was performing his rounds within the HPCI room, he discovered that flow indicating switch, FS2310, which should indicate total HPCI flow, indicated approximately -170 gpm rather than the expected zero gpm. The HPCI pump was not in operation. This flow switch is interlocked with the HPCI minimum flow valve, allowing it to open with total HPCI flow less than 300 gpm and HPCI discharge pressure greater than 125 psig. The flow switch would close the minimum flow valve once HPCI total flow reached 600 gpm. With the correct operation of the HPCI minimum flow valve in question, HPCI was declared inoperable. It is believed that the cause of the faulty indication is air in the instrument sensing lines feeding the flow switch. Troubleshooting efforts will begin early tomorrow morning. The NRC Resident Inspector was notified HOO NOTE: see event #38029 * * * RETRACTED AT 1359 EDT ON 7/11/2001 BY JOHN KARRICK TO FANGIE JONES * * * "This condition was reported (EN #38058, June 7, 2001) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to [D] mitigate the consequences of an accident.' NUREG-1022, Rev. 2 guidance for this reporting criterion essentially requires any unplanned HPCI LCO at BWRs to be reported as a loss of a single train safety system. Further review of this event indicates that, since only the flow switch for the HPCI minimum flow valve was inoperable, the minimum flow valve instrument Tech Spec could and should have been entered instead of the HPCI system LCO. The instrument spec. (TS 3.3.5.1, Condition E) provides a 7-day completion time to return the instrument to service. If the instrument is not restored in 7 days, then the 14-day HPCI system LCO would be entered. The instrument was returned to service the following day. In addition, an assessment of the as-found condition (irrespective of TS) concluded that the HPCI system was capable of performing its intended safety function with this switch in its as-found condition. Therefore, there was no event or condition that could have prevented safety function fulfillment and this event is being retracted. No other reporting criteria apply to this event." The licensee notified the NRC Resident Inspector. The R3DO (David Hills) was notified. | 47 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-06-08
38057 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-06-07 18:30 | 2001-06-07 20:53 | 2001-06-07 | POTENTIAL NON-CONSERVATISM IN MAIN STEAM LINE BREAK ACCIDENT IDENTIFIED DURING REACTOR POWER UPDATE ANALYSES "During preparation of a new analyses for reactor power uprate, a potential non-conservatism was discovered regarding the main steam line break accident with an assumed single failure of a main feedwater regulating valve. This non-conservatism could negatively impact the resultant peak containment pressure that would be reached in the event of an accident. The current Point Beach accident analysis does not appear to properly account for the volume of high temperature feedwater that would be released inside containment during a main steam line break accident. It does not appear to correctly model failure of the feedwater regulating valve to close. "Based on the revised analyses performed by the reactor vendor (Westinghouse) at the uprated power conditions, peak containment pressure could reach 64.2 psig. No revised analysis data is yet available for the currently licensed power level; however, the uprated analysis bounds the current plant design. The 64.2 psig value exceeds the containment design pressure of 60 psig. "The Bases for Technical Specification 1 5.3.6.A.1 .a states, The safety design basis for the containment is that the containment must withstand the pressures and temperatures of the design basis LOCA without exceeding the design leakage rate. The design allowable leakage rate La is 0.4% of containment air weight per day at 60 psig . Containment operability is maintained by limiting the overall containment leakage rate to within the design allowable leakage rage (La). "FSAR section 5.1 documents that the containment can withstand pressure loadings at least 50% greater than those calculated for the postulated loss-of-coolant accident alone, and 25% greater than those calculated for the postulated loss-of-coolant accident with a coincident design earthquake (FSAR 14.3.4 states that containment pressure will peak between 52 and 54 psig). "Since the revised analysis is only for uprated power conditions, it does not exactly predict containment pressure results at the current licensed power level. However, the new analysis calls the results of the current analysis into question. Therefore, this report is being conservatively made to document this concern. The containment has been determined to be operable per the guidelines of Generic Letter 91-18. Mitigating circumstances include the fact that calculations in the FSAR document that the containment is capable of withstanding the higher pressure of the revised analysis. "The containment will continue to perform its safety function. Any radiological release during a main steam line break accident is assumed to vent directly to the atmosphere (through the break), independent of containment integrity and is within current analyses." Westinghouse is performing a reanalysis with corrective actions to be determined. The licensee informed the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2001-06-07
38056 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2001-06-06 16:30 | 2001-06-06 20:53 | 2001-06-06 | OFFSITE NOTIFICATION OF HYDRAZINE SPILL "On June 6, 2001, between 1200 and 1300 hours PDT, personnel were unloading hydrazine at a site HAZMAT pad and inadvertently spilled about 20 gallons. All 20 gallons were contained within the concrete pad and berm and were subsequently recovered for disposal. No hydrazine was released to the environment and no employees were injured. While this did not represent a significant environmental event, at about 1630 PDT on June 6, 2001, SCE began notifying the Office of Emergency Services, the National Response Center, and the San Diego Department of Environmental Health. Consequently, Southern California Edison is providing this notification in accordance with 10 CFR 50.72(b)(2)(xi) for notification of other government agencies. At the time of this occurrence, both Units 2 and 3 were operating at about 100% power; Unit 1 remains permanently defueled. SCE will notify the NRC Resident Inspectors about this notification and will provide them with a copy of this report." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-06
38055 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2001-06-04 | 2001-06-06 17:37 | 2001-06-07 | AGREEMENT STATE REPORT REGARDING PACKAGE DAMAGED DURING OVERSEA SHIPMENT The New York City Bureau of Radiological Health was contacted on 6/6/2001 by a Japan Airlines (JAL) representative regarding a damaged shipment of 104 µCi of I-125 (liquid). The package was being shipped from New England Nuclear in Boston, Massachusetts to China Isotope Corporation in Beijing, China. The package had been transported by truck to JFK Int'l Airport, where it was loaded onto a JAL aircraft. The JAL representative reported that the package was badly damaged and leaking upon arrival in Tokyo, Japan. Representatives of the Bureau of Radiological Health and Radiac (a contractor for JAL) surveyed the building at JFK Int'l Airport where the package had been stored, but found no radioactive contamination. The caller was unsure of actions taken at the airport in Tokyo. HOO NOTE: Provided above information to the DOT National Response Center. * * * UPDATE ON 6/7/01 @ 1132 BY BORRI TO GOULD * * * A JAL representative notified New York City Bureau of Radiological Health that they measured 4000 cpm in the freight container at the Tokyo airport. Also a worker at the JFK airport admitted that he broke the package when loading it on the plane. Notified REG 1 RDO(Evans) and NMSS EO(Hickey) * * * UPDATE 1518EDT ON 6/7/01 FROM BOB GALLAGHAR TO S. SANDIN * * * "Date: June 7, 2001 "Update Information from Massachusetts Radiation Control Program "Provided by Robert Gallaghar, Supervisor Inspection & Enforcement, Materials Section "PACKAGE DAMAGED DURING OVERSEA SHIPMENT "The package was being shipped from PerkinElmer Life Sciences in Boston, Massachusetts to China Isotope Corporation in Beijing, China. The package contained 130 mCi (4.8 GBq) iodine-125 as NaI in < 1 ml liquid. External radiation measurement imply that 1 to 30 mCi of I-125 may have been released from the shielded container into the surrounding packaging material. The package was secured in a plastic bag and held in a cordoned off area. "On June 6, 2001 a contamination survey was performed of the JAL facility at JFK and confirmed no contamination. JAL representatives confirmed that the incident was promptly reported to the Japan Bureau of Radiation Protection. An inspector from the Japan Radioisotope Association has made radiation and contamination surveys. "The package was one of several in a 3.8 cubic meter shipping container. A radiation reading of 3.8 mr/hr at 1 meter was reported outside the lead shielding. JAL representatives have informed PerkinElmer there were two spots of contamination, one on the floor of the container and one on a pallet, both places having been in contact with the package. No other contamination was found in the area or on any persons." The Massachusetts Radiation Control Program informed NRC Region I (Duncan White). Notified R1DO(Evans) and NMSS(Susan Frant). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2001-06-06
38054 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-06-05 23:35 | 2001-06-06 15:58 | 2001-06-06 | TEMPORARY LOSS OF CRITICALITY ACCIDENT ALARM SYSTEM DUE TO POWER FAILURE "On Tuesday, June 5, at 1135 PM, a power supply generator automatically shut-down due to low oil pressure, temporarily de-powering the criticality accident alarm system (CAAS). The power generator was in use due to on-going testing activities related to prevention of inadvertent UPS-related system failures. The status of the generator's oil pressure was identified prior to the shutdown and plans to re-route power and repair the generator were actively underway when the shutdown occurred. All SNM operations had been notified prior to the shutdown of the potential need to stop movement of SNM, and movement was stopped immediately upon loss of power to the CAAS. At 11:40 PM power was restored and the CAAS was again functioning normally." The licensee has informed the NRC Resident Inspector and NRC Region II regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 1 | 2001-06-06
38053 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-06-05 10:48 | 2001-06-05 13:24 | 2001-06-05 | UNEXPECTED TRIP OF THE "1A2" REACTOR COOLANT PUMP CAUSED A TURBINE TRIP/REACTOR TRIP. On 06/05/01 at 1048ET St. Lucie Unit 1 experienced an unexpected trip of the "1A2" Reactor Coolant Pump. This was immediately followed by an automatic reactor trip from the Reactor Protection System on reactor coolant low flow and subsequent turbine trip. All rods fully inserted into the core. Approximately one minute later the "1B" Main Feedwater pump tripped and then the Auxiliary Feedwater System actuated, "B" Electric Driven Auxiliary Feedwater Pump and the Turbine Driven Auxiliary Feedwater Pump, to the "1B" Steam Generator. The Reactor Coolant System is stable in Mode 3, Hot Standby, with the secondary steaming via the steam bypass control system and feedwater from the "1A" Main Feedwater Pump. The causes of the Reactor Coolant Pump trip and the Main Feedwater pump trip are currently under investigation. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Steam generator safety valves opened/closed. No leaking steam generator tubes. "1A" Component Cooling Water Heat Exchanger and the "1A" Reactor Vessel Level Monitoring System were inoperable during the reactor trip. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2001-06-05
38052 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-06-05 | 2001-06-05 04:59 | 2001-06-05 | LOSS OF PROCESS COMPUTER WITH LINK TO SAFETY PARAMETERS DISPLAY SYSTEM The plant process computer system failed. This system provides a link to the Safety Parameter Display System (SPDS). Immediate actions were taken to restore the computer and SPDS to no avail. The plant computer group representative has been called in to address the computer problem. Work continues to try and restore the computer to operation. Also, the availability of the Emergency Response Data System (ERDS) availability is questionable. The licensee notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2001-06-05
38051 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2001-04-11 08:27 | 2001-06-04 16:57 | 2001-06-04 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DURING POST-MODIFICATION TEST ACTIVITIES "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A), to describe an invalid actuation of the primary containment isolation system. "Unit 2 was in mode 5 on day 24 of a scheduled refueling outage with the reactor cavity flooded. Unit 3 was at 100 percent power. The impact on the facility from the event was minimal. The plant equipment responded correctly. "On April 11, 2001 at 0827 hours Central Daylight Time, Unit 2 received invalid Group 2, 3, 6 and 8 Primary Containment Isolation Signals (PCIS) during performance of Post-Modification Testing (PMT) activities. The PCIS isolations were a result of an invalid low reactor water level signal generated when the power fuses were removed during the test, "The following actuations/isolations occurred: (Group 3) Reactor Water Cleanup system isolated, (Group 6) Stand by Gas Treatment system Trains A, B, and C started, Control Room Emergency Ventilation B started, and ventilation systems that were not removed from service. Groups 2 and 8 components were removed from service to support outage activities, subsequently, no equipment response occurred. "The effected systems were returned to their pre-event configuration. There were no safety consequences or compromises to the health and safety of the public. The event was entered into TVA's corrective action program for resolution. "The NRC Site Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-06-04
38050 | -1 | WESTERN MISSOURI MEDICAL CENTER |  |  |  |  | 2001-06-04 08:00 | 2001-06-04 12:52 | 2001-06-04 | PATIENT ADMINISTERED INCORRECT DOSE AND CHEMICAL FORM OF TECHNETIUM-99m A patient was prescribed a dose of 17 mCi of Tc-99m (MDP) for a bone scan; however, the patient actually received a dose of 5 mCi of Tc-99m (collatec). The licensee stated that a medical technician picked up the wrong syringe. The patient and attending physician have be informed by the licensee. * * * RETRACTION 1542 6/4/2001 FROM WHITCOMB TAKEN BY STRANSKY * * * After discussion with NRC Region III, the licensee has determined that this event does not constitute a medical misadministration. Notified R3DO (Clayton). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.33 |  |  |  | 0 | 2001-06-04
38049 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-06-04 09:10 | 2001-06-04 09:24 | 2001-06-04 | OFFSITE NOTIFICATION TO THE DEPARTMENT OF NATURAL RESOURCES The licensee discovered a dead sea turtle on the cleaning racks of the intake structure. The species of turtle is unknown and the licensee is calling the Department of Natural Resources for help in determining if the turtle is an endangered species. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-04
38048 | 0 | COMPUTALOG WIRELINE SERVICES |  |  |  |  | 2001-06-03 15:30 | 2001-06-03 21:41 | 2001-06-03 | DENSITY MEASURING DEVICE FELL INTO THE GULF OF MEXICO. DIVERS WILL RETRIEVE IT MONDAY MORNING. A density measuring device stripped off its wireline and fell into the Gulf of Mexico. The well is between 25 to 50 miles offshore from New Orleans. Chevron Oil owns the Well. Well # 1 in the Gulf of Mexico is located at OCSG 13982. The density measuring device contains a 17mCi cesium-137 source and the source is double encapsulated within another holder. The density measuring device is approximately 1.688 inches in diameter and 40 feet long. The device is at a depth of 123 feet of water on a hard bottom next to the well head (light ocean currents in the area). The make of the density measuring device is a Gammatron, Model "CSV", and its serial number is "V948". A special diving crew will go down in the morning to retrieve the density measuring device. The diving crew has been briefed that they will be retrieving a radioactive source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-06-03
38047 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-06-02 15:30 | 2001-06-02 18:03 | 2001-06-02 | OFFSITE NOTIFICATION TO STATE The licensee notified the state public service commission concerning an injured employee who will spend the night in the hospital. A watch stander fell off a ladder. No contamination involved. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2001-06-02
38046 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-06-02 01:55 | 2001-06-02 14:16 | 2001-06-02 | SAFETY SYSTEM ACTUATION "At 0155 on 06-02-01 the Plant Shift Superintendent (PSS) was notified of an activation of the High Voltage UF6 Release Detection System at the C-315 Tails Withdrawal Building. An Instrument Mechanic was walking down job in preparation for connecting a safety sample buggy to valve SW-53. In order to verify which instrument line was the correct one to connect to the buggy, the mechanic moved the quarter inch copper line. The mechanic reported that the line broke and he saw smoke come from the area. Personnel in the area evacuated to the Area Control Room (ACR) and the Plant Emergency Squad was notified. Subsequent to the release, UF6 Detector heads YE-10-2-6 and YE-10-2-7 alarmed in the ACR. Detector head YE-10-2-6 is a TSR required Q component. The Plant Emergency Squad mitigated the release and the area was turned over to Operations. "High volume air samples and wipe samples by Health Physics personnel indicate no widespread radiological contamination. Contamination was confined to the immediate area at the broken instrument line. Precautionary urine samples submitted by the two employees near the release indicated fluoride uptakes below plant recall limits of 5 mg/L. Analysis for uranium uptake indicated one employee's results were below detectable limits. The other employee's results indicated an uptake 7.3 µg U/L, which is above the plant recall limit of 5.0 µg U/L but below the restriction limit of 40 µg U/L. A follow-up urinalysis will be performed upon this employee upon his return to work at 1900 hours on 6-2-01. "This safety system actuation is reportable to the NRC as required by Safety Analysis Report, section 6.9, table 1 criteria J.2, Safety System actuation due to a valid signal as a 24-hour event notification, "The NRC Resident inspector has been notified of this event. "PGDP Problem Report No. ATR-01-2653; PGDP Event Report No. PAD-2001-022; Event Worksheet Responsible Division: Operations" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-06-02
38045 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-06-01 14:02 | 2001-06-01 19:53 | 2001-07-12 | INADVERTENT LOSS OF POWER TO A SAFETY BUS "At 1402 PST, with Columbia Generating Station in Mode 5, a loss of 230 KV offsite source (startup transformer) occurred. This resulted in a loss of voltage to the Div 2 safety related bus (SM-8) which was automatically reenergized by the 115 KV offsite source (backup transformer). All plant systems and components responded as expected. No core alterations were in progress. SM-8 was inoperable but energized at the time of the event due to planned outage maintenance. There was no challenge to the plant shutdown safety plan as a result of this loss of offsite power. The loss of power was a result of a lightning strike offsite on the Bonneville Power Administration (BPA) electrical grid. Restoration of the 230 KV source is pending repairs to damage on the BPA grid. This notification is being made pursuant to 10CFR50.72(b)(3)(iv)(B)(8). This is a valid actuation of an Emergency AC electrical power system." The licensee notified the NRC Resident Inspector. * * * RETRACTION 1741 FROM SHERMAN TAKEN BY STRANSKY * * * "Columbia Generating Station hereby retracts a report made to the NRC Operations Center on June 1st, 2001 at 1953 hours. Event Notification number was 38045. The report was made pursuant to 10 CFR 50.72(b)(3)(iv)(B)(8) and documented that a lightning strike resulted in a loss of a 230kV offsite power line to a safety related electrical bus (SM-8) due to a startup transformer tripping offline. At the time of the event, the plant was already shut down in Mode 5. The safety related electrical bus was automatically reenergized by the backup offsite 115 kV electrical source through the backup transformer. "It was assumed at the time of the report that a loss of offsite power was an actuation of an emergency AC power system. Upon further review, we have concluded that an automatic bus transfer of offsite power is an alternate normal power supply and not in the scope of NUREG-1022 as an actuation of an emergency AC power source. Our licensing basis documents also refer to the emergency diesel generators as the source of all emergency AC power." The NRC resident inspector will be informed of this retraction. Notified R4DO (Cain). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2001-06-01
38044 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-05-31 15:15 | 2001-06-01 13:28 | 2001-06-01 | INADVERTENT LOSS OF POWER TO THE CRITICALITY ACCIDENT ALARM SYSTEM "On Thursday, May 31, at 3:15 pm, during diagnostic maintenance activities on UPS systems, a circuit breaker was automatically opened which temporarily de-powered the criticality accident alarm system (CAAS). The maintenance activity was being performed to diagnose system problems in order to prevent inadvertent UPS-related system failures. During the event NFS safety personnel were continuously monitoring the status of the CAAS and immediately alerted management of the failure, as did the maintenance personnel performing the diagnostic procedures, and all primary operations were ordered to stop movement of SNM. At 3:35 pm power was restored and the CAAS was again functioning normally." The cause of the trip is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 1 | 2001-06-01
38043 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-04-30 23:13 | 2001-06-01 11:43 | 2001-06-01 | INVALID SPECIFIED SYSTEM ACTUATION On April 30, 2001, during a refueling outage and with the primary containment open for personnel access, an unexpected Group III Primary Containment Isolation System (PCIS, EIIS code: JM) actuation occurred. Operators were attempting to remove 24 VDC battery chargers from service (1D51 and 1D52). The section of the procedure used de-energized the whole Division I 24 VDC bus. As a result, the Offgas system radiation monitor (RM4116A) was the de-energized causing an invalid Group III PCIS isolation. This actuation is considered a complete isolation for a Group III signal. The components of the system that were in service at the time of the actuation operated as designed upon receipt of the isolation signal. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-06-01
38042 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-04-11 00:05 | 2001-05-31 17:03 | 2001-05-31 | INADVERTENT LOSS OF 'A' RPS BUS The following is taken from a faxed report: This 60-day optional report in accordance with 10CFR50.73(a)(1), is being made under the reporting requirement of 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of the Containment Isolation System. On April 11, 2001, at 0005 hours, the control room received an alarm for loss of the 'A' Reactor Protection System (RPS) bus. As a result of the loss of the 'A' RPS bus the following actuations occurred: an A1 & A2 RPS half scram, a Nuclear Steam Supply System Shutoff (NSSSS) logic A & C trip, tripping of the 'A' and 'B' Reactor Water Clean Up (RWCU) pumps due to closure of the inboard isolation valve BG-HV-F001, recirculation sampling isolation, and closure of the inboard Main Steam Line Drain valve AB-HV-F016 The 'A' RPS bus was shifted to the alternate feed at 0023 and the RPS A1 & A2, the NSSSS, and the primary containment isolation signals (PCIS) were reset. At 0036, recirculation sampling was restored. Valve, BG-HV-F001 and AB-HV-F016 were reopened at 0039 hours. The above actuations and isolations were expected as a result of the loss of the 'A' RPS bus. These actions and isolations were due to an invalid signal resulting from the inadvertent de-energization of the 'A' RPS bus. Fire Protection Operators were performing testing of the smoke detectors in the RPS motor-generator (MG) set room using a test pole. When the Fire Protection Operator in the overhead was handing the test pole to the Fire Protection Operator on the floor, the pole slipped and struck breaker switch for H1SB-1AN410 (A RPS EPA breaker), causing the breaker to open. Opening of the breaker lead to the loss of the 'A' RPS bus. After determining that no damage occurred to breaker H1SB-1AN410, the 'A' RPS was restored to the normal power source. The impact on the plant safety from this event was minimal. The isolations and equipment losses during the event caused only a minor plant transient and the equipment performed as expected. After the plant was stabilized and the cause of the loss of the 'A' RPS was identified, the half scram was reset. This event has been entered into the corrective action program. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2001-05-31
38041 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-31 13:30 | 2001-05-31 16:52 | 2001-05-31 | BULLETIN 91-01 - 24 HOUR REPORT The licensee, during a review of the plant surveillance program, discovered a surveillance that was supposed to be done every 6 months was missed the last time and is about 6 months overdue. The following is taken from a faxed report: At 1330 hrs. the Plant Shift Superintendent was notified that a required surveillance for NCSA 705_040 was not performed in the required periodicity. This surveillance is necessary to ensure that uranium bearing material is not accumulating in the piping due to either precipitating out or through bonding with oil-bearing material which then layers out in the piping. By not performing this surveillance one of the barriers for maintaining double contingency was lost for this operation thus making this a reportable event. SAFETY SIGNIFICANCE OF EVENTS: The surveillance required to perform non-destructive analysis (NDA) on piping of the 705 geometrically safe overhead storage (GSS) was not performed. However, based on the historic evidence as discussed in sections 4.3 and 4.5 of analysis performed for this system it is highly unlikely that material is accumulating in the piping and thus the safety significance of this event is low. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): Without measuring a significant amount of material could accumulate in GSS piping and result in an unsafe condition. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The parameter which was violated during this upset was maintaining the concentration of material in the GSS piping to a safe level through periodic NDA surveillance of various piping in the GSS. It should be noted that the physical integrity of the piping in question (i.e., that containing the uranium-bearing material) was maintained. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF: Based on the most recent sampling of solution contained in the GSS the amount of uranium involved is small (approximately 0.0002 grams uranium/liter) NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Did not perform the required surveillance within the allotted time period. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Isolated the GSS from other influents at 1335 hrs. Will commence NDA measurements 06/01/01. The licensee notified the NRC Resident Inspector and the local DOE representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2001-05-31
38040 | 0 | UNIVERSITY OF PITTSBURGH MED. CENT. |  |  |  |  | 1996-09-03 18:00 | 2001-05-31 11:24 | 2001-05-31 | MEDICAL MISADMINISTRATION The following is taken from a faxed report: The following event is being reported as a medical misadministration in accordance with the May 22, 2001, directive of NRC Region I representatives. At 6:00 PM on September 3,1996, a patient was implanted with six ribbons, each containing four Iridium-192 seeds. The seeds each contained 1.01 millicuries (total activity of 24.2 millicuries). The ribbons were placed in catheters implanted into the patient's right jaw and secured by crimping a metal button around the catheter. The corresponding written directive prescribed a treatment time of 47 hours. At 4:45 PM on September 5, 1996, the radiation oncologist arrived to remove the sources and determined that one ribbon was missing from the treatment site. The Radiation Safety Office (RSO) was notified. The five remaining ribbons were removed from the patient and a survey was done of the patient, the patient's room and surroundings. The missing ribbon was located on the floor in front of a laundry bin. The ribbon was secured and returned to storage. The RSO investigated this event and determined that all six ribbons were in place at 8:00 AM on September 5th when the day nurse checked the patient and documented the status of the brachytherapy implant in the patient's record. (Note: Prior to this event nurses were required to evaluate and document the status of brachytherapy implants at the beginning of each work shift.) At approximately 9:30 AM the patient complained of discomfort and experienced significant vomiting. This condition persisted through the remainder of the day. A Patient Service Technician (PST) reported that she changed the patient's gown and bed linens at approximately 2:30 PM. Staff physicians, nurses and residents evaluated the patient throughout that day as documented in the patient's record. However, such documentation does not include an indication or the status of the implant. The licensee concluded that the brachytherapy ribbon likely became dislodged from the treatment site due to the patient's vomiting and/or self-intervention sometime between 9:30 AM and 2:30 PM on September 5th. The ribbon was apparently entangled in the patient's bed linens until the linens were changed by the PST at 2:30 PM; whereupon the ribbon dropped from the soiled linens when they were placed in the linen storage bin. It is also possible that the ribbon may have become dislodged at the time (2:30 PM) the patient's gown was being changed. Assuming the worst case that the brachytherapy ribbon became dislodged at 9:30 AM, the deviation from the total prescribed treatment dose due to the single ribbon missing for 7.5 hours is 2.7 percent, The possible localized radiation dose outside the treatment Site was also evaluated. If it is assumed that with patient movement the average location of the ribbon would be 10 cm from the patient's body. then the closest area of the body exposed would receive a radiation dose of less than one rad. This radiation dose is no more than the lower extremities would receive from the prescribed brachytherapy implant procedure and substantially less than that which would be received by the upper torso and head in areas near the implant site. If the ribbon became dislodged when the patient's gown was being changed, there would be no significant radiation dose to any portion of the patient's body since the source had been removed from the bed at that time. Based on its review of the circumstances surrounding this event and the possible associated radiation exposures, the licensee concluded that the event did not constitute a misadministration or recordable event. However, in consideration of the possible ramifications of a future such event, the licensee implemented a policy requiring that documented checks of the implant site be performed at four hour intervals by nursing personnel. (Note: The NRC's regulations and guidance are silent on the issue of frequency of monitoring implants.) The Radiation Oncologist, did not feel that this event would impact on the well being of the patient. The patient's referring physician was verbally notified of this event at the time of its occurrence. Full details of the event were documented and placed in the incident file to be reviewed during the next NRC inspection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0 | 2001-05-31
38039 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-30 11:00 | 2001-05-31 10:17 | 2001-05-31 | FIRE PROOF COVER OVER A PROCESS OPENING COULD NOT PERFORM ITS INTENDED FUNCTION. NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 1400, 05/30/01 the Plant Shift Superintendent (PSS) was notified that the Zetex material used as a fire proof cover on the # 3 low speed purge and evacuation pump has deteriorated to the point of failure such that it could not perform its intended function. The material was being used according to CP2-CO-CN2030, as a fire proof cover over a process opening. The material has become brittle and failed to the point of leaving openings to the process system. NCSA GEN-10, Removal and Handling of Contaminated Equipment from the Cascade at PGDP, requires fire proof covers to be installed on cascade system openings to prevent the introduction of moderation from a sprinkler activation, lube oil leak, or RCW leak. Double contingency for this scenario is established by implementing two controls on moderation. One leg of double contingency is based on the fire proof cover preventing a moderator release from entering the open process system. Since the fire proof cover deteriorated to the point of leaving openings to the process system, the ability to prevent introduction of moderator was lost. This control was violated and double contingency was not maintained. SAFETY SIGNIFICANCE OF EVENTS: A material credited to perform a criticality safety related function was not able to perform its function. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: In order for criticality to be possible, greater than 10 kg of a moderator would have to enter the open process system and interact with a uranium deposit greater than the minimum critical mass in a geometry favorable for a criticality. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Maximum assay of 1.08 wt.% U235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on the unlikelihood of a moderator release (Sprinkler, RCW, oil) into the open process system during the time the system is open. Since there was no moderator release into the system, this leg of double contingency was maintained. The second leg of double contingency is based on the fire proof cover preventing a moderator release from entering the open process system. Since the fire proof cover deteriorated to the point of leaving openings in the process system, the ability to prevent introduction of moderator was lost. The control was violated and double contingency was not maintained. Since double contingency is based on two controls on moderation, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The degraded Zetex fire proof material was replaced with an approved AQ-NCS aluminum cover. Other cascade openings using Zetex material are being inspected for signs of degradation and will be replaced as necessary. The use of Zetex material as a fire proof cover will be re-evaluated. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2001-05-31
38038 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-05-11 | 2001-05-30 18:07 | 2001-05-30 | A 47.5 CURIE IR-192 SOURCE WOULD NOT RETRACT INTO THE CAMERA DUE TO RESISTANCE IN THE GUIDE TUBE. Radiographers were performing field site radiography at a refinery and a radiograph was required at about the 80 foot level on the refinery structure. The collimator was firmly taped to a wooden pole attached to the structure. The AEA Technologies, Model 660B camera and controls were placed on the next level down. Two guide tubes were connected end to end to connect camera and collimator. The area was secured and the shot timed. At the end of the exposure the radiographer attempted to retract the AEA Tech. model 424-9 source and discovered that it would only come back part way. After several unsuccessful attempts cranking the source back and forth, the radiographer left the source in the fully extended position (in the collimator) and called the RSO for assistance. The RSO made sure the site was roped off and under observation and then called AEA Technology to send a retrieval expert. The state Division of Radiation Protection was also notified and staff sent to observe the recovery operation. The retrieval was performed by using a crane to hook onto the camera and, once the collimator was cut free from the structure, to lay out the camera and the dangling guide tube and collimator behind a concrete barrier. The control cable was also stretched out straight using the crane. Once in place and shielded, the control cable was used to easily retract the source. The manufacturer has taken the device and guide tubes for analysis. However, the immediate supposition is either dirt in the guide tube or too tight of a turn in the guide tube may have created enough friction to prevent the source from retracting smoothly even though it cranked out without difficulty. The highest exposures received due to this event were to the two individuals involved in cutting the collimator loose from the structure. The crane operator and a radiographer each received 4 millirem while using a 10 foot pole pruner to cut the wooden stick holding the collimator. One other individual received 1 millirem exposure during this event. What is the notification or reporting criteria involved? Equipment malfunction. Activity and Isotope(s) involved: 47.5 Ci Ir-192. Overexposure? Two individuals received 4 millirem whole body and one individual received 1 millirem whole body exposures. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2001-05-30
38037 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-05-30 13:08 | 2001-05-30 17:20 | 2001-07-20 | REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM WAS DECLARED INOPERABLE. The RCIC system was inoperable and available for planned maintenance and surveillance testing. During the planned surveillance testing, the mechanical overspeed mechanism for the RCIC turbine was discovered to be tripped with no overspeed trip testing having been performed. The overspeed trip mechanism may be degraded thereby constituting a condition that could have prevented the system from performing its function. RCIC is currently in standby and inoperable but available. Troubleshooting is in progress to determine the cause of the trip. This report may be retracted if the cause of the trip is determined to not affect the operability of the system. The NRC resident inspector was notified. ***** RETRACTION FROM THOMAS SCWALECK TO LEIGH TROCINE AT 1537 ON 07/20/01 ***** The following text is a portion of a facsimile received from the licensee: "On 5/30/01, during Reactor Core Isolation Cooling (RCIC) surveillance testing, the overspeed trip mechanism was discovered tripped with no overspeed testing having been performed. The overspeed trip mechanism was discovered tripped after a section of the surveillance testing that closed the trip/throttle valve and then cycled the trip solenoid several times. Nine Mile Point determined that, because of degraded engagement between the trip tappet nut and the head lever, the overspeed mechanism was susceptible to tripping during the cycling of the trip solenoid with the throttle valve tripped. Additionally, Nine Mile Point concluded that with the throttle valve latched open and RCIC aligned for operation, the overspeed trip mechanism would not have been susceptible to tripping. Therefore, the conditions that resulted in the tripping of the RCIC overspeed trip mechanism during the surveillance would not have prevented RCIC from performing its function. Based on the above, we are retracting the 50.72(b)(3)(v)(D) notification made on 5/30/01." The licensee notified the NRC resident inspector. The NRC operations officer notified the R1DO (Cook). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2001-05-30
38036 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-05-30 09:20 | 2001-05-30 12:51 | 2001-05-30 | On 4/27/01 Syncor reportedly shipped 68 I-125 bracytherapy seeds each containing 250 microcuries, to a facility in Atlanta, GA. The facility reported receiving 66 seeds. An investigation was unable to determine how many seeds were actually shipped. The discrepancy is believed due to a miscount at the time of shipment from Syncor. They are still investigating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2001-05-30
38035 | 0 | BOWSER-MORNER INC |  |  |  |  | 2001-05-27 09:30 | 2001-05-29 10:30 | 2002-04-22 | TROXLER GAUGE STOLEN FROM COMPANY TRUCK AT RESIDENCE Sometime between 0200-0930 hours on 5/27 a company truck was broken into removing a Troxler gauge and it's case. The gauge was properly stowed and it's case attached to the truck bed using a chain and lock. The truck was parked overnight at the residence of the employee at 402 Lochmoor Drive in Temperance, MI. The stolen Troxler is a model 3401B, S/N 13442, whose last measured activity on 4/30/01 was 5.6 mCi Cs-137 and 39 mCi Am-241/Be. The Monroe County Sheriffs Department in Temperance, MI and Ohio Department of Health were both notified. The licensee plans on issuing a press release. ****UPDATE ON 04/22/02 AT 1647 ET BY ALLEN TAKEN BY MACKINNON**** The above mentioned gauge was recovered this morning by the City of Bryan Local Emergency Management Agency. The gauge was found this morning in a ditch along side a highway still in its yellow case by some children. The source handle of the gauge was still locked and the only thing wrong was that the lock to the case had been broken off. The children that had found the gauge in its case called 911 and it was recovered by local law enforcement agency and given to the City of Bryan local Emergency Management Agency. The licensee was notified and picked up the gauge this morning. The gauge was leak tested and was found to be in perfect condition. R3DO (Jacobson) & NMSS EO (Wayne Hodges) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | OH | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2001-05-29
38034 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2001-05-27 06:18 | 2001-05-27 08:40 | 2001-05-27 | AUTOMATIC SCRAM FOLLOWING MAIN TURBINE TRIP DURING SURVEILLANCE TESTING "Unit 2 was operating at 80% Reactor Power, 937 Mwe. LOS-RP-M5, Turbine Control Valve Surveillance was in progress. An Automatic Main Turbine Trip and Reactor Scram occurred at 0618. Initial investigation indicates the cause of the Main Turbine Trip was High Vibration and Electro Hydraulic Controls (EHC) Master Turbine Trip. "All systems operated as designed, there were no ECCS actuations. The lowest Reactor Water Level was minus 10 inches and recovered to the normal band. Reactor Pressure responded normally. No Safety Relief Valves Actuated. All Control Rods fully inserted. "2A and 2C Circulating Water Pumps tripped during the Electrical Bus transfer following the Main Turbine Trip. This is suspected to be caused by electrical perturbation on the system but will be further investigated." The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
38033 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-05-24 20:15 | 2001-05-25 18:36 | 2001-05-25 | 24-HOUR REPORT MADE IN ACCORDANCE WITH FACILITY OPERATING LICENSE "On 5/24/01 at 2015 hrs, Nine Mile Point Unit 2 experienced a sudden failure on the control circuitry of one of two Reactor Recirculation System flow control valves. The failure mechanism of the 'B' flow control valve produced reactor core flow changes in both the increase and decrease directions which had a resultant effect of raising and lowering reactor power. At the time of the failure, Nine Mile Point Unit 2 was operating at 100% power. The core flow changes occurred within a ninety second period and changed neutron flux (APRM) by approximately 30 to 40%. Plant conditions were stabilized by hydraulically locking the malfunctioning flow control valve in a stable position. Reactor Power is now 87% of rated. No Technical Specification Limiting Condition for Operation (LCO) violations are known to have occurred. "This report is being made as required by the Nine Mile Point Unit 2 Facility Operating License #NPF-69 section 2.F. During this event, Reactor Power may have nominally exceeded 102% of rated for several seconds. As such, this event is required to be reported to the NRC Operations Center within 24 hrs as a violation of License section 2.C(1) Maximum Power Level. Event analysis is continuing and may result in retraction of this notification at a later date." The licensee will inform the NRC resident inspector of this notification. | 0 | 87 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
38032 | 0 | UNIVERSITY OF MED. AND DENT. OF NJ |  |  |  |  | 2001-05-23 16:30 | 2001-05-25 16:21 | 2001-05-25 | MISSING IR-192 SEEDS On 5/23/01, six ribbons of Ir-192 seeds were implanted into a patient as part of a treatment. When the ribbons were removed from the patient at approximately 1000 on 5/25/01, only five of the six ribbons were recovered. The patient stated that one of the ribbons had come out approximately one hour after implantation and he had discarded it in the trash; however, the doctor had not observed any disturbance to the implantation site during an examination conducted on 5/24/01. The missing ribbon contains nine seeds; each seed contains 0.49 mg Ra equivalent activity. The licensee has conducted an exhaustive search of the facility but has been unable to locate the missing seeds. In addition, interviews were conducted with housekeeping personnel. The licensee has contacted the NRC Region I office regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0
38031 | 0 | TRISTATE INSPECTION AND CONSULTANTS |  |  |  |  | 2001-05-24 21:10 | 2001-05-25 10:15 | 2001-05-25 | SOURCE HANG-UP AT A TRISTATE INSPECTION AND CONSULTANTS TEMPORARY JOB SITE IN HOMER CITY, PENNSYLVANIA The licensee reported that there was a source hang-up at a temporary job site in Homer City, Pennsylvania. The radiography camera involved was an Amersham-660B which contained a 52-curie iridium-192 source. When the source hang-up occurred, the crew involved (two radiographers) secured the area and notified an AEA Technologies Retrieval Team. Prior to the Retrieval Team's arrival, the Tristate crew (with assistance from other workers) was able to successfully shield the guide tube, straighten it out, and retrieve the source to its shielded position. As a result, the AEA Technologies Retrieval Team was not required. A pocket dosimeter for one of the original two crew members when off scale at some point during the process, but it was also reported that the radiographer had dropped it two exposures prior to this one. He then noticed that the dose had increased by 10 millirem, but it remained on scale. It was later re-zeroed, and it was still approximately 10 millirem high. The second radiographer's total dose was 85 millirem. The licensee plans to send the dosimetry out for analysis today. The licensee also plans to return the camera to Amersham for possible repairs. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0
38030 | 0 | CA RADIATION CONTROL PRGM |  |  |  |  | 2001-04-24 | 2001-05-24 23:05 | 2001-05-29 | AGREEMENT STATE REPORT On 4/24/2001, an irradiator facility experienced a loss of electrical power to a programmable logic controller (PLC) which resulted in the inability to automatically lower the source racks. The source racks were manually lowered to a safe condition upon discovery of the failure. The following information was provided by the licensee to the California Radiation Control Program on 5/15/2001: "Description of Events: "The first indication that there was a problem came at 9:00 p.m. 4/24/01, when the in-line water monitor signaled a failure. The Shift Leader took appropriate action per the Emergency Procedures and determined that there was no radiation present in the water system. He notified the QA Technician, who had performed a calibration of the monitor that afternoon. "After reviewing the procedure followed for calibration routine and determining that no problems occurred with the calibration that would trip the alarm, the QA Technician, notified the facility Radiation Protection Office (RPO). She determined that this was a false alarm, probably caused by air bubbles in the system, as has previously occurred with the water monitor. [... Permission was given] to allow the system to continue running with the water alarm disarmed until more investigation could be performed in the morning. "Starting at about 7:00 a.m., additional water counts, using the monitor, were taken and resulted in normal background readings. Since the routine counts showed expected background levels and the alarm did not activate again, the concluded that a pocket of water bubbles from a filter change had worked its way through the system and caused spurious readings on the monitor, which had occurred on previous occasions. All of the events to this point were consistent with this determination. "At 8:20 am., the Operator notified the RPO that the in-line alarm was sounding again. On reviewing the PLC control panel, she noted that none of the indicators on the panel were lit, as they should have been, even though the computer monitor (PLC user interface) was operating. In concert with the Plant Manager, they determined that the audible alarm that the Operator heard was not the in-line monitor, but was an alarm indicating that the PLC was off-line. "Further investigation revealed that the system conveyor had stopped moving (i.e., product was stationary within the cell), but that the source racks bad not automatically returned to the shielded position, as they should have, the source racks were manually lowered from the roof by 8:40 a.m. During this time, the door interlock continued to function properly, prohibiting access to the cell through the personnel access door. "In determining the probable cause of the event, the first evaluation was that the power supply had malfunctioned. However, upon further investigation, it was determined that the most probable cause was an electrical short in the system. After extensive trouble-shooting and investigation, the electrical short was finally located in the line going to one of the emergency pull cords in the cell. The cable had actually melted at the point of the failure. "That part of the systems was rewired and the system restarted at approximately 4:00 p.m. The safety system was checked for proper operation and routine processing resumed at 4:45 p.m. "Evaluation of Event and Root Cause: "Upon Engineering review of the electrical drawings, it was determined that a short circuit on the pull cords or other devices could have tripped one of the circuit breakers, power from which feeds the PLC and other modules in the PLC rack. The audible alarm was the PLC Off Line Sonalert, which, as intended, served as a warning the PLC was not operating. With the PLC off, there was no power control to lower the source racks. In normal circumstances of power failure, the uninterruptible power supply (UPS) provides adequate emergency power to lower the source racks by releasing the hoist brakes in a pulsed mode. However, with the PLC not operating, this power was not supplied to the brakes, which then had to be released manually. "The water monitor alarm activation was probably caused by shorting line voltage to the grounding circuit. This momentary surge in current, particularly on the ground path, could cause an erroneous indication at the monitor. Other facilities have had spurious water monitor alarms resulting from ground fault conditions. "Corrective Actions and Additional Considerations: "Corrective actions to the event are: "1. The circuit will be modified to ensure the PLC does not lose power if a device or device wiring causes a short circuit. "2. Additional training will be provided to operators to be more cognizant of the system response to a PLC off-line fault. While the PLC off-line alarm is a local alarm, meaning that it sounds at the control console and does not active general alarms throughout the warehouse, all system operations are stopped, including overhead conveyors and the 4-shelf elevator (i.e., device that shifts totes among positions in the carrier). The absence of movement in these systems should have alerted the operator to a systemic failure of the controls. In this instance, the tune period between the equipment failure and initial resolution (manually lowering the source racks) was only a few minutes. Because the door interlock continues to function under these circumstances, the situation did not pose a radiation safety hazard to the operator or other personnel. Although, operator training currently includes instructions for determining console power status and the proper procedure for lowering the source racks under circumstances such as occurred here, the training will be reinforced and repeated "3. To avoid further problems with the in-line water monitor alarm, an evaluation is being conducted to determine whether the water monitor can be connected to an isolated-ground receptacle and circuit. This would have the effect of making the monitor less affected by stray currents, and other sources of 'noise' on the power line." * * * UPDATE 0945EDT ON 5/29/01 FROM CA RAD CONTROL PRGM TO S. SANDIN * * * California Radiation Control Prgm update to identify NMED Report Number XCA52 for this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
38029 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-05-24 18:09 | 2001-05-24 21:50 | 2001-12-10 | HPCI DECLARED INOPERABLE "During a reactor startup following a refueling outage, HPCI was declared inoperable and is reportable under 50.72(b)(3)(v)(D) and 50.72(b)(3)(vi) as a single failure. "Upon completion of HPCI system operability testing, it was discovered that the HPCI system flow controller indicated approximately 500 GPM verses an expected 0 GPM. Since the plant is in MODE 2 and reactor pressure is greater than 150 PSIG, HPCI was declared inoperable and a 14-day LCO was entered per TS 3.5.1, condition F. "The preliminary investigation results are that air in the HPCI system flow transmitter sensing lines is causing the erroneous flow indication. Troubleshooting efforts are in progress." The NRC resident inspector has been informed of this event by the licensee. ***** RETRACTION FROM JOHN KARRICK TO LEIGH TROCINE AT 1536 EDT ON 12/10/01 ***** The following text is a portion of a facsimile received from the licensee: "This is a retraction of event number 38029 from May 24, 2001. The initial report involved an erroneous reading on the flow-indicating controller (FIC-2309) for the HPCI system. At the time of the discovery, the consequence of FIC-2309 reading high was believed to be a non-conservative speed demand signal to the HPCI turbine such that the actual HPCI injection flow would fall short of that required (assuming an auto start with no operator action). As a result, HPCI was declared inoperable and a report was made. A calculation has since concluded that actual HPCI operability would not have been lost given the as-found condition. Also, the quarterly surveillance test to prove HPCI operability had just been successfully completed. During the time HPCI was considered inoperable, it remained available for use (as documented in Operator logs). Therefore, there was no actual loss of HPCI as a single train safety system and there was no event or condition that could have prevented safety function fulfillment. This event is being retracted. A formal cancellation letter to withdraw the LER (331/2001-002) is also being mailed." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Anne Marie Stone). | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
38028 | 0 | WA DIVISION OF RADIATION CONTROL |  |  |  |  | 2001-05-17 | 2001-05-23 18:22 | 2001-05-24 | AGREEMENT STATE REPORT "ABSTRACT: A 0.326-millicurie I-125 seed was damaged and leakage occurred. Five Medi-Physics OncoSeed model 6711 brachytherapy seeds were loaded in a hollow needle for insertion into a prostate implant patient. During the insertion attempt, the needle tip struck bone. The radiation oncologist withdrew the needle and determined there was a slight bend in the needle. In attempting to straighten the needle, the radiation oncologist broke the needle into two pieces. The most distal seed was crimped and broken into two pieces as well. All items potentially in contact with the broken seed were immediately isolated. Contamination on the exterior of the broken seed was 0.012 microcuries. The patient was not contaminated. The broken seed will be held for decay. Implant personnel were instructed not to bend loaded needles to prevent this from recurring. "What is the notification or reporting criteria involved? WAC 246-221-265 Leaking source "Activity and Isotope(s) involved: 0.326 millicuries of I-125" HOO NOTE: Event entered late - updated for dispatch in 5/25/01 events package. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
38027 | 0 | CONVAL INC |  |  |  |  | 2001-05-23 | 2001-05-23 17:03 | 2001-05-23 | NONCOMPLIANCE INVOLVING FLOW COEFFICIENT VALUES OF 366 VALVES OF TWO BODY STYLES SUPPLIED OVER THE COURSE OF 15 YEARS TO TWO NUCLEAR POWER PLANTS IN THE US The noncompliance involves flow coefficient values (Cv) of 366 valves of' two body styles supplied over the course of 15 years to two nuclear power plants in the United States. The breakdown is as follows: GPU, Oyster Creek; 122 Qty.- 1/2" Angle Body Ball Check Valves used in Charging Water Riser Isolation Niagara Mohawk, Nine Mile Point Unit 1; 114 Qty.- 1/2" Angle Pattern Ball Check Valves used in Charging Water Riser Isolation 130 Qty.- 3/4" Tee Pattern Ball Check Valves used in SCRAM Discharge Riser Isolation Information was developed that led to an engineering investigation and the May 21, 2001 report by Conval's Quality Assurance Manager, Howard Smith II of the potential safety related noncompliance deviation. The procurement document specifications for Niagara Mohawk, Nine Mile Point Unit 1 defined a Cv requirement of 3.5 for both the Angle and Tee Pattern Ball Check Valves. The procurement document specifications for GPU, Oyster Creek specified a Cv of 6 for the Angle Pattern Ball Check Valves. Preliminary laboratory test reports generated during Conval's recent engineering investigation revealed actual Cv values of both valve styles to be below 1.5, significantly lower than those required by the procurement documents. While there are no indications that the valves will mechanically malfunction, the fluid flow rates permitted in the forward direction will be below those anticipated in the procurement document specifications and, therefore, may constitute a safety related issue according to the intended use of the valves. There are no nonconforming parts affecting the operation of the valves. The lower Cv values are a consequence of the internal geometry of these Conval valve designs. If requested, Conval's Engineering Manager, David Boyden, will propose a retrofit of parts which, upon user acceptance, could be implemented within 4 weeks following user approval. The changes would significantly increase the flow capacity of the affected valves. The two (2) nuclear plants affected have been verbally notified of this potential safety related noncompliance deviation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21 |  |  |  | 0
38026 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2001-05-23 14:45 | 2001-05-23 16:19 | 2001-05-31 | DISCOVERY OF CRIMINAL ACT INVOLVING INDIVIDUAL GRANTED ACCESS TO THE SITE. COMPENSATORY MEASURES NOT FULLY IMPLEMENTED THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED CONTACT NRC HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL INFORMATION * * * RETRACTED AT 1600 EDT ON 5/31/01 BY ERICK MATZKE TO FANGIE JONES * * * Further investigation of the issue determined that the event notification was not reportable and retracts the notification of event #38026. The licensee notified the NRC Resident Inspector. R4DO (Dale Powers) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0
38025 | 0 | US ARMY |  |  |  |  | 2001-05-21 | 2001-05-23 14:05 | 2001-05-23 | LOST CHEMICAL AGENT DETECTOR(CAD) The US Army in Aberdeen, Md. Reported that the 7th Chemical Co. 83rd Chemical Battalion at Ft Polk, La. lost a Chemical Agent Detector in the training area during a training exercise. The CAD contained 300 microcuries of Am-241. A 100% inventory and complete search was conducted, but it was not recovered. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
38024 | -1 | TRISTATE INSPECTION AND CONSULTANTS |  |  |  |  | 2001-05-22 11:30 | 2001-05-23 07:45 | 2001-05-23 | APPEARANCE THAT A TRISTATE INSPECTION AND CONSULTANTS RADIOGRAPHER EXCEEDED THE 5-REM ANNUAL LIMIT The licensee is reporting this event due to the appearance that a radiographer exceeded the 5-rem limit for the year. The individual's dose (year to date) is 5,050 millirem. The licensee's initial investigation indicates that the individual did not actually receive all of the indicated dose. Apparently, the individual routinely put his badge in his tool box at the end of the day, and the second shift crew used the individual's tool box without realizing that the badge was inside. Therefore, the badge received additional exposure during the course of the second shift. Apparently, the tool box was located in a vehicle which was parked inside the boundary ropes in a refinery lay-down area where the crew shoots weld coupons. It was reported that the second shift crew did not routinely use the individual's tool box, and there were no unusual doses with the individual's partner or with any of the other radiographers. The radiographer whose badge is in question is being restricted from radiography work until the licensee's investigation has been completed. The licensee is waiting on letters from the radiographer whose badge is in question and from the radiographer who used the tool box containing the badge during the second shift. The licensee plans to submit a written report within 30 days. (Call the NRC operations officer for a licensee contact telephone number.) * * * UPDATE ON 5/23/01 @ 1426 BY DURKIN TO GOULD * * * RETRACTION The licensee is retracting this event since the event occurred in the State of Ohio, an agreement state. They will report it to that State. Notified Reg 3 RDO(Burgess) and NMSS EO(Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2202(b)(1) |  |  |  | 0
38023 | 0 | OREGON STATE UNIVERSITY |  |  |  | 1000 KW TRIGA MARK II | 2001-05-22 16:35 | 2001-05-22 20:17 | 2001-05-22 | LOST/UNACCOUNTED FOR KEYS COMPENSATORY MEASURES WERE PUT INTO PLACE BUT WERE INADVERTENTLY REMOVED FOR A 1-HOUR PERIOD. (CONTACT THE NRC OPERATIONS OFFICER FOR ADDITIONAL DETAILS.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | OR | NPR |  | 73.71(b)(1) |  |  |  | 0
38022 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-05-22 18:35 | 2001-05-22 19:24 | 2001-05-22 | SUSPECTED ARSON COMPENSATORY MEASURES WERE TAKEN UPON DISCOVERY. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. (CONTACT THE NRC OPERATIONS OFFICER FOR ADDITIONAL INFORMATION.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0
38021 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-05-22 06:16 | 2001-05-22 08:42 | 2001-05-22 | TURBINE TRIP/REACTOR TRIP. ALL SYSTEMS OPERATED AS EXPECTED. This notification is being made to report that Salem Unit 1 has experienced an automatic reactor trip. All rods fully inserted into the core. The reactor trip was caused by a main turbine trip. The cause of the main turbine trip is under investigation. Post trip, main feedwater to steam generators was isolated due to the feedwater air lock, which is expected on a reactor trip. The auxiliary feedwater system automatically started on low steam generator water levels, and this was also expected on a reactor trip. Auxiliary feedwater pumps "21," "22," and "23" all automatically started and fed the steam generators. The turbine-driven auxiliary feedwater pump, "23," has been shut down by procedure since the "21" and "22" motor-driven auxiliary feedwater pumps were maintaining adequate feedwater flow. Main feedwater restoration is in progress. Salem Unit 1 is currently in Mode 3 (Hot Standby). Reactor coolant temperature is currently 547 degrees F, and plant pressure is 2235 psi. All emergency core cooling systems and all engineered safety feature systems are available. There are no shutdown technical specification limiting conditions for operation (LCO) in effect. There is one non-shutdown technical specification LCO in effect due to the power distribution monitoring system being inoperable. The system is functional, but post isolation testing will not be completed for some time. The only major secondary equipment unavailable is number one station air compressor, which is out of service for oil filter replacement. It is expected to be restored to service today. The emergency diesel generators are fully operable if needed, and the electrical grid is stable. The licensee plans to notify the Lower Alloways Creek Township of this event. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
38020 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2001-05-21 07:59 | 2001-05-21 20:04 | 2001-05-23 | FAILURE OF PROGRAMMABLE LOGIC CONTROLLER(PLC) CAUSED LOSS OF ACTIVE ENGINEERED CONTROLS ON CONVERSION LINE 4 24 HOUR 91-01 BULLETIN At approximately 0759 the decanter tripped off line on conversion line 4. Subsequently line 4 was shutdown at 0805. An error in the display program was initially suspected. With conversion line 4 shut down, instrument technicians were called. The technicians attempted to correct the problem with the display program to no avail. An instrumentation and controls (I/C) engineer was called and tracked the problem to the line 4 PLC. Since it was determined that the PLC processor for line 4 had faulted, the processor was reset and tested. The test was satisfactory. Line 4 was restarted at approximately 1000. At approximately 1030 line 4 was shut down due to a plugged duplex valve at the inlet of the calciner. During this shutdown, a process engineer was informed about the earlier events. The process engineer became concerned about the status of the safety significant controls on line 4 and contacted a nuclear criticality safety (NCS) engineer at approximately 1130. The NCS engineer was present in the control room at approximately 1140. A time-line of events was reconstructed. The NCS engineer reviewed the sequence of events with the I/C engineer. It was determined that an output fault in an I/O card caused the processor to go into fault mode but all outputs did not go to their correct (OFF) state. The NCS engineer determined that in the time period from 0759 until line 4 was secured at approximately 0805, the active engineered safety significant controls (SSCs) on line 4 were unavailable, and less than double contingency protection existed in the vaporization system during that time period. The SSCs are considered to have been in place for the 1000 startup and remained in place until the shutdown at 1030, although the cause of the initial failure had not been determined. Conversion operators on line 4 were instructed by the NCS engineer to not restart line 4 until the cause of the PLC failure was determined and corrected. Line 4 remains shutdown pending further investigation. Justification for Continuing Operations on Lines 1, 2, 3 and 5: Line 4 utilizes a unique Numalogic PLC system while Lines 1, 2, 3, and 5 utilize a different programmable logic system. There is no reason to believe the Numalogic error is possible on the other lines. The manufacturer of the other programmable logic system (utilized on Lines 1,2,3 and 5) was contacted and stated that their cards cannot fail into any state other than all OFF. Conversion Lines 1, 2, 3 and 5 remain in operation. Double Contingency Protection Double contingency protection for the vaporizer is based upon control of mass (prevent/detect a UF6 leak) and geometry (prevent/detect accumulation of moderator in a non-favorable configuration in the bottom of the vaporizer). Double contingency protection on the cylinder (in vaporizer) is based upon moderation control (prevent back-flow of moderator from the hydrolysis column into the cylinder). It was determined that less than double contingency protection remain for these systems and greater than a safe mass was involved. In accordance with Westinghouse Operating License (SNM-1107), paragraph 37.3 (c.5), this event meets the criteria for a 24 hour notification because it constitutes a "nuclear criticality safety incident, in an analyzed system, for which less than previously documented double contingency protection remains . . and: greater than a safe mass is involved, but a sufficient number of the controls that were lost are restored within four (4) hours such that double contingency protection is restored." As Found Condition See "Reason for Notification" above. Summary of Activity An unknown PLC failure led to the shutdown of conversion line 4. It was determined that less than double contingency protection existed on the line 4 from 0759 to 0805. Therefore, the NCS engineer directed that line 4 could not be restarted until the cause of the failure was determined and corrected. Conclusions Loss of double contingency protection occurred. At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. This notification is the result of equipment failure, not a deficient NCS analysis. ***** UPDATE RECEIVED AT 1120 ON 05/23/01 FROM BILL NEWMYER TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "Westinghouse has proceeded with investigation of the cause of the Numalogic PLC failure on Conversion Line 4. This investigation has discovered that the design of the Line 4 - Numalogic 700 PLC may fault to an undesirable state. A service bulletin update for the Numalogic PLC describes this condition." "A modification to the PLC (described in the manufacturer's bulletin) is necessary to correct this condition. This modification was completed on the PLC. The PLC was subsequently tested by faulting the PLC, and the correct output condition was achieved." "Further testing of the control logic was performed to ensure that the output from the PLC, when faulted, will produce the correct valve responses for Conversion Line 4. This functional test revealed that even though the PLC faulted to the correct output values, the valves did not respond correctly." "Discovery of the problem with Conversion Line 4 prompted investigation to determine if the other Conversion Lines (1, 2, 3, and 5) would experience a similar error (i.e., the PLC faults to the correct output but the valves fail to respond correctly). Testing of Conversion Line 5 (which uses a different PLC logic system) revealed the same deficiency." "Based on this information, Conversion Lines 1, 2, 3, and 5 have been shutdown pending further evaluation of the correct system response assuming a PLC fault condition. Modifications will be made to each Conversion Line to correct the PLC system response prior to restarting each Conversion line." The licensee notified onsite NRC headquarters inspectors. The NRC operations officer notified the R2DO (Bernhard) and NMSS EO (Hickey and Broaddus). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0
38019 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2001-05-21 15:05 | 2001-05-21 16:43 | 2001-05-21 | UNUSUAL EVENT - BOMB THREAT IMMEDIATE COMPENSATORY MEASURES WERE TAKEN UPON DISCOVERY. AN UNUSUAL EVENT WAS DECLARED AT 1520 CDT. CONTACT HOO FOR FURTHER INFORMATION. * * * UPDATE ON 5/21/01 @ 2005 BY HOBBS TO GOULD * * * The NOUE was terminated at 2000 EDT based on a completed search which turned up no abnormalities. Notified Reg 3 RDO(Burgess), NRR EO(Zwolinski), and FEMA(Canupp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | UNUSUAL EVENT | 3 | MO | NPR |  | 73.71(b)(1) |  |  |  | 0
38018 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2001-05-18 16:30 | 2001-05-21 12:30 | 2001-05-21 | This licensee is authorized for the receipt, possession, processing, storage, handling and shipment of radioactive waste resins. During routine operations at the facility, a spill of approximately four cubic feet occurred from one of the process vessels. The vessel was shut down and the facility evacuated. It is estimated that 29 millicuries of activation and mixed fission products were released during the spill. The material was released into a controlled area. There were no environmental releases. Negative pressure was maintained during the event. The HVAC system was shut down after the release as was the thermal system to the process vessel. During the investigation, five individuals were slightly contaminated as confirmed by nasal swipes. Invivo counting of these individuals will be conducted on Wednesday, May 23 at Oak Ridge National Laboratory. Temperatures in the area have now decreased enough for personnel to enter and make a physical evaluation. Video cameras recorded the event and it is believed at this time that the vessel was overpressurized. A complete investigation and root cause analysis will be performed by the licensee to determine the cause of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
38017 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-05-21 01:50 | 2001-05-21 12:26 | 2001-05-21 | FAILURE OF THE EARLY WARNING SYSTEM SIRENS The operating system for the early warning system sirens failed. This will prevent activation of the early warning sirens. The sirens failed at 0150 on 5/21/01. The failure is currently being investigated. The NRC Resident Inspector will be notified. * * * UPDATE ON 5/21/01 @ 1246 BY BAHNER TO GOULD * * * The system was restored at 0940. The NRC Resident Inspector was notified. The Reg 4 RDO(Shaffer) was notified | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
38016 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-20 03:56 | 2001-05-20 10:47 | 2001-05-23 | VALID HIGH LEVEL DRAIN SECONDARY ALARM At 0356 on 05/20/01, the PSS office was notified that a High Level Drain Secondary alarm was received on the C-360 position 1 (autoclave 1) Autoclave Water Inventory Control System (WICS). The WICS system is required to be operable while heating in mode 5 (heat mode) according to TSR 2.2.4.2. The autoclave was checked according to the alarm response procedure and the alarm was determined to be due to a valid signal. The autoclave was removed from service and the Water Inventory Control System was declared inoperable by the Plant Shift Superintendent. Autoclave # 1 was removed from service and is inoperable. The NRC Resident Inspector was notified of this event by the certificate holder. * * * UPDATE ON 5/23/01 @ 1709 BY BEASLEY TO GOULD * * * RETRACTION THIS EVENT HAS BEEN RETRACTED. Following the WICS activation, System Engineering lead a troubleshooting effort by Instrument and Control Maintenance and Operations personnel. This included inspection of the drain, testing of the WICS system using the approved autoclave functional test procedure, and a review of the recorded system data. This effort concluded that the actuation was initiated by an invalid signal from the secondary condensate probe. Testing indicated that the sensitivity band of the secondary probe had shifted in the conservative direction and alarmed without the presence of water. Based on the conclusion that the actuation was caused by an invalid signal and not a condition the WICS is designed to protect against, the reporting criteria is not met. Therefore the subject notification is being retracted. The NRC Resident Inspector was notified. Reg 3 RDO(Burgess) and NMSS EO(Essig) were informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
38015 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-05-20 00:56 | 2001-05-20 06:31 | 2001-05-20 | DURING SURVEILLANCE TESTING THE AUTO TRANSFER TO STARTUP POWER FAILED TO PICK UP A VITAL BUS. During performance of Part 2 of surveillance test procedures M-13H (4kV Bus H Non-SI Auto Transfer Test) the auto transfer to startup power failed to pick up the bus when the auxiliary feeder breaker was opened. This was a result of the startup feeder breaker being in the test position. This resulted in the 4kV and 480 V bus H being de-energized. For this test diesel generator 2-2 is in manual and it did not load to the bus. With the dead bus the procedure contains a contingency to return diesel generator 2-2 to auto to re-energize bus H. This was done. This was a valid actuation of a diesel generator auto start due to bus undervoltage. Power was lost to bus H for about one minute, no important vital loads were lost and RHR was powered from a different vital bus. Surveillance test procedure M-13H is divided into four parts. The surveillance test procedure assumes that you perform parts 1,2, 3, and 4 in order. Part 1 of the surveillance was done 2 days ago. Part 1 placed the startup feeder breaker in the test position. Later parts 3 and 4 of the surveillance test procedure were performed. Nothing in parts 3 or 4 of the surveillance test procedure took the startup feeder breaker out of its test position. When part 2 of the surveillance test procedure was performed it has the testing personnel look at the control panel to verify that the startup feeder breaker is racked in. With the breaker in test the control board looks exactly the same as if the breaker was racked in. There should have been something to state that the breaker was in test but it was not done. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
38014 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-05-19 07:57 | 2001-05-19 10:07 | 2001-05-19 | Safeguards system degradation related to detection/monitoring, loss of all security systems due to total power outage. Power outage caused criticality alarm which necessitated an evacuation. All clear to return at 0908 ET. Compensatory measures were in place during this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1
38013 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2001-05-19 03:06 | 2001-05-19 09:52 | 2001-05-19 | On May 19, 2001, at approximately 0306 MST Palo Verde Unit 3 experienced a reactor trip (reactor protection system actuation) from 19% rated thermal power due axial shape index trips on all four channels of the core protection calculators.(CPCs). All control element assemblies inserted and plant equipment response was normal and as expected. Prior to the plant trip, Unit 3 had reduced power to 19% and had stabilized as part of pre-planned activities to perform maintenance on the main turbine, which had been taken offline at 0252 MST. The unit was at normal temperature and pressure prior to the trip. After the plant rip, control room staff entered the emergency operating procedures and diagnosed the event as an uncomplicated reactor trip with no emergency classifications being required. The primary plant was stabilized in Mode 3 in forced circulation with both steam generators used for heat removal. Unit 3 is stable at normal operating temperature and pressure in Mode 3. Other than the reactor protection system actuation no other engineered safety feature actuations occurred and none were required. The event did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or health and safety of the public. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
38012 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-05-19 04:06 | 2001-05-19 07:46 | 2001-05-19 | UNIT 2 ON NATURAL CIRCULATION AFTER A AUTOMATIC REACTOR TRIP. Unit 2 reactor coolant pump low flow reactor trip occurred due to a loss of a non-vital 6.9kV bus. The cause of the trip was human error while manipulating electrical plant equipment for planned work. The trip caused a loss of all non-ESF power to Unit 2. All safety systems actuated as required (all rods fully inserted into the core). The plant is currently in Mode 3 (Hot Standby) on natural circulation. No radioactive releases occurred. The licensee took their system Auxiliary Transformer out of service for planned work. The Auxiliary Transformer is the normal offsite power supply to Unit 2 ESF (vital) buses. Unit 2 was cross tied to Unit 1 offsite power supply to supply power to the Unit 2 vital buses while Unit 2 Auxiliary Transformer was out of service. While preparing to restore the auxiliary transformer to service personnel were sent to the 6.9kV non-ESF switchgear room to pull the potential transformer fuses. Instead they pulled the bus potential transformer fuses which resulted in a loss of the bus which in turn tripped the reactor coolant pumps. The bus potential transformer fuses are located in a drawer just above the potential transformer fuses drawer. Once the drawer is opened the fuses come out of their holder. After the reactor trip the diesel driven and the motor driven auxiliary feedwater pumps started. The diesel driven auxiliary feedwater pump was secured and now the motor driven auxiliary feedwater pump is supplying water to maintain proper steam generator water levels. The steam generator atmospheric valves are being used to maintain the plant in Hot Standby, no primary to secondary leakage. Both emergency diesel generators were manually started and they are supplying electrical power to the vital buses and power to two non-vital buses. The Unit 2 cross tie to Unit 1 offsite power supply was de-energized after Unit 2 emergency diesel generators were brought into service. If the emergency diesel generators are loss it will take less than 5 minutes to return Unit 1 offsite power back to Unit 2 ESF (vital) buses. All emergency core cooling systems are fully operable and pressurizer water level is within its proper range. Offsite power should be restored in about 4 hours. Unit 1 is at 100% power. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 05/19/01 AT 1127 ET BY CAROL ROCHA TAKEN BY MACKINNON * * * The purpose of this update is to notify the NRC within 8 hours of a valid actuation of the Unit 2 Auxiliary Feedwater System. Both trains of Auxiliary Feedwater actuated, as expected, on a Low-2 Steam Generator Level Signal. Division 11 4 kV offsite power was restored to the vital buses via 242-1 (at 0901CT) and 242-2 (at 0906CT). 6.9kV non -vital power was restored at 0727 CT and 0726CT. The emergency diesel generators "2A" & "2B" were secured at 0907CT and 0929CT respectively. A Reactor Coolant Pump was started and forced flow was restored to the reactor coolant system. R3DO (Shear) & NRR EO (Zwolinski) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
38011 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-17 16:37 | 2001-05-18 15:37 | 2001-05-25 | 24-HOUR NRC BULLETIN 91-01 RESPONSE At 1640 CDT on 05/17/01, the Plant Shift Superintendent (PSS) was notified that the independent verification required by procedure CP2-CU-CH2137 was not performed. The maintenance segment was not independently verified to be isolated. The same person signed for performance as well as the verification of the segment isolation. NCSA 400.009 requires that fissile operations that credit AQ-NCS function that is disabled due to maintenance must be identified independently and disabled using a tagout prior to disabling the feature and commencing maintenance. This is done to prevent operation of a system while an AQ-NCS component function is disabled. Since the independent verification was not performed, the process condition was not maintained. Therefore, double contingency was not maintained. SAFETY SIGNIFICANCE OF EVENTS: While the NCS control was violated, the fissile operation containing the component(s) undergoing maintenance was tagged out using LOTO both as a standard maintenance practice in C-400 and due to other NCS requirements. In addition, the equipment items removed had no AQ-NCS function which was affected by the maintenance actions. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): In order for criticality to be possible, the components undergoing maintenance must have an AQ-NCS function that is disabled, and the affected operations must be subsequently performed with fissile solution. Additionally, the maintenance activity must be one of the relatively few maintenance activities that do not require tagout for another NCS reason, such as to prevent fissile solution from leaking from the system. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing independently verifying the prevention of the affected fissile operation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Maximum assay of 2.75 wt. % U-235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on preventing operation of the Cylinder Wash Facility during maintenance affecting the AQ-NCS component. The components were properly identified as non-AQ-NCS; therefore, this control was not violated. The second leg of double contingency is based on independently preventing operation of the Cylinder Wash Facility during maintenance affecting the AQ-NCS component. The requirement to independently verify the AQ-NCS function of all components affected by maintenance was not performed. The control was violated, and the process condition was not maintained. Since the independent verification was not performed, the process condition was not maintained. Therefore, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: This condition was identified while reviewing completed maintenance work packages. There is no action that can be performed to resolve this condition and bring the process back into compliance since the maintenance activity has been completed. The NRC Resident Inspector was notified, and the DOE Representative will be informed. * * * UPDATE ON 5/22/01 @ 1235 BY HUDSON TO GOULD * * * As a result of this NCS violation, a review of work packages was initiated to determine if other instances exist where the required second signature was not obtained. On 05/21/01 at 1520 CDT, the PSS was notified that another incident involving the violation of this requirement was discovered pertaining to maintenance on the RF (radio frequency) furnace. The NRC Senior Resident has been notified of this event by Paducah personnel. The Reg 3 RDO (Burgess) and the NMSS EO (Cool) were informed by the NRC Operations Officer. * * * UPDATE 1440 ON 5/25/2001 FROM WALKER TAKEN BY STRANSKY * * * "This report updated on 5-25-01 to document the results of NCS reevaluation of the subject incidents. It has been determined that double contingency was maintained and these incidents are not reportable. "The first leg of double contingency is based on preventing fissile operation of the equipment during maintenance affecting the AQ-NCS component. The components were properly identified as non-AQ-NCS, therefore, this control was not violated. "The second leg of double contingency is based on independently preventing fissile operation of the equipment/system during maintenance affecting the AQ-NCS component. The requirement to independently verify the AQ-NCS function of all components affected by maintenance was not performed so this control was violated. Since the component does not have an AQ-NCS function, there was no process parameter being relied on for double contingency. Therefore, the process condition was maintained. "Although the independent verification was not performed, there was no reliance on NOS parameters since the component had no AQ-NCS function. Therefore there was no parameter to lose and the process condition was maintained. Therefore, double contingency was maintained." The NRC resident inspector has been informed of this update. Notified R3DO (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
38010 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2001-05-11 | 2001-05-18 15:20 | 2001-05-18 | MEDICAL MISADMINISTRATION A patient was being treated with Ir-192 and after 2 minutes of treatment verification of the location of the wire could not be made and a decision to terminate the treatment was made. When they attempted to terminate the treatment a problem arose with the clutch mechanism on the device which resulted in the wire slipping. The manufacturer was called and the medical staff continued to troubleshoot the system. The delivery wires for the system were cleaned and the treatment was resumed. On 5/14/01 the University RSO investigated the situation and decided not to use this device until it was evaluated by the manufacturer. On 5/16/01 it was discovered that the cable had some lubricant that leached from the cable and caused increased friction in the treatment catheter. Further evaluation of the film that was shot during this procedure determined that the source was between 4.5 and 5mm from where the treatment site was, therefore there was a delivery to an area that was unintended. The patient and physician were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0
38009 | -1 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-05-18 12:30 | 2001-05-18 15:08 | 2001-06-14 | AN UNANALYZED CONDITION WAS FOUND WHEN AN EXISTING PIPE TRENCH BLOCKOUT PATHWAY SEPARATING TWO ROOMS WAS FOUND TO BE BLOCKED. After reviewing the Unit 2 flooding calculation (environmental calculations for Auxiliary Feedwater and performing a walkdown of the area, it was determined that the calculation model which assumed an existing pipe trench blockout pathway separating the 2 rooms to be an open pathway. This pathway was found to be blocked leading to an unanalyzed condition. A PRA evaluation was performed for this condition. The result of this evaluation shows that the potential degraded condition due to the sealed pathway and missing backwater check valves in the drain lines does not pose a significant increase in the core damage risk. However, an additional review on May 15, 2001, it was deemed that the cumulative risk increase is potentially significant assuming the condition existed since initial evaluation. Therefore, this issue is being conservatively reported pursuant to 10 CFR 50.72 (ii)(B). No Technical Specification OPERABILITY issues are identified as a result of this event. Additionally this event has been evaluated per GL 91-18 and actions are being taken to be in compliance with the flooding calculations. The NRC Resident Inspector will be notified. * * * RETRACTED AT 1657 EDT ON 6/14/01 BY STEVEN SEWELL TO FANGIE JONES * * * "On 5/18/01 at 1508 hours, Comanche Peak Unit 2 reported an unanalyzed condition per 10CFR50.72(b)(3)(ii)(B) [EN# 38009). Specifically, the reported condition involved Unit 2 flooding/environmental calculations for the Auxiliary Feedwater (AFW) system that assumed an existing pipe trench blockout pathway separating 2 rooms to be an open pathway. During a walkdown of the area, it was determined that the pathway was sealed and backwater check valves did not exist in all floor drain lines from the three AFW pump rooms. This as-found configuration led to an unanalyzed condition where all three AFW pumps could be potentially incapacitated by a piping break in any one of the AFW pump rooms. This condition was determined to have existed since initial licensing and an initial, conservative, PRA evaluation of this condition determined that the cumulative risk increase was potentially significant. "Subsequently, a detailed deterministic analysis was performed to determine the consequence of flooding given the as found conditions. That evaluation shows that in no case is there a flooding scenario that results in the loss of all three AFW pumps. Comanche Peak Unit 2 has three pump trains (two 50% capacity motor driven pumps and one 100% capacity steam turbine driven pump). The worst case scenario is flooding in one of the motor driven AFW pump rooms which results in the loss of both motor driven pumps. In this case, the evaluation shows that the turbine driven pump is not disabled. Further, the flood waters do not adversely impact any other safety related equipment modeled in the PRA. The deterministic evaluation further concluded that a break occurring in the turbine driven pump room does not adversely impact either of the motor driven pump rooms. "The results of this evaluation show that the potentially degraded condition due to the sealed pathway and missing backwater check valves does not pose a significant core damage risk increase as a result of potential consequential equipment failures. Therefore. Comanche Peak requests that the 5/18/01 10CFR50.72(b)(3)(ii)(B) reportable event for Unit 2 be retracted." The licensee notified the NRC Resident Inspector. The R4DO (John Pellet) has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
38008 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-18 11:18 | 2001-05-18 12:32 | 2001-06-07 | 4 HOUR 91-01 BULLETIN During normal operations, a concern was identified of a potential fissile material operation in equipment that had been previously identified as an operation that contained material <1 % U-235. Upon investigation of the concern Nuclear Criticality Safety Personnel identified an unanalyzed condition in the X-330/333 "A" booster. Based on the identified condition this is a 4 hour reportable event. Currently the equipment is isolated. A sample shows the equipment contains material at <1% U-235. SAFETY SIGNIFICANCE OF EVENTS: LOW. the equipment is shutdown and has a pressure of 0.8 psia. The maximum mass in the X-330 to X-333 "A" compressor at this pressure is 41 gram U-235 POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For a criticality to occur, the mass in the compressor would have to increase to greater than 10.35 kg. The material then would have to be moderated and the deposit would have to reflected CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY. CONCENTRATION, ETC.): Enrichment and Mass ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Estimated enrichment is 1.5 weight percent U-235, the mass is estimated at 41 grams. The form of the material would be UF6. The optimum safe mass and critical mass at an enrichment of 1.5 % U-235 is 4.5 Kg and 16.502 Kg respectively. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES There were no NCSA controls on the identified equipment because the enrichment in the equipment was to be less than 1 weight percent U-235 in an operating cascade. In the current configuration it is not credible that enrichment would be exceeded. The deficiency was the equipment was not isolated from equipment that is allowed to see enrichment greater than 1 weight percent U-235. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The Plant Shift Superintendent directed the "A" booster isolated. The equipment was sampled and found below 1% U-235. Engineering continues to investigate the issue. The NRC Resident Inspector was notified and the DOE Representative will be informed. * * * UPDATE ON 06/07/01 AT 1313 ET BY RICHIE TAKEN BY MACKINNON * * * After further review this is not reportable because an additional evaluation determined the enrichment in the affected equipment did not exceed 1 weight percent U235, and the plant condition remained within that assumed by the NCSA and SAR. Therefore no violation occurred. R3DO (B. Clayton) & NMSS EO (John Hickey) notified. The NRC Resident Inspector was notified of this update by the Certificate Holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
38007 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-17 14:40 | 2001-05-18 08:36 | 2001-05-30 | SAFETY EQUIPMENT FAILURE At 1440 on 05/17/01, the Plant Shift Superintendent (PSS) was notified by engineering that load cell calibration data for the C-333 U/5 C/9 and C-337 U/2 C/2 freezer sublimers is suspected to be non-conforming. The load cells are part of the High High Weight Trip System for the freezer sublimers which is required by TSR to be operable. It is suspected that a batch of 24 load cells do not meet the specifications credited in the existing setpoint calculations and the calibration procedures. The load cell calibration data from 2 other load cells in this batch indicated less weight than what is actually applied. It has been determined that this deficiency may affect the freezer sublimers ability to actuate the High High Weight Trip System at the required Limited Control Setting (LCS). This deficiency would not affect the ability of the freezer sublimers to actuate the High High Weight Trip System below the Safety Limit (SL). These 2 suspected freezer sublimers were declared inoperable by the PSS. The safety system deficiency is reportable to the NRC as required by 10CFR76.120(c)(2). The equipment is required by TSR to be available and operable and should have been operating. No redundant equipment is available and operable to perform the required safety function. The NRC resident inspector was notified.. * * * UPDATE ON 5/30/01@ 2337 BY WALKER TO GOULD * * * RETRACTION Following the Identification of this problem, the suspected load cells were removed from service and tested. The test results were evaluated by the responsible System Engineer against the F/S set-point calculations and, although outside the optimum error band, the load cells were within the allowable error band and could have performed their intended safely function to trip the F/S at or below the High-High Weight Safety System setting. Thus, 10 CFR 76.120 (c)(2) reporting criteria is not met and the subject notification is being retracted. R3DO (M. Ring) notified. The NRC Resident Inspector was notified. The DOE Representitive will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0
38006 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-05-17 20:40 | 2001-05-17 22:14 | 2001-05-18 | NOTIFICATION OF THE OCONEE COUNTY SHERIFF'S OFFICE The switchboard was notified by an individual of a possible bomb threat concerning the Oconee site that was left on her home answering machine. The licensee notified the Oconee County Sheriffs Department to investigate. No other law enforcement agencies have been notified. They do not consider it a credible threat. The NRC Resident Inspector will be notified. * * * UPDATE ON 5/18/01 @ 1936 BY CONSTANCE TO GOULD * * * The FBI and the County Sheriff have determined that the bomb threat was not a credible threat. The NRC Resident Inspector will be informed. The Reg 2 RDO(Wert) was notified. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
38005 | -1 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2001-05-08 02:10 | 2001-05-17 14:46 | 2001-07-02 | INTERRUPTION OF THE COOLING FUNCTION PERFORMED BY THE PRIMARY LOOP OF THE BACKUP SPENT FUEL POOL COOLING SYSTEM OCCURRED FOR 20 MINS. "On May 8, 2001 P3 was in RO-11, and the reactor was de-fueled with all discharged fuel in the Spent Fuel Pool (SFP). SFP cooling was provided by the Backup Spent Fuel Pool Cooling system (B/U SFPCS) because the normal Spent Fuel Cooling system was out of service for maintenance. At approximately 0210 hours on May 8, 2001, the water supply to the secondary loop of the B/U SFPCS was interrupted due to a loss of power involving IP3's demineralized water source. This water interruption subsequently caused a low differential pressure trip of the primary loop pump of the B/U SFPCS. Operator response re-gained the dernineralized water supply to the secondary loop. SFP cooling from this system was restored. The cooling function performed by the primary loop of the B/U SFPCS was interrupted for approximately 20 minutes total. A Root Cause Team investigation was commenced the morning of May 8, 2001 to review this event. This event is being considered potentially reportable under 10 CFR 50.72 (b)(3)(v)(B). Investigation into the cause and reportability of this event is ongoing and this ENS report is being made at this time due to the continuing investigation of reportability." Temperature increased from 151 to 155°F. The NRC Resident Inspector was notified along with state and local agencies. Their US Congressman was also notified. * * * RETRACTION 0912 7/2/2001 FROM PRUSSMAN TAKEN BY STRANSKY * * * "On May 17, 2001, Entergy notified the Operations Center that a loss of Back-up Spent Fuel Pool Cooling System (BUSFPCS) was potentially reportable (ENS 38005). Reporting was under 10 CFR 50.72(b)(3)(v)(B) 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to... (B) remove residual heat.' Entergy is hereby retracting that notification. The event was subsequently determined to be not reportable. Section 3.2.7 of NUREG-1022, Revision 2 (NRC guidance for reporting), says the 'intent of these criteria is to capture events that would have been a failure of a safety system to properly complete a safety function, regardless of whether there was an actual demand.' The NUREG goes on to say that the 'definition of the systems included in the scope of these criteria is provided in the rules themselves. It includes systems required by the TS to be operable to perform one of the four functions (A) through (D) specified in the rule.' Examples 1 and 2 in NUREG 1022, Section 3.2.7 illustrate that events or conditions associated with a system not in the TS are not reportable because of that fact. Example 2 states 'If such systems are required by Technical Specifications to be operational and the system is needed to fulfill one of the safety functions identified in this section of the rule then system level failures are reportable. If the system is not covered by Technical Specifications and is not required to meet the single failure criterion, then failures of the system are not reportable under this criterion.' Based on the statements contained in NUREG 1022, Revision 2, Entergy concluded that the event was not reportable. The BUSFPCS and SFPCS are not in IP3 TS and the only TS parameter associated with this event was the pool level. The pool level was maintained within limits at all times." The NRC resident inspector has been informed of this retraction. Notified R1DO (Barkley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0
38004 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-03-22 07:07 | 2001-05-17 13:47 | 2001-05-17 | This report is being made in accordance with 50.73a)(1), which states, in part, "In the case of an invalid actuation reported under §50.73 (a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER." These invalid actuations are being reported under §50.73 (a)(2)(iv)(A). On March 22, 2001, at 0707 hours, during the performance of Maintenance Surveillance Test (1MST-DG13R), "DG-3 Loading Test," steps performed out of sequence resulted in invalid actuation of Primary Containment Isolation system (PCIS) Group 6 valves and Secondary Containment Isolation dampers due to interruption of electrical power to the Emergency Bus E3. During a "dry run" of the test, instrumentation and controls technicians inserted the actual test signals before the Unit 1 "CAC Purge Vent Isol Ovrd Switch," 1-CAC-CS-5519, was placed in the "OVERRIDE" position, as required by the procedure. The purpose of placing the switch in the "OVERRIDE" position is to prevent a P015 Group 6 isolation, Secondary Containment isolation, and Standby Gas Treatment (SBGT) system actuations when Emergency Bus E3 is de-energized as part of the test. The actuations of PCIS Group 6 valves and Secondary Containment Isolation dampers were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). At 0715 hours, Emergency Bus E3 was energized by its normal power source. By 0726 hours, the PCIS Group 6 isolation logic was reset, the Reactor Building Ventilation system was returned to service (i.e., the Secondary Containment isolation was reset), and both SBGT trains A and B were placed in standby. PCIS Group 6 valves include isolation valves from the Containment Atmosphere Control, Containment Atmosphere Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling systems. Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in AR 29889. The NRC Resident Inspector was notified of this 60-Day report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0
38003 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2001-04-16 14:15 | 2001-05-17 11:43 | 2001-05-17 | FOR CAUSE TESTING A non-licensed employee was determined to be under the influence of illegal drugs during for cause testing. The employee's unescorted access to the plant has been terminated. Ask the HOO of further information The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Refueling; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0
38002 | 0 | MD DEPT OF THE ENVIRONMENT |  |  |  |  | 2001-05-10 14:30 | 2001-05-17 08:19 | 2001-05-17 | MEDICAL MISADMINISTRATION On Tuesday, May 8, at 4:30 PM, at Franklin Square Hospital a patient was given a vaginal implant consisting of 10 ribbons each with 8 Ir-192 seeds. The activity per seed was about .495 mgRaEq, for a total implant of 39.6 mgRaEq (71.0 mCi). The intent was to deliver 60 cGy/hr to the periphery of the implanted treatment volume (4 cm diameter 8 cm long, for V= 100 cm3) for 50 hours for a total implant dose of 3000 cGy. This dose was to add to the already delivered external beam dose to that volume of 4500 cGy, for a total of 7500 cGy. The patient was checked by the physician on Wednesday at 2:30 PM (after 22 hours) and all the needles were in place. The next check by the physician was at the time of removal, at 6:30 PM on Thursday. He found one needle with its ribbon of 8 seeds lying loosely on the folds of the bed sheet by the patient's hip, and 3 additional needles had also backed out by about 3 cm from their implanted positions. The patient was judged to be unable to describe the circumstances of the displacements. Computer reconstruction showed that the reduction in the total tumor dose from the ribbon displacements was less than 10% and affected less than 15% of the implanted volume. And the corresponding increase in the position of the 50% isodose line at the other end of the implant was only about .5 cm. The physician has stated that he believes the patient had adequate brachytherapy treatment, and that no further interventions would be necessary. As for the dose to the patient from the dislodged ribbon, the physician has stated that there should not be significant dose to any viscera but to the skin and soft tissues. He does not think it has clinical significance for this patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0
38001 | 0 | WATERFORD | 3 |  |  | [3] CE | 2001-05-17 05:47 | 2001-05-17 07:21 | 2001-05-17 | UNUSUAL EVENT DECLARED - UNAUTHORIZED ACCESS INTO THE PROTECTED AREA. Immediate compensatory actions taken upon discovery. The licensee contacted the St. Charles Parish Sheriff's Office. The NRC resident inspector was notified. The unusual event was declared at 0547 and terminated at 0556. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 0
38000 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-05-16 22:59 | 2001-05-17 01:38 | 2001-05-17 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) INOPERABLE At 2259 hours on 5/16/01, the SPDS portion of the Emergency Response Facilities Computer System (ERFCS) was noted to be inoperable because the system time was not updating. The Technical Support Center (TSC) keyboard is not available nor is the Control Room Unit keyboard available for either Unit. Both Local Emergency Operations Facility (LEOF) and Central Emergency Operations Facility (CEOF) SPDS data links were unavailable. Initial indication of loss of ERFCS function was computer linkage failure at 2159 hours on 5/16/01. The ERFCS was rebooted satisfactorily with a new power supply. All portions of the system were noted to be functioning correctly at 0120 hours on 5/17/01. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37999 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-05-16 19:00 | 2001-05-16 23:53 | 2001-09-10 | NRC BULLETIN 91-01 RESPONSE - CRITICALITY CONTROL - (4-Hour Report) During the revision to NCSE 052 and 039, it was discovered that the condenser could potentially be pressurized greater than 35.5 psia when the condenser supply and return valve are both closed without a fluorinating environment in the process gas system. NCSA CAS-002/011 allow both the supply and return valves to be closed when draining the condenser without a fluorinating environment. NCSEs 052 and 039 rely on the condenser supply valve to be closed enough to prevent the condenser from being pressurized above 35.5 psia during the time the return valve is closed and maintenance personnel relieve the pressure on the condenser. Based on recent discussions, it was discovered that closure of the supply valve may not provide sufficient isolation to prevent the condenser from being pressurized above 35.5 psia with the return valve closed because of potential seat leakage of the supply valve. The licensee has stopped all maintenance activities which could create this condition. Also, samples will be taken where this maintenance has occurred to check that the freon still complies with the water content limits. Paducah personnel notified the NRC resident inspector. ***** UPDATE RECEIVED AT 1500 EDT ON 06/21/01 FROM CALVIN PITTMAN TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from Paducah personnel: "At 1900 [CDT] on [05/16/01], the Plant Shift Superintendent (PSS) was notified of a deficient Nuclear Criticality Safety Evaluation. NCSAs CAS 002 and CAS 011 allow both the Recirculating Cooling Water (RCW) supply and return valves to be closed when draining the R-114 condenser without a fluorinating environment. The NCS evaluations rely on the RCW supply valve to be closed enough to prevent the condenser from being pressurized above 35.5 psia during the time the RCW return valve is closed and maintenance relieves the pressure on the condenser. Based on recent discussions between NCS and maintenance personnel, it was discovered that closure of the RCW supply valve might not provide sufficient isolation to prevent the condenser from being pressurized above 35.5 psia with the return valve closed. The RCW system provides cooling water to the R-114 condenser, which removes heat from the freon system. The freon is used to remove the heat of compression from the process gas system. The R-114 pressure is maintained above the RCW pressure to form a barrier between the process gas and the RCW cooling water, thus preventing moderation from occurring should a leak in the condenser occur. If the RCW pressure is allowed to rise above 35.5 psia, the potential exists that the RCW pressure could exceed that of the R-114 pressure. At this point, an actual condition of RCW pressure greater than 35.5 psia has not been identified." "UPDATE [on 06/20/01] ATRC 01-3248: During the Engineering review to determine permanent corrective actions, additional immediate corrective actions have become necessary. It has been determined that when the condenser return valve is open, condenser pressure can also be affected when the return header alignment is changed (i.e., closure of RCW loop isolation valves, RCW building header valves, cooling tower riser valves, etc.). Controls have been implemented to ensure that changes to the RCW system do not impact our ability to maintain R-114 pressure above RCW pressure." "SAFETY SIGNIFICANCE OF EVENTS: The controls credited for the isolation of the condenser to ensure the pressure at the condenser does not exceed 35.5 psia do not meet the intent of the NCSE for isolation. Therefore, the NCSE analysis is deficient and double contingency is not maintained. However, the probability for a criticality is unlikely due to the number of conditions that must be met in order for a criticality to be possible." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): In order for a criticality to be possible, the following conditions must exist. With the condenser supply and return valves closed, the supply or return valve must be leaking to allow the condenser pressure to exceed the minimum coolant pressure of 35.5 psia. With the configuration of the supply valve closed and the return valve opened, the RCW return system must be changed (i.e. closure of loop isolation valves, RCW building header valves, cooling tower riser valves, etc.) enough that the affected condenser pressure increased greater than 35.5 psia. The process gas equipment must be at a UF6 negative and contain a UO2F2 deposit greater than a critical mass. The condenser must have a leak of sufficient rate and duration to allow enough water to overcome the down comer allowing liquid water to enter the cooler. The cooler must also have a simultaneous leak, which would allow wet coolant to leak into the process gas side of the equipment at a location, which would allow moderation of the deposit." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two controls for moderation." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Maximum assay of 5.5 wt. % U235" "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of [the] double contingency is based on isolation of the RCW condenser by closing the supply valve to maintain the condenser pressure less than 35.5 psia. Based on discussions with maintenance personnel, the current leak rates of the supply valve may be greater than the amount assumed to ensure the condenser pressure does not exceed 35.5 psia when the return valve is closed. Also, when the return valve is open, the RCW return system could be changed (i.e., closure of loop isolation valve, RCW building header valves, cooling tower riser valves, etc.). Therefore, the intent of this control has not been met, and this leg of double contingency was not maintained." "The second leg of [the] double contingency is based on the independent verification of the isolation of the supply valve and when the return valve is required to be open, verification that the return valve is open. Since adequate isolation of the supply valve cannot be ensured based on verification of supply valve closure or return valve open, when required, the intent of this independent verification control was not met. Therefore, this leg of double contingency was not maintained." "Since isolation of the RCW condenser with the supply valve closed and the return valve closed or opened may not meet the intent of the isolation requirement to maintain the condenser pressure less than 35.5 psia, these controls are deficient and double contingency has not been maintained." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Until the NCSEs and NCSAs can be revised and additional controls established:" "Condenser Return Valve Closed" "1. All maintenance activities related to closing the condenser return valve on a system, which is at a UF6 negative, have been stopped. This does not apply to systems that are not connected to the supply line or the C-310 TOPS Boosters." "2. The coolant systems for condensers, which had the return valve closed without a fluorinating environment present, will be sampled in accordance with NCSA CAS-002 to verify the CFC-114 still complies with the water content limits." "3. The return [valves] on condensers, which currently have the return valve closed, fluorinating environment removed (at a UF6 negative), and is connected to the supply line, will be opened." "RCW Building Return System (based on ATRC-01-3248)" "4. The plant power level will be maintained below 400 MW until NCSE changes are completed and/or necessary controls are implemented or specific evolutions are evaluated by NCS and approval is given." "5. Both building RCW return header valves to a given header will not be closed." "6. At least 3 cooling tower risers for every large pump and 2 risers for every small pump will be kept in service." "7. Respective building RCW bypasses will be closed before isolating an RCW system loop." "8. For any auxiliary systems not protected by a delta P alarm (i.e., A-310 Booster, A-335 Booster, C-337 B Booster) except the C-310 TOPS Booster, any activity that requires verification that the condenser return valve is open will also verify other valves in the return path to the applicable RCW return header are also open." Paducah personnel notified the NRC resident inspector. The NRC operations officer notified the R3DO (Bruce Jorgensen) and NMSS EO (Patricia Holahan).] * * * UPDATE 1705EDT ON 8/21/01 FROM CALVIN PITTMAN TO S. SANDIN * * * The following information was provided as an update: "The plant has completed and approved a USQD [Unreviewed Safety Question Determination] to allow the plant power level to be increased to 850 MW." The NRC resident inspector has been informed. Notified R3DO(Gardner) and NMSS(Essig). * * * UPDATE 1300 9/10/2001 FRIN BEASLEY TAKEN BY STRANSKY * * * "NCSE 039/NCSA CAS-011 and NCSE 052/NCSA CAS-002 have been revised, approved, and implemented by the plant. These analyses are no longer considered deficient. The analysis incorporates additional controls associated with the cascade RCW system that are necessary for double contingency above a power level of 850 MW." The NRC resident inspector has been informed. Notified R3DO (Burgess) & NMSS (Wayne Hodges) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37998 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-05-16 16:00 | 2001-05-16 19:16 | 2001-05-16 | REACTOR WATER CLEANUP SYSTEM ISOLATION DURING APPROACH TO CRITICALITY AND MANUAL REACTOR SCRAM The following text is a portion of a facsimile received from the licensee: "During approach to criticality[,] the reactor water cleanup (RWCU) system isolated on high temperature out of the non-[regenerative] heat exchanger. The cause of the high temperature was due to air entering the system from an ongoing local leak rate test. The RWCU system was providing the letdown path to control [reactor] water level from control rod drive cooling [water] flow. The control room was unable to recover the RWCU system and made the decision to manually scram the [reactor]. A manual actuation of [the reactor protection system] was inserted by placing the [reactor] mode switch to shutdown. All rods [fully] inserted[,] and all systems responded as expected." The NRC resident inspector was in the control room at the time of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37997 | -1 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-05-16 11:11 | 2001-05-16 18:26 | 2001-06-05 | DISCOVERY THAT THE CONTROL ROOM HABITABILITY SYSTEM MAY NOT MEET DESIGN REQUIREMENTS UNDER CERTAIN CONDITIONS The following text is a portion of a facsimile received from the licensee: "The control room habitability system may not meet design requirements under certain conditions. Specifically, any design accident where the control room bottled air pressurization system actuates and the exhaust fan of the cable vault and tunnel area trips with the supply fan to the cable vault and tunnel continuing to run, the minimum delta pressure between these areas may not be maintained." "The control room bottled air systems of both Unit 1 and 2 have been declared inoperable, and a 7-day [technical specification action statement has] been entered." The licensee plans to notify the NRC resident inspector. * * * RETRACTED AT 1141 EDT ON 6/6/01 BY JAMES CROSSMAN TO FANGIE JONES * * * After subsequent engineering evaluation, the licensee has determined that this event was not reportable and is retracting the event notification. The evaluation concluded that the effect of a failure of a non-safety related component on the control room envelope and bottle air system is not required during a design basis accident. Therefore, the proposed (not actual) failure assumptions are not considered reasonable and there is no need to report this condition. The licensee notified the NRC Resident Inspector. The R2DO (Ken Barr) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37996 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-05-16 16:06 | 2001-05-16 16:52 | 2001-05-16 | OFFSITE NOTIFICATION/INFORMATION REGARDING A RECYCLE FACILITY SHIPMENT CONTAINING RADIOACTIVE MATERIALS The following text is a portion of a facsimile received from the licensee: "Indian Point is making the following notification pursuant to 10CFR50.72(b)(2)(xi) and in accordance with Station Administrative Order 124, Item 47." "This report is being made pursuant to 10CFR50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.'" "At approximately 1230 hours today[,] IP-2 was notified by KARTA Industries, a recycle facility, that a shipment made by KARTA to Ohio was returned because it contained radioactive material. KARTA plans to notify the New York State Department of Environmental Conservation (DEC) of this event. This report is being made for information only since the waste does not appear to be associated with Indian Point operations. When notified by KARTA, IP-2 dispatched radiation protection personnel to the KARTA facility in Peekskill, NY. By 1330 [hours,] IP-2 RP personnel surveyed the returned bale and determined it showed [approximately] 2.5 mrem/hr on contact. Since IP-2 has expertise in radiation protection[,] it was decided to bring the bale to the IP-2 site to ensure proper control and disposal. Isotopic analysis of a sample of the bale material indicates mostly I-131[,] which indicates a medical treatment, not material from a nuclear power plant. KARTA does handle recyclable material from hospitals in the Peekskill vicinity. IP-2 will assay the entire bale and ensure proper disposal. IP-2 has been informed by KARTA that KARTA plans to notify the New York State Department of Environmental Conservation (DEC)." The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37995 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-05-15 16:00 | 2001-05-16 16:12 | 2002-10-03 | AGREEMENT STATE REPORT REGARDING THE THEFT OF A TROXLER GAUGE FROM THE RESIDENCE OF A WINGERTER LABORATORIES, INC. EMPLOYEE IN MIAMI, FLORIDA The following text is a portion of a facsimile received from the Florida Bureau of Radiation Control: "Incident Number[:] FL01-057" "Incident Date[:] 15-May-01" "Licensee or Owner[:] WINGERTER LABORATORIES, INC." "City, State, and Zip Code[:] Miami, FL 33181" "License #[:] 0673-1" "License Type; Category[:] Specific; 3L(1)" "Isotope(s)[:] Cs-137, Am-241" "Activity(s)[:] N/A" "Material Form; Chemical Form; Physical Form[:] N/A" "Portable Disposition of Material[:] Unknown" "Exposure? No" "Incident Category[:] Loss of Control - Lost , Abandoned, or Stolen Materials" "Location Classification[:] Unrestricted Area" "Incident Description[: A licensee] operator[, ...,] was transporting [the] gauge from [a] jobsite to [the] office and stopped off at [a] personal residence (@ [approximately] 1600 hrs.). [The employee] left [the] truck running while he went into [the] residence. When [the] employee returned, [the] truck and gauge were missing. [The key] ring for [the] truck also contained keys to [the] gauge[,] employees residence[,] and personal vehicles. Company has issued [a] press release in the Miami Herald newspaper offering $1,000 for information on [the] return of [the] truck/gauge. [The truck] was reported recovered at 1500 on 16 May. [The gauge] is still missing." "Device Type (Quantity)[:] Soil moisture/Density Gauge" "Manufacturer[:] Troxler" "Model Number[:] 3411-B" "Serial Number(s)[:] 7400" "Emergency Groups at Scene[:] USNRC, State Warning Point" "Organizations Notified[:] Metro Dade PD" "Media Contacted[:] None" (Call the NRC operations officer for state and licensee contact information, the incident location, and licensee operator name.) ***UPDATE 10/3/02 0809 EDT JERRY EAKINS TO MIKE NORRIS*** "Pick-up truck, driven by [ ],scrap metal collector, tripped the monitor alarm. [ ]identified the isotope as Cs- 137 with an Exploraniun instrument. After consultation with this office, [ ] unloaded the truck, identified the gauge, and placed it in a secure locked box until the inspector picked it up. The gauge had been reported stolen on 15 May 01, incident report FL01-057. Incident tag # K-31 was issued. Gauge was returned to licensee." The source was secured and locked. Surveys indicated no leakage from the source. Notified R2DO (Henson) and NMSS EO (Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37994 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-05-16 10:18 | 2001-05-16 12:25 | 2001-05-16 | TURBINE TRIP FOR UNKNOWN REASONS AND SUBSEQUENT REACTOR SCRAM The following text is a portion of a facsimile received from the licensee: "Nine Mile Point Unit 2 experienced a turbine trip and reactor scram (Reactor Protection System (RPS) actuation) from approximately 90% power. All control rods fully inserted. Reactor water level lowered to below Level 3 (159.3 inches indicated, RPS actuation level) following the scram due to high power scram. Level recovered to above Level 8. (203.8 inches indicated, high level feed pump trip level). The operating feed pumps tripped as designed, and the 'A' [feed pump] was restarted. Level was restored to the normal band. Reactor pressure control continues to be controlled using the main condenser and a normal cooldown is in progress. Cause of the turbine trip is under investigation." The licensee stated that there were no related maintenance or surveillance activities ongoing at the time of the turbine trip. None of the relief valves lifted, and all containment parameters are currently normal. All emergency core cooling systems (ECCS) are available, and no ECCS actuations were required during this event. Other than the reactor scram, there were no engineered safety features actuations, and none were required. There was nothing unusual or misunderstood except for the cause of the turbine trip, and all systems functioned as required in response to the turbine trip and subsequent reactor scram. The licensee notified the NRC resident inspector and the State. The licensee also plans to issue a press release. | 0 | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37993 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-05-15 07:00 | 2001-05-16 05:38 | 2001-05-16 | PLANT MAY HAVE OPERATED ABOVE 100% POWER During power up-rate data verification, Byron Station identified that an improper feedwater density factor and thermal expansion coefficient had been used to calculate feedwater flow constants (referred to as AMAG constants) on Units 1 and 2. The improper constants resulted in a non-conservative determination of reactor power via the thermal power calorimetric calculation. Thermal power was underestimated by 0.12 percent rated thermal power. The improper AMAG constants have been utilized since AMAG was implemented at Byron Station in May of 2000 (Unit 1 on 5/16/00 and Unit 2 on 5/12/00). It is believed since May of 2000 either unit may have exceeded 100 percent rated thermal power over an eight hour period based on the non-conservative AMAG constants. There is no evidence that either unit ever exceeded 102.0 percent rated thermal power. A formal review of past power history for both units is in progress. The AMAG constants have been corrected for Unit 2 and are in progress for Unit 1. Unit 1 is being maintained at or below 99.88 percent rated thermal power until the AMAG constants have been corrected. The licensee notified the NRC resident inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0
37992 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-05-15 16:08 | 2001-05-15 16:44 | 2001-05-15 | MAJOR LOSS OF EMERGENCY PREPAREDNESS CAPABILITIES IN THE CALVERT COUNTY AREA At 1608 on 05/15/01, the control room was notified that 40 of the 49 [emergency] sirens failed to respond [during] the weekly silent test at 1445. The apparent cause is currently believed to be a potential transformer failure. Troubleshooting and repairs are in progress. The licensee notified the NRC resident inspector. | 100 | 68 | 0 | 100 | 68 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37991 | 0 | STORK TWIN CITY TESTING |  |  |  |  | 2001-05-08 09:00 | 2001-05-15 15:31 | 2001-05-15 | STUCK IRIDIUM-192 SOURCE AND FAILURE TO MAKE AN EVENT NOTIFICATION WITHIN 24 HOURS On 05/05/01, an X-ray crew in Heron Lake, MN, was inspecting a flat bottom tank using an Amertest-660A device containing 80 curies of iridium-192. At 0900 CDT, during performance of an exposure, the stand that the guide tube was connected to fell over and kinked the tube. As a result, the crew could not initially retract the source. The crew subsequently followed procedures and successfully retracted the source to its shielded position. There were no overexposures as a result of this event. In preparation for submitting a 30-day letter, the licensee discovered (today) that this event should have been reported as a 24-hour event notification. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MN | MAT | [5 empty] | 0
37990 | 0 | NC DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-05-12 | 2001-05-15 14:56 | 2001-05-30 | AGREEMENT STATE REPORT REGARDING A TROXLER MOISTURE DENSITY GAUGE LOST/STOLEN FROM S&ME IN WINSTON SALEM, NORTH CAROLINA The following text is a portion of a facsimile received from the North Carolina Department of Environment and Natural Resources, Division of Radiation Protection: "SUBJECT: Incident 01-14" "Today, a North Carolina Portable Gauge Licensee (S&ME 041-0922-1 Greensboro) reported a loss/theft of a Portable Moisture Density Gauge from Winston Salem, NC, between the evening on Friday, May 11, 2001, and Saturday, May 12, 2001. Local and State law enforcement agencies were notified on Saturday, May 12, 2001. This Agency was notified by NC Emergency Management of the incident at [1630] on Monday, May 14, 2001. The Licensee reported the incident to this Agency [on] May 15, 2001." "The device that was lost/stolen is:" "Troxler 3411B Moisture Density Gauge SN 14682 Cs-137 #50-3361 8 mCi Am-241:Be #47-10037 40 mCi" (Call the NRC operations officer for a State contact telephone number.) * * * UPDATE ON 05/30/01 AT 0938 ET BY SHARN JEFFRIES TAKEN BY MACKINNON * * * Troxler gauge was found by a member of the public and returned to the licensee. The licensee has shipped the gauge to Troxler for inspection and testing. R2DO (R. Bernhard) & NMSS EO (Fred Brown) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0
37989 | 0 | OTTWELL MALBY |  |  |  |  | 2001-05-15 10:30 | 2001-05-15 10:42 | 2001-05-15 | STRUCTURE FIRE INVOLVING NUCLEAR GAUGE The licensee reported that a fire is currently occurring at their field office. A Troxler Model 3411 moisture/density gauge is currently stored in the building. The sources are locked in their safe positions, and the gauge is located in a storage locker. The licensee has notified local police and fire departments regarding the presence of this device. ***** UPDATE RECEIVED AT 1515 ON 05/15/01 FROM TOD CRAMER TO LEIGH TROCINE ***** The licensee is updating this event notification. The gauge was not damaged in the fire. There was some water damage, and that area of the building was reported to be underwater after the fire. The HAZMAT team obtained a surface reading on the gauge, and the reading was 1 millirem per hour. The gauge was intact, and there was no heat damage, melting, or physical damage. The licensee plans to perform a wipe test and possibly repair the gauge. The licensee notified the Fire Department, HAZMAT, local/city police agencies, and NRC region 3 office (Jim Hastings). The NRC operations officer notified the R3DO (Parker) and NMSS EO (Cool). (Please call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MI | MAT | [5 empty] | 0
37988 | 0 | US ARMY |  |  |  |  | 2001-05-11 | 2001-05-14 11:16 | 2001-05-14 | LOST CHEMICAL AGENT ALARM AT FT. IRWIN, CA. The U.S. Army Aberdeen Proving Grounds reported the loss of a chemical agent alarm, model number GID-3. The alarm contains two nickel-63 sources each with an activity of 15mCi. The chemical agent alarm was lost at FT. Irwin, CA during training exercises on May 11, 2001. Search is in progress to locate the alarm. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37987 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2001-05-14 00:20 | 2001-05-14 02:21 | 2001-05-14 | OFFSITE NOTIFICATION DUE TO DIESEL FUEL SPILL ONSITE The licensee notified the Maine Department of Environmental Protection regarding the spillage of approximately 25 gallons of diesel fuel. The fuel oil was spilled when the fuel tank of a truck was punctured as it was driving over a temporary ramp. The spill has been contained. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37986 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2001-05-12 05:29 | 2001-05-12 09:55 | 2001-05-12 | ALERT DECLARED AND TERMINATED DUE TO INADVERTENT CRITICALITY ALARM ACTIVATION "Maintenance personnel were changing out nuclear criticality detectors (NCDs) as part of an annual PM. Maintenance personnel in central guard station inadvertently turned the alarm key in an out-of-order sequence, causing the criticality alarm system to sound. The error was corrected immediately. The alarm system is fully in service." The licensee stated that no actual criticality occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | [10 empty] | ALERT | 4 | WA | FUE | [5 empty] | 0
37985 | 0 | INOVISION |  |  |  |  | 2001-05-10 | 2001-05-11 15:05 | 2001-07-11 | 10 CFR 21 REPORT - INTERIM REPORT ABOUT R-11 MONITOR PROBLEM The following is taken from a faxed report: Deviation being evaluated: An R-11 Monitor installed in Korea has been reported as having a rapid increase in displayed concentration and analog output values. Initial evaluation of the problem indicates the cause may be in one of the base 960 firmware modules, which are also installed in some US nuclear power plants. The significance of the problem is still under evaluation to determine if it could create a substantial safety hazard. The initial report was received on March 15, 2001. Evaluation information to date: The problem is a rapid increase in displayed concentration and analog output values. The problem is not apparent at low levels of activity where low count rates and statistical variation mask the increase. When activity is near the upper range of the monitor, this spike in calculated activity has triggered radiation alarms and could place the channel into over range. The spiking in activity is believed to be due to the microprocessor being unable to read and clear a register within the allotted time. This results in a higher accumulated count value when the register is finally read. Since the problem is directly related to processor workload, the problem is most likely to occur in a complex channel configuration with multiple detectors (such as a PIG or Extended Range) and where the microprocessor is highly tasked with RMS computer or isolator communications. For single range channels, the result of the spike would be a false radiation alarm and possibly an over range condition as well, although this has not been reported to the best of our knowledge. The other possibility is that this situation could occur on an Extended Range monitor thereby placing the channel in 'accident' or high range mode. If this occurs, the normal range is shut down and/or by-passed. If the accident range detector is brought online below its minimum operating range and the normal range detector is shut down, an unmonitored release might be possible. A more detailed analysis of the firmware in specific channels is needed to determine if this last condition is possible. The possible defect is believed at this time to only affect Model 960 firmware modules upgraded or purchased since 1992. Evaluation completion date: July 10. 2001 * * * UPDATED AT 1215 EDT ON 7/11/2001 BY JANICE BROWNLEE TO FANGIE JONES * * * Inovision faxed a follow-up to the interim report. "Component containing defect: Firmware in Type IIA 960 Systems with a Real Time Clock (RTC) integrated circuit, programmed for use in pulse counting applications, and equipped with the following controller modules: Model 960CD-220 (P/N 960CD-220-10) Model 960CD-221 (P/N 960CD-221-10) Model 960CD-223 (P/N 960CD-223-10) "Monitors utilizing ionization chamber detectors are not affected "The above controllers were equipped with Real Timer Clock and additional firmware to control the RTC. "Affected facilities: The Pacific Gas and Electric's' Diablo Canyon Nuclear Power Plant is the only domestic, NRC licensed user affected by this defect. Their purchase orders ZS-7204A-AAO and ZS-7204B-AAO are affected and were shipped from 1991-1993. There were 20 potentially affected PROMs from those orders. Other potentially affected customers are located in Korea (KEPCO, KAREI) and in Belgium (SEMO, Electrabel). Notifications have been or will be sent to the affected facilities with further specific information. "Corrective Action: Although there is a sporadic firmware program problem, we do not believe that problem represents a significant safety concern. It is our intention to notify the customers that are potentially affected by this anomaly and to identify for them the affected monitors/channels within their facility within 30 days The problem is only potentially present if the facility has the TARGET COUNT algorithm enabled. We will recommend that the facilities discontinue use of this algorithm. (Diablo Canyon does not use this function). "As discussed earlier, a preliminary firmware fix has been identified. The decision to take further action will be addressed with each of the potentially affected facilities." The R4DO (Chuck Cain) and NRR (Vern Hodge) have been notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0
37984 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-05-10 | 2001-05-10 17:30 | 2001-05-10 | AGREEMENT STATE REPORT - STOLEN RADIOGRAPHY DEVICE "On May 10, 2001, the Agency was notified by telephone that a truck containing a radiography device was missing and possibly stolen. SPEC 150, Camera #23, source serial number KB 0109, 40 curies iridium-192, cannot be located. The police found the truck, but the device was not inside. "The Agency is investigating." Incident 7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37983 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-05-10 11:10 | 2001-05-10 17:10 | 2001-05-10 | AGREEMENT STATE REPORT - STOLEN GAUGE CONTAINING RADIOACTIVE ISOTOPES A Troxler moisture density gauge (model #3440, serial #28940) was stolen from a truck parked at the Metric Engineering, Inc. office located at 13940 S.W. 136th Street, Suite 200, Miami, Florida 33186. The gauge contains 8 mCi Cs-137 and 40 mCi Am-241:Be. The gauge has been recovered. "Licensee states their inspector, Dylan Grove, reported the gauge was stolen from the back of his truck at 11:10 AM on this date at the above location. The lock securing the gauge to the vehicle was cut. The name and phone number of the licensee was displayed on the gauge. The licensee reported the theft to this office at 2:05 PM. At approximately 3:00 PM, the licensee reported the gauge had been returned to their SR 436 field office by an anonymous gentleman. The gauge was reportedly undamaged. This incident has been transferred to the Radioactive Materials section for further action. An inspection of the work site by a state inspector is scheduled for 11 May 01." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37982 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2001-05-09 14:00 | 2001-05-10 14:57 | 2001-05-10 | AGREEMENT STATE REPORT - IMPROPER RADIOGRAPHY OPERATION The Oregon Department of Health Radiation Protection shut down a radiography operation in North Portland at 1400 PDT on 5/9/2001 by Professional Services Industries (PSI). There were no operating survey instruments, the operators did not have alarming dosimeters, and warning signs were not posted. There was a 2-mR line set up at 6 feet from the 80-curie source. There will be an enforcement conference at 1300 PDT on 5/11/2001. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0
37981 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2001-05-09 15:00 | 2001-05-10 13:43 | 2001-05-10 | INADVERTENT FAILURE TO INCLUDE INDIVIDUALS IN RANDOM DRUG SCREENING POOL The licensee discovered that three individuals were inadvertently left out of the computerized list of individuals subject to random drug screening. Immediate compensatory actions have been taken. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | MD | POW |  | 26.73 |  |  |  | 0
37980 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2001-05-10 07:20 | 2001-05-10 08:08 | 2001-05-10 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY The licensee discovered that a contract employee falsified a personal history questionnaire resulting in unescorted access to the Protected Area being granted inappropriately for a period of 25 days. Immediate compensatory actions were taken upon discovery. (Contact the NRC operations officer for additional details.) The licensee submitted this notification in accordance with 10 CFR 73.71(b)(1); 10 CFR [Part] 73, Appendix G, paragraph I.b; and draft Regulatory Guide DG-5008 (RG 5.62), December 1997 The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0
37979 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-05-09 20:05 | 2001-05-09 21:53 | 2001-05-09 | MANUAL TURBINE TRIP - AUTOMATIC REACTOR TRIP Initiated manual turbine trip due to condenser vacuum differential pressure which resulted in an automatic reactor trip. Reactor power prior to the trip was 12.5%. The cause of the high condenser vacuum differential pressure is undetermined at this time. All control rods fully inserted, reactor coolant pumps are running. The steam generators are being fed with auxiliary feed. Decay heat is being removed by dumping steam with the turbine bypass atmospheric dumps. There are no known S/G tube leaks. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37978 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-05-09 15:06 | 2001-05-09 20:37 | 2001-05-09 | TECH SPEC REQUIRED SHUTDOWN Initiation of a unit shutdown began at 1700 May 9, 2001, as required by T.S. 3.7.B because Unit 2 Diesel Generators D5 and D6 were declared inoperable at 1506. They were declared inoperable because it was determined that they may not be capable of long-term operation as assumed in the plant accident analyses. This determination is based on the discovery that the diesel fuel and lubricating fluids in the engines may be incompatible and may damage the engines based on a re-review of industry operating experience. The plant will go to Mode 5 and remain their until corrective actions are complete. The licensee notified the NRC resident inspector. | 0 | 18 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37977 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-05-09 14:20 | 2001-05-09 16:23 | 2001-05-10 | FIRE PROTECTION REQUIREMENTS NOT MET It has been discovered that all necessary compensatory actions for inoperable fire barriers are not included in the stations operating procedures for conditions when the swing 125 VDC and 250 VDC battery chargers are in service supplying the 'B' DC Electrical subsystem. The required degree of separation per 10CFR50 Appendix R does not exist between divisions when either swing charger is connected to the 'B' DC Electrical subsystem. Use of the swing chargers is not a normal lineup but has occurred during the past three years. The uncompensated lack of an adequate fire barrier between divisions of safe shutdown equipment is considered an unanalyzed condition that significantly degrades plant safety. The licensee notified the NRC resident inspector. * * * UPDATED AT 2153 EDT ON 5/10/01 BY STEVE WHEELER TO FANGIE JONES * * * "The purpose of this follow-up is to clarify statements made in the original report. "The first statement in the report states that '....all necessary compensatory actions for inoperable fire barriers are not included in the station's operating procedures.' The only compensatory measures not included in procedures are those concerning providing a fire watch when the swing charger is in service. "With respect to the statement regarding 'uncompensated lack of an adequate fire barrier between divisions of safe shutdown equipment is considered an unanalyzed condition,' the condition exists only when the swing charger is in service and a fire watch has not been established. "The final statement concerning 'an unanalyzed condition that significantly degrades plant safety,' the District provides the following clarification. During the periods when no fire watch was established, no actual fire occurred in the fire area, no power was lost or interrupted and the batteries were functional." The licensee notified the NRC Resident Inspector. The R4DO (Jeff Shackelford) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37976 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-05-09 14:07 | 2001-05-09 14:45 | 2001-05-09 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY. IMMEDIATE COMPENSATORY ACTIONS TAKEN UPON DISCOVERY. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 0
37975 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-05-08 15:28 | 2001-05-08 19:24 | 2001-05-08 | REACTOR TRIP - LOW STEAM GENERATOR LEVEL On 05/08/2001, Unit 2 experienced a automatic Reactor Trip due to low water level in the 2A Steam Generator. Prior to the reactor trip, Instrument and Control Technicians were tuning the 2A Main Feed Water Regulating Valve digital control system. The 2A Main Feed Water Regulating Valve went fully closed, and the Control Room Staff was unable to reopen the valve. At the same time as the Reactor Trip, the Auxiliary Feed Water System actuated due to low water level in the 2A Steam Generator. After the Reactor Trip all Control Rods Fully inserted into the core, all automatic systems operated as designed, and no primary to secondary leakage was detected. The plant is stable in Mode 3, reactor coolant pumps are running and decay heat is being removed by using the main turbine bypass valves. Steam generator water level has been restored and main feed is being used to feed the steam generators. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37974 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2001-05-08 16:28 | 2001-05-08 18:56 | 2001-05-08 | SPECIFIED SYSTEM ACTUATION "With the plant in a refueling outage, during restoration of the CRD system, ongoing maintenance prevented restoring and opening the scram discharge volume vents and drains. Leakage slowly filled the scram discharge volume. At 1628, level reached the trip setpoint and initiated a RPS trip signal. This is considered a valid initiation signal. All systems responded as expected. No control rod movement occurred and no refueling operations were in progress. Scram has not been reset due to ongoing maintenance." The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37973 | 0 | HENRY FORD HOSPITAL |  |  |  |  | 2000-04-20 12:00 | 2001-05-08 14:10 | 2001-05-08 | MEDICAL MISADMINISTRATION Unintended deviation from a written directive in the use of an investigational temporary brachytherapy implantation device on 04/20/00. Device is the Proxima Therapeutics, GliaSite RTS (a 2-4 cm balloon catheter). The device is being investigated under the NABTT # 9801 Multi-center open label clinical study to evaluate the performance of the Proxima GliaSite RTS in patients with recurrent brain tumors undergoing surgical resection. In this study, the GliaSite RTS is implanted in the tumor resection bed at the time of surgery. Two weeks following surgery, a solution of lotrex and saline is infused into he balloon catheter in order to deliver the radiation dose. Following a specified dwell time, the lotrex is removed from the balloon and the balloon is then surgically removed from the patient's brain. Prior to therapy, radiographic contrast media is infused into the balloon to verify the balloon placement. This contrast media is removed just prior to the infusion to the lotrex. All fluid volumes are tracked to determine the exact volume of fluid in the balloon at all times. In the specific treatment plan where the deviation from the written directive occurred, was prescribed by a Radiation Oncologist and infused into a balloon by a Nuclear Medicine Physician with a dwell time of 70 hours. Following the prescribed dwell time the lotrex was removed and an initial assay of the retrieved lotrex demonstrated a 60% apparent reduction in retrieved activity as compared to the administered activity. The reduced activity measured in the retrieval fluid was to be due to a mixture of contrast media with the lotrex in the fluid. By diluting the retrieved fluid, to remove attenuation characteristics of the contrast media, the total administered activity was measured. Since the contrast media was causing attenuation of the radioactivity in the retrieved fluid, resulting in a reduction of the Dose Calibrator readings, it is assumed the radiation dose to the tissue surrounding the balloon was also reduced. The absorbed dose to the tissue cannot be determined accurately due to the uncertainty in the homogeneity of the iodine-125 and contrast media in the GliaSite RTS during the therapy. Therefore, the attenuation characteristics and absorbed energy within the tissue cannot be accurately modeled. During the investigation of this incident, all steps contained within the Henry Ford Hospital and NABTT #9801 Quality Management Programs were followed. This incident notification of the patient, physicians and all attending staff within 4 hours following the retrieval of the lotrex that an apparent discrepancy in the activity retrieved existed. In addition, all trash and urine were verified to have been retrained and surveys of these waste showed negligible readings. All room surveys also showed no contamination. The patient, as well as fluid retrained from the surgical site and the GliaSite RTS all demonstrated no contamination. The patient was not harmed by the event. To prevent contrast contamination during this therapy in the future an additional flushing of all fluid from the balloon prior to infusion of the lotrex will be done. The NABTT #9801 study is intended as a Phase 1 device trail rather than a clinical efficacy trail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0
37972 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2001-05-08 10:04 | 2001-05-08 12:44 | 2001-05-08 | TECH SPEC REQUIRED SHUTDOWN On 5/8/01, at approximately 1004, the Hope Creek Generating Station initiated a unit shutdown to comply with the provisions of Technical Specification (TS) 3.0.3, TS 3.0.3 was entered at 0820 when both trains of the Main Steam Line Isolation Valve Sealing System (MSIVSS) were declared inoperable. The 'B' MSIVSS had been inoperable since 5/4/01 due to a malfunctioning flow transmitter with the associated TS, 3.6.1.4 1 entered. On 5/8/01, at 0508, a Potential Transformer fuse failure associated with the 'C' Class 1E 4.16kV bus tripped two of four channels of Loss of Voltage relay protection for that bus. The tripped channels provide start permissives for the 'C' EDG and have actuated to the tripped condition to provide those permissives. During subsequent investigation of the extent and consequences of the fuse failure, it was determined at 0820 hours that the fuse failure also affected the 'C' Emergency Diesel Generator (EDG) synchroscope rendering the 'C' EDG inoperable due to its inability to meet the surveillance requirement of TS 4.8.1.1.2.h.10 Since the 'C' EDG provides the 1E power to the 'A' MSIV Sealing System both trains of the MSIV Sealing System were considered inoperable and TS 3.0.3 was entered. Investigation into the cause of the fuse failure is ongoing. With the exception of the 'A' Control Room Emergency Filtration System, all other safety-related systems were operable at the time of the event. The licensee notified the NRC resident inspector, the State of New Jersey and Lower Alloways Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37971 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2001-05-08 00:09 | 2001-05-08 01:52 | 2001-05-14 | REACTOR WAS MANUALLY SCRAMMED FROM 22% POWER DUE TO FAILURE OF RECIRC PUMP TO RESTART A manual scram was inserted at 0009 on 5/8/01. The scram was conducted in accordance with plant procedures, IOI-8 "Manual Scram," due to a failure of the reactor recirculation pump "A" to restart during a downshift from fast to slow speed operation. Plant response to the manual scram was as anticipated, all rods fully inserted, no ECCS actuations occurred and no SRVs opened. Reactor vessel water level reached Level 3 (177.7 inches) and operators entered the Plant Emergency Instructions. At 0016, the Plant Emergency Instructions were exited. The cause of the "A" recirculation pump failure to restart is being investigated. The NRC Resident Inspector was notified. * * * RETRACTION 1132 5/14/2001 FROM RUSSELL TAKEN BY STRANSKY * * * "A 10CFR50.72(b)(2)(iv), RPS Actuation, four- (4) hour non-emergency notification was initially made on 5-8-2001, due a Manual Reactor Scram while critical. The Shift Supervisor conservatively defaulted with the reportability determination and made the notification. Subsequently the plants corrective action program required a confirmatory review of the condition and its reportability by the staff. "The reportability review by the plant staff determined that the condition was not event driven since viable options were available. The options included: continue operation in single loop until the Recirculation Pump 'A' breaker was repaired and the pump restarted, shutdown by manually inserting control rods or enter Shutdown by Manual Scram, utilizing plant procedures IOI-4 and IOI-8 respectively. The operators followed IOI-8 which purpose is to provide general directions and guidelines for initiating a planned shutdown by a manual reactor scram. It is intended to be entered during a non-emergency condition with plant conditions stable. Use of this procedure requires prior approval of the Operation's Manager and was obtained. "After Operations reviewed the available options, it was concluded at management's discretion, that the plant would be shutdown to repair the Recirculation Pump 'A' breaker and the Recirculation Pump 'B' seal, via IOI-8. "The power plant was then configured for a controlled reactor scram in an orderly manner without delay. House electrical loads were shifted to the startup source: HPCS, which had been out of service for scheduled maintenance was made available to support the scram if required; the Motor Feed Pump was started and reactor level and pressure were adjusted to support the scram. Reactor pressure was raised to support performance of control rod scram time surveillance testing during the scram. "The reactor was scrammed on 5/8 at 0009 hrs. All equipment functioned as expected. The plant underwent a controlled cooldown resulting in RHR 'A' being placed in service just prior to 0800 hrs. The shutdown evolution as chronologically described below complied with plant procedures, license conditions, and Technical Specifications. License Commitments were reviewed for compliance, and no issues were identified. "Chronology "May 7, 2001 16:20 Start 101-3 power reduction for B33 'B' seal temperature. 17:22 Power reduction suspended while seal temperature stable. 19:42 Restarted 101-3 power reduction; B33 'B' seal at 200°F. 20:50 533 pump downshift incomplete. 'B' in slow; 'A' in off. 20:52 Enter ONI-51: B33 Pump 'A' tripped. Reactor Engineer contacted. Power 22%; Loop Flow 'B' 6.25%; B33 in Loop Manual. Technical Specification Power/Flow limits met w/o adjusting power or flow. 21:01 B33-F067A - closed per ONI. 21:10 B33-F067A - reopened per ONI. 22:16 Attempted restart of B33 'A' Pump. 22:46 Raised Reactor Pressure for scram testing. 22:51 House electrical loads transferred to Start-up Transformer. 23:49 Motor Feed Pump started for SCRAM. 23:55 HPCS In secured status with operator ready to place in standby if needed during SCRAM. "May 8, 2001 00:09 Manual SCRAM inserted per IOI-8, PEI-B13 entered on Level 3 as expected. 00:13 SCRAM Reset. 00:16 PEI-B13 Exited. "Subsequent review has determined that although a plant outage was determined to be the appropriate option, there was no urgency and sufficient planning was involved to ensure a controlled shutdown occurred. The determination concluded that this plant shutdown should be considered a pre-planned sequence and was performed at Management's discretion and oversight. The level 3 scram that occurred as part of he post Scram transient was an expected part of the preplanned sequence. Therefore, this condition is not reportable and ENF 37971 is retracted." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Shear). | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37970 | 0 | NEB DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2001-05-01 | 2001-05-07 16:22 | 2001-05-08 | AGREEMENT STATE REPORT The event took place at a coal plant where a nuclear gauge is installed on a coal chute. Not following established maintenance procedures led to workers entering the chute with the source exposed. A field of approximately 450 mr/hr was created. Whole body exposure was calculated based on a five hour stay time resulting in an estimate of 2.25 Rem for the most exposed individual. Two other individuals were involved with lower total exposure. The source involved is believed to be Cs-137 with an activity between 100 and 200 mCi. * * * UPDATE ON 05/08/01 AT 1429 ET BY JOHN FASSELL TAKEN BY MACKINNON * * * Four workers were exposed instead of three and all four of the workers were radiation workers for the Neb Public Power District. Calculated whole body radiation exposure to the four workers: 2250 mrem, 1361 mrem, 611 mrem, and 450 mrem. The whole body dose was based on total exposure time multiplied by the maximum measured rate at the beam port, 450 mrem/hr. The individuals were approximately one foot away from the beam port The operations center informed the R4DO (Shackelford) and NMSS EO (Hickey). * * * UPDATE AT 1300 EDT ON 5/11/01 BY JOHN FASSELL TO FANGIE JONES * * * Three of the workers have been determined to be members of the public and only one of the workers is a radiation worker. Further evaluation of the doses has been done with consideration to time motion study, geometry, surveys, and shielding by a utility company CHP. The radiation worker who was reported at 1361 mrem is now at 182 mrem. The workers (considered members of the public) reported at 2250 mrem is now at 285 mrem, reported at 611 mrem is now 87 mrem, and reported at 450 mrem is now 57 mrem. The R4DO (Jeff Shackelford) and NMSS (John Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37969 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2001-05-07 14:43 | 2001-05-07 15:23 | 2001-05-07 | MANUAL REACTOR TRIP - LOSS OF CIRCULATING WATER PUMP Operators manually inserted a reactor trip when a circulating water pump tripped. The "A" pump was out for maintenance with divers in the water bay. As a precaution for the safety of the divers, the travelling screens on the "B" water bay were stopped and tagged. Kelp started building up on the "B" traveling screens and the licensee pulled the divers from the water and restarted the "B" screens. As the screens started to move an increase in pressure across the screens and led to the pump trip. The plant response to the trip was normal all control rods fully inserted. The plant is stable in mode three. Reactor coolant pumps are running and decay is being removed by dumping steam to the main condenser (two circulating water pumps are still running). The licensee notified the NRC resident inspector, the State DEP and the town of Waterford. A press release is planned. | 0 | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37968 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-05-06 03:10 | 2001-05-06 06:02 | 2001-05-15 | MAIN TURBINE STOP VALVE FAILED TO CLOSE DURING TESTING The #4 main turbine stop valve failed to close during the performance of turbine valve testing procedure. Failure of the turbine valve to close affects the turbine stop valve closure scram function of both A&B reactor protection trip systems. Reactor power is currently being reduced to less than 45% power which is required when the minimum conditions for the turbine stop valve closure scram function are not satisfied. The licensee believes the cause of the problem is probably due to a bad solenoid valve. The NRC Resident Inspector will be notified. **** RETRACTION RECEIVED AT 1641 EDT ON 05/15/01 FROM PATRICK DECKER TO LEIGH TROCINE **** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "[...] On [05/06/01], we reported the failure to close of Main Turbine Stop Valve #4 during routine testing. Subsequently, it was learned that the failure affected the test circuit only and had no effect on the normal operation of the stop valve. Therefore, this event is not reportable. The test circuit failure has been corrected, and the Main Turbine Stop Valve #4 retested successfully." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Parker). | 73 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0
37967 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-05-05 15:23 | 2001-05-05 15:33 | 2001-05-05 | OFFSITE NOTIFICATION REGARDING DISCOVERY OF AN EMACIATED LOGGERHEAD SEA TURTLE IN THE INTAKE CANAL The following text is a portion of a facsimile received from the licensee: "[The licensee] notified [the] Florida Fish & Wildlife Commission of [the discovery of an] emaciated loggerhead sea turtle in need of rehabilitation. The State was notified @ 1523 hrs [on] 05/05/01." The licensee plans to notify the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37966 | 0 | UNIVERSITY OF PENNSYLVANIA |  |  |  |  | 2001-05-04 16:30 | 2001-05-05 11:51 | 2001-05-07 | DISCOVERY OF A BRACYTHERAPY MISADMINISTRATION INVOLVING A LEAKING IODINE-125 SOURCE AT THE UNIVERSITY OF PENNSYLVANIA IN PHILADELPHIA At approximately 1000 on 05/04/01, the licensee administered a prostate implant involving the 94 iodine-125 seeds on the order of about 1/2 millicurie per seed. (It is currently believed that the intended dosage for the patient was approximately 47 millicuries. The licensee reported that the intended dose is received from decay of the seeds which remain in the patient after treatment.) Surveys were performed after the administration, and one of the implant needles had readings that were higher than expected. At that time, it was assumed that a source was stuck in the applicable needle (a more likely scenario). However, at approximately 1630, removable contamination (due to a leaking source) was discovered on the applicable needle. It is currently believed that one of the seeds may have been damaged during the needle loading process, and that the damaged seed was implanted into the patient during treatment administration. At this time, there is only [one]complication that is expected as a result of the leaking iodine-125 source. It was reported that the activity from the leaking source could get into the blood stream and that the thyroid would filter the radio-iodine. Therefore, the patient may receive an unintended thyroid dose. The authorized user was notified, and the patient was informed. The patient was also prescribed Lugols solution (a potassium iodide solution) to minimize the unintended iodine-125 thyroid uptake from the leaking seed. Initial estimates indicate a thyroid activity measurement of 73 nanocuries. [Based on normal thyroid turnover, a dose of about 320 millirem is calculated to the thyroid.] The licensee plans to notify the referring physician. (Call the NRC operations officer for a licensee contact telephone number.) * * * UPDATE ON 5/7/01 @ 1059 FROM FORREST TO GOULD * * * This update was to make the event clear. The changes appear in the brackets[ ]. Notified Reg 1 RDO(Cook) and NMSS EO(Frant) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 35.33 |  |  |  | 0
37965 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2001-05-04 06:15 | 2001-05-04 13:40 | 2001-05-16 | AGREEMENT STATE REPORT REGARDING A STOLEN TROXLER GAUGE The following text is a portion of a facsimile received from the Nevada Health Division Radiological Health Section regarding a Significant Event Report: "1. Event Report ID No. [-] NV-01-02" "2. License No. [-] 00-11-0255-01" "3. Licensee [-] Las Vegas Paving" "4. Event time, date, location [-] 6:15 a.m., May 4, 2001, 7/11 Convenience Store, Losse & Cheyene Road, North Las Vegas, Nevada." "5. Event type (e.g., misadministration, lost source, overexposure, etc.) [-] Theft of Troxler Model 4640B portable gauge." "6. Any notifications i.e., other agencies, patient, press release, FBI, etc. [-] North Las Vegas Police Dept. notified by licensee." "7. Event description: release, isotope, activity, exposure(s), dose, contamination level, equipment malfunction, model, serial No., etc. [-] Chain securing Troxler Model 4640B gauge to pickup bed was cut, and gauge was stolen from licensee's truck while gauge user was in [convenience] store. Gauge is a Troxler Model 4640B, s/n 1658." "8. Transport vehicle description if known [-] Pickup truck." "9. Media attention [-] N/A" (Call the NRC operations officer for State contact information.) *** UPDATE (FAX) RECEIVED AT 1228 EDT ON 05/15/09 FROM LARRY BOSCHULT TO LEIGH TROCINE *** The following text is a portion of a facsimile received from the Nevada Health Division Radiological Health Section: "The licensee recovered the gauge May 10, 2001. The gauge was found by a pedestrian. They saw the licensee's phone number on the gauge and called them. The licensee immediately retrieved the gauge. The lock on the gauge transport case was broken, but the gauge was still locked. The gauge has been leak tested and placed in storage pending the outcome of the leak test." The NRC operations officer notified the R4DO (Spitzberg) and NMSS EO (Hickey). (Call the NRC operations officer for State contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0
37964 | 0 | 3M COMPANY |  |  |  |  | 2000-10-22 | 2001-05-03 14:06 | 2001-05-03 | 3M COMPANY REPORT REGARDING A W. L. GORE FACILITY LOSS OF A STATIC ELIMINATOR CONTAINING 10 MILLICURIES OF POLONIUM-210 On 09/12/00, 3M Company (located in St. Paul, Minnesota) announced its intent to purchase W. L. Gore (located in Eauclaire, Wisconsin). The acquisition took place during late October or early November 2000. On 03/14/01, 3M Company representatives visited the newly acquired W. L. Gore facility and discovered the existence of static eliminators. An audit was subsequently performed, and 3M Company was able to account for all but one static eliminator. Apparently, the W. L. Gore facility received the polonium static eliminator in question on 08/10/00. This static eliminator was manufactured by Nuclear Radiation Development (NRD), and it was comprised of an in-line ionizer tube approximately 4 inches long and 1/4 inch in diameter with 10 millicuries of polonium-210 plated on the inside of the device. The static eliminator was installed on a large circuit substrate manufacturing machine for use in the W. L. Gore facility under the NRD general license (1429-1811GL). On 09/06/00, the circuit substrate manufacturing machine was sent back to its manufacturer (Everrett Charles) for an upgrade. The static eliminator was reported to be on the machine when it was shipped to Everrett Charles (location unknown); however, the static eliminator was determined to be missing after Everrett Charles returned the upgraded machine to W. L. Gore on 10/22/00. Everrett Charles was notified of the missing static eliminator during the week of 04/09/01. NRD was also notified during the week of 04/16/01. It was reported that searches were performed, but the missing static eliminator was not found. (Call the NRC operations officer for a 3M Company contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37963 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-03-12 00:30 | 2001-05-03 13:36 | 2001-05-03 | ACTUATION OF DIVISION 1 BALANCE-OF-PLANT OUTBOARD ISOLATION VALVES - INVALID SYSTEM ACTUATION The following text is a portion of a facsimile received from the licensee: "On March 12, 2001, at approximately 0030 hours, the Perry Nuclear Power Plant experienced an actuation of Division 1 Balance-of-Plant (BOP) outboard isolation valves. At the time of the event, the plant was in Mode 5 (Refueling), and had been subcritical for approximately 23 days. The reactor pressure vessel (RPV) head was removed and the refuel cavity and upper containment pools were flooded; no core alterations were in progress at the time. Shutdown cooling was being provided by the Fuel Pool Cooling and Clean-up system (FPCC), which was aligned to the upper containment pool. The isolation signal closed one or more valves in each of the following Division 1 subsystems: FPCC, Containment Drywell purge, Two-Bed Demineralized Water System, Fire Protection, Liquid Radwaste Sumps, Liquid Radwaste Disposal, Instrument Air, Containment Vessel Chilled Water, Condensate Transfer and Storage. In addition, the isolation signal caused a temporary interruption of shutdown cooling flow through the FPCC system, until it was re-established by on-shift Operations personnel." "The event is considered an invalid system actuation, and is reportable under 10 CFR 50.73(a)(2)(iv)(A). The isolation was not initiated in response to actual plant conditions or parameters, and was not a manual initiation. It meets the criteria specified in 10 CFR 50.73(a)(2)(iv)(B)(2) as a general containment isolation signal affecting containment isolation valves in more than one system. Therefore, notification is being provided via 60-day optional phone call in accordance with 10 CFR 50.73(a)(1). All systems functioned as expected for a partial BOP (outboard) isolation." "The interruption of shutdown cooling lasted for 111 minutes, from 0030 hours to 0221 hours on March 12, 2001. During this time, the reactor water temperature increased approximately 3 degrees, from 99 to 102 degrees. The estimated time to boil was conservatively calculated at 28 hours. The affected Fire Protection (drywell CO2) isolation valve was not required to be open, since the fire-protected equipment was secured during the refueling outage. Repositioning of the other valves did not present operational concerns; they were re-opened per restoration procedures. The cooling flow path was available immediately with manual operator action." "The BOP isolation was attributed to scheduled maintenance activities being conducted in the Control Room. The replacement of a bayonet-socket-style relay caused two fuses to blow in the BOP manual initiation logic circuit. The apparent cause was an inadvertent ground from the seismic strap of the new relay during installation that resulted in the required logic for the isolation." "This event was documented in the Corrective Action Program. Remedial actions include review of the event with instrumentation and control technicians, and evaluation of depowering valves which could interrupt shutdown cooling during maintenance activities." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Startup | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0
37962 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-05-03 07:00 | 2001-05-03 09:54 | 2001-05-03 | LOCAL LEAK RATE FAILED At 0700, on 05/03/01, the Control Room was informed that the HPCI Steam Exhaust Check Valves, V23-3 & V23-4, failed their local leak rate test such that the minimum pathway leakage rate was exceeded, greater than 193.674 scfh which is in excess of 0.6La Tech Spec limit. The valves were declared inoperable and repairs are underway. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37961 | 0 | ABB POWER DISTRIBUTION |  |  |  |  | 2001-05-02 | 2001-05-02 16:29 | 2001-05-02 | "NOTIFICATION OF POTENTIAL DEFECT PER 10 CFR 21 K-LINE CONTROL DEVICE CLOSE COIL HAIRPIN RETAINER "On 01/25/01, Grand Eagle Service reported a failure to close of K-Line circuit breaker during 'as found' service testing due to a malfunctioning replacement control device. The cause of the malfunction was determined to be the use of an inadequate hairpin retainer in the control device. Specifically, the retainer on the close coil armature pivot pin becomes dislodged from its slot allowing the pin to wander from the proper position inside the armature. "The cause of this failure was determined to be a design change oversight. In November of 1998, Engineering Change Notice number 5319 was issued specifying a change from hairpin retainer part number 53152C00 to part number 53152D00 in K-Line 708392T## series Control Device assemblies. This change was made in the interest of ease of assembly. For the purpose of this notice, this issue affects only K-Line circuit breakers which have a mechanical 'black box' control device containing an internal close coil. "Corrective action for this incident has been taken. On February 16, 2001, ECN number 5999 was issued reversing the 1998 change and specifying the use of Hairpin Retainer part number 53152C00. All control device Assemblers and Team Leaders were informed of the ECN and trained on the use the correct hardware. All of the D type retainers were removed from the control device assembly station and replaced with the C item. Additionally, all applicable control devices in the manufacturing facility, either installed in production or completed circuit breaker units or in component stock, were pulled and reworked. "This report of defect, once again, is only applicable to K-Line Type circuit breakers with a mechanical Control Device containing an internal close coil purchased between November 1998 and February 15th, 2001. All circuit breakers containing the defective control device are subject to this failure mode. Those control devices should be repaired or replaced as soon as feasibly possible. "This Part 21 report is the second report regarding mechanical Control Devices that has been issued in the last six months. All replacement control devices ordered as a result of the Part 21 report dated December 20, 2000 are subject to this defect if shipped from the Florence, South Carolina manufacturing facility prior to February 16th, 2001. "ABB will notify all customers who purchased this product." HOO NOTE: See previous report #37663. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | SC | OTH | PAR | 21.21 |  |  |  | 0
37960 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-05-01 15:31 | 2001-05-02 14:50 | 2001-05-02 | 24-HOUR OPERATING LICENSE NPF-12, SECTION 2 REPORT DUE TO EXCEEDING LICENSED POWER LIMIT "V. C. Summer Station experienced a plant transient as a result of a feedwater heater level transmitter failure. The transient resulted in core power exceeding licensed limit of 2900 megawatts thermal (MWT) at 1531 hours on May 1, 2001. Preparations were underway to reduce power when the feedwater heaters were reset and power stabilized at less than 2900 MWT. The duration of the transient was less than seven minutes. "The loss of feedwater heater string resulted in a lowering of steam generator feedwater supply temperature and subsequent drop in reactor coolant system Tcold (cold leg temperature). "Subsequent investigation by Engineering and Independent Safety analyses Group personnel indicated core power reached 102.7% of maximum power as indicated by core differential temperature (delta T). Core delta T was determined to be the most reliable indication of core power during this transient. " The cause of the feedwater heater level transmitter failure is currently under investigation. No automatic load reduction or other safety actuation occurred." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0
37959 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-05-02 12:55 | 2001-05-02 13:20 | 2001-05-02 | OFFSITE NOTIFICATION TO THE FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION INVOLVING AN INJURED LOGGERHEAD SEA TURTLE FOUND IN THE INTAKE CANAL "At approximately 11:15 A.M. on 5/2, an injured Loggerhead Sea Turtle was recovered from the plant's intake canal. The Turtle was alive and will be sent to a rehabilitation facility for care as required by the plant's Sea Turtles permit. The Florida Department of Environmental Protection was notified of the event. The notification of the DEP necessitates a 4-hour phone call to the NRC per 50.72 (b)(2)(xi)." The licensee informed the NRC resident inspector. | 50 | 100 | 0 | 50 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37958 | 0 | CALUMET TESTING SERVICES INC. |  |  |  |  | 2001-05-02 04:30 | 2001-05-02 09:18 | 2001-05-02 | AMERSHAM RADIOGRAPHY CAMERA DRIVE CABLE BROKE OFF Radiographers from Calumet Testing Services Inc., out of Griffith, Indiana, were taking radiography shots at NIPSCO Electric Generating Station located in Michigan City, Indiana. They were using an Amersham A424-9 radiography camera with a 660B exposure device. The radiography camera contains a 90 curie Iridium-192 source. The end of the drive cable broke off at the tip. The Radiographer and his assistant placed lead shielding over the tube containing the source. The Radiation Safety Officer (RSO) was informed of this incident and he took extra lead shielding and a extra crank out to the site. On arrival to the site the RSO had extra lead shielding placed over the source. The back of the camera was removed and a 6 to 8 foot retrieval device was used to pick up the exposure tube and drop the source out the front of the tube. The retrieval device then was used to retrieve the source and place it in its stored position in the camera. The RSO stated that this is the second time in the last couple of years where the end of the drive cable has broken off. Film badges of the individuals that were exposed to the source will be read later today. The estimated exposure to the following individuals were taken from their pocket dosimeters: radiographer received 200 millirems, radiographer assistant 40 millirems, person who retrieved the source exposure was 200 millirems and the RSO received 10 millirems. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0
37957 | 0 | WATERFORD | 3 |  |  | [3] CE | 2001-05-01 17:00 | 2001-05-01 20:22 | 2001-05-01 | UNANALYZED CONDITION DUE TO INADEQUATE FIRE PROTECTION INVOLVING POWER SUPPLIES FOR EDG FUEL OIL TRANSFER PUMPS "During a review of the site Appendix R program, W3 [Waterford 3] Engineering personnel discovered that the power supplies to both of the Emergency Diesel Generator Fuel Oil Transfer Pumps were not protected in accordance with 10CFR 50 Appendix R. The 480V power cables for both trains were found unprotected in Fire Area RAB 27. A fire in this room could potentially damage both Emergency Diesel Generator Fuel Oil Transfer Pumps power supply cables and would then impact the amount of time the Emergency Diesel Generators could operate. Due to the fire barriers missing on the above equipment and not providing the required amount of separation of safe shutdown trains, this condition is considered an unanalyzed condition that significantly degrades plant safety. This condition is reportable under 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "As a compensatory action fire watches have been established for the affected area in accordance with the site Technical Requirements Manual." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37956 | 0 | HAMOT MEDICAL CENTER |  |  |  |  | 2001-04-26 15:00 | 2001-05-01 14:28 | 2001-05-01 | PATIENT RECEIVED ONLY 110 OF THE 150 MILLICURIES I-131 PRESCRIBED DUE TO TECHNICIAN ERROR A patient undergoing treatment for thyroid cancer was prescribed a dose of 150 millicuries of I-131. The nuclear pharmacy dispensed the dose in three capsules which was confirmed by assay at the hospital. The technician administered the dose at approximately 1500EDT on Thursday, 4/26. The empty container was returned to the nuclear pharmacy on Friday, 4/26. Upon inspection of the returned container on Monday, 4/30, pharmacy personnel found a capsule containing approximately 40 millicuries I-131 stuck inside. The on-staff radiologist and patient were informed. The patient will be monitored for the next six months and a decision involving any additional treatment will be made at that time. The prescribing physician will be informed of the misadministration by the radiologist. The administering technician was administratively disciplined and the issue of delivering dose will be addressed as a training item. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0
37955 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-08 08:45 | 2001-04-30 12:54 | 2001-04-30 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION CAUSED BY SETPOINT DRIFT "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of a specific system, namely Primary Containment Isolation System (PCIS). "On March 8, 2001 at 08:45 hours the main control room received a 2A Uninterruptible Power Supply (UPS)/Reactor Protection System (RPS) trouble alarm and verified the following Engineered Safety Features (ESF) isolations: Drywell Chilled Water (DWCW), Reactor Enclosure Cooling Water (RECW), Instrument Gas and Containment Leak Detector. "The control room also received an electro-hydraulic control (EHC) electrical malfunction alarm with a loss of cooling fans and inaccurate indication of stop valve and combined intercept valves. Additionally, some cabinet fans, 60 Hz solenoid valves and the bypass jack were also lost. "These expected isolations were bypassed by procedure for the given condition, and were subsequently restored to their normal operating position. The isolations were due to an invalid signal resulting from the failure of a circuit board trim potentiometer for the undervoltage relay (27-AY24801) of the 2A RPS breaker (2A-C248-52). Failure analysis of the undervoltage relay (ABB Model No. 211T4175F) identified that the trim potentiometer was heat sensitive (manufacturing defect) which caused the relay setpoint to drift up to the actual line voltage, tripping the breaker. "The 2A RPS undervoltage relay was replaced and the isolations were reset at 15:39 hours. "The impact on the plant from this event was minimal. The selective isolations and equipment losses during the transient did not result in a plant transient, and the equipment performed as expected. "This event has been entered into the site-specific corrective action program for resolution and generic implications. Industry operational experience (CE) and vendor database searches identified no related issues for this model relay. "The NRC site resident has been informed." | 0 | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0
37954 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-04-30 11:00 | 2001-04-30 11:38 | 2001-04-30 | PLANT LOST BOTH COMMERCIAL AND ENS PHONE SYSTEMS The plant lost both their commercial and ENS phone systems due to a fiber optics cable cut. Ameritech is currently troubleshooting and they do not know at this time when service will be restored. The licensee has microwave communication available. They have verified communications with other agencies. The NRC Resident Inspector was notified. * * * UPDATE 1702EDT ON 4/30/01 FROM MILLER TO S. SANDIN * * * "At 1100 on 4/30/01 The Emergency Notification System (ENS) and the commercial telecommunications capability to dial offsite was found to be non-functioning. Communications with outside agencies has been verified through the microwave transmission lines (RERP Lines). The cause is being attributed to a problem with an offsite fiber optics cable and an investigation is underway by the local telecommunications company. The ENS and commercial telecommunications lines were verified functional at 1650." The licensee informed the NRC resident inspector. Notified R3DO(Leach) | 48 | 0 | 0 | 46 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37953 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-04-29 22:50 | 2001-04-30 02:24 | 2001-04-30 | EXPECTED LOSS OF SPDS FOR GREATER THAN 8 HOURS Planned maintenance removed safety parameters display system (SPDS) from service for greater than 8 hours. This requires a notification per 10 CFR 50.72(b)(3)(xiii) for loss of assessment capabilities. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37952 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2001-04-29 11:28 | 2001-04-29 12:19 | 2001-04-29 | TURBINE TRIP - REACTOR TRIP The loss of a circulating water pumped led to a turbine trip and reactor trip. All rods inserted after the trip and the plant is stable in mode 3. Reactor coolant pumps are running and the steam generators are being fed with the mainfeed system. The main condenser is available for decay heat removal. One steam generator safety valve may have lifted during the transient, but is closed now. The cause of the circulating water pump trip is unknown. The licensee informed the NRC resident inspector as well as State and local governments. * * * UPDATE AT 1715 ON 4/29/01 BY FRANKS RECEIVED BY WEAVER * * * This update corrects the time of the event from 1151 to 1128. There was also a specified system actuation after the trip. Two auxiliary feedwater pumps started after the trip on low steam generator level. Once level was restored the pumps were secured. The licensee notified the NRC resident inspector. The operations center notified R1DO (Silk). | 0 | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37951 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-04-29 00:50 | 2001-04-29 03:18 | 2001-04-29 | MANUAL SCRAM DUE TO DEGRADING VACUUM CONDITIONS The licensee had reduced power to 16% and removed the main generator from service due to a stator water leak on the generator exciter causing a ground. After the main generator was off line vacuum started deteriorating and the reactor was manually scrammed. All rods fully inserted and all systems functioned normally. The plant is presently using the reactor core isolation cooling (RCIC) system for makeup and the safety relief valves to the suppression pool for decay heat removal. The cause of the deteriorating vacuum condition is under investigation. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0526 EDT ON 4/29/01 BY TOM VEITCH TO FANGIE JONES * * * The plant is using RCIC for pressure control and the motor driven feedpump for makeup to the reactor coolant system. Also, at 0116 EDT there was an automatic main steam valve isolation due to the deteriorating vacuum condition, an expected action. This is reportable under 10 CFR 50.72(b)(3)(iv)(B) as an 8 hour report. The licensee notified the NRC Resident Inspector. The R3DO (Thomas Kozak) was notified. * * * UPDATE AT 1641 ON 4/29/01 BY TODD HENDERSON TO DOUG WEAVER * * * At approximately 0215 on 04/29/2001, the Main Steam Isolation Valves closed automatically as a result of the continued loss of vacuum. In a 0530 update to the original notification, this isolation was reported as a specified system actuation in accordance with 10 CFR 50.72 (b)(3)(iv)(A). In that update, the time of the actuation was originally reported as 0116 on 04/29/2001. At approximately the same time, Reactor Core Isolation Cooling (RCIC) was started to assist with pressure control. At 0227, main condenser vacuum was broken. At 0247, a Safety Relief Valve (SRV) was opened and closed to control pressure, with the motor driven feed pump supplying feedwater. Approximately 2 minutes after the first SRV was cycled, a High Pressure Core Spray (HPCS) RPV Level 2 (130" above the top of active fuel) initiation signal was received which started the HPCS pump and Division 3 emergency diesel generator. No injection to the RPV occurred (or should have occurred) because reactor level was above the level where injection was required (Level 8 219" above the top of active fuel). A Division 2 Balance of Plant isolation signal and Redundant Reactivity Control System Level 2 also occurred at this time (with expected plant response including the tripping of both Recirculation pumps). The source of this signal has not yet been determined. At approximately 0430, a Reactor Pressure High/Drain Temperature Low alarm was received, indicating thermal stratification in the reactor pressure vessel due to the loss of reactor recirculation. This originally delayed placing shutdown cooling in operation, but the condition has been cleared allowing progress toward initiating shutdown cooling. The plant is currently in mode 3, with reactor level and pressure being maintained with periodic cycling of Safety Relief Valves and operation of RCIC. Residual heat removal (RHR) train 'B' is being used for suppression pool cooling. Actions are in progress to place RHR train 'A' in shutdown cooling, and bring the plant to Mode 4. The Senior Resident Inspector has been informed of the event. The operations center notified the R3DO (Kozak). | 0 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37950 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-04-28 16:00 | 2001-04-28 21:10 | 2001-04-28 | UNANALYZED CONDITION - BORON RESIDUE ON REACTOR VESSEL HEAD PENETRATIONS Preliminary reactor head visual inspection indicates a small amount of boron residue surrounding four control rod drive mechanism head penetrations. These indications are similar to those previously reported for unit one and unit three. Additional inspection will be performed to determine the cause of identified boron accumulation. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37949 | 0 | MONTANA DEPT OF TRANSPORTATION |  |  |  |  | 2001-04-27 12:00 | 2001-04-27 22:50 | 2001-04-27 | DAMAGED TROXLER GAUGE A Troxler moisture/density gauge model 3440 was run over on a construction site. The gauge contains 8 mCi of Cs-137 and 40 mCi of Am-241. The serial number of the gauge is 20993. The gauge was not seriously damaged. The gauge was surveyed for contaminated and none was found. The gauge has been removed from the job site and placed in storage pending further action. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | MT | MAT | [5 empty] | 0
37948 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2001-04-27 14:51 | 2001-04-27 17:13 | 2001-04-27 | REACTOR SCRAM UNIT 3 scrammed on low reactor water level (+8") due to flow and power oscillations from 3B reactor recirculation pump. The 3B recirculation motor generator set could not be tripped from the main control room and was tripped locally. All rods fully inserted during the scram. The unit is currently stable in mode 3. There were no ECCS injections nor did any SRVs lift. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37947 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2001-04-26 17:45 | 2001-04-26 22:26 | 2001-05-21 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM (CREFS) INOPERABLE The licensee entered a 7 day LCO when high vibrations were noticed on the booster fan. The fan was declared inoperable and led to CREFS being declared inoperable since it is a single train system. Licensee intends to repair the system prior to expiration of the LCO. The licensee notified the NRC resident inspector. * * * RETRACTION ON 05/21/01 AT 1140 ET BY D. VANDERKAMP TAKEN BY MACKINNON * * * A subsequent engineering evaluation of the fan motor bearings concluded that the motor, even though noisy with elevated vibration levels, was capable of performing it's support role in the Control Room Emergency Filtration System safety related function as required per Technical Specifications. Therefore, this event is being retracted. R4DO (Mark Shaffer) notified. The NRC Resident Inspector will be notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37946 | 0 | DELAWARE EMERG MANAGEMENT AGENCY |  |  |  |  | 2001-04-26 | 2001-04-26 17:36 | 2001-04-26 | RECOVERY OF TROXLER GAUGE The Delaware Emergency Management Agency (DEMA) reported the recovery of what appears to be a Troxler moisture density gauge. The gauge was recovered in New Castle, DE just off of I-95. The gauge appears to be intact with the source in the shielded position. No model or serial numbers were available. DEMA requested NRC assistance to remove the gauge. The gauge is isolated pending resolution. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | DE | MAT | [5 empty] | 0
37945 | 0 | CROWE BUTTE RESOURCES |  |  |  |  | 2001-04-26 11:30 | 2001-04-26 15:29 | 2001-04-26 | LEAK IN BRINE POND LINER The licensee has confirmed a leak in the pond liner based on an increase in the conductivity of the water between the inner and outer liners (the leak is in the inner liner). No release to the environment has occurred. The licensee believes the leak is small based on the increase in conductivity with only a small accompanying increase in water level in the area between the liners. The licensee will pump down the pond and attempt to find and repair the leak. This could take one to two weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MINING EVENT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37944 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2001-04-25 16:22 | 2001-04-25 18:27 | 2001-04-25 | The Washington county Emergency Response (911) was called to report a grass fire Northwest of the plant. The fire was outside the owner controlled property. The fire was reported as extinguished at 1720 CT. Site fire brigade was not assembled. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37943 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-04-24 16:00 | 2001-04-25 17:28 | 2001-04-25 | STOLEN CPN MOISTURE DENSITY GAUGE Geo Technical Exploration Inc., on 04/24/01 at 1600 PT reported to the State of California Radiation Control Program that a CPN Model 3 moisture density gauge had been stolen from the back of a truck probably on the evening of 04/19/01. The CPN gauge was in its manufacturer case and chained to the truck. The CPN gauge was discovered missing on the morning of 04/24/01 by the licensee. The San Diego Police were notified of the theft and a reward has been offered for the recovery of the CPN gauge. The serial number for the stolen moisture density gauge is M30069611. The gauge contained between 8 to 10 millicuries of Cesium-137 and between 20 to 30 millicuries of Americium-241. The State of California case assignment number is 042401. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37942 | 0 | SPEC GROUP HOLDING |  |  |  |  | 2001-04-25 05:40 | 2001-04-25 15:56 | 2001-04-25 | AMERSHAM INDUSTRIAL RADIOGRAPHY CAMERA SOURCE FAILS TO RETRACT. In Maidsville, West Virginia, this morning around 0540 ET an Amersham industrial radiography camera source failed to retract into its shielded position. The crank assembly, the remote handling part of the industrial radiography camera, has a lock on the crank assembly. After the radiographer had cranked the source out he placed the crank down and the lock tumbler went in and locked the control cable. After the shot had been taken the radiographer put the key in and pulled the lock assembly out but it failed to release the control cable which prevented the source from being retracted to its shielded position. While still at the controls the radiographer unscrewed a couple of threads on the control cable and manually pulled the 75 curie Iridium-192 source back to its shielded position. The radiographer picked up an additional 30 mrems due to manually pulling the source back to its shielded position. The licensee tagged the camera and ordered new equipment from Amersham to repair the camera. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0
37941 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-04-24 02:06 | 2001-04-24 03:23 | 2001-04-24 | DECLARATION OF AN UNUSUAL EVENT DUE TO A SMALL DEBRIS FIRE ON A STEAM GENERATOR PLATFORM DURING THE PERFORMANCE OF EDDY CURRENT TESTING At 0148 CDT, the control room was notified of a fire in the Unit 1 containment. It is currently believed that a problem with eddy current testing equipment (possibly an electrical fault) resulted in a fire involving a small pile of debris on the 8-foot elevation steam generator 'A' platform. The fire brigade was dispatched immediately, and the fire was extinguished within 2 to 3 minutes of the time the extinguishing agent (water) was applied. Offsite assistance was not required. At 0211 CDT, a second team provided the control room with a confirmatory report that the fire had been successfully extinguished. There were no reports of injuries or the spread of contamination as a result of the fire. The exact time the extinguishing agent was applied to the fire was not known at the time of this event notification. Because the exact duration of the fire (i.e., less than or greater than 10 minutes) was not known, the licensee declared an Unusual Event at 0206 CDT as a conservative measure. At the time of this event, Unit 1 was defueled, and Unit 2 was operating at 100% power. The licensee notified Manitowac and Kewaunee Counties, the Sate of Wisconsin, and the NRC resident inspector. ***** UPDATE AT 0343 EDT ON 04/24/01 FROM MIKE MEYER TO LEIGH TROCINE ***** The licensee terminated the Unusual Event at 0243 CDT. The licensee plans to notify Manitowac and Kewaunee Counties, the Sate of Wisconsin, and the NRC resident inspector. The NRC operations officer notified the R3DO (Kozak), NRR EO (Richards), IRO (Mamish), and FEMA (Canupp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37940 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-04-23 20:12 | 2001-04-23 21:35 | 2001-04-23 | LOSS OF ALL ANNUNCIATORS IN THE MAIN CONTROL ROOM At 2012 CT, the licensee entered an Unusual Event per EAL 4.1.2, unplanned loss of most or all safety system annuncuators. Plant computer remained on line but will not give alarms. I&C Technicians have been called in to investigate. All emergency core cooling systems are fully operable, and the electrical grid is stable. The licensee notified state and county officials that they had entered an Unusual Event. "Initial indication of loss of annunciators was received via annunciator 'Annunciator System Trouble.' Abnormal Procedure 2.4.8.2, 'Annunciator Failures,' was entered, and the determination was made that all annunciators in the Main Control Room [were] lost." The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 04/23/01 AT 2211 ET BY S. JOBE TAKEN BY MACKINNON * * * Unusual Event Terminated at 2105 CT. "At 2105 [CT,] the Emergency Director exited the EAL when the Main Control Room Annunciator System 'A' was restored by re-booting the Ronan System for the Main Control Room." State and Local officials were notified that the Unusual Event was exited. The NRC Resident Inspector will be notified of this update by the licensee. The NRC operations center notifications were the same as the above. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37939 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2001-04-21 14:54 | 2001-04-21 19:17 | 2001-04-21 | UNEXPECTED AUTOMATIC REACTOR SCRAM DURING TURBINE CONTROL VALVE TESTING During plant start-up from forced outage 01-01, with the plant at 58% power, an automatic reactor scram occurred. The scram occurred during the main turbine control valve testing due to an apparent turbine pressure control system malfunction. Automatic reactor scram occurred at the RPV High Pressure Scram Setpoint. All other systems functioned as expected during and after the transient. The unit is currently stable in Mode 3, Hot Shutdown, with reactor pressure and level within normal bands. Investigation in progress to determine cause of malfunction. Safety Relief Valves opened and closed during the transient. All Emergency Core Cooling Systems are fully operable and the electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 58 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37938 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-04-21 08:53 | 2001-04-21 10:19 | 2001-04-21 | UNANTICIPATED AUTOMATIC MAIN STEAM ISOLATION VALVE (MSIV) CLOSURE AND REACTOR WATER CLEANUP [RWCU] SYSTEM ISOLATION DUE TO LEVEL RACK REFERENCE LEG NOTCHING The following text is a portion of a facsimile received from the licensee: "During cooldown of the reactor vessel with all rods fully inserted, the [MSIVs] automatically closed in response to a reactor high level concurrent with low reactor pressure (main steam line pressure <810 with reactor level at +55.4 inches). Reactor pressure was at 100 psig when the isolation occurred. Approximately 1 hour later, another level perturbation occurred resulting in automatic isolation of the [RWCU] system and the inboard MSIV drain valve. The level perturbations are occurring in the 'A' train level rack only. It appears to be caused by non-condensable gasses coming out of solution in the 'A' level rack reference leg (notching). The 'A' train water level indication system is considered to be inoperable, and the applicable [limiting condition for operation] actions have been taken." The licensee stated that a planned reactor scram was performed prior to this event in order to facilitate commencement of a scheduled refueling outage. Apparently, the RWCU system isolation resulted from a spurious low level signal to the actuation system when the reference leg was being back filled. This was reported to be so quick that it was not seen on any control room instruments. The RWCU system has been placed back in service and is being used for level control. The MSIVs are still closed, but the isolation signal has been reset. However, the notching phenomenon is still being experienced. The licensee plans to change the decay heat removal path from the main steam system and place the RCIC system in test mode. As the reference leg is back filled and flushed out, the licensee plans to plan to go back to utilization of the main steam system. The NRC resident inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0
37937 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2001-04-21 03:20 | 2001-04-21 07:02 | 2001-05-14 | UNIT 2 HPCI INOPERABLE DUE TO FAILED TURBINE EXHAUST LINE VACUUM BREAKER CHECK VALVES The following text is a portion of a facsimile received from the licensee: "At 0320 [CDT] on April 21, 2001, Unit [2] HPCI was declared inoperable when two check valves failed to meet acceptance criteria during the performance of [procedure] QCOS 2300-18, HPCI STEAM EXHAUST VACUUM BREAKER LINE CHECK VALVES IST FUNCTIONAL TEST. Two of the four HPCI turbine exhaust line vacuum breaker check valves were found to have failed to close. The exhaust line containing the failed check valves was isolated at the start of the surveillance using motor-operated isolation valves contained in the exhaust line. The failed check valves remain isolated." The licensee stated that Unit 2 is in a 14-day limiting condition for operation as a result of this issue. The licensee notified the NRC resident inspector. ***** RETRACTION RECEIVED AT 1829 EDT ON 05/14/01 FROM TOM OSELAND TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "We have completed our evaluation and have determined that the HPCI [system] was always capable of performing its intended safety function." "BACKGROUND" "On 4/21/01 at 0116 hours [CDT], plant operators began surveillance QCOS 2300-18, 'HPCI Steam Exhaust Vacuum Breaker Line Check Valves IST Functional Test.' The surveillance test is performed to confirm that valves 2-2399-64 and 2-2399-65 open and close by applying air pressure to the check valves. During the test, these valves were found to meet the acceptance criteria in the open direction. The function of these valves is to open to provide a flow path from the suppression chamber to the HPCI turbine steam exhaust piping to prevent a vacuum. Following HPCI operation, the steam condensing in the suppression pool and exhaust line would cause the suppression pool water to be drawn up the exhaust piping." "At 0320 hours [CDT], the station equipment operator performing the test indicated that the 2-2399-64 and 2-2399-65 valves failed to close. These valves must close during HPCI operation to prevent steam flow from the HPCI turbine steam exhaust piping to the suppression chamber. Station operators declared the HPCI system inoperable when the test revealed that these valves did not close. Subsequently, operators initiated an ENS phone call to the NRC in accordance with the Exelon reportability manual SAF 1.8, 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function' (10CFR50.72(b)(3)(v))." "Repairs were initiated, and at 1806 hours [CDT] on 4/21/01. Following repairs, the HPCI vacuum breaker valves 2- 2399-64 and 2- 2399-65 passed the IST test criteria and HPCI was declared operable." "At approximately 1200 hours [CDT] on 4/22/01, the operators tested the 2-2399-66 and 2-2399-67 valves. They were found to meet the acceptance criteria in both the open and closed direction. These valves are a redundant set to the 2-2399-64 and 2-2399-65 valves." "ANALYSIS" "The 2-2399-64 valve and 2-2399-66 valve are in series on the same line. This same configuration also exists on a different line for the 2- 2399-65 and 2-2399-67 valves [...]." "During HPCI operation, either the 2-2399-64 valve or the 2-2399-66 valve and either the 2-2399-65 valve or the 2-2399-67 valve must close to prevent HPCI exhaust steam from flowing to the suppression chamber atmosphere which would cause an increase in containment pressure and temperature. The HPCI system is designed to exhaust the steam to the suppression pool. The exhaust is discharged below the water level in the suppression pool to ensure the steam is condensed." "The acceptable test results of the 2399-67 and 2399-66 valves would allow HPCI exhaust steam during operation to be discharged below the water level of the suppression chamber to ensure that steam was condensed and HPCI operation would not be impeded." "Although, the failure of the 2-2399-64 and 2-2399-65 to close was identified the as-found acceptable condition (ability to close) of the 2-2399-67 and 2-2399-66 valves would have ensured the ability of the vacuum breaker line to perform as required and thus allow HPCI to meet its safety function." "Based on the above, it has been concluded that HPCI was always capable of performing its safety function." Therefore, the licensee is retracting this event notification. The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Shear). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37936 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-04-20 19:31 | 2001-04-21 02:31 | 2001-06-15 | UNANTICIPATED EMERGENCY DIESEL GENERATOR START DURING THE PERFORMANCE OF TESTING The following text is a portion of a facsimile received from the licensee: "This is notification of valid system actuation in accordance with 10CFR50.72(b)(3)(iv)(A)." "At 1931 [CDT] on 04/20/01, the 'B' emergency diesel generator (EDG) automatically started during testing of the local emergency start pushbutton. This was conducted as part of a pre-planned test for restoration following maintenance. However, during the test, the system actuated in a way that was not part of the planned test. Initial test of the signal was unsuccessful, and the start signal was not reset prior to restoring the EDG to the standby lineup. Subsequently, when the start failure relay was locally reset, the EDG automatically started." "The unit was in no MODE at the time of the actuation." The licensee plans to notify the NRC resident inspector. * * * UPDATE ON 06/15/01 @ 0829 BY BARTON TO GOULD * * * RETRACTION The following text is a portion of a facsimile received from the licensee: "[...] After further review, it has been determined that this event is not reportable. At the time of the event, the 'B' Emergency Diesel Generator had been properly removed from service for engine governor modification and was being tested prior to be declared operable. The signal generated was part of a test procedure and an invalid signal, thus not satisfying the reporting requirements of 10CFR50.72(b)(3)(iv)(A). In addition, since the signal was invalid and the 'B' Emergency Diesel Generator had been properly removed from service, a Licensee Event Report is not required within sixty days per 10CFR50.73(a)(2)(iv)(A). Callaway considers this event not reportable and is therefore retracting this event report recorded as Event #37936." The licensee plans to notify the NRC resident inspector. The Reg 4 RDO (Pellet) was notified by the NRC operations officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37935 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2001-04-20 06:20 | 2001-04-20 12:40 | 2001-04-25 | AGREEMENT STATE REPORT - STOLEN HUMBOLDT NUCLEAR GAUGE The device was stolen from a truck after the chain had been cut, the travel case was locked. The theft was reported to the Tulsa police department and a reward will be offered by the licensee. The device was a Humboldt model 5001B serial #3475 containing Cs-137 and Am-241. * * * UPDATE ON 04/25/01 AT 1734 ET BY MIKE BRODERICK TAKEN BY MACKINNON * * * The Humboldt nuclear gauge was recovered. Geo Systems Engineering Incorporated has taken swipes of the gauge and have sent the swipes to be analyzed. R4DO (Jones) and NMSS EO (Brach) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0
37934 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2001-03-10 13:30 | 2001-04-20 10:19 | 2001-04-20 | INVALID ACTUATION OF THE "B" EMERGENCY SERVICE WATER PUMP OCCURRED This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically Emergency Service Water (ESW). On March 10, 2001, during performance of a surveillance test on the Emergency Diesel Generator Logic, an invalid actuation of the "B" ESW pump occurred. The event was caused by a jumper inadvertently being left installed when the surveillance test required the jumper to be momentarily installed. The jumper simulated an initiation signal on 1 EDG. As the test progressed, the "B" ESW pump received an initiation signal and started. The "B" ESW pump started as expected for the given conditions and was subsequently returned to standby per plant procedures. No deficiencies were noted during operation of the "B" ESW pump. This event has been entered into the site-specific corrective action program for resolution. The resident has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0
37933 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-04-19 14:40 | 2001-04-19 17:24 | 2001-06-13 | DEGRADED APPENDIX "R" FIRE BARRIER While conducting a walk down inspection of 10CFR50 Appendix R Barriers, two degraded gypsum walls were identified. The two walls are intended to serve as three hour rated Appendix R barriers. The inspection of the walls revealed that a segment of the walls approximately 6 feet by 6 inches was not constructed as required. The two walls provide separation of safe shutdown equipment in the event of an Appendix R design basis fire. The walls separate the charging pumps, a dedicated shutdown system component, from the safety injection pumps which are alternate shutdown system equipment. Although the walls are not constructed as designed, they appear to be completed to about 75% of design and are judged capable of providing some protection. Nevertheless, the walls are declared inoperable and compensatory actions according to the Kewaunee Fire Plan have been initiated. The walls are declared inoperable due to not having any documented analysis to support the design basis rating. The licensee notified the NRC resident inspector. * * * UPDATE AT 1517 ON 6/13/01 BY HARRINGTON RECEIVED BY WEAVER * * * The licensee has retracted this event based upon further review. On 4/19/01 Kewaunee Nuclear Power Plant (KNPP) reported to NRC via the Event Notification System (ENS) an unanalyzed condition related to two Appendix R fire barriers. The report was made based on a cursory visual inspection of two barriers that appeared to be missing a portion of a layer of gypsum board. Based on what appeared to be less than the three required layers of gypsum board, a conservative assumption was made that the barriers did not meet design requirements. Since the ENS report was filed, the barriers were partially disassembled to gather data for-performing a fire hazards analysis of the apparently degraded barriers in accordance with Generic Letter 86-10. Disassembling the barriers revealed that what appeared to be a partially missing layer was in fact an additional partial layer of gypsum board. Based on the additional data gathered from disassembling the barriers, the barriers met design requirements for a three hour rated Appendix R fire barrier. Therefore, the barriers were not degraded and an unanalyzed condition never existed. Consequently, the reporting criteria for an unanalyzed condition was not exceeded and is the basis for retracting the ENS report notification made on 4/19/01. The licensee notified the NRC resident inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37932 | 0 | U.S. ARMY |  |  |  |  | 2001-04-17 | 2001-04-19 15:52 | 2001-04-19 | LOST TRITIUM SOURCE The U.S. Army reported the loss of a 1.6 Ci H-3 source. The source is part of an M64A1 Sight. The sight was undamaged and double bagged in plastic bags and then placed inside two cardboard boxes, the outer box was unlabeled. The sight was then transported to a local landfill in Jennings Parish, LA. The licensee was unable to locate the sight at the landfill. The licensee will notify the State of Louisiana. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37931 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-04-19 12:30 | 2001-04-19 14:09 | 2001-04-19 | A licensed employee was determined to be under the influence of alcohol during a for cause test. The employee's access to the plant has been suspended. NRC employees may contact the operations center for additional details. The licensee notified the NRC resident inspector. | 80 | 100 | 0 | 80 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0
37930 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2001-04-19 05:00 | 2001-04-19 12:45 | 2002-10-15 | THEFT OF MOISTURE/DENSITY GAUGE On 19 April 2001, the licensee reported the theft of a Campbell-Pacific moisture/density gauge, model CPN MC3, serial number M370403663, from the Foxtree Apartments, northwest corner of McKellips and Scottsdale Roads, Tempe, Arizona. The gauge was locked in its transport container chained in the back of a 1999 Dodge Ram 1500, 2WD Quad Cab pickup, Arizona license CA 63664. The truck itself was stolen early in the morning of 19 April. The theft has been reported to the Tempe police. A reward is being offered. The gauge contains approximately 8 millicuries of cesium 137 and 40 millicuries of americium-beryllium. The State will notify the FBI, Mexico, and the states of Colorado, Nevada, Utah, New Mexico and California. * * * UPDATE 1645EDT ON 10/15/02 FROM AUBREY V. GODWIN TO S. SANDIN VIA FAX * * * "Date: October 15, 2002 Time: 1:00 PM (MST) Supplemental Notice 01-5S "First Notice: 01-5 "On April 19, 2001 the licensee report[ed] the theft of a Campbell-Pacific International, Inc., moisture/density gauge, model MC3, SN# M370403663 and a 1999 Dodge Ram 1500 truck. At approximately 7:15 PM, Oct. 12, 2002, the Agency duty officer was informed that the Phoenix PD bomb squad had found a device containing radioactive material. Upon investigation, the Agency determined that the device was the one stolen in 2001 from the Licensee. The device was not locked and wipe indicated the outside was not contaminated. The device is being returned to the licensee. "The states of CO, CA, UT, NV, NM, and U.S. NRC and FBI as well as Mexico are being notified [of] the status of this incident." Notified R4DO(Pick) and NMSS(Hodges). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0
37929 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-04-18 | 2001-04-19 11:53 | 2001-04-19 | The following is the text from a facsimile sent by the Florida Bureau of Radiation Control. In November 2000, the licensee switched to metal needles requiring a new/different type of transfer tube for the Nucletron HDR unit which is used to treat prostrate cancer patients. The new transfer tube was 1400mm long. The previous tube was 1200mm long. Licensee physicist had a family emergency and left the country. Replacement physicists were performing QA /QC on the HDR to treat a prostate patient when they noticed that the dwell position of the HDR unit was programmed to a 1200mm distance. Since November it is possible that 18 prostrate patients may have essentially not been treated if the source really stopped 200 mm short. Each patient received 3-4 HDR fractions and an external beam (linear accelerator dose). Licensee has not yet been able to talk to their physicist and will not use the transfer tube until resolved. Florida will conduct an on-site investigation next week. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37928 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2001-04-18 14:05 | 2001-04-18 17:45 | 2001-04-18 | SAFE SHUTDOWN TRAIN ELECTRICAL SEPARATION NOT ADEQUATE "HNP is in mode one, 100% power and stable. HNP personnel have determined during an engineering review that fuses intended to maintain safe shutdown train separation in the event of a fire in the 'A' Switchgear room are not capable of performing their intended function due to a design error. A fire in one fire area could result in the inability to isolate a Pressurizer Power Operated Relief Valve (PORV) and associated block valve. These fuses were intended to protect against this condition by isolating the PORV Block Valve circuit on an electrical short due to a fire. These fuses provide power for indication on the plant computer only. "The fuses creating this condition have been removed restoring proper train separation." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37927 | 0 | HI DEPARTMENT OF HEALTH |  |  |  |  | 2001-04-17 15:30 | 2001-04-18 15:29 | 2001-04-18 | NRC LICENSED SOURCE INVOLVED IN AUTOMOBILE ACCIDENT The caller reported that an NRC licensed moisture/density gauge was involved in an automobile accident. The gauge was in its case, which was undamaged. Radiation readings taken at the scene were less than 1 mR/hr. The state contacted the NRC licensee, and has already reported the event to NRC Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | HI | OTH | GEN |  |  |  |  | 0
37926 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2001-04-18 11:50 | 2001-04-18 12:38 | 2001-04-18 | PLANNED OFFSITE NOTIFICATION REGARDING THE DISCOVERY OF A DEAD AMERICAN CROCODILE The following text is a portion of a facsimile received from the licensee: "[At 1150 on 04/18/01, the licensee was] notified by Land Utilization of a deceased American Crocodile. [It was] discovered at [the] far west end of the cooling canals. [The] State of Florida will be notified by Land Utilization later today." The licensee notified the NRC resident inspector and plans to notify the State. It was reported that the State may inform other federal agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37925 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-04-17 15:42 | 2001-04-17 17:40 | 2001-04-18 | VALID CONTAINMENT VENTILATION ISOLATION "While in Mode Undefined (core offloaded), Salem Unit 1 received a Containment Ventilation Isolation signal due to elevated count rate on 1R11A, the Containment Particulate Radiation Monitor. The 1R11A setpoint is set two times background in accordance with Tech Spec 3.3.3.1 for Mode 6. Background count rate prior to the CVI was 2100 cpm (counts per minute). The alarm setpoint was 2980 cpm. "The observed count rate when the actuation occurred was 3300 cpm. Maintenance activities in progress included the breech of 14SJ43, Cold Leg Injection Check Valve. Elevated airborne activity was expected due to this evolution and had been discussed by Control Room personnel. When 1R11A exceeded its setpoint, all containment ventilation isolation valves closed as designed. This actuation has not impacted the Unit 1 outage. "Plant status before and after event: Reactor Coolant System drained to mid-loop RCS at approximately 90°F Core completely offloaded Mode Undefined" The NRC resident inspector has been informed of this event by the licensee. * * * Retraction 1213 4/18/2001 from Sue Simpson taken by Bob Stransky * * * "This notification is a retraction of the 8-hour report made IAW 10CFR50.72(b)(3)(iv)(A) on April 17, 2001 (event time 1542, reported at 1740). "This event notification is being retracted because subsequent investigation determined that the containment ventilation isolation does not meet the definition of reportable system actuations listed in 10CFR50.72(b)(3)(iv)(B)." The NRC resident inspector will be informed by the licensee. Notified R1DO (Ruland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37924 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2001-04-17 13:30 | 2001-04-17 17:24 | 2001-04-17 | EMERGENCY NOTIFICATION SIRENS INOPERABLE "During modification of siren system, testing resulted in 30% of the sirens not communicating with the activation points. Modification stopped. Troubleshooting in progress." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37923 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-04-16 07:10 | 2001-04-17 05:46 | 2001-04-17 | 24-HOUR REPORT INVOLVING A VALID ACTUATION OF A "Q" CLASS SAFETY SYSTEM "At 0710 hours on 04/16/01, Autoclave #4 in the X-344 UF6 Sampling Facility had an 'AUTOCLAVE HI HI PRESSURE' alarm activation. This alarm initiates an 'Autoclave Shell High Pressure Containment Shutdown', which causes the autoclave containment isolation valves ('Q' components) to actuate. The containment isolation valves closed, as designed. The initiating devices for this alarm are redundant pressure switches with a TSR set point of 8.0 psig. Autoclave #4 was in TSR Operational Mode IV (Feeding, Transfer, or Sampling) at the time of the alarm activation. Operations personnel immediately responded to the alarm in accordance with the approved Alarm Response Procedures. Autoclave #4 was placed in TSR mode VII (Shutdown) by operations personnel and declared inoperable by the Plant Shift Superintendent. "Instrument Maintenance was requested to perform 'as-founds' on the 'Autoclave Pressure Loop Instrumentation'. The results of this data indicated that the instrumentation associated with the 'Autoclave Internal Pressure Loop' was found to be within acceptable 'as-found' tolerance. Based on these results, this event is being reported as a valid safety system actuation, a 24-hour NRC event. An Engineering Evaluation has been requested to investigate the circumstances surrounding this safety system actuation." Operations will inform the DOE site representative and has informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37922 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-04-16 | 2001-04-16 15:17 | 2001-04-16 | 10 CFR PART 21 REPORT "This report is being submitted in accordance with 10CFR21.21(d) to address a reportable defect. The defect deals with a replacement Foxboro differential pressure transmitter that was found shorted to ground in the conduit pressure seal assembly during the installation process." The NRC resident inspector will be informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21 |  |  |  | 0
37921 | 0 | WASHINGTON UNIVERSITY |  |  |  |  | 2001-03-20 | 2001-04-16 14:30 | 2001-04-16 | RADIOACTIVE MATERIAL DISCARDED AT SANITARY LANDFILL The licensee reported that one vial of P-32 (1 mCi) was inadvertently discarded at a landfill. The licensee believes that the vial and the shipping pig were left in the shipping box, which was placed in the trash. The licensee was unable to locate the source before it was taken to the landfill. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37920 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-04-15 11:50 | 2001-04-15 17:15 | 2001-06-08 | BOTH LOW PRESSURE COOLANT INJECTION (LPCI) PATHS TEMPORARILY INOPERABLE Procedure inadequacies for venting RHR System using Ops Manual B.08.01.03-05 resulted in Tech Spec LCO(s) 3.5.A declaring both LPCI Injection Paths inoperable (72 Hour LCO) and Tech Spec 3.5.C for one Division of Containment Spray and Cooling inoperable (7 Day LCO) NOT entered. Contrary to Ops Procedure #2145 RHR System Discharge Venting these LCO(s) should be entered when RHR is vented. Notifications are being made because a vent valve was opened which made both LPCI Injection Paths inoperable. This condition at the time of discovery could have prevented the fulfillment of the safety function or system that is needed for Residual Heat Capacity. The vent valve is closed and verified closed. The RHR System is Operable at this time. The licensee notified the NRC resident inspector. * * * UPDATE 1645EDT ON 6/8/01 FROM DUANE SCHMIDT TO S. SANDIN * * * The licensee is retracting this report based on the following: "On April 15, 2001, we reported that the opening of a vent valve made both LPCI Injection Paths Inoperable causing the loss of the LPCI safety function. This operation was a planned evolution in accordance with approved procedures, as it was prescribed by the Operations Manual. As such, there was not a loss of the LPCI safety function and thus this is not reportable per the guidance in NUREG 1022, page 56." The licensee informed the NRC resident inspector. Notified R3DO(Clayton). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0
37919 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-04-14 12:00 | 2001-04-14 18:06 | 2001-04-14 | LEAKAGE DISCOVERED ON "B" HOT REACTOR COOLANT SYSTEM (RCS) HOT LEG INSTRUMENT NOZZLE CONNECTION. A maintenance supervisor reported that there was leakage on a pipe to nozzle connection on line I-3/4-RC-126. After further investigation this line has been determined to be the "B" RCS Hot Leg instrument nozzle connection for differential pressure (D/P) transmitter PDT-1121D. PDT-1121D measures the D/P across "B" Steam Generator. This D/P is used as input to the "D" channel Reactor Protection System low flow trip. A chemistry sample confirms boric acid and active iodine. Leakage was reported to be indeterminate i.e., no drops per hour could be quantified. This problem will be corrected before going above 190 degrees F. An LER will be issued. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37918 | 0 | WA DIVISION OF RADIATION CONTROL |  |  |  |  | 2001-03-14 | 2001-04-13 15:56 | 2001-04-13 | AGREEMENT STATE REPORT INVOLVING A MISSING KRYPTON-85 SOURCE The following event was E-mailed to the Headquarters Operation Center. The licensee reported the loss of an approximately 147 millicurie Kr-85 source (originally 300 millicuries in 1989). The source, an Amersham model KAC.D3, serial number 7341-BK, was mounted in a Data Measurements Corporation source holder model BCL-1. The source assembly was supposed to have been removed from a Data Measurements Corporation Paper Weight Basis Profiler that was being decommissioned in late 1999. A wooden box, labeled as containing the source assembly, was transferred to the licensee's new RSO in 2000 and dutifully inventoried until March 2001. Based on survey measurements, the new RSO became suspicious of the wooden box and discovered upon opening it that it contained the detector assembly rather than the source assembly. A search of the site failed to locate the source. The licensee believes that the source was most likely left on the Paper Weight Basis Profiler and recycled as scrap metal. Alternatively, it could have been discarded into waste sent to the landfill. No records for the decommissioning of the Profiler have been found and the individual who performed the decommissioning is no longer employed by the licensee. Disposition/recovery: Presumed to be irretrievably lost. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37917 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-04-13 14:00 | 2001-04-13 14:55 | 2002-07-22 | STOLEN HUMBOLDT NUCLEAR GAUGE The device was stolen from a job site in Valrico, Florida, from a truck after the chain had been cut. The theft was reported to the police department, and a reward will be offered by the licensee. The device was a Humboldt (model #5001, serial #1287) containing Cs-137/Am-241(8/40 millicuries). ***** UPDATE RECEIVED AT 1728 ON 07/22/02 FROM CHARLIE ADAMS TO LEIGH TROCINE ***** A member of the public discovered the stolen Humboldt soil moisture density gauge (model #5001, serial #1287) today in Plant City, Florida (between Tampa and Orlando near Lakeland) not far off of Interstate 4. The gauge was originally stolen on 04/13/01, and a Deputy at the site reported that the gauge looked like it had been at the discovery site for a long time. It was reported that the gauge appeared to be in the case and did not appear damaged. Representatives from the Hillsborough County Sheriff's Office are currently guarding the device at the discovery site, and a Florida Bureau of Radiation Control representative is en route to the scene. (Call the NRC operations officer for a Florida Bureau of Radiation Control contact telephone number.) The NRC operations officer notified the R2DO (Charlie Payne) and NMSS EO (Eric Leeds). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0 | 2002-07-25
37916 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-04-03 | 2001-04-10 14:59 | 2001-04-13 | AGREEMENT STATE REPORT REGARDING RECOVERY OF FIVE ABANDONED CESIUM-137 SOURCES IN SAN DIEGO, CALIFORNIA. The following text is a portion of a document that was E-mailed to the NRC operations center by the California Radiation Control Program: "On the evening of 4/3, the Hazardous Incident Response Team (HIRT) here in San Diego responded to a situation involving an abandoned radiation source at a Vons parking lot located at 620 Dennery Rd., SD 92154. A Vons clerk reported that a person told him that a bomb was left in the parking lot. When the clerk returned with his manager, the man was gone. A black case was left in a shopping cart, which the clerk opened [...]. No bomb was present, but there was a lead container containing a radiation source. The maximum reading the HIRT obtained at the scene was 12 mRem/hr at the surface of the lead container; HIRT took possession of the source." "[Jon Dillon (DHS-RHB)] was contacted the next morning to assist in evaluating this source of radiation. There was an old label on the outside of the pig that indicated Nuclear Associates as the manufacturer and that there was a total activity of 320 mCi of Cs-137 in what appeared to be five sources. No date was indicated, and the To: line only stated Tijuana. Using a portable MCA, [it was determined] that the sources inside the pig were in fact Cs-137. Using [a] Victoreen 450P, [the] measured a range of exposures [was determined to be] from 10 mR/hr to 28 mR/hr at various positions around the lead pig. In order to identify the sources, [the pig was] carefully opened[, and] five small cylindrical sources [could be seen] recessed in the lead pig. The sources were about 1/8" in diameter, and only about a 1/8" of the length was visible. [It was estimated] that these sources were 3/4" to 1" in length. The Victoreen quickly jumped up to 5.8 R/hr, so [the pig was] quickly closed [...] to return the dose down to the mR range. [The pig was] re-sealed [...] with duct tape and the original metal band[, and then the container was] temporarily placed [...] back in the 5 gallon pail that the HIRT team used to recover the source. The container was then appropriately labeled for storage." "Dave Cammell, who is with [the] HIRT, contacted Nuclear Associates directly regarding this source, and they are sending a package to ship this source back to them. At this time, [it is not known] what the sources were used for. By the physical condition of the label and the tape on the pig, [it was estimated] that this is 15-20 years old, if not more. The [sources] will be secured in the HIRT laboratory until [the shipping materials are received] from Nuclear Associates. There has been no media attention thus far." Law enforcement investigation revealed that this incident was not malicious in nature. Call the NRC operations officer for state contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37915 | 0 | ARKANSAS DEPT OF HEALTH |  |  |  |  | 2001-04-12 15:32 | 2001-04-12 16:55 | 2001-04-12 | AGREEMENT STATE REPORT OF A MEDICAL MISADMINISTRATION At 1532 CT on 04/12/01, Saint Joseph Regional Health Center located in Hot Springs, Arkansas, notified the Arkansas Department of Health of the following Medical Misadministration: Since March 7, 2001, a patient at Saint Joseph Regional Health Center received a total of 24 treatments, 2 grays each, for a total dose of 48 grays to the back of his left hand instead of to his left knuckle. The applicator needles were 5 centimeters shorter than the applicator (stopping shorter than where they were supposed to stop). The source used for the radiation treatments was Iridium-192. State of Arkansas licensee number for the licensee is ARK-342-BP-04-02. State of Arkansas will send personnel out to investigate this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0
37914 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-04-11 13:15 | 2001-04-12 13:23 | 2001-04-12 | NRC BULLETIN 91-01 24 HOUR NOTIFICATION AN NCS ADMINISTRATIVE REQUIREMENT NOT MET. On 04/11/01, it was discovered that C-333 Unit 2 Cell 1 freon systems were at zero freon level without current independent verification documentation that the cell was less than 1.0 wt% U235 in violation of NCSA CAS.011. An independent assay verification was performed in May of 2000, however the cell was subsequently placed onstream and taken back offstream and shutdown in October of 2000. Since shutdown, independent assay verification had not been performed when the freon was drained and prior to implementation of NCSA CAS.011. Due to independent assay verification not being performed prior to implementation of NCSA CAS.011, and NCS administrative requirement was not met. Upon discovery, independent assay verification was immediately performed and cell assay was determined to be less than 1.0 wt% U235. SAFETY SIGNIFICANCE OF EVENT: Double contingency was not maintained. Although the required documentation was not verified at the tome the R-114 level was removed from the cell, the assay of the cell was well known through historical process knowledge. Upon discovery, the historical cascade gradient was reviewed and it was determined that the cell was less than 1.0 wt% U235. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S)) OF HOW CRITICALITY COULD OCCUR: In order for criticality to be possible, the shutdown cell would need to have an unsafe mass of moderated uranium with an enrichment greater than 1.0 wt% U235. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two controls on assay. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): 0.7183 wt% U235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on verification that the equipment contains uranium enriched to less than 1.0 wt% U235. The verification of assay was not performed. Therefore, the control was violated and the first leg of double contingency was lost. The second leg of double contingency is based on independent verification that the equipment contains uranium enriched to less than 1.0 wt% U235. This independent verification was not performed. Therefore, the control was violated and the second leg of double contingency was lost. Since double contingency is based on two controls on assay, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: An independent assay verification was performed and documented, which indicated that the assay was less than 1.0 wt% U235. The NRC Resident Inspector was notified of this event by the Certificate Holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37913 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-04-11 17:15 | 2001-04-11 19:01 | 2001-04-11 | FAILURE OF STANDBY GAS TREATMENT SYSTEM CHARCOAL FILTERS TO PASS A TECHNICAL SPECIFICATION REQUIRED SURVEILLANCE The licensee reported that the 'A' train of standby gas treatment did not pass a test involving an in-place charcoal absorber test with halogenated hydrocarbon tracer (freon). This technical specification required surveillance test is performed approximately every 18-months. The unit was placed in a 7-day limiting condition for operation for the 'A' train of standby gas treatment prior to the test. The unit remains in that LCO as a result of this test. The 'B' train is currently operable. The licensee's investigation is in progress. At this time, the licensee believes that the problem is the result of bypass leakage. The licensee plans to verify the root cause and retest the system tomorrow. This event was reported as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material and mitigate the consequences of an accident. The licensee notified the NRC resident inspector and plans to notify state and local officials. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0
37912 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-04-11 11:18 | 2001-04-11 12:24 | 2001-04-11 | NATIONAL WEATHER SERVICE TONE-ALERT RADIOS OUT OF SERVICE FOR PLANNED MAINTENANCE The following text is a portion of a facsimile received from the licensee: "[The] Control Room [and] Emergency Planning Department [were] notified (via [the] Nine Mile Point Unit 1 Control Room) by Jim Holman of [the] Oswego [County] Emergency Management Office that the tone-alert radios for the National Weather Service (NWS) were out of service (OOS) as of 1118 on 04/11/01 and are expected to be returned to service (RTS) at 1400 on 04/11/01. The system was taken OOS for planned maintenance. [The] Oswego Sheriff's Department is prepared to perform route alerts if necessary." "Review - 10 CFR 50.72(b) [and] 10 CFR 50.72(a)(2)" The licensee notified the NRC resident inspector and plans to notify applicable local and state agencies. (Refer to event #37911 for a similar event notification from Nine Mile Point.) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37911 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2001-04-11 11:18 | 2001-04-11 12:06 | 2001-04-11 | NATIONAL WEATHER SERVICE TONE-ALERT RADIOS OUT OF SERVICE FOR PLANNED MAINTENANCE The following text is a portion of a facsimile received from the licensee: "[The] Emergency Planning Department at Nine Mile Point [Unit 1 was] notified by Jim Holman of [the] Oswego County Emergency Planning Department that the tone-alert radios for the National Weather Service (NWS) were out of service (OOS) as of 1118 on 04/11/01 and are expected to be returned to service (RTS) at 1400 on 04/11/01. The system was taken OOS for planned maintenance. [The] Sheriff's Department [is] prepared to perform route alerts if necessary per procedure EPIP-EPP-30 (Prompt Notification System Problem Response). [The] control room [was] notified [of the event] at 1125 on 04/11/01." "(10 CFR 50.72(b) and 10 CFR 50.72(a)(2) apply.)" The licensee notified the NRC resident inspector and county sheriff. The licensee also plans to notify applicable local and state agencies. (Refer to event #37912 for a similar event notification from Fitzpatrick.) * * * UPDATE ON 4/11/01 AT 1523 BY SHEEHAN TO GOULD * * * The radio was back in service at 1515. The NRC Resident Inspector will be notified. Reg 1 RDO(Linville) was notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37910 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2001-04-11 04:50 | 2001-04-11 11:37 | 2001-04-11 | LOSS OF EMERGENCY PLAN SIRENS The site reported the loss of six emergency plan sirens which constitutes a major loss of emergency offsite communications for greater than one hour. This was caused by a loss of power due to high winds and downed power lines. Power was restored to the sirens at 0807 CDST. The NRC Resident Inspector was notified. The licensee will make a press release to the news media. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37909 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 1999-03-31 | 2001-04-11 11:30 | 2001-04-11 | SECURITY REPORT Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. Refer to the HOO Log for additional details. The licensee notified the NRC Resident Inspector. See EN #37908. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0
37908 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-04-11 10:35 | 2001-04-11 11:17 | 2001-04-11 | SECURITY REPORT Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. Refer to the HOO Log for additional details. The licensee notified the NRC Resident Inspector. See EN #37909. | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0
37907 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-04-10 19:50 | 2001-04-11 05:55 | 2001-04-11 | SECURITY REPORT Safeguards system degradation related to monitoring. Immediate compensatory measures taken upon discovery. The licensee intends to notify the NRC Resident Inspector. Refer to the HOO Log for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 0
37906 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-04-06 22:30 | 2001-04-10 23:55 | 2001-04-10 | NRC BULLETIN 91-01 24 HOUR REPORT The following is from a faxed report: On 4/6/01, R-114 evacuation from C-337 Unit 1 Cell 8 was performed as a non-fissile operation without independent verification documentation that the cell was less than 1.0 wt. % U235 in violation of NCSA CAS.011. Since documentation to determine the assay was not reviewed prior to removing the R-114 vapor pressure, an NCS administrative requirement was not met. SAFETY SIGNIFICANCE OF EVENTS: Double contingency was not maintained. Although the required documentation was not verified at the time tile R-114 vapor pressure was removed from the cell, the assay of the cell was well known through historical process knowledge. Upon discovery, the historical cascade gradient was reviewed and it was determined that the cell was less than 1.0 wt. % U235. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for criticality to be possible, the shutdown cell would need to have an unsafe mass of moderated uranium with an enrichment greater than 1.0 wt. % U235. CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two controls on assay. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): 0.7183 wt. % U235 NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on verification that the equipment contains uranium enriched to less than 1.0 wt. %. The verification of assay was not performed. Therefore, the control was violated and the first leg of double contingency was lost. The second leg of double contingency is based on independent verification that the equipment contains uranium enriched to less than 1.0 wt. % U235. This independent verification was not performed. Therefore, the control was violated and the second leg of double contingency was lost. Since double contingency is based on two controls on assay, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: An independent assay verification was performed and documented, which indicated that the assay was less than 1.0 wt. % U235. Crew briefings have been held to remind them of the requirements of the NCSA. The licensee notified the NRC Resident Inspector and intends to notify the DOE representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37905 | -1 | ROBINSON | 2 |  |  | [2] W-3-LP | 2001-04-10 13:30 | 2001-04-10 18:49 | 2001-04-18 | DISCOVERY OF REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE POSSIBLY VIA A CONTROL ROD DRIVE MECHANISM ASSEMBLY SEAL WELD The following text is a portion of a facsimile received from the licensee: "On 4/10/01, during the removal of mirror insulation from the reactor vessel head while shut down, deposits of residual boric acid were found on the periphery of the Reactor Pressure Vessel Head outside of the Control Rod Drive Mechanism (CRDM) Shroud. Subsequent investigation, by visual inspection of the area within the shroud, revealed additional amounts of boric acid. The source of the leak, based on initial observation, appears to be a CRDM assembly seal-weld leak about 18 inches above the vessel head insulation. A leak from this location would constitute Reactor Coolant System Pressure Boundary leakage. Initial inspection of the reactor vessel head areas, in the vicinity of the boric acid deposits outside of the shroud, revealed no damage to the reactor vessel head." The licensee notified the NRC resident inspector. * * * UPDATE ON 04/18/01 @ 1123 BY GARROU TO GOULD * * * RETRACTION On 4/10/01, during the removal of mirror insulation from the reactor vessel head while shut down. deposits of residual boric acid crystals were found on the periphery of the Reactor Pressure Vessel Head outside of the Control Rod Drive Mechanism (CRDM) shroud. Subsequent inspection at CRDM canopy seal welds and the reactor vessel head in the vicinity of the boric acid crystal deposits was conducted with the head off the reactor vessel and the shroud and some mirror insulation removed. The identified source of the observed boric acid crystals was two very small locations on the canopy seal weld of CRDM No. 68 at location B10. Leakage through the canopy seal weld is not pressure boundary leakage as described in the Technical Specifications and Bases. The structural integrity of the CRDM housing is maintained by the threaded connection. The canopy seal weld does not maintain the structural integrity of the reactor coolant system. Therefore, the original notification made pursuant to 10CFR 50.72(b)(3)(ii)(A) is retracted. The NRC Resident Inspector was notified. Reg 2 RDO(Landis) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37904 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2001-04-09 | 2001-04-10 08:38 | 2001-04-12 | AGREEMENT STATE REPORT INVOLVING A LOST TROXLER MOISTURE DENSITY GAUGE "Baltimore, MD (April 9,2001)-The Maryland Department of the Environment (MDE) has received a report that a moisture density gauge containing nuclear material is missing from a contractor in Fallston, Harford County, Maryland. Engineering consultants Campbell and Nolan Associates, Inc. reported that the device apparently fell from the back of a pick-up truck as it was leaving a construction site in Harford County on the morning of April 9, 2001. "The gauge is believed to have been lost between Monmouth Meadows on Singer Road and the offices of Campbell and Nolan Associates located at 2813 Bel Air Road in Fallston, Maryland. "The portable device is used to measure the moisture and density of soil. The gauge, a Troxler, model 3430 [S/N 26218], is yellow in color and approximately 3' X 2' X 2'. The device contains radioactive material identified as Cesium-137 on an extendable rod and Americium-241 encased in the device. Campbell and Nolan personnel reported that the device was secured with a padlock to prevent inadvertent exposure of the radioactive source. The radioactive material is not a threat to public health and safety as long as it remains intact within the device's shielded enclosure." Call the Operations Center for contact information. * * * UPDATED AT 1000 EDT ON 4/12/01 BY ALAN JACOBSON TO FANGIE JONES * * * MDE reported that the gauge has been recovered undamaged. Notified the R1DO (William Ruland) and NMSS (Don Cool). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0
37903 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2001-04-06 | 2001-04-09 19:19 | 2001-04-09 | AGREEMENT STATE REPORT REGARDING AN IODINE-131 SPILL IN A PROCESSING ROOM AT SYNCOR PHARMACEUTICALS IN DENVER, COLORADO An iodine-131 spill occurred on the evening of 04/06/01 at Syncor Pharmaceuticals in Denver. Apparently, one of two pharmacists dropped a vial containing 250 millicuries of iodine-131. This occurred in a normal processing room where capsules are made. However, at the time of the incident, the fume hood was out of operation. As a result, the ventilation was not proper for the ongoing activities. The two pharmacists involved took agents to block their thyroids and did their best to contain the spill. At this point in time, the thyroid bioassays indicate minimal uptake of radio-iodine, and the licensee has not identified any contamination outside the room. The processing room is not completely clean at this point. There are a few spots with absorbent material and shielding. The licensee plans to address this later today. The fume hood is operating at this time, and it does have charcoal filters in line with the exhaust. The licensee is taking actions to determine if there was any release of iodine outside the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0
37902 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2001-04-09 09:54 | 2001-04-09 11:08 | 2002-04-19 | OFFSITE NOTIFICATION TO THE NATIONAL MARINE AND FISHERIES SERVICE AS A RESULT OF THE ENDANGERED SEA TURTLES NON-LETHAL TAKE LIMIT BEING EXCEEDED "On April 09, 2001 at 0940 the 40th non-lethal sea turtle take in the biennial period occurred. "In accordance with Crystal River Unit #3 Operating License, Appendix B, Environmental Protection Plan (Non-Radiological), 'Endangered or threatened sea turtles shall be protected in accordance with the Incidental Take Statement issued by the National Marine and Fisheries Service (NMFS).' The NMFS has established numerical limits on live takes, lethal takes causally related to plant operation, and lethal takes not related to plant operations. "The NMFS must be notified within five days whenever: a. The 40th non-lethal take occurs in the biennial period, or b. The third causally related mortality occurs in the biennial period, or c. The sixth non-causally related mortality occurs in the biennial period. "The current biennial period for monitoring sea turtle takes began January 1, 2001. "Thus, in accordance with Crystal Unit #3 Administrative Instruction 571, Sea Turtle Rescue and Handling Guidance, the NMFS must be notified within five days. "In accordance with Crystal River Unit #3 Compliance Procedure 151, External Reporting Requirements, this 40th non-lethal sea turtle take is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made." The licensee will inform the NRC resident inspector. * * * UPDATE 0944EDT ON 4/10/01 FROM R. SWEENEY TO S. SANDIN * * * "On April 10, 2001 at 0859 the 41st non-lethal sea turtle take in the biennial period occurred." The licensee informed the NRC resident inspector. Notified R2DO(Julian). ***** UPDATE RECEIVED AT 0911 ON 04/17/01 FROM CHRISTOPHER PELLERIN TO LEIGH TROCINE ***** The 42nd, non-lethal, sea turtle take in the biennial period occurred at 0810 on April 17, 2001. The licensee notified the NRC resident inspector. The NRC operations officer notified the R2DO (Ernstes). * * * UPDATE 1125 EDT ON 5/1/01 FROM DAVID SCHULKER TO FANGIE JONES * * * "On May 1, 2001 at 0805 a turtle was identified as the 43rd rescued, live sea turtle in this biennial period. This sea turtle will be kept for a short observation period and then safely returned to the environment." The licensee will inform the NRC Resident Inspector and the National Wildlife and Fisheries Service. Notified R2DO(Jay Henson). * * * UPDATE ON 5/29/01 BY FERGUSON TO SANDIN * * * On May 29, 2001 at 0943 two turtles were identified as the 44th and 45th rescued, live Sea turtles in this biennial period. These healthy sea turtles will be kept for a short observation period and then safely returned to the environment. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902. The NRC Resident Inspector was notified. The REG2 RDO(Barr) was informed. * * * UPDATE 2014 EDT 6/4/2001 FROM RAWLS TAKEN BY STRANSKY * * * On June 4, 2001 at 1815, the 46th non-lethal sea turtle (Kemp's Ridley) take in the biennial period occurred. The license has informed the NRC resident inspector. Notified R2DO (Barr). * * * UPDATE 1315EDT ON 6/10/01 FROM CHARLES J. MORRIS TO S. SANDIN * * * On June 10, 2001 at 1100, the 47th non-lethal sea turtle take in the biennial period occurred. The license has informed the NRC resident inspector. Notified R2DO (Bonser). * * * UPDATE 0952 ON 8/20/2001 FROM FERGUSON TAKEN BY STRANSKY * * * On August 20, 2001 at 0815, the 48th non-lethal sea turtle take in the biennial period occurred. The licensee as informed the NRC resident inspector. Notified R2DO (Payne). * * * UPDATE 1216 ON 9/3/01 BY SCHULKER TO GOULD * * * On September 3, 2001 at 0845 a turtle was identified as the 49th rescued, live sea turtle in this biennial period. This turtle has an injury to the lower jaw and is being transported to the Clearwater Marine Science Station for treatment. It has not been determined at this time if the injury is casually related to Crystal River Operations. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902. The NRC Resident Inspector and other government agencies will be notified. Notified Reg 2 RDO(Lesser) ***** UPDATE FROM RICHARD SWEENEY TO LEIGH TROCINE AT 0910 ON 10/28/01 ***** The following text is a portion of a facsimile received from the licensee: "On October 28, 2001, at 0030, a turtle was identified as the 50th rescued, live sea turtle in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made." The licensee plans to notify the national Marine and Fishery Services and the NRC resident inspector. The NRC operations officer notified the Region 2 Incident Response Center (McCree). ***** UPDATE FROM CURTIS McKEOWN TO JOHN MacKINNON AT 1005 ON 10/30/01 ***** The following text is a portion of a facsimile received from the licensee: "On October 30, 2001, at 0826, two turtles were identified as the 51st and 52nd rescued, live sea turtles in this biennial period. Additionally, a turtle rescued on October 30, 2001, has been identified as the 53rd live sea turtle rescued in this biennial period." "This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made." The licensee notified the NRC resident inspector and plans to notify the national Marine and Fishery Services. The NRC operations officer notified the Region 2 Incident Response Center (Loren Plisco). **** UPDATE FROM CURTIS McKEOWN John MacKinnon AT 1052 ON 11/01/01 ***** "On November 01, 2001 at 0916 a turtle was identified as the 54 the rescued, live sea turtle in this biennial period. This is reportable as a 4-hour report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902." R2IRC notified. The licensee notified the NRC Resident Inspector of this event. ***** UPDATE FROM BRYAN FERGUSON TO LEIGH TROCINE AT 0938 ON 11/03/01 ***** The following text is a portion of a facsimile received from the licensee: "On November 3, 2001, at 0840, a green sea turtle was identified as the 55th rescued, live sea turtle in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. [...]" The licensee plans to notify the national Marine and Fishery Services and the NRC resident inspector. The NRC operations officer notified the Region 2 Incident Response Center (Ken Barr). ***** UPDATE FROM RICKY RAWLS TO LEIGH TROCINE AT 1126 ON 11/04/01 ***** The following text is a portion of a facsimile received from the licensee: "On November 3, 2001, at 1035, two sea turtles were identified as Kemp's Ridley sea turtles. This is Crystal River Unit 3['s] (CR-3) 56th and 57th rescue of live sea turtles in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. [...]" The licensee plans to notify the national Marine and Fishery Services and the NRC resident inspector. The NRC operations officer notified the Region 2 Incident Response Center (Jim Hufham). * * * UPDATE 1046 EST ON 11/6/01 FROM RICK SWEENEY TO FANGIE JONES * * * "On November 06, 2001 at 0905, a sea turtle was identified as Kemp's Ridley sea turtle. This is Crystal River Unit 3 (CR-3) 58th rescue of a live sea turtle in this biennial period. This is reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902." The licensee notified the NRC Resident Inspector. The R2DO (Caudle Julian) was notified. * * * UPDATE 1149 11/11/01 FROM SCHULKER TAKEN BY STRANSKY * * * "On November 11, 2001 at 1045, a rescued sea turtle was Identified as a Kemp's Ridley. This is the 59th rescue of a live sea turtle at Crystal River Unit 3 (CR-3) in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902." The licensee informed the NRC resident inspector. Notified R2 IRC. * * * UPDATE ON 11/17/01 @ 0846 BY SCHULKER TO GOULD * * * On November 17, 2001 at 0815, a rescued sea turtle was identified as a Kemp's Ridley. This is the 60th rescue of a live sea turtle at Crystal River Unit 3 (CR-3) in this biennial period. This is Reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902. The NRC Resident Inspector will be informed. Notified Reg 2 RDO Julian. * * * UPDATE ON 11/19/01 @ 1112 BY BANDHAUER TO GOULD * * * On November 19, 2001 at 0935, a rescued sea turtle was identified as a green sea turtle. This is the 61st rescue of a live sea turtle at Crystal River Unit 3 (CR-3) in this biennial period. This is reportable as a 4-Hour Report under 10 CFR 50.72(b)(2)(xi) as this event is related to the protection of the environment for which a notification to other government agencies has been or will be made. This is an update to event 37902. The NRC Resident Inspector was notified and other Government Agencies will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37901 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-04-09 05:07 | 2001-04-09 06:48 | 2001-04-10 | PRESS RELEASE PREPARED CONCERNING WORKERS TRANSPORTED TO AREA HOSPITAL AND PLANNED NOTIFICATION TO THE OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION (OSHA) "A news release is planned regarding the following incident: "At 0304 [CDT] this morning, 13 Contract Individuals working in the 2B Main Condenser experienced respiratory distress. The individuals all exited the condenser under their own power for medical attention. Seven individuals were transported offsite to a local area hospital for treatment. The remaining 6 are under the care of the onsite medical staff. An investigation is ongoing. "Additional information: At the current time, the Byron site is preparing information to be made available to the media upon request." The licensee informed the NRC resident inspector. ***** UPDATE RECEIVED AT 1313 EDT ON 04/09/01 FROM SCOT SWANSON TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "[...] The Byron Site Vice President arranged for a meeting with the local media to present available information and answer questions. Exelon Corporation is arranging the press release. In summary:" "Exelon Byron Station had an incident at 0304 [CDT] on 04/09/01 that involved 13 individuals supporting the Unit 2 outage. They were working in the Unit 2 Main Condenser and had to leave due to respiratory distress. Of the 7 that were transported to local Rockford Memorial hospital, 4 have been admitted for observation. [...]" "This is reportable to OSHA under 29 CFR 1904.8." The licensee stated that four individuals were admitted to the hospital for observation at 0830 CDT. Therefore, the required 8-hour notification to OSHA is due by 1630 CDT. The licensee also stated that Unit 2 is presently in Mode 6 (Refueling). Mode 6 was entered at 0938 CDT on 04/09/01. The licensee plans to notify the NRC resident inspector and OSHA. A press release has been made. The NRC operations officer notified the R3DO (Geoffrey Wright). Call the NRC Operations Center for a licensee point of contact. ***** UPDATE RECEIVED AT 1637 EDT ON 04/10/01 FROM STEVE GODBY TO LEIGH TROCINE ***** The following text is a portion of a press release that was received from the licensee via facsimile: "[...] - All seven contract workers from Byron Generating Station transported to Rockford Memorial Hospital Monday morning have been released." "The workers had been building scaffolds inside the Unit 2 condenser as part of a refueling outage that started over the weekend. Shortly after 3:00 a.m. [CDT], an oxygen monitor worn by a member of the team alarmed. The employees immediately left the area according to plant procedures." "The seven employees were transported to the hospital after complaining of dizziness and trouble breathing. Three were quickly released Monday, and the other four were admitted for observation and released by 8:30 p.m. [CDT] Monday night." "An investigation showed that fumes from an anti-corrosive agent in piping connected to the condenser had flowed into the condenser, causing the symptoms" "The pipes have been vented and drained to remove the residual fumes. There are no other sources of chemicals that would affect the air quality inside the condenser." "The work area has been determined to be safe. It remains well ventilated, and monitoring equipment will continue to verify safe atmospheric conditions in the condenser." The licensee notified the NRC resident inspector, OSHA, and the media. The NRC operations officer notified the R3DO (Geoffrey Wright). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37900 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2001-04-08 16:15 | 2001-04-08 22:15 | 2001-04-18 | BOTH EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE "Both Division 1 and Division 2 standby diesel generators were declared inoperable. This report is being made per 10CFR50.72(b)(3)(v)(A), in that both standby diesels were in a condition such that they may not have been able to fulfill their intended safety function. "The division 1 diesel generator was declared inoperable because both diesel generator room exhaust fans were found rotating backwards. The division 2 diesel generator was declared inoperable due to one exhaust fan rotating backwards and the outside air temperature exceeding 72°F. The cause of the fan blades' reverse rotation is under evaluation. Reverse fan blade rotation may cause longer in-rush starting currents which could cause the fan motors to trip. "With two diesel generators inoperable, the plant entered Technical Specification 3.8.1, a 2-hour shutdown Action Statement. "Division 1 and 2 diesel room exhaust fans stopped rotating, and the outside air temperature lowered to less than 72°F The Technical Specification Action Statements were exited. Periodic monitoring of the fans has been established to address reoccurrence of the condition." The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTED AT 1400 EDT ON 4/18/01 BY THOMAS RESTUCCIO TO FANGIE JONES * * * The licensee is retracting the event notification based on the following: "Event notification 37900 was written due to the inoperability of Division I and II emergency diesel generators. The diesel generators were declared inoperable due to the diesel generator room exhaust fans spinning backwards. The issue was that under reverse rotation, starting currents may exceed trip values rendering the exhaust fans inoperable and, as a result, causing the diesel generators to be declared inoperable. "At the time of discovery it was identified that the diesel generator exhaust fans for Division I and II were observed to be rotating backwards at approximately 10-15 rpms. An engineering analysis performed by the licensee has determined that the tans can be spinning backwards up to 235 rpm and will start and operate normally if needed. There will be no adverse affect on the fans operability to perform their design safety function." The licensee notified the NRC Resident Inspector. The R1DO (William Ruland) was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0
37899 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-04-08 11:15 | 2001-04-08 11:21 | 2001-04-08 | OFFSITE NOTIFICATION INVOLVING A LOGGERHEAD TURTLE FOUND IN THE INTAKE CANAL "At 1115[EDT] on 4/8/01 a notification was made to the Florida Fish and Wildlife Conservation Commission regarding a live Loggerhead Turtle found in the intake canal. The turtle will be sent off site to a rehabilitation facility. The notification to a state government agency requires notification to the NRC." The licensee informed the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37898 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-04-07 21:23 | 2001-04-07 23:30 | 2001-04-07 | MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER FLOW "While performing 14236-2, 'SGFPT A and B Trip TADOT [trip actuation device operational test]' on SGFPT A, the link disabling the trip signal to the running SGFPT B was not fully opened, resulting in a trip of SGFPT B. The reactor was manually tripped due to no SGFPT's running. Both trains of the Reactor Protection System functioned as expected. A Feed Water Isolation was received as expected from P4-Low Tavg. An Aux Feed Water Actuation Signal (AFWAS) was generated on the trip of both SGFPT's for both MDAFW pumps and on Lo-Lo Steam Generator level in two of four Steam Generators for the TDAFW pump. The Steam Generator Blow Down system also Isolated properly on the AFWAS signal. The plant is currently stable in Mode 3. A shut down was in progress at the time of this event for a planned refueling outage. The refueling outage will continue as planned." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 46 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37897 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-04-06 19:43 | 2001-04-06 20:46 | 2001-04-07 | UNUSUAL EVENT DECLARED DUE TO FIRE IN EXHAUST HOOD DUCTING A fire occurred in an exhaust hood duct in the Unit 2 chemistry sample room during the processing of an oil sample. The fire was located inside the ducting. Offsite departments responded to the site. An Unusual Event was declared at 1943 EDT. The fire was extinguished at 2022 EDT. The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE 0012EDT ON 4/7/01 FROM CARLOS CONTRERAS TO S. SANDIN * * * The licensee terminated the Unusual Event at 2300EDT on 4/6/01 based on the fact that the fire had been extinguished, current stable plant conditions, and adequate support staff availability. The licensee informed state/local agencies and the NRC resident inspector. Notified R1DO(McFadden), EO(Grimes) and FEMA(Bardon). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37896 | 0 | MID WEST TESTING |  |  |  |  | 2001-04-06 15:00 | 2001-04-06 17:50 | 2001-04-06 | LOST MOISTURE/DENSITY GAUGE The licensee reported that a Humboldt Model HS-EZ moisture/density gauge (serial #3310) fell from the bed of a pickup truck in Hazlewood, MO. The device was not stored in its case at the time of the loss. The unit contains one 11 millicurie Cs-137 source and one 44 millicurie Am-241/Be source. The licensee was unable to locate the gauge after retracing the route of the vehicle. The licensee has contacted the local police department for assistance in recovering the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37895 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2001-04-06 09:09 | 2001-04-06 13:27 | 2001-04-06 | AUTOMATIC REACTOR SCRAM DUE TO BLOWN FUSE IN FEEDWATER CONTROL SYSTEM "This report is bring made per 10CFR50.72(b)(2)(iv)(B) RPS actuation, 4 hour notification for Unit 2 and 10CFR50.72(b)(3)(iv)(A) System Actuation not including RPS, 8 hour notification for Units 1 and 2. "At 0909, Friday 4-6-01, U-2 automatically scrammed. Initial investigations indicate that a blown fuse in the Feedwater control system caused the reactor Recirculation pumps to downshift. The resultant level swell caused reactor water level to reach the level 8 trip setpoint (plus 55 inches). The main turbine tripped on the high reactor water level. The reactor scrammed due to the main turbine Stop Valves closure with reactor power above 25% power. All control rods fully inserted. "The Turbine driven reactor feedwater pumps tripped as designed. The Motor Driven Reactor Feedwater pump feed regulating valve locked out, the cause is not known at this time. Reactor Core Isolation Cooling (RCIC) was initiated manually by the operators for reactor pressure and level control. "A primary containment level 2 isolation (primary containment cooling, containment monitoring. process sample, Unit 1 and 2 Reactor Building Ventilation. Unit 1 and 2 Standby Gas treatment initiation, Reactor water cleanup, reactor Recirculation hydraulic power units and others) occurred at approximately minus 40 inches. "The lowest Reactor water level reached was minus 44 inches and was recovered to normal level utilizing RCIC. RCIC was operated in manual mode following erratic operation in automatic, the cause is not known at this time. System isolations have been restored with exception of reactor water cleanup on U-2. "The station is taking action to investigate the cause of the blown fuse and erratic RCIC operation." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37894 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-04-05 15:26 | 2001-04-05 18:41 | 2001-04-05 | UNUSUAL EVENT DECLARED DUE TO UNCONTROLLED BRUSH FIRE THREATENING OFFSITE POWER SUPPLIES The licensee declared an Unusual Event at 1526 PDT due to an uncontrolled brush fire near the site. The licensee was performing a controlled burn of grasses near the site when the fire went out of control. Heavy smoke from the fire caused a fault on the incoming 230kV power line, resulting in a loss of startup electrical power to both units. All six EDGs automatically started, but did not load. The licensee has notified local government agencies, and has requested assistance from the California Department of Forestry. The NRC resident inspector is currently onsite. * * * UPDATE 1913 EDT 4/5/01 FROM SKAGGS TAKEN BY STRANSKY * * * The licensee reported that the fire has been extinguished. Startup power has been restored to the startup transformers, with restoration of power to individual buses still underway. * * * UPDATE 2005 EDT 4/5/01 FROM SKAGGS TAKEN BY STRANSKY * * * The Unusual Event was terminated at 1700 PDT. Startup power has been restored to all individual buses. Notified R4(Brockman), NRR (Grimes), FEMA (DePuy). * * * COMMISSIONERS ASSISTANTS' BRIEFING 2030 EDT 4/5/01 * * * Briefer: W. Jones. Participants: Brockman, Merschoff, Smith, et. al. (R4), Wessman (IRO), Grimes (NRR), Camper (NMSS), Beecher (OPA), Lohaus (STP), Hauber (OIP), Morris (EDO), Paperiello (DEDMRS), Tschiltz, Levin (Comm. Meserve), Hiltz (Comm. Dicus), Beall (Comm. McGaffigan) Davis (Comm. Diaz), Thoma, Stauss (Comm. Merrifield). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37893 | 0 | YALE UNIVERSITY |  |  |  |  | 2001-04-05 | 2001-04-05 16:54 | 2001-04-05 | MISSING PO-210 SOURCE A 50 µCi Po-210 source has been discovered missing. The source was leased from a vendor under a general license. The caller stated that the source had been used in a science fair project, and then inadvertently discarded into the trash. The university is currently attempting to determine whether the trash from this residence was taken to a sanitary landfill or an incinerator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | MAT | [5 empty] | 0
37892 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-04-05 10:38 | 2001-04-05 12:30 | 2001-04-05 | Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. Contact HOO for additional details. The NRC Resident Inspector will be notified. | 0 | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 0
37891 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-04-04 08:27 | 2001-04-04 18:35 | 2001-04-04 | NRC BULLETIN 91-01 24 HOUR REPORT The following is a portion of a faxed report: "At 0827 Pressure in 33-5-4 was found to be 13.80 psia. The pressure requirement in 33-5-4 is 14 psia when not in a fluorinating environment as required in NCSA PLANT 333-15.A05. The Plant Shift Superintendent directed the facility to enter an anomalous condition. Pressure was regained in the equipment and the facility exited the anomalous condition." "SAFETY SIGNIFICANCE OF EVENTS:" "Safety significance of this event is low. The deposit size in the cell is less than H/U=4 safe mass and the cell is isolated from the operating cascade. If the unbuffered condition were permitted to continue for a long period of time, the H/U of the deposit could eventually reach a maximum of 4. However, since the mass of the deposit is known to be less than or equal to the safe mass at H/U=4, a criticality could not occur." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR):" "For a criticality to occur the deposit in the cell would have to be moderated the mass of the deposit would have to increase and the deposit would have to be reflected." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.):" "Mass and Moderation" "ESTIMATED AMOUNT, ENRICHMENT FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS):" "The estimated enrichment of the cell is 1.27% U-235, the mass is less than safe mass." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES:" "The NCS control was a dry air buffer to >14 psia. The control was established by pressuring the cell to 16.5 psia. The cell was found to be at 13.8 psia." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED:" "The cell was restored to a pressure >14 psia at 0850." Portsmouth personnel notified the NRC Resident Inspector and the DOE representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37890 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2001-04-04 07:00 | 2001-04-04 17:32 | 2001-04-04 | AGREEMENT STATE REPORT CONCERNING STOLEN GAUGE "On the morning of April 4, 2001, the Alabama Office of Radiation Control was advised that a CPN model AC-2 asphalt content gauge (serial number A29099099) had been stolen from the facilities of Jackson Paving and Construction, Inc. located in Scottsboro, AL. Jackson Paving and Construction, Inc. is authorized to possess and use the device under Alabama Radioactive Material License No. 1167. The device contains 100 millicuries of Am-241/Be and the theft was discovered at approximately 7:00 am CDT on April 4, 2001. Along with the gauge, other items such as a generator, torches, radio, etc. were also stolen. The theft is being investigated by the Scottsboro City Police. The device was not in the transport container at the time of the theft. "The licensee's building located in Skyline, Alabama was also broken into and the two incidents may or may not be related. Local Emergency Management Agency personnel were advised to inform the Jackson County Sheriff and local police that stolen radioactive devices are typically abandoned quickly by the thief because they have no sale value." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0
37889 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-04-04 10:12 | 2001-04-04 10:50 | 2001-04-04 | REACTOR COOLANT SYSTEM LEAKAGE >10 GPM AS OBSERVED FROM CONTROL ROOM INDICATIONS "EMERGENCY PLAN ENTRY DUE TO CONTROL ROOM INDICATION OF REACTOR COOLANT SYSTEM LEAKAGE GREATER THAN 10 GPM. IT APPEARS THAT SHUTDOWN COOLING RELIEF VALVE V-3483 LIFTED WHILE ATTEMPTING TO PLACE '1A' TRAIN OF SHUTDOWN COOLING IN SERVICE. WHEN V-3481, HOT LEG SUCTION VALVE, WAS OPENED, APPROXIMATELY 300 GALLONS OF REACTOR COOLANT WAS DIVERTED TO A HOLDUP TANK OVER A PERIOD OF 2 MINUTES. THE LEAK, ESTIMATED AT 150 GPM, WAS ISOLATED BY CLOSING HOT LEG SUCTION VALVE V-3480. AN UNUSUAL EVENT WAS ENTERED AND TERMINATED IMMEDIATELY AT 1012 HOURS AS THE LEAK HAD BEEN TERMINATED AT THE TIME OF THE NOTIFICATION. "THIS EVENT IS SIMILAR TO EVENT #37882." RCS PRESSURE AND TEMPERATURE IS CURRENTLY 260 PSIG AND 250 DEGREES F, RESPECTIVELY. THE RELIEF VALVE SETPOINT IS 330 PSIG. FOLLOWING THE PREVIOUS EVENT, THE RELIEF VALVE V-3483 WAS REMOVED AND BENCH TESTED WITH NO ABNORMALITIES RELATED TO THE SETPOINT PRESSURE FOUND. PRESENTLY, THERE ARE TWO (2) RCPs RUNNING WITH A THIRD AVAILABLE AND THE "1B" SHUTDOWN COOLING TRAIN IN SERVICE. THE LICENSEE PER A PROCEDURAL REQUIREMENT INVOLVING LOW PRESSURE OPERATION OF THE RCPs (RCP SEAL PROTECTION) IS IN A 12 HOUR TIME PERIOD ENDING AT 1600 HOURS. THE CURRENT PLANS ARE TO INCREASE RCS PRESSURE TO GREATER THAN 350 PSIG. BOTH STEAM GENERATORS ARE AVAILABLE TO REMOVE DECAY HEAT. UNIT 1 HAS BEEN SHUTDOWN FOR APPROXIMATELY 50 HOURS. AN EVENT RESPONSE TEAM HAS BEEN ASSEMBLED TO RECOMMEND APPROPRIATE CORRECTIVE ACTIONS FOLLOWING COMPLETION OF AN INVESTIGATION. THE LICENSEE INFORMED STATE/LOCAL AGENCIES AND THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37888 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2001-04-03 23:51 | 2001-04-04 07:22 | 2001-04-04 | REACTOR SCRAM ON WEST SCRAM DISCHARGE VOLUME HIGH WATER LEVEL DUE TO APPARENT LEAKAGE THROUGH THE SCRAM VALVES The following text is a portion of a facsimile received from the licensee: "During a refueling outage while picking up a hold order on the control rod drive system, water level in the scram discharge volume instrument volume started to rise from apparent leakage through the scram valves. At 2351 [CDT,] a reactor scram was received on the west scram [discharge volume] high water level. All expected alarms and actuations were received. All control rods were initially 'full in,' and no rod movement occurred." The licensee stated that there was nothing unusual or misunderstood and that all systems functioned as required. The licensee also stated that at the time of the event, work was being performed on the scram discharge volume drain valves which inhibited the ability to drain the scram discharge volume. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37887 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2001-04-03 23:58 | 2001-04-04 02:19 | 2001-04-04 | MANUAL REACTOR SCRAM FROM 27% POWER DUE TO A RECIRULATION PUMP TRIP FOR UNKNOWN REASONS WHILE THE UNIT WAS IN SINGLE LOOP OPERATION The following text is a portion of a facsimile received from the licensee: "[The] unit was operating [in] single loop (2A [recirculation] pump operating) when the 2A [recirculation] pump tripped. The [nuclear station operator] manually scrammed the unit as required by procedure. During the event, Group II and III isolations were received. All equipment operated as expected. [The] unit is [currently] stable in Mode 3. Restart is being evaluated." The licensee stated that reactor vessel water level decreased to +5 inches and that the Group II and III isolation setpoint was +8 inches. The Group II and III isolations have been reset, and ventilation has been restored. The normal reactor feedwater system is currently being utilized to supply water to the reactor vessel, and containment parameters are normal. The steam dumps to the condenser were available but not needed. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37886 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-04-03 16:09 | 2001-04-03 16:12 | 2001-04-03 | STATE AGENCY NOTIFIED OF INJURED LOGGERHEAD TURTLE FOUND IN THE INTAKE CANAL The licensee notified the Florida Fish and Wildlife Conservation Commission regarding an injured loggerhead turtle found in the plant's intake canal. The turtle will be sent out for rehabilitation. The licensee intends to notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37885 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-04-03 12:00 | 2001-04-03 15:03 | 2001-04-03 | NOTIFICATION OF LOCAL GOVERNMENT AGENCY DUE TO SPURIOUS SIREN ACTUATION The licensee notified Claiborne County Civil Defense that a single offsite emergency siren sounded spuriously for about 25 minutes today starting about 1200 CDT. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37884 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-04-03 | 2001-04-03 14:10 | 2001-04-03 | MOISTURE DENSITY GAUGE RUN OVER AND DAMAGED Geo Solutions reported to the State of California that a Humbolt moisture density gauge was run over at a work site in Atascadero, CA. The case is cracked, but the insides appear intact. The licensee is contacting the vendor for proper handling. There is no further information at this time. * * * UPDATED AT 1732 EDT ON 4/3/01 BY RECA OMAR TO FANGIE JONES * * * Geo Solutions Radiation Safety Officer made a further report about the gauge. The source is intact, the electronics are still working, and a survey indicated no leakage. The gauge has been placed in storage until the vendor takes possession and performs a leak test. A construction bulldozer ran over the gauge. The R4DO (Linda Smith) and the NMSS EO (Patricia Holahan) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37883 | 0 | MALLINCKRODT, INC. |  |  |  |  | 2001-04-03 | 2001-04-03 11:59 | 2001-04-03 | PHARMACY RECEIVED GENERATOR WITH SLIGHTLY HIGH SURFACE READING The Mallinckrodt Pharmacy received a generator with a surface reading of slightly greater than the 200 millirem per hour from the Mallinckrodt facility in St. Louis, Missouri. There was no surface contamination, the swipe test was negative. The package had a transport index of 6.0 with a yellow 3 label package with transport index of 1.5. The manufacturer has been notified and is investigating the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MN | MAT | [5 empty] | 0
37882 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-04-02 17:10 | 2001-04-02 17:35 | 2001-04-02 | REACTOR COOLANT SYSTEM LEAKAGE >10 GPM AS OBSERVED FROM CONTROL ROOM INDICATIONS The licensee was in the process of placing the '1A' train of shutdown cooling system in service, when relief valve V-3483 lifted. Opening V-3481, shutdown cooling hotleg suction valve, caused pressurizer level to decrease about 4% in 5 minutes which corresponds to about 80 gpm. The leak was terminated when V-3481 was closed. The Unusual Event was declared and terminated at 1710 EDT when the leak was isolated. The licensee intends to notify the NRC Resident Inspector and has notified the State of Florida. (REFER TO EVENT #37889 FOR A SIMILAR EVENT.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37881 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-04-01 17:38 | 2001-04-02 14:20 | 2001-04-02 | LOSS OF POWER TO CRITICALITY ALARM SYSTEM "At approximately 1738 hours on April 1, 2001 power was lost to the Criticality Alarm System rendering it non-functional for about 10 minutes. Power was restored and the system is now functioning. Processing and handling of special nuclear material(SNM) was not occurring during the power outage. An investigation is underway regarding this event and a written report/notification will be provided within 30 days." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 1
37880 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-04-02 04:02 | 2001-04-02 06:53 | 2001-04-04 | GREATER THAN 1 PERCENT OF STEAM GENERATOR # 3 TUBES FOUND TO BE POTENTIALLY DEGRADED. At approximately 0402 CT on 04/02/01, Comanche Peak discovered that more than 1% (52 out of 4772 tubes) of the inspected tubes in Steam Generator # 3 are potentially degraded. The degraded tubes are being evaluated to be removed from service. This event meets the criteria of C-3 as described in their Technical Specification section 5.5.9. Additional data is being collected and will be analyzed to assist in determining the cause of the event. An LER will be issued to further document this issue. The other three Steam Generator tubes are being inspected. The NRC Resident Inspector will be notified of this event by the licensee. * * * UPDATE ON 04/03/01 AT 0653 ET BY RAUL MARTINEZ TAKEN BY MACKINNON * * * GREATER THAN 1 PERCENT OF STEAM GENERATOR # 4 TUBES FOUND TO BE POTENTIALLY DEFECTIVE. At approximately 0500 CT on 04/03/01 Comanche Peak discovered that more than 1% (49 out of 4777 tubes) of the inspected tubes in Steam Generator # 4 are potentially defective. The defective tubes are being evaluated to be removed from service. This event meets the criteria of C-3 as described in the their Technical Specification section 5.5.9. Additional data is being collected and will be analyzed to assist in determining the cause of the event. The licensee is presently inspecting Steam Generators 1 and 2. R4DO (Linda Smith) notified. The NRC Resident Inspector will be notified of this update by the licensee. ***** UPDATE AT 0015 EDT ON 04/04/01 FROM RAUL MARTINEZ TO LEIGH TROCINE ***** GREATER THAN 1% OF THE INSPECTED STEAM GENERATOR #2 TUBES WERE FOUND TO BE POTENTIALLY DEFECTIVE. The following text is a portion of a facsimile received from the licensee: "At approximately 2237 [CDT] on [04/03/01,] Comanche Peak Unit 1 discovered that more than 1% of the inspected tubes in steam generator #2 [were] potentially defective. The defective tubes are being evaluated to be removed from service." "This event meets the criteria of C-3 as described in [...] Technical Specification section 5.5.9 and is being reported pursuant to the requirements of 10 CFR 50.72(b)(3)(ii)(A). Additional data is being collected and will be analyzed to assist in determining the cause of the event." "[The total number] of inservice tubes in [steam generator] #2 = 4,476 tubes. [The total number] of tubes discovered defective at this time = 52 tubes." The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R4DO (Linda Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37879 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-04-01 01:45 | 2001-04-02 03:42 | 2001-04-02 | NRC BULLETIN 91-01, 24 HOUR NOTIFICATION INVOLVING REFRIGERANT-114 (R-114) NOT IMMEDIATELY SAMPLED TO DETERMINE MOISTURE CONTENT On 03/31/01, R-114 was transferred from a rail car to the C-335 R-114 drain tank. Following the transfer from the rail car it was determined that the C-335 R-114 drain tank was over the desired fill level and the decision was made to transfer the R-114 from the drain tank to C-335 Unit 4 Cell 9 R-114 system. The R-114 transfer to C-335 Unit 4 Cell 9 from the C-335 drain tank was completed at 1740 CST on 03/31/01. Following the 1900 shift change on 03/31/01 the C-335 building personnel questioned if the R-114 in C-335 Unit 4 Cell 9 should be sampled for moisture. A review of the independent assay verification for C-335 Unit 4 Cell 9 revealed the assay was greater than 1 wt% U235 assay and at 0145 CST on 04/01/01 it was determined that moisture sampling was required and the Plant Shift Superintendent was notified. NCSA CAS-011 requires that if R-114 is transferred to a cell that is above 1wt%U235 assay, the R-114 in the cell must be immediately sampled to determine the moisture content. Since the time between the transfer of the R-114 to the cell and the actual sampling was determined to not meet the NCSA requirement of immediate sampling and is therefore an NCS violation. SAFETY SIGNIFICANCE OF THE EVENT: Although a time limit to determine moisture is not possible, the control requires sampling to start immediately as defined in the TSR. Sampling was delayed in violation of the control procedure. POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for criticality to be possible, the following sequence must occur: Wet R-114 must leak into the process gas portion of the system which contains a larger that critical mass fissile deposit. Sufficient time to enable the hydrogen of the deposit must pass and the deposit must be in a critical geometry for criticality to be possible. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS AND % CASE CRITICAL MASS): 1.5185 wt%U235 NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on immediately sampling of R-114 for water content. Actual moisture content was within acceptable specifications but the sample was not taken in accordance with the time requirement for control. Specifically the control requires immediate sampling upon completion of the addition of R-114. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The R-114 was sampled at 0300 on 04/1/01 with the moisture level determined to be within specifications. The NRC Resident Inspector was notified of this event by the Certificate Holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37878 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2001-03-31 10:58 | 2001-03-31 17:05 | 2001-03-31 | DISCOVERY OF BORIC ACID RESIDUE BUILDUP ON RCS HOT LEG SPARE THERMOWELL On March 31, 2001, at approximately 10:58 mountain standard time (MST) engineering personnel performing preplanned visual examinations of reactor coolant system (RCS) piping in accordance with procedure requirements discovered boric acid residue on RCS hot leg spare thermowell 1JRCETW0121HB. The visual observation was characterized as white streaks fanning out from the hot leg and continuing up the taper of the thermowell with some build-up on the top of the tapered portion. There were no signs of dripping, spraying, puddles of liquid, or liquid running down the nozzle or hot leg The residue appeared dry. Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.14 permits no reactor coolant system (RCS) pressure boundary leakage and therefore, the discovery of leakage (presumed boric acid residue) from the hot leg thermowell was a degradation of a principal safety barrier. Therefore, the ENS notification of this event is in accordance with 10CFR50.72(b)(3)(ii). The control room personnel entered LCO 3.4.14 Condition B and are continuing to place the plant in Mode 5. The RCS was being cooled down in preparation for Unit 1's ninth refueling outage. At the time of discovery, the RCS was at approximately 300 degrees F and 725 psia. An investigation of this event will be conducted in accordance with the licensee's corrective action program. The cracking of Alloy 600 components both at Palo Verde and industry-wide has been attributed to axially oriented, primary water stress corrosion cracking (PWSCC). PWSCC is not considered a significant threat to the structural integrity of the RCS boundary or the thermowell as this type of cracking typically results only in small leaks, The bases for this conclusion is that if PWSCC occurred at Palo Verde, the cracks would be predominately axial in orientation. As in this case, the cracks would result in visibly detectable leakage that would be apparent during visual examinations, performed as part of walkdown inspections, before significant damage to the reactor coolant boundary occurred. Palo Verde has a program for replacing the Alloy 600 thermowells. This thermowell was scheduled for replacement during this refueling outage. The plans to replace the thermowell remain unchanged. No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37877 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-03-30 18:16 | 2001-03-31 10:17 | 2001-03-31 | Safeguards system degradation related to detection alarms being inoperable. Immediate compensatory measures taken upon discovery. The licensee will notify the NRC Resident Inspector. Call Headquarters Operation Officer for further details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0
37876 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-03-31 01:45 | 2001-03-31 08:43 | 2001-03-31 | BORIC ACID DEPOSIT DISCOVERED AROUND ONE CONTROL ROD DRIVE MECHANISM (CRDM) MECHANICAL SEAL HOUSING. During an inspection of the reactor head area following shutdown for a refueling outage, a boric acid deposit and a small amount of water were found on one (of 45) CRDM mechanical seal housing. These deposits may potentially indicate reactor coolant system through-wall leakage. Further investigation will be performed following plant cooldown to determine whether deposits resulted from through-wall leakage or mechanical joint leakage, and appropriate corrective actions will be taken prior to startup from the refueling outage. Boric acid was spread over a one square foot area and there is not any significant buildup of boric acid deposits. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37875 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-03-30 10:05 | 2001-03-30 10:08 | 2001-03-30 | OFFSITE NOTIFICATION - DEAD GREEN SEA TURTLE FOUND IN PLANT INTAKE At 1005 EST on 3/30/01, a notification was made to the Florida Fish and Wildlife Conservation Commission regarding a dead green sea turtle found in the plant's intake net. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37874 | 0 | FRAMATOME ANP RICHLAND INC |  |  |  |  | 2001-03-29 | 2001-03-29 17:58 | 2001-03-29 | PART 21 - AN INCORRECT COMPUTER CODE WAS SUPPLIED BY FRAMATOME TO FOUR LICENSEES FOR CALCULATION OF THE MINIMUM CRITICAL POWER RATIO (MCPR) In the performance of the analysis used to establish the MCPR operating limits, the use of an inappropriate reference temperature resulted in an overprediction of the thermal conductivity of the fuel. This overprediction produced MCPR operating limits that were lower than they should have been. Therefore, the MCPR limits must be raised by up to 0.01 or 0.02, depending on the affected power plants. The MCPR must be raised by up to 0.01 from the limits previously provided for Dresden Units 2 and 3, and for Quad Cities Units 1 and 2. The MCPR limits for LaSalle Units 1 and 2 must be revised by up to 0.01 for power levels of 60 percent and above and by up to 002 below 60 percent. Calculations for Susquehanna Units 1 and 2 were affected but the MCPR limits were unchanged. Continued compliance with the over-pressurization criteria specified by the ASME code has been demonstrated. All units, including Susquehanna, have been notified. Compensatory measures have been provided to the affected plants until confirmatory analyses have been completed. The appropriate reference temperature has been installed in the computer code used for the MCPR analysis. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0
37873 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2001-03-29 11:00 | 2001-03-29 14:42 | 2001-04-25 | SECONDARY CONTAINMENT BYPASS LEAKAGE FAILED TO MEET ACCEPTANCE CRITERIA During the reportability review of Condition Report 01-1582 it was identified that a degraded condition had existed that is required to be reported per 10 CFR 50.72 (b)(3)(ii). It was confirmed that Secondary Containment Bypass leakage did not meet the acceptance criteria of less than or equal to 0.0504 La for Type B and C LLRTs. Specifically the minimum pathway leakage limit is 4340 sccm, however, the as found value was 20,653 sccm (adjusted for instrument accuracy). The dominant leakage (18,110 sccm) was from the High Pressure Core Spray Valve 1 E22-F0012, packing. The penetration for this system credits the 1 E22-F0012 (located outside Containment) as the inboard barrier and the closed system as the outboard barrier, therefore, packing leakage in this case results in minimum pathway leakage. The plant was in Refuel Outage 8 when the leakage was identified. The valve has since been repacked and the current leakage is within limits. The NRC Resident Inspector was notified. * * * RETRACTED AT 0945 EDT ON 4/25/01 BY THOMAS VEITCH TO FANGIE JONES * * * The licensee is retracting this event notification. After review of the event, it has been determined that the net leakage is within the limits of Technical Specification acceptance criteria of less than or equal to 0.0504 La for Type B and C LLRTs. "Subsequent to the event notification, it has been determined that the mechanical joint leakage associated with ECCS lines are accounted for in the Primary Coolant Sources Outside Containment program and are not included in the Secondary Containment Bypass Leakage totals due to being closed loop systems outside containment. The result of the net leakage has been determined not to exceed the Technical Specification limit and therefore this condition is not reportable and ENF 37873 is retracted." The licensee notified the NRC Resident Inspector. The R3DO (Thomas Kozak) has been notified. | 84 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37872 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-03-29 10:45 | 2001-03-29 14:22 | 2001-03-29 | HIGH LEVEL CONDENSATE PROBES ACTIVATED ON AUTOCLAVE #4 At 1045 hours on 03/29/01, both the "A" and "B" High Level Condensate probes activated on Autoclave #4 in the X-344 UF6 Sampling Facility causing a High Condensate Alarm. The activation of either of these probes will cause the autoclave steam supply valves ( "Q" components) to actuate (close). The steam supply valves closed, as designed, autoclave #4 was in TSR Mode II (HEATING) at the time of the alarm activation. Operations personnel immediately responded to the alarm in accordance with the approved Alarm Response Procedures. The alarm reset when operations personnel drained excess condensate from autoclave drain line, and then acknowledged the alarm at the local autoclave control panel. All autoclave (and cylinder) operating parameters were determined to be within normal ranges. Autoclave #4 was placed in TSR mode VII (Shutdown) by operations personnel and declared inoperable by the Plant Shift Superintendent. Based on the actuation of both High Level Condensate probes, this event is being reported as a valid safety system actuation, a 24 hour NRC event. An Engineering Evaluation has been requested to investigate the circumstances surrounding this safety actuation. The DOE Representative will be informed. Reg 3 (Monty Phillips) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37871 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2001-01-31 15:59 | 2001-03-29 13:43 | 2001-03-29 | INVALID ACTUATION OF THE "A" EMERGENCY DIESEL GENERATOR On January 31, 2001 at 1559 while performing an air roll of the "A" Emergency Diesel Generator (EDG) as part of the restoration of the EDG to an operable status, the EDG started. This occurred because the fuel racks were not properly tripped as required by the operating procedure. The operator had attempted to trip the fuel racks, but did not hit the trip button with sufficient force to trip the racks. As a result the EDG started and came up to speed, but the EDG did not progress through the loading sequence since there was no loss of power. Control Room personnel were immediately notified and the EDG was properly shutdown by initiating an emergency trip from the Control Room. The actuation of the EDG occurred due to human error and procedural inadequacy and was not due to actual plant conditions. Therefore, the actuation was not a valid actuation. The "A" EDG had been declared inoperable under Technical Specification 3.8.1.1.b to perform a six hour loaded run. 10CFR50.73(a)(2)(iv) excludes reporting an invalid actuation if the equipment is properly taken out of service. However, the EDG was "not properly taken out of service" at the time as described in NUREG-1022 to qualify for the exclusion to reporting the invalid actuation. Although the EDG had been declared inoperable, it was still "available". If an Engineered Safeguards Actuation System (ESAS) signal had occurred, the EDG would have been available to perform its function. In order to qualify for the exclusion from reporting this invalid actuation, the undervoltage start capability from ESAS would have to have been defeated, the flow of fuel to the EDG stopped, or other appropriate action taken. Therefore, this event is reportable as a 60-day ENS phone call. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.73(a)(1) |  |  |  | 0
37870 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2001-03-29 03:20 | 2001-03-29 07:55 | 2001-03-29 | LOSS OF 6 EMERGENCY PLAN SIRENS The licensee had a problem with the 69 kV power grid in southern Coffey County, which in turn caused the loss of 6 emergency plan sirens at 0220 CST on 3/29/01. At 0320 CST, the criteria for making a 10 CFR 50.72 report on a major loss of emergency communications was met. At 0432 CST the sirens were restored to normal operation. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37869 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-03-28 18:53 | 2001-03-28 20:50 | 2001-03-28 | UNIT 1 EXPERIENCED A GENERATOR TRIP FOR REASONS UNKNOWN At 1853EST on 3/28/01, Unit 1 experienced a main generator trip, turbine trip and reactor scram. The first out indication showed "power load unbalance." There were no maintenance or surveillance activities ongoing at the time. All control rods fully inserted. During the transient reactor vessel water level decreased to a minimum of -31 (Div I) and -37 (Div II) inches as shown on level recorders. Both HPCI and RCIC initiated but did not inject due to level increasing above the -35 inches setpoint required for the injection valves to open. The four low-low pressure setpoint (1120 psig) SRVs, i.e., "A", "C", "G" and "F", opened and reseated controlling reactor pressure. Subsequent to the investigation, it was determined that the "B" SRV also momentarily lifted based on a review of computer edits and an approximate 10 degree F increase on the temperature recorder. The highest recorded pressure was 1125 psig. Group II isolations occurred as expected including initiation of the Standby Gas Treatment System. All isolations have been reset and the affected equipment restored to standby status. Unit 1 is currently stable in hot shutdown with reactor pressure controlled using bypass valves to the main condenser. Condensate feed is in service supplying makeup with the reactor recirculation pumps at minimum speed. An event review team is responding to the site to determine the root cause. Three 230KV breakers, i.e., two generator output and one switchyard, opened during the transient. Unit 1 will remain shutdown pending the results of the investigation and completion of other scheduled maintenance. The licensee informed the NRC resident inspector and does not plan a press release at this time. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37868 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2001-03-28 | 2001-03-28 16:47 | 2001-03-28 | PART 21 REPORT INVOLVING REPLACEMENT SIEMENS ELECTRICAL BREAKER COMPONENTS NOT MEETING DESIGN SPECIFICATIONS "On March 26, 2001, Carolina Power & Light Company (CP&L) determined the following condition to be reportable in accordance with 10 CFR Part 21. "Description of Defect or Failure to Comply: "Siemens RLN/RLNF breaker cubicle Mechanism Operated Cells (MOC) were supplied to the Harris Nuclear Plant (HNP) as replacements which do not match design specifications. The parts procured were received with improper push bar length and configuration. The length and configuration are critical characteristics of this component. Improper length and configuration of the push bar on the MOC can result in the MOC not actuating upon breaker closure as per design. These parts were received commercial grade and dedicated onsite by CP&L for use in safety-related applications. CP&L's inspection of critical characteristics failed to identify that the component was not manufactured in accordance with the approved design specifications. Therefore, the defective MOCs were available in HNP stores for installation in safety-related applications. "HNP has identified a potential application where, had the subject MOC been installed, safety related functions designed to help mitigate the consequences of design basis events could have been lost. "A more detailed 30 day report will be submitted to the NRC in accordance with 10 CFR 21.21 by April 25, 2001." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 21.21 |  |  |  | 0
37867 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-03-28 13:35 | 2001-03-28 16:22 | 2001-03-28 | FITNESS FOR DUTY REPORT INVOLVING A CONTRACT EMPLOYEE A contract employee was determined to be under the influence of an illegal drug during a random test. The employee's access to the plant has been terminated. The licensee informed the NRC resident inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.73 |  |  |  | 0
37866 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2001-03-27 18:30 | 2001-03-28 14:16 | 2001-03-28 | AGREEMENT STATE REPORT INVOLVING A RECOVERED TROXLER MOISTURE DENSITY GAUGE On 3/27/01 at 1830CST, the Mississippi Division of Rad Health was notified by Mississippi Emergency Management that the South Haven Fire Department had recovered a Troxler Moisture Density Gauge, Model 3411D, S/N 5155. The locks were still in place and the source was not exposed. The gauge is in custody awaiting notification of the licensee. HOO NOTE: The gauge was reported stolen from a construction site in Memphis, Tennessee, in 1994. See event #26822. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0
37865 | 0 | PARKVIEW HOSPITAL |  |  |  |  | 2001-03-26 11:45 | 2001-03-27 13:45 | 2001-03-27 | MEDICAL MISADMINISTRATION INVOLVING A HIGHER THAN PRESCRIBED THERAPEUTIC DOSE OF I-131 DELIVERED An elderly 65 year old female patient was prescribed a therapeutic 125 millicurie dose of I-131. The administering technician inadvertently delivered 160 millicuries of I-131. The error is attributed to the past practice of physicians ordering 150 millicuries doses (+/- 10%) which is what the technician ordered from the nuclear pharmacy without explicitly verifying the prescribing physician's order. The patient and referring physician were informed of the misadministration by the prescribing physician. Administrative measures including separate verification of the prescribed dosage have been implemented by the licensee to prevent recurrence. The prescribing physician concluded that there was no change in the clinical outcome and that the increased dosage did not pose a high risk for the patient. The licensee will submit a written followup report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0
37864 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2001-03-24 16:01 | 2001-03-24 19:24 | 2001-03-24 | PRESSURE BOUNDARY DEGRADATION FOUND DURING TESTING AFTER SHUTDOWN "On March 18, 2001, following shutdown for a scheduled refueling outage, Arkansas Nuclear One (ANO) Unit I performed a routine visual inspection of the Reactor Vessel (RV) head area per NRC Generic Letter 88-05. This inspection revealed an increase in the amount of boric acid crystals in the area of one Control Rod Drive Mechanism (CRDM) nozzle over the amount that had been present during the previous inspection. Results of the visual inspection were inconclusive regarding the source of the leakage. No other CRDM nozzle showed similar boron buildup. Prior to unit shutdown, on March 16 the total unidentified Reactor Coolant System leak rate was determined to be 0.087 gpm, significantly less than the 1 gpm allowed by Technical Specifications. After the RV head was removed and placed on the storage stand, additional inspections were conducted. At approximately 1601 on March 24, 2001, eddy current and ultrasonic testing revealed an RCS pressure boundary leak. Using ultrasonic test (UT) methods one crack was identified in the wall of CRDM nozzle #56. The UT data indicates that the crack is on the downhill side of the nozzle. It extends approximately 0.8 inches below the weld and extends upward to approximately 1.0 inches above the weld. The depth of the crack is approximately 0.2 inches. This crack is consistent with industry experience associated with Primary Water Stress Corrosion Cracking (PWSCC) in similar components that have been evaluated as part of the NRC Genetic Letter 97-01 response. These cracks do not pose a significant safety risk during plant operation. ANO plans to perform repairs during the current outage. Since the crack resulted in leakage through the Reactor Coolant System pressure boundary, this condition is being reported as a non-emergency eight-hour report in accordance with 10 CFR 50.72(b)(3)(ii), degradation of a principal safety barrier." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37863 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-03-24 00:30 | 2001-03-24 10:39 | 2001-03-24 | OFFSITE NOTIFICATION REGARDING DISCHARGE OF WATER OFFSITE "On 3/24/01, at 0845, a determination was made that a report to the TNRCC [Texas Natural Resource Conservation Commission] is required for a discharge of water to Squaw Creek Reservoir. An estimated 1000 gallons of fire protection water was discharged due to a ruptured pipe in warehouse C. The water contains no hazardous constituents that have assigned reportable quantities; however, a report to the TNRCC will be made in accordance with water quality regulations." The NRC resident inspector has been informed of this report by the licensee. | 88 | 100 | 0 | 88 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37862 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-03-24 03:08 | 2001-03-24 08:35 | 2001-03-24 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "This report is being made in accordance with 10 CFR 50.72(b)(2)(i). "Columbia Generating Station started a plant shutdown 03:08. At 23:15 yesterday, a rise in drywell pressure was observed Coolant leakage was confirmed by a rising trend in drywell particulate monitors. Upon investigation, this leakage was confirmed to be due to cycling RCIC-V-63, the RCIC steam supply inboard isolation valve, during the performance of a Surveillance Procedure. "At 23:30, a rise in drywell unidentified leakage rate was observed. At 01:56 an entry into Technical Specification 3.4.5.B for greater than a 2 gpm rise in a 24 hour period was made. At 03:08, an entry into Technical Specification 3.4.5 A was made for unidentified leakage greater than 5 gpm. At this time, the decision to begin a controlled reactor shutdown was made. "RCIC-V-63 was backseated to terminate leakage at 03:55. At 03:58 it was determined the backseating successfully stopped the leakage. The downpower was terminated at 04:19. Indications of leakage are trending down. At 04:30, the leakage had decreased below the Technical Specification limits and reactor power was increased to 100%." The NRC resident inspector has been informed of this event by the licensee. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37861 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-03-16 07:00 | 2001-03-23 19:02 | 2001-03-23 | STOLEN MOISTURE DENSITY GAUGE The Twining Labs reported a stolen Troxler moisture density gauge, Model 3430, serial # 20467. The sources are nominal 30 millicuries of Cs-137 and 10 millicuries Am-241/Be. The local police were notified (police report # 01-23615) and a reward was posted for the return. The theft occurred on 3/16/01 about 0700 PST. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37860 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2001-03-22 14:43 | 2001-03-22 17:06 | 2001-03-22 | SECURITY REPORT Unescorted access was granted inappropriately. Immediate compensatory measures were taken upon discovery. (Contact the NRC operations center for additional details.) The licensee notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 0
37859 | 0 | COGEMA MINING, INC. |  |  |  |  | 2001-03-21 | 2001-03-22 16:54 | 2001-03-22 | CONDITION OF LICENSE REPORT INVOLVING MINE IN EXCURSION STATUS The following is taken from a faxed report: Notification of a Reportable Event per License Section 11.2 Reported Event: A routine monthly water sample collected on March 21, 2001 from monitor well 5MW43, exceeded 2 of its 3 upper control limits (UCLs). A confirmation sample was collected March 22, which also exceeded 2 UCLs. Monitor well 5MW43 was then placed on excursion status as per license Section 11.2 and its sampling frequency increased to weekly. 5MW43 is a perimeter ore zone monitor well located approximately 300 feet south of the Mine Unit 5 boundary at the Christensen Mine, Campbell County Wyoming. Note that Mine Unit 5 is currently in groundwater restoration and that the nearest community is Linch, Wyoming approximately 16 miles to the southeast. Analysis Data: Conductivity Uranium Date Chloride mg/l umhos/cm2 Alkalinity mg/I mg/l U308 Sampled UCL 22.7 UCL 1004 UCL 134.3 no UCL 3-21-01 7.5 1116 163.0 <0.4 3-22-01 7.4 1133 169.0 <0.4 Health and Environmental Hazards: None Investigative Action: Collect additional samples from this well to further evaluate the water quality. Since the chloride concentration remains near its baseline level, it is felt that this is not an actual excursion from the Mine Unit. Written Notification: A written notification with further information will be submitted to NRC Fuel Cycle Licensing Branch Chief within 7 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | MINING EVENT | [9 empty] | NON EMERGENCY | 4 | WY | OTH | GEN |  |  |  |  | 0
37858 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-22 11:10 | 2001-03-22 16:10 | 2001-04-24 | RCIC DECLARED INOPERABLE During an investigation of a ground on Div I 125/250 volt D.C. bus, the source of the ground was determined to be 2E51-F008 primary containment isolation valve. 2E51-F008 is the outboard steam supply to reactor core isolation coolant (RCIC). It was closed and de-energized. 2E51-F008 closure rendered RCIC system inoperable. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 04/24/01 AT 1453 ET BY S. HOWARD TAKEN BY MACKINNON * * * Plant Hatch FSAR has been revised such that the Control Rod Drop accident limiting event path evaluated in the safety analysis (subsection 15.3.2) does not rely on RCIC to mitigate this Design Basis Accident (DBA). None of the DBAs, as evaluated in the safety analysis (section 15.3), rely on RCIC for event mitigation. RCIC will no longer be an NRC notification when declared inoperable. Therefore, this NRC notification is being retracted. R2DO (Paul Fredrickson) notified. The NRC Resident Inspector was notified was notified of this retraction by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0
37857 | 0 | U.S. ARMY |  |  |  |  | 2001-02-21 | 2001-03-22 14:34 | 2001-03-22 | MISSING M187 PANORAMIC TELESCOPE LEVEL DEVICE A M187 panoramic telescope was found with a missing level vial, a sealed tritium source of 0.075 curies at Fort Bragg, North Carolina. The second level vial was broken and a wipe test indicated no contamination of the instrument. A search was conducted of the reservation with negative results. A written report will be made to NRC Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37856 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-03-21 21:30 | 2001-03-22 02:16 | 2001-04-23 | DRYWELL TO TORUS BYPASS LEAKAGE NOT REEVALUATED FOR POWER RERATE "An unanalyzed plant condition may exist due to Drywell to Torus bypass leakage as defined in Tech Spec Bases 3.7.A was not reevaluated for power rerate. The original evaluation determined that the maximum allowable leakage capacity was 0.12 square feet. When power rerate was being evaluated, General Electric assumed that Monticello was bound by a generic evaluation for the drywell to torus allowable capacity of an 0.01 square feet." Corrective action includes a reevaluation, as appropriate. The licensee informed the NRC resident inspector. * * RETRACTION ON 04/23/01 AT 1805 ET BY JIM MCKAY TAKEN BY MACKINNON. Retraction of notification made on March 22, 2001. The notification stated that an unanalyzed plant condition may exist due to a drywell to torus vacuum breaker bypass leakage [which] was not re-evaluated for power rerate. Upon further revaluation conducted by General Electric Company and based on a review of the original analysis, the bounding assumptions used to calculate the maximum allowable bypass leakage area was effectively independent of reactor power and are, therefore, not adversely impacted by power rerate. As such, an unanalyzed condition does not exist. R3DO (Tom Kozak) notified. NRC Resident Inspector will be notified of this retraction by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37855 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2001-03-21 22:45 | 2001-03-21 23:10 | 2001-03-21 | ALERT DECLARED - SMALL FIRE ON AN EMERGENCY DIESEL BEARING COVER The licensee declared an Alert when paint on the outboard generator bearing cover of the #14 EDG caught fire. The fire was put out in less than one minute with a portable CO2 extinguisher. The fire occurred at 2211 and the Alert was declared retroactively at 2245. It was also terminated at 2245. All other emergency equipment is operable. The plant continued to operate at 100 percent power throughout the event. The licensee notified the NRC resident inspector, Monroe County, Wayne County, the Province of Ontario and the State of Michigan. The Operations Center made the following additional notifications. CANADA - PERREAULT, OIP - BRESKOVIC, OPA - BEECHER | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37854 | 0 | USAF RADIOISOTOPE COMMITTEE |  |  |  |  | 2001-01-01 | 2001-03-21 17:54 | 2001-03-21 | LOST AMERICIUM SOURCES Four chemical agent detectors were discovered on Kelly Air Force Base in San Antonio, Texas. Each detector contains one or two Am-241 sources. Each source has an activity of 160 µCi. The origin of the detectors has not been determined. The detectors had been mistakenly given to a subcontractor about one year ago and then were returned to the Air Force a few months ago. The licensee has discussed this event with Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37853 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2001-03-20 21:00 | 2001-03-21 12:59 | 2001-03-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE "Between 7:00 and 9:00 PM, March 20, 2001, in a shopping area at 54th Street and Ray Road a Troxler Model 3411B moisture/density gauge, SN 11906, was stolen along with the truck containing the gauge. The truck is a 1993, white Chevrolet S-10 pickup, AZ tag # 141CAE. This information was supplied by the Radiation Safety Officer. The gauge contains an 8 millicurie cesium 137 source and a 44 millicurie americium-241/beryllium source. The gauge was locked to the pickup bed. Chandler Police Department is investigating this matter, report # 01-24824. The LICENSEE is offering a $500.00 reward. The Agency will be issuing a press release. "The LICENSEE and the Agency continue to investigate this event. "The states of Utah, California, Colorado, New Mexico, and Nevada together with the U.S. NRC, the U.S. FBI and Mexico are being notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0
37852 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-20 08:00 | 2001-03-20 14:51 | 2001-03-20 | DEGRADED WHILE SHUTDOWN With Unit 2 in Mode 5 on the 11th day of its 10th Refuel and Inspection Outage, it has been determined that the CRD Seismic Island leakage rate criterion of 508 mI/hr has been exceeded. During performance of the Hydraulic Leak Test of CRD Seismic Island Check Valves, SE-259-150, a leakage rate of 20 ccm was recorded for Test 1 (valve # 246027) and a leakage rate of 14.3 ccm was recorded for Test 2 (valve 246028). With this leak rate, the 'Minimum Path' CRD Seismic Island Check Valve leak rate is 858 mI/hr. This leak rate exceeds the criteria of 508 mI/hr specified in FSAR Table 6.2-15, Evaluation of Secondary Containment Bypass Leakage Pathways. This condition constitutes a degraded plant condition and requires an 8 hour ENS Notification in accordance with 10CFR50.72(b)(3)(ii)(A). The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37851 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-03-19 10:57 | 2001-03-19 18:02 | 2001-03-19 | GREATER THAN 1% OF STEAM GENERATOR TUBES DEFECTIVE "During refueling outage 2RE08, the results of steam generator tube inspections in steam generator 2C were classified as category C-3 in accordance with Technical Specification 4.4.5.2.d) in that 48 tubes out of 4,615 (i.e.,> 1%) have been found to be defective. All defective steam generator tubes will be plugged before the steam generators are returned to service. There were not any adverse safety consequences or implications as a result of this event. This event did not adversely affect the safe operation of the plant or the health and safety of the public. The cause of the imperfections is outside diameter stress corrosion cracking." South Texas Project conducted a steam generator tube inspection results conference call with Region IV, the Senior Resident Inspector, and Nuclear Reactor Regulation this afternoon. The occurrence of the C-3 condition was noted during the call. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37850 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2001-03-19 12:32 | 2001-03-19 14:22 | 2001-03-20 | REACTOR SCRAM On 3/19/2001, at 1232 a reactor scram signal was received, all rods inserted after the scram. Reactor Pressure Vessel (RPV) water level dropped below 127" (normal water level is about 160") which actuated primary containment isolation signals for groups 2, 3 and 5. RPV water level is being controlled by feedwater and RPV pressure control is via turbine bypass valves. The plant is stable. The cause of the reactor scram is under investigation. The licensee notified the NRC resident inspector and will notify the state authorities. A press release may be issued. * * * UPDATE AT 1257 ON 3/20/01, BY KRITZER RECEIVED BY WEAVER * * * "The cause of the 3/19/2001 scram has been determined to be faulty auxiliary contacts in Reactor Protection System (RPS) relay 5A-K13D. The auxiliary contacts failed to open during reset of a ½ scram condition on the RPS "B" auto scram channel inserted during surveillance testing earlier in the shift. There were no means available to the operators to detect this failure. Subsequent surveillance testing of RPS "A" inserted a ½ scram on RPS "A" auto scram channel which resulted in the energization of backup scram valve 3-140B. The energization of the backup scram valve vented the scram air header which led to the full reactor scram. Repairs have been completed and the plant is preparing for restart." The licensee notified the NRC resident inspector. The Operations Center notified R1DO (Jenison). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37849 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-03-19 10:30 | 2001-03-19 11:10 | 2001-03-19 | SECURITY REPORT UNESCORTED ACCESS GRANTED INAPPROPRIATELY. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE NRC RESIDENT INSPECTOR HAS BEEN INFORMED. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 0
37848 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-19 08:00 | 2001-03-19 10:44 | 2001-03-19 | SECONDARY CONTAINMENT BYPASS LEAKAGE RATE WAS EXCEEDED "With Unit 2 in Mode 5 on the 10th day of its 10th Refuel and Inspection Outage, it has been determined that the Secondary Containment Bypass Leakage (SCBL) rate criteria of 9 scfh has been exceeded. During performance of Local Leak Rate Test SE-259-045, a leakage rate of 3,838 sccm was recorded for the Division 2 RHR Drywell Spray Containment Isolation Valve HV251F016B. With this leak rate, the Min Path SCBL leak rate was calculated to be 4,312 sccm (or 9.14 scfh). This leak rate exceeds the Technical Specification 3.6.1.3 criteria of 9 scfh for SCBL. They will rework the valve and retest." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37847 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-03-18 01:00 | 2001-03-18 05:07 | 2001-03-18 | Unaccounted for security weapon. Compensatory measures were put into place immediately following discovery. Contact HOO for additional information. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 0
37846 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-03-18 02:12 | 2001-03-18 04:12 | 2001-03-18 | THE EOF IS CONSIDERED UNAVAILABLE DUE TO PARTIAL LOSS OF POWER. A partial loss of electrical power to the Emergency Operations Facility (EOF) occurred at 0212 CST. The partial loss of power resulted from opening a circuit breaker that appeared to be tripped. The failed circuit feeds lighting in the EOF as well as various other support loads. Based on the partial loss of electrical power, the EOF is being considered unavailable. Callout of electrical support is in progress for troubleshooting and repair. The NRC Resident Inspector will be informed. ***** UPDATE AT 1216 EST ON 03/18/01 FROM SCOTT MAGLIO TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "This is a followup notification to the initial call made at 0312 [CST] on 03/18/01. Restored electrical power to the Emergency Operations Facility at 1010 [CST]. The partial loss of power to the facility was caused by a fault on one of the parking lot lighting circuits. This circuit has been isolated. Facility and equipment checks have been initiated." The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R4DO (Johnson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37845 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-03-17 21:13 | 2001-03-18 00:03 | 2001-03-18 | REACTOR TRIP FROM 100% POWER DUE TO DECREASING STEAM GENERATOR WATER LEVELS During 100% power operation of Unit 2, the Reactor Protection System (RPS) properly initiated an automatic Reactor Scram signal in response to decreasing Steam Generator (S/G) water levels. Steam Generator water levels were decreasing due to an 'A' Main Feedwater Pump trip, which in turn had been caused by an 'A' Condensate Pump trip. All rods fully inserted into the core, and all Safety Systems operated as designed. The cause of the Condensate Pump trip is not currently known, and investigation is continuing. No Radiological Releases, RCS leaks, or S/G leaks occurred during this event. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37844 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-03-16 11:00 | 2001-03-17 10:55 | 2001-03-23 | 24 HOUR 91-01 BULLETIN - GEOMETRY VIOLATION At 1100 on 3/16/01, a seal test buggy was found without signs or tags as required by NCSA-PLANT_031 (Potable Sampling/Test Buggies and Carts). Upon investigation of the test buggy, the chemical trap was found to have a nominal diameter of four inches and a length of twenty two inches. The four inch diameter violates the passive design control 2(b) which requires a three inch nominal diameter and a thirty three inch length. Nuclear Criticality personnel have determined the maximum loading of the effected trap to be 76 gram U-235 at 3% assay. 76 grams is lower than the 350 gram safe mass limit. The NCSE contingency analysis considers credible, a maximum five inch nominal diameter to remain subcritical. SAFETY SIGNIFICANCE OF EVENTS: Safety significance is considered very low. The NCSA requirement is three, three inch nominal diameter chemical traps. However, the NCSE allows for three, five inch nominal diameter chemical traps and remain subcritical, POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): Based on the bounding calculations for five inch diameter chemical traps, there no critical pathways involved CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Geometry is the controlled parameter that was violated ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The amount of uranium is unknown, however, it is not expected to be above 350 grams U-235 due to the operation performed with this buggy and the fact that the maximum loading of a 4" X 22" chemical trap is only 76 grams U-235 at 3% assay. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The control violated was the geometry control of the chemical trap. The chemical trap was required to be three inch schedule 40 pipe, but it was found to be a nominal four inch diameter pipe. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED; The test buggy was posted with temporary signs as required by NCSA-PLANT_031. The buggy will remain in the anomalous condition boundary until NDA results are obtained. Disposition of the buggy will be determined based on the NDA results. The NRC Resident Inspector was notified. The DOE Representative will be informed. * * * UPDATE AT 1346 EST ON 3/23/01 BY JIM McCLEARY TO FANGIE JONES * * * "NDA measurements show the chemical trap described above contains 1.6 +/- 0.8 grams and the pump contains 1 gram of U-235. Total U-235 content including error is 3.4 grams U-235. TSR 3.11.2 requires an NSCE for operations with uranium enriched to 1 wt% and contains 15 grams or higher U-235. Therefore this buggy is not a fissile material operation and not a violation of NCSA-PLANT_031." The licensee notified the NRC Resident Inspector and the DOE representative. The R3DO (Gary Shear) and NMSS EO (Brian Smith) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37843 | 0 | WATERFORD | 3 |  |  | [3] CE | 2001-03-15 09:00 | 2001-03-15 13:53 | 2001-03-15 | OFFSITE NOTIFICATION REGARDING THE DISCOVERY OF A DEAD BROWN PELICAN ON THE CIRCULATING WATER INTAKE STRUCTURE The following text is a portion of a facsimile received from the licensee: "On 3/15/01 at 0900 CST, the Waterford 3 Control Room Staff was notified that it was discovered that a Brown Pelican (Pelecanus occidentalis) had died on the [Waterford 3] Circulating Water Intake Structure. The Brown Pelican is listed as an endangered species. Reports were that the bird was injured the previous night (3/14/01) as a result of an attack by white pelicans. The bird was identified as a brown pelican when it was found dead on the morning of 3/15/01. The Waterford 3 Environmental Protection staff notified the Louisiana Department of Wildlife and Fisheries [... at 0920 CST on 3/15/01. ... (Call the NRC operations officer for the applicable address, telephone number, and contact name.) The Louisiana Department of Wildlife and Fisheries representative] stated that she would pass the information along to the proper department and that Waterford 3 would be contacted if further investigation was needed. The dead bird was placed in a plastic bag and transported to the freezer in the environmental monitoring lab for storage." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37842 | 0 | JAMESON MEMORIAL HOSPITAL |  |  |  |  | 2001-03-14 | 2001-03-15 11:15 | 2001-03-15 | POSSIBLE RADIATION EXPOSURE ABOVE THE NRC REGULATORY LIMIT OF 5 REM Based on calculation methods used by the Pennsylvania Department of Environmental Protection and the National Society of Radiation Physicists, the total body dose received by a cardiologist at Jameson Memorial Hospital received last year was 3,069 mR which is less than the limit of 5,000 mR/yr. On 03/13/01, an NRC physicist using a different methodology for calculating total body dose calculated that the cardiologist received a total body dose of 5,401 mR last year. The cardiologist received most of the dose from x-ray related activities (regulated by the Commonwealth of Pennsylvania). However, the cardiologist received some exposure from doing stress tests on patients, which mostly involves the use of NRC licensed material (technetium-99m). No adverse health effects are expected. On 03/14/01, NRC Region 1 issued a Preliminary Notification (PNO-I-01-006) describing this event in more detail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2202(b)(1) |  |  |  | 0
37841 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2001-03-14 17:52 | 2001-03-14 20:20 | 2001-03-14 | UNIT 2 EXPERIENCED A TURBINE TRIP - REACTOR TRIP ON LOSS OF LOAD "At 1752 hours on 3/14/01, the St. Lucie Unit 2 reactor automatically tripped on a turbine loss of load signal. Prior to the trip, the output breaker on the 2A Control Element Drive motor generator set opened for an unknown reason. Shortly thereafter, various Control Rod trouble alarms annunciated and the Control Rods dropped into the core due to loss of power on the Control Rod busses. The loss of power to the Control Rod busses initiated a turbine trip, which in turn generated a Reactor Protective System trip signal on loss of load. All Control Rods inserted fully. Standard Post Trip actions were completed satisfactorily with all safety functions met. "Following the trip, it was noticed that the 2A1 non-safety related 6.9KV electric busses did not automatically transfer to the Startup Transformers. This resulted in the loss of power to the 2A1 and 2B2 Reactor Coolant Pumps and the 2A Main Feedwater pump. The cause for the failure to transfer is being investigated. Due to the loss of the Reactor Coolant Pumps, the Reactor Coolant System was manually depressurized to 1850 psia per plant procedures. "The Auxiliary Feedwater Actuation System automatically actuated on low Steam Generator level as expected for reactor trips from high power level. Steam Generator level is currently being maintained by the 2B Main Feedwater pump. "The reactor is currently stable in Mode 3 and the cause of the trip is under investigation." No primary safety or reliefs lifted during the transient. Decay heat is being removed via the bypass valves to the main condenser. The AFW pumps are operating but not supplying feed to the Steam Generators. The licensee had not verified whether any atmospheric dumps cycled. There is no known Steam Generator tube leakage at this time. Normal offsite power remains available and there was no impact on Unit 1 which is operating at 100% power. Unit 2 will remain in Hot Standby pending development and completion of corrective actions. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37840 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2001-03-14 14:10 | 2001-03-14 20:13 | 2001-04-24 | HPCI DECLARED INOPERABLE DUE TO FAILURE OF EXHAUST LINE VACUUM RELIEF VALVES TO FUNCTION DURING IST TESTING "During routine testing of the Unit 2 High Pressure Coolant Injection system (HPCI) exhaust line vacuum relief valves (VRV), it was discovered that both VRVs failed to open at their In Service Test (IST) required differential pressure value. The Unit 2 HPCI system has been declared inoperable and repairs are in progress. "This event is being reported in accordance with 10CFR50.72(b)(3)(v)(D) due to a failure of a single train system which prevents fulfillment of a safety function." With HPCI inoperable this places Unit 2 in a 14-day Limiting Condition of Operation. All other ECCS systems have been verified operable. The licensee informed the NRC resident inspector. * * * RETRACTION ON 04/24/01 AT 1254 ET BY STEVE BECK TAKEN BY MACKINNON * * * The original design function of the affected vacuum relief valves was to prevent damage to the HPCI exhaust line rupture disks. A failure of the rupture disks would result in steam being discharged into the HPCI Room and subsequent isolation of the HPCI system on high room temperature. A modification to the rupture disk installed backing support plates to ensure that repetitive vacuum conditions in the exhaust line would not result in fatigue failure of the rupture disks. As a result of the modification, the vacuum relief valves are no longer required to open to protect the rupture disks. Based on an Engineering evaluation, it was concluded that the HPCI exhaust line vacuum relief valves design function is not required to support HPCI system operability. NUREG 1022, Rev. 2, allows "removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevent the system from performing its function)." In this case, HPCI was removed from service for planned maintenance per plant procedures and Technical Specifications. The condition found (vacuum relief valve inoperability) would not have prevented HPCI from performing its safety function; therefore this event is not reportable per 10CFR50.72(b)(3)(D) or 10CFR50.73(a)(2)(v). R1DO (David Silk) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37839 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-14 15:08 | 2001-03-14 18:02 | 2001-05-14 | UNIT 2 EXPERIENCED AN UNEXPECTED LOSS OF SHUTDOWN COOLING DUE TO TRIPPING OF VARIOUS POWER SUPPLY BREAKERS "Unit 2 was in Mode 5 on the fifth day of its 10th Refuel and Inspection Outage. At 1508 hours, the unit experienced an unexpected loss of Division 1 RPS Power supply. The loss of power was a result of the Electrical Protection Assembly (EPA) A & C breakers and motor generator output breaker tripping. The cause is under investigation. "The loss of power caused the RHR Shutdown Cooling suction valve HV251F009 to close. This is a common suction valve to both divisions of RHR and resulted in the complete loss of RHR Shutdown Cooling. The reactor currently has its head removed with the reactor cavity flooded up with the gates to the spent fuel pool removed. A Supplemental Decay Heat Removal system was in service at the time, but was not considered fully capable of decay heat removal. Reactor coolant temperature increased less than 2 degrees during the 37 minutes SDC was out of service. The RPS power supply was switched to its alternate supply and SDC was restored at 1545 hours. In accordance with 10CFR50.72(b)(3)(v) this represents a loss of a safety system which removes residual heat and requires an 8 hour ENS call. In addition to the isolation of RHR SDC, RWCU isolated due to containment valve HV244F001 closing, and Unit 2 HVAC Zone 3 (refuel floor) isolated. These isolations constitute an actuation of a Containment Isolation signal that affected multiple systems, and is reportable per 10CFR50.72(b)(3)(iv)(A)." Peak temperature after losing SDC was 105 degrees. The licensee informed the NRC resident inspector. ***** UPDATE RECEIVED AT 1542 ON 05/15/01 FROM GORGON E. ROBINSON TO LEIGH TROCINE ***** The licensee is updating this event notification to change the event reporting requirements from an 8-hour event notification to a 60-day notification of invalid system actuations. The following text is a portion of a facsimile received from the licensee: "ENS Notification # 37839 documented that the loss of the Unit 2 Division 1 RPS power supply on 3/14/01 required an 8-hour ENS notification for actuation of a containment isolation signal that affected multiple systems and a loss of a safety function required to remove residual heat (10CFR50.72(b)(3)(iv)(A) and 10CFR50.72(b)(3)(v)(B), respectively). After subsequent evaluation of the event, the reportability determination is being changed to retract the 8-hour notification and provide the required a 60-day ENS notification for an invalid actuation that affected multiple systems. See the discussion below." "The initial condition was reported per 10CFR50.72(b)(3)(v)(B), loss of safety function that is needed to remove residual heat. A subsequent review of the event and reporting requirements by PPL has concluded that the event is not reportable per this section of the rule. In this case, the 37-minute interruption did not and would not have prevented the fulfillment of the RHR shutdown cooling function." "The original notification stated that an actuation of a containment isolation signal that affected multiple systems was reportable as an 8-hour ENS notification per 10CFR50.72(b)(3)(iv)(A). For this event, a half-scram while the unit was shutdown, was the result of an invalid signal since it was due to loss of RPS power. Except for critical scrams, invalid actuations are not reportable by telephone under 10CFR50.72. Therefore, this 60-day optional report, as allowed by 10CFR50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of general containment isolation signals affecting isolation valves in more than one system." "At 15:08 on March 14, 2001, with Unit 2 in Mode 5 at 0% power, the primary power supply to the 'A' Reactor Protection System (RPS) power distribution panel was lost when the Motor-Generator (MG) Set generator in that division failed. This resulted in Primary Containment Isolation System actuations including isolation of [a] Residual Heat Removal shutdown cooling suction valve and other automatic system initiations. RPS as well as other plant systems functioned as designed in response to the event. The 'A' RPS distribution panel was swapped to alternate power, and all isolations were reset by 16:10. The loss of power was due to a failure of the 'A' RPS M-G set generator. The generator failed due to a manufacturing defect of an internal conductor connection. The failed generator was replaced, and other like-in-kind generators will be inspected. There were no safety consequences or compromises to the health or safety of the public. This event has been entered into the site-specific corrective action program for resolution. Internal and industry events were reviewed to assess if a generic problem exits with this type of generator. No evidence of similar failures was found, which indicates that a generic problem does not exist." "The NRC site Resident Inspector has been notified." The NRC operations officer notified the R1DO (Rogge) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0
37838 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2001-03-09 06:45 | 2001-03-14 16:37 | 2001-03-14 | HIGH PRESSURE COOLING INJECTION (HPCI) RENDERED INOPERABLE DUE TO FAULTY BATTERY CHARGER "Investigation of the failure of battery charger 1R42-S031 on 3/9/2001 (reference Condition Report 2001001827) has determined that the Unit 1 HPCI system was inoperable from the time of receipt of the first 'HPCI System Inverter Circuit Failure' annunciator until the time charger 1R42-S031 was removed from service. During this time (approximately 15 to 20 minutes), the HPCI system inverter was tripping on high voltage and resetting automatically when voltage levels returned to normal. The voltage fluctuations causing the inverter to trip and reset were caused by an internal fault in charger 1R42-S031: a bad fuse was making intermittent connection resulting in intermittent firing of the charger's silicon-controlled rectifiers (SCRs) and rapidly changing current and voltage outputs. These fluctuations and the random tripping of the HPCI system inverter rendered the HPCI system unreliable, and hence inoperable, until the cause of the fluctuations was corrected, that is, until the charger was removed from service. Determined to be reportable 3-14-2001 @ 1338 EST." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37837 | 0 | CHRISTIANA CARE HEALTH SERVICE |  |  |  |  | 2001-03-14 07:10 | 2001-03-14 13:15 | 2001-03-14 | 24-HOUR REPORT INVOLVING POTENTIAL PERSONNEL OVEREXPOSURE At approximately 0710EST a technician at the Christiana Care Health Services spilled a tube in the corner of the hot lab containing between 30-50 ml of Technetium-99m milked from the generator. The activity was measured as 650 millicuries immediately prior to the spill. The hot lab was promptly evacuated. There was no personnel contamination involved. Initial rad surveys of the affected area showed between 80 and 200 mr/hr prior to decontamination. Following final decontamination measured rad levels taken at 1000EST were approximately 10 to 40 mr/hr. Access to the lab has been restored, however, the corner area is taped off and covered by plastic to minimize the spread of contamination and allow for decay. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | DE | HOS |  | 20.2202(b)(1) |  |  |  | 0
37836 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-03-14 10:30 | 2001-03-14 13:11 | 2001-03-14 | OFFSITE NOTIFICATION TO VARIOUS AGENCIES CONCERNING AN OIL SPILL ONSITE "At 10:30 AM on 3/14/2001 the following agencies were notified of an oil leak on site. New Hampshire DES National Response Center US Coast Guard Environmental Protection Agency (EPA) "About 1 gallon of oil was observed on top of a concrete pad near the vehicle maintenance shop. The oil came through the pad via cracks in the concrete. There is an oil line that runs under this pad from a 6000 gallon above ground tank. The tank has been isolated, local storm drains have been protected and a contractor is on site to excavate the area and determine the extent of the problem. The notifications were made as a precautionary measure since the quantity of oil under the concrete pad is unknown. The oil was first observed on 3/13/01 at approximately 1600." The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37835 | 0 | SAINT VINCENT MEDICAL CENTER |  |  |  |  | 2001-03-12 17:00 | 2001-03-14 09:17 | 2001-03-14 | DEFECTIVE IODINE-125 SEEDS. One hundred thirty-three (133) I-125 sources each with an activity of approximately 0.3 millicuries were received by the Saint Vincent Medical Center located in Bridgeport, CT. The I-125 seeds are used for prostate implants. Upon receiving the sources they were counted and the seeds' activity was checked. They were then placed in a sterilization tray which has 10 wells (the seeds were distributed among the 10 wells). The tray has a cover which allows for steam circulation. The same day or the following morning the trays were sent forth to be sterilized. After sterilization the seeds are taken out of the sterilizer and the sterilizer surveyed. Nothing detectable was noted. Later that day the seeds were removed from the wells and loaded into needles. At the conclusion of this process the licensee did a survey of the area. It was then when the licensee found a rather high level of radiation, not high enough to be a seed. After further investigation the licensee concluded that the sterilization tray was contaminated and highly contaminated in the area of at least 5 of the 10 wells. The licensee's assumption is that one or more the seeds opened up during sterilization. The seeds were fine prior to sterilization. Total estimated removable contamination found on the tray was 4 microcuries. A more through survey was performed on everything that had came in contact with the tray. It was found that the inner wrapping that goes around the tray before it is placed in the sterilizer was contaminated. Nothing else that had come in contact with the tray was found to be contaminated. Personnel do not seem to be contaminated. The two people who were involved in the loading process are scheduled to have thyroid uptake exams today. This incident was reported to the seed manufacturer, Best Industries, and the seeds will be shipped back to them. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21 |  |  |  | 0
37834 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-03-13 14:45 | 2001-03-13 18:07 | 2001-05-11 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE DUE EXCESSIVE MOISTURE IN LUBE OIL "At approximately 1100 hours, operators observed oil puddled around the HPCI lube oil sump vents and observed a slightly higher than normal sump level. The system engineer was consulted and recommended lowering sump level and sampling for moisture. "At 1445, water was observed in the sample taken from the HPCI lube oil sump. The amount of water observed (approximately 1/2 gallon) was such that compliance with a maximum recommended lube oil moisture content of 5% could not be assured. A conservative decision was made to declare HPCI inoperable. The system is inoperable but available. The plant is in a 7-day LCO per T.S. 3.5.C." The licensee informed the NRC resident inspector. ***** RETRACTION RECEIVED AT 0933 ON 05/11/01 FROM ART ZAREMBA TO LEIGH TROCINE ***** The initial notification regarded the HPCI system being declared inoperable because of an unknown quantity of water in the lube oil sump. The licensee subsequently drained, cleaned, and refilled the lube oil sump and determined exactly how much water intrusion had occurred. The licensee's engineering evaluation determined that the technical requirements were not exceeded (based on the acceptance criteria for the percentage of water in the system) and that the HPCI system was in fact operable. Therefore, the licensee is retracting this event notification. The licensee notified the NRC resident inspector. The NRC operations officer notified the R1DO (Cook). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37833 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-03-13 14:15 | 2001-03-13 17:18 | 2001-03-13 | SAFETY EQUIPMENT FAILURE RELATED TO STEAM LEAK ON AUTOCLAVE #3 "At 1415 hours on 3/13/01 after questioning by the Senior NRC Resident Inspector concerning a steam leak on autoclave (A/C) #3 in the X-344, it was discovered that an as found reading (pressure decay test) was not performed on A/C #3 prior to the Maintenance department replacing the o-ring during the evening of 3/12/01. Without performing the pressure decay test there is no possible method to verify if the o-ring would have performed its safety function. This test would have been used to determine if an observed steam leak on A/C #3 that occurred at 1050 hours during the early phase of an applicable heating mode on 3/12/01 would have been classified as a Safety Equipment Failure per the plant's NRC Event reporting Criteria. "Since the As Found Reading (pressure decay test) was not performed, the failure of the o-ring as observed by the steam leak on A/C #3 in the X-344 building, is being reported as a 'Safety Equipment Failure' per table 6.9.1 section J of the SAR." Operations has informed the NRC resident inspector and the DOE site representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0
37832 | 0 | PENNSYLVANIA STATE UNIVERSITY |  |  |  |  | 2001-03-13 | 2001-03-13 11:39 | 2001-03-13 | MISSING TRITIUM TUBE FROM EXIT SIGN During removal of tritium exit signs from the campus, one of the signs in the Academic Projects Building was found to be missing one of four tubes of tritium. The tube originally contained a maximum of 6 Curies in April, 1983 and 2.3 Curies today, it is not considered a hazard to the public. The licensee does not know if the tube was missing when the sign was installed or has been removed since. The sign was originally in a different building. The sign is a Everglow Safety Sign, model #710-1 and serial #14867. The licensee will contact NRC Region 1 (Thompson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37831 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-03-12 17:45 | 2001-03-13 08:24 | 2001-03-14 | NRC BULLETIN 91-01 - 24 HOUR REPORT The following is taken from the faxed report: ON 3/12/01 AT 1745 HOURS X-705 OPERATIONS PERSONNEL WERE CONDUCTING ROUTINE INSPECTIONS OF THE TUNNEL BASEMENT AREA WHEN THEY IDENTIFIED THAT THE SCAVENGER SYSTEM WOULD NOT OPERATE IN THE 'AUTOMATIC' OR THE 'MANUAL' MODE. NCSA-0705_035.A05 REQUIREMENT 5d STATES "THE SCAVENGER PUMP SWITCH VERIFIED NOT TO BE IN THE 'MANUAL' MODE WHILE UNATTENDED." THE STATUS OF THE SCAVENGER PUMP SWITCH WAS IN 'AUTOMATIC' MODE BUT IT WAS IDENTIFIED WHEN TESTED THAT THE PUMP WOULD NOT OPERATE IN THE 'AUTOMATIC' OR THE 'MANUAL' MODE BUT WOULD OPERATE IN THE 'MANUAL BY-PASS' MODE. THIS VIOLATES THE INTENT OF THE NCSA REQUIREMENT WHEREBY THE PUMP WOULD NOT START AUTOMATICALLY NOR WAS THE PUMP MANNED IN THE 'MANUAL' MODE. THE FACT THAT A TIME FRAME EXISTED WHEN THE PUMP WOULD NOT START IN THE 'AUTOMATIC' MODE AND DURING THIS SAME TIME FRAME THE PUMP WAS NOT MANNED IN THE 'MANUAL' MODE CONSTITUTES A LOSS OF ONE CONTROL WHICH IS RELIED ON TO MEET THE DOUBLE CONTINGENCY PRINCIPAL, SAFETY SIGNIFICANCE OF EVENTS: LOW = The failure of the Scavenger Pump to operate In the automatic mode represents the loss of one control (5d) relied upon for double contingency. The failure of the Scavenger Pump to operate in the automatic mode would allow the Scavenger System Storage Tank to overflow and solution to collect on the floor of the basement The size of the floor area and the remaining control on the amount of solution transferred make a criticality nearly non-credible. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Six of eight Fissile Solution Storage Banks fail in such a way that all of the Fissile Solution collects in the tunnel basement floor. This is sufficient Fissile Solution to exceed the safe depth of 1.5 inches for solutions containing greater than 100 wt.% U-235. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Volume Control was lost when the Scavenger Pump failed. Geometry Control was maintained throughout this event. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OP CRITICAL MASS): The Tunnel Storage System receives Fissile Solution for various operations in the X-705 Facility. The most likely form is UO2F2 in solution with a maximum enrichment of 100 wt.% U-235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Automatic Mode of Scavenger Pump failed. Pump not manned in Manual Mode, 5d Control lost. Note: Pump would operate in the Manual By-Pass Mode but the pump was unmanned. Since no Fissile Solution leaked and allowed >1.5 inches of solution to collect on the floor the second control was maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Entered Anomalous Condition. Assigned Operator to man the system until facility status was verified. Immediately verified no evolutions in progress that could challenge the Scavenger System. Tagged out the power supplies to all facility equipment that could challenge the Scavenger System. Emergent Work authorized by Plant Shift Superintendent for repairs to Scavenger System. Called in off-duty Nuclear Criticality Safety Staff to assess compliance, create Anomalous Condition Report and oversee the efforts to establish the lost control. Control established at 2038 hours by manning the pump controls. The licensee notified the NRC Resident Inspector as well as the DOE representative. * * * UPDATE 1808EST ON 3/14/01 FROM JOE HALCOMB TO S. SANDIN * * * The following update was submitted to clarify the above report: "03/14/01 - Update #1 - The Nuclear Criticality Safety (NCS) Group performed a follow up assessment of the above event. A revision to the NCS Anomalous Condition Report was issued and it determined that the malfunction of the scavenger system did not constitute a loss of an NCS control and that double contingency was maintained. The previous issue would not have been reported based on the revised NCS Anomalous Condition Report." The licensee informed the NRC resident inspector and DOE site representative. Notified R3DO(Wright) and NMSS(Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37830 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-03-12 18:40 | 2001-03-12 20:47 | 2001-03-12 | UNANALYZED CONDITION DUE TO AN INADEQUATE HELB BARRIER DURING A POSTULATED FEEDWATER LINE BREAK "An unanalyzed plant condition may exist regarding a HELB barrier within the turbine building. The HELB barrier in question separates two different trains of essential 480 volt motor control centers and may be inadequate if subjected." An Extent of Condition investigation of High Energy Line Break (HELB) barriers determined that a barrier separating two adjacent areas (upper and lower) in the turbine building may not withstand a 0.6 psid due to a postulated heated feedwater line break. This could result in the loss of both trains of equipment controlled by 480 volt MCCs. The licensee will develop appropriate corrective action. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37829 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2001-03-12 08:31 | 2001-03-12 16:59 | 2001-03-12 | LOSS OF VARIOUS COMMUNICATIONS CAPABILITIES DUE TO SEVERE WEATHER "Following a series of severe thunderstorms that passed through the Baton Rouge area during the night it was discovered and reported to the Main Control Room at 0831 that all offsite sirens, State and Local Hotlines, the ESP Computer Notification System and Emergency Preparedness Radio were not available. Commercial telephones and NRC ETS phone lines were available during this period and continue to be available. The Offsite sirens were transferred to the backup transmitter within 10 minutes of discovery and restored as of 0828. As of 1500 hours, all but 2 State and Local Hotlines were restored. Efforts to restore the remaining communications systems continue." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37828 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-03-12 10:28 | 2001-03-12 16:23 | 2001-03-12 | 24-HOUR VIOLATION OF LICENSEE CONDITION DUE TO EXCEEDING THERMAL POWER LIMIT "License restriction of 3445 MWth for the unit was exceeded. Highest reading N-16 power was 104.93%. Highest reading Nuclear Instrumentation Power was approximately 97%. This event was initiated by a failure of Main Turbine EHC fluid pressure switch, which closed [the] extraction steam valves to [the] feedwater heaters. Unit has been stabilized at 85% Reactor Power." Control Room Operators received a feedwater heater high level alarm alerting them to the isolation of extraction steam to both the high and low pressure feedwater heaters on both feedwater trains. The isolation of extraction steam caused a decrease in feedwater temperature thus adding positive reactivity which increased reactor thermal power. Operators responded promptly by reducing turbine load. The licensee plans on replacing the failed pressure switch and resuming full power operations. The licensee informed the NRC resident inspector. | 0 | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
37827 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-03-12 00:45 | 2001-03-12 11:32 | 2001-03-12 | A supervisor contractor was determined to be under the influence of alcohol during a for cause fitness for duty test. The individuals access to the protected area was terminated. Call HOO for further details. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 26.73 |  |  |  | 0
37826 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2001-03-12 10:30 | 2001-03-12 11:25 | 2001-03-12 | OFFSITE NOTIFICATION DUE TO FUEL OIL SPILL The licensee notified the Maine Department of Environmental Protection (DEP) about a fuel oil spill. The spill was from a fuel tank on a portable compressor, at about 1015 EST the fuel line broke dumping about 30 gallons on the ground. About 20 to 25 gallons went into the storm water system and ended up in the adjacent cove. The licensee is working on containing the spill on the water and has contained the balance of the spill on the ground. The licensee has also notified the State Nuclear Inspector, the National Response Center, and will notify NRC Region 1 Decommissioning Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37825 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-03-11 01:19 | 2001-03-11 04:28 | 2001-03-11 | TECHNICAL SPECIFICATION REQUIRED MANUAL REACTOR TRIP DURING PLANT SHUTDOWN At 0109 EST on 3/11/01 with the reactor already subcritical during the insertion of control bank 'B', the licensee noted that the group 2 step counter stopped moving at 53 steps. Technical specification 3.1.3.3 requires the reactor trip breakers to be opened within 15 minutes and at 0119 EST the licensee performed a manual reactor trip opening the trip breakers. The plant is entering a refueling outage and the problem will be corrected before startup. The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37824 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-03-10 15:15 | 2001-03-10 22:29 | 2001-03-22 | TECHNICAL SPECIFICATION (TS) SHUTDOWN "At time 2058 (EST) on 03/10/01, Unit 2 commenced a normal rampdown to cold shutdown for refueling. The unit was in action statement that expires at 1515 on 03/11/01. The action statement of TS 3.6.1.3.b had been entered at 1515 on 03/10/01 when 2-PT-62.1 failed. This test was a routine pre-outage test on the containment equipment hatch personnel access air lock. The unit shutdown was planned for this date and time. Repairs to the failed component will be made with unit in mode 5." The licensee thinks that the equipment hatch inner air lock door equalizing valve is leaking by. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1301 EST ON 3/22/01 BY JIM CROSSMAN TO FANGIE JONES * * * The licensee is retracting this event notification. The original notification was conservatively made. At the time the plant had planned to shutdown for a refueling outage and it was unknown at the time if repairs could have been made within the 24 hour time clock required by technical specifications. The problem with the hatch turned out to be minor in nature and easily corrected, thus the plant would not have been required to shutdown per the technical specifications. The problem was excessive amount of hardened grease applied to the seal surface. The grease was removed and the air lock successfully passed leakage testing all within about one hour. The licensee notified the NRC Resident Inspector. The R2DO (Mark Lesser) was notified. | 0 | 71 | 0 | 0 | 72 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37823 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-03-10 17:05 | 2001-03-10 18:59 | 2001-04-26 | DIFFERENTIAL PRESSURE TO OPEN THE SUPPRESSION CHAMBER TO DRYWELL VACUUM BREAKERS DISCREPANCIES WERE IDENTIFIED. During review of Inservice Testing requirements, while the plant was in shutdown, discrepancies were identified with acceptance criteria for the torque values used to determine the equivalent differential pressure to open the suppression chamber to drywell vacuum breakers. The measured torque values indicate that the differential pressure required to fully open the suppression chamber to drywell vacuum breakers would be greater than that assumed in containment analyses. The suppression chamber to drywell vacuum breakers insure that the 2 psig external design pressure for the primary containment drywell suppression chamber and vent system is not exceeded and containment integrity is assured. The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTION ON 04/23/01 AT 1805ET BY JIM MCKAY TAKEN BY MACKINNON * * * Retraction of notification made on March 10, 2001. The notification stated that discrepancies were identified with acceptance criteria for the torque values used to determine the equivalent differential pressure to open the suppression chamber to drywell vacuum breakers. The measured values indicated a greater differential pressure required to fully open then assumed in containment analysis. Upon further evaluation and review of the containment analyses, the results of the containment analysis were effectively independent and not adversely impacted by the suppression [chamber to drywell vacuum breaker full open differential pressure assumption in the range of concern. Therefore, an unanalyzed condition that significantly degrades the plant safety did not exist.] R3DO (Tom Kozak) has been notified. NRC Resident Inspector will notified of this retraction by the licensee * * * UPDATE 1000EDT ON 4/26/01 TO S. SANDIN * * * The above retraction was updated to include information shown in brackets which had been submitted but inadvertently omitted from the report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37822 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-10 04:14 | 2001-03-10 04:50 | 2001-03-10 | COURTESY NOTIFICATION FOR ENTRY INTO 10TH REFUELING "This is a Courtesy Notification and does not fall within 10CFR50.72 Guidelines. "Susquehanna Unit 2 was manually shutdown on 3/10/01 to enter its 10th Refueling and Inspection outage. At 1630 hours on 3/9/01, a controlled shutdown was commenced by reducing recirc flow and then inserting control rods. At 03:45 on 3/10/99, the Main Turbine was manually tripped with power at 17.5%. At 04:14 with power at 21% the reactor mode switch was taken to shutdown placing the unit in condition 3. All control rods fully inserted. Rx Water level dropped to approximately -1 inch as recorded on wide range instrumentation, and was restored using Feedwater. There were no ECCS initiations or Diesel Generator starts. No safety/relief valves lifted. There were no challenges to containment or fuel as a result of the shutdown. "The shutdown is continuing according to schedule and is scheduled to return to service in 35 days." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0
37821 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-03-09 12:51 | 2001-03-09 20:46 | 2001-03-12 | LOSS OF BOTH CONTROL ROD DRIVE MOTOR GENERATORS CAUSES REACTOR TRIP During performance of work on the 'B' Rod Drive Motor Generator set, the output breaker for 'A' Rod Drive Motor Generator set opened causing a loss of power to the Rod Control System. The cause of the 'A' Rod Drive Motor Generator set output breaker opening is being investigated. With a loss of power, all rods were de-energized and inserted into the core. Rod K-10 developed an alarm and the problem was determined to be a faulty circuit card. The circuit card was replaced and the problem corrected. This event resulted in a Reactor Protection System (RPS) actuation, when rods were inserted, an Over Temperature delta T (OTdeltaT) trip was generated which generated the RPS actuation. After the RPS system actuated, an Auxiliary Feedwater System actuation was generated. It was concluded this event is reportable per 10CFR50.72(b)(3)(iv)(A) since: (1) The actuation of the Reactor Protection System occurred after the rods were at the bottom of the Reactor core (i.e. shut down) as indicated by computer point alarm printout. The NRC Resident inspector was notified of this event by the licensee. * * * UPDATE 1500EST ON 3/12/01 FROM ROBERT BARTON TO S. SANDIN * * * The licensee is updating this report with the following information: "Update to the NRC Notification of Reactor Trip due to Loss of Both Rod Drive Motor Generator Sets at Callaway Event Number 37821. "This 4-hour call is being made to the NRC 1) to inform the NRC that a Notification was made to the Missouri Public Service Commission reporting the Reactor Trip due to the loss of both Rod Drive Motor Generators which resulted in an outage expected to last longer than 72 hours and 2) to clarify information presented on March 9, 2001 concerning the Reactor Trip due to a loss of electrical power to the Rod Control System at the Callaway Plant. Time of Notification to NRC Ops Center 1400 Event Number assigned by NRC 37821 NRC staff contacted at Ops Center Steve Sandin Event Time (time of notification) 1400 Event Date (date of notification) 3/12/0 1 Mode/Power before event 2/1 percent Reactor Power Mode/Power after event 2/1 percent Reactor Power Event Classification 10CFR50.72(b)(2)(xi) Was NRC Resident notified Yes Was State notified No Was other local government agencies notified Yes Is media press release planned No Anything unusual or not understood about the event N/A Did all systems function as required N/A "1) The following was reported to the Missouri PSC at 1248, 3/12/01: 'The following is a report to the Missouri Public Service Commission (MPSC) involving a Reactor Trip due to a loss of both Rod Drive Motor Generators at the Callaway Plant and is reportable under 4CSR240-20.080(3)(B) because the outage is expected to last longer than 72 hours. 'At 1251 on March 9, 2001, work was commencing on one Rod Drive Motor Generator when the alternate Rod Drive Motor Generator electrical output breaker failed open. This caused the Reactor Control Rods to be de-energized and insert into the Reactor core. Thc rod insertion shut the Reactor down and the plant continues to remain shut down to support repairs on equipment not related to the primary Reactor systems.' "2) On March 9, 2001, the NRC Ops Center was informed of the Reactor Trip at Callaway that occurred because of a loss of both Rod Control Motor Generators. During the notification, it was mentioned that the press had been notified and a copy of the statement faxed to the NRC Ops Center also reflected this. What was not covered was the time of the news release. The news media was faxed a release at 1645 on 3/9/01. This information is being supplied to ensure clarity that the NRC had been notified of a news release within the required 4-hour time limit. "The NRC Resident Inspector was notified of this event by the licensee." Notified R4DO (Johnson). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) |  |  | 0
37820 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2001-03-08 12:00 | 2001-03-09 15:57 | 2001-03-09 | MEDICAL MISADMINISTRATION The following text was taken from an email sent to the NRC's Operations Center from the State of Illinois. The RSO at Loyola University Medical Center, IL-01131-02, Maywood, IL, called at approximately 12:30 p.m., 3/9/01, to report a reportable event involving the Cordis Intravascular Brachytherapy (IVB) system. He stated that two patients undergoing cardiac therapy on the previous day, had been treated with the Ir-192 seeds to prevent restenosis in a stent. The prescribed dose was 8 gray (800 rads) to the tunica media layer of the heart. However, the calculated dose to one of the patients was12.5 gray (1250 rads) (56% overdose) and 14.3 gray (1,430 rads) (79% overdose). The cause of the problem appears to be due to a new method for this institution to determine the actual dose to the intended organ. In the past, dwell times were based on 14 gray being delivered at 2 mm distance from the radioactive sources. This new procedure requires an intravascular ultrasound device to be used and measurements from the intended treatment portion of the heart and the sources are determined. These measurements then determine the dwell time for the prescribed dose. This new measurement method and possible communication problems while taking the measurements and using the measurements contributed to the problem. No further use of this system will be conducted until these problems are resolved and the Radiation Safety Committee and the Department are satisfied that there will be no recurrence. . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | HOS | [5 empty] | 0
37819 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2001-02-16 12:00 | 2001-03-09 15:18 | 2001-03-09 | Agilent Technologies reported the loss of two electron capture detectors. Each detector contains a 15 mCi Ni-63 source. Because the Ni-63 is plated on the inside of the device and Ni-63 is a low energy Beta emitter, the risk of exposure to the public is low. The detectors were last accounted for in December 1995. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37818 | 0 | PALISADES | 1 |  |  | [1] CE | 2001-02-08 14:37 | 2001-03-09 09:31 | 2001-03-09 | MISSING LOW ACTIVITY SOURCE "During a routine inventory of licensed radioactive sources, one low activity, mixed isotope source could not be accounted for. The source contained a total of approximately 0.992 microcurie, of which approximately 0.154 microcurie was americium-241. Since the quantity of americium-241 in this source was more than ten times greater than the quantity specified in Appendix C of 10CFR20, a telephone report is required in accordance with 10CFR20.2201(a)(1)(ii). None of the other isotopes in the source exceeded reportable quantities specified in Appendix C. The low activity and relatively large physical size of the source are such that it would not be a significant radiological hazard. A search of the site failed to locate the source. It is not likely that a person could have inadvertently carried the source out of the radiologically controlled area (RCA) on his body since the source would have caused the RCA exit monitors to alarm. We have concluded that the source was most likely discarded by mistake inside the RCA into a yellow trash bag with other radioactive waste. The low level radioactive waste from the time period in question was shipped off site to a licensed vendor and has been incinerated." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0
37817 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-03-09 01:45 | 2001-03-09 07:18 | 2001-03-09 | 24 Hour Notification of High Pressure Fire Water Fire Protection System Impairment per Station Administration Order (SAO) 124 Item 64 and SAO-703 Addendum I Item 2.b.1.b.i. "At 0145 on March 9, 2001, the high pressure Fire Water Protection System is degraded due to planned maintenance work. The inner and outer high-pressure fire headers are split to provide protection for work on the valves for 12 Fire Main Booster Pump. 12 Fire Main Booster Pump is inoperable during this tag-out. The Diesel Fire Pump is in service to maintain header pressure for the outside fire header. 11 Fire Main Booster Pump is in operation providing fire header pressure for the inside fire header. Contingency hoses have been staged to provide fire water supply to cross connect the inside and outside headers in the event of a failure on either header. SAO-703 Addendum I Item 2.a.1.a states one fire main booster pump out of service is a 7-day action statement to return it to operable status. The headers being separated or any part of the fire protection piping or valves not being able to perform its function other than the specific instances described in SAO-703 requires an alternate fire protection system shall be established. The alternate fire protection system was established within 24 hours to ensure compliance with SAO-703 as described above. A special report will be submitted to the NRC Regional Administrator of the Region 1 Office outlining this event within 14 Days." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
37816 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-03-09 01:30 | 2001-03-09 04:30 | 2001-05-15 | MODE CHANGE DUE TO LITERAL INTERPRETATION OF REQUIREMENTS "To meet compliance with literal interpretation of Tech Spec 3.7.A.5 and 3.8.B.6, containment venting and purging using SBGT is required above 'Cold Shutdown.' Plant is < 212°, all rods in BUT mode switch was in 'Refuel.' To comply with Tech Specs, a Tech Spec shutdown with mode switch was performed. All rods were already in but it wasn't a preplanned shutdown evolution. Other similar 'Cold Shutdown' Tech Spec compliance issues are being looked at." An automatic scram signal was generated when the mode switch was taken to the 'Shutdown' position. Although all control rods were already inserted, the licensee considers this action to be reportable as a valid safety system actuation. The NRC resident inspector will be informed of this event by the licensee. **** RETRACTION RECEIVED AT 1641 EDT ON 05/15/01 FROM PATRICK DECKER TO LEIGH TROCINE **** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "[...] On [03/09/01], we reported the failure to literally comply with [Technical] Specification 3.7.A and 3.8.B.6. This event is being retracted since 1) the requirement to use SBGT 'above' Cold Shutdown does not apply to plant conditions where the plant is below the Cold Shutdown temperature of 212 degrees F with the mode switch in 'refuel,' and 2) moving the mode switch back to shutdown from 'refuel' was required to comply with a prerequisite of an approved plant procedure. Therefore, this was part of a preplanned sequence." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Parker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Refueling; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0
37815 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-03-05 16:08 | 2001-03-08 13:04 | 2001-05-15 | LOW PRESSURE CORE SPRAY STRUCTURAL ANALYSIS DID NOT CONSIDER ALL POSSIBLE FLOW CONDITIONS "On March 5, 2001, it was discovered that the structural analysis of in-vessel Core Spray piping did not consider all applicable flow conditions. A notification should have been made at that time because the effect of the unanalyzed condition on degradation of plant safety was not considered with respect to all plant operating conditions (i.e., the plant was shut down at the time of discovery). Preliminary analysis results indicated that previous analyses are bounding." This issue will be resolved before the next plant startup. The licensee will notify the NRC resident inspector. **** RETRACTION RECEIVED AT 1641 EDT ON 05/15/01 FROM PATRICK DECKER TO LEIGH TROCINE **** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "[...] On [03/08/01], we reported that structural analysis of the in-core spray piping did not consider all the applicable flow conditions. Upon re-evaluation, this is not reportable since: 1) this condition only affected one train of core spray piping, and 2) the flaw condition believed to have been overlooked was determined [analytically] to be bounded by [existing] analyses." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Parker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37814 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-03-08 09:59 | 2001-03-08 11:44 | 2001-03-08 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISOR A non-licensed supervisor was determined to be under the influence of alcohol during a random test. The employee's access has been terminated. The licensee will inform the NRC resident inspector. Contact the Operations Center for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.73 |  |  |  | 0
37813 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-03-07 09:00 | 2001-03-08 01:03 | 2001-03-08 | 24 HOUR NRC BULLETIN 91-01 REPORT "On 3-7-01 at 0900 hours , in preparation to implement NCSA-PLANT091 it was discovered that PORTS has a plutonium-239 (Pu-239) source that exceeds the mass control limit of the unimplemented NCSA. This new NCSA was Plant Operations Review Committee (PORC) approved but is not activated. NCSA-PLANT091 establishes minimum masses for several fissile isotopes for determining when Nuclear Criticality Safety (NCS) controls are required. For Pu-239, the control limit is 7.2 grams. The sealed source contains 32 grams of Pu-239. An anomalous condition was entered and a boundary established around the source pending NCS review. Upon further review, NCS determined that there is not an active NCSA/NCSE to control the Pu-239 source. The storage of the Pu-239 source is considered unanalyzed since there is not an active NCSA/NCSE documenting the double contingency of this storage. "The safety significance of this event is very low. The Pu-239 source is in a storage unit at the X-326 Health Physics (HP) Source Storage Vault. The storage unit provides spacing from other materials and there were no other fissile materials near the storage unit that would require NCSA controls. Spacing from other fissile material is not an issue. NCSA-PLANT021 determined that the safe mass of Pu-239 is 207 grams. The source contains 32 grams Pu-239 and is well below the safe mass value of 207 grams. Double contingency exists, but has not been formally documented in an implemented Nuclear Criticality Safety Evaluation. "The discovery of this source is a legacy issue This source was transported to PORTS in 1961 from offsite. This source has not been used since NRC regulation of PORTS. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is very low. The discovery of this source is a legacy issue. This source was transported to PORTS In 1961 from offsite. The subcritical mass limit for Pu-239 per ANSI/ANS-8.15 is 450 grams. "This source has not been used since coming under NRC regulation. There are no Radiation Work permits (RWP) or procedures that use this source. There is no reason to believe that the source has been removed from its storage unit. The storage unit provides some spacing from other materials and there were no other fissile materials in the storage area that would require spacing for NCS. Double contingency exists, but it has not been documented in an Implemented Nuclear Criticality Safety Evaluation. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "A violation of an NCSA for other fissile materials in conjunction with placement near the Pu-239 source would be required before criticality would be credible or a much larger mass of Pu-239 would be required. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Although an NCSA was not in place, the mass of Pu-239 was only a fraction of the Pu-239 safe mass and there were no other fissile materials in the storage area that would require spacing for NCS. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "The licensed material was 32 grams of Pu-239 in the form of a sealed source. This is approximately 7% of a subcritical mass (450 grams per ANSI/ANS-8.15). "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "There were no established controls over this material. However, much less than a safe mass was involved and there were no other fissile materials in the storage area that would require spacing for NCS. Therefore, the significance of this event is very low. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "Upon discovery, a boundary was established and an anomalous condition entered." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37812 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-03-07 11:00 | 2001-03-07 13:11 | 2001-04-09 | MOTOR DRIVEN EMERGENCY FEEDWATER (EFW) PUMP STARTED UNEXPECTEDLY While paralleling the DG-1B with offsite power, the "B" Motor Driven EFW pump started . The start occurred as the Bus 6 Unit Auxiliary Transformer breaker was closed. The licensee verified Emergency Feedwater Flow was not required and secured the Motor Driven EFW pump. The pump ran for 2 minutes and 28 seconds. All four (4) Steam Generator Water Levels increased less than 10% narrow range. The licensee is investigating the cause of the pump start. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1124EDT ON 4/9/01 FROM DAMON RITTER TO S. SANDIN * * * "The following is a retraction for event number 37812 dated March 7, 2001: "On 3/7/2001 at 13:11 (EST), Seabrook Station reported an actuation of the Emergency Feedwater System pursuant to 10CFR50.72(b)(3)(iv)(A). Since the report was made, an evaluation of the equipment and events has been performed. 10CFR50.72(b)(3)(iv)(A) requires that an eight hour report be submitted for 'Any event or condition that results in valid actuation of any of the systems listed in [10CFR50.72(b)(3)(iv)(B)]...' The Emergency Feedwater System is listed as item (6) of 10CFR50.72(b)(3)(iv)(B). Valid actuations are those events that result from 'valid signals' or from intentional manual initiation, unless it is part of a pre-planned test. Valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. An evaluation of the equipment and events has determined that the pump start was due to an invalid signal. Since a valid actuation signal was not present, this event is not reportable pursuant to 10CFR50.72(b)(3)(iv)(A)." The licensee will inform the NRC resident inspector. Notified R1DO(Linville). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37811 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2001-03-05 13:15 | 2001-03-06 11:52 | 2001-05-18 | CRITICALITY ALARM MAY NOT COVER AREA USED FOR STORAGE The licensee discovered that an area in Building 306 East, that was used recently for storage of HEU, may not be covered by the Nuclear Criticality Safety Alarm system. The storage area is part of the Nuclear Critical Safety evaluations and there is no question that the area meets the requirements for use as storage. However, 10 CFR 70.24 requires coverage by the criticality detector/alarm system for arrays containing more than 700 grams of uranium-235. The documentation could not be located that coverage for the area in question is covered. The licensee started calculations to develop new documentation for the coverage area. Immediate actions were taken to stop all movements of SNM within the areas of questionable coverage. Further actions will be to install additional criticality detectors/alarms to ensure coverage of all arrays in the area. The licensee notified the NRC Resident Inspector and R2 (David Ayres). * * * 0850 on 5/18/01 by Droke received by Weaver * * * The licensee has retracted this event notification. Continued evaluation of the coverage area has led to the conclusion that all areas in questions were covered by the existing criticality alarm system. The licensee notified the NRC resident inspector. The operations center notified the R2DO (Wert) and NMSS (Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 1
37810 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-03-05 23:24 | 2001-03-06 00:24 | 2001-03-07 | DISCRETIONARY UNUSUAL EVENT DECLARED DUE TO A MOMENTARY LOSS OF OFFSITE POWER DURING AN ONGOING SEVERE WINTER STORM AND SUBSEQUENT AUTOMATIC REACTOR TRIP DUE TO GRID INSTABILITY During an ongoing severe winter storm, the 345-kV breakers tripped open and re-closed resulting in a momentary loss of offsite power. An automatic reactor trip also occurred at 2324 on 03/05/01 due to electrical grid instability. (The exact cause of the reactor trip is currently under investigation because there was no first out indication.) All rods fully inserted. The reactor coolant pumps tripped as expected, and one has been placed back in service. Both emergency diesel generators automatically started but did not load. Availability of the condenser was also lost due to the loss of power, and operators closed the main steam isolation valves. There were no radiation releases, and there were no reactor coolant system or steam generator tube leaks. All systems functioned as required with one exception. The steam-driven emergency feedwater pump failed to automatically actuate. At this time, the unit is in Mode 3. Normal charging and letdown, pressurizer heaters and sprays, and one reactor coolant pump are being utilized for primary system level, pressure, and transport control. Water is being supplied to the steam generators via an electric-driven emergency feedwater pump, and the atmospheric dumps are being utilized as the heat sink. Containment parameters are normal. The grid is currently available for offsite power, and the emergency diesel generators are still running. Based on a discretionary shift management call, the licensee declared an Unusual Event at 2336 on 03/05/01. The licensee stated that a "Discretionary Event" under item 18A refers to an event in progress (or has occurred) that indicates a potential degradation of the level of safety of the station. The licensee plans to notify the NRC when the Unusual Event has terminated or if conditions degrade. A severe winter storm is currently ongoing. At the time of the event, the unit was experiencing winds at a rate of approximately 50 miles per hour. The licensee reported that these strong winds were ongoing and that only a few inches of snow had fallen (although up to 2 feet is expected). The licensee notified the state at 2347 on 03/05/01 and plans to notify the NRC resident inspector as well as applicable local officials. The licensee also plans to issue a press release. ***** UPDATE AT 0222 ON 03/06/01 FROM JIM HILL TO LEIGH TROCINE ***** This update provides both clarifications/corrections to the original event notification and additional information regarding licensee plans. CLARIFICATIONS/CORRECTIONS: Prior to the event, two of three offsite power lines had been lost in close succession. The remaining offsite line was subsequently lost, and its breaker re-closed within a short duration. This resulted in the momentary loss of offsite power and subsequent plant transient. This initial electrical imbalance was sufficient to result in the automatic starting and loading of both emergency diesel generators. CURRENT STATUS: The unit remains in the Unusual Event, and winds are currently sustained at a rate of approximately 40 miles per hour. All three offsite power lines have been restored. Both emergency diesel generators remain in operation and continue to provide power to both vital (emergency) buses. The non-vital buses have been re-energized from offsite power. An additional auxiliary pump (the startup feedwater pump) has also been started to provide additional water to the steam generators. This pump is a non-safety related housekeeping pump. PLANS: Within the next half hour, the licensee plans to commence a discretionary plant cooldown and plans to place the unit in Mode 5 (Cold Shutdown). At some point in time, the licensee also plans to secure the electric-driven emergency feedwater pump and rely on the startup feedwater pump to supply water to the steam generators. The licensee notified the NRC resident inspector and an onsite member of an NRC residual heat removal inspection team. The NRC operations officer notified the R1DO (Conte), NRR EO (Bateman), and IRO (Miller). ***** UPDATE AT 0438 ON 03/06/01 FROM JIM HILL TO LEIGH TROCINE ***** The licensee has commenced a plant cooldown and anticipates that it will take approximately 6 hours for the unit to reach Cold Shutdown. Other than commencement of the cooldown, there has been no change in plant conditions or equipment status. The licensee stated that the criteria for exiting the Unusual Event have been met. However, the licensee currently plans to remain in the Unusual Event for a while longer because the high line insulators onsite are still arcing and are suspect and because the in-house vital buses are still being powered by the emergency diesel generators. The licensee notified an onsite member of an NRC residual heat removal inspection team, who in turn notified the NRC resident inspector. The NRC operations officer notified the R1DO (Conte), NRR EO (Bateman), and IRO (Miller). ***** UPDATE AT 0800 ON 03/06/01 FROM JOHN LaVALLEY TO LEIGH TROCINE ***** The licensee called to provide the following status update: The unit remains in the Unusual Event. The reactor coolant system is currently at 445 degrees F, and the cooldown is still in progress via utilization of boration and the atmospheric steam dumps. The emergency diesel generators are still supplying power to the vital buses. The licensee currently plans to place the unit in Mode 5 (Cold Shutdown) and then to restore the secondary side of the plant (assuming that offsite power supplies are stable). The NRC operations officer notified the R1DO (Conte) and NRR EO (Tappert). *** UPDATE AT 1509 ET ON 03/06/01 FROM JOHN LaVALLEY TO JOHN MACKINNON ***** The licensee called to provide the following status update: The unit remains in the Unusual Event. The reactor coolant system is currently 360 degrees F, and cooldown is still in progress. The licensee will reduce reactor coolant system temperature to approximately 240 degrees F. The emergency diesel generators are still supplying power to the vital buses. The licensee is waiting for Load Dispatcher permission to take down one 345kV line at a time to clean the lines bushing. After the bushings for the 3 345kV lines have been cleaned and the grid is stable, the licensee will make a determination whether to exit the Unusual Event. Additional information: After the reactor trip the Turbine Driven Auxiliary Feedwater pump failed to start. The licensee thinks that the pump tripped on overspeed. Licensee is investigating this problem. The NRC operations officer notified the R1DO (Bellamy) and NRR EO (C. Grimes) ****UPDATE AT 1619ET ON 03/06/01 FROM M KILEY TO JOHN MACKINNON***** The licensee called to provide the following clarification to event write up: The exact cause of the reactor trip as indicated by the "First Out Light" was "Power Range Negative Flux Rate Hi". Secondly, both Emergency Diesel Generators automatically started and loaded all safety related loads associated with Emergency Electrical Buses 5 and 6. The NRC operations officer notified the R1DO (Bellamy) and NRR EO (Tad Marsh). * * * UPDATE 1055 EST ON 03/07/01 FROM RON STRICKLAND TAKEN BY BOB STRANSKY * * * The licensee terminated the Unusual Event at 1040 EST on 03/07/01. The offsite electrical grid is stable with two independent sources available. Offsite power has been restored to emergency bus (E-5), and the licensee is preparing to realign the other emergency bus to offsite power as well. The unit remains stable in Mode 4 (Hot Shutdown). The NRC resident inspector has been informed of this update by the licensee. Notified R1DO (Bellamy), NRR EO (Marsh) and FEMA (Steindurf). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0
37809 | -1 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2001-03-05 16:00 | 2001-03-05 17:56 | 2001-03-23 | CONTROL ROOM EMERGENCY VENTILATION DECLARED INOPERABLE. Control Room Emergency Ventilation was declared inoperable at 1600 hours. This was a result of the Lab carbon sample analysis not meeting Technical Specification 3.4.5.c of greater than 90% radioactive methyl iodine removal capability when tested. This required entering into a 7 day shutdown Limiting Condition for Operation. Carbon sample analysis is required per Technical Specification to be performed once per cycle (2 years). Licensee is in the process of replacing the carbon. The NRC Resident Inspector was notified of this event. * * * RETRACTED AT 1411 EST ON 3/23/01 BY JOHN PARRISH TO FANGIE JONES * * * After further testing and calculations it was determined that the value was above the technical specification requirements and the event was not reportable and retracts the event notification. The licensee intends to notify the NRC Resident Inspector. The R1DO (Kenneth Jenison) has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37808 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-02-27 | 2001-03-05 17:45 | 2001-03-05 | FOUR RADIOGRAPHERS EXCEEDED ANNUAL EXPOSURE LIMIT. After receiving a Radiation Dosimeter Report on 01/22/01 for wear date of 11/20/00 through 12/19/00, it was discovered the licensee had 4 individual personnel dosimeters exceeding the annual limits of 5 rem/yr. Participants ID and reported doses are listed below: 1. Participant 00089 ID # 466313013, 5553 mrem. 2. Participant 00190 ID # 452717589, 5661 mrem. 3. Participant 00174 ID # 453959946, 4673 mrem plus as assessment of 417 mrem for a lost dosimeter equal a sum of 5091 mrem. 4. Participant 00255 ID # 222582111, 3995 mrem, plus previous employment assessment of 1065 mrem equal a sum of 5060 mrem. After receiving and reviewing the dosimetry reports phone notification was made confirming the resulting exposures exceeding annual limits in accordance with 25 TAC requirements. At this time the licensee is awaiting the final dosimetry reports for 2000 year to date. Upon receipt of the final dosimetry reports the licensee will set up an investigation date and time. Texas Department of Health is investigating to obtain additional information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37807 | 0 | SAINT LUKE'S HOSPITAL |  |  |  |  | 2001-02-23 11:15 | 2001-03-05 15:13 | 2001-03-06 | POSSIBLE MEDICAL MISADMINISTRATION A remote afterloader device failed to function as it was intended during a random FDA trial. The remote afterloader was in automatic, and it was supposed to insert an intravascular, brachytherapy, 93-mCi, P-32, wire source into a patient. The remote afterloader device did not operate properly, and it inserted and withdrew the wire source 4 times. No dwell time was recorded by the afterloader since the wire source inserted less than 5 seconds each time before the wire source was automatically withdrawn. The patient was supposed to have received a total dose of 20 grays. The patient received a dose much less than intended. The FDA was notified of this event by the licensee. ***** UPDATE AT 0958 EST ON 03/06/01 FROM SCOTT SORENSEN TO LEIGH TROCINE ***** The licensee called the NRC Operation Center to clarify that the trial afterloader device was under the operator's control and that the device's internal safety checks and sensors caused the source to be removed and would not allow the dose to be delivered as intended. The following text is a portion of a clarification received from the licensee via an E-mail at 1024 EST on 03/06/01: "Radiation therapy was not delivered as prescribed during [an] FDA-approved clinical trial for Intravascular Brachytherapy. A 93-mCi P-32 wire was to be placed across a coronary artery lesion for approximately 5 minutes of dwell time. Multiple attempts were made to place the source at the treatment position. However, an internal safety trigger in the afterloader caused the source wire to be withdrawn from the patient immediately upon source arrival at the targeted treatment site. The licensee extended the active wire a total of 4 times into the patient, followed by immediate, automatic withdrawal by the afterloader. No dwell time was recorded at the treatment location, and transit time through the patient's arteries was approximately 5 seconds each way. The procedure was abandoned without the patient receiving the intended 20 Gray dose. The event was under direct supervision of [an] NRC-approved Radiation Oncologist and the institution's Radiation Safety Officer. The FDA was notified of the study protocol deviation by the licensee." (Call the NRC operations officer for licensee contact information.) The NRC operations officer notified the R3DO (Madera) and NMSS EO (Sturz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.33 |  |  |  | 0
37806 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-05 10:13 | 2001-03-05 12:25 | 2001-04-24 | REACTOR CORE ISOLATION COOLING (RCIC) TRIPPED UNEXPECTEDLY DURING TESTING. Received RCIC "B" logic isolation signal causing RCIC in-board isolation valve, 2E51-F007, to close resulting in RCIC trip signal. I&C personnel were performing 57SV-CAL-003-25 ATTS transmitter calibration for RCIC "B" steam line differential pressure transmitter 2E51-N057B when the isolation occurred and this instrument caused the isolation. Investigation is in progress to determine the cause. Received isolation signal at 1013 ET, I&C backed out of the procedure returning 2E51-N057B transmitter to service and RCIC isolation was reset and RCIC returned to standby at 1105 ET. All other Emergency Core Cooling systems were fully operable during the time period RCIC was declared inoperable. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION ON 04/24/01 AT 1453 ET BY S. HOWARD TAKEN BY MACKINNON * * * Plant Hatch FSAR has been revised such that the Control Rod Drop accident limiting event path evaluated in the safety analysis (subsection 15.3.2) does not rely on RCIC to mitigate this Design Basis Accident (DBA). None of the DBAs, as evaluated in the safety analysis (section 15.3), rely on RCIC for event mitigation. RCIC will no longer be an NRC notification when declared inoperable. Therefore, this NRC notification is being retracted. R2DO (Paul Fredrickson) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0
37805 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-03-03 10:28 | 2001-03-03 18:48 | 2001-03-13 | VARIOUS SAFETY SYSTEM ACTUATIONS DURING A PLANNED SHUTDOWN "While performing a planned shutdown for maintenance, an automatic scram and group isolations occurred due to low Reactor water level. "The sequence of events was as follows: Initial manual scram was inserted at 09:42 CST to complete the shutdown as part of the plant shutdown procedure. Following the initial manual scram, 'B' Reactor Feed Pump (RFP) tripped on high water level. 'A' RFP was previously secured as part of the shutdown procedure. For undetermined reasons, 'B' RFP was unable to be returned to service. An attempt was made to start the 'A' RFP but efforts were stopped due to high vibrations received on 'A' RFP. Reactor Core Isolation Cooling (RCIC) was manually started to provide make up to the RPV [Reactor Pressure Vessel]. The subsequent shrink due to the relatively cool water being added caused water level to lower to the low level scram set point (level 3), and at 10:28 CST an automatic scram initiated, together with Group 2 (Primary Containment), Group 3 (Reactor Water Cleanup) and Group 6 (Secondary Containment) isolations. The Scram and automatic isolations functioned as designed, except Group 3 had been previously actuated due to high Non-regenerative Heat Exchanger temperature while initiating blowdown to the main condenser for level control. Level was restored to approximately 17 inches above the low level scram set point and the scram was reset. RCIC flow was lowered in anticipation of swell due to heating, and level again lowered. A manual scram was inserted approximately 4 inches prior to the low level scram set point. Level was recovered using RCIC, and, following resetting of the scram, water level was restored to the normal level, RCIC secured, and condensate system used to raise level to the shutdown level band. Level is presently being maintained using the condensate system. "Investigation is on-going for the cause of being unable to restore 'B' RFP to service following the high level trip, and the reason for the high temperature isolation of RWCU [Reactor Water Cleanup]. "The Senior Resident Inspector has been notified." The licensee is making preparations to place the unit in cold shutdown in the next 2-4 hours. * * * UPDATE 1215EST ON 3/13/01 FROM DAVID VANDERKAMP TO S. SANDIN * * * The licensee is providing the following clarification as an update: "This is a follow-up report for event #37805 which was reported 3/3/2001 by Cooper Nuclear Station (CNS). The purpose of this follow-up is to clarify information provided in the initial eight hour report and to provide additional event information. "The initial report described reactor water level anomalies during a normal planned shutdown for a scheduled mid-cycle outage. The initial report indicated that the 'B' reactor feedwater pump could not be reset and restarted. It was also reported that the 'A' reactor feedwater pump was unavailable. However, a more accurate characterization of the condition is that the 'A' reactor feedwater pump was started after being shutdown for some time. Due to the cold condition, vibration levels higher than expected were observed. The highest vibrations seen were well below the procedural limit requiring turbine trip. Operators made a conscious decision not to use the 'A' reactor feedwater pump other injection sources were available. The 'A' reactor feedwater pump was available and operators were aware of its availability, if needed. "The shrink of water level that caused the automatic scram on low water level was initially attributed to the injection of cold water by RCIC. Subsequent evaluation has found that the shrink was due to a combination of the RCIC injection and that of steaming down due to normal pressure control via the Main Turbine Bypass Valves. Operators did not fully understand this interaction at the time of its occurrence. "An additional condition not described in the initial report is concerned with a transient on the Reactor Equipment Cooling (REC) System. In an attempt to control high reactor water level, a blowdown was established via the Reactor Water Cleanup (RWCU) System. This blowdown was excessive and caused boiling in the REC system at the RWCU Non-Regenerative Heat Exchanger. This boiling resulted in a rapid expansion of the REC system volume with the excess spilling out the REC surge tank vent. An automatic isolation of the RWCU system due to high temperature terminated the condition. Subsequent collapse of the steam voids in the REC System caused the level in the REC surge tank to drop below the Technical Specifications allowed value for 5 minutes. During this time period the REC System was declared inoperable and then was returned to operable status after operators refilled the surge tank. The REC System continued to operate during this transient. "The REC System is designed to provide cooling water for the removal of heat from equipment, such as the room coolers for the core spray pump rooms and HPCI pump room, required for a safe reactor shutdown following a Design Basis Accident or transient. With a loss of room cooling, the ability of the Emergency Core Cooling Systems to perform their required safety functions can no longer be assured. The investigation into the REC surge tank event continues, and the evidence to date indicates that the REC System transient was very short and REC remained available during the entire event. In addition, the reactor was shutdown during this transient. This potential loss of safety function is reportable as an eight hour report under 10CFR50.72(b)(3)(v)(B) pending a final evaluation. This is in addition to the eight hour report (Event #37805) previously made due to the valid actuation of the Reactor Protection System and Containment Isolation Systems. Both of these reports will be discussed in one Licensee Event Report (LER)." The licensee will inform the NRC resident inspector. Notified R4DO(Johnson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | POT RHR INOP |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  |  | 0
37804 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-03-03 02:50 | 2001-03-03 03:37 | 2001-03-03 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO FAILURE OF TWO FEEDWATER FLOW CHANNELS TO RESPOND DURING A PLANT STARTUP The following text is a portion of a facsimile and E-mail received from the licensee: "While performing a plant startup two channels of feedwater flow on [the] B Main Feed line failed to respond. Investigation showed that both transmitter's output was too low to support operability. These transmitters provide the feed flow signal that, in conjunction with low steam generator water level, provide a reactor trip. At 0225, [Technical Specification] 3.0.3 was entered, and power was reduced at 0250 to a nominal 11%." "We expect to complete calibration/repairs on at least one of the transmitter loops prior to 0725. If at least one transmitter loop is not repaired, we must be in Hot Shutdown by 0925." The licensee notified the NRC resident inspector. | 11 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37803 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-03-01 22:17 | 2001-03-02 20:58 | 2001-03-02 | NON-CFR REPORT INVOLVING A VALID ACTUATION OF A "Q" QUALITY CLASS SAFETY SYSTEM "On 3/1/01 at 2217 hours, Facility Operations Personnel received an alarm indicating that Cascade Automatic Data Processing (CADP) smoke head 'SXE-2783', located inside the housing near the LAW (low assay withdrawal) compressor 'AB', had actuated. Operations Personnel were taking actions to secure the LAW Station at the time of this actuation. Operations Personnel responded immediately to investigate the cause for the alarm. Upon arrival, no source for the alarm could be identified[. The] smoke head reset at 2226 hours. The PSS (plant shift superintendent) requested a firing plot for all smokeheads in the immediate area be printed for this time frame. The firing plots indicate that five (5) smokeheads did recognize activity however, the activity was minimal and did not actuate any other smoke heads. The PSS notified the Facility Operations Personnel of his findings and requested they have the housing panels removed for internal investigation to identify any evidence of out gassing. Upon completion of this investigation, it was identified that a minor out gassing had occurred. With this information this event is reportable due to the valid actuation of a 'Q' Quality Class Safety System." Operations personnel informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37802 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2001-03-02 | 2001-03-02 17:45 | 2001-05-11 | AGREEMENT STATE REPORT INVOLVING POTENTIAL OVEREXPOSURE The Kansas Department of Health and Environment was notified by Hutchinson Hospital Corporation that a Cardiologist may have received an overexposure. The source and extent of the potential overexposure are under investigation. This is Kansas Case Number KS010006. This report will be updated when more details are available. * * * UPDATE AT 1230 EDT ON 5/11/01 BY JAMES HARRIS TO FANGIE JONES * * * "The event report by the licensee shows an interventional cardiologist received 10,115 mrem for the year 2000. The exposure was due to x-ray and not the radioactive material program at the hospital. The is the only physician in the area who performs these procedures and he performs more than 600 procedures in a year. Observations of the physician show the portable shielding, because of its design or limitations in placement, may have been a detriment to the procedure and therefore was not used or improperly used in many cases. "Corrective actions: New shielding with a better design has been purchased. A new shield curtain has been purchased to better control the side scatter from the x-ray tube. New lead equivalent glasses have been purchased. Shielding has been added to the x-ray head to harden the beam and reduce low energy scatter. The safety staff is providing increased oversight." The R4DO (Jeff Shackelford) and NMSS (John Hickey) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0
37801 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2001-03-02 13:00 | 2001-03-02 15:06 | 2001-03-02 | MONITOR WELL IN EXCURSION STATUS Crow Butte Resources shallow monitor well #SM6-13 in uranium solution mine unit #6 in Crawford, NE, was placed in excursion status due to sulfates concentration measuring 26 mg/l exceeding the UCL (Upper Control Limit) of 21 mg/l and the multiple chloride concentration measuring 9.1 mg/l exceeding the UCL of 8 mg/l. The licensee believes these are normal variations. A license amendment has been approved which would exclude reporting of normal variations. However, since the NE UIC (Underground Injection Control) permit has not been modified, the licensee informed the NE DEQ (Department of Environmental Quality) Onsite Representative and will inform the NRC Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MINING EVENT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37800 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2001-03-02 | 2001-03-02 13:30 | 2001-03-02 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE Between 2300 PST on 3/1/01 and 0700 PST on 3/2/01, a Troxler Model 3430 gauge, S/N 25510, was stolen out of a Delta Geotechnical Consultants, Inc. pickup truck in Las Vegas, NV. The licensee confirmed that the gauge was chained to the truck bed. The Las Vegas Metro Police were informed. Delta Geotechnical Consultants, Inc. is a Utah based corporation operating in Nevada under reciprocity of the Utah Rad. Material License. This is NV Event Report ID No. NV 01-001. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0
37799 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-03-02 05:30 | 2001-03-02 10:10 | 2001-03-23 | PLANT DECLARED RCIC INOPERABLE. During a panel walkdown, it was discovered that the RCIC flow controller setpoint pointer was indicating erratically. Therefore, the flow controller was declared inoperable resulting in RCIC being declared inoperable. Troubleshooting is currently being performed on the controller. This condition put the plant in a 14-day LCO action statement. The NRC Resident Inspector will be notified. * * * UPDATE 1055EST ON 3/23/2001 FROM ERIC OLSON TO S. SANDIN * * * The licensee is retracting this report based on the following: "During a control room tour on Friday, March 2, 2001, the output of the reactor core isolation cooling system (RCIC) controller FIC-1340-1 was observed oscillating between downscale (-value) up to approximately +2% as indicated on the output demand meter. Initial testing measured voltages at the input test terminals and found a steady flow signal applied to the controller. Voltage measurements taken at the output test jacks found the output oscillating between 9 to 11 milliamps, consistent with the oscillation of 2% on the demand meter. In an effort to help pinpoint the source of this problem, the set-point tape was adjusted down to the minimum value allowing the deviation meter to come on scale (± 10% measuring the signal error between flow input and set-point). In this mode, oscillation of the deviation meter was observed, consistent with demand. The controller was then taken to manual and the output demand meter became stable. These two simple functional checks suggested the source of oscillation was limited to the automatic control circuitry of the GEMAC controller, based on the stable voltage measurement at the controllers input and the stable output when placed in manual. The most probable cause for the oscillation would be weak/aging power supply capacitors used in the controller's automatic circuitry. "The RCIC system was declared inoperable and the NRC was notified at 1010 on March 2, 2001 in accordance with 10CFR50.72(b)(3)(v) based on the belief that the controller was not operable. "Troubleshooting was performed and it was decided to replace the controller with the identical controller from the RCIC alternate shutdown panel (ASP). RCIC was then tested using procedure 8.5.5.1 with satisfactory results. The controller that had been removed from the RCIC panel was bench tested and the results indicated that the controller would have allowed the RCIC system to reach a stable rated 400 gpm flow control. "On Friday March 9, 2001, the controller from the alternate shutdown panel was also noted to be oscillating about the '0' position, repeating the condition described in PR01.9190. Problem report PR01.9210 was written to describe this similar condition. It was concluded that the RCIC test could be performed with the controller exhibiting some oscillation. The test results demonstrated that the controller and therefore, RCIC was operable. Further troubleshooting is in progress to determine the cause of the oscillations. One possibility is that the source of the oscillations has to do with equipment grounding and other equipment tests occurring on Fridays. Further investigation is in progress. "The reporting criteria of 10 CFR 50.73 were evaluated as follows; "For (a)(2)(v); not reportable. The initial observation on Friday, March 2, 2000, of oscillations on FIC-1340-1 indicated that the individual controller was inoperable and needed maintenance. The controller was replaced with the identical controller from the alternate shutdown panel (ASP). The newly installed controller was tested and RCIC was verified to be operable. Bench testing of the removed controller indicated that it would have performed its safety function. A similar oscillation was noted on the new controller on Friday March 9, 2001. RCIC was tested even though the controller appeared to be oscillating. The testing verified the operability of the installed controller and confirmed the conclusion that the original controller would have been operable. Since the original controller would have been operable, the observed oscillations could not have prevented the fulfillment of the RCIC safety function and therefore, is not a reportable condition. "It is recommended that the 10 CFR 50.72 notification made on March 2, 2001 be retracted." The licensee informed the NRC resident inspector. Notified R1DO(Jenison). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37798 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-03-02 01:15 | 2001-03-02 06:51 | 2001-03-02 | BOTH PRIMARY CONTAINMENT HYDROGEN RECOMBINERS WERE DECLARED INOPERABLE. During operation of Unit 2 at 100% power, it has been determined that both Primary Containment Hydrogen Recombiners for the Suppression Pool Chamber are inoperable. The 'A' recombiner had previously been removed from service for maintenance activities, when the station's 'B' Emergency Diesel Generator was declared inoperable after the main control room received an unexpected trip alarm on the diesel. The diesel failure is not reportable due to three diesels remaining operable. However, Technical Specifications require that the 'B' recombiner be declared inoperable if the 'A' recombiner is inoperable. This failure requires a 8-hr ENS Notification under 10CFR50.72(b)(3)(v)(D), loss of a safety function to mitigate the consequences of an accident. The 'B' Emergency Diesel was declared inoperable due to a failed relay. The NRC Resident Inspector was notified. Technical Specification 3.8.1, condition 'B,' required action b.2, states, "Declare the required feature supported by the inoperable diesel generator inoperable when the redundant required features are inoperable also." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37797 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-03-01 09:55 | 2001-03-01 18:37 | 2001-03-01 | ALERT NOTIFICATION SYSTEM DISCOVERED INOPERABLE "At 0955, KNPP was notified by the Kewaunee County Sheriffs Office of a disconnected cable which supplies the siren encoder for the Alert Notification System. Subsequent investigation identified that the transmitter was removed during remodeling, disabling the system from being activated by the Kewaunee County Dispatch Office, potentially as early as Monday, 2/26/01. Normal siren activation would be accomplished from the Algoma Emergency Operations Center, but the Kewaunee Dispatch location would be used in the event of a fast breaking incident. It is believed that processes in place would have lead the Kewaunee Dispatch to pursue alternate methods of activating the sirens, however, it is not clear that this would have been performed in a timely manner. Compensatory measures have been established for the Kewaunee Dispatch/Sheriff to notify the Kewaunee Emergency Director of the need to activate the sirens. The Emergency Director has the capability to activate the sirens remotely and will maintain this activation function manned until the equipment issues at the Kewaunee Dispatch have been resolved." The licensee informed local authorities and the NRC resident inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37796 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-02-23 16:45 | 2001-03-01 17:00 | 2001-03-01 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE 2/23/01 "At approximately 4:45pm on Friday 2/23/01 a technician realized a truck with a gauge chained in the back had been stolen. The stolen gauge is a Troxler Model 3430, serial # 30170. The gauge contained two sources: 8 millicuries of Cs-137, serial # 7501851, and 40 millicuries of Am-241:Be, serial # 47-27094. [The technician] had checked the gauge our for use at a jobsite near 1960 Highway 59 in Humble, Texas. [The technician] is a trusted employee and has worked for the company for a long time. The Houston Police Department was notified. 3/1/01 "The truck and gauge were recovered and returned to the Licensee on 2/28/01. The gauge was still locked in the back of the truck; it was undamaged. A New Orleans, Louisiana resident noticed the truck parked in front of their residence and called the New Orleans Police Department. The Houston Police Department was notified and arranged the recovery. "The Licensee will submit a written report providing additional details on 3/2/01." Texas Incident #7726. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37795 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-02-19 09:45 | 2001-03-01 17:00 | 2001-03-01 | AGREEMENT STATE REPORT INVOLVING A MISSING NUCLEAR DENSITY GAUGE On 2/15/01 an employee of QC Laboratories, Inc. went to a jobsite and never returned. The police were notified and are looking for the individual and the company's 1997 Nissan truck. The employee was in the possession of a nuclear density gauge manufactured by Humbolt Scientific, Inc., model #HS-5001EZ, serial #3145. The gauge contains two sources; 10 millicuries Cs-137 (as of 7/14/97 or 10/30/98) and 40 millicuries Am-241:Be. On 3/1/01 additional information was available updating this incident. The gauge has been recovered. The Nissan truck with the gauge locked securely was parked at a drug rehab facility where the operator had checked himself in. Texas Incident #7718. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37794 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-03-01 08:22 | 2001-03-01 12:55 | 2001-03-01 | MANUAL REACTOR TRIP DUE TO LOSS OF OPERATING CIRCULATING WATER PUMPS "South Texas Project Unit 2 makes the following report in accordance with 10CFR50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A): "At 08:22 CST on 3/01/01, a manual Reactor Trip was initiated due to failure of a switchyard breaker and subsequent loss of all operating Circulating Water Pumps. All Control Rods fully inserted into the Reactor Core. The Auxiliary Feedwater system actuated on low-low Steam Generator Water Level and a Feedwater isolation signal occurred as expected on a trip from 95% power. Pressurizer heater group 'A' did not energize on low RCS pressure as required. Cause of the heater group to fail to energize is not known at this time. All four (4) Reactor Coolant pumps remain in operation and decay heat is currently being removed via the atmospheric steam dumps. No radiation above state, federal, and plant operational limits was measured by South Texas Project's radiation monitoring system." The licensee is presently making efforts to restore an operating Circulating Water Pump so as to establish Main Condenser vacuum. Three Circulating Water Pumps were operating at the time with the fourth out-of-service. The licensee has a measured 20gpd Steam Generator tube leakage. The offsite rad release is within allowable limits. No other safety equipment is out of service. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37793 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2001-03-01 05:00 | 2001-03-01 06:33 | 2001-03-01 | THE LICENSEE NOTIFIED STATE AND COUNTY OFFICIALS OF A TRANSIT STRIKE IN WESTCHESTER COUNTY. The licensee was notified that transit employees of the Liberty Bus Company in Westchester County will be going on strike. The licensee made the offsite notifications to assure that the contingency plans are in effect to deal with the strike. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37792 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-03-01 05:00 | 2001-03-01 05:42 | 2001-03-01 | THE LICENSEE NOTIFIED STATE AND COUNTY OFFICIALS OF A TRANSIT STRIKE IN WESTCHESTER COUNTY. The licensee was notified that transit employees of the Liberty Bus Company in Westchester County will be going on strike. The licensee made the offsite notifications to assure that the contingency plans are in effect to deal with the strike. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37791 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-03-01 00:17 | 2001-03-01 03:19 | 2001-03-01 | REACTOR WAS MANUALLY TRIPPED AT LESS THAN 1% POWER A manual reactor trip was initiated at 0017 on 3/01/01 due to 2 shutdown control rods remaining on the bottom while initiating control rod withdrawal. This occurred during low power physics testing and a trouble shooting plan for a misaligned Shutdown bank B Control rod (G-9). The rod had already been realigned to the other rods in shutdown bank B @ 43 steps. The Shutdown bank was inserted into the core to zero steps per the trouble shooting plan. After the step counters and rod control were reset and Shutdown bank B rods were being withdrawn, it was discovered that 2 rods had not moved and were still on the bottom with 14 steps demanded. The Shutdown bank was re-inserted to zero steps (fully inserted). After further discussion, the shift supervisor called for a manual reactor trip. The reactor operator tripped the Reactor and the Crew entered the Emergency Operation Procedures (EOP-1.0, Reactor trip/safety injection, and EOP-1.1, Reactor trip recovery). All systems functioned as designed. The problem with the rod control system is not understood and trouble shooting is continuing. Note: The 2 rods that did not move were rods G-9 and L-5, both in Shutdown bank B. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37790 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-02-28 10:30 | 2001-02-28 17:29 | 2001-02-28 | OFFSITE NOTIFICATION (Call the NRC Operations officer for additional information.) The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37789 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-02-28 10:57 | 2001-02-28 15:13 | 2001-02-28 | EARTHQUAKE FELT ONSITE At 1057PST an earthquake in Western Washington State with a magnitude of 7.0 was felt onsite. The epicenter is located 11.3 miles NE of Olympia, WA and 14.9 miles West South West of Tacoma, WA. The depth of the earthquake was 30 miles. Seismic sensors did not detect the seismic activity. Plant inspection performed after the earthquake found no abnormal conditions. The NRC Resident Inspector was notified of this information call by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW | [5 empty] | 0
37788 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2001-01-12 12:08 | 2001-02-28 14:42 | 2001-02-28 | 10 CFR PART 21 REPORT REGARDING A SUBSTANTIAL SAFETY HAZARD WITH A WOODWARD GOVERNOR EGB UNIT The following text is a portion of a facsimile received from the licensee: "On 1/12/01, V. C. Summer Nuclear Station (VCSNS) determined that a Substantial Safety Hazard could exist with Woodward governor EGB units failing to properly control the Emergency Diesel Generator [(EDG)]. A condition report (received on 1/12/01) from B. F. Goodrich/Fairbanks Morse indicated there was binding of the terminal shaft internal to an EGB unit removed from the 'A' EDG at VCSNS. The disassembly inspection found that the binding of the terminal shaft was due to the use of clamping screws, which were 1/8 inch longer than specification, resulting in binding on the output servo piston connecting rod. "This error was made during the prior refurbishment of the EGB by Engine Systems Inc. (ESI), the Woodward Governor nuclear representative, on 2/24/00. The use of the longer screws resulting in binding in the unit is considered a defect, which was introduced during the repair process by ESI. "[VCSNS] utilizes these EGB units on both the 'A' and 'B' EDGs. The above condition produced severe frequency oscillations on the output of the 'A' EDG. This condition could have been introduced to any EGB during refurbishment by ESI, passed acceptance testing, and be present on both EDGs. In an emergency condition, both EDGs could fail, resulting in the loss of safety function for the emergency on-site power supply. "The EGB units currently installed on both EDGs have been refurbished by Fairbanks Morse with properly specified parts. Fairbanks Morse will perform all future EGB refurbishment work for VCSNS. Other cause and corrective actions associated with the governor issues are being addressed under Root Cause Analysis report RCA 01-0235, 'Diesel Generator 'A' Governor Problems.' " The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Refueling; FMode1: Startup | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0
37787 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-02-28 | 2001-02-28 14:40 | 2001-02-28 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF THREATENED SPECIES ONSITE The licensee notified the National Marine Fisheries Service that a live green sea turtle was discovered in the plant intake structure. The turtle was released into the Pacific Ocean. The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37786 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2001-02-28 10:30 | 2001-02-28 12:30 | 2001-02-28 | POSSIBLE OVEREXPOSURE OF RADIOGRAPHER The licensee notified the State of Mississippi that the TLD reading for an employee during the period of January 2001 was 14.624 rem. However, the TLD readings for the radiographer's assistants during the same period were normal, and the individual's pocket dosimeter indicated a total dose of approximately 350 mrem during the period. The licensee's RSO is investigating this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0
37785 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2001-02-27 11:45 | 2001-02-28 09:55 | 2001-02-28 | ACTUAL INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA. Immediate compensatory measures were taken upon discovery. Contact the HOO for additional information. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.73 |  |  |  | 0
37784 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-02-27 19:15 | 2001-02-27 23:38 | 2001-02-27 | 24 HOUR REPORT REQUIRED BY PLANT OPERATING LICENSE "This notification is being made to report a violation of the Salem Unit 2 Operating Licensee Section 2.C.10, 'Fire Protection.' Approximately 95% of the installed emergency lights on Unit 2 have been rendered inoperable as a result of discharge testing. Per the Fire Protection Program, these lights being inoperable would require that suitable hand held lighting be available to operators required to perform Appendix 'R' shutdown activities. These lights were checked and of the 16 lights(8 per Unit) 8 did not pass the required 3 minute test(at 1915). This constituted a violation of the fire protection program requirements and could have reduced operators ability to respond to a shut-down from outside the control room. The 8 inoperable hand held lights have been replaced with operable hand held lights, bring the unit into compliance with the Fire Protection Program at 2020 on 2/27/01." The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0
37783 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-02-26 14:26 | 2001-02-26 17:31 | 2001-02-26 | OFFSITE NOTIFICATION REGARDING CONTAMINATED INJURED INDIVIDUAL TAKEN OFFSITE "At 1350, an injury occurred to a worker when the individual fell and injured his back. At 1426, the worker was attended by local Emergency Medical Personnel who transported the individual to our local Hospital. Initial frisking of the individual showed no contamination, but due to his back injury his back was not able to be completely monitored until arrival to the hospital. At the hospital, it was determined the individual had three small (quarter size) and very low level contaminated spots of 100 counts corrected above the background of 80 counts per minute. One spot was located in the back of the individual's head and immediately removed with water. Two additional spots were detected on the worker's pants and these were also immediately removed. The individual was further surveyed and no contamination was found. No dose was received by the individual as a result of the contamination. The decon materials and clothing was contained and returned to the plant by radiation safety supervision. The ambulance, hospital personnel and hospital materials were all surveyed and released as no contamination was detected. "It was determined at 1555, that the individual was contaminated and per our procedures notifications will be made to the State Of Ohio and the local county Emergency Management Agencies of the incident. Due to the offsite notifications a 4 hour non-emergency call is required." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0
37782 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2001-02-26 09:07 | 2001-02-26 11:12 | 2001-02-26 | OFFSITE NOTIFICATION REGARDING THE DEATH OF A PLANT EMPLOYEE The following text is a portion of a facsimile received from the licensee: "At 0907 this morning, the Main Control Room was informed that a plant employee had been pronounced dead by a doctor at a local hospital. The death is believed to be the result of natural causes." "At 0636 EST, an emergency medical call was received in the Main Control Room (MCR), stating that a Harris Nuclear Plant (HNP) employee had been found unconscious at his desk in a plant office area. Offsite assistance was requested. The Site First Aid Team was dispatched and began resuscitation efforts. No pulse or respiration was present when the First Aid Team arrived. The employee was transported via ambulance to a local hospital." "Representatives of the surrounding counties and the State of North Carolina were provided a courtesy notification regarding the request for offsite medical assistance. The NRC Senior Resident was informed." "It is anticipated that a news release will occur as a result of the medical emergency." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37781 | 0 | OHIO DEPT OF HEALTH |  |  |  |  | 2001-02-21 12:00 | 2001-02-26 09:08 | 2001-02-26 | AGREEMENT STATE REPORT - ALUMINUM CONTAMINATED WITH DEPLETED URANIUM The entrance gate radiation detectors at IMCO Recycling were tripped on February 20, 2001, by a load of aluminum leaving the facility that had been melted into ingots and de-ox cones. The load was detained at the facility and the unprocessed scrap associated with the contaminated processed aluminum was surveyed. A total of four pieces of depleted uranium was found attached to pieces of aluminum scrap. The Department was notified on February 21, 2001, of the incident. The processed aluminum had maximum contact readings of 50 uR/hr with an 8 uR/hr background. IMCO hired a contract Health Physicist to survey the facility prior to the arrival the Department staff. All process areas from the scrap aluminum storage area, through the smelting furnaces, to the final product and byproduct areas were surveyed. No contamination was found. Wipe tests of the depleted uranium revealed loose removable contamination, as would be expected for the exposed depleted uranium surfaces. A total of 118,000 pounds of aluminum ingots and de-ox cones have varying levels of contamination since the processing is a pseudo-continuous smelting process. Follow-up information tracked the origin of the scrap aluminum to Cousin's Industries, in Oceanside, NY. The NY Department of Health has been notified of the incident and the intent to return the materials to Cousin's Industries. There is reportedly a total of eight shipments of the scrap aluminum. The first shipment did not set off radiation alarms at IMCO. The second and third shipments were those identified at the IMCO facility, with five more shipments in route or remaining at the Cousins Industry facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0
37780 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-02-24 15:10 | 2001-02-24 18:04 | 2001-02-24 | HIGH PRESSURE COOLANT INJECTION (HPCI) AND BOTH INJECTION PATHS OF LOW PRESSURE COOLANT INJECTION (LPCI) DECLARED INOPERABLE. HPCI and both injection paths of LPCI have been declared inoperable as a result of not meeting inservice testing of injection check valves as required by Technical Specification 4.15.B. Technical Specification shutdown required by Technical Specification 3.5.A (4), be in a Hot Shutdown condition within 24 hours (start time 1510 CT) . Plant shutdown commenced at 1608 CT. Licensee was reviewing ASME Code Section XI requirements as a result of a snubber problem encountered last week. While reviewing ASME Code Section XI requirements it was determined that HPCI and LPCI injection test valves may not meet ASME Code Section XI inservice testing requirements as specified per their Technical Specification. The reactor has to be shutdown in order to test the LPCI injection test valves since personnel have to enter the drywell. A soft shutdown of the reactor will be performed (the reactor will not be scrammed from power). All other Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Electrical grid is stable. The NRC Resident Inspector will be notified by the licensee of this event. | 94 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0
37779 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-02-24 03:06 | 2001-02-24 03:24 | 2001-03-25 | SAFEGUARDS DEGRADATION RELATED TO AREA BOUNDARY IMMEDIATE COMPENSATORY ACTIONS TAKEN UPON DISCOVERY THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. ADDITIONAL DETAILS MAY BE OBTAINED FROM THE OPERATIONS CENTER. * * * RETRACTED AT 2121 EST ON 3/25/01 BY RAY MARTIN TO FANGIE JONES * * * The licensee is retracting this event based on reportability evaluation. Additional details may be obtained from the operations center. The licensee intends to notify the NRC Resident Inspector. The R1DO (Kenneth Jenison) was informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 0
37778 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-02-23 21:19 | 2001-02-24 01:13 | 2001-02-24 | MANUAL REACTOR TRIP - SAFETY/RELIEF VALVE OPENED AT POWER Unit 2 was manually shutdown as required by plant procedures and Technical Specifications for an actuation of a single reactor coolant system safety/relief valve. A rapid plant shutdown from critical at 85% power was performed. The shutdown required a manual actuation of the reactor protection system. All rods inserted normally on the manual scram. All plant systems operated as expected. Reactor level decreased below the low level 3 reactor protection setpoint immediately following the scram as a result of normal system response. Current plant conditions: The reactor is in HOT SHUTDOWN at 106 psig progressing towards COLD SHUTDOWN. Reactor level is stable being controlled by condensate injection. The safety/relief valve remains open. Suppression Pool Cooling is in service with pool temperature 94 degrees Fahrenheit. The 2N SRV was the one that opened. The licensee had been in the process of shutting down to make repairs to this valve when it fully opened. It is believed to have a faulty pilot valve. The licensee notified the NRC resident inspector. * * * UPDATE AT 0859 ON 2/24/01 BY RICH RECEIVED BY WEAVER * * * The 2N reactor coolant safety/relief valve reseated at 130 psig reactor coolant pressure. The MSIVs were reopened and plant cool down continued. Unit 2 is currently in OPCON 4 with the "2B" Loop of Shutdown Cooling in service. Reactor coolant temperature is less than 200 degrees F. The licensee notified the NRC resident inspector. R1DO (Meyer) notified. | 0 | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0
37777 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-02-23 22:20 | 2001-02-24 00:53 | 2001-02-24 | MANUAL REACTOR SCRAM DURING PLANT SHUTDOWN "On 02/23/01, at 22:20 during a planned Brunswick Unit 2 reactor shutdown for refueling a manual reactor scram was inserted. The sequence of events was as follows. At approximately 37% reactor power a turbine EHC malfunction annunciator was received and turbine bypass valves were observed opening. A turbine trip occurred on generator reverse power. A generator primary lockout signal caused the site's four emergency diesels to start. The emergency busses remained powered from offsite power, therefore the diesels did not load. With the turbine control system malfunction, a manual reactor scram was inserted. An expected reactor vessel level shrink occurred where level lowered to approximately 150" (normal vessel level is approximately 187"). This vessel level caused a group 2 and group 6 isolation signal for the respective primary containment isolation valves. These valves isolated properly." An investigation is in progress to understand the cause of the turbine control system malfunction. Other plant systems functioned as designed. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37776 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-02-23 16:05 | 2001-02-23 20:11 | 2001-02-23 | EMERGENCY RESPONSE DATA ACQUISITION AND DISPLAY SYSTEM (ERDADS) FAILED. At 1605 ET ERDADS CPU module overheated and failed, causing a loss of the ERDADS system. ERDADS system was returned to service at 1710 ET. The NRC Resident Inspector will be notified by the licensee of this event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37775 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-02-18 | 2001-02-23 18:14 | 2001-02-23 | A TROXLER MODEL 4302 GAUGE AND A CPN MODEL 503 GAUGE WERE REDUCED TO CHARRED METAL IN A FIRE. NO EARLY INDICATION OF RADIOACTIVE LEAKAGE. In the early morning of Sunday, February 18, a fire destroyed the Wahluke Produce, Inc., office and potato processing building. The building was also used for storage of two portable gauges containing radioactive material. A Troxler Model 4302 depth probe, serial number 116, containing 11 millicuries (407 megabecquerels) of americium 241/beryllium and a CPN Model 503 soil probe, serial number H36066789, containing 50 millicuries (1850 megabecquerels) of americium 241/beryllium, were reduced to charred metal and ash. The sealed sources were stored in their shields and transport boxes at the time of the fire. All records of the business were destroyed in the fire, including the radioactive materials license and related information such as how to contact the department. The licensee was able to reach the gauge consultant who in turn notified the department on February 22, 2001. Department staff responded to the scene on February 23 and dug the two gauges out of approximately two feet of ash and debris. The gauges were surveyed and placed in 5 gallon buckets in a secure area to await retrieval by the licensee's gauge consultant that evening. There was no early indication of leakage based on the department's survey and a leak test and shielding evaluation will be done by the consultant. The fire remains under investigation although at this time it is not believed to have been arson. What was the notification or reporting criteria involved? WAC 246-221-250 Washington State Report number WA-01-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37774 | 0 | SAN ONOFRE | 1 |  |  | [1] W-3-LP,[2] CE,[3] CE | 2001-02-20 21:09 | 2001-02-23 14:50 | 2001-02-26 | UNIT 1 SHIFT SUPERVISOR TESTED POSITIVE FOR ALCOHOL DURING A RANDOM FITNESS FOR DUTY TEST. "On February 20, 2001, after reporting for a non-scheduled work shift at about 1800 PST, the supervisor was informed he had been selected for a random fitness for duty (FFD) test. As allowed by plant procedures, the supervisor entered the protected area (PA) at about 1820 PST, but not any vital areas, before reporting for FFD testing at about 2000 PST. At 2109, breathalyzer test results were positive for alcohol. The supervisor requested that a blood sample be used for confirmatory testing. Pending blood sample testing results, the supervisor's PA access was immediately terminated and he was placed on investigatory suspension. "On February 23, 2001, during an NRC inspection exit interview, NRC inspectors commented that SCE should not wait on blood testing results to determine reportability of this occurrence. Consequently, even though evaluation of the blood sample test results by the Medical Review Officer (MRO) have not been completed, SCE is reporting this occurrence . SCE will implement appropriate disciplinary actions if completion of the blood sample test result evaluation by the MRO confirms the initial test results." The NRC Resident Inspector will be notified of this event report. ***** UPDATE AT 1130 EST ON 02/26/01 FROM CLAY WILLIAMS TO LEIGH TROCINE ***** The licensee called to provide a time correction. The breathalyzer test results were positive for alcohol at 2109 PST in lieu of 2019 PST. The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R4DO (Linda Howell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0
37773 | 0 | U.S. ARMY |  |  |  |  | 2000-12-15 12:00 | 2001-02-23 13:16 | 2001-02-23 | THREE CHEMICAL AGENT MONITORS FOUND MISSING DURING AN INVENTORY CHECK. During an inventory check on 12/15/2000 by the First Signal Brigade Unit located in Yongsan, Korea, it was discovered that 3 chemical agent monitors each containing 15mCi's of Nickel-63 were found missing. An investigation into the loss of the three chemical agent monitors was initiated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37772 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-02-22 18:30 | 2001-02-22 21:34 | 2001-02-22 | "EVEN" TRAIN CORE SPRAY, RHR OR RHRSW PUMPS OPERATION FROM THE ALTERNATE SHUTDOWN SYSTEM COULD BE LOST DUE TO A POSTULATED HOT SHORT. An Alternate Shutdown System design deficiency resulting in a vulnerability to a single hot short during a Control Room Cable Spreading Room fire has been identified. The effect of the postulated hot short would be to actuate the Bus 16 load shed logic while the bus is powered from the emergency diesel generator. This could result in the inability to operate the even train Core Spray, Residual Heat Removal (RHR) or RHR Service Water pumps. No means are in place to circumvent the postulated hot short. A one hour fire watch patrol in the cable spreading room and control room has been established with Alternate Shutdown System inoperable. All other Emergency Core Cooling Systems are fully operable. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0
37771 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-02-21 18:45 | 2001-02-22 16:28 | 2001-02-22 | OFFSITE NOTIFICATION MADE TO MISSOURI PUBLIC SERVICE COMMISSION An onsite apprentice welder injured his left hand. Onsite Medical Emergency Team evaluated the injury and had the individual transported offsite to the local hospital. The Missouri Public Service Commission was notified of this incident by the licensee. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37770 | 0 | SAN ONOFRE | 1 | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2001-02-21 13:00 | 2001-02-21 18:59 | 2001-02-21 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF DEAD BROWN PELICAN The licensee made a call to the U. S. Fish and Wildlife Agency at 1300 PST to notify them of a dead brown pelican found within the protected area. The pelican was found at 0800 PST and identified it as a brown pelican, protected by the Endangered Species Act, at 1200 PST. The licensee intends to notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Decommissioned | Power Operation | Cold Shutdown | Decommissioned | Power Operation | Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37769 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-02-21 15:15 | 2001-02-21 17:29 | 2001-02-21 | DISCOVERY OF A HATCH PLUGGED THAT SHOULD NOT BE PLUGGED The licensee was conducting an engineering review of HELB analysis in the reactor building which revealed the fact that a hatch was plugged that should not be plugged per the analysis. The plug is thought to have been in place since about 1983. This questions operability of various safety related power supplies. This discovery puts the plant into a 24 hour plant shutdown technical specification. The licensee expects to fix the problem prior to the 24 hour clock time limit. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37768 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-02-21 13:30 | 2001-02-21 16:34 | 2001-02-21 | DISCOVERY OF 2 FIRE DOORS THAT MAY NOT MEET APPENDIX R REQUIREMENTS The licensee discovered that two Appendix R Barrier Doors may not have automatically closed when required. The doors are normally open doors, designed to close automatically when a single temperature sensitive fusible link melts. Contrary to the design it was discovered that the installation of the doors and associated fusible links may prevent the doors from closing. In one scenario it would require two fusible links to melt to get the door closure. This condition existed due to Kewaunee's failure to properly install the actuation equipment. Prior to the discovery, the doors have been closed as part of efforts involving a previous door failure (Event #37668 and LER 2001-01-00). The licensee will keep the doors administratively closed until the problems are corrected. The licensee notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37767 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-02-20 08:46 | 2001-02-20 22:30 | 2001-02-20 | NRC BULLETIN 91-01 24 HOUR REPORT The following is a portion of a faxed report: On 02/20/01 at 0848 hours the Plant Shift Superintendent's office was informed that a Nuclear Criticality Safety Analysis (NCSA) was deficient. NCSA-PLANT088, Storage of Abandoned Equipment, utilizes the NCS calculation document NCS-CALC-98-029, which contains the following non-conservative assumptions: The KENO model used a radius of 6.35 cm to model the inner diameter of a 5-inch pipe. This does not bound all nominal 5-inch diameter pipe. Standard 5-inch pipe can have an inner diameter of 5.345 inches (13.5763 cm) which would require a radius of 6.7882 cm. This document modeled a UO2F2 - H2O mixture with an H/U ratio of 4. The use of this H/U ratio is acceptable for cascade piping due to the way the cascade is operated. It is not acceptable for use in other buildings (i.e. X-705, X-700, and X710) if the pipe is filled with fissile material. An H/U ratio of at least 16 should have been used to bound pipes in the other buildings. NCS-CALC-98-029 provides part of the basis for defining what a safe geometry is in NCSA-PLANT088.A00 (Storage of Abandoned Equipment). The calculation models a spacing violation between two 5.0-inch diameter 10-ft long pipes containing 100% enriched UO2F2 at an H/U of 4. Each pipe modeled in the calculation contains approximately 125,000 grams of U-235 at 100% enrichment. The USEC possession limit for HEU outside of shutdown cascade equipment is 1000 grams U-235. Control 1a in NCSA-PLANT088.A00 defines a safe geometry based on having a nominal pipe diameter of 5-inches or less, as well as limiting the length of the pipe to less than 10-feet and specifying that the pipe has not been exposed to oily material. Since 'nominal' 5-inch diameter pipes may have diameters slightly larger than 5.0-inches, control 1a is not consistent with the assumption in calculation NCS-CALC-98-029 of exactly 5.0-inch diameter. Therefore, NCSA-PLANT088.A00 is technically deficient, NCSA-PLANT088.A00 is currently active in various buildings on plant site. None of the equipment currently regulated by NCSA-PLANT088.A00 used the definition of safe geometry (as defined in control 1A in NCSA-PLANT088.A00) to show double contingency. Rather, all equipment currently under NCSA-PLANT088 is controlled based on being below a safe mass, which the NCSA allows as an alternative to controlling the geometry. Therefore, double contingency can still be shown for all equipment currently regulated by NCSA-PLANT088.A00 (based on spacing and mass controls). As part of the response to this incident, other NCSAs were investigated which referenced either NCS-CALC-098-029 or NCSA-PLANT008 as part of their safety basis, It was determined that NCSA-PLANT062.A04 (Cascade Maintenance Equipment Removal and Storage) has the same problem as NCSA-PLANT088.A00. In addition, NCSA-0705_ 041.A01 (Material Handling and Storage in X-705) and NCSA-PLANT048.A04 (Contaminated Metal) also reference either calculation NCS-CALC-98-029, NCSA-PLANT088.A00, or PLANT062.A04 as part of their safety basis for storage of favorable geometry equipment. While there may be items stored under these NCSAs based on the controls defining favorable geometry, none of these items individually can contain greater than a safe mass because of the requirements of TSRs 2.2.3.16 and 2.7.3.15. These TSRs require any removed cascade equipment containing greater than a safe mass under optimum moderation conditions to be decontaminated within 72 hours. Since there can be no equipment stored under any of the affected NCSAs containing greater than a safe mass, this incident is being reported to the NRC as a 24-hour event report. SAFETY SIGNIFICANCE OF EVENTS: The non-conservative assumption in NCS-CALC-98-029 has a low safety significance for the following reasons: The calculation assumed two 5-inch 10 foot long pipes completely filled with a UO2F2-H2O mixture (H/U ratio of 4) containing approximately 125,000 grams of 100% enriched U-235. This case bounds the entire operating history of the plant. Current plant requirements limit the production of enriched uranium to 10 wt% U-235. Any material greater than 10% is currently contained within shutdown cascade piping (which is covered by other NCSAs not affected by this incident), or is limited to 1000 grams U-235 by the USEC possession limits. There is no equipment currently controlled by NCSA-PLANT088.A00 that uses a safe geometry as one control for double contingency. While there may be equipment covered under NCSAs PLANT062, PLANT048, or 0705_041 that use safe geometry as a control, TSRs 2.2.3.16 and 2.7.3.15 (Removed Equipment with Deposits) ensure that any such equipment containing greater than a safe mass is decontaminated to less than or equal to a safe mass within 72 hours of removal. The safe mass required by these TSRs is based on optimum moderation conditions. As a result of these TSRs and their implementing procedures, there is no removed equipment currently stored on plant site under any of the affected NCSAs which contains greater than a safe mass. Since the safe mass is defined as less than half of the minimum credible critical mass, a criticality would not have occurred even if a spacing violation had occurred. The calculation in question was intended to demonstrate subcriticality in the event of a spacing violation between two favorable geometry pipes. Since there are no known spacing violations between such equipment, there remains at least one control in place to prevent criticality (spacing) in all cases. The normal storage of favorable geometry equipment in a properly spaced configuration was not affected by this discovery. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): Two 10 foot long 5 inch pipes containing a mixture of UO2F2-H2O mixture (H/U ratio of 16) containing I00 wt% U-235 placed adjacent to each other could achieve criticality. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameters for equipment which could be affected by this event are spacing and geometry. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No specific equipment was identified as being out of compliance. Therefore, the amount, enrichment or form is not known. However, it is known that no individual piece of equipment stored under the affected NCSAs contains greater than a safe mass, due to the TSR requirements. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The calculation document for a spacing violation between two favorable geometry components contained a non-conservative assumption which was not properly flown into the NCSA controls. The spacing control remained in place. Thus, one control used for double contingency was rendered invalid. The deficiency will be corrected by revising the NCSA controls to be consistent with the calculation. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Daily Operating Instructions (DOI) stating "No further equipment shall be implemented under NCSA-PLANT088 until the deficiency Is corrected." The licensee has notified the NRC Resident Inspection and DOE. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37766 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2001-02-19 21:08 | 2001-02-20 01:56 | 2001-02-20 | TECH SPEC REQUIRED SHUTDOWN COMMENCED AFTER DECLARING BOTH STANDBY GAS TREATMENT (SGT) TRAINS INOPERABLE "While performing Surveillance 6.SUMP.101, Z SUMP AND AIR EJECTOR HOLDUP LINE DRAIN OPERABILITY TEST (IST), Z-1 sump pump exceeded its operability time limit of 151 seconds by 3 seconds. When Z-2 sump pump was subsequently tested, the pump failed to start on the essential HI-HI level switch. Both sump pumps were declared INOPERABLE. These pumps support Standby Gas Treatment OPERABILITY. The SGT line from the plant runs underground to the Elevated Release Point tower, and the offgas line and SGT both enter this sump. The pumps remove condensation from both the offgas lines and SGT, and must be available post-accident to prevent flooding of the SGT lines. "Per administrative direction in the Surveillance procedure, both trains of SGT were declared INOPERABLE at 2108. Per Technical Specification 3.6.4.3, Condition D, with two SGT subsystems INOPERABLE in Mode 1, the Required Action is to enter LCO 3.0.3 immediately. LCO 3.0.3 requires the plant to be in Mode 2 within 7 hours, Mode 3 within 13 hours, and Mode 4 within 37 hours. A power reduction was commenced at 2250. Present power level is 54%. "Engineering personnel have responded to the plant and are evaluating the two conditions." The above surveillance is performed quarterly. The licensee noted a past history of problems with the system's level switches. The current rate of power reduction is approximately 100 MW/hr or 12-15% reactor power. The licensee informed the NRC resident inspector. * * * UPDATE 0441 2/20/01 FROM TERRY BORGAN TO S. SANDIN * * * Tech Spec required shutdown exited at 0334CST after engineering determined that one train of SGT was OPERABLE. The Unit remains in a 7-day LCO for the other INOPERABLE train. Notified R4DO(Pick). | 54 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37765 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-02-19 20:30 | 2001-02-19 23:38 | 2001-02-19 | UNANALYZED CONDITION FOR RESIDUAL HEAT REMOVAL CAPABILITY The licensee has determined that torus cooling initiation has not been validated as part of operator actions to be initiated within 10 minutes of a design basis accident in the containment. The licensee, as an interim action, has added an extra licensed operator whose only responsibility is the initiation of torus cooling at the direction of the emergency operating procedures. Further analysis is being carried out for a final resolution. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37764 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2001-02-19 12:00 | 2001-02-19 15:24 | 2001-02-19 | THE OHIO EPA NOTIFIED OF AN UNINTENTIONAL DISCHARGE OF CONDENSER COOLING WATER The Ohio EPA was notified of an unintentional bypass of the wastewater treatment system as required by the NPDES Permit. No reportable quantities were discharged. This was a non-radioactive effluent, main condenser cooling water. The license intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0
37763 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-02-16 12:30 | 2001-02-19 13:47 | 2001-02-19 | AGREEMENT STATE REPORT OF PERSONNEL OVEREXPOSURE The following is a portion of the information provided: "Approximately 12:30 am February 16 following a shoot, the source was reeled into what was thought to be a locked position. A complete survey was not done to confirm position of the source. The two individuals involved proceeded in front of the camera to set up the next shot, taking less than 5 minutes. When they went to unlock the source they realized that it was not locked and noticed the survey meter was off scale. They exited the area and fully retracted the source. Both pocket dosimeters were off scale. One rate alarm meter was turned off and the other had a low battery and did not give a audio alarm. Film badges showed 2.9 and 39.2 R exposure. The individual with the high exposure has had blood drawn for analysis but no results are available yet. Landauer has been asked recheck the film badge readings. The wrong state office was notified 16 February. This office was notified 19 February." The camera contains a 58 Ci source of Ir-192. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37762 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-02-19 06:12 | 2001-02-19 13:04 | 2001-02-19 | LOSS OF EMERGENCY COMMUNICATIONS TO THE STATE The licensee lost the emergency communications line to the states of Alabama and Georgia at 0512 CST on 2/19/01 due to the failure of a communications power inverter located offsite in Dothan, Alabama. The inverter was restored at 0758 CST, restoring the emergency communications line. All other communications were available during this time. The licensee intends to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37761 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-02-18 22:45 | 2001-02-19 03:00 | 2001-04-18 | HIGH PRESSURE COOLANT INJECTION SYSTEM (HPCI) DECLARED INOPERABLE "During normal monitoring of the standby lineup of the High Pressure Coolant Injection System (HPCI), the building rounds operator noticed that the HPCI discharge flow switch (23FS-78) was indicating 140 gpm with zero actual flow. This flow switch controls the operation of the HPCI pump minimum flow valve during HPCI operations. Upon further investigation by the operating crew, it was also determined that the HPCI pump discharge flow transmitter was exhibiting sporadic flow spikes of 50 to 100 gpm with zero system flow. This flow signal is used to control HPCI turbine speed and flowrate. Based on these findings, the HPCI system was declared inoperable per Technical Specification 3.5.c and a 7 day Limiting Condition for Operation was entered." The licensee called in an engineering team to address this problem. The licensee will inform the NRC resident inspector. * * * RETRACTION 1529 4/18/01 FROM PAGE TAKEN BY STRANSKY * * * "On 2/19/01 at 0300 EST, the James A. Fitzpatrick nuclear power plant notified the NRC that the High Pressure Coolant injection (HPCI) System had been declared inoperable due to indicated flow on a local discharge flow switch indication and sporadic flow spikes on the pump discharge flow transmitter while the system was in the standby lineup. The report was made pursuant to 10CFR50.72(b)(3)(v)(D) under Event Notification number 37761. "Based upon further review, it has been determined that, despite the problems noted, HPCI would have performed its safety function. The local HPCI discharge flow switch indication has no safety-related function. The associated safety-related switches operated within the prescribed setpoint tolerances. The hydraulic and mechanical portions of the system cannot respond to change as quickly as the electronic components, and therefore were not affected by the higher frequency sporadic spiking on the pump discharge flow transmitter. Maintenance was performed to address the associated degraded conditions. "Based upon the ability of the HPCI System to perform its safety function, the above notification is being retracted." The NRC resident inspector will be informed of this retraction. Notified R1DO (Ruland). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37760 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-02-18 21:00 | 2001-02-19 01:22 | 2001-02-19 | INDICATION OF PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING VISUAL INSPECTION OF REACTOR VESSEL HEAD "Event: Preliminary Reactor Vessel Head visual inspection indicates a small amount of boron residue surrounding 6 Control Rod Drive mechanism head penetrations. These indications are similar to those previously reported during U-1 EOC-19 refueling outage. "Initial Safety Significance: Preliminary indication of leakage through Reactor Coolant System Pressure Boundary. "Corrective Action(s): Additional inspections will be performed to determine the cause of identified boron accumulation." Unit 3 is currently in mode 5 (Cold Shutdown) depressurized to atmosphere with RCS temperature at 120 degrees F. The licensee is making preparations to enter mode 6 (Refueling) in order to lift the RV Head. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37759 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-02-16 21:37 | 2001-02-17 12:49 | 2001-02-17 | VALID ACTUATION OF SAFETY SYSTEM "At 2137 hours on 02/16/01, both the 'A' and 'B' High Level Condensate Alarms activated on Autoclave #1 in the X-343 Feed and Sampling Facility. The activation of either of these alarms will cause the autoclave steam supply valves ('Q' components) to actuate (close). The steam supply valves closed, as designed, upon the activation of the High Condensate Alarms. Autoclave #1 was in TSR Mode II (HEATING) at the time of the alarm activations. Operations personnel immediately responded to the alarms in accordance with the approved Alarm Response Procedures. Both alarms reset when the operations personnel acknowledged the alarms at the local autoclave control panel. All autoclave (and cylinder) operating parameters were determined be to within normal ranges, Autoclave #1 was placed in TSR mode VII (Shutdown) by operations personnel and declared Inoperable by the Plant Shift Superintendent's Office. Based on the actuation of both High Level Condensate alarms, this event is being reported as a valid safety system actuation, a 24-hour NRC event. An Engineering Evaluation has been requested to investigate the circumstances surrounding this safety system actuation." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37758 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-02-16 10:20 | 2001-02-17 03:17 | 2001-02-17 | SAFETY EQUIPMENT FAILED TO FUNCTION AS REQUIRED BY TECHNICAL SAFETY REQUIREMENT "At 1020 on 02-16-01, the Plant Shift Superintendent (PSS) was notified of a safety system failure in the C-315 building. While closing the cylinder valve on a full liquid cylinder, the valve failed to close completely when a shear pin broke on the emergency cylinder valve closure mechanism. At the time of the failure the cylinder valve was still approximately one eighth of a turn open. The operator manually closed the valve thus placing the cylinder in a safe mode. The emergency cylinder valve closure mechanism is part of the Low Voltage UF6 Release Detection and Isolation System at the Withdrawal Stations, and is required to be operable according to TSR 2.3.4.1. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or falls to function as designed. "The NRC Senior Resident has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0
37757 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2001-02-16 16:30 | 2001-02-16 19:41 | 2001-02-20 | HIGH PRESSURE CORE SPRAY SYSTEM DECLARED INOPERABLE "During performance of 1C3 battery all-cell checks, battery cell #38 was found to be >0.020 below the average for specific gravity. Tech Spec 3.8.6, 'Battery Cell Parameters,' requires declaring 1C3 battery inoperable. This caused entry into Tech Spec 3.8.4 Action D, which is to declare the High Pressure Core Spray system inoperable. This requires entry into a 14 day LCO. This event is reportable since High Pressure Core Spray is a single train system." The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTED AT 1549 EST ON 2/20/01 BY CHRIS MILLER TO FANGIE JONES * * * The licensee is retracting this event notification. After further review it has been determined that the entry conditions for the LCO were not met and the division 3 batteries were never inoperable. The licensee notified the NRC Resident Inspector. The R4DO (Linda Smith) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37756 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-02-15 23:20 | 2001-02-16 16:36 | 2001-02-16 | VALID ACTIVATION OF SAFETY SYSTEM "At 2320 hours on 02/15/01, both the 'A' and 'B' High Level Condensate Alarms activated on Autoclave #2 in the X-343 Feed and Sampling Facility. The activation of either of these alarms will cause the autoclave steam supply valves ('Q' components) to actuate (close). The steam supply valves closed, as designed, upon the activation of the High Condensate Alarms, Autoclave #2 was in TSR Mode IV (FEEDING) at the time of the alarm activations. Operations personnel immediately responded to the alarms in accordance with the approved Alarm Response Procedures. Both alarms reset when the operations personnel acknowledged the alarms at the local autoclave control panel. All autoclave (and cylinder) operating parameters were determined be to within normal ranges. Autoclave #2 was placed in TSR mode VII (Shutdown) by operations personnel and declared Inoperable by the Plant Shift Superintendent's Office. Based on the actuation of both High Level Condensate alarms, this event is being reported as a valid safety system actuation, a 24-hour NRC event." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37755 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2001-02-16 15:05 | 2001-02-16 15:40 | 2001-02-16 | OFFSITE NOTIFICATION DUE TO RECEIPT OF CONTAMINATED ITEMS "While performing routine surveys, Turkey Point Health Physics personnel discovered low levels of radioactivity on several plastic Caution signs received from the Byron Nuclear Power Station. The signs were surveyed at Turkey Point prior to use in the site's radiation controlled area. These items were counted in a Small Articles Monitor (SAM) and indicated low level contamination was present. In total, 6 out of approximately 650 items surveyed indicated the presence of low level fixed activity. The highest level measured was 7,000 disintegrations per minute (dpm) using a standard HP-210 (pancake GM) probe. Isotopic analysis indicates cobalt-60 and manganese-54. One item had low levels of loose surface contamination (57 dpm/100 cm2). The items identified with low level fixed contamination are now being held inside the Turkey Point radiation controlled area. The signs were shipped in cardboard boxes and no loose surface contamination was found on the exterior of the boxes "Florida Power & Light Company has notified the Byron Station and the State of Florida (Department of Health, Bureau of Radiation Control) of this matter." The licensee has informed the NRC resident inspector of this notification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37754 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-02-16 08:15 | 2001-02-16 14:47 | 2001-02-16 | FITNESS FOR DUTY REPORT A non-licensed employee tested positive for the use of illegal drugs during a random test. The test results were confirmed positive by the licensee Medical Review Officer. The individual's access to the plant has been suspended in accordance with the licensee's FFD program. The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0
37753 | 0 | MARTIN MARIETTA ANDERSON CREEK QUAR |  |  |  |  | 2001-02-15 | 2001-02-16 10:59 | 2001-02-16 | TRANSPORT AND SUBSEQUENT DISCOVERY OF SCRAP METAL CONTAINING 50 MILLICURIES OF CESIUM-137 (NRC GENERALLY LICENSED MATERIAL) AT MARTIN MARIETTA ANDERSON CREEK QUARRY On 02/13/01, Martin Marietta Anderson Creek Quarry (located in Rockville, Virginia, near Richmond) shipped scrap metal to Cycle Systems (a scrap yard located in Lynchburg, Virginia). Cycle Systems surveyed the material and discovered 50 millicuries of cesium-137. (The material was apparently a sensor or level gauge from a conveyer system.) Cycle Systems notified the quarry and the State of Virginia. The State of Virginia notified the NRC Region 2 office, and the NRC Region 2 office (Wade Loo) contacted the quarry. The material was returned to the quarry on 02/15/01. The shutter is currently locked closed, and the material has been placed in an office. Martin Marietta Anderson Creek Quarry believes that the material may have come from another quarry. The actual source of the material is currently being investigated. (Call the NRC Operations Center for quarry contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | VA | MAT | [5 empty] | 0
37752 | 0 | JACOBS PAN AMERICAN |  |  |  |  | 2001-01-13 | 2001-02-15 17:14 | 2001-02-15 | POSSIBLE OVEREXPOSURE OF EXTREMITY The licensee reported that an individual may have received an overexposure (~ 2 R) of the right hand. The individual's hand may have come within 3/8 inch of a 40 Ci source. An NRC Region II inspector is currently at the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 20.2202(a)(1) |  |  |  | 0
37751 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-02-15 14:17 | 2001-02-15 15:45 | 2001-02-15 | MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER PUMP Operators manually tripped the reactor after the Unit 1 East main feedwater pump tripped due to loss of condenser vacuum in the East main feedwater pump condenser. All systems functioned as expected following the trip. The unit is currently stable in Hot Standby. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37750 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-02-14 16:00 | 2001-02-14 20:00 | 2001-02-14 | ANALYSES OF AN ELECTRICAL BOX DOES NOT MEET THE FIRE RESISTANCE OF APPENDIX R The Kewaunee Engineering staff, while conducting a review, recognized that they could provide no analyses to support compliance to 10CFR50, Appendix R, for an electrical wiring pull box. The box provides an enclosure for dedicated safe shutdown equipment wiring, 'A' train equipment. The box is located in an alternate safe shutdown equipment room, 'B' train, where the box provides protection against fire. However, though the analyses of the box provides assurance that the design will protect the 'A' train equipment wiring from a fire, it does not provide a three hour barrier consistent with Appendix R requirements. Therefore, this places the plant in an unanalyzed condition. The box was designed and installed in the early to mid 1980s. Compensatory measures have been taken to ensure continued safe plant operation. The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0
37749 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-02-14 08:51 | 2001-02-14 17:05 | 2001-02-16 | BOTH TRAINS OF CONTAINMENT COOLERS AND ONE TRAIN OF CONTAINMENT SPRAY INOPERABLE The following text is a portion of a facsimile received from the licensee: "On 2/14/01, the 'A' train containment cooling train was removed from service at 0507 CST for associated circuit breaker work. At 0851 CST the 'B' Train Essential Service Water pump was started to support performance of the 'A' Train SIS/CIS Slave Relay Test. "The 'B' Essential Service Water pump failed to achieve rated flow and pressure and was declared inoperable at 0851 CST. This resulted in entry into Technical Specification LCO 3.6.6, Required Action F.1 for both trains of containment coolers inoperable and one train ('B') of Containment Spray inoperable. LCO 3.6.6 Required Action F.1 also requires entry into LCO 3.0.3. Technical Specification 3.0.3 was entered at 0851 CST and exited at 1123 CST when the 'A' train of Containment Cooling was returned to service. The plant remains in Technical Specification LCO 3.7.8 Required Action A.1 (72-Hour Action Statement) for one train ('B') of Essential Service Water inoperable. "This condition at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences for an accident. It was concluded that this event was reportable per 10CFR50.72(b) (3) (v) since: (1) Both trains of containment cooling were lost as a result of the unanticipated failure of the 'B' train Essential Service Water pump in conjunction with the 'A' train containment coolers being removed from service. (2) Cascading through technical specification resulted in the loss of 'B' train containment spray system. "The failure of the 'B' train Essential Service Water pump is under evaluation." The licensee notified the NRC Resident Inspector. UPDATE 1706 2/15/2001 VIA FACSIMILE TO STRANSKY * * * "Upon investigation of the 'B' Essential Service Water pump problem, an obstruction was found in the suction of the pump. The obstruction was subsequently removed and the pump was then started to evaluate the operability condition of 'B' Essential Service Water pump. The pump was evaluated for normal flow, discharge pressure, and vibration. All parameters were found within normal operating limits, the 'B' Essential Service Water pump was declared Operable at 0231 on 2/15/O1 and Technical Specifications 3.7.8.A.1 and 3.8.1.B were exited." Notified R4DO (Pick). *** UPDATE AT 0615 ON 02/16/01 - LEIGH TROCINE CALLED SITE (JOHN DAMPS) *** The obstruction was a 20-foot long piece of tygon tubing. It was reported that the tubing had been hanging from a funnel near a hole in a pre-lube tank for the pump's seals. Apparently, the tubing fell into a drain and made its way to the pump suction. The licensee stated that the resident inspectors were aware of this information. The NRC operations center notified the R4DO (Pick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37748 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-01-01 | 2001-02-14 12:33 | 2001-05-14 | AGREEMENT STATE REPORT OF STOLEN HUMBOLDT GAUGE The following text is a portion of a facsimile received from the Texas Department of Health, Bureau of Radiation Control: "On Monday January 1, 2001, a moisture/density gauge was stolen from the back of a pickup truck that was parked at an apartment complex in Harlingen, Texas. The technician who had used the gauge went to his apartment from 10:00 am to 1:00 p.m. after completing work at one job site. When the technician was getting into his truck, he noticed the lid on the gauge transport case was cracked open and the gauge was missing. "The stolen gauge is a Humboldt Model 5001-C, serial number 1467. The gauge contained two sources: 10 millicuries of Cs-137, source serial No. 692GH, and 40 millicuries of Am-241:Be, source serial No. NJO1429. "The Licensee notified the Harlingen Police Department, this Agency, and the manufacturer. The Licensee placed an ad in a local newspaper offering a $500 reward for the return of the gauge." Call the NRC operations officer for contact information. ***** UPDATE RECEIVED AT 1606 EDT ON 05/14/01 FROM HELEN WATKINS TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the Texas Department of Health, Bureau of Radiation Control: "This is a followup report. The gauge was found and returned to the licensee." The following text is a portion of a letter provided to the Texas Department of Health by the licensee on 03/12/01: "[...] This gauge has been recovered. [...] The gauge was in good working order, and had not visibly been abused. The lock that keeps the source rod from being exposed was intact, and no visible signs of removal were visible. Upon transporting [the] gauge back to the laboratory[, ... ] a leak test [was performed,] and [the gauge was] sent [...] to SUNTRAC Services for [analysis. ... Less] than 0.0001 µCi were found on Alpha, Beta, and Gamma rays. [...]" The NRC operations officer notified the R4 DO (Spitzberg) and NMSS EO (Reamer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37747 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-02-14 04:08 | 2001-02-14 10:49 | 2001-02-14 | HIGH PRESSURE FIRE HEADER IMPAIRMENT AND SURVEILLANCE PER STATION ADMINISTRATIVE ORDER (SAO) 703 (24-Hour Report in accordance with the license) The following text is a portion of a facsimile received from the licensee: "The high pressure Fire Water Protection System is degraded due to planned maintenance work. The inner and outer high-pressure fire headers are split to provide protection for work on the valves for [the] 12 Fire Main Booster Pump. [The] 12 Fire Main Booster Pump is inoperable during this tag-out. The diesel fire pump is in service as the alternate fire protection for the outside fire header. [The] 11 Fire Main Booster Pump is in service for the inside header. SAO-703 states [that] one fire main booster pump out of service is a 7-day action statement to return it to operable status. The headers being separated or any part of the fire protection piping or valves not being able to perform [their] function other than the specific instances described in SAO-703 [require] an alternate fire protection system shall be established. This was established within 24 hours to ensure compliance with SAO-703 as described above. A special report shall be submitted to the NRC Regional Administrator of the Region 1 Office outlining this issue within 14 days." The licensee notified the NRC resident inspector and plans to notify the NRC Region 1 office (Pete Eselgroth). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
37746 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2001-02-03 | 2001-02-14 10:00 | 2001-02-14 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER NUCLEAR DENSITY GAUGE The following text is a portion of a facsimile received from the Texas Department of Health, Bureau of Radiation Control: "This is an initial notification of a stolen nuclear gauge. The gauge was stolen on Saturday February 3, 2001, from the parking lot of the Midway Point Restaurant, [...], Dallas, Texas, while the [driver] ate lunch between jobs. The Licensee's initial report indicates that the gauge was secured in it's transport case and chained to the company pickup with chain and lock. The driver noted that the gauge, the lock, and chain were all missing. The stolen gauge was a Troxler Model 3430, Serial Number 31580. The gauge contained two sources: 8 millicuries of Cs-137, Source Serial No. 750-6419, and 40 millicuries of Am-241:Be, Source Serial No. 47-28229. A Police Report was filed with the Dallas Police Department (Report Service #0083748-K - [...]). The operator reported the loss to his supervisor and a report was telephoned to this Agency on February 5, 2001. Two written reports were faxed to the Agency [...]. The gauge has not been recovered to date. An Agency investigation is ongoing. The Texas Licensee (L02356) is Rone Engineers [located in] Dallas, Texas [...]." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37745 | 0 | MERCY HOSPITAL |  |  |  |  | 2001-02-13 23:30 | 2001-02-14 09:37 | 2001-02-14 | POSSIBLE MISADMINISTRATION AT MERCY HOSPITAL IN PORT HURON, MICHIGAN A patient was receiving a treatment with a gynecological implant containing two cesium-137 sources (with 13.74 milligrams radium equivalent each). The patient was reportedly restless and moving around quite a bit, and the applicator was in its proper position at 2100. However, when nurses checked on positioning of applicator at 2330 on 02/13/01, it was discovered that the applicator had gotten past the sutures and come out completely. The implant treatment procedure was terminated at that time. Based on the minimum and maximum amount of time that the applicator may have been in the proper position, the patient received between 66% and 71% of the intended dose. Conservative calculations (assuming that the applicator came out at 2100) revealed doses to unintended areas were not anticipated to cause adverse health complications as a result of this exposure. The patient has been informed. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.33 |  |  |  | 0
37744 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2001-02-14 02:30 | 2001-02-14 07:44 | 2001-02-14 | SANITARY WELL WATER FAILURE DUE TO A LINE RUPTURE (24-Hour Report involving the potential inability to mitigate the circumstances of an accident) Honeywell Metropolis Works is a fuel cycle facility that performs UF6 conversion. At approximately 0230 CST, a 6-inch diameter sanitary process line ruptured. As a result, the licensee secured (shut down) both the safety showers and the process. The ruptured line has been isolated, and process water has been valved into the safety showers. However, the licensee has not yet brought up the process. Repair planning is underway. The licensee plans to notify the NRC Region 3 office, an onsite NRC inspector (Mary Thomas), and the NRC resident inspector at Paducah (Courtney Blanchard). (The USEC Paducah facility is located across the river.) Call the NRC operations officer for a licensee contact telephone number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0
37743 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-02-14 01:50 | 2001-02-14 02:51 | 2001-02-14 | THE LOSS OF A 480-VOLT BUS DUE TO A PERSONNEL ERROR DURING SURVEILLANCE TESTING RESULTED IN THE AUTOMATIC START OF THREE EMERGENCY DIESEL GENERATORS. At 0150 on 02/14/01, 480-volt bus 3A was lost due to incorrect operation of a switch during performance of a surveillance test. An individual performing the test needed to simultaneously hold a switch in the bypass position while a test button was pressed, and the switch was not held in the correct position. As a result, an undervoltage signal was inserted on the bus when the test button was pushed, and all three emergency diesel generators automatically started as designed. The licensee stated that the emergency diesel generators do not automatically load on the loss of an internal bus and that all automatic functions operated properly. The licensee also stated that the loss of any 480-volt bus places the unit in a shutdown action statement in accordance with Technical Specification 3.0.1. However, power (via an emergency diesel generator) was restored to the bus in accordance with procedures at 0215, and restoration of power satisfied the action statement requirements in Technical Specification 3.0.1 within 25 minutes. The licensee is currently in the process of restoring normal bus power supply. The licensee stated that bus 3A is one of the power supplies for the 22 safety injection pump. This bus also supplies power to the 21 residual heat removal pump, 22 and 25 service water pumps, 24 fan cooler unit, 21 auxiliary boiler feed pump, 22 charging pump, 21 backup heater for the pressurizer, and 23 instrument bus (via the 23 battery charger). The licensee plans to notify the NRC resident inspector and applicable government agencies. The licensee may also issue a press release. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37742 | 0 | WATERFORD | 3 |  |  | [3] CE | 2001-02-13 16:54 | 2001-02-13 21:18 | 2001-02-13 | AUTOMATIC REACTOR TRIP DURING TURBINE VALVE TESTING "On 2/13/2001 at 1654 CST Waterford 3 sustained a reactor trip from 82% RTP. The reactor trip was most probably caused by variable over power trip, which is a core protection calculator auxiliary trip. Actuation of the emergency feedwater system also occurred due to shrinkage of coolant in the steam generator caused by the reactor trip; however, no emergency feedwater was actually fed into the steam generators. Actuation of the emergency feedwater system is a normal occurrence following a reactor trip. This condition is reportable under 10CFR50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system when the reactor is critical, which is a 4 hour report; and 10CFR50.72(b)(3)(iv)(A), any event or condition that results in valid actuation of the emergency feedwater system, which is an 8 hour report. At the time of the trip Waterford 3 was performing turbine valve testing per OP-903-007. Governor Valve 3 was being tested and sporadically started opening and closing." The plant is stable in Hot Standby with excess heat removed via forced circulation to the steam generators and steam released through the bypasses to the main condensers. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37741 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2001-02-13 | 2001-02-13 17:11 | 2001-02-15 | AGREEMENT STATE REPORT OF A STOLEN TROXLER GAUGE "This first notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is that which is available after preliminary investigation and is basically all that is known by the Agency Staff at this time. "Date: 02/13/01 Time: 0430-0815 AM, MST First Notice No.: 01-01 "Arizona Licensee: Ricker-Atkinson-McBee & Assoc. License: No. 07-406 "Description of the event: Between the hours of 0430 AM and 0815 AM a Troxler Moisture Density Gauge, Model #3440, S/N 26981 was stolen from the licensee's facility while locked and chained in the bed of the users 2000 Dodge Dakota Pickup Truck, Arizona Lic. #523FCY. The gauge and scatter block were removed from the transport case and the case remained in the pickup. A reward of $500.00 is being offered by the licensee upon return of the gauge. "The states of Utah, California, Colorado, New Mexico, and U.S. NRC Region IV, USNRC-DC, U.S. FBI and the governor's office are being informed of this incident." *** UPDATE AT 1108 EST ON 02/15/01 VIA FACSIMILE FROM AUBREY V. GODWIN TO LEIGH TROCINE *** The following text is a portion of a facsimile received from the Arizona Radiation Regulatory Agency: "This Supplemental Notice constitutes EARLY additional informational notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation and is basically all that is known by the Agency Staff at this time." "Date: February 15, 2001 Time: 9:00 AM (MST) First Notice: 01-01 Arizona Licensee: Ricker-Atkinson-McBee & Associates [in] Tempe, AZ License No.: 07-406 [...]" "On February 13, 2001, the LICENSEE reported the [theft] of a Troxler Model 3440 moisture density gauge. A First Notice No. 01-01 was issued to report this event to appropriate agencies. Late February 14, 2001, a pawn shop in Phoenix reported that they had obtained a nuclear gauge and wished to release it to the proper authorities. The gauge was recovered from the pawn shop with locks intact. The Phoenix PD is investigating the circumstances of the transfer of the device to the pawn shop." "The LICENSEE and the Agency continue to investigate this event." "The states of Utah, California, Colorado, New Mexico, and Nevada together with the U.S. NRC, the U.S. FBI, and Mexico are being notified of this event." (Call the NRC operations officer for both State and licensee contact information.) The NRC operations officer notified the R4DO (Pick) and NMSS EO (Cool). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0
37740 | 0 | UNION HOSPITAL |  |  |  |  | 2001-02-13 | 2001-02-13 15:42 | 2001-02-13 | LOST SOURCE - SEED USED FOR PROSTATE PROCEDURE The hospital discovered that one seed out of 110 seeds, apparent activity is .311 mCi I-125 (full activity is .587 mCi) was missing after the completion of an implant procedure. An extensive search of the operating room, equipment, drains, laundry, and hallways failed to discover the missing seed. The patient was scanned and the best analysis is that the patient received the proper number of seeds. There is little or no threat to the public health or safety. The hospital contacted NRC Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0
37739 | 0 | COOPER POWER SYSTEMS INC |  |  |  |  | 2001-01-18 | 2001-02-13 11:53 | 2001-02-13 | THE LICENSEE REPORTED A MISSING ELECTRON CAPTURE DETECTOR During a physical inventory of radiation sources, the licensee reported that an electron capture detector for a gas chromatograph, used in a chem lab, was missing on the last inventory performed on 01/18/01. The device was a PerkinElmer model PE009-0282 serial # 1648 containing Ni-63 <15 millicuries. A search was made, but the device did not show up. It was last inventoried approximately three years ago. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | WI | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0
37738 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2001-02-13 10:40 | 2001-02-13 10:57 | 2001-02-13 | FLORIDA FISH AND WILDLIFE CONSERVATION COMMISSION WAS NOTIFIED THAT A SICK SEA TURTLE NEEDED REHABILITATION. The licensee rescued a sea turtle from the intake canal. As a result, the licensee notified the Florida Fish and Wildlife Conservation Commission that the turtle had been rescued and needed rehabilitation. The resident inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37737 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2001-02-12 14:45 | 2001-02-13 10:00 | 2001-02-13 | SEALED SOURCE DELIVERED TO THE INCORRECT ADDRESS On 01/25/01 AEA Technology QSA, Inc., shipped a packaged 500 mCi promethium-147 sealed source via FED EX to Impact Systems located in Los Gatos, CA. On 02/01/2001 Impact Systems called AEA Technology QSA asking where the package was. AEA Technology QSA, Inc., contacted FED EX and was informed that the package had been delivered to Fastech Integration, Inc., located at 101 Albright St., Los Gatos, CA. FED EX went back to the address to reclaim the package and to complete the delivery to Impact Systems. FED EX said that they would notify AEA Technology QSA, Inc., and let them know if there was a problem. AEA Technology QSA, Inc., received a second call from Impact Systems on 02/07/01 asking where the package was. AEA Technology QSA, Inc., immediately contacted FED EX on 02/07/01. On 02/12/01 FED EX informed AEA Technology QSA, Inc., that they had gone back to Fastech Integration, Inc., and spoke to the individual who has signed for the package, but the receiver stated she did not have the package. The State of Massachusetts informed the State of California of this event and are still following up on this event. * * * UPDATE AT 1511 EST ON 2/13/01 BY ROBERT GALLAGHAR TO FANGIE JONES * * * The source has been located by Fastech Integration, Inc. and delivered to Impact Systems, the company that ordered the source. The package was intact. The State of Massachusetts will inform the State of California of the event update. The R1DO (Clifford Anderson), R4DO (Greg Pick), and NMSS (Fred Sturz) have been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0
37736 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2001-02-09 | 2001-02-12 15:04 | 2001-02-12 | AGREEMENT STATE REPORT FROM TENNESSEE Tennessee Report Number: TN-01-014 "Event description: On 2/9/01 a fire occurred in a dust collector while torch cutting operations were ongoing. The dust collector is located in an area of known contamination. The individuals present were wearing respiratory protection and full anti-contamination clothing as required by the Radiation Work Permit. When the employees noticed smoke coming from the air filter bank (dust collector), they shut off the ventilation pump drawing air through this particular bank and as a result the fire extinguished itself without adding water or any other extinguishing media. The Oak Ridge Fire Department responded and took hoses in the area but did not use them. The dust collector feeds directly into the main building ventilation pre/HEPA bank that was NOT impacted by this event. The main bank was isolated, opened, and determined not to have been affected. MSC has two parallel pre/HEPA systems for the main building thus allowing them to shut down and isolate one system while the other is online and functional. The housing for the dust collection system was not damaged. There were no personnel contaminated as a result of this event. The workplace air samplers were pulled and determined not to exceed 20% of a DAC for the most restrictive isotope being handled, which in this case was Uranium-238. The building was evacuated a result of the event. The prefilter had been replaced in this unit approximately three days prior to the event. There was damage to the prefilter. DRH staff are onsite investigating the event. These events do not pose a threat to public health and safety, but may be reportable under 1200-2-5-141(2)(c)4 of State Regulations for Protection Against Radiation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
37735 | 0 | STANDARD TESTING AND ENGINEERING CO |  |  |  |  | 2001-02-10 | 2001-02-11 19:11 | 2001-02-17 | STOLEN TROXLER GAUGE A Troxler 3430 serial #16299 was stolen out of the back of an employee's truck while it was parked at his house in Del City(a suburb of Oklahoma City). The gauge, which contained 8 millicuries Cs-137 and 40 millicuries Am-241/Br, was triple locked in the back of the truck. It was stolen on the night of 2/10/01 or the morning of 2/11/01. The local police were notified. Troxler was notified and they will notify the state. * * * UPDATE 1409 2/17/2001 FROM HURST TAKEN BY STRANSKY * * * The gauge was recovered earlier today. It was found intact in its case. The licensee is currently performing a wipe test of the device to be sure that there was no leakage. Notified R4DO(Pick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | OK | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
37734 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-02-09 16:30 | 2001-02-09 18:37 | 2001-02-09 | LOSS OF BOTH LONG DISTANCE COMMERCIAL AND ALL FTS COMMUNICATIONS. The licensee has lost all FTS communications and long distance commercial lines. They have microwave capability via their Houston office for long distance and local service is still available from the site for contacting county officials. The NRC Resident Inspector was notified. * * * UPDATE ON 2/9/01 @ 2156 BY BRINKLEY TO GOULD * * * FTS Communication was restored at 2156 EST along with their commercial long distance. The NRC Resident Inspector will be notified. Reg 4 RDO(Sanborn) was informed. | 100 | 48 | 0 | 100 | 48 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37733 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2001-02-09 15:15 | 2001-02-09 17:13 | 2001-02-15 | LOST/UNACCOUNTED FOR SECURITY WEAPON. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. CONTACT HOO FOR ADDITIONAL INFORMATION THE RESIDENT INSPECTOR WILL NOTIFIED * * * RETRACTION 1508 2/15/2001 FROM HAMM TAKEN BY STRANSKY * * * The licensee has determined that this event is not reportable under 10 CFR 73.71, and this report is being retracted. The NRC resident inspector will be informed. Notified R4DO (Pick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0
37732 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2000-12-29 | 2001-02-09 15:39 | 2001-02-09 | UNATTENDED MOISTURE DENSITY GAUGE FOUND ON A CURB AT AN APARTMENT COMPLEX. A Troxler Model 3440 series #29497 nuclear moisture density gauge belonging to Ground Engineering Consultants was found on the morning of 12/30/00 by the Aurora Police Department, who notified and requested the Fire Department and the Colorado Dept of Health to respond to the site. The gauge apparently had been left on the curb by a Ground Engineering employee who had unloaded it the night before from his truck near his apartment entrance prior to parking his vehicle in his parking space. When he returned to his apartment he inadvertently left the gauge at the curb where the police discovered it the next morning. That morning when the employee realized what was going on outside, he immediately went out to meet with the fire department and properly secured the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0
37731 | 0 | U.S. ARMY |  |  |  |  | 2001-02-08 | 2001-02-09 11:19 | 2001-02-13 | LOST SOURCE AT FT. RILEY, KANSAS The U.S. Army Aberdeen Proving Grounds reported the loss of a chemical agent detector, model number M43A1. The detector contains 300 microcuries of Am-241. The exact date, time and circumstances of the loss are not known. * * * UPDATE 1150EST ON 2/13/01 FROM JEFF HAVENNER TO S. SANDIN * * * The Rock Island Depot updated this report to provide the following additional details: The detector was lost during an Infantry training exercise. The unit involved is currently at Ft. Irwin, CA and unavailable for questioning. The RSO at Ft. Riley intends to conduct a search of the exercise area when the snow melts. Notified R1DO(Anderson), R3DO(Phillips) and NMSS(Sturz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37730 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2001-02-07 09:00 | 2001-02-09 09:30 | 2001-02-09 | AGREEMENT STATE REPORT FROM NEBRASKA Received report from State of Nebraska in chronological or time line format. Contents of report is summarized below: Silverhawk Aviation Aircraft carrying 3 boxes of radiopharmaceuticals crashed approximately 1 mile away from the Ainsworth Airport located in Nebraska. The contents of the RAM packages were 18 unit doses of Technetium-99m totaling 23.4 gigabecquerels. State Highway Patrol has verified that 2 of the 3 RAM packages were unopened and that the third package was breached. One package read 1 mrem/hr on contact (normal), the other unopened package read 100 mrem/hr at 1 meter, and that the third package was broken open in the plane and no unit doses were left in the package. Contamination on scene. Bryan Enterprises Mobile Nuclear Medicine Van was available to survey the area. Nebraska State Patrol was on scene. Responders at the scene were in full HAZMAT gear and are being monitored | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0
37729 | 0 | DRAPER ADEN ASSOCIATES |  |  |  |  | 2001-02-08 21:00 | 2001-02-08 23:09 | 2001-02-08 | LOST TROXLER GAUGE The licensee reported that a Troxler model 3411 serial #16727 (8.5 millicuries Cs-137 and 40 millicuries Am-241 Be) fell out of the back of an employees truck between work and home (approx. 15 to 20 miles). They made a search of the route taken by the employee, but they did not find it. The licensee notified the local police department. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
37728 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-02-08 19:00 | 2001-02-08 20:07 | 2001-02-08 | PLANT DECLARED SSPS(SOLID STATE PROTECTION SYSTEM) INOPERABLE Reactor shutdown was initiated at 1900 due to train "B" SSPS being declared inoperable. Technical Specifications 3.3.1.1 and 3.3.2.1, which were entered at 1628, requires the Unit to be in hot standby within 6 hours. The problem was caused by a redundant power supply to the "B" train being declared inoperable, and an incorrect procedure. Procedure changes are currently being developed to correct it. The NRC Resident Inspector was notified. * * * UPDATE ON 2/8/01 BY JOHNSON TO GOULD * * * Procedural changes were complete at 2030 and power reduction was terminated at 58% and power was stabilized between 50 and 55 percent. The plant will maintain that power level until feed pump repairs are complete(approx. 4-5 hrs). The NRC Resident Inspector was notified. The Reg 3 RDO(Clayton) and NRR EO(Marsh) were informed. | 60 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37727 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-02-08 14:47 | 2001-02-08 17:35 | 2001-03-27 | BOTH REACTOR RECIRCULATING SAMPLE LINE CONTAINMENT ISOLATION VALVES DECLARED INOPERABLE During operation of Unit 2 at 100% power, it has been determined that both Primary Containment Isolation Valves for the Reactor Recirculating Sample Line are inoperable. During restoration from maintenance activities on the line, the outboard isolation valve[HV243F020] failed to stroke closed. Following several attempts the valve was closed. The valve was declared inoperable, and as required by Technical Specifications an attempt was made to close the inboard isolation valve[HV243F019]. The inboard valve also failed to close. The air supply was isolated to the outboard valve to deactivate it, and the pathway was confirmed to be isolated. The problem with the outboard valve is due to a bad solenoid. The problem with the inboard valve is under investigation. They were able to get both valves closed when the inboard valve finally closed on its own an hour later. The NRC Resident Inspector was notified. * * * UPDATE 1244EST ON 3/27/01 FROM BOESCH TO S. SANDIN * * * This report is retracted based on the following: "ENS Notification # 37727 on 02/08/01 at 1735 reported that both Unit 2 Reactor Recirculating System sample line Primary Containment Isolation Valves (PCIVs) were declared inoperable. This event is now being retracted. "The original notification stated that during restoration from maintenance activities on the sample line, the outboard PCIV (HV243F020) initially failed to stroke closed via a manual signal from the control room. The inboard PCIV (HV243F019) also failed to close via a manual signal from the control room. HV243F020 was subsequently closed via a manual signal and deactivated to ensure primary containment integrity. Based on the information at the time of the event, HV243F019 and HV243F020 were determined to be incapable of performing their design basis function of closing automatically when the condition was initially observed. The initial condition was reported under 10CFR50.72(b)(3)(v)(C), loss of safety function to mitigate the consequences of an accident and 10CFR50.72(b)(3)(ii)(A), nuclear power plant including its principal safety barriers being seriously degraded. Investigation of the initial condition was not immediately pursued since containment integrity was maintained with HV243F020 deactivated closed, the penetration was not required for sampling purposes and the Unit 2 Refueling Outage was scheduled to begin 3/10/01. "The subsequent investigation and Engineering evaluation of HV243F020 during the Unit 2 Refueling Outage showed that the design basis function of closing automatically to ensure primary containment integrity was not impacted during the initial observation on 2/8/01. Therefore, HV243F020 had been capable of isolating the subject primary containment penetration and an ENS notification per 10CFR50.72(b)(3)(v)(C) and 10CFR50.72(b)(3)(ii)(A) was not required." The licensee informed the NRC resident inspector. Notified R1DO(Evans). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0
37726 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-02-07 18:29 | 2001-02-07 23:15 | 2001-02-07 | UNIT 2 MANUAL REACTOR TRIP FOLLOWING THE LOSS OF THE "A" REACTOR COOLANT PUMP DURING ELECTRICAL BUS REALIGNMENT "SOUTH TEXAS PROJECT ELECTRIC GENERATING STATION, UNIT 2, MAKES THE FOLLOWING REPORT PER 10 CFR 50.72(b)(2)(iv)(B). "AT 1829 ON 2/7/01, OPERATORS MANUALLY TRIPPED THE REACTOR FOLLOWING LOSS OF POWER TO A REACTOR COOLANT PUMP DURING ELECTRICAL BUS REALIGNMENT. PLANT DESIGN REQUIRES FOUR REACTOR COOLANT PUMPS RUNNING WHEN THE REACTOR IS CRITICAL. THERE IS NO AUTOMATIC REACTOR TRIP FOR A LOSS OF A SINGLE REACTOR COOLANT PUMP BELOW 40% REACTOR POWER. "WE ALSO MAKE THE FOLLOWING REPORT PER 10 CFR 50.72(b)(3)(iv)(A). "DURING ELECTRICAL BUS REALIGNMENT, POWER WAS LOST TO TRAIN 'A' 4.16KV ENGINEERED SAFETY FEATURE BUS. DIESEL GENERATOR 21 AUTOMATICALLY STARTED AND BEGAN SUPPLYING POWER TO THE BUS. THE LOSS OF OFFSITE POWER SIGNAL RESULTED IN THE ACTUATION OF THE FOLLOWING TRAIN 'A' EQUIPMENT: ESSENTIAL COOLING WATER, COMPONENT COOLING WATER, AUXILIARY FEEDWATER, ESSENTIAL CHILLED WATER, CONTROL ROOM HVAC AND FUEL HANDLING BUILDING HVAC. "ESSENTIAL CHILLER 22A STARTED ON THE LOSS OF POWER SIGNAL BUT WAS SUBSEQUENTLY DECLARED INOPERABLE DUE TO HIGH OIL TEMPERATURE." OPERATORS WERE ATTEMPTING TO TRANSFER POWER ON 13.8KV BUS "2F" WHEN THE SUPPLY BREAKER OPENED DUE TO OPERATOR ERROR. ALL CONTROL RODS INSERTED FOLLOWING THE TRIP. OFFSITE POWER HAS BEEN RESTORED TO THE "2F" BUS AND THE DIESEL GENERATOR RETURNED TO STANDBY. AN EVENT RESPONSE TEAM IS EVALUATING THE TRIP. THE LICENSEE ANTICIPATES RESTORING THE "A" RCP IN APPROXIMATELY TWO HOURS. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0
37725 | 0 | COGEMA MINING, INC. |  |  |  |  | 2001-02-05 | 2001-02-07 14:00 | 2001-02-07 | CONDITION OF LICENSE REPORT INVOLVING MINE IN EXCURSION STATUS "Notification of a Reportable Event per License Section 11.2 "Reported Event: A routine quarterly (every 3 months) water sample collected on February 5, 2001 from monitor well M2, exceeded 2 of its 3 upper control limits (UCLs). A confirmation sample was collected February 6, which also exceeded 2 UCLs. Monitor well M2 was then placed on excursion status as per license Section 11.2 and its sampling frequency increased to weekly. M2 is a perimeter ore zone monitor well located approximately 300 feet east of the restored Production Unit 2 boundary, at the Irigaray Mine, Johnson County Wyoming. The nearest community is Linch, Wyoming, approximately 23 miles to the southeast. Analysis Data: Conductivity Uranium Date Chloride mg/l umhos/cm2 Alkalinity mg/l mg/I U3O8 Sampled UCL 18.0 UCL 685 UCL 131.1 no UCL 2-05-01 19.5 806 95.3 <0.4 2-06-01 20.5 799 97.3 <0.4 Health and Environmental Hazards: None investigative Action: Conduct further sampling to try to determine the extent and direction of the excursion. Written Notification: A written notification will be submitted to NRC Uranium Recovery Branch Chief within 7 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | MINING EVENT | [9 empty] | NON EMERGENCY | 4 | WY | OTH | GEN |  |  |  |  | 0
37724 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2001-02-07 10:00 | 2001-02-07 11:14 | 2001-02-07 | POSSIBLE OVEREXPOSURE B-D, Incorporated located in Sumter, South Carolina reported the following event to the State of South Carolina. B-D, Incorporated has a 2.3 million curie irradiator onsite. On 02/02/01, B-D, Incorporated received from Landauer the radiation exposure data on their film badges for the months of November through December, 2000. The Radiation Safety Officer for B-D Incorporated did not review the film badge results until 02/05/01. Upon reviewing the data, the RSO discovered that one of the film badges had been exposed beyond its limit (> 1000 Rad). The person whom the film badge had belonged to was administered a blood test today, 02/07/01. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 2 | SC | OTH | GEN | 20.2202(a)(1) |  |  |  | 0
37723 | 0 | U.S. ARMY |  |  |  |  | 2001-02-03 12:00 | 2001-02-07 10:47 | 2001-02-07 | TWO CHEMICAL AGENT DETECTORS AND ONE CHEMICAL MONITOR STOLEN. Two M22GID3 Chemical Agent Detectors, and one Chemical Agent Monitor where shipped in a connex container (closed secured container) by railway from Ft Campbell, KY to Ft Polk, LA. Upon arrival to Ft Polk it was discovered that the connex container had been broken into and the two M22GID3 Chemical Agent Detectors and one Chemical Agent Monitor were missing. Ft Polk military police are investigating this event. Each Chemical Agent Detector contains 30mCi of Ni-63 and the Chemical Agent Monitor contains 15mCi of Ni-63. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0
37722 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2001-02-06 21:52 | 2001-02-06 23:44 | 2001-02-06 | TURBINE GENERATOR LOCKOUT - REACTOR TRIP A turbine generator lockout caused a unit 2 reactor trip. All rods fully inserted. A loss of main condenser vacuum caused operators to shut the Main Steam Isolation Valves. Decay heat is being removed by use of the steam generator atmospheric dumps. The steam generators were initially fed by the auxiliary feedpumps, but are now being fed using the normal feedwater system. The plant is stable in mode 3. The cause of the turbine generator lockout is not known. The loss of condenser vacuum was caused by the cross over steam dumps opening. These valves opened because of a turbine overspeed condition, believed to have occurred as the turbine was unloaded because of the generator trip. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37721 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2001-02-06 | 2001-02-06 22:45 | 2001-02-06 | AGREEMENT STATE REPORT INVOLVING A STOLEN PORTABLE GAUGE "This is notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection. "STATUS: new Licensee: GeoEngineers City and state: Redmond, WA License number: WN-I0204-1 Type of license: Portable Gauge Date of event: February 6, 2001 Location of Event: North Bend, WA ABSTRACT: An authorized user had taken his work equipment home with him in preparation for an early start to a temporary job site. At approximately 5:45 AM the authorized user loaded his work truck with his equipment, including a CPN model MC-3DR portable gauge, serial number MD0069648, which contains 10 millicuries of cesium 137 and 50 millicuries of americium 241/beryllium. The gauge, in its orange transport box, was loaded into the back of an open-bed full-size Chevy pickup and secured to the bed of the truck with a cable and lock. The authorized user left his truck running and went back into the house to finish a cup of coffee; when he came out again his truck was gone. He reported the theft to the King County Sheriff and to his RSO. The Washington Department of Health was notified about 11:45 AM. The Department advised the licensee to offer a reward. As of this report (2 PM, February 6), the vehicle and gauge are still missing. What is the notification or reporting criteria involved? WAC 246-221-240 (Reports of stolen, lost or missing radiation sources.)" WA event report WA-01-004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37720 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2001-02-06 | 2001-02-06 16:16 | 2001-02-06 | AGREEMENT STATE REPORT INVOLVING A MISSING DENSITY GAGE The Illinois Department of Nuclear Safety reported that a general license density gauge source used by Best Food in their Summit/Argo facility was missing. The source, a 100 mCi Am-241, was installed in an Industrial Dynamics model CI-2C series density gauge. The device without the source, i.e., detector, was in storage in a vault and not in use at the time. The last known presence of the source was on 11/3/97. State inspectors observed that the source was missing on two separate occasions (12/7/00 and 1/5/01) during construction activities. Best Foods conducted extensive interviews with current employees and was not able to determine the whereabouts of the source. A consultant was hired by the company to assist in the investigation. After surveying about 200,000 sq. ft. the consultants speculated that source was either disposed of as scrap or returned to the manufacturer with no record keeping or possibly stolen. The manufacturer who is located in Torrance, CA was contacted and they too have no record of a source return. Best Foods intends to continue their investigation and the State of Illinois is available to assist, as requested. There are no plans at the present to involve law enforcement at this time. The manufacturer's specification indicates an exposure of 5 mR/hr at 15 inches from this unshielded alpha source. The State of Illinois notified the NRC R3ASO(Lynch). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0
37719 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2001-02-06 01:48 | 2001-02-06 10:43 | 2001-02-20 | PRIMARY CONTAINMENT DECLARED INOPERABLE Primary Containment was declared inoperable at 0148 CST on February 6, 2001, due to the failure of meeting the acceptance criteria for the suppression chamber to drywell vacuum breaker operation. While performing the 31 day surveillance, PC-AO-NRV30, suppression chamber to drywell vacuum breaker failed to indicate full close. The valve was subsequently stroked a second time and full closure indication was received. Estimated time of 2 minutes and 6 seconds when valve did not indicate full close. During this time frame when the valve was not indicating full close, Primary Containment was inoperable. Upon full closure of the valve, Primary Containment was returned to operable status. Engineering continues to evaluate the condition. TS action statement of LCO 3.6.1.8 B, requires the vacuum breaker to be closed in 12 hours. Required action not completed in the completion time requires the reactor to be in Mode 3 (Hot Shutdown) in twelve hours in Mode 4 (Cold Shutdown) in thirty-six hours. The NRC Senior and Resident Inspectors have been notified. * * * RETRACTED AT 1638 EST ON 2/20/01 BY ANDREW OHRABLO TO FANGIE JONES * * * "The suppression chamber to drywell vacuum breaker has two types of position indication available. They are a disc position switch, which only provides a red light indication for open, and a hinge position switch, which provides a red light indication for open and a green light indication for closed. Subsequent evaluation determined that the hinge position indication did show the vacuum breaker in the closed position upon the initial stroking and is adequate for making this determination, i.e., proper calibration. The disc position switch did not turn out the red indication light because of the slow closure of the disc due to what is believed to be a faulty non-essential air operator. "CNS investigation has found that the suppression chamber to drywell vacuum breaker was capable of performing its safety function in the open and close directions during this event. The suppression function of the Primary containment was not degraded as originally thought. Therefore, this event is not reportable under the requirements of 10CFR50.72 and event 37719 is retracted." The licensee notified the NRC Resident Inspector. The R4DO (Linda Smith) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37718 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2001-02-05 18:07 | 2001-02-05 20:55 | 2001-02-06 | MAJOR LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER CONDITIONS "On February 5, 2001 at 1807 it was determined that 24 of 44 Emergency Sirens in the southern Chester County area were inoperable due to the storm passing through the area. Power was lost to these sirens. This constitutes approximately 55% of the sirens in a localized area. "There are currently a total of 34 of 165 sirens inoperable in the EPZ due to the storm or approximately 21%. Power restoration to the area is in progress. Estimated time to restore all the sirens is not known at this time. "Current Siren Status Berks County 1 Inoperable Montgomery County 7 Inoperable Chester County 26 Inoperable There are 165 Sirens total in the EPZ." The licensee will inform the NRC resident inspector. * * * UPDATE 0133 2/6/2001 FROM SOSSON TAKEN BY STRANSKY * * * "As of 00:08 on 2/6/01, the following conditions exist for inoperable Emergency Sirens in the Limerick EPZ: Berks County None Inoperable Montgomery County 4 Inoperable Chester County 13 Inoperable There are currently 17 out of 165 sirens inoperable, or 10.3%. This represents an improvement from 34 inoperable." The NRC resident inspector will be informed. Notified R1DO (Bellamy). * * * UPDATE 0549 2/6/2001 FROM SOSSON TAKEN BY STRANSKY * * * "As of 05:12 on 2/6/01, the following conditions exist for inoperable Emergency Sirens in the Limerick EPZ: Berks County None Inoperable Montgomery County 4 Inoperable Chester County 3 Inoperable There are currently 7 out of 165 sirens inoperable, or 4.2%." The NRC resident inspector will be informed. Notified R1DO (Bellamy). | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0
37717 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-02-05 17:25 | 2001-02-05 19:16 | 2001-02-05 | SECURITY REPORT SAFEGUARDS SYSTEM DEGRADATION RELATED TO MONITORING AREA BOUNDARY. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE LICENSEE INFORMED STATE/LOCAL AGENCIES AND WILL INFORM THE NRC RESIDENT INSPECTOR. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 0
37716 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-02-05 03:15 | 2001-02-05 05:02 | 2001-02-07 | 10 CFR 73.71(b) SECURITY REPORT Safeguards system degradation related to detection/monitoring. Immediate compensatory measures taken upon discovery. Contact the NRC Operations Center for additional details. The NRC resident inspector will be informed of this event by the licensee. * * RETRACTION ON 02/07/01 AT 1132 ET BY GREG JANAK TAKEN BY MACKINNON* * * This event is being retracted because the individuals who entered the Protected Area were fully authorized and had completed the search process. The procedure was, however, violated. This event is being made a loggable event only, Not Reportable. R4DO (Sanborn) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 9 | 0 | 100 | 9 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 0
37715 | -1 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-02-04 12:45 | 2001-02-04 14:52 | 2001-02-09 | DISCOVERY OF VALVE CLOSED THAT COULD AFFECT ACCIDENT MITIGATION "While performing troubleshooting operation on the Unit 1 Crossover Steam Dump System an Instrument Air Valve was discovered to be closed, when it should have been open. This closed valve (IA-1553) isolates Instrument Air to the Crossover Steam Dump Valves rendering the system inoperable. This system is required to be operable by the FSAR Appendix T and Power must be <437 MWe if the system is inop. At the time of discovery power was <437 MWe, however initial investigation leads to the conclusion that this valve has probably been closed since October, 2000. Since Crossover Steam Dumps provide protection for a Turbine Overspeed Accident and is part of the PBNP Design Basis it was conservatively decided to make this 8-hour report. Unit 1 will remain < 437 MWe until the system is fully restored and tested. An investigation is continuing." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 2/9/01 @ 1630 BY ADAMS TO GOULD * * * RETRACTION This event reported that the cross over steam dump system was discovered to be inoperable because of a mis-positioned instrument air valve. This was reported as a condition that could have prevented fulfillment of a safety function for a SSC [structure, system, and component] needed to mitigate the consequences of an accident. Upon closer evaluation of the condition and examination of the applicable licensing bases, they have determined that this condition is not reportable for the following reasons: 1. The cross over steam dump system is not a TS controlled system. The turbine overspeed protection system TS LCOs and surveillances were removed from the TS by License Amendments 176 and 180 on August 6,1997. 2. NUREG 1022, Rev 2, Page 54, clarifies that the systems included in the scope of criteria for 50.73(a)(2)(v) are those systems, required by the TS to be operable to perform one of the four functions specified in the rule. As noted in item 1, the cross over steam dump system is not in the TS. 3. A review of the accident analysis in FSAR Section 14.1.12 established that there is no mention of the cross over steam dump system for mitigation of this accident. Therefore, the Licensee is retracting this event. The NRC Resident Inspector was notified. The Reg 3 RDO(Clayton was notified) | 80 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37714 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2001-02-04 01:18 | 2001-02-04 04:25 | 2001-02-04 | AUTOMATIC TURBINE TRIP/REACTOR SCRAM DURING TESTING During performance or routine turbine valve testing, an automatic turbine trip and subsequent reactor scram occurred due to low turbine emergency trip system pressure. The unit is currently stable in Condition 3 (Hot Shutdown) with reactor vessel water level being maintained by the motor driven feedwater pump and reactor pressure being controlled via the steam bypass valves to the main condenser. All systems functioned as expected. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37713 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2001-02-03 15:27 | 2001-02-03 18:47 | 2001-02-04 | UNUSUAL EVENT DECLARED DUE TO FIRE LASTING MORE THAN 15 MINUTES The plant was in the process of raising power after exiting shutdown operations and were at 39% power when a non-class 1E breaker failed at 1514 PST causing a loss of power to a non-safety electrical bus. This in turn caused the loss of some secondary plant equipment which led to the loss of condenser vacuum, condensate pumps, feedwater pumps, and other equipment leading to a trip of the plant. The breaker failure resulted in a fire which lasted until 1544 PST and the Unusual Event was declared at 1527 PST. The plant also lost all the control room annunciators for a period of time, they have been recovered. The plant is stable in Hot Standby with the reactor coolant pumps running, auxiliary feedwater supplying the steam generators, and excess heat being released through the steam generator atmospheric dumps. The main steam isolation valves are closed as a result of the secondary equipment that was lost. The emergency diesel generators were running unloaded on automatic start signal from the loss of the non-class 1E bus. Electrical power continues to be provided to all safety busses and the unaffected parts of the non-safety busses from offsite power. The licensee notified the NRC Resident Inspector and state and local authorities. * * * UPDATE AT 1956 EST ON 02/03/01 BY BOB CONOSCENTI TO FANGIE JONES * * * The licensee has determined that one breaker failed catastrophically causing the loss of one 4160 VAC bus and pieces of the breaker assembly caused grounds in another 480 VAC bus causing its loss. The plant is stable in Hot Standby. The licensee notified the NRC Resident Inspector. The Unusual Event was terminated at 1544 PST. The R4DO (Blair Spitzberg), NRR EO (Richard Wessman), IRO Manager (Charles Miller), and FEMA (Gene Nupp) have been notified. * * * COMMISSIONER'S ASSISTANTS' BRIEFING 1000 2/4/2001 * * * Briefer: Charles Marshall. Participants: Mamish (IRO), Richards, Wessman (NRR), Dricks (OPA), Combs (STP), Hauber (OIP), Madden (OCA), Morris (EDO), Levin (Chrm Meserve), Cain (Comm Dicus), Sharkey (Comm McGaffigan), Davis (Comm Diaz), McCabe (Comm Merrifield), Brockman, Henerson, Kramer (R4). | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | -1 | N | N | A/R | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37712 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-02-03 03:40 | 2001-02-03 03:51 | 2001-02-03 | OFFSITE NOTIFICATION The licensee contacted offsite government agencies to inform them that the unit commenced a refueling outage. The NRC resident inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Startup; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37711 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-02-02 10:30 | 2001-02-03 01:50 | 2001-02-03 | TWO CRITICALITY ALARM HORNS FAILED TO SOUND DURING TESTING "At 1030 on 2-2-01 the PSS was informed that the two Criticality Accident Alarm System (CAAS) pneumatic horns for building C-337-A failed to sound properly during testing. The system is required to be operable according to TSR 2.4.4.3.b for the prescribed modes of operation. Even though the system was declared inoperable at the time of the failure it is possible that the system would not have performed its intended safety function had it been required prior to being declared inoperable. The two horns were replaced and satisfactorily tested. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0
37710 | 0 | U.S. ARMY |  |  |  |  | 2000-12-03 | 2001-02-02 11:13 | 2001-02-05 | MISSING M67 MORTAR SIGHT DEVICE The licensee reported that an M67 Mortar Sight Device was lost in December 2000 at Ft. Polk, LA during a training exercise for the 2nd Armored Cavalry. The device contains multiple tritium sources with an aggregate activity of 5.8 Curies. The licensee does not believe the device was inadvertently sent to the landfill, however, there are no specific plans to attempt recovery. The training area is restricted and inaccessible to the general public. * * * UPDATE 1059 2/5/2001 FROM HAVENNER TAKEN BY STRANSKY * * * The licensee called to clarify the initial report. Personnel at Ft. Polk are currently attempting to determine how the assigned unit lost track of the source and locate it. Notified R3DO (Clayton). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37709 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC. |  |  |  |  | 2001-02-01 | 2001-02-01 13:11 | 2001-02-01 | 10 CFR PART 21 REPORT FOR MODEL 353C AND 353C1 CONDUIT SEALS "This notification relates to Model 353C and 353C1 conduit seals which exhibit an electrical short condition. Any model 353C and 353C1 conduit seal which does not indicate a short condition is deemed acceptable and this notification is not applicable to such units. "This notification is not applicable to units which are currently operational, or have successfully completed a functional test by the customer that would verify the insulation resistance of the lead wires. "RNII [Rosemount Nuclear Instruments, Inc.] does not have sufficient information to determine the safety impact related to plant applications. Licensees must determine the impact on plant operations and plant safety and take action as deemed necessary." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0
37708 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2001-02-01 07:30 | 2001-02-01 11:12 | 2001-02-01 | DISCOVERY THAT THE MAIN STEAM ISOLATION VALVE (MSIV) MAX PATH LIMIT COULD HAVE BEEN EXCEEDED DUE TO INABILITY TO DEPRESSURIZE THE STEAM LINE The following text is a portion of a facsimile received from the licensee: "[The] Unit 2 [Reactor Core Isolation Cooling] System was removed from service to perform scheduled maintenance. Control Room operators closed the inboard containment isolation valve, HV249F007, to depressurize the steam line. The steam line did not depressurize as expected. Operators then closed the outboard containment isolation valve, HV249F008, and were successful in isolating the pathway and depressurizing the steam piping. At 07:30, the inboard isolation valves were declared inoperable. Due to the inability to depressurize the steam line and following a technical review of the system response and supporting data, it appears that the MSIV max path limit could have been exceeded, and therefore, this event is reportable under 10CFR50.72(b)(3)(ii), Degraded or Unanalyzed Condition." The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0
37707 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2001-01-31 21:47 | 2001-02-01 01:08 | 2001-02-01 | UNIT 1 EXPERIENCED AN AUTOMATIC REACTOR SCRAM FOLLOWING FAILURE OF A MAIN POWER TRANSFORMER "At 21:47 CST, U-1 automatically scrammed from a main turbine 'NON-EHC' trip caused from a failure of a main power transformer. The main power transformers received an auto deluge signal and an acrid smell is reported in the area. The main generator tripped from the loss of the main power transformer causing the main turbine to trip, which caused an automatic reactor scram. The fast closure of the main turbine valves caused a reactor pressure spike which tripped both reactor recirculation pumps and caused two safety relief valves to actuate. "All automatic actions initiated as designed, but the following anomalies were noted; - 1A circulating water pump tripped - Division 1 alternate rod insertion failed to reset on scram recovery - 1B recirculation pump received a low oil level alarm on restart attempt - U2 received an electrical perturbation from the U1 scram which resulted in a loss of the 2A heater drain pump and two heaters. Cram rods were inserted in accordance with Operating procedures. U2 was stabilized at 930 MWE." All rods fully inserted. The two safety relief valves reseated after actuation. Decay heat is currently being removed via the bypass valves to the main condenser. RCIC is inoperable but available, if needed. There are no challenges to offsite power and the system auxiliary transformer is fully available. The licensee is presently resetting the deluge system in order to assess if there is mechanical damage on the 1 west main power transformer and will determine whether a U-1 cooldown is required to evaluate the 1B recirculation pump problem. The NRC resident inspector was informed and is currently onsite. * * * UPDATE AT 2007 EST ON 2/1/01 BY SHANE MARIK TO FANGIE JONES * * * "This is a follow up notification to event #37707 to enhance and clarify plant response following the post scram investigation. It was determined that a bushing/insulator failure on the 'C' phase of the 1 West Main Power Transformer failed causing the lockout of the main generator. The failed bushing/insulator is not located directly on the 1 West Main Power transformer but is located on the first main tower between the transformer and the switchyard. "During the turbine trip and reactor scram the reactor vessel level instrumentation spiked causing a 'ringing phenomenon' initiated from the increase in pressure. This phenomenon was identified from the transient analyses data and seen during previous pressure transients. The ringing in the level instrumentation caused varying level indication (<1/2 second cycles) which is indication only, not a real change in reactor level. This ringing phenomenon caused to the actuations and 1/2 isolations identified during the scram. "The following is offered to clarify the anomalies identified during the event. 1. The main steam isolation valves received a 1/2 group one isolation due to the ringing phenomenon. 2. Reactor recirculation pumps tripped off due to the ringing phenomenon. 3. Four safety relief valves opened. Previously reported as two. All four safety relief valves re-closed properly. 4. Reactor building ventilation tripped due to the inboard isolation dampers closing on low voltage transient. 5. The main generator voltage regulator failed to auto transfer to manual. 6. A division one ground was received and was subsequently isolated to three alarm points associated with the main power transformers which received a deluge on the bushing fault." The licensee notified the NRC Resident Inspector. The R3DO (David Hills) has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37706 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-01-31 11:45 | 2001-01-31 18:48 | 2001-03-21 | POTENTIAL INABILITY TO CONTROL A RADIOACTIVE RELEASE At 1145 on 1/31/01, the door to the auxiliary engineered safeguards suction side vestibule in unit 2 was found stuck open. This bypasses the normal flowpath for both trains of ESF fans and renders them inoperable. The plant made an unrecognized entry into Technical Specification 3.0.3 until the door could be closed, which occurred in approximately one minute. This eight hour report is being made in accordance with 10 CFR 50.72 based on the temporary inability to control a possible radioactive release. The licensee notified the NRC resident inspector. * * * UPDATE AT 1543 ON 3/21/01, BY CHERBA RECEIVED BY WEAVER * * * The licensee has retracted this event based on the following analysis. "Subsequent evaluation concluded that if a postulated accident had occurred while the door was open, control room doses would be less than 10CFR Appendix A, GDC-19 limits and site boundary doses would remain within CNP's accident analysis assumptions. This conclusion is based on an actual measured total ECCS unfiltered leakrate of 0.02292 gpm, which is less than the CNPs established limit of 0.2 gpm via the unit vent stack. Since the total leakrate is less than 0.2 gpm, the AES system is not required to filter the building effluent to maintain control room habitability during a postulated accident. In addition, it was concluded that the ECCS pump and heat exchanger rooms would not have experienced temperatures greater than previously evaluated if a postulated accident had occurred while the door was open. This was due primarily because of the low supply air temperature (28 degrees Fahrenheit) and near freezing lake water temperature. "Based on the above, this event would not have impacted the radiation removal capability of the AES ventilation system. As such, this notification is being made to retract event 37706 made on January 31, 2001." The licensee informed the NRC resident inspector. The operations center notified the R3DO (Shear). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0
37705 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2001-01-31 14:00 | 2001-01-31 17:24 | 2001-01-31 | OFFSITE NOTIFICATION - SEWAGE SPILL At approximately 1400 CST on 01/31/01, an untreated sewage spill, overflowing from an underground manhole cover, of approximately 200 gallons occurred outside of the Generation Support Building. The sewage spilled into the storm drains which drain into East Creek. The spill has been isolated and contained. The spill occurred outside the Protected Area but remained inside the Owner Controlled Area during the event with no spillage reaching the Mississippi River. The Louisiana Department of Environmental Quality was notified by River Bend personnel at 1451. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37704 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2001-01-09 09:30 | 2001-01-31 15:08 | 2001-01-31 | POTENTIAL FOR THE CONTROL ROOM OPERATORS TO EXCEED GENERAL DESIGN CRITERIA 19 LIMITS DURING AN ACCIDENT Following evaluation and analysis, FPL identified a condition that could have potentially led to the control room operators receiving a dose in excess of GDC 19 limits during accident conditions. St. Lucie recently identified weaknesses in the Unit 2 procedures that could result in the operators not taking action to manually align the control room outside air intakes to pressurize the control room when the control room ventilation system is operating in the emergency recirculation mode. The procedures direct which outside air intake should be used depending on existing radiological conditions. However, the procedures do not direct the operators to establish outside makeup air (i.e.. throttle open the outside air intake valves) if minimum control room pressurization is met. In addition to the procedural weaknesses identified, the control room differential pressure indicators exhibit a small positive pressure bias that could have misled the operators into believing that the control room was maintained at a positive differential pressure without the need to open the outside air intake valves. During the course of the hypothesized accident, operation of the control room ventilation system in this condition would have been ultimately discovered and corrected by the technical advisors in the Technical Support Center or Emergency Operations Facility. St. Lucie issued Night Orders to the operating crews to clarify operational requirements for the control room ventilation systems until the requisite procedure changes are implemented. The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37703 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-11-27 12:00 | 2001-01-31 13:09 | 2001-02-01 | PART 21 REPORT ON CAP SCREW FAILURE USED IN AN AUXILIARY FEEDWATER PUMP AT THE BEAVER VALLEY POWER STATION UNIT ONE One of the four cap screws on the collar of the hydraulic balancing drum of the steam-driven Auxiliary Feedwater pump (AFP) 1FW-P-2 failed. The head of the screw broke off and became lodged in the area between the stuffing box extension and the balancing drum collar, preventing 1FW-P-2 from starting on 11/27/00. The root cause of the cap screw failure was material defect. Final metallurgical analysis revealed that the failure was due to intergranular failure. The defects noted in the fastener surface were attributed to the original manufacture of the cap screw. The probable cause of the failure was the propagation of manufacturing cracks under static preload, which caused tensile stress of approximately 88% of the yield stress of the cap screw. Hydrogen absorption and diffusion into regions of high stress caused propagation of the cracks. The failure was a time delayed process. The material defect led to the failure of one AFP cap screw which prevented the AFP from starting. Failure of one or more Auxiliary Feedwater Pumps to start when required, would result in a major degradation of essential safety related equipment, and the required Auxiliary Feedwater System may not have been able to perform its safety related function, which would constitute a substantial safety hazard. Though not attributed as part of root cause for the one cap screw failure, two related noteworthy non-compliant issues were identified with the four cap screws found on the 1FW-P-2 AFP collar. An emission spectrograph test run on a cap screw showed a chromium content of 0.148% (indicating the screw was carbon steel). The vendor Material Release for 1FW-P-2 (MR 912004) shows that the cap screws are 410 stainless steel that should have contained 12% chromium. FENOC is not able to conclude whether operating with carbon steel cap screws (in place of the required stainless steel) could have caused the AFP to fail. The cap screws also had hardness values of 41-44 HRC (Hardness Rockwell C). The purchase specification requires 410 stainless steel with a hardness less than 22 HRC. Although carbon steel bolts are less susceptible to stress corrosion cracking than stainless steel bolts, FENOC is not able to conclude whether operating with carbon steel cap screws with a hardness of 41-44 HRC (in excess of the required hardness limit of 22 HRC) could have caused the AFP to fail. THE LICENSEE ALSO SUBMITTED THE FOLLOWING INFORMATION RELATED TO THE REPLACEMENT SCREWS THAT WERE ORDERED FROM FLOWSERVE CORPORATION AND MANUFACTURED BY U.S. BOLT: The specified maximum hardness value was exceeded for 16 of 20 cap screws supplied for use on a balancing drum located on the Auxiliary Feedwater Pump (AFP) shaft. Exceeding the hardness limit makes these cap screws susceptible to stress corrosion cracking. Therefore, the defect, if gone undetected and installed, could have caused these cap screws to fail during their operating life. A failed cap screw could jam and prevent a standby AFP from starting. Failure of one or more AFPs to start when required, would result in a major degradation of essential safety related equipment, and the required Auxiliary Feedwater System may not have been able to perform its safety related function, which would constitute a significant safety hazard. As such, the defect is reportable pursuant to 10 CFR Part 21 requirements. HOO NOTE: This report was modified to identify the licensee rather than the reporting organization (FirstEnergy Nuclear Operating Company) which is the owner/operator of Beaver Valley. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 21.21 |  |  |  | 0
37702 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-01-30 17:25 | 2001-01-30 19:40 | 2001-01-30 | LOW CONTROL ROOM PRESSURE WHEN CONTROL ROOM VENTILATION IN OPERATION During testing of CRHEAFS (Control Room High Efficiency Air Filtration System) the licensee was not able to maintain the control room at a positive pressure as required. CRHEAFS was inoperable at the time the problem was noted due to planned maintenance (but still available). The area outside the control room is at a higher pressure causing air inflow into the control room while CRHEAFS is operating. When the ventilation in the area outside the control is secured, the proper positive pressure is maintained in the control room. Procedures are being revised to require securing of the outside ventilation system if CRHEAFS operation is required. The licensee is continuing to investigate this problem and has notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37701 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-01-30 00:15 | 2001-01-30 01:34 | 2001-01-30 | SAFETY RELIEF VALVES WERE DECLARED INOPERABLE A Technical Specification shutdown was initiated as required by T.S. 3.6.E.2 following the discovery that not all of Section XI requirements were met with respect to the safety relief valves. The safety relief valves were declared inoperable @ 1830 on 1/29/01. The reactor conditions shall be as follows within 24 hrs: reactor pressure <110 psig and reactor temperature <345°F. The NRC Resident Inspector was notified. * * * UPDATE ON 1/30/01 @ 1049 BY CORRIGAN TO GOULD * * * "At 0126 CST, January 30, 2001, NRC approved the Licensee's verbal request for a notice of enforcement discretion (NOED) concerning Technical Specification 3.15.A. 1. Specifically, this allows us to use the corrective action process, including consideration of Generic Letter 91-18, to resolve non-conformances with Section Xl of the ASME code. In the case of SRVs, a favorable operability determination will allow us to consider SRVs operable in spite of existing non-conformances with Section Xl of the ASME code. Further, the NOED allows us to assess operability of any additional identified non-conformances with Section Xl through our condition report process rather than to immediately declare the affected component inoperable as required by Technical Specification 3.15.A.1. Continuance of this NOED is contingent on NRC receipt, by close of business on February 1, 2001, of our written NOED request and a license amendment request to move inservice inspection requirements to a licensee controlled program. The NOED remains in effect until the license amendment request is dispositioned (expected about March 5, 2001)." The NRC Resident Inspector was notified. The Reg 3 RDO(Hills) was notified. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37700 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2001-01-29 18:10 | 2001-01-29 19:38 | 2001-01-29 | FISH KILL Clinton Power Station personnel have been investigating the cause of a fish kill on Clinton Lake that was first discovered on January 24, 2001. After reviewing environmental data, CPS has sufficient evidence to conclude that the plant trip on December 18, 2000, following a Group 1 isolation was the cause of the fish kill. During this event, the main steam isolation valves closed and all decay heat was removed through the suppression pool instead of the main condenser and discharge flume to the lake. With the sudden loss of heat, input into the discharge flume and the lake in the vicinity of the flume discharge, a rapid drop in lake temperature shocked the fish in this area causing a kill of an estimated 7000 fish. The majority of these fish were carp and buffalo head. CPS has provided pertinent plant data to the Illinois Department of Natural Resources and the Illinois Environmental Protection Agency. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0
37699 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2001-01-29 16:20 | 2001-01-29 16:31 | 2001-01-29 | OFFSITE NOTIFICATION The licensee reported a spill of mercury greater than one pound mass to the State of Connecticut Department of Environmental Protection. The spill was just over one pound mass and occurred in the primary auxiliary building. The spill has been contained and a contractor has been contacted to clean up the spill. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37698 | 0 | WATERFORD | 3 |  |  | [3] CE | 2001-01-28 22:45 | 2001-01-29 05:36 | 2001-03-21 | PRESSURIZER STEAM SPACE SAMPLE ISOLATION VALVES FAILED TO CLOSE At 2245 on 1/28/01 it was discovered that PSL-303 and PSL-304, Pressurizer Steam Space Sample Inside and Outside Containment Isolation Valves would not close when their respective control switches at OP-8 in the Control Room were taken to the "Close" position. The valves had been open since 1455 that same day to perform degas of the Pressurizer. The Nuclear Plant Operator first took the switch for PSL-304 to the "Close" position and observed that the valve continued to indicate "Open". He then took the Switch for PSL-303 to the "Close" position, and observed that valve continue to indicate "Open". Technical Specification 3.6.3 was entered and a Nuclear Auxiliary Operator was dispatched to verify the position of PSL-304 locally. PSL-304 was found to be in the open position and the on-shift chemistry technician confirmed that there were still indications of flow through the sample line. Another attempt to close PSL-304 was made using the switch on CP-8 in the control room. The Nuclear Auxiliary Operator observed that the valve moved approximately one quarter-inch in the closed direction. At 2257 PSL-304 was closed using the manual gagging device. At 2310 PSL-304 was de-energized to comply with the action requirements of Technical Specification 3.6.3.b. At 0007 on 1/29/01, another attempt was made to close PSL-303 using the control switch at OP-8. This attempt was successful. The affected containment penetration is a one-half-inch line and is currently isolated. They are investigating the cause. The NRC Resident Inspector was notified. * * * UPDATE AT 1717 ON 3/21/01, BY PIPKINS RECEIVED BY WEAVER * * * "This is an update to Event Number 37698, which was reported on 1/29/2001 at 05:36 [EST]. After further evaluation by Entergy, the valve vendor (Flowserve Engineering) was notified (March 16, 2001) concerning an apparent defect in design related to inadequate internal valve clearances that resulted in galling and subsequent binding of the subject valves (PSL-303 and PSL-304). The vendor was asked to review the condition as a potential 10 CFR Part 21 [report]. The vendor contacted Entergy today (3/21/01) and indicated that, after review, they agree that the valve failure is a Part 21 issue and agreed to issue the Part 21. The subject valves are 1/2 inch, 2500 Ib, WKM model 70-18-9 DRTS cage-guided globe valves. In addition to the original reporting criteria given in the call on 1/29/2001, the condition is also reportable under 10 CFR50.72.(b)(3)(ii)(A) as a condition involving principal safety barriers being seriously degraded. Entergy has reviewed all of the safety-related applications of the subject valves at Waterford 3 for other potential cases of common mode failure." The licensee notified the NRC resident inspector. The operations center notified the R4DO (Pellet). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(ii)(A) |  |  | 0
37697 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-01-28 22:28 | 2001-01-28 23:38 | 2001-01-29 | STEAM GENERATOR BLOWDOWN ISOLATED FOLLOWING ALARM RECEIVED ON RAD MONITOR R-49 An alarm was received for rad monitor R-49, Steam Generator radiation monitor, due to a spike. This resulted in automatic closure of the Steam Generator Blowdown isolation valves which is an ESF actuation. All other primary to secondary leakage parameters were normal. At the time of the spike, the Nuclear NPO was adjusting 24 S/G sample flow to obtain the required flow (as found: 35gph, required: 38-40gph). AOI 1.2(Steam Generator Tube Leak Procedure) was entered and supplemental monitoring was initiated. There are no indications of primary to secondary steam generator tube leakage. The NRC Resident Inspector was notified. * * * UPDATED AT 1350 ON 1/29/01 BY GOETHCHIUS, RECEIVED BY WEAVER * * * Upon further review, the closure of these isolation valves is not reportable per 10 CFR 50.72. These containment isolation valves are limited to a single system and therefore, no reporting is required. Investigation of the issue will be in accordance with our corrective action process. This event is retracted The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0
37696 | 0 | CITIZENS GENERAL HOSPITAL |  |  |  |  | 2001-01-25 16:00 | 2001-01-26 17:58 | 2001-01-30 | DISCOVERY OF THE POSSIBLE LOSS OF TWO GADOLINIUM-153 SOURCES AT CITIZENS GENERAL HOSPITAL IN NEW KENSINGTON, PENNSYLVANIA Due to an ongoing merger with Allegheny Valley Hospital, Citizens General Hospital ceased nuclear medical activities and properly transferred all sources (except for two gadolinium-153 sources) to Allegheny Valley Hospital (located within approximately 2 miles). The gadolinium sources were not included because Allegheny Valley Hospital was not licensed for gadolinium-153. (A license amendment has been requested.) Accordingly, the gadolinium-153 sources were being kept in Hot Lab at Citizens General Hospital in the meantime. Approximately 3 weeks ago, a closeout survey was preformed of the Nuclear Medicine Department at Citizens General Hospital (where the gamma camera was located and recorded were done). The results indicated that there were no activities. There was also documentation in place to prohibit use of the Hot Lab because it had not yet been closed out. It was reported that an unknown individual made arrangements to de-install and sell the gamma camera and other equipment. Two individuals (middlemen for other companies) arrived yesterday (01/25/01) with a crew. The individuals were told that they could take the gamma camera and other items but not to touch the gadolinium sources, which were located in the Hot Lab. This morning (01/26/01), it was discovered that the gadolinium sources were missing. Apparently, the de-installation crew left a mess and took more than they were authorized to take including a refrigerator, survey meters, signs off the walls, etc. The Director of Materials Management did not have a list. It is currently believed that the sources were removed at approximately 1600 EST on 01/25/01 by an individual who worked for BC Technical, and it was reported that the sources may currently be in Salt Lake City, Utah. The other individual worked as an independent for Jet Services and was believed to be involved with removal of the gamma camera. The licensee was able to contact this individual, who in turn informed the licensee that the other individual's company (BC Technical in Salt Lake City) had a license to transfer radioactive materials. Therefore, there was an impression that they were doing the hospital a favor by getting rid of sources for the hospital. The licensee also contacted the company based in Salt Lake City, Utah. The individual who actually removed the sources was not available because he was performing a de-installation at another hospital. The missing gadolinium sources had an activity of 200 millicuries each approximately 2 years ago. The current activity level was conservatively estimated to be approximately 50 millicuries each. The licensee has notified the NRC Region 1 office (Michelle Beardsley). (Call the NRC operations officer for licensee contact information and contact information regarding the individuals involved in the de-installation and removal of equipment.) * * * UPDATE AT 1330 ON 1/30/01 BY BUKOVITZ, RECEIVED BY WEAVER * * * The sources were returned to the hospital on 1/27/01. The sources had been shielded the entire time and the radiation field on the exterior of the shielding was less than 1 mr/hr. The licensee has notified the NRC Region 1 office (Michelle Beardsley). The Operations Center notified the R1DO (Holody). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37695 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2001-01-03 | 2001-01-26 16:00 | 2001-01-26 | AGREEMENT STATE REPORT REGARDING THE LOSS OF A 9-MICROCURIE Cs-137 STABILIZATION SOURCE DURING A BLOW-OUT AND FIRE AT A WELLHEAD The following text is a portion of a facsimile that was sent from the State of New Mexico: "AGREEMENT STATE EVENT REPORT ID NO. NM-01-01" " ... " "NEW MEXICO" " ... " "LICENSEE - Schlumberger" "NUMBER - WL197" "LOCATION - Artesia, NM" "OTHER PARTIES - Yates Petroleum Corp." "DISCOVERY DATE / REPORT DATE - 12/29/[00] / 01/03/01" "EVENT TYPE - Loss of RAM" "EVENT DESCRIPTION -" "While logging a well[,] the tool was expelled from the hole by a blow-out and fire at the wellhead. The down hole instruments were violently ejected from the hole striking the rig and breaking into pieces. ... After the resulting fire was under control, the intact sources were located in the equipment debris and shipped to the company's source storage facility in Houston. This was accomplished using survey meters, source handling tools[,] and shielding. Dose calculations for all employees involved in the retrieval indicate a 16-microrem dose to all but one, who was estimated to have received 0.4 millirem." "The tool being used contained 5 sources: one Cs-137 source of 1.7 [curies], one Am-241[/]Be source of 16 [curies], two (2) Cs-137 stabilization sources of 9 microcuries[,] and one (1) Cs-137 stabilization source of 0.6 microcuries." "The analysis of the equipment in Houston confirmed the integrity of the sources and the fact that one of three stabilization sources was missing. The instrument that impacted the top of the rig is where this source was contained. The remaining rig and surrounding area [were] surveyed[,] but the source could not be found. After extensive surveys[,] the search was terminated. The lost source was one of the [9-microcurie] sources and is an exempt quantity." "CORRECTIVE ACTIONS - Blow-outs will occur during normal drilling operations. The response of Schlumberger was appropriate and complete." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0
37694 | -1 | WAUSAU HOSPITAL |  |  |  |  | 2001-01-24 07:30 | 2001-01-26 11:36 | 2001-02-16 | MEDICAL MISADMINISTRATION A Cs-137 vaginal cylinder implant was loaded at 9:30 am on 1/23/01. The written directive called for a total implant time of 49 hours. During a check of the patient at 7:30 am on 1/24/01, the authorized user found the loaded vaginal cylinder on the patient's toilet seat. The patient's nurse stated that the source came out at about 6:30 am on 1/24/01 (i.e., after about 42% of the prescribed dose was delivered). The licensee was not sure how the source got to where it was found. The authorized user placed the cylinder in a lead pig and transported it to the secured storage area. The authorized user decided to write another written directive and reload the patient at 10:00 am on 1/24/01 with a prescribed implant time of 7 hours. After the 7 hours, the sources were explanted as intended. The authorized user decided to deliver the remaining radiation dose to the treatment site via teletherapy. At 6:00 am on 1/24/01, the nurse emptied the patient's foley bag and noted that the patient was in bed. Between 6:00 and 6:30 am on 1/24/01, the nurse noticed that the patient was leaving the bathroom to go back to bed. The nurse also noticed that the patient's "T-binder" (used to hold the applicator in place), was loose, so she tightened it. The authorized user visited the patient at 7:30 am and noticed that the T-binder was on the bathroom floor and the loaded vaginal cylinder was on the toilet seat. Based on nurse interviews, all nurses caring for the patient were badged, and none of them handled the applicator. ***** UPDATE/RETRACTION AT 1043 EST ON 02/16/01 FROM JEFF LIMMER TO LEIGH TROCINE ***** An investigation was performed, and the NRC Region 3 office (Tony Go and Geoffrey Wright) notified the license that there was patient intervention. Therefore, the licensee is retracting this event. The NRC operations officer notified the R3DO (Monte Phillips) and NMSS EO (Brian Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 35.33 |  |  |  | 0
37693 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-01-26 10:00 | 2001-01-26 11:29 | 2001-01-30 | POSSIBLE REACTOR COOLANT SYSTEM (RCS) LEAKAGE Possible RCS boundary leakage from around a part length CRDM housing. Dry boric acid crystal buildup, less than one cup, was found around a part length CRDM housing. Licensee will have to remove missile shield, etc. to determine which part length CRDM housing has the leak or possibly leaked in the past. Currently the licensee is cooling down the plant and should be in a cold shutdown condition in 6 or 7 hours from 1130 ET. The NRC Resident was notified of this by the licensee. * * * UPDATE ON 1/30/01 @ 1123 BY HICKEY TO GOULD * * * Wet boric acid was identified on the mechanical seal area at the top of CRDM H-14. and a small ring of dry boric acid was found at the CRDM B-8 vent plug cap. Neither leak point constituted RCS pressure boundary leakage, as defined in Technical Specifications. H-14 and B-8 are both abandoned part-length CRDM housings. Boric acid had run down the outside of the H-14 housing, but there was no visual indication of leakage in the welded areas. The welds on H-14 were examined by NDE; no indications were found. Unit 4 was refueled in October, 2000. Neither of these leaks was identified during the restart inspection at the end of the refueling outage. The top closure assembly on both housings was replaced with a threaded and welded plug design. Preparations are underway to return Unit 4 to service. The NRC Resident Inspector was notified. The Reg 2 RDO(Wert) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0
37692 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-01-26 08:15 | 2001-01-26 09:57 | 2001-01-26 | LOSS OF SPENT FUEL NUCLEAR ISLAND COOLING. Both 12kV feeder lines to the Spent Fuel Nuclear Island deenergized causing a loss of cooling to the Spent Fuel Island. Initial Spent Fuel Nuclear Island temperature was 91 degrees F. In one hour and forty five minutes after a loss of power the water temperature of the Spent Fuel Island increased from 91 degrees F to 92 degrees F. Worst case time to boil is 84 hours. Licensee entered EAL MU3 (Unusual Event for a loss of Spent Fuel Island Cooling) at 0815CT. 12kV power was initially lost at 0715CT. Radiation Monitor in the Spent Fuel Island Area is functioning properly and radiation levels in the area are normal. The licensee expects to have Spent Fuel Island Cooling back in service in less than one hour. Licensee notified State and Local officials. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE BY M. RODE AT 1039 ET TAKEN BY MACKINNON * * * Unusual Event was terminated at 0939 CT after power was restored and the highest Spent Fuel Island water temperature reached was 92 degrees F. R3DO (J Creed), IRO (Congel), NRR EO (Ed Goodwin), and FEMA (Steindurf) notified. The NRC Resident Inspector will be notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37691 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2001-01-25 19:51 | 2001-01-25 21:03 | 2001-01-30 | MANUAL REACTOR TRIP DUE TO TWO DROPPED RODS IN DIFFERENT BANKS The following text is a portion of a facsimile received from the licensee: "While conducting a plant shutdown due to a dropped rod in shutdown bank 'B' (H-6), another rod in control bank 'D' (H-10) dropped. In accordance with [procedure] 4-ONOP-028.3, 'Dropped RCC,' with two dropped rods in different banks the reactor was manually tripped and [procedure] 4-EOP-E-0 was entered. All equipment operated as expected, and [the] plant is stable in Mode 3. [An] investigation is in progress to determine [the] reason for [the] dropped rods." The licensee stated that all rods fully inserted. Auxiliary feedwater automatically started as expected and has since been secured. Normal feedwater is currently being utilized to supply water to the steam generators, and the main condenser is available as the heat sink for secondary steam. Normal charging, makeup, and letdown are being utilized for primary system inventory control. Pressurizer heaters and sprays are being utilized for primary system pressure control, and the reactor coolant pumps are being utilized for primary system transport control. Offsite power is available. There were no emergency core cooling system actuations, and none were required. The licensee plans to notify the NRC resident inspector. * * * UPDATE ON 1/30/01 @ 1123 BY HICKEY TO GOULD * * * The H-6 rod drop was determined to be due to a circuit discontinuity In a bulkhead connector. One hundred percent of the bulkhead connectors for the 45 Control Rod Drive Mechanisms (CRDMs) were inspected. Investigation is in progress to determine the cause of the connector discontinuity. The NRC Resident Inspector was notified. The Reg 2 RDO(Wert) was notified. | 0 | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0
37690 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2001-01-25 16:53 | 2001-01-25 20:10 | 2001-01-25 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO A SNUBBER ISSUE The following text is a portion of a facsimile received from the licensee: "A review of compliance with Plant Technical Specifications relative to safety-related snubber operability requirements has revealed that certain elements of the inservice inspection and testing program were not satisfied. The discovery and resultant evaluation has also determined that the 72-hour LCO applicable to snubbers has elapsed. An engineering evaluation to support an operability determination of these snubbers is in progress. In the interim the plant has defaulted to the most restrictive LCO associated with the subject equipment and has commenced an orderly shutdown." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37689 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-01-25 07:00 | 2001-01-25 17:29 | 2001-01-25 | FITNESS-FOR-DUTY REPORT REGARDING A CONTRACT SUPERVISOR WHO TESTED POSITIVE FOR ALCOHOL DURING A RANDOM TEST At 0700 CST on 01/25/01, the licensee received confirmatory results indicating that a contract employee supervisor tested positive for alcohol during a random test. The individual's access has been pulled, and a review of the individual's work has been performed. (Contact the NRC operations officer for additional details.) HOO NOTE: The licensee stated that the load reduction on Unit 1 (100% power to 86% power) was not related to this event notification. (Contact the NRC operations officer for additional details.) | 86 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.73 |  |  |  | 0
37688 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2001-01-25 15:00 | 2001-01-25 15:02 | 2001-01-25 | OFFSITE NOTIFICATION REGARDING A STRANDED SEA TURTLE The following text is a portion of a facsimile received from the licensee: "At 1500 on 01/25/01, notification of a sea turtle stranding was made to the Florida Fish and Wildlife Conservation Commission. [The sea] turtle has minor injuries and require[s] rehabilitation and transport to [the] Florida Fish and Wildlife Conservation Commission. Notification [to the NRC was] made due to notification of other government agencies." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0
37687 | 0 | US AIR FORCE |  |  |  |  | 2001-01-23 | 2001-01-25 14:00 | 2001-01-25 | NUCLEAR MATERIAL WAS DISCOVERED IN A TRASH TRUCK MAKING A DELIVERY TO A TRASH YARD A trash truck hauling trash from Hickam AFB to the Hawaii Electric Company's trash yard set off the portal monitor upon entry into the yard. The driver immediately returned to Hickam AFB where he had picked up the trash load. A Major from the Trippler Medical Center was dispatched to Hickam AFB and surveyed the material and determined that it was 1 millicurie of I-131 which could be a radiopharmaceutical. The truck was secured and surveyed and measured 18 mr/hr at the back truck surface and 1 mr/hr at one meter from the truck. It was determined that the material was picked up with a load of trash from the Billeting Office on Base and it appears was probably bodily excretions from an individual housed at the billets who recently had been treated with radiopharmaceuticals. There is no way to determine the individual or where the treatment was administered. The material will be transferred to the Trippler Medical Center where it will be held for 3 months for decay. ***** UPDATE AT 2112 ON 01/25/01 FROM ARTHUR MORTON TO LEIGH TROCINE ***** Arthur Morton of Trippler Army Medical Center called to NRC Operations Center to ask a question. The NRC operations officer notified R3DO (Creed) that the Army was also participating in corrective actions for this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
37686 | 0 | COGEMA MINING, INC. |  |  |  |  | 2001-01-24 10:00 | 2001-01-25 13:23 | 2001-01-25 | GROUNDWATER RESTORATION SPILL INTO AN ONSITE DRY DRAW IN JOHNSON COUNTY, WYOMING (48-hour report in accordance with the license) The following text is a portion of a facsimile received from the licensee: "Reported Event - A groundwater restoration spill was discovered on 01-24-01, which was estimated at 13,392 gallons. License Section 12.4 states that the 'NRC staff considers any spill of 10,000 gallons or more to be significant from an operations standpoint, regardless of the chemical and radioactive characteristics of the spill.' Therefore, the NRC [Operations] Center is notified as instructed by this license section. Note that the Wyoming Department of Environmental Quality was also notified." "Spill Date, Time, and Gallons - January 23 (10:00 [MST]) to January 24, 2001 (10:00 [MST]), estimated at 13,392 gallons" "Spill Location - Irigaray Project, Unit 9, Well HP-63, NW, NW, S16, T45N, R77W, Johnson County, WY. The spill entered a dry draw where it was contained and didn't enter any surface water or leave the NRC permit area." "Spill Cause - The spill resulted from human error when the pump in restoration well LP-63 was inadvertently energized and allowed to pump groundwater onto the surface." "Spill Source and Analysis - The spill consisted of groundwater from a wellfield which had completed the final phase of restoration. The spill contained only 3.1 mg/I uranium as U." "Health or Environmental Hazards, and Corrective Actions - No recovery of the spill was conducted since the groundwater was from a wellfield which had completed the final phase of restoration and is considered clean. The nearest community is Linch, Wyoming, approximately 21 miles to the SSE. No health or environmental hazards are anticipated." "Written Notification - A written notification will be submitted to NRC Fuel Cycle Licensing Branch Chief within 7 days." The licensee stated that the water was considered to be clean and that this event was reported because of the quantity of water involved in the spill. The licensee also stated that drinking water standards for uranium content are 5 mg/l and the spill contained only 3.1 mg/I uranium as U. In addition, the licensee reported that a Wyoming Department of Environmental Quality representative was onsite when the spill occurred and that the State representative did not have any problem with the spill. It was determined that there was no adverse impact to the public or the environment. (Call the NRC Operations Center for licensee contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MINING EVENT | [9 empty] | NON EMERGENCY | 4 | WY | MAT | [5 empty] | 0
37685 | 0 | SKW-MBT SERVICES, INC. |  |  |  |  | 2001-01-18 12:00 | 2001-01-25 09:48 | 2001-01-25 | POSSIBLE NONCONFORMANCE RELATED TO THE PERFORMANCE OF EMBECO 636 (CMTR) GROUT. SKW-MBT Management, Inc. supplied Embeco 636 (CMTR) Grout, as a nuclear safety-related product, to six customers since June 1999. This product may have been purchased through either ChemRex, Inc. or Master Builders, Inc; both of these companies are part of SKW-MBT Management Inc. "Recently, to ensure continued quality of the products that ChemRex and SKW-MBT provide, samples of our stock of Embeco 636( CMTR) Grout that were late in shelf life were submitted to re-analysis by our Quality Control (QC) Department. Based upon the results of the analysis of some of the samples, we want to inform you of a possible shelf life issue that may exist for specific lot(s) under certain conditions. During the course of preparation for application, Embeco 636 (CMTR) Grout, lot number M4-73733PO, if mixed to a fluid consistency may possibly segregate. "Based on our review and in accordance with the requirements and operating procedures of the SKW-MBT Quality Assurance Program, we are notifying nuclear facilities that have ordered Embeco 636 (CMTR) since June 1999 of this situation described above" Customers: Davis Besse Power Station, Peach Bottom Power Plant, Limerick Generating Station, Robinson Plant, Cook Nuclear Plant (both units), and Beaver Valley Power Station. (Call the NRC Operation Center for licensee contact information) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0
37684 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-01-25 02:47 | 2001-01-25 06:53 | 2001-03-23 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE. At 0247 ET on 01/25/01, the flow transmitter controller for HPCI system spiked from zero to approximately 1500 gpm. The HPCI system was in standby lineup at the time. The flow indication has been slowly drifting down. A similar event occurred on 01/23/01 at 0725ET. HPCI was declared inoperable. The flow transmitter, 23FT-82, and flow switch, 23FS-78, were vented and a small amount of air was noted. The flow indication returned to zero (normal standby indication). After a HPCI operability surveillance test, HPCI was declared operable at 1332 ET on 01/24/01. After the second flow indication perturbation on 01/25/01, HPCI was again declared inoperable with an LCO start date of 01/23/01 at 0725 ET (7 days to returned HPCI to operable status). The cause of this condition is still under investigation. All other systems are operable. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1528 EST ON 3/23/01 BY MARK ABRAMSKI TO FANGIE JONES * * * "Engineering evaluation subsequent to this event has determined that the HPCI system would have performed its' intended function as credited in the LOCA analysis and therefore this 10 CFR 50.72 notification is retracted." The licensee notified the NRC Resident Inspector. The R1DO (Kenneth Jenison) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0
37683 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-01-24 03:30 | 2001-01-24 12:20 | 2001-01-24 | 24-HR REPORT REQUIRED BY STATION ADMINISTRATIVE ORDERS FOR THE FIRE PROTECTION PLAN "Indian Point #2 Station "High Pressure Fire Header Impairment "Fire Impairment and Surveillance per Station Administration Order 703. "NRC event # 37683. The high pressure Fire Water Protection System is degraded due to planned maintenance work. The inner and outer high-pressure fire headers are split to provide protection for work on the valves for 12 Fire Main Booster Pump. 12 Fire main booster pump is inoperable during this tag-out. The diesel fire pump is in service as the alternate fire protection for the outside fire header. 11 and 12 fire maintenance pumps are supplying the inside header with 11 Fire Main Booster Pump available as a back up. SAO-703 states one fire main booster pump out of service is a 7-day action statement to return it to operable status. The headers being separated or any part of the fire protection piping or valves not being able to perform its function other than the specific instances described in SAO-703 requires an alternate fire protection system shall be established. This was established within 24 hours to ensure compliance with SAO-703 as described above. A special report shall be submitted to the NRC Regional Administrator of the Region 1 Office outlining this event within 14 Days." The licensee informed the NRC resident inspector. | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
37682 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2001-01-23 07:25 | 2001-01-24 07:36 | 2001-03-23 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE. The flow controller for the High Pressure Coolant Injection (HPCI) system is indicating approximately 1400 gpm with the HPCI system in the standby condition. Because the cause of this condition is not known at this time, the HPCI system is considered inoperable. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1528 EST ON 3/23/01 BY MARK ABRAMSKI TO FANGIE JONES * * * "Engineering evaluation subsequent to this event has determined that the HPCI system would have performed its' intended function as credited in the LOCA analysis and therefore this 10 CFR 50.72 notification is retracted." The licensee notified the NRC Resident Inspector. The R1DO (Kenneth Jenison) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0
37681 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-01-23 15:10 | 2001-01-23 20:47 | 2001-01-23 | LOSS OF CONTAINMENT INTEGRITY INVOLVING PERSONNEL AIRLOCK INTERLOCK FAILURE "On 23 January 2001, at 1510 hours, during the removal of radiation survey equipment from the lower containment personnel airlock, the airlock doors interlock failed. This allowed the inadvertent opening of both containment airlock doors at the same time for less than one minute. This resulted in a short entry into Technical Specification 3.6.1.1, for Primary Containment integrity and entry into Technical Specification 3.6.1.3, for inoperable Containment Airlock Doors. There was no radioactive release as the result of this event." The cause of the interlock failure is under investigation. Currently the licensee is controlling entry administratively. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0
37680 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2001-01-23 11:09 | 2001-01-23 19:03 | 2001-01-25 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM DECLARED INOP ON LOW FLOW "On January 23, 2001, while performing the Control Room Emergency Filtration System (CREVS) monthly surveillance, the system flow was found to be 1741 SCFM [standard cubic feet per minute]. The required Technical Specification flow is 2000 SCFM +/- 10%. "The CREVS system was declared inoperable per Technical Specification 3.8.D and both Units entered a 7 day shutdown LCO. "This is being reported in accordance with 10CFR50.72(b)(3)(v)(D). "The initial flow measured was 1741 SCFM. Approximately 15 minutes later the flow was measured to be within Technical Specification limits. The station is continuing an evaluation of this issue." The licensee informed the NRC resident inspector. * * RETRACTION ON 01/25/01 AT 1107 ET BY D. NOHR TAKEN BY MACKINNON * * * The licensee has completed their evaluation and has determined that the CREVS was always capable of performing its intended function in response to a LOCA. Therefore the licensee is retracting this event. R3DO (Jim Creed) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0
37679 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2001-01-23 13:20 | 2001-01-23 18:16 | 2001-01-23 | CONTRACT SUPERVISOR CONFIRMED POSITIVE FOR ILLEGAL DRUG USE DURING RANDOM TEST A contract supervisor was determined to be under the influence of an illegal drug during a random test. The individual's access to the plant has been terminated. The licensee informed the NRC resident inspector. Contact the Headquarter Operation Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.73 |  |  |  | 0
37678 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-01-22 13:50 | 2001-01-23 09:41 | 2001-01-23 | FITNESS FOR DUTY A nonlicensed employee was determined to have used an illegal drug during a random test. The employee's access to the plant has been suspended. Contact the Headquarters Operation Officer for additional details. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.73 |  |  |  | 0
37677 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-01-23 06:19 | 2001-01-23 09:00 | 2001-01-23 | PLANT SHUTDOWN REQUIRED DUE TO FAILURE OF SHUTDOWN BANK "D" TO FULLY WITHDRAW DURING SURVEILLANCE TESTING The licensee was performing rod surveillance testing when shutdown bank "D" failed to withdraw. Entry was made to Technical Specification 3.0.3 at 0619 CST as more than one rod failed to withdraw. The plant commenced shutdown at 0712 CST. See related event #37675. The licensee notified the NRC Resident Inspector. | 0 | 27 | 0 | 0 | 29 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37676 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2001-01-23 01:46 | 2001-01-23 02:24 | 2001-01-23 | UNUSUAL EVENT DECLARED ON LOSS OF ALL ANNUNCIATORS FOR GREATER THAN 15 MINUTES The licensee was conducting daily light checks of annunciators when they did not clear when the test signal was reset. The declaration of Unusual Event was made at 0146 EST in accordance with the Emergency Action Level procedure and entry was also made into the abnormal procedure for the loss of annunciators. The plant computer was still available for alarm monitoring and 2 operators were placed at the control panels for close monitoring of plant conditions. The plant was maintained at stable conditions. The watch stations outside of the control room were augmented to provide additional monitoring of outside control panel alarms which would not be received in the control room. Electricians and Instrumentation Technicians have started investigating the problem. The licensee notified the NRC Resident Inspector and the state and local authorities. * * * UPDATED AT 0242 EST ON O1/23/01 BY JOHN VOISSEM TO FANGIE JONES * * * The Unusual Event was terminated at 0237 EST. The alarm lights cleared on their own and subsequent test of alarm function was satisfactory. Additional personnel are in transit to the site to conduct further testing. The licensee will notify the NRC Resident Inspector as well as state and local authorities. Notified the R2DO (Rudolph Bernhard), NRR EO ( John Hannon), IRO Manager (Joseph Giitter), and FEMA (Belcher). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0
37675 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2001-01-22 14:05 | 2001-01-22 16:35 | 2001-01-22 | UNIT 2 COMMENCED A UNIT SHUTDOWN FOLLOWING A FAILURE OF ROD POSITION INDICATION DURING SURVEILLANCE TESTING During control rod exercise surveillance testing, shutdown bank "C" indication failed to respond to rod motion. Tech Sec 3/4.1.3.1 action b was entered which requires that the unit be placed in mode 3 (Hot Standby) within 6 hours. The licensee commenced a shutdown and anticipates having Unit 2 offline by 1900 hours. The licensee informed the NRC resident inspector. | 0 | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37674 | 0 | WATERBURY HOSPITAL |  |  |  |  | 2001-01-18 16:00 | 2001-01-22 16:22 | 2001-01-22 | TREATMENT INVOLVING I-131 TO PREGNANT FEMALE In August of 2000, a female patient received 12.15 millicuries I-131 as prescribed for hyperthyroidism. The patient when questioned did not disclose that she was pregnant at the time. The licensee in discussion with Region I (Shanbaky) on 1/19 was requested to make a voluntary notification with a written followup report. Hoo Note: Region I issued PNO-I-01-002 to address this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | HOS | [5 empty] | 0
37673 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2001-01-21 15:28 | 2001-01-21 18:29 | 2001-03-01 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM INOPERABLE At 1528 the Control Room Emergency Filtration System (CREFS) was declared inoperable when fire door H305 was noted to hang open instead of fully closing when personnel passed through the door. BLDG-DOOR-H305 is a Control Room Envelope Door. CREFS is a single train system. When CREFS was determined to be inoperable Technical Specification LCO 3.7.4 condition A was entered. This LCO requires the restoration of CREFS to OPERABLE status within 7 days or be in MODE 3 within 12 hours and MODE 4 within 36 hours. Following the transfer of CREFS to DIV 1 power at 13:30, it was subsequently noted that the control room blast doors seemed harder to open than normal. The ventilation lineup for the Control Building was verified to be correct. During this verification it was determined that BLDG-DOOR-H305 would not operate properly and the door and CREFS were declared inoperable. Ventilation flow through other Control Room Boundary Doors appears [to]be abnormal for the present ventilation lineup. A Fire Watch has been stationed at BLDG-DOOR-H305. A Problem Identification Report has been initiated to identify that BLDG-DOOR-H305 will not close by itself from the fully open position. The ventilation lineup has not been changed since the discovery of this condition for evidence preservation. The Ventilation System Engineer is responding to the Site to assist with troubleshooting of the ventilation system. The licensee notified the NRC resident inspector. * * * UPDATE 1514EST ON 3/1/01 FROM DAVID VANDERKAMP TO S. SANDIN * * * The licensee is retracting this report based on the following: "Basis for Retraction: "Event Number 37673 reported a condition at Cooper Nuclear Station (CNS) where the Control Room Emergency Filtration System (CREFS) was declared inoperable. This was a result of the control room envelope boundary being declared inoperable due to a fire door not closing automatically when it was opened raising questions about integrity of the envelope. "On a specific occasion, a fire door that allows access from the control room access hall to the computer room, was unable to close without assistance. This was discovered when an operator passed through the door and it failed to close behind him. He had to manually assist the door closed. The door was declared inoperable as a fire boundary door and a fire watch was posted. Since the door forms part of the control room envelope boundary, that boundary was also declared inoperable due to concerns about the envelope integrity. Therefore, CREFS was declared inoperable. "Technical Specifications require that the control room envelope be maintained at a positive pressure in the emergency line-up on the control room ventilation system but not in the normal line-up. This should be considered a normal operation of the door for entry and exit per Technical Specification Bases 3.7.4. This states that: '...in addition, the control room boundary must be maintained, including the integrity of the walls, floors, ceilings, ductwork and access doors, such that the pressurization limit of SR 3.7.4.4 can be met. However, it is acceptable for access doors to be open for normal control room entry and exit, and not consider it to be a failure to meet the LCO.' "There was no condition present that would challenge the integrity of the Control Room envelope, other than the door not closing automatically. The door was manually closed while being used for access. Signs are posted at doors that should be closed to ensure that doors are closed after they are opened. The operator passing through this door closed the door when it would not close by itself. Not withstanding the fact that the door was closed as required; a Fire Watch was posted to better ensure that the door was properly closed until the reason for it's not automatically closing was determined. No major components failed. "The cause of the door not automatically closing was determined to be a mis-positioned, manually operated damper. The mis-positioned damper caused a decreased positive pressure inside the Control Room envelope boundary impacting the automatic door closure. If an accident had occurred while this damper was mis-positioned, the Control Room Emergency Filtration System would have performed its safety function as designed and continued to be operable. "Based on this updated information, the District has determined that this event is not reportable under the requirements of 10CFR50.72(b)(2)(iii)(D), and as such, event 37673 is retracted." The licensee will inform the NRC resident inspector. Notified R4DO(Howell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37672 | -1 | FROEDTERT MEMORIAL LUTHERAN HOSP |  |  |  |  | 2001-01-17 18:30 | 2001-01-19 16:59 | 2001-04-11 | POTENTIAL MEDICAL MISADMINISTRATION A patient being treated with a Leksell gamma system model 23004 type B received a treatment to the wrong site. The intended dose or dose delivered were not available. The dose was delivered to the wrong location because the head frame had been installed in the wrong position. The correct site was subsequently treated. The hospital is in the process of informing the patient and the referring physician. The attending physician did not believe the mistake would pose a problem to the patient. ***** UPDATE AT 1439 EDT ON 04/11/01 FROM MARCUM MARTZ TO LEIGH TROCINE ***** After discussions with the NRC Region 3 staff (Bob Gattone), it was determined that this event did not involve a medical misadministration. Therefore, the licensee is retracting this event notification. The NRC operations officer notified the R3DO (Wright) and NMSS EO (Smith). Call the NRC operations officer for a licensee contact telephone number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | WI | HOS |  | 35.33 |  |  |  | 0
37671 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-01-19 11:45 | 2001-01-19 11:58 | 2001-01-19 | UNIT 2 DECLARED AN UNUSUAL EVENT BASED ON IDENTIFIED REACTOR COOLANT SYSTEM (RCS) LEAKAGE > 10 GPM At 1145EST on 1/19/01, Unit 2 declared an Unusual Event based on RCS leakage of 10.0015 gpm. The location of the leakage is the "C" loop unit bypass valve 2-RC-MOV-2587. The leakage is through the packing leakoff line to the primary drain tank. There are minor elevated rad levels in the stripper cubicle where the drain tank is located. HP personnel are monitoring this area. The licensee expects to have Unit 2 offline by 1600EST today. Tech Spec 3.4.6.2 requires that identified RCS leakage be less than 10 gpm or that the unit be placed in cold shutdown by 0300EST on 1/21/01. The licensee anticipates completing repairs while in mode 3 at which time they will exit the Unusual Event. The licensee informed both state/local agencies and the NRC resident inspector. * * * UPDATE AT 2314 on 1/19/01, BY BROWN, RECEIVED BY WEAVER * * * 2-RC-MOV-2587 was opened electrically and manually backseated. This reduced RCS leakage below 10 gpm and the unusual event was terminated at 2323EST. The plant is stable in mode 3 and the licensee is developing a plan to repair the valve. Repairs may be done with the plant in mode 3. The licensee will notify the NRC resident inspector. The operations center notified the RDO (Rodgers); EO (Leeds); FEMA (Steindurf) | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor |  |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | VA | POW | [5 empty] | 0
37670 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2001-01-18 20:40 | 2001-01-18 21:22 | 2001-01-18 | EMERGENCY OPERATIONS FACILITY HIGH RADIATION FILTRATION SYSTEM INOPERABLE Work in progress to modify the High Rad Filtration System left the system inoperable. The modification is intended to make the system auto restart after a loss of power event. Workers left the job site with the modification incomplete, thus rendering the system inoperable. Workers have been called back to the site to either restore the system or complete the modification. Operators were following up on an annunciator that alarmed at 1730 and discovered that some work had been done on the system. The licensee notified the NRC resident inspector and state and local governments. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37669 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2001-01-17 12:00 | 2001-01-18 15:59 | 2001-01-18 | AGREEMENT STATE REPORT "Novoste Beta-Cath System, A1000 Series, device ejected the source train just prior to treating a patient. The shielded bailout box was used and most of the sources went immediately into the bailout box. All remaining sources were located and placed in the bailout box. The patient was removed from the room when the incident occurred. No misadministration occurred as patient treatment had been completed and no sources remained in the patient. The incident occurred on the 25th use of the device (device has a built in counter). Licensee contacted the manufacturer of the device on the day of the incident. Physicist and Radiologist were present during incident. Isotope: Strontium 90 Amount of Activity: < 300 millicuries" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | GA | OTH | AGR |  |  |  |  | 0
37668 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2001-01-18 12:00 | 2001-01-18 13:51 | 2001-01-18 | FIRE BARRIER DOOR MAY NOT HAVE BEEN PERIODICALLY TESTED On 1/15/2001, it was discovered that an appendix R fire barrier door may not have been periodically tested according to requirements. On 1/18/2001, during functional testing, the subject door failed to close completely. The subject door is a normally open door that by design should automatically close when a temperature sensitive fusible link is actuated. When tested the door closed to all but the last two to three inches of travel. Under the presumption that the door is required to close completely to fulfill it's design function this event is conservatively being reported as a failure to meet Kewaunee's Appendix R design basis. The licensee notified the NRC resident inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37667 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-01-17 16:20 | 2001-01-17 19:12 | 2001-01-17 | TURBINE TRIP/REACTOR TRIP DURING TURBINE CONTROL TESTING. Reactor Trip due to Turbine Generator trip greater than 69% power. All rods fully inserted into the core. Feedwater isolation due to reactor trip with Tave less than 564 degrees F (this is a design feature and was expected). Both Motor Driven Auxiliary Feedwater pumps automatically started as expected due to the Feedwater Isolation. As far as the licensee knew at the time of the call no Primary or Secondary PORVs or Code Safety Valves opened. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable. "1A" Nuclear Service Water pump is out of service for planned maintenance (currently being returned to service) and the "1A" Auxiliary Building Ventilation is also inoperable for planned maintenance. Currently the cause of the turbine trip is unknown. Turbine Control Testing was in progress at the time of the trip. The licensee will notify North & South Carolina and surrounding counties of the reactor trip. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37666 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-12-20 12:00 | 2001-01-17 16:20 | 2001-01-18 | LOST HUMBOLDT 5001EZ NUCLEAR GAUGE This is an initial notification of a lost nuclear gauge. The gauge was lost on December 20, 2000, while being transported in an unsecured manner and not in it's transport case. The gauge was a one month old Humboldt 5001EZ. The gauge was probably lost along Highway 90 and 36th Street in San Antonio, Texas. A Police Report was filed (Report # 00805997/01). The operator performed an extensive search for the gauge along the highway. A notice was posted in the San Antonio Express News with a reward offered. The gauge has not been recovered to date. Investigation is on going. Further details will be sent as they are received at the Texas Department of Health. * * * UPDATE 0818 1/18/2001FROM OGDEN TAKEN BY STRANSKY * * * A representative of the Texas Department of Health called the Operations Center to correct and clarify the initial report. The gauge is a Humboldt 5001EZ, not a 5001EX as initally reported. Additionally, the Texas licensee is Reed Engineering Group of Houston. [HOO Note: the text of the initial report above has been corrected.] Notified R4DO (Kennedy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37665 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2001-01-11 11:00 | 2001-01-17 11:43 | 2001-01-17 | DURING A SMALL BREAK LOSS OF COOLANT ACCIDENT PEAK CLADDING TEMPERATURES COULD EXCEED 2200 DEGREES F. B&W Owners Group Preliminary Safety Concern (PSC) was written on July 28, 2000 to document a concern with RELAPS analyses of Core Flood Tank (CFT) line break LOCAs. The issue involves the impact of a 2 minute delay in tripping reactor coolant pumps (RCPs). In the event of a small break loss of cooling accident involving the core flood line, peak cladding temperatures could exceed 2200 degrees F. However, this issue does not impact Oconee during normal operation since Oconee has three high pressure injection (HPI) pumps. The Oconee design basis includes starting a second HPI pump within 10 minutes, which would prevent excessive peak clad temperatures. On January 17, 2001, at 1100 hours, preliminary analyses revealed that plant conditions, allowed by Oconee Technical Specifications 3.5.2.B and 3.5.2.C may necessitate either reducing reactor power to approximately 50% (versus 75%) or tripping RCPs within 1 minute versus 2 minutes of loss of subcooling margin to maintain clad temperatures less than 2200 degrees F. In these specific plant conditions, the single failure of the second HPI pump or failure of an HPI train would prevent starting a second HPI pump and injecting within 10 minutes. This is being conservatively reported as a condition that alone could prevent the fulfillment of a safety function. This condition is only a concern during extended operation with one HPI pump or train out of service. Procedural guidance in place requires turning off the RCPs as an immediate manual action in response to loss of subcooling margin. Operators in training typically secure the RCPs well within 1 minute of loss of subcooling margin during unannounced casualty scenarios. Operators are evaluated on the time critical action of securing the ROPs within two minutes; however, the time critical action of securing the RCPs within 1 minute has not yet been validated using our appropriate processes. Therefore, as an interim measure, Oconee intends to reduce thermal power to <50% rated thermal power (RTP) instead of <75% RTP whenever TS 3.5.2.B or 3.5.2.0 is entered. This action ensures that the acceptance criteria of 10CFR50.46 are satisfied. The NRC Resident Inspector was notified. Problems encountered during the event: None. | 18 | 100 | 100 | 18 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37664 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-01-16 | 2001-01-17 07:47 | 2001-01-17 | FITNESS FOR DUTY REPORT A contract manager tested positive for illegal drug use. The individual's site access privileges have been terminated. The licensee will contact the NRC resident inspector regarding this report. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.73 |  |  |  | 0
37663 | 0 | ABB POWER DISTRIBUTION |  |  |  |  | 2001-01-15 15:20 | 2001-01-15 16:33 | 2001-01-15 | POTENTIAL DEFECT PER 10 CFR PART 21 CONTROL DEVICE FOR HK AND K-LINE CIRCUIT BREAKERS In December 1998, Sequoyah Nuclear Plant (Chattanooga, TN) experienced a failure to close of a 7.5HK500/1200 Medium Voltage circuit breaker (Serial Number 48672-A101-1-3B) manufactured 3/30/1973. The cause of the breaker failure as determined by TVA was a failure of the Control Device (Part Number 191921T06). Specifically, a movable contact within the Control Device was found to have a broken spring retainer, which is a protuberance holding the return spring in place on the contact. This broken spring retainer allowed the spring to move out of its intended position, causing failure of the control contacts to make and break properly. This occurrence was documented and evaluated by the Tennessee Valley Authority Central Laboratories & Field Testing Service in their Technical Report #99-0550 on 11 February 1999. On February 29, 2000, Catawba Nuclear Station (York, SC) experienced a failure to close of a 5HK250/1200 Medium Voltage circuit breaker (Serial Number 50465F-1 -10186) manufactured 3/28/1979. The cause of the breaker failure as determined by Duke Power and ABB Florence was similar to the failure reported by TVA in 1998. Material analysis of the failed movable contact concluded that the material for the contact was correct to that specified. A dissected profile analysis of the failed contact revealed that the material at the base of the spring retainer on the movable contact was thin and failed due to fatigue. This failure was documented and evaluated by Duke Engineering Testing and Laboratory Services in their Metallurgical Analysis Report #2624 on 29 March 2000. On October 30, 2000, during a routine inspection of a Control Device on a 7.5HK500/1200 Medium Voltage circuit breaker (Serial Number 50464L-2-07210) manufactured 2/29/1979, Catawba Nuclear Station found a movable contact that had failed in a similar manner as the other two previously reported. This failure was documented and evaluated by Duke Engineering Testing and Laboratory Services in their Metallurgical Analysis Report #2726 on 01 November 2000. The cause of these three failures was fatigue of the metal at the base of the spring retainer on the movable contacts, due to insufficient metal mass at the base of the retainer. The spring retainer on the contact is formed with a die by punching the movable contact from the opposite side of the electrical contact mounting location during fabrication. The height of the spring retainer, therefore, determines the amount of material left at the base. Corrective action for this incident has been taken. After further investigation, ABB Florence has determined that the height of the spring retainer was changed in September 1979 to a lower specification, leaving more material at the base of the spring retainer. The movable contact formed with the greater spring retainer height specification prior to 1979 has a small possibility of failure as discussed above. There have been no other reports of movable contact failures. There have been only these three reports of this movable contact failure since the control device was introduced to the market in 1960. Since its introduction, more than 22,000 control devices have been produced for both HK and K-line type circuit breakers, each with 5 movable contacts. ABB therefore believes this problem is not significant enough to require immediate action from users. However, we recommend that control devices older than 1981 be replaced with new control devices on both HK and K-line breakers at the next scheduled maintenance of the breaker. ABB will notify all customers who purchased this product. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | SC | OTH | PAR | 21.21 |  |  |  | 0
37662 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2001-01-11 11:30 | 2001-01-12 15:33 | 2001-01-12 | AGREEMENT STATE REPORT INVOLVING FIRE IN AN INCINERATOR AIR EFFLUENT CLEANING SYSTEM "Event description: The licensee called to report a fire in their incinerator's air effluent cleaning system. The fire in the baghouse lasted approximately two hours. The building was evacuated, and onsite personnel extinguished the fire. The baghouse filter has not yet been opened to assess the damage. The area is secured and no routine operations are ongoing at this time. Smears taken in the area were maximum of 100-dpm/100 sq. cm. Clean up of the area has not begun. The total release from this event is estimated to be 0.013 microcuries of depleted uranium. Sample results will be available soon. "These events do not pose a threat to public health and safety but may be reportable under 1200-2-5-.141(2)c.(4). "Media attention: None" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
37661 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2001-01-12 09:28 | 2001-01-12 13:40 | 2001-01-12 | INVALID ACTUATION OF AN ENGINEERED SAFETY FEATURE SYSTEM During performance of "A" Train Trip Actuations Device Operational Test a reactor protection signal was generated when a procedure step was inadvertently skipped. At the time this occurred the "A" reactor trip bypass breaker was closed when the trip signal was generated. This caused the "A" reactor trip breaker to open. The reactor did not trip because the "A" bypass breaker was closed. This event resulted in an invalid actuation of an Engineered Safety Feature system. It was concluded that this event was reportable per 10CFR50.72(b)(2)(ii) since: (1) This actuation was not anticipated to occur as part of this pre-planned evolution since the trip signal was expected to be inhibited by the omitted procedure step and (2) The omitted step resulted in the system not being properly removed from service as required by the surveillance procedure (source range trip signal not being bypassed or inhibited). The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37660 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-01-12 10:30 | 2001-01-12 13:36 | 2001-01-12 | AN ACTING SUPERVISOR TESTED POSITIVE FOR AN ILLEGAL DRUG DURING A RANDOM TEST A non-licensed employee was determined to be under the influence of marijuana during a random test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.73 |  |  |  | 0
37659 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2001-01-11 17:15 | 2001-01-11 17:37 | 2001-01-11 | DISCOVERY OF CONDITION INVOLVING INABILITY OF THE LOW PRESSURE COOLANT INJECTION (LPCI) SYSTEM TO PERFORM DESIGN FUNCTION BETWEEN APRIL 1999 AND JANUARY 2001 "On 1/2/01, discovered incorrect relays (27-B2X2 and 27-B2Z2) had been installed in Bus B6 (480 VAC swing bus) during RFO 12 (April, 1999). The bus transfer logic was declared inoperable at the time and entry was made into a 7-day cold shutdown LCO for LPCI. "Further analysis of the circuit has determined that the B6 Bus would have remained de-energized following a loss of offsite power if the 'A' side power supply became unavailable (i.e., 'A' Emergency Diesel failed or 'A' 125 VDC Battery failed). "This condition is outside the design in accordance with Pilgrim Station FSAR. "The relays were replaced with the correct design and the LPCI LCO cleared at approximately 0745 Sunday, January 7, 2001." The licensee will inform the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37658 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2001-01-09 12:20 | 2001-01-09 13:08 | 2001-01-17 | NEUTRON MONITORING DETECTOR MISSING FROM SHIPMENT The licensee reported that one local power range monitor (LPRM) detector was missing out of a shipment from GE Reuter-Stokes in Twinsburg, OH. The missing detector contains 0.00027g of U-235 (0.00121g total U) in the form of solid uranium oxide. The licensee has contacted the vendor to determine whether an error occurred in preparation of the shipping papers. The NRC resident inspector will be informed of this event by the licensee. * * * UPDATE 1529 FROM KIDDER TAKEN BY STRANSKY * * * At 1355, the licensee was informed that the missing LPRM detector is currently located at the GE Reuter-Stokes facility and had not been shipped. The NRC resident inspector has been informed of this update. Notified R3DO (Jacobson). * * * RETRACTION 1015 01/17/2001 FROM RUSSELL TAKEN BY STRANSKY * * * "Investigation by the licensee and the manufacturer discovered that the LPRM had been maintained in a secure, locked area at GE Reuter-Stokes and had been kept under appropriate controls. Accordingly, no reporting criterion is applicable to this event under 10CFR50.72 or 10CFR70.52. Additionally, the SNM is not of sufficient quantity that 10CFR73.71(a)(1) or 10CFR20.2201 apply. "Event Notification 37658 is therefore retracted." The NRC resident inspector has been informed of this retraction by the licensee. Notified R3DO (Lanksbury). | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS OF SNM/CRIT | LOSS OF SNM/FISSILE | SAFEGUARDS REPORTS |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 70.52(a) | 70.52(b) | 73.71(b)(1) |  | 0
37657 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2001-01-09 04:01 | 2001-01-09 08:13 | 2001-01-09 | ISOLATION CONDENSER STEAM CONDENSATE HIGH FLOW SWITCHES OUT OF CALIBRATION "During performance of DIS 1300-07, Isolation Condenser Steam Condensate High Flow Switch Calibration, DP switch 3-1349A as found trip setpoint was outside of T.S. limits. The as found value was -17.5 in WC and the T.S. limit is </= to 14.8 in WC. Later in the same surveillance, DP switch 3-1349B as found trip setpoint was outside of T.S. limit is </= 14.8 in WC. These are the Div 1 and Div 2 Isolation Condenser Condensate High Flow isolation instruments. With both these switches inop, the Isolation Condenser would not have isolated at the appropriate time on a valid high condensate flow signal. The Isolation Condenser was already isolated when the out of tolerance switches were discovered and the switches were calibrated satisfactorily prior to unisolating the Isolation Condenser." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37656 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-01-08 11:27 | 2001-01-08 20:27 | 2001-01-08 | 24-HOUR NRC BULLETIN 91-01 REPORT "At 1127 hours, 01/08/01, the Plant Shift Superintendent's (PSS) office was notified of a discrepancy in the U-235 Mass log in room 229, X-710 Lab Services Facility. A NCS Anomalous Condition was initiated and NCS Engineer personnel were contacted to investigate the discrepancy. Investigation revealed that two containers were moved from room 229 into room 330 without being logged out of room 229 or logged into room 330. The failure to log the movement of the two containers into and out of the respective mass inventories represents a loss of controls 2a and 2b of NCSA-0710_022.A01. Since the NCSE takes credit for these controls to satisfy both legs of the double contingency principle, this event involves the loss of both controls credited for double contingency. At 1430 hours, 01/08/01, NCS Engineering reported that compliance with NCSA-0710_022.A01 was reestablished This event does not involve greater than a safe mass and moderation is not a control (primary or otherwise) in the affected NCSA/NCSE. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is low. The U-235 mass inventory in Room 330 is 129.1 grams, which is well below the safe mass limit if 230 grams of U-235 for oily material. The failure to log the container movement at no time challenged the safe mass limit. A minimum of 588 grams U-235 (Reference POEF-LMUS-44) would be needed to support a criticality at the analyzed enrichment limit (100%) under optimum conditions "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "If the safe U-235 mass limit was at the maximum allowable value for operations involving oily material, and these two containers were added to the mass present, there would need to be an additional 347 grams of U-235 present in the room before a critical mass for full reflection, optimum moderation and spherical geometry were exceeded for oily conditions. For this amount of U-235 to be present, multiple errors in the log book would need to occur. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "The control Parameter for this operation is mass. NCSA-0710_022 places two controls on this parameter. The combined mass of all fissile material is limited to 350 grams of U-235 for non-oily/greasy material and 230 grams of U-235 if oily/greasy material is present. The NCSA requires that a log of U-235 mass inventory be maintained to demonstrate that the mass limit is not exceeded. Each log entry consists of the mass value plus analytical uncertainty. A log entry is made by the person responsible for the movement of U-235 into the room and is verified by a second knowledgeable person. "ESTIMATED AMOUNT, ENRICHMENT. FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "There were approximately 100 containers in room 330 that contain 129.1 grams of U-235 in both solid and liquid form. Out of these containers there were approximately 33.7 grams U-235 enriched to greater than 20% in fire room at the time of this event. The NCS analysis assumes 100% enrichment in developing the mass limit and does not control enrichment. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Two containers with >500 ppm U-235 concentration and greater than 1.0 weight percent U-235 enrichment were not logged out of room 229 nor were they logged into room 330. Since they were not logged in or out, no verification was performed. The safety significance of this event is low due to the small amount of U-235 involved." The NRC resident inspector has been informed of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37655 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2001-01-08 11:50 | 2001-01-08 16:32 | 2001-01-30 | HPCI SYSTEM DECLARED INOPERABLE "The High Pressure Coolant Injection (HPCI) system was declared inoperable due to an air line leak. The unplanned loss of a single train system (such as HPCI) is reportable as a loss of safety function. The air line supplies air to air-operated valves for draining the steam supply line to ensure that the HPCI steam supply line does not fill with water. Upon a HPCI initiation signal that would cause the steam supply valve to open or on a loss of air pressure, these air-operated valves automatically shut. With the degraded condition of the air supply line, assurance could not be maintained that the steam lines would be maintained clear of water. HPCI is presently available and capable of injecting if required." The NRC resident inspector has been informed of this notification by the licensee. * * * UPDATE ON 1/30/01 @0951 BY WHEELER TO GOULD * * * RETRACTION The affected air line supplies air to air operated drain valves for draining the HPCI System steam supply line. On a HPCI System initiation signal or on a loss of instrument air (i.e. the failure or isolation of the air supply line), the HPCI System steam supply line drain valves would automatically close. In this condition, in the response to high level alarms, manual opening of the HPCI System steam supply line drain valves would have been performed, in accordance with procedures, to ensure the HPCI System steam supply line remains clear of water. However, no water had accumulated in the HPCI System steam supply line prior to or during the condition (as evidenced by the lack of alarms). In the event water had accumulated in the HPCI System steam supply line and had not been removed, the HPCI turbine has been designed and tested to ensure that water carry-over (from the reactor vessel) will not cause damage to the turbine. The HPCI System has adequate capacity to accept the small losses in efficiency due to any moisture carryover. In addition, in preparation for and during maintenance/repair of the air supply line, no actions were taken which would have prevented the HPCI System from functioning. Based on this analysis, the HPCI System was fully capable of performing its safety functions and HPCI System Technical Specification Surveillance Requirements continued to be satisfied at all times. The HPCI System remained operable during this period. Therefore, Event Number 37655 is retracted. The NRC Resident Inspector was notified. Region 4 RDO (Spitzberg) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(D) |  |  | 0
37654 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2001-01-07 09:30 | 2001-01-08 13:54 | 2001-01-08 | CLOSED FIRE DAMPERS WOULD RESULT IN BYPASS OF HEPA FILTERS "On January 6, 2001, during testing of the auxiliary building ventilation system, it was noted that the flow through the HEPA-charcoal train did not meet the Technical Specification acceptance criterion. Upon further investigation by plant personnel on January 7, 2001 at 0930 it was discovered that fire damper ABF13 had closed. Closure of this damper resulted in the closure of damper ABS8 (an excess flow damper). On January 8, 2001, at 1030 following further engineering evaluation, it was determined that with these dampers closed, filtration of the effluents from the pipe chase and RHR areas would not have been processed through the HEPA-charcoal absorber. This condition does not meet the assumptions of the Salem offsite dose analysis, and therefore the condition meets the reporting requirements of 10 CFR 50.72(b)(2)(iii). As of January 7, 2001 at 1605 dampers ABF13 and ABS8 were open and flow through the HEPA-charcoal train was verified to meet Technical Specification acceptance criterion." The NRC resident inspector will be informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37653 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2001-01-08 | 2001-01-08 10:14 | 2001-01-16 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following is taken from a faxed report: A Troxler gauge containing 8 mCi Cs-137 and 40 mCi Am-241:Be was stolen. The Ft. Lauderdale Police case number is 013072. Florida DOT bright orange van parked at owners address was stolen sometime between 6 a.m. Sunday (7th) and 7 a.m. Monday (8th). A Troxler gauge was in a locked box in the van. The keys to the gauge were not in the van. The police have been notified. * * * UPDATE AT 1120 AM ON 1/16/01 BY CHARLES ADAMS TO FANGIE JONES * * * The van and gauge were recovered on 1/13/01 in Plantation, FL. The office was notified on 1/16/01. The gauge was undisturbed in the van and is in custody of the owner. The Florida Bureau of Radiation Control notified NRC Region II. The R2DO (Charles Ogle) and NMSS EO (Joseph Holonich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37652 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2001-01-07 06:00 | 2001-01-07 09:50 | 2001-01-07 | SECURITY REPORT Safeguard system degradation related to area boundary. Immediate compensatory measures taken upon discovery. The licensee notified the NRC Resident Inspector. Refer to HOO Log for additional details. | 0 | 100 | 90 | 0 | 100 | 90 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 0
37651 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2001-01-06 18:30 | 2001-01-06 20:50 | 2001-01-06 | COURTESY CALL TO THE NATIONAL RESPONSE CENTER (NRC) MADE AFTER SPILLING APPROXIMATELY 25 GALLONS OF SULFURIC ACID. A courtesy call was made to the National Response Center that was made to report a sulfuric acid spill at the plant water treatment area. The Corporate Environmental and Regulatory Affairs Department, which the licensee calls ERAD, was notified. ERAD, in turn, notified the Minnesota State Pollution Control Agency. The Minnesota State Pollution Control Agency suggested a courtesy call to the National Response Center. Approximately 25 gallons of sulfuric acid was spilled (reportable quantity is 65 gallons of greater). A small amount, less than 10 gallons, of acid drained to their Turbine Building Sump of which a very small amount may have been released. The NRC Resident Inspector was notified. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37650 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2001-01-05 08:48 | 2001-01-05 12:25 | 2001-01-05 | REACTOR MANUALLY TRIPPED FROM 80% POWER LEVEL DUE TO EXCESSIVE MAIN TURBINE GENERATOR HYDROGEN LEAK. "At 0848 CT on 01/05/01 ANO Unit 1 reactor was manually tripped due to excessive hydrogen leakage on the main turbine generator. Reactor power was reduced from 100% to 80% prior to the manual reactor trip. No ESF actuations occurred following the trip. The unit is currently stable at Hot Shutdown conditions." Hydrogen leak on the main turbine generator was first noticed around 2100 hours CT on 01/04/01. Normal hydrogen pressure in the main turbine generator is 70 psi. The licensee stated that they were losing approximately 3 psi per hour. The licensee evacuated the Turbine Building as a precaution. After reactor power had been reduced to 80% power the hydrogen leak increased at which point the licensee manually tripped the reactor. All rods fully inserted into the core. Once Through Steam Generator atmospheric valves operated properly. The licensee stated that they have a 0.17 gallon per day primary leak to secondary system leak. All Emergency Core Cooling Systems and the Emergency Generators are fully operable if needed. Once Through Steam Generator water levels are being maintained using main feedwater, one main feedwater pump operating. At the time of the notification the licensee had not located the source of the hydrogen leak. The licensee notified Arkansas Department of Health. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 01/05/01 AT 1734 ET BY REX KNIGHT TAKEN BY MACKINNON * * * When the reactor was tripped, discharge canal temperature dropped from 52 degrees F to 37 degrees F. This caused a large number of Thread Fin Shad to die. A member of the public called the Arkansas Game and Fish (AG&F) Commission about the Shad. ANO has contacted the AG&F Commission and explained the situation. A Press Release is not planned at this time. NRC R4DO (Bill Johnson) notified. The NRC Resident Inspector was notified of the event update by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(vi) |  |  | 0
37649 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2001-01-02 | 2001-01-05 11:22 | 2001-01-05 | STOLEN NUCLEAR MOISTURE DENSITY GAUGE The licensee reported that a Campbell Pacific Nuclear moisture density gauge was stolen from a storage unit in Oceanside, Ca between 1530 on 12/29/00 and noon on 12/30/00. Model # of the gauge was MC-3 and its serial # is M380504284. The gauge contained approximately 8 millicuries of cesium-137 and 40 millicuries of americium/beryllium. The licensee will offer a reward. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37648 | 0 | COLORADO DEPARTMENT OF HEALTH |  |  |  |  | 2001-01-05 08:00 | 2001-01-05 10:02 | 2001-01-05 | AGREEMENT STATE REPORT - MOLYBDENUM-99/TECHNETIUM-99m GENERATOR LOST WHILE IN SHIPMENT DUPONT PHARMACEUTICALS SHIPPED A 750 MILLICURIE MOLYBDENUM/TECHNETIUM GENERATOR VIA FEDEX TO THE SAN LUIS VALLEY REGIONAL MEDICAL CENTER IN ALAMOSA, CO ON 12/28/00. AS OF THIS DATE THE SHIPMENT HAS NOT BEEN RECEIVED. THERE WAS NO FEDEX TRACKING NUMBER AND DUPONT COULD NOT GIVE THE STATE ANY INFORMATION BECAUSE THEIR COMPUTERS WERE DOWN. * * * UPDATE ON 1/5/01 @ 1037 BY PENTECOST TO GOULD * * * THE GENERATOR WAS LOCATED @ 0830MST AT THE FEDEX DENVER FACILITY AND IT IS IN TRANSIT TO THE MEDICAL FACILITY. NOTIFIED REG 4 RDO(JOHNSON) AND NMSS(SMITH) WERE NOTIFIED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0
37647 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2001-01-05 06:20 | 2001-01-05 06:38 | 2001-01-17 | THE MOTOR FOR MS-V-1C HAS BEEN DECLARED INOPERABLE TMI identified a condition that is outside the design basis of the facility at 0620 hours on January 5, 2001. The condition is that MS-V-1C may not be capable of being closed within 120 seconds as described in the bases for Technical Specification 4.8.2 and FSAR Section 10.3. The bases for TS 4.8.2 and FSAR Section 10.3 both state that the valve is capable of being remotely closed within 120 seconds from the Control Room. With the motor inoperable, the valve cannot be remotely closed within 120 seconds. The condition was found during routine surveillance testing and subsequent evaluation. During the surveillance testing the valve is stroke closed 10% and then returned to its normal operation position of full open. The valve stroke closed to the 10% closed position without incident. During the return of the valve to the full open position sparks were observed and a burning odor was present. However, the sparking ceased and the motor successfully traveled to the fail open position (verified by visual observation of the valve stern position). Subsequent visual inspection of the valve and motor, interviews with the technicians, the system engineer and the Electrical Foreman resulted in the declaration of the inoperability of the motor for MS-V-1C. This deficient condition has been documented in the TMI Corrective Action program. Troubleshooting of the motor for MS-V-1C is in progress. Interim action has been taken to provide for the expeditious manual closure of the valve and those actions are contained in an approved plant procedure. The Resident Inspector will be informed. * * * RETRACTION ON 01/17/01 AT 1729ET BY J. SCHORK TAKEN BY MACKINNON * * * Based on additional information gathered during trouble shooting and repair of MS-V-IC conducted on January 5, 2001, subsequent to the submittal of the immediate notification, it was determined that there is reasonable assurance that MS-V-IC would have performed its intended safety function to remotely close from the control room when demanded. Therefore, no condition outside the design basis for the facility existed and the immediate report made on January 5, 2001 is being withdrawn. The basis for the reasonable assurance that the valve would have performed its intended safety function is described below. During the partial stroke surveillance test, the spark and burn smell occurred very briefly while the valve was traveling open. The sparking immediately stopped and the valve continued to travel uninterrupted until it was full open. The surveillance was completed satisfactorily. The breaker for the valve motor did not trip and no fuses were blown. Power remained available to stroke the valve after the event. Based on the short duration of the spark and the fact that the motor continued to operate, there was no reason to believe the stroke time would have changed. Prior to opening or disturbing the motor terminal box, the breaker was manually opened and the resistance from each phase to ground was checked from the breaker. A high voltage Meggar was used to perform the test. The Meggar results showed that neither the power cables, termination, nor motor windings were grounded. This indicated that the motor and cables were in working condition. The motor terminal box was opened without disturbing the power cables inside the box. There was clear evidence that a bare point on one of the ring lug terminations had made contact with the aluminum terminal box. A small portion of a ring connector was bare. There was a burn mark on the ring connector and on the terminal box. A small piece of the aluminum terminal box was missing at the point where the lug would have contacted the box. The as-found gap between what were the contact points was approximately 0.25". Based on this evidence, it was clear that a sharp corner of the ring lug had rubbed against the terminal box until it wore through the insulating tape that was wrapped around the lug. The metal lug then contacted the aluminum terminal box, which temporarily shorted the phase to ground. The resulting spark knocked off a small piece of the terminal box at the contact point creating a gap that immediately cleared the short. The duration of the short was not long enough to cause the breaker to open. Based on the above, there is reasonable certainty that the component would have performed its function when commanded. Therefore, from a past operability perspective, the component was always capable of performing its design basis function. When the component was declared out of service, the plant entered a maintenance evolution to determine and correct the cause of the spark. Entering the maintenance evolution to trouble shoot and correct the cause of the spark was not a condition prohibited by the Technical Specifications. There is no time clock associated with removing the remote closing capability from service for maintenance. NRC Region 1 RDO (Barkley) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37646 | 0 | HOLTEC INTERNATIONAL |  |  |  |  | 2000-10-18 12:00 | 2001-01-04 15:59 | 2001-01-05 | 10 CFR PART 21 NOTIFICATION FOR DISCREPANT WEIGHT OF SPENT FUEL RACKS Spent fuel racks removed from Byron Nuclear Power Plant were discovered to have as-found weights ranging from approximately 8,200 to 10,500 lbs more than the weights used in the analyses supporting the original design and licensing of these racks and in the design of the lifting equipment used to lift the racks. The analyses related to seismic loadings, bearing pad design, spent fuel pool liner fatigue, and possibly others used to design and license these racks may no longer be conservative when the additional weight is considered. The actual impact on these analyses has not, to our knowledge, been evaluated. The impact on the design of the lifting equipment is that the design safety factors for the lifting equipment, while still above 1.0, may not meet the minimum safety factors in NUREG-0612 and associated reference documents. Braidwood Nuclear Station has four similarly designed racks provided by the same supplier. * * * UPDATE ON 1/5/01 @ 0946 BY GUTHERMAN TO GOULD * * * The manufacturer of the spent fuel racks reported in the initial reports was Joseph Oat Co of Camden, NJ. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0
37645 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-12-15 12:00 | 2001-01-04 12:01 | 2001-01-04 | AGREEMENT STATE REPORT ANCORE (previously SAIC) had requested to delete three nuclides from their CA RML. One of the items ANCORE asked to be deleted were fuel rods containing SNM. A letter for additional information concerning transfer/disposal of the fuel rods went out on May 25, 2000 but received no response. Tom Schell contacted the current RSO, David Mahood. Mr. Mahood stated that the fuel rods were sent to Combustion Engineering before he came to ANCORE. Mr. Mahood further added that his questions to the previous RSO failed to produce any new information or documents concerning the fuel rods. Tom Schell also contacted Brian Horn of the US NRC and the US Nuclear Tracking Database confirms the transfer of the three fuel rods to SAIC in San Diego, a different California license, in September 1989. A review of the Compliance and Licensing Folders SAIC's San Diego License (License Number 2290-37) was done but independent confirmation relating to the receipt of fuel rods containing SNM at SAIC in San Diego were not found. A Note: California regulations only require record keeping for three years, however 10 CFR 150.16 appears to have been violated. Personnel of California Radiologic Health Branch were informed. STATE OF CALIFORNIA REPORT NUMBER CA010003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37644 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2001-01-03 15:30 | 2001-01-03 18:27 | 2001-01-03 | PHYSICAL SECURITY REPORT - 1 HOUR The licensee discovered a potential compromise of classified safeguards information and took immediate compensatory measures. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 0
37643 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2001-01-02 17:00 | 2001-01-03 15:03 | 2001-01-03 | NRC BULLETIN 91-01 24 HOUR REPORT The following is quoted from the written report: At 1700, on 1/2/01 The Plant Shift Superintendent (PSS) was notified that the mass of U-235 was incorrectly copied from a Request for Waste Classification (RWC) onto the Waste Consolidation Container Log Sheet and incorrectly independently verified in violation of NCSA.WMO.004. Independent verification of the consolidation drum mass is used to ensure the total mass dose not exceed the 120 gram U-235 limit. The particular drum in question contains less than 15 grams of U-235. [This event actually occurred on 6/21/2000 and was found during a normal review of records on 01/02/2001] The NRC resident inspector has been notified of this event. PGDP Problem Report No. ATRC-01-0024; PGDP event Report No, PAD-2001-001 Event Worksheet Responsible Division: Production Support SAFETY SIGNIFICANCE OF EVENTS: Even though less than 15 grams of U-235 was involved in this incident, independent verification was not properly performed. This type of administrative control is used throughout the PGDP NCS program. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, multiple drums would have to be incorrectly consolidated and the resulting mass contained within the drum would need to exceed 1500 grams of U-235 at an enrichment of 5.5%. (This all was generated onsite and has an enrichment of less than 2.1 %.) CONTROLLED PARAMETERS (MASS, MODERATION GEOMETRY CONCENTRATION ETC): Double contingency for this scenario Is established by implementing two independent controls on mass ESTIMATED AMOUNT, ENRICHMENT FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Less than 15 grams of U~235 at an enrichment of less than 2.1%. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on correctly calculating the cumulative U-235 mass in the consolidation drum to ensure the 120 gram limit is not exceeded. The actual mass was incorrectly copied from the RWC onto the consolidation log sheet, making it impossible to correctly calculate the consolidated mass. Therefore, the control was violated and the first leg of double contingency was lost. The second leg of double contingency is an administrative control to independently verify that the mass was copied correctly and the cumulative mass total is correct. The independent verification did not identify that the incorrect mass was copied. This control was violated and this leg of double contingency was not maintained. Since double contingency is based on two controls on mass, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The area was immediately roped off and posted to control access and prevent the movement of fissile/potentially fissile material within the area. The actual mess of U-235 in the consolidation drum was verified to be less than 15 grams which reestablished control. The waste consolidation container log sheet was corrected and independently verified prior to removing the ropes and postings. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37642 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2001-01-02 15:36 | 2001-01-02 22:05 | 2001-01-03 | AUXILIARY FEEDWATER PUMP AUTOMATIC START The plant sustained a main turbine trip on steam generator high level, cause under review. The turbine trip caused a main feedwater trip which caused an automatic start of the 21 and 23 auxiliary feedwater pumps, as designed. The licensee review of the event determined, later in the evening, that the pump starts were reportable under 10 CFR 50.72(b)(2)(ii). The licensee notified the NRC Resident Inspector. * * * UPDATED AT 1633 EST ON 01/03/2001 BY ROBERT ALLEN TO FANGIE JONES * * * "The following is an update to NRC event report 37642: ESF Actuations "Indian Point Unit 2 sustained inadvertent ESF component actuations following a main turbine trip on high steam generator level that occurred during preparation for admitting steam to roll the main turbine for plant startup. There was no reactor trip nor was one required. The main turbine was latched with the stop valves open and the control valves closed. Steam Generator level control was in manual as is normal at low reactor power levels. A second condensate pump was started which caused an increase in main feedwater pressure which caused increasing steam generator levels. Operator attempts to reduce flow were unsuccessful and a high steam generator level turbine trip signal caused the main turbine stop valves to close (trip) and caused the main feedwater pump to trip. This high level trip signal also resulted in the closing of the main feedwater pump discharge valves (ESF valves), the closing of the steam generator blow down isolation valves (ESF valves) and the starting of the motor driven Auxiliary Feedwater pumps (ESF) as designed." The licensee intends to notify the NRC Resident Inspector. | 5 | 0 | 0 | 6 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37641 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2000-12-31 01:30 | 2000-12-31 06:33 | 2000-12-31 | MANUAL ACTUATION OF CONTAINMENT EMERGENCY COOLER UNITS "On December 31, 2000, at about 0130 PST, containment normal cooler unit ME201 tripped on indicated high temperature (cause under investigation). During preparations to start the opposite train containment normal cooler Unit (ME202), in response to the expected slow increase in containment temperature, Operators manually started the 4 containment emergency cooler units (an engineered safety features system). At about 0220 PST Operators started normal cooler unit ME202 and stopped the 4 ECUs. Consistent with the guidance provided in NUREG-1022, Rev 1, SCE is reporting this occurrence in accordance with 10CFR50.72(b)(2)(ii) for a manual start of an ESF component. "At the time of this occurrence Unit 2 was operating at about 100% power, Unit 3 was operating at about 85% power; and Unit 1 remains permanently defueled. SCE will notify the NRC resident inspectors about this occurrence and will provide them a copy of this report." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37640 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-12-30 12:20 | 2000-12-30 17:05 | 2000-12-30 | 24-HOUR REPORT REGARDING ACTIVATION OF SMOKE HEADS "At approximately 1220 hours on 12/30/00, a process operator was conducting weekly valve status checks on the cell floor above the extended range products station when three CADP smoke heads alarmed. The operator did see a visible haze and smell HF as he immediately left the area. 'See and flee' emergency procedures were immediately implemented. The affected ERP withdrawal station was in an applicable TSR mode (withdrawal) at the time of the alarm. Results of all surveys performed for airborne HF and radiation were less than MDA. At 1324 hours an 'all clear' was granted on emergency response. PORTS is reporting this alarm as a valid actuation of a 'Q' safety system, which is the CADP smokehead." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37639 | 0 | CT RESOURCE RECOVERY AUTHORITY |  |  |  |  | 2000-12-29 19:00 | 2000-12-30 01:49 | 2000-12-30 | EXPLOSION AT WASTE PROCESSING FACILITY INVOLVING LICENSED GAUGE AT APPROXIMATELY 1900EST ON 12/29/00 AN EXPLOSION OCCURRED IN THE PRIMARY SHREDDER WHICH IS ATTACHED TO THE BAGHOUSE AT THE CONNECTICUT RESOURCE RECOVERY AUTHORITY (CRRA), MID-CONNECTICUT PROJECT WASTE PROCESSING FACILITY. THE BAGHOUSE CONTAINS A LICENSED NUCLEAR GAUGE CONTAINING A Cs-137 SOURCE USED TO MONITOR AIRBORNE PARTICLES TO ALERT OPERATORS OF TRASH (DUST) BUILDUP. THE LICENSEE CONFIRMED USING A GEIGER COUNTER THAT THE SOURCE AND HOUSING WERE NOT DAMAGED. THE LICENSEE NOTIFIED THE CT DEPARTMENT OF ENVIRONMENTAL PROTECTION. THE LICENSEE IS MAKING THIS NOTIFICATION AS REQUIRED BY CHAPTER 7, NUCLEAR LEVEL DETECTOR, OF THE METROPOLITAN DISTRICT COMMISSION (MDC) WASTE PROCESS SAFETY MANUAL. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN |  |  |  |  | 0
37638 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-12-29 21:31 | 2000-12-29 22:03 | 2000-12-29 | EMERGENCY NOTIFICATION SPEAKERS INOPERABLE The licensee reported that the emergency notification speakers in New London, CT could not be operated from either the primary nor the secondary locations. The municipality had planned to use the speakers to provide information regarding an impending winter storm. The problem was traced to faulty wiring and has been repaired. The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37637 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2000-12-28 07:41 | 2000-12-28 12:21 | 2001-01-05 | CONTROL BUILDING VENTILATION ISOLATION "At 0741 CST the Control Building Emergency Filtration System automatically initiated on a Control Building Intake Gas High Activity alarm. The cause of the Gas High Activity alarm is under investigation." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE ON 12/29/00, 0024 ET BY MYERS TAKEN BY MACKINNON * * * During the day, trouble shooting was performed to determine the source of the actuation at 0741 CST today. Surveillance Procedure 6.PRM.317, CONTROL ROOM AIR SAMPLING SYSTEM ELECTRONIC CALIBRATION, was performed, and all indications were within specification. A source check of the gaseous channel was also performed per Instrument Operating Procedure 4.17, and the response of the monitor was normal. Air sampling was conducted, and no indications of abnormal radiation were identified. The Control Room Emergency Filtration System was returned to the standby lineup. At 1933, the Control Room Emergency Filtration System again initiated on a high gaseous activity signal. All equipment functioned as required. The Control Building Ventilation Radiation Monitor has been declared inoperable, and the Control Room Emergency Filtration System remains in service, aligned in the accident mode. The NRC Resident Inspector was notified. Note: The Control Building Ventilation Radiation Monitor consists of three channels, with two required to be operable. The Iodine channel is also presently inoperable. The actuation logic requires only one channel of the three to initiate Control Room Isolation and start the Emergency Booster (pressurization) fan. Noble gas sample was taken at 2142 CST. All readings were normal. NRC R4DO (C. Marschall) notified. * * * UPDATE ON 1/5/01 @ 1113 BY VAN DER KAMP TO GOULD * * * RETRACTION Event Number 37637 reported a condition at Cooper Nuclear Station (CNS) where the Control Room Emergency Filtration System (CREPS) automatically initiated on a Control Building Intake Gas High Activity alarm. Surveillance testing found no abnormalities with the system and air sampling found no indications of abnormal radiation levels. A subsequent identical event occurred later the same day and was reported to the NRC Operations Center in an update. Subsequent troubleshooting has found a solder connection, that connects gas monitor components to ground, had come apart. Discussions with the manufacturer of the monitor confirm that the loss of ground can cause spiking in the displayed background reading. CNS investigation has found that the initiation of the CREPS was due to an invalid signal, i.e., not due to an actual elevated radioactive concentration. Per 10CFR50.72(b)(2)(ii), invalid actuations of CREFS are not required to be reported and EN 37637 is retracted. The NRC Resident Inspector will be notified of this event by the licensee. The Reg 4 RDO(Johnson) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37636 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2000-12-27 13:30 | 2000-12-27 18:03 | 2001-01-22 | HIGH PRESSURE CORE INJECTION (HPCI) SYSTEM DISCOVERED INOPERABLE "On 12/27/00 at 1330 hours QCOS 2300-09 (U-1 HPCI Vent Verification) was in progress following QCOS 2300-11 (CCST/Torus Level Switch Functional Testing). During the process of vent verification of the U-1 HPCI system, the vent valves were open approximately 6.5 minutes prior to receiving water through the vent lines; the U-1 HPCI system was found inoperable. Performance acceptance criteria of QCOS 2300-09 states that venting times >40 seconds could he construed as a preconditioning action per NRC IN 97-16 and as such the U-1 HPCI system possibly could not have performed its' safety function prior to the venting that took place on 12/27/00 at 1330. The last successful vent of the U-1 HPCI system was completed on 11/30/00. An investigation is underway to try to determine the time of the loss of fill and the cause. This 4-hour ENS notification is being made in accordance with 10 CFR 50.72(b)(2)(iii)(D)." The licensee notified the NRC Resident Inspector. * * * UPDATE 2052EST ON 1/22/01 FROM MIKE MacLENNAN TO S. SANDIN * * * The licensee is retracting this report based on the following: "This is a retraction of the ENS call made on 12/27/00, event #37636, concerning the inoperability of the Unit One HPCI system due to an inadequate fill and vent of the pump discharge line. "We have completed our evaluation and have determined that HPCI would have successfully injected coolant to the reactor if the system was initiated in response to a LOCA." The licensee informed the NRC resident inspector. Notified R3DO(Creed). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37635 | 0 | NC DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-12-27 14:20 | 2000-12-27 15:52 | 2000-12-27 | DELIVERY VEHICLE WRECK WHILE CARRYING RADIOACTIVE MATERIAL, NO CONTAMINATION On 12/22/00 a Courier Dispatch was involved in an accident while transporting a Mo-99 generator, incident number ICD-00-47. The accident occurred in Monroe, NC at the intersection of highways 116 and 74, about a half mile from the delivery point, Union Regional Med Center Nuc Med. The Radiation Safety Officer (RSO) went to the scene and made a determination of no contamination on the driver, vehicle, or package outside. The package, no apparent damage, was transferred to Union Regional Med Center Nuc Med. There was no other radioactive material in the transport. The incident has been closed and a written report to the NRC will follow. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0
37634 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-12-27 10:31 | 2000-12-27 12:47 | 2001-04-03 | REACTOR CORE ISOLATION COOLING SYSTEM (RCIC) DECLARED INOPERABLE The licensee was performing the procedure to reset the RCIC isolation, after a surveillance was completed, when the closed inboard steam isolation valve (MO-1301-16) went to dual indication while opening the outboard steam isolation valve (MO-1301-17). Both steam isolation valves to the RCIC turbine were closed and the RCIC system was declared inoperable. The licensee is investigating the problem. Active limiting conditions for operation were entered for the RCIC system and the primary containment isolation function of the RCIC inboard steam isolation valve (MO-1301-16). The licensee notified the NRC Resident Inspector. * * * RETRACTED AT 1414 EDT ON 4/3/01 BY ERIC OLSON TO FANGIE JONES * * * The licensee is retracting this event notification. The following was submitted as the basis for the retraction. "On December 27, 2000, the RCIC system was taken out of service to perform routine surveillance in accordance with PNPS procedures 8.M.2-2.6.1 and 8.M.2-2.6.4. After resetting the RCIC isolation after performance of the High Steam Flow surveillance, operations personnel opened valve, MO-1301-17. Approximately 5 seconds into the opening stroke, MO-1301-16, the inboard isolation valve, gave dual indication. During the initial opening of the MO-1301-17 valve, the RCIC turbine inlet steam line began to pressurize due to trapped pressure between the MO-1301-16 and MO-1301-17 valves and increased to approximately 437 psig when it began to decrease at about one pound per two seconds. The Control Room operator then gave MO-1301-16 valve a closed signal after the valve indicated dual indication for 16 seconds and the valve then indicated full closed. The steam line continued to depressurize at the same rate until operations closed the MO-1301-17 valve. This indicated that although MO-1301-16 showed dual Indication, it was closed and the seating surfaces were tight and the containment isolation function was operable. "The test that was being performed was testing the primary containment isolation system (PCIS) and this surveillance was satisfactory with both inboard and outboard isolation valves closing upon initiation. Additionally, MO-1301-16 was stroke timed in accordance with PNPS procedure 8.5.5.4 and the times were within the expected limits. "After the initial indication of leakage, the Control Room management conservatively declared MO-1301-16 and the RCIC system inoperable until further investigation could be performed. Troubleshooting was conducted in accordance with PNPS procedure 3.M.1-34. The conclusion was that while dual indication had occurred, the valve had been closed and primary containment isolation was operable. "For (a)(2)(i) (B): not reportable. The initial indication of leakage through containment Isolation valve MO-1301-16 was evaluated. The source of the pressure was steam trapped between the isolation valves during the previous testing. The valve was subsequently determined to have been closed and containment isolation was maintained. "For (a)(2)(v): not reportable. There was no component or system failure. The containment isolation function was maintained. "For (a)(2)(vii): not reportable. It was determined that there was no component or system failure. The containment isolation function was maintained. "Please note that RCIC was 'made' inoperable by closing the referenced motor-operated valves (MO-1301-16 and MO-1301-17) to perform their primary containment isolation function in accordance with Technical Specification 3/4.7.A.2. After the operability determination, the valves were opened and RCIC was again operable per TS 3/4.5.D." The licensee notified the NRC Resident Inspector. The R1DO (Jack McFadden) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | LICENSEE 24 HR REPORT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37633 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-12-26 08:47 | 2000-12-26 09:21 | 2000-12-26 | STATE AGENCY NOTIFIED OF INJURED SEA TURTLE FOUND IN THE INTAKE CANAL "At approximately 0847 on 12/26/00, a notification was made to the Florida Fish and Wildlife Conservation Commission regarding an injured sea turtle found in the plant's intake canal. The turtle will be sent out for rehabilitation." The licensee notified both the state and NRC resident inspector. * * * UPDATE 1032EST ON 12/26/00 FROM DAVID ALBRITTON TO S. SANDIN * * * The Florida Fish and Wildlife Conservation Commission was informed that a second injured sea turtle was found in the intake canal. The licensee notified both the state and NRC resident inspector. Notified R2DO(Ernstes). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37632 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-12-23 06:15 | 2000-12-23 15:02 | 2000-12-23 | FACILITY HAS PROBLEMS WITH FREEZING STANDPIPES THAT SUPPLY WATER TO THEIR HIGH PRESSURE FIRE WATER SYSTEMS. During a discussion between the Paducah and Portsmouth Plant Shift Superintendents (PSS), the Portsmouth PSS stated that their facility was having a problem with the standpipes freezing that supply water to their High Pressure Fire Water (HPFW) systems. Following this discussion, the Paducah PSS instructed all building managers containing HPFW systems to check the temperatures of the standpipes. Following this temperature survey, two systems in the C-337 building were discovered to have abnormally low temperatures. In order to verify operability, Fire Services personnel performed flow tests on these two systems. During this testing, it was discovered that the standpipe for HPFW system D-2 was frozen, and the system could not perform its specified safety function. The High Pressure Fire Water System is required to be operable according to TSR 2.4.4.5. HPFW system D-2 was declared inoperable at 0615 on 12-23-00, and a fire patrol was initiated as required by the TSR. During follow up investigation, it was discovered that six of the eight exhaust fans and a section of recirculating louvers that supply heat to this area were not functioning. The NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
37631 | -1 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-12-22 12:25 | 2000-12-22 16:54 | 2000-12-23 | PLANT ENTERED 14 DAY LCO DUE TO HIGH PRESSURE COOLANT INJECTION BEING INOPERABLE HPCI was declared inoperable after failing testing. During the performance of 2-SI-3.5.1.7 HPCI MAIN AND BOOSTER PUMP SET DEVELOPED HEAD AND FLOW RATE TEST AT RATED REACTOR PRESSURE, the HPCI system could not be verified to be vented. The probable reason for not being able to make this verification is due to a faulty flow gauge in the HPCI piping system. The NRC Resident Inspector will be notified. * * * RETRACTED AT 0240 EST 0N 12/23/00 BY MICKEY HUNTER TO FANGIE JONES * * * "The 4 hour report made in accordance with 10CFR50.72.b.2.iii at 1630 on 12/22/2000 is being retracted for the following reasons: During the performance of 2-SR-3.5.1.7 HPCI MAIN AND BOOSTER PUMP SET DEVELOPED HEAD AND FLOW RATE TEST AT RATED REACTOR PRESSURE, there were indications of flow through the vent line during initial Surveillance testing however; the test methodology used in the Surveillance could not verify that flow. We revised the Surveillance methodology to prescribe an alternate process of determining flow. The Surveillance test was reperformed satisfactorily and verified indications of flow that was observed in the previous performance of the Surveillance test. Thus this proved operability of HPCI during previous performance of Surveillance test." The licensee notified the NRC Resident Inspector. The R2DO (Mike Ernstses) was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iii)(A) |  |  |  | 0
37630 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2000-12-22 09:45 | 2000-12-22 11:29 | 2001-02-19 | LOSS OF POWER TO THE TECHNICAL SUPPORT CENTER (TSC) Breaker 13-40 tripped with the ground flag dropped. This breaker supplies primary power to the TSC. There is a backup diesel generator available to supply power to the TSC but will not be energized until it is determined that there is no ground at the TSC. Once the TSC D/G is energized the facility will once again be available. The licensee notified the NRC resident inspector. * * * Update at 1150 on 12/22/00 by Hubbard received by Weaver * * * The diesel generator is now supplying the TSC with electrical power (as of 1041 CST). Investigation continues into why breaker 13-40 tripped. Notified the R4DO(Jones). * * * RETRACTED AT 1309 EST ON 2/19/01 BY CHRIS REEKIE TO FANGIE JONES * * * The licensee is retracting this event. Upon review of the potential loss of emergency communications and assessment capability they have determined that no such loss would have happened with the initial problem. The licensee notified the NRC Resident Inspector. The R4DO (Greg Pick) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37629 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-12-21 11:50 | 2000-12-21 12:19 | 2000-12-21 | PLANT DECLARED AN UNUSUAL EVENT AT 1150 EST DUE TO AN INADVERTENT CARBON DIOXIDE DISCHARGE An inadvertent (personnel error) discharge in a localized area (switchgear room) of the reactor building occurred. The CO-2 discharge has been stopped, area ventilation is in progress, and all personnel were evacuated and accounted for. The Nine Mile Point 2 Fire Department was activated to help with this problem and is still in the area until the area is ventilated. The NRC Resident Inspector was notified along with the State and local Government and other agencies. * * * UPDATE ON 12/21/00 @ 1646 BY LANGE TO GOULD * * * The NOUE was terminated at 1639 following thorough air sampling of the affected areas to check the oxygen levels. The oxygen levels checked good and the NOUE was terminated. The NRC Resident Inspector was notified along with the State, local and other Government agencies. The HOO notified FEMA(Cegielski), EO(Marsh), RDO(Dimitriadis), IRO(Congel) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37628 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-12-21 10:40 | 2000-12-21 11:52 | 2000-12-21 | UNAVAILABILITY OF THE TECHNICAL SUPPORT CENTER (TSC) DURING MAINTENANCE The following text is a portion of a facsimile received from the licensee: "Qualitative testing results associated with V-FU-17 (TSC-EVS system) prompted the need to replace the associated charcoal filter elements. During the period of filter element replacement, the TSC-EVS system [was] unavailable. As such, the ability to maintain the TSC as an Emergency Response Facility during an event involving a radioactive release is challenged." "This constitutes a condition reportable to the NRC per 10CFR50.72 (degradation of [an] Emergency Response Facility)." Testing is ongoing prior to restoring the TSC to standby mode. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37627 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-12-20 20:08 | 2000-12-20 22:58 | 2001-01-11 | FAILURE OF A REACTOR CORE ISOLATION COOLING (RCIC) BYPASS TO CONDENSATE STORAGE TANK VALVE TO FULLY STROKE DURING STROKE TIME TESTING The following text is a portion of a facsimile received from the licensee: "EVENT: At 2008 on 12/20/00 during performance of OPT-10.1.8 (RCIC System Valve Operability Test), the 2-E51-F022 (RCIC bypass to condensate storage tank) failed to fully stroke during stroke timing of the valve. A valve thermal overload annunciator was received. This rendered the Brunswick Unit 2 RCIC system inoperable. RCIC was not in operation at the time of this failure." "INITIAL SAFETY SIGNIFICANCE EVALUATION: Minimal safety significance. Remaining ECCS systems are operable." "CORRECTIVE ACTION(S): Determine the cause of the 2-E51-F022 valve failure. Return the Unit 2 RCIC system to operable following repair of 2-E51-F022." The licensee stated that this event did not result in any radiological release or reactor coolant leaks. The licensee also stated that all systems functioned as required and that there was nothing unusual or misunderstood. This event placed the unit in a 14-day technical specification limiting condition for operation. The licensee notified the NRC resident inspector. * * * RETRACTION ON 01/11/01 AT 1059ET BY CHARLES ELBERFELD TAKEN BY MACKINNON* * * Upon further evaluation, it has been determined that the conditions resulting in the RCIC system being declared inoperable for Technical Specification LCO 3.5.3 did not result in a loss of the system's function to remove residual heat. The function of the RCIC system is to respond to transient events by providing makeup coolant to the reactor. The RCIC system is not an Engineered Safety Feature system, and no credit is taken in the Updated Final Safety Analysis Report (UFSAR) for RCIC system operation mitigating the consequences of a postulated accident. The RCIC system is designed to operate either automatically or manually following reactor pressure vessel (RPV) isolation accompanied by a loss of normal coolant flow from the reactor feedwater system to provide adequate core cooling and control of the RPV water level. Its operational purpose is to provide an alternate source of reactor coolant to the vessel and to provide sufficient cooling to remove residual heat following reactor shutdown and loss of feedwater flow without requiring depressurization of the reactor. Neither the 2-E51-F022 being de-energized in the open position, nor the questionable capability of the 2-E51-F029 resulted in the loss of the ability of the RCIC system to remove residual heat. In the case of the RCIC Bypass to Condensate Storage Tank valve 2-E51-F022, with the valve de-energized in the open position, injection flow into the RPV is not diverted to the Condensate Storage Tank, or into the High Pressure Coolant Injection system due to additional closed valves in the test flow path. Therefore, if the RCIC system had been called upon to perform its needed function to remove residual heat, the system would have performed as required. In the case of the RCIC Torus Suction valve 2-E51-F029, although the ability for the RCIC system sump suction to align to the Torus must be available to meet its Technical Specification LCO Operability requirements, the RCIC system has the capacity to meet its function to remove residual heat when aligned to the Condensate Storage Tank. Although the RCIC system is a single train injection system, it has redundant suction flow paths that are fully capable of meeting these injection requirements. Loss of one suction flow path does not prevent the RCIC system from performing its required function to remove residual heat. Subsequently, it has been determined that the malfunction of the RCIC system components did not adversely impact that system function to remove residual heat. Carolina Power and Light Company has determined that this event does not meet 10 CFR 50.72 or 10 CFR 50.73 reporting criteria and this notification is being retracted. NRC R2DO (Chuck Ogle) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37626 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2000-12-20 20:14 | 2000-12-20 22:25 | 2001-01-12 | AUTOMATIC CONTROL ROOM VENTILATION SYSTEM SHIFT FROM NORMAL TO EMERGENCY RECIRCULATION MODE WHILE A PLANNED GAS DECAY TANK RELEASE WAS IN PROGRESS The following text is a portion of a facsimile received from the licensee: "At 2014, with a gas decay tank release in progress (total activity 0.215 Ci, (Kr-85 = 0.214 Ci, Xe-133 = 0.001 Ci)), control room ventilation gas monitor R-36 went into alarm causing ventilation to shift to mode F. During the [2-second] spike, R-36 counts went from 30 cpm to 856 cpm and back to 30 cpm. Local air samples taken by the RP Tech both in the control room and in the area of the control room ventilation intake revealed no activity." The licensee stated that the gas decay tank release was planned and that the counts going through the plant stack were considered normal. (These counts peaked at 120 cpm.) The licensee stated that the planned gas decay tank release was within both the expected and required release limits. The wind was blowing in a favorable direction, and the stability class for meteorological conditions was stable. Although counts have returned to normal, the licensee plans to leave control room ventilation in the emergency recirculation mode until tomorrow morning. The licensee notified the NRC resident inspector. * * * UPDATE ON 1/12/01 @ 1113 BY GOMEZ TO GOULD * * * RETRACTION Rochester Gas and Electric (RG&E) is retracting this notification. This event was originally thought to be in response to a valid radiological condition because a waste gas decay tank release was in progress at the same time as this event. RG&E has confirmed that the alarm on Control Room Noble Gas radiation monitor R-36 that occurred at 20:14 EST on December 20, 2000, causing the shift in Control Room ventilation to "Mode F" (emergency recirculation mode), was the result of a spurious spike on R-36. The alarm was not in response to any radiation condition, Local samples taken by radiation protection technicians on December 20, both in the Control Room and in the area of the Control Room ventilation intake, revealed no activity. The Plant Process Computer (PPCS) plots show that R-36 counts were steady just before and immediately after the spike. Further engineering evaluation of this event has determined that the alarm on R-36 was caused by a sudden spike and was not in response to any radiation condition. Therefore, this event is not reportable and is retracted. Other occurrences of spiking on R-36 took place during December 2000 and January 2001. Some of these spikes resulted in alarms on R-36 and subsequent shift in Control Room ventilation to "Mode F". These alarms were recognized at the time of alarm as invalid actuations of the HVAC System for the Control Room, and did not result in NRC notification. Trouble-shooting and corrective maintenance is on-going on the R-36 monitor. The licensee has notified the NRC Resident Inspector. The Region 1 RDO (Lew) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37625 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-12-20 13:05 | 2000-12-20 19:04 | 2000-12-20 | NRC BULLETIN 91-01 RESPONSE (24-HOUR REPORT) - LOSS OF ONE CONTROL IN THE DOUBLE CONTINGENCY The following text is a portion of a facsimile received from the Paducah personnel: "The C-331 E and F surge drum room temperature was found to be at 103 degrees F in violation of NCSA.CAS-005. Requirement 3.2.6 of this NCSA states that when the surge drums contain UF6, they shall be operated at a minimum temperature of 105 degrees F. This temperature requirement prevents hydrogen fluoride (HF) from condensing at the maximum pressure rating of the drums. Should HF condense it could moderate any UF6 that might be present." "SAFETY SIGNIFICANCE OF EVENTS:" "HF cannot condense at 103 degrees F and 20 psia. The drum pressures were all less than 1 psia; therefore, it was not possible to condense HF." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR:" "In order for a criticality to be possible, HF would have to condense. Therefore, the temperature of the drums would have to be less than 80 degrees F, and the drum pressures would have to exceed 20 psia." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.):" "[Since the double] contingency is based on two controls on moderation and [since] the temperature control was lost, double contingency was not maintained." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS):" "The surge drums contain an estimated 1425 pounds of UF6 at less than 1 weight % U235 assay." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES:" "The first leg of double contingency is an administrative control, which limits the surge drum room temperature to a minimum of 105 degrees F. The control was violated, and the first leg of double contingency was lost." "The second leg of double contingency is an administrative control to maintain the drum pressures below 20 psia, which is the maximum rated pressure for the drums. This control was not violated, and this leg of double contingency was maintained." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED:" "Temperature loss was due to low outside ambient temperature. Building temperature was raised and surge drum room temperature rose above minimum required temperature. Additional heating for the area is being considered." Paducah personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37624 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-12-20 08:55 | 2000-12-20 18:01 | 2000-12-20 | FITNESS-FOR-DUTY REPORT REGARDING A NON-LICENSED SUPERVISOR'S RANDOM POSITIVE TEST FOR ALCOHOL A non-licensed supervisor tested positive for alcohol during a random test. This was a first time positive test for this individual. The individual was removed from site, and the individual's badge was placed on administrative hold. The licensee made this 24-hour event notification in accordance with 10 CFR 26.73(a)(2)(iv). The licensee notified the NRC resident inspector. | 2 | 100 | 0 | 0 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Startup | Power Operation |  | Startup | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0
37623 | 0 | SOUTHEAST MO STATE UNIVERSITY |  |  |  |  | 2000-12-19 13:30 | 2000-12-20 13:52 | 2000-12-21 | LOST STRONTIUM-90 SOURCE The school has lost a 20-mCi Sr-90 sealed source. It is unknown how long it has been missing. A search of physical areas and records have been unsuccessful in locating the source. As long as the source remains sealed it presents little of no threat to the public. The source was used as part of an ionization cell for an ion capture detector. The equipment was sold sometime back at auction. The paperwork for the equipment does not indicate that the source was included in the sale. The school has been in contact with NRC Region 3 (Kevin Null). ***** UPDATE AT 1151 EST ON 12/21/00 FROM CHRIS McGOWEN TO LEIGH TROCINE ***** A Southeast Missouri State University representative called to provide corrected/clarifying information. There is a possibility that the equipment was previously sold at auction, but the licensee does not know exactly what happened to it. In addition, the source was used as part of an ionization cell for an ion capture detector on a gas chromatograph. The NRC operations officer notified the R3DO (Kozak) and NMSS EO (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37622 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2000-12-20 10:35 | 2000-12-20 11:37 | 2000-12-20 | OFFSITE NOTIFICATION TO STATE DEP DUE TO OIL SPILL ON SITE The licensee notified the Connecticut Department of Environmental Protection (DEP) about an oil spill due to operator error. The waste oil separator was in operation filling a 55-gallon drum when the operator overflowed the drum. The spill was contained on the concrete pad, there was no release offsite or to the water. Cleanup is now in progress. The licensee notified NRC Region 1 (John Wray). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37621 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-12-20 04:17 | 2000-12-20 06:31 | 2000-12-20 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP CAUSED BY TRANSFORMER GROUND The apparent cause of the reactor trip was a turbine trip caused by a ground overcurrent relay actuation on the 2X01 transformer (main power out transformer). Heat removal is via the steam dumps to the main condenser with main feedwater supplying the steam generators. All systems operated as required. The licensee is investigating the cause of the ground indication. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 63 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37620 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-12-19 13:40 | 2000-12-19 17:05 | 2000-12-19 | UNPLANNED CLOSURE OF STEAM GENERATOR BLOWDOWN ISOLATION VALVES DURING FUNCTIONAL TESTING OF A STEAM GENERATOR BLOWDOWN TANK LEVEL CONTROL VALVE AND ITS ASSOCIATED SOLENOID VALVE The following text is a portion of a facsimile received from the licensee: "Instrumentation and control personnel were functionally testing the steam generator blowdown tank level control valve, BT-106, and its associated solenoid valve, SV-33029. A non-ESF temperature switch, TS-16218, was manually actuated to test SV-33029. This resulted in an unplanned closure of steam generator blowdown isolation valves BT-2A/MV-32077 and BT-3B/MV-32080. These valves have containment isolation functions for a steam line break inside containment and are also required to close on auxiliary feedwater system actuation." The licensee stated that all systems functioned as required and that there was nothing unusual or misunderstood. The licensee also stated that this event did not place the unit in a technical specification limiting condition for operation. The steam generator blowdown isolation valves have been returned to their normal configuration. The licensee notified the NRC resident inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37619 | 0 | OCONEE |  | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-12-19 13:52 | 2000-12-19 14:55 | 2000-12-19 | INITIATION OF A TECHNICAL SPECIFICATION (TS) REQUIRED SHUTDOWN DUE TO BOTH TRAINS OF THE CONTROL ROOM VENTILATION SYSTEM BEING DECLARED INOPERABLE The following text is a portion of a facsimile received from the licensee: "At 1305 on 12/19/00 during Low Pressure Service Water (LPSW) testing on Unit 1, an alarm was received on the operating 'A' Control Room Ventilation System chiller. Upon investigation, it was determined that the 'A' chiller had tripped due to a loss of service water flow to the chiller condenser. The chiller service water pumps take suction from a Condenser Cooling Water (CCW) line, which also supplies suction to the LPSW pumps. The LPSW testing was aborted, and a normal alignment for CCW was completed. Several attempts were made by Operations and Maintenance to restart the 'A' chiller with no success. An attempt was then made to start the 'B' chiller, and it also tripped. At 1352, the [Operations Shift Manager (OSM)] determined that no chillers were operable and declared both trains of Control Room Ventilation System inoperable. [TS Limiting Condition for Operation (LCO)] 3.0.3 was entered at 1352 on [Units] 2 and 3 per [TS] 3.7.16." "At [1452] hours, Operations began a controlled shutdown of both Units 2 and 3. Units 2 and 3 were operating at 100% power in Mode 1 at the start of the event. Unit 1 was in Mode 6 as part of a refueling outage." "The temperature in the shared Unit 1 and 2 Control Room is currently 75°F. Actions have been taken to restore service water to one of the chillers. One chiller is currently in operation but [has] not yet been declared operable." The licensee stated that the 'A' and 'B' chillers supply the control room ventilation system for all three units. Units 1 and 2 share a common control room. Unit 3 is located in a separate control room, but it is served by the same chilled water system and chillers. The licensee also stated that the TS LCO requires that at least one control room ventilation system train be returned to service or that the units be placed in Mode 3 within 12 hours. The licensee anticipates exiting this LCO within the required time frame. The licensee notified the NRC resident inspector. ***** UPDATE AT 1609 ON 12/19/00 FROM RANDY TODD TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "At 1455 on 12/19/00, Oconee Nuclear Station reported initiation of a shutdown required by [TS] 3.7.16 which invokes TS 3.0.3. The TS affected both Units 2 and 3." "This shutdown was due to loss of both chillers associated with the chilled water system that serves the Control Room Ventilation System. Units 2 and 3 began reducing power from 100% in Mode 1 at 1452 (not 1352 as initially reported)." "Following the initial notification, the NRC residents were informed." "At 1521, the 'B' chiller was declared operable, allowing Units 2 and 3 to exit TS 3.0.3 and to stop power reduction at approximately 99%." "An investigation into the cause of the chiller trips is continuing." "Unit 1 was in Mode 6 for a refueling outage and was not in the mode of applicability for TS 3.7.16." The licensee stated that power ascension was commenced at 1521 and that the Units 2 and 3 are currently operating at 100% power. The NRC operations officer notified the R2DO (Mike Ernstes). | 0 | 99 | 99 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37618 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2000-12-19 11:05 | 2000-12-19 13:59 | 2000-12-19 | OFFSITE NOTIFICATION REGARDING A 1/2-GALLON HYDRAULIC FLUID SPILL INSIDE THE OWNER CONTROLLER AREA At 1105 on 12/19/00, a hydraulic line on demolition equipment broke due to a mechanical failure resulting in approximately 1/2 gallon of hydraulic fluid spilling to the ground. The equipment was sitting on top of a 5-foot high mound of rubblized concrete. Therefore, the hydraulic fluid actually spilled onto the concrete, but it was reported as being the ground because the hydraulic fluid had the potential to get to the ground. The applicable area has been covered, and absorbent material has been placed around the area. Decommissioning personnel currently plan to dig out the area of rubblized concrete and place it in a metal shipping container. The rubblized concrete was part of the previous containment that had been removed. There were no reports of contamination, and there were no liquid or gaseous releases involved. The licensee notified the State of Connecticut at 1350 on 12/19/00. The licensee also notified the NRC Region 1 office (John Wray and Maria Miller). At this time, it is not known whether or not a press release will be issued. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37617 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2000-12-18 16:00 | 2000-12-19 11:29 | 2000-12-19 | AGREEMENT STATE REPORT A sprinkler actuation in a high bay at the GTS Duratek facility caused radioactive contamination (low levels of Co-60) to be spread throughout a decontamination facility and outside the building onto ground within the owner controlled property. The facility was being used to decontaminate some used steam generators. The state reported that a storm drain is located outside of the building, but that the licensee was able to cover the drain in time to block any flow. The state of Tennessee is continuing their investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
37616 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-12-18 18:45 | 2000-12-18 21:00 | 2000-12-18 | AUTOMATIC REACTOR SCRAM ON REACTOR PRESSURE VESSEL (RPV) LOW LEVEL 3 WHILE THE UNIT WAS IN HOT SHUTDOWN (Refer to event #37614 for details regarding a previous reactor scram.) The following text is a portion of a facsimile received from the licensee: "At 1845 CST, the plant was in Mode 3 with the scram reset. Roughly 5 hours earlier the plant had experienced a scram upon a Group 1 isolation. While re-opening the MSIVs to re-establish the main condenser as the heat sink and transfer pressure control, the plant experienced an RPV Low Level 3 and scrammed." "The MSIVs are now open, the scram reset, and level and pressure are stable." The licensee stated that RPV Low Level 3 occurs at +8.9 inches narrow range. It was reported that the unit experienced a problem with the procedure which delayed opening of the MSIVs. As pressure creeped up which caused the pumps that were feeding the vessel to feed less. Therefore, level started creeping down as pressure started creeping up. It is not believed that level went much below RPV Low Level 3 because water would have been injected as a result of the scram. The licensee stated that there were no engineered safety feature actuations or emergency core cooling injections and that none were required. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37615 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-12-18 14:36 | 2000-12-18 19:30 | 2000-12-18 | TRIP OF A RECIRCULATION PUMP DUE TO LOSS OF A SUPPORT SYSTEM FOLLOWING LOAD SHEDDING FROM AN ESSENTIAL BUS The following text is a portion of a facsimile received from the licensee: "During surveillance testing of the Division I undervoltage logic, a step was performed out of sequence. This resulted in load shedding from the Division I essential bus. Undervoltage actuations occurred as expected including a trip of one reactor [recirculation] pump. Plant operation was stabilized in single loop operation with recovery planning in progress." The licensee stated that the unit was operating at 100% power prior to the event and that it is currently operating at 65% power (in single loop operation). It was reported that the trip of the recirculation pump was not the direct result of the undervoltage condition. It actually occurred due to the loss of a support system because the load shedding resulted in a loss of power to an oil pump that supplied the recirculation pump. All systems functioned as expected, and there was nothing unusual or misunderstood. The licensee notified the NRC resident inspector. | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37614 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-12-18 13:29 | 2000-12-18 15:58 | 2000-12-19 | AUTOMATIC REACTOR SCRAM DUE TO ISOLATION OF THE MAIN STEAM ISOLATION VALVES DURING THE PERFORMANCE OF MAINTENANCE/SURVEILLANCE (Refer to event #37616 for details regarding an additional reactor scram.) The following text is a portion of a facsimile received from the licensee: "At 1329 CST, the plant experienced an isolation of the Main Steam Isolation Valves [(MSIV)] which subsequently initiated an automatic reactor SCRAM. The [MSIV] Closure was part of a Group I isolation which is believed to be caused by performance of a maintenance surveillance on the Main Steam Line Tunnel Leak Detection System." "The plant is stable, and there were no other abnormal occurrences in conjunction with this event." "Since closure of the [MSIV] is an actuation of the Reactor Protection System, this condition is being reported pursuant to 10CFR50.72(b)(2)(ii)." The licensee stated that all control rods fully inserted due to the reactor scram and that the reactor core cooling isolation system was manually actuated and secured during this event. There were no emergency core cooling systems actuations, and none were required. The licensee's investigation is currently ongoing. The licensee also stated that water is currently being supplied to the reactor vessel via normal condensate and feedwater and that safety relief valves are being utilized for pressure control. Containment parameters were reported to be normal, and offsite power is available. The emergency core cooling systems are also available if required. The licensee notified the NRC resident inspector and the State. ***** UPDATE AT 1357 EST ON 12/19/00 FROM DALE SHELTON TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "This is an Update to [...] provide current status of investigation and repairs." "Investigation into this event has determined that the cause of the MSIV isolation was performance of a Channel Functional Test of the Division 2 Main Steam Line Tunnel Ambient Temperature channel at the same time that an unidentified failure of a Digital Signal Conditioning (DSC) card in the circuitry for the Division 1 Main Steam Line Tunnel Ambient Temperature channel existed. This resulted in satisfying the 2 out of 4 logic for the MSIV isolation." "Plans are still being developed for repair the DSC card. Although Technical Specifications would allow entry into Mode 2 prior to repair, a decision has not yet been made if the card will be repaired prior to entry into Mode 2. The Facility Review Group will review any repair plans that would be implemented in [Modes] 1 or 2." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Tom Kozak). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37613 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-12-18 06:40 | 2000-12-18 09:52 | 2001-01-11 | CONTAINMENT FAN COOLER UNITS DECLARED INOPERABLE "At 0640 on 12/18/00, '11' service water accumulator was declared inoperable based on water level low out of specification for Technical Specifications. This condition was identified following calibration of the 'B' level device. The service water accumulators support containment integrity by ensuring the containment fan coils remain properly filled during a design basis accident. Tech Spec 3.6.1.1 and Tech Spec 3.6.2.3 were entered for containment integrity and '11' and '12' containment fan coil unit inoperability. Actions were taken within one hour to comply with containment integrity Tech Spec. The service water accumulator was filled to within specification at 0713 at which time Tech Spec 3.6.1.1 was exited. The '11' and '12' containment fan coil units were restored to operable at 0744 and Tech Spec 3.6.2.3 was exited. Actions are underway to calibrate the 'A' channel of level indication. All power plant parameters remained stable throughout the event and no other safety systems were affected." The NRC resident inspector will be informed of this notification by the licensee. * * * UPDATE 1312EST ON 1/11/01 FROM BENSON BINGGELI TO S. SANDIN * * * The licensee is retracting this report based on the following: "On December 18, 2000, a four-hour report was made for Salem Unit 1 in accordance with 10CFR50.72(B) (2) (iii) due to the water level for the 11 Service Water accumulator being out of specification low based on readings from the 'B' level device. The service water accumulators support containment integrity by ensuring the containment fan coils remain properly filled during a design basis accident. "There are two level devices, 'A' and 'B', associated with each SW accumulator. During the time that the 'B' level device indicated that the SW accumulator was out of specification, the 'A' level device continued to show that the accumulator level was within the required level specification. "Following the calibration of the 'B' level device which showed that level on the 'B' channel was reading low out of specification, M&TE equipment (differential pressure gauge) was connected to the 11 SW accumulator to provide an independent reading of the tank level. The M&TE equipment confirmed that the 11 SW accumulator level was within 0.5 inches of the level indicated by the 'A' level device. Based on this confirmation, the 'A' level device on the 11 SW accumulator is providing an accurate indication of level in the tank. "Since the 'A' level device readings were within the required Technical Specification level band for the 11 SW accumulator, the 11 SW accumulator was always operable and capable of performing its design basis function. Based on this information, the 4-hour report is being retracted." The licensee will inform the NRC resident inspector. Notified R1DO(Lew). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37612 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-12-17 16:15 | 2000-12-17 17:43 | 2000-12-17 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY The licensee determined that the Emergency Response Data System (ERDS) was unavailable as of 1615 EST on 12/17/00. The Salem TSC lost normal power at 0954 EST and the diesel generator started as designed and supplied power as designed. On loss of normal power to the TSC, the phone line to transmit date from the ERDS system is supplied by a backup battery system with an expected life of 8 hours. At 1615 EST the batteries were down powered and the capability to transmit ERDS to the NRC was loss. Troubleshooting and repairs are proceeding, but the time for restoration is unknown at this time. The licensee intends to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37611 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-12-17 08:23 | 2000-12-17 13:01 | 2000-12-17 | AUTOMATIC ESF ACTUATION - SUPPRESSION POOL CLEANUP ISOLATION "Received isolation of Suppression Pool Cleanup (SPC) System while performing I&C surveillance testing. "A Division 1 RHR/RCIC area temperature isolation signal was input for the test. The actual isolation is normally bypassed during the surveillance. Upon receiving the isolation, the surveillance was secured. "Upon investigation, the screws connecting the terminal block of the isolation bypass switch were found to have backed out such that with the keylock switch taken to the bypass position the contacts of the switch did not change status. "All isolations took place as designed The Division I SPC suction valve (RHS-A0V63) and discharge valve (RHS-A0V64) closed. All RHR valves which receive an isolation on this signal are normally closed valves. The Division I RCIC isolation did not take place due to the isolation signal being removed prior to a time delay relay timing out. "The suppression pool cleanup system was secured." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37610 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2000-12-17 05:45 | 2000-12-17 06:35 | 2000-12-17 | PRIMARY CONTAINMENT ISOLATION DUE TO LIGHTNING STRIKE "During the performance of Primary Containment venting for a planned Primary Containment (Drywell) entry, an invalid ESF actuation occurred. A lightning strike at the Main Offgas Stack caused the B Main Stack Radiation Monitor to lose communications and initiate a Primary Containment Isolation Signal to all Outboard Primary Containment ventilation valves 6" and greater. The Primary Containment Isolation Valves open at the time of Primary Containment venting were the 18" Torus vent valves. The Outboard 18" Torus vent valve was the only ESF actuation. Since the ESF signal was invalid, but caused an actuation of an ESF, this event is reportable under 10CFR50.72(b)(2)(ii)." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 18 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37609 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-12-17 03:12 | 2000-12-17 06:18 | 2000-12-17 | RHR INOPERABLE DUE TO LOGIC FAILURE "Logic for shutdown cooling would have prevented placing the shutdown cooling system in service. System not currently required. A component in the logic system experienced high resistance which simulated a high temperature condition." The licensee has declared the shutdown cooling system inoperable. The NRC resident inspector will be informed of this event by the licensee. | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37608 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-12-16 23:00 | 2000-12-17 00:57 | 2000-12-18 | MANUAL REACTOR TRIP DUE TO CLOSURE OF TURBINE GOVERNOR VALVES "Unit 1 manually tripped the reactor at 2300 on 12/16/00. The unit was in the process of performing main turbine valve operability testing when all four Governor Valves went closed. The crew manually tripped the reactor and entered emergency operating procedures. Primary pressure continued to lower to the Safety Injection actuation setpoint. All ESF equipment actuated and performed as expected with the exception of one Source Range Nuclear Instrument. The cause of the Safety Injection actuation is not fully understood at this time." The NRC resident inspector has been informed of this event by the licensee. ***** UPDATE AT 2330 EST ON 12/18/00 FROM JOHN PIERCE TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from the licensee: "This is a supplemental notification to EVENT #37608 for a [1-hour] report for any event that results or should have resulted in Emergency Core Cooling System (ECCS) discharge into the RCS as a result of a valid signal (10CFR50.72(b)(1)(iv)(B)) and [for a 4-hour] notification [for] RPS actuation and ESF actuation (10CFR50.72(b)(2)(ii))." "Unit 1 was preparing to [perform] main turbine valve operability testing when all four governor valves went closed. Unit 1 was manually tripped at 2300 [CST] on 12/16/2000, and emergency operating procedures were entered. Safety injection occurred approximately 1 minute and 25 seconds following the reactor trip. All ESF equipment responded normally during the safety injection including initiation of auxiliary feedwater (AFW) flow to the steam generators. RCS pressure lowered to approximately 1470 psig within approximately 6 minutes of safety injection actuation prior to recovering and increasing pressure. Taking manual control to close the pressurizer spray valves, after indicating not fully closed, and throttling AFW flow appeared to stop the pressure decrease. Safety injection termination criteria was met, and the safety injection was terminated by approximately 2348 hours [CST]." "The highest RCS pressure was 2303 psig. An adequate margin of subcooling was maintained, and the reactor head area indicated it remained water solid during the transient. Maximum pressurizer level during the event was approximately 63.8%. Following termination of the transient, it was noted that RCS temperature did not return to the expected no-load temperature value. Plant walk down found 3 of 12 steam dump valves approximately 10% open which contributed to the initial plant cooldown. These valves were isolated." "An STP Event Review Team is analyzing plant data to determine the [detailed] sequence of events and cause of event." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Bill Jones). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ECCS INJECTION | ESF ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(ii) | 50.72(b)(1)(iv) | 50.72(b)(2)(ii) |  | 0
37607 | -1 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-12-16 12:03 | 2000-12-16 13:42 | 2000-12-19 | SECURITY REPORT Safeguard system degradation related to area doors and monitoring. Immediate compensatory measures taken upon discovery. The licensee notified the NRC Resident Inspector. Refer to HOO Log for additional details. ***** UPDATE AT 1913 EST ON 12/19/00 FROM TERRY D'ORAZIO TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "An ENS notification was made on 12/16/00 at 1342 [EST] to report the loss of alarm communication function at the [...]. This report was made pursuant to 10 CFR [Part] 73, Appendix G. The loss was compensated for within 10 minutes of discovery by [...]. After a review of NUREG 1304 and Reg Guide 5.62, [the licensee has] concluded that this event is a loggable occurrence, not a 1-hour reportable event. Therefore, the 12/16/00 notification is being retracted." (Contact the NRC operations officer for additional details.) The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Kozak). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 0
37606 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-12-15 17:30 | 2000-12-15 21:27 | 2000-12-15 | 24 HOUR REPORT - SAFETY SYSTEM ACTUATION "At 1730 on 12/15/00, the PSS office was notified that a primary condensate alarm was received on the C-337A position 3 East autoclave Water Inventory Control System (WICS). The WICS system is required to be operable while heating in mode 5 according to TSR 2.2.4.2. The autoclave was checked according to the alarm response procedure, removed from service and the Water Inventory Control System was declared inoperable by the Plant Shift Superintendent. "This safety system actuation is reportable to the NRC as required by Safety Analysis Report, section 6.9, table 1, criteria J.2, Safety System actuation due to a valid signal as a 24-hour event notification. "The NRC Senior Resident inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37605 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-12-15 | 2000-12-15 19:25 | 2000-12-15 | AGREEMENT STATE REPORT The following is taken from an e-mail report: This is notification of an event in Washington state as investigated by the WA Department of Health, Division of Radiation Protection. STATUS: new/closed Licensee: NorthWest Inspection, Inc. City and state: Richland, WA License number: WN-IR065-1 Type of license: Industrial Radiography Date of event: December 15, 2000 Location of Event: Pasco, WA ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) The building where the licensee stores its radiography equipment suffered a major fire in the early morning of December 15, 2000. The building, constructed of concrete block walls with a wood/plywood type roof, is primarily occupied by the local Pipe Fitters Union which has offices, classrooms and a welding test area in the portion of the building that burned. The licensee's industrial radiography camera and a source changer were locked in a 3/8 inch steel, lead-lined, cabinet next to the concrete block wall. Because of the licensee's inability to take immediate protective actions necessary to avoid exposure to sources of radiation or releases of radioactive material that could exceed regulatory limits, the licensee immediately notified the department. For several hours the licensee was not permitted to enter the area to determine whether damage had occurred to his equipment which contains depleted uranium for shielding and one 35 curie Iridium-192 source. The licensee was not able to retrieve the equipment until the debris from the burned out roof was cleared that afternoon. Staff from the department was on-scene to survey the radiography camera and source changer and take appropriate smears to check for contamination. No contamination was noted. The licensee secured the equipment in his truck (normal mode of transportation for these items) pending license amendment for a new storage location. What is the notification or reporting criteria involved? WAC 246-221-250 Notification of incidents (Immediate notification) Activity and Isotope(s) involved: 35 curies Ir-192; depleted uranium. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37604 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-12-14 16:30 | 2000-12-15 18:59 | 2000-12-19 | STOLEN LEAD ANALYZER CONTAINING 6 mCi CADMIUM-109 This report is made under 10 CFR 20.2201(1)(a)(1). A lead analyzer containing 6 mCi of Cd-109, used for checking for lead in paint, was stolen while momentarily unattended in the hall of the Edison Middle School. The school authorities and police have been notified. A reward of $500 has been posted. There is little threat to the public as readings on contact are only 100 - 200 µR/hr when source is exposed. NMED # CA000035 ***** UPDATE AT 1302 EST ON 12/19/00 FROM ROBERT FUNDERBURG TO LEIGH TROCINE ***** The California Radiation Control Program reported that the stolen lead analyzer was returned yesterday. The source was shielded, and it was reported that the individual was not harmed. The NRC operations officer notified the R4DO (Bill Jones) and NMSS EO (Don Cool). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37603 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-10-14 | 2000-12-15 15:37 | 2000-12-15 | AGREEMENT STATE REPORT The following is taken from an e-mail report: This is notification of an event in Washington state as identified by the WA Department of Health, Division of Radiation Protection during a routine license inspection. STATUS: new/closed Licensee: MDS Pharma Services, Inc. City and state: Bothell, WA License number: WN-L0106-1 Type of license: Research lab Date of event: October 14, 1999 Location of Event: Bothell, WA ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH onsite investigation; media attention) On October 14, 1999, a Yellow II packaged from Amersham Corporation, Arlington Heights, IL, was delivered by Federal Express to the licensee. The package contained 5 millicuries of H-3 and 10 microcuries of I-125 in sealed vials. Laboratory personnel measured 10 mR/hr on the package surface with nothing detectable at a meter thus verifying the Yellow II label. The package appeared in good shape and personnel unpacked the contents and determined that the exterior of the vials and inner packaging were free of contamination. However, upon surveying the empty packaging, the outside corner of the outer package was determined to be contaminated. 12,000 counts per minute of removable contamination were noted using a sodium iodide detector. No reading was detected on the wipe using a pancake probe leading the licensee to conclude the source of the activity was most likely I-125. The licensee immediately called ChemTrec which in turn notified shipper. Amersham called the licensee and informed the RSO that Amersham would take care of any additional notifications including the carrier. The licensee documented the event and instituted additional handling procedures for all future receipts. On December 5, 2000, during a routine license inspection by the WA Department of Health, the inspectors noted the incident report and that the licensee had failed to notify the department as required (the department estimated the removable contamination to be 120,000 DPM and thus required to be reported). The licensee was cited for failing to notify the department. This report is being made to complete the record. What is the notification or reporting criteria involved? WAC 246-221-160 Procedures for picking up, receiving, and opening packages. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37602 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-12-14 14:00 | 2000-12-15 12:39 | 2000-12-15 | PART 21 REPORT CONCERNING POSSIBLE INOPERABILITY OF A SAFETY RELATED STATIC INVERTER "On December 14, 2000, Entergy determined that a potential defect existed in the Indian Point 3 safety related 34 static inverter supplied by Westinghouse. Six (6) aluminum electrolytic capacitors manufactured by Mallory Inc. (part number CGS432T200X4C) were purchased from Westinghouse (part number 454A8391110) as commercial grade components. The capacitors were identified as replacement parts in the Westinghouse instruction manual for the 34 static inverter. The capacitors were subsequently dedicated for use in the Indian Point 3 safety related static inverter 34. The dedication program did not identify a mounting restriction since this is not typically a critical characteristic for replacement parts. The Westinghouse instruction manual, used for procurement, did not specify any restriction on mounting orientation. Indian Point 3 (IP3) considers this a deviation. IP3 was notified, by Westinghouse letter dated September 5, 2000, that an internal design change to the capacitor had been made by Mallory that imposed the mounting restriction. Mounting of the capacitors in a horizontal direction could result in catastrophic failure of the component (i.e., short circuit) and render the 34 static inverter and associated instrument bus inoperable. IP3 considers this a potential substantial safety hazard because IP3 is not designed for a postulated design basis accident with a single failure (e.g., failure of another inverter) and the failure of the 34 static inverter. On October 26, 2000 the plant was shutdown and corrective action was completed to replace the inverter capacitors prior to their failure. An operating experience event report is being prepared for distribution to the industry. Westinghouse has discontinued use of this model Mallory capacitor. The Indian Point 3 staff has not ascertained other potential users or uses of the capacitors." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21 |  |  |  | 0
37601 | 0 | U.S. AIR FORCE |  |  |  |  | 2000-12-14 | 2000-12-15 11:05 | 2000-12-15 | DISCOVERY OF RADIOACTIVE MATERIAL AT A SCRAP YARD IN ORLANDO, FLORIDA, THAT COULD POSSIBLY BE TIED TO THE U.S. AIR FORCE At 0950 on 12/15/00, Patrick Air Force Base (AFB) in Florida notified Bolling AFB in Washington D.C. of the discovery of radioactive material that may be tied to the U.S. Air Force at a scrap yard (E&H Car Crushing) in Orlando, Florida. Patrick AFB received the report late in the afternoon on 12/14/00. It was determined that the material involved a rocket body from a titan rocket that belonged to a memorabilia collector who apparently obtained the rocket body from the U.S. Air Force approximately 10 years ago. (The memorabilia collector died, and his estate either transferred or sold the rocket body to the scrap yard.) Other radioactive materials were also discovered in the same vicinity (a 55-gallon drum containing scrap metal, a metal bale, and a titan nose cone), but there is no proof that this other material belonged to either the memorabilia collector or the U.S. Air Force. It was reported that the rocket body contain a magnesium/thorium alloy. However, the activity and percent weight is not know at this time in order to identify whether or not the material meets the unimportant quantity requirements in 10 CFR 40.13, paragraph 4. The U.S. Air Force plans to contact its Occupational Health Team in San Antonio, Texas, in order to have them survey the material next week. They also plan to dispose of the rocket body (at a minimum) and to possibly dispose of the other questionable material as well. It was reported that a law firm surveyed the material and got readings of 2 mR/hour on contact and less than 200 µR/hour at a distance of 5 feet. The type of equipment used to perform these surveys and the qualifications of the individuals taking the surveys for the law firm were not known a the time of this notification. The licensee plans to notify their lawyer as well as the NRC Region 4 office (Chuck Cain). The NRC Region 2 office plans to notify the State of Florida. (Call the NRC operations officer for a contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37600 | 0 | U.S. ARMY |  |  |  |  | 2000-11-16 | 2000-12-15 09:59 | 2000-12-15 | DISCOVERY THAT A LEVEL VIAL CONTAINING 75 MILLICURIES OF TRITIUM WAS MISSING FROM AN M-18 GUNNERS QUADRANT AT FORT POLK, LOUISIANA During an audit at Fort Polk (near Alexandria, Louisiana) on 11/16/00, the licensee discovered that a level vial was missing from an M-18 gunners quadrant. Fort Polk reported this event to Rock Island, Illinois, on 12/05/00. The licensee stated that the missing level vial contained both 75 millicuries of tritium and some amount of alcohol. Apparently, the alcohol portion of the level vial can be broken without breaking the tritium source. In addition, the vial did not have a serial number, and there is no way to specifically identify it. The licensee currently believes that the Army still has possession of the missing source, and it is not believed that the source is in the public domain. The licensee also believes that this event represents an undocumented transfer from one gun to another. It was hypothesized that the alcohol portion of a level vial may have been broken, the broken level vial may have been replaced with an intact level vial from another M-18 gunners quadrant, and the broken vial may have been placed in radioactive waste. The gun crew was interviewed and stated that they were out doing drills on one day. They went out again the next day, and the level vial was missing. The guns had not been moved out of the motor pool, and therefore, the vial did not disappear along the road anywhere. The licensee stated that this was a 30-day report to the NRC. In addition to this notification, the licensee plans to submit a written report to the NRC Region 3 office. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37599 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-12-14 21:30 | 2000-12-15 03:53 | 2000-12-15 | ISOLATION OF A CONTAINMENT INSTRUMENT AIR HEADER FROM ITS NORMAL SUPPLY AND ACTUATION OF THE ASSOCIATED BACKUP NITROGEN BOTTLE BANK PROGRAMMER The following text is a portion of a facsimile received from the licensee: "At 2130 PST, the plant experienced an isolation of the 'B' Containment Instrument Air (CIA) header from its normal supply and actuation of the associated backup nitrogen bottle bank programmer. The isolation and actuation were due to an actual system low pressure caused by performance of a maintenance procedure in conjunction with a failed heater in the non-safety related normal Containment Nitrogen (CN) system." "The CIA system supplies nitrogen to provide motive force for safety-related valves inside the primary containment. The valves are reactor pressure vessel Safety Relief Valves (SRVs) and inboard Main Steam Isolation Valves (MSIVs)." "Evaluation of computer information indicates that pressure on the 'A' CIA header may have been below the administrative allowable value for the associated pressure switch. Investigation continues as to why the isolation and [actuation] involved only the 'B' train." "The plant is stable, and there were no other abnormal occurrences in conjunction with this event." The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37598 | 0 | DRIESENGA & ASSOCIATES, INC. |  |  |  |  | 2000-12-14 08:00 | 2000-12-14 21:28 | 2000-12-14 | TROXLER GAUGE STOLEN AND RECOVERED A model 3440 Troxler moisture/density gauge was stolen from a company truck by cutting the chain restraining it. The theft occurred about 0800 on 12/14/00 in Wyoming , MI. The gauge contains <10 mCi Cs-137 and <50 mCi Am-241. A report was filed with the Wyoming Police Department, who also recovered the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37597 | -1 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-12-14 06:00 | 2000-12-14 18:33 | 2000-12-20 | OVERPOWER CONDITION DUE TO FEED TEMPERATURE CALCULATION ERROR "Braidwood Station Operating License condition 2.C.1 restricts licensed thermal power level to 3411 MW thermal. From December 13, 2000 at 0410 to December 14, 2000 at 0600, Braidwood Unit 2 was operated at a power level of 100.55 percent in violation of this license condition. "On December 14, 2000 at 0600 the station Thermal Performance Engineer discovered that Feedwater inlet temperature was not being calculated correctly by the plant process computer. Following a transfer of computer room ventilation trains on December 12, 2000 at 1800 feedwater calculated temperatures were 3°F higher than actual feedwater temperatures. This resulted in the process computer calorimetric reading 0.6% low. Reactor power was adjusted using this incorrect calculation resulting in the overpower condition. "Following identification of the error, Unit load was reduced to ensure that reactor power was less than 100%. Nuclear instrumentation was verified to be indicating less than 100%. No adjustment to the nuclear instrumentation was performed using the incorrect calculation. "This is being reported pursuant to License Condition 2.g, which requires notification within 24 hours of the violation of any condition in section 2.c of the Operating License." The licensee notified the NRC Resident Inspector. ***** UPDATE AT 1539 CST ON 12/20/00 FROM JIM ROYSTON TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "The initial report to the NRC (Event #37597) was based upon an observation of a 3°F increase in the indicated Feedwater temperature (a primary input to the Calorimetric calculation) following a Computer room temperature change initiated by a swap of the ventilation system. An increase of 3°F in Feedwater temperature results in a 0.55% reduction in Calorimetric power. A declining Calorimetric indication results in Operator action to increase and maintain that indication at 100%. Because of this, the initial indication was that the Unit was inadvertently increased to 100.55%." "Upon execution of troubleshooting it was discovered that the temperature measurement problem was caused by miss-wired RTD temperature elements, which are used to compensate thermocouples for their cold reference junction temperature. From this data, a correction to the temperature measurements was performed such that the true Feedwater temperatures were determined during the event. After applying this correction, it was determined that prior to the event the unit was operating at 99.488%. Following the event, at the highest power level period, the unit was operating at 99.935%. This data also confirms the conclusion that Unit 2 did not exceed 100% power. As an additional check, Calorimetric calculations were performed independently of those executed on the Plant Process Computer which indicate that no problems exist." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Kozak). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0
37596 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-12-14 17:15 | 2000-12-14 18:02 | 2001-10-05 | THE LOCATION OF 2 FUEL PINS IN THE SPENT FUEL POOL IS UNKNOWN "As part of the ongoing decommissioning of Millstone Unit 1, a detailed documentation of the fuel currently in the Unit 1 spent fuel pool is underway. A detailed verification of spent fuel pool content records was part of this effort. During this process, workers identified a discrepancy in the paperwork relating to the location of two spent fuel pins that were removed from a fuel assembly in October 1972. A search is underway; however, these fuel pins have not yet been located among the 2,884 fuel assemblies containing more than 140,000 fuel pins currently in the spent fuel pool. In addition, workers are also searching pertinent records. "Due to the radiation levels of the fuel pins, if they were removed from the spent fuel pool, the use of a shielded cask would have been required and the shipment could have only been made to a licensed facility. Any other movement of these pins from the site would have been immediately detected by the site radiation monitoring system. Therefore, there is a high degree of confidence that these pins are not in an unrestricted area and are under the control of a licensed facility; either here in the spent fuel pool or possibly at a licensed radioactive waste disposal site. As a result, we are also confident that no overexposure of workers or members of the public has resulted. An independent team with relevant expertise is on-site to assist in an ongoing investigation to determine the location of the 2 fuel pins." The licensee notified NRC Region 1 (Todd Jackson) and the state of Connecticut. The licensee intends notifying the NRC Resident Inspector. * * * UPDATE 1031EDT ON 10/5/01 FROM R. MALONEY TO S. SANDIN * * * The licensee is updating this report as follows to include the results of their investigation: "DETAIL: "On October 1, 2001, Northeast Utilities provided its final report on the Millstone Unit No. 1 fuel rod accountability project to DNC (Dominion Nuclear Connecticut). This project was undertaken after it was determined that 2 fuel pins from a Millstone Unit No. 1 spent fuel assembly could not be accounted for. The NU project team conducted extensive inspections of the Millstone Unit No. 1 spent fuel pool as well as comprehensive reviews of material accountability and waste shipment records and interviews of personnel historically involved with these activities. On the basis of this report, DNC concludes it is unlikely that the pins are in the Millstone Unit No. 1 fuel pool. The investigation into the disposition of the pins found no evidence to indicate that the pins were diverted and concluded that the pins were most likely intermingled with other contaminated material removed from the Unit No. 1 spent fuel pool and shipped to a licensed low level waste repository. The report concludes, based on a study performed by a reputable expert, that the health and safety of the public has not been adversely impacted by this condition. "This condition is reportable under 10CFR70.52(a) as a loss of special nuclear material. "ACTIONS TAKEN: "A team of DNC personnel has reviewed the report and interviewed members of the NU project team to obtain clarifications and additional information. A separate root cause is being prepared by NU for this event. "RECOMMENDED ACTIONS: "Incorporate into the MP1 decommissioning plan, as necessary, any DNC recommendations for additional future spent fuel pool inspections. "ADDITIONAL INFORMATION: "Dominion Nuclear Connecticut (the licensee) will be delivering copies of the final report to NRC Headquarters and Region I offices for placement on the docket today (10/05/01)." The licensee informed the NRC resident inspector. The NRC operations officer notified the R1DO (Conte), NRR EO (Tappert), NMSS EO (Brown), IRO (Wessman), NRR IAT (Skelton), NMSS IAT (Weber), NMSS (Essig), Region 1 (Pangburn), OPA (Jasinski), and Liaison Team (Stauss). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOST/STOLEN LNM>10X | LOSS OF SNM/CRIT |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) | 20.2201(a)(1)(ii) | 70.52(a) |  | 0
37595 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2000-12-14 11:50 | 2000-12-14 14:15 | 2000-12-14 | OFFSITE NOTIFICATION TO THE U.S. COAST GUARD ABOUT A FUEL OIL SPILL The licensee notified the U.S. Coast Guard of a spill of less than 5 gallons of diesel fuel oil released to the discharge canal. Absorbent booms are deployed across the discharge canal and in the storm drain discharge to the canal. The licensee notified the NRC Resident Inspector and will notify the state of Arkansas. | 0 | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37594 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-12-14 06:30 | 2000-12-14 08:40 | 2000-12-14 | AUTOMATIC REACTOR TRIP DUE TO A BLOWN CONTROL POWER FUSE ON AN INTERMEDIATE RANGE NEUTRON DETECTOR The following text is a portion of a facsimile received from the licensee: "[The Unit 2] reactor automatically tripped at 0630 [CST] due to a blown control power fuse on intermediate range neutron detector 2N35. Reactor power at the time of the trip was in the source range [10E+4] cps, well below the actual intermediate range trip setpoint. [Unit 2] is exiting a refueling outage, the reactor was made critical at 0543 [CST]. Troubleshooting is in progress. The heat removal mechanism is steam dump discharge from the steam generator atmospheric relief valves. There are no known steam generator tube leaks." The licensee stated that auxiliary feedwater was supplying water to the steam generators both before and after the trip. The unit is currently stable in Mode 3. Pressurizer heaters and sprays, normal charging and letdown, and the reactor coolant pumps are being utilized for primary system pressure, inventory, and transport control. Containment parameters are normal, and offsite power is available. There were no engineered safety actuations or emergency core cooling system actuations, and none were required. The licensee stated that all systems functioned as required and that there was nothing unusual or misunderstood. There were no related maintenance activities ongoing at the time if the trip. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37593 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2000-12-11 12:00 | 2000-12-13 16:30 | 2000-12-13 | AGREEMENT STATE REPORT - FOUR IR-192 SEEDS LOST One ribbon consisting of four Ir-192 seeds with a total activity of 3.2 mCi was lost. The seeds were being used to treat a patient and are believed to have been disposed of accidentally in biomedical hazardous waste. The hospital has been surveyed to no avail. The licensee believes the seeds are being transported to a waste facility in Clinton, IL. The facility has been notified to expect the shipment and to perform the necessary surveys. The licensee will recover the seeds if found at the waste facility. The licensee also contacted the R3 state liaison officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0
37592 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-12-13 07:52 | 2000-12-13 11:52 | 2000-12-19 | SECURITY WEAPON IN A PROTECTED AREA UNACCOUNTED FOR ABOUT 10 SECONDS. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THE EVENT BY THE LICENSEE ***** UPDATE AT 1212 EST ON 12/19/00 FROM MICHAEL GROVES TO LEIGH TROCINE ***** The licensee is retracting this 1-hour event notification following conversations NRC Region 4 office personnel (Bruce Ernest). It was determined that this event was loggable rather than reportable due to the short duration that the weapon was unattended. The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R4DO (Bill Jones). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 0
37591 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-12-12 09:50 | 2000-12-12 18:38 | 2000-12-12 | BULLETIN 91-01 24 HOUR REPORT ON 12/12/00, AT 0950 HOURS IT WAS DISCOVERED BY A NUCLEAR CRITICALITY SAFETY STAFF MEMBER THAT A NUCLEAR CRITICALITY SAFETY APPROVAL (NCSA) SPACING CONTROL WAS LOST IN A SEAL CAN STORAGE AREA WITHIN THE X-333 PROCESS BUILDING. IT WAS IDENTIFIED THAT TWO (2) GROUPS OF SEAL CANS WERE NOT SPACED IN ACCORDANCE WITH CONTROL #9 OF NCSA-PLANT064.A05. THE SPECIFIED NCSA REQUIRES THAT GROUPS OF UP TO FIFTY (50) SEAL CANS CAN BE SPACED A MINIMUM OF 48" EDGE-TO-EDGE. ONE GROUP OF 50 AND ONE GROUP OF 20 SEAL CANS WERE DISCOVERED SPACED AT 46" EDGE-TO-EDGE. THIS EVENT RESULTED IN A LOSS OF ONE CONTROL FOR SPACING (INTERACTION CONTROL) BETWEEN SEAL CAN GROUPS AND OTHER URANIUM BEARING MATERIALS. THE MASS AND MODERATION OF URANIUM IN THE SEAL CANS (ADMINISTRATIVE CONTROLS) AND THE SIZE OF THE SEAL CAN (PASSIVE DESIGN FEATURE) REMAINED INTACT THROUGHOUT THIS EVENT. THUS, ONLY ONE CONTROL RELIED UPON FOR DOUBLE CONTINGENCY WAS LOST. NCSA-PLANT064.A05 CONTROL RE-ESTABLISHED AT 1000 HOURS UNDER THE DIRECTION OF THE NCS ON SCENE STAFF MEMBER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37590 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS |  |  |  |  | 1998-07-15 12:00 | 2000-12-12 15:32 | 2000-12-12 | PART 21 REPORT Pursuant to 10CFR Part 21 Paragraph 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you of a deviation related to a single model 710DU0CL calibration unit with serial number 0515346. As a result of an isolated human error, this single calibration unit was originally shipped in July 1998 with the stable calibration current ramp rate out of specification. This deviation was identified when the calibration unit was returned to Rosemount Nuclear Instruments, Inc for an unrelated issue. The calibration unit has been reworked and now performs within specification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0
37589 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2000-11-30 14:19 | 2000-12-12 13:23 | 2000-12-12 | REACTOR BUILDING DOOR NOT FULLY SHUT - CONTAINMENT INTEGRITY VIOLATED "On November 30, 2000, at 1419, operators discovered that Secondary Containment was breached with the inner rollup door in the Reactor Building track bay not fully closed, and the outer door was inoperable. The Station Shift Supervisor entered Technical Specification Limiting Condition for Operations, 3.4.1.a.2 and 3.4.1.b, which required the initiation of a shutdown if Secondary Containment was not restored within 4 hours. At 1440, operators verified that the inner rollup door was closed with a properly inflated door seal. The Station Shift Supervisor subsequently exited Technical Specification Limiting Conditions for Operation 3.4.1.a.2 and 3.4.1.b. The available information at the time indicated that the door had only been open for 2 hours, 39 minutes. "After completion of an investigation that was delayed due to repairs on the inoperable outer door, on December 12, 2000, at 1215, it was determined that the earlier information about the door being closed was not credible. Based on this conclusion, the door was actually open for 24 hours, 10 minutes. This resulted in a condition that could have prevented the fulfillment of the safety function of secondary containment, that affects the control of the release of radioactive material." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37588 | 0 | USAF RADIOISOTOPE COMMITTEE |  |  |  |  | 2000-12-07 15:00 | 2000-12-12 12:13 | 2000-12-12 | UNACCOUNTED FOR STRONTIUM 90 SOURCE A 500 µCi Sr-90 source used in a helicopter was unaccounted for by the Air Force. The source was discovered on a helicopter with Air Force markings located at Ft. Eustis, Virginia. Although the aircraft had Air Force marking, the Air Force could not immediately account for the source involved or state whether or not the aircraft still belonged to the Air Force. An instructor was showing some students the helicopter when he noticed the source was in the exposed position. The source is part of a device used to look for failures or fractures on the helicopter's blades. A contractor was called and the source was properly stowed. A swipe survey was performed but the results were not known by the caller. The students are believed to be military personnel. The time spent around the aircraft was approximately 50 minutes, however because the source is located near the rotors, exposure is believed to be minimal. This device has an expected dose rate of 75 mr/hr at one foot according to the sealed source device registry. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37587 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-11-21 12:00 | 2000-12-11 19:00 | 2000-12-11 | AGREEMENT STATE REPORT This is notification of an event in Washington state as reported to the WA Department of Health Division of Radiation Protection. STATUS: new (related to events #WA-00-054 and #WA-00-046) Licensee: Transalta Centralia Mining LLC City and state: Centralia, WA License number: WN-I0241-1 Type of license: Fixed Gauge Date of event: November 21 & 23, 2000 Location of Event; Centralia, WA ABSTRACT: (where, when, how, why; cause. contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) The licensee notified the WA Department of Health, Division of Radiation Protection, that replacement rods (installed after source rod failures documented in Washington event reports #WA-00-046 and WA-00-054) had failed on November 21 and November 22. As reported previously, the Ronan Engineering Company Model SA-4 gauging device (containing up to 74 gigabecquerels of cesium-137 in an Amersham Model CDC.711M source) is operated by lowering the source at the end of an approximately six foot source rod into a dry well. The gauge is removed from service by pulling up on the source rod until the source enters the shielded body of the gauge. The source rod was originally constructed in several screw-together sections. Failure number 1 (September 13) was the apparent result of mechanical vibration loosening the upper screw joint until it came apart as the source rod was being lifted. Failure number 2 (October 5) was presumed to be metal fatigue in that the male threaded portion of the lower screw joint snapped off from the rod as it was being lifted. Since an exact replacement rod was no longer available from Ronan, the actual replacement consisted of two rod sections connected at each joint by a spring-loaded brass pin and a short manufactured adapter that was tooled for the pin connector at one end and a threaded male connector at the other. Failure number 3 (November 21) and failure number 4 (November 23) also occurred while lifting the source rod. In both instances, the lower pin-connected joint failed apparently as a result of the increased tension as the source enters the shield overcoming the spring tension on the brass pin, thus 'popping' the connector loose. After the second failure of this type, the gauge was taken out of service and the manufacturer requested to provide an exact replacement rod. The 'old style' screw-together sections were installed December 7. The 'new' pin-connected rods provided for the other three gauges had not been installed because no problems had occurred. The licensee plans to replace all four gauges by the end of 2001 when new process equipment is installed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37586 | -1 | SAN ONOFRE | 1 | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2000-12-11 06:55 | 2000-12-11 10:55 | 2000-12-11 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO MONITORING PROTECTED AREA BOUNDARY. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL DETAILS. * * * UPDATE AT 1543 ON 12/11/00 AT 1543 BY PLUMLEE, RECEIVED BY WEAVER * * * The licensee requested this event be retracted. The event is an example listed in Generic Letter 91-03 as a loggable event and hence should not have been reported. The licensee will notify the NRC resident inspector. The Operations Officer notified the R4DO (Cain). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 0
37585 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-12-11 04:05 | 2000-12-11 04:42 | 2000-12-11 | PLANT ENTERED TECHNICAL SPECIFICATION REQUIRED SHUTDOWN PRIMARY LEAK EXCEEDING ALLOWABLE VALUES. At 0320 Unit 2 received indications of a primary leak in containment that exceeded allowable values in Tech Spec 3.4.6.2. These indications included containment gas activity alert alarm, Pressurizer level reduction, Pressurizer spray valve closure and an increase in charging flow. Indicated charging/letdown mismatch is 7 gpm. Calculated primary leak rate estimate based on VCT and Pressurizer level changes was 9.5 gpm at 0400. At 0412 Unit 2 began a plant shutdown at 2% per minute. This constitutes the initiation of a plant shutdown required by Tech Specs. A containment entry is planned to identify the source of the leak. The entry will be made after the reactor is subcritical. The NRC Resident Inspector will be notified. * * * UPDATE ON 12/11/00 @ 0603 BY THOMAS TO GOULD * * * Update at 0543: Estimated RCS leak rate based on charging/letdown mismatch exceeds 10 gpm. An Unusual Event was declared at 0536 due to Unidentified Leakage exceeding 10 gpm. Current leak rate estimate is between 12 and 20 gpm. Plant is currently at 22% power. The NRC Resident Inspector was notified. FEMA(Bagwell), RDO(Rogge), EO(Zwolinski), and IRO(Miller) * * * UPDATE ON 12/11/00 @ 0825 * * * NRC entered monitoring mode at 0825. * * * UPDATE ON 12/11/00 @ 1412 PER RICK HASSELBERG * * * The plant entered cold shutdown at 1357 and exited the unusual event at 1405. The leak rate has been reduced to 5 gpm. The NRC exited monitoring mode at 1412. FEMA (Canupp), R1DO (White) and NRR EO (Tappert) notified. | 0 | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37584 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-12-09 11:55 | 2000-12-09 13:23 | 2000-12-09 | DISCOVERY OF A DEFICIENCY THAT COULD POTENTIALLY COMPROMISE THE ABILITY OF A FIRE BARRIER TO PROVIDE ADEQUATE PROTECTION IN THE EVENT OF A FIRE The following text is a portion of a facsimile received from the licensee: "During destructive examination of the Kaowool fire barrier system used to protect Appendix R raceways, a deficiency was identified that could potentially compromise the ability of the fire barrier to provide adequate protection for at least one train of redundant safe shutdown capability in the event of a fire. The affected plant area is the Division 2 [engineered safety feature] switchgear room, where redundant functions of both the Division 1 and 2 Standby Service Water systems could be affected. Fire protection program compensatory actions, i.e., [an] hourly firewatch has been in place since the deficiencies as identified in SECY 99-204 were documented at Grand Gulf. The area has detection and automatic fire suppression [systems] that are OPERABLE. Additionally, because of the outcome of the above mentioned examination, a continuous firewatch has been established as an additional compensatory measure." The licensee stated that the hourly fire watch has been in place since 09/01/99. The hourly fire watch is required be technical specifications; however, the continuous fire watch has been established as an additional conservative measure. The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37583 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-12-09 10:15 | 2000-12-09 12:40 | 2000-12-09 | AUTOMATIC REACTOR TRIP DURING PERFORMANCE OF A REVISED PROCEDURE FOR A SOLID STATE PROTECTION SYSTEM (SSPS) AND REACTOR TRIP BREAKER OPERABILITY TEST The following text is a portion of a facsimile received from the licensee: "While performing a new revision to [procedure] 14421-1, 'SOLID STATE PROTECTION SYSTEM AND REACTOR TRIP BREAKER TRAIN B OPERABILITY TEST,' a reactor trip occurred from Intermediate Range High Flux while performing section 5.3, SAFETY INJECTION RESET TIMING CIRCUIT TEST. Both trains of [the] reactor protection system functioned as expected. A feedwater isolation was received as expected from P4-Low Tavg, but only from SSPS Train A due to SSPS Train B being in 'TEST' for the surveillance in progress. Also, an [auxiliary feedwater] actuation signal (AFWAS) was received from Steam Generator Lo-Lo level in all four steam generators, but only the [turbine-driven auxiliary feedwater pump] pump and [motor-driven auxiliary feedwater pump] pump A started, again due to SSPS Train B being in 'TEST.' The steam generator blowdown system also isolated properly on the AFWAS signal. The plant is currently stable in Mode 3, and an Event Review Team is currently being formed. At 1207, Train B SSPS was restored to [its] normal configuration. No estimated restart date is currently available." The licensee stated that all control rods fully inserted as a result of the trip. It was also reported that all systems functioned as required based on the configuration of the plant at the time of the event (SSPS Train B in test) and that there was nothing unusual or misunderstood. The root cause of the reactor trip is currently under investigation. The unit is currently stable in Mode 3 (Hot Standby). Normal charging and letdown, pressurizer heaters and sprays, and the reactor coolant pumps are being utilized for primary system inventory, pressure, and transport control. Secondary steam is being dumped to the condenser, and auxiliary feedwater is being supplied to the steam generators. All containment parameters are normal, and offsite power is available. The NRC resident inspector was in the control room watching performance of the surveillance procedure at the time of the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37582 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-12-04 05:30 | 2000-12-08 20:06 | 2000-12-08 | STOLEN ASSOCIATED SOILS ENGINEERING, INC, MOISTURE DENSITY GAUGE The following text is a portion of a facsimile received from the State of California, Department of Health Services, Radiologic Health Branch: "A CPN Moisture/Density gauge, model MC1 DR, S/N MD 01005909, was picked up from the office [in Long Beach, CA] on 12/03/00. It was locked down in the back of the truck of the gauge user [...]. The gauge was stolen between 2100 [PST] on 12/03/00 and 0530 [PST] on 12/04/00 from [the user's] trailer [park located in ...] Orange, CA [...]." It was reported that the licensee notified the local Police Department and that the gauge contained an unknown quantity of americium-241/beryllium. (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37581 | 0 | TRU-TEC SERVICES, INC. |  |  |  |  | 2000-12-08 03:30 | 2000-12-08 18:47 | 2000-12-11 | RECEIPT OF A TRU-TEC SERVICES, INC., CONTAINER OF BROMINE-82 THAT APPEARED TO HAVE BEEN OPENED AND RE-PACKAGED INCORRECTLY DURING TRANSPORT BETWEEN TEXAS A&M AND ST. CROIX IN THE VIRGIN ISLANDS On 12/04/00, Tru-Tec Services, Inc., shipped an empty container from their facility in La Porte, Texas, to Texas A&M via Acme Trucking. The container was similar in shape to a propane tank (but taller). It was lead filled and weighed between 700 and 750 pounds. It also had a 3-inch by 3-inch cavity inside and a lid with a T-bar to hold the lid in place. Texas A&M loaded the empty container with bromine-82, and the activity of the bromine-82 at noon on 12/04/00 was 900 millicuries. The bromine-82 was double encapsulated (inside three glass ampoules which were also inside a metal swagelock container with a screw on cap). After Texas A&M loaded the container, Acme Trucking transported the container to Federal Express at Intercontinental Airport in Houston, Texas, on 12/04/00. Apparently, the container arrived at a Federal Express hub in Memphis, Tennessee, on 12/05/00, and it remained there until 12/07/00. On 12/07/00, the shipment left Memphis, Tennessee, via Federal Express and arrived in Puerto Rico on the morning of 12/08/00. It was then transported by 4 Star Air Cargo to St. Croix in the Virgin Islands. Tru-Tec Services, Inc., received the container between approximately 1600 and 1630 EST on 12/08/00. Upon arrival in St. Croix, Tru-Tec personnel discovered a problem with the container. It appeared that the container had been opened and put back together incorrectly. The container's T-bar was missing, and the lid was upside-down with the bromine-82 on the outside of the container rather than shielded on the inside of the container. The bromine-82 appeared to be intact. Smear tests were performed using a GM detector, and there was no evidence of contamination or of a breech in the double encapsulated material. Survey readings with the bromine-82 unshielded on the outside of the package resulted a dose rate of 6 millirem per hour at a distance of 6 feet. The bromine-82 is currently under control and in the possession of the Tru-Tec Services, Inc. The bromine-82 was intended for use in tracer studies at chemical plants, and it was manufactured at Texas A&M. It was reported that the half life of bromine-82 is 35 hours, and the estimated activity of the material at noon on 12/08/00 would have been 140 millicuries. bromine-82 is a strong gamma emitter. The Tru-Tec Services, Inc. main office is located in Delaware. The licensee plans to contact the carriers and plans to attempt to trace its path and discover who came into contact with the container. (Call the NRC operations officer for licensee contact information.) * * * UPDATE ON 12/11/00 @ 1140 BY BRIAN SMITH(NMSS) TO GOULD * * * Correction of the dose rate from 6 millirem per hour to 60 millirem per hour at a distance of 6 ft. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | TRANSPORTATION EVENT | [8 empty] | NON EMERGENCY | 4 | TX | MAT | [5 empty] | 0
37580 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-12-08 11:15 | 2000-12-08 12:07 | 2000-12-08 | DISCOVERY OF SURFACE RADIATION READINGS IN EXCESS OF TRANSPORTATION LIMITS ON 3 OF 30 CYLINDERS SHIPPED FROM WESTINGHOUSE ELECTRIC COMPANY IN COLUMBIA, SOUTH CAROLINA At 1115 hours on 12/08/00, USEC Portsmouth health physics personnel determined that an inbound shipment of empty, 2.5-ton, healed cylinders had external radiation levels in excess of the limits in 10CFR71.47. The shipment involved 30, empty, 2.5-ton, healed cylinders from Westinghouse Electric Company in Columbia, South Carolina; and surveys showed that three rear cylinders had radiation readings of 225 to 250 millirem per hour on contact. This exceeds the 10CFR71.47 limit of 200 millirem per hour and meets the 1-hour reporting criteria of 10CFR20.1906(d)(1). The truck will be properly dispositioned on the plant site. Portsmouth personnel are in the process of making notifications to Westinghouse Electric Company (the shipper) and Hitman Transport Company (the carrier). There was nothing unusual or misunderstood, and all systems functioned as required. Portsmouth personnel notified the NRC resident inspector and plan to notify the Department of Energy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | [10 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37579 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-12-08 06:30 | 2000-12-08 08:05 | 2000-12-08 | UNIT 1 EXPERIENCED A REACTOR TRIP/TURBINE TRIP DUE TO LOW-LOW STEAM GENERATOR WATER LEVEL "Unit 1 reactor and turbine trip, first out annunciator was '13' steam generator low-low level. Preliminary indications are that a feedwater isolation signal was generated, although actual conditions were not present. This resulted in the feed reg and its bypass valves closing, resulting in the low-low level. All aux feedwater pumps started on the level signal and maintained steam generator water inventory. The plant is currently in mode 3 (hot standby) at normal operating temperature and pressure." All control rods fully inserted. The main condenser is in service removing decay heat via the bypass valves. There were no maintenance activities ongoing which could have resulted in the trip. All systems functioned as required. The licensee will inform local agencies and has informed the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37578 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-12-07 22:55 | 2000-12-07 23:35 | 2000-12-07 | LOSS OF THE PROMPT NOTIFICATION SYSTEM The following text is a portion of a facsimile received from the licensee: "A complete loss of the prompt notification system has occurred [at 2255], which [is] considered to be a major loss of offsite notification capability. The prompt notification system is a NOAA weather radio system [out of Jacksonville, Florida]." The licensee stated that people are currently being dispatched to work on the problem and that the system was returned to service at 2335. The licensee notified applicable state and local officials and plans to notify the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37577 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-12-07 | 2000-12-07 20:10 | 2000-12-07 | AGREEMENT STATE REPORT REGARDING THE DISCOVERY THAT A PACIFIC TECHNICAL INDUSTRIES RADIOGRAPHER'S EXPOSURE EXCEEDED 5 REM ANNUAL LIMIT The following text is a portion of a facsimile received from WA Department of Health (DOH), Division of Radiation Protection: "This is notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection." "STATUS: new" "Licensee: Pacific Technical Industries" "City and state: Bellevue, WA" "License number: WN-1R053-1" "Type of license: Industrial radiography" "Date of event: November 2000" "Location of Event: Bellevue, WA" "ABSTRACT (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention)[:] An industrial radiographer has exceeded the annual exposure limit of 5 rem. The licensee was notified by the dosimetry service on September 27 that the radiographer had received 4.3 rem through August 2000. The Department mailed a copy of [Information Notice] IN 2000-15 to all radiography licensees on October 26. Upon receipt of the Information Notice, the licensee was prompted to review the radiographer's daily pocket dosimeter records and at that time determined that the total dose was already likely to be 5.1 rem. The radiographer was immediately reassigned to non-radiation work, the dosimeter was sent for processing, and the Department was notified. On December 7, the licensee reported the results of the dosimetry as received from the dosimetry service. The radiographer had received 5.217 rem. The licensee indicated that the radiographer had received more exposure than usual due to a heavy workload in confined spaces such as tanks and other vessels where getting in and out was difficult or even hazardous. The relatively short exposure times involved led the radiographer to remain in the confined space hut as far as practical from the source and crank handle. The licensee is being cited for failure to control the exposure of the radiographer." "What is the notification or reporting criteria involved? WAC 246-22l-010 Occupational limits for adults." "Activity and Isotope(s) involved: Curie amounts of Ir-192" "Overexposure? (Number of workers/members of public; dose estimate; body part receiving dose; consequence)[:] One radiographer received 5.217 rem whole body exposure; 5.210 rem to the lens; and 5.248 rem shallow dose." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37576 | 0 | HUNT VALVE COMPANY, INC. |  |  |  |  | 2000-12-06 | 2000-12-07 19:19 | 2000-12-07 | 10 CFR PART 21 REPORT OF A DEVIATION - IDENTIFICATION OF A DEFECT WITH A COMPONENT ON VALVE ASSEMBLIES SUPPLIED TO USEC The following text is a portion of a facsimile received from Hunt Valve Company, Inc.: "We have discovered a material failure within our manufacturing process for the 1" UF-6 valves manufactured in accordance with ANSI N14.1. During our normal visual inspection[,] a few packing nuts were noted to have cracks located on the hex flats. These cracked packing nuts have been isolated to heat codes AXP and AFD." "These valves were manufactured and shipped against contract No. 566948 for USEC. Our records indicate that we have shipped Lot Serial [Nos.] 200027-36 through 200027-40 containing the heat code AXP packing nuts, and Lot Serial [Nos.] 200027-5 [and] 200027-19 through 200027-35 containing heat code AFD. The total number of valves included in these shipments is 2,300 of which 1,300 are known to be from the affected heat codes (see attached table). All other inventory has been accounted for and isolated. These valves have been located at USEC and are being returned to Hunt Valve for replacement nuts." "We are currently undergoing an investigation to determine the source of the defect but feel compelled to inform you by this communication of our preliminary findings. [...]." "Heat Code Lot Serial [No.] Date Shipped Quantity (Total Supplied) AXP (735 pcs) 200027-36 11/22/00 97 200027-37 11/22/00 100 (233 in stock 12/4/00) 200027-38 11/22/00 100 (100 on a shipment in shipping) 200027-39 11/22/00 100 200027-40 11/22/00 100 AFD (972 pcs) 200027-5 5/31/00 10 200027-19 8/14/00 9 (294 in stock 12/4/00) 200027-20 8/14/00 7 200027-21 8/31/00 30 200027-22 8/31/00 44 200027-23 8/31/00 39 200027-24 8/31/00 33 200027-25 8/31/00 29 200027-26 10/5/00 53 200027-27 10/5/00 52 200027-28 10/5/00 67 200027-29 10/5/00 54 200027-30 10/5/00 62 200027-31 11/3/00 58 200027-32 11/3/00 45 200027-33 11/3/00 23 200027-34 11/3/00 35 200027-35 11/3/00 28" (Call the NRC operations officer for contact information). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0
37575 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-11-07 | 2000-12-07 14:29 | 2000-12-07 | LOSS OF A RADIOACTIVE CALIBRATION SOURCE CONTAINING 0.022 MICROCURIES OF AMERICIUM-241 The following text is a portion of a facsimile received from the licensee: "[...] This is a non-emergency event being reported in accordance with 10 CFR 20.2201(a)(2)(i) which references [10 CFR] 50.72. The event did not directly affect operation of Oconee unit(s) 1, 2, or 3." "[...] This report is categorized under 10 CFR 20.2201(a)(1)(ii)." "[...] Description of event:" "On [11/07/00,] a radioactive calibration source, designated as ONS-1075, was recognized as missing inside the Oconee restricted area. Following an unsuccessful search, it was classified as lost. [10 CFR] Part 20 requires a telephone report to the NRC Operations Center within 30 days from the date of loss of this quantity of licensed material. In addition, 10 CFR 20.2201(b) requires a written report within 30 days following the telephone report. The written report will be submitted within that period." "Description of the lost licensed material[:]" "The lost calibration source was a 47 mm glass fiber filter material impregnated with 0.022 microcurie[s] of [Am]-241, covered with mylar and contained in a stainless steel planchet. This quantity is 22 times the 10 CFR [Part] 20, Appendix C quantity. For comparison, the average home smoke detector contains a source of approximately 1 microcurie." "Circumstances under which the loss occurred[:]" "On 10/30/00[,] an individual used the source used to calibrate a radiation measuring device. Prior to returning the source to its storage location, the individual, who was experiencing elevated blood pressure, was relieved from duty and was referred to his personal physician. On 11/07/00, after being released to return to work by his physician, the individual resumed the calibration process and noted the absence of the calibration source." "Probable disposition of licensed material[:]" "Following a search and investigation associated with the missing calibration source (see below), it was concluded that the most probable disposition of the lost source was inadvertent disposal as dry active waste." "Exposures of individuals to radiation[:]" "No individuals are believed to have been exposed to this material. A dose assessment assuming a hypothetical maximally exposed individual concluded that external exposure would be negligible, and internal dose would be 49 mRem CEDE if ingested or 11.4 Rem CEDE if inhaled. Given the probable disposition and physical characteristics of this source, it is unlikely that this source was ingested or inhaled; therefore, it is not considered credible that any individual could receive the maximum calculable dose from this source." "Action taken to recover the material[:]" "On 11/07/00[,] the individual conducted a search of the source's storage area and all reasonable areas where the source would be used in order to continue the calibration. When the source was not found, the individual notified his supervisor, and the search was expanded to include the individual's office area and some personal effects. Because the calibration source is very similar in appearance to common samples used to quantify removable surface radioactive contamination, it was suspected that the calibration source had been mistakenly discarded as sample waste. No dry active waste shipments had been made during the elapsed time between 10/30/2000, when the source was last known to have been used, and 11/7/00, when the search was conducted. However, a significant amount of waste had accumulated at the collection point. This waste was visually searched, but the source was not located." "Measures that have been, or will be, adopted to ensure against a recurrence of the loss of licensed material[:]" "This type of calibration source is similar in appearance to routine samples prepared for counting in the detector. Oconee will pursue a method for better marking of these sources to minimize the possibility of a source being visually mistaken for a waste sample." The licensee notified the NRC resident inspector. NOTE: The licensee stated that Oconee Unit 1 was operating at 100% power at the time of the event (on 11/07/00). However, the Unit 1 is currently defueled as part of a planned refueling outage. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0
37574 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2000-12-06 19:00 | 2000-12-07 11:43 | 2000-12-07 | 24-HOUR NRC 91-01 BULLETIN REPORT INVOLVING LOSS OF MASS AND DENSITY CONTROLS IN TWO CARRYOVER STORAGE TANKS "At approximately 1900 hours on December 6, 2000 GNF-A Operations identified that two tanks, believed to be empty, contained liquid bearing very low concentrations of uranium. The tanks involved are V-109B and V- 113. "The total mass of uranium involved is 282 grams U, well below the established safe mass limit of 22,036 grams U at 5% enrichment. No unsafe condition existed. "The accumulation occurred due to carryover via a common Vent Off-Gas (VOG) system from V-104 to the two tanks found to contain liquid. The independent mass and density controls on V-104 remained fully functional. The potential for carryover via the VOG system was not anticipated and represents an unanalyzed condition. "The solution in both V-109B and V-113 was sampled and pumped back into V-104 under the direction of Nuclear Safety. The total solution volume in V-109B was 2960 gallons with a concentration of 22 ppm U (~247 grams U). The total solution volume in V-113 was 1,507 gallons with a concentration of 6.1 ppm U (~35 grams U). The VOG header has been isolated to prevent reoccurrence. Investigation and additional corrective actions are pending. "This event is reported pursuant to NRC Bulletin 91-01 (within 24 hours) due to identification of an unanalyzed condition involving less than a safe mass of uranium." SAFETY SIGNIFICANCE OF EVENTS: Low safety significance - low concentration POTENTIAL CRITICALITY PATHWAYS INVOLVED BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Multiple failure modes required before a criticality accident could occur. Incident involves less than a safe mass of uranium. CONTROLLED PARAMETER(S) (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Mass: V-104 process vessel limited to safe mass by upstream active engineered controls on uranium concentration in material feed (independent uranium monitor and pipe detector NDA measurement). Density: independent differential pressure density control tied to particulate removal (centrifugation) and air sparging. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST BASE CRITICAL MASS): Affected equipment Contained < 300 grams of uranium (total). Established safe heterogeneous mass limit for U02 enriched to 5% is 25 kgs (or 22. 036 grams U). NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The 4-inch overflow line located on tank V-104 beneath the VOG header failed to prevent carryover into the VOG header. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Solution in V-109B and V-113 sampled for U concentration, results acceptable. 2. Solution in V-109B and V-113 pumped back into V-104; VOG header tie-in blank flanged to prevent reoccurrence. 3. Investigation and additional corrective actions pending. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0
37573 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2000-12-06 09:42 | 2000-12-06 11:48 | 2000-12-06 | REACTOR SCRAM - LOW REACTOR VESSEL WATER LEVEL An automatic reactor scram occurred on low reactor vessel water level. All systems responded as expected. Operators noted lowering reactor vessel water level and were attempting to respond to the problem when the low reactor vessel water scram setpoint was reached. The lowest water level seen during the transient was -10", neither HPCI nor RCIC started. Reactor feedwater was maintained throughout the event. Recirculation pumps are running and decay heat is being removed by steaming to the main condenser. The cause of the feedwater transient is under investigation. The licensee notified NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37572 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2000-12-06 | 2000-12-06 11:38 | 2000-12-12 | AGREEMENT STATE REPORT INVOLVING TWO STOLEN MOISTURE DENSITY GAUGES "This First Notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation, and is basically all that is known by the Agency Staff at this time. "Date: December 6, 2000 Time: 9:00 AM (MST) First Notice: 00-16 "Arizona Licensee: Dames and Moore License No. 07-228 7500 North Dreamy Draw Drive Phoenix, AZ 857020 "At approximately 2:00 PM, December 5, 2000, the Agency received a report advising that 2 Troxler Model 3440 moisture/density gauges were missing. This information was supplied by the Dames and Moore Radiation Safety Officer. The information supplied indicated that the LICENSEE was unsure when the gauges were taken. They were last seen on December 4, 2000 in a locked storage building at 1790 East River Road, Tucson, AZ. Each gauge contains a 8 millicurie cesium 137 source and a 44 millicuries Americium 241 :Beryllium source. The serial numbers for the gauges are 13024 and 17318. The storage building was locked and had 24 hour security guard surveillance. The lock had been cut. Tucson PD is investigating this matter. The LICENSEE is offering a $500.00 reward. The Agency will be issuing a press release. "The LICENSEE and the Agency continue to investigate this event. "The states of Utah, California, Colorado, New Mexico, and Nevada together with the U.S. NRC, the U.S. FBI and Mexico are being notified of this event." * * * UPDATE AT 1632 ON 12/12/00 BY FAX * * * Text of Fax provided by the Arizona Radiation Regulatory Agency. "The Agency Duty Officer received a call from the DPS Duty Officer at about 7:00 PM indicating that a teenage boy had found one of the Soil Density Moisture Gauges and had taken it to his home. Arrangements were made by the Agency to dispatch two people to pick up the gauge. The first gauge was discovered by three teenage boys in Tucson and brought to the boys' home. The condition of this gauge (SN: 17315) was excellent. The second gauge (SN: 13024) was discovered on a dirt road at the East end of Linda Vista Rd. approximately 5 miles north of the first site. Again, this gauge was in excellent condition. Leak tests were taken of both gauges and are being evaluated by the agency. The gauge carrying cases were both intact. However, the gauges could not be secured with locks through the gauge handles. Also, at the second site were found two additional pieces of equipment that had been taken from the original storage shed. The gauges were released to a Dames and Moore representative." The operations center informed the R4DO (Cain) and NMSS EO (Greeves). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0
37571 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2000-12-04 15:30 | 2000-12-05 15:55 | 2000-12-05 | PERSON RECEIVED GREATER THAN 50 REM TO THE SKIN THIS EVENT AS FAXED IN NEN Life Sciences Product's called to report an event which resulted in one person receiving greater than 50 rem to the skin. On December 4, 2000, at approximately 1530 hours, an NEN Life Sciences employee was transferring remotely 3.5 curies in 3 ml of Yttrium-90 in a vial from it's shielded dispensing container back to storage in a hot cell. During the transfer the cap fell off, allowing the vial to fall from the remote handling device and causing the material to be splashed onto the employee. The employee immediately contacted on site Radiation Safety Officer, who decontaminated the employee and had the employee shower. Initial dose estimate for the highest effected area is 230 rads to the skin of the chin. A preliminary bioassay indicates an uptake of less than 1 microcurie; more bioassays will be taken. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0
37570 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-12-05 10:08 | 2000-12-05 12:00 | 2000-12-05 | OFFSITE NOTIFICATION MADE DUE TO SPILLING 35 GALLONS OF HYDRAULIC FLUID. A 4 hour non-emergency report is being made in accordance with 10 CFR 50.72 (b)(2)(vi) for an event where notification to a state agency has been made. At approximately 1020 hours on December 5, 2000, offsite notification was made to the Virginia State Department of Environmental Quality (DEQ) and the Local Emergency Planning Coordinator. At approximately 0905 hours on December 5, 2000, hydraulic fluid from a crane, located outside the protected area, leaked to the ground. Clean up activities were initiated and the spill was contained. At the time of the spill the ground adjacent to the crane was frozen keeping the fluid on the surface. No fluid reached any navigable waters. The quantity of hydraulic fluid that leaked to the ground was determined by refilling the hydraulic fluid reservoir and measuring the delta. At 1008 hours on December 5, 2000, it was determined 35 gallons of fluid leaked to the ground. The leak was the result of a broken clamp on a hydraulic fluid hose. Station procedures require immediate notifications if more than 25 gallons of oil are released to the soil. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37569 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2000-12-05 | 2000-12-05 10:10 | 2006-03-01 | LOST STRONTIUM-90 SOURCE The United States Cattle Corporation went out of business and sold all its equipment to Southern Diversified of Baldwin, MS in 1999. Included was a WebArt/1000 MSP source of 25 mCi of Sr-90 (it would be 17 mCi today by calculation). The Mississippi Division of Rad Health was not informed of the transfer. When this was discovered the state office tried to locate the source. Contacting Southern Diversified it was determined that all the materials were scrapped at Northeast Metal Processors in Plantersville, MS. The state conducted a search at the yard without finding the source. The source is presumed lost. * * * UPDATE AT 1029 EST ON 3/1/06 FROM B.J. SMITH TO S. SANDIN * * * The following information was received via email: "Location of Incident: Northeast Metal Processors at Plantersville, MS "Description of Incident: Received notification on 2-21-06 at 3:00 PM from Ohmart/Vega Corporation that a Ohmart radioactive device was found by a scrap metal facility. The gauge was a Ohmart Model BAL/WebArt/1000 containing 25 mCi of Strontium-90, Serial No. 10133. Apparently, a load of scrap was sent to Nucor Steel in Tuscaloosa, AL, where it set off the alarm at the scale monitor. The load was returned to the scrap metal facility in Mississippi. DRH contacted Northeast Metal Processors and determined that the device had been reported as lost in March 2000 (NRC Event # 37569). The gauge was originally purchased by U. S. Cattle Corporation. In 1999, U.S. Cattle sold all its machinery to Southern Diversified located in Baldwin, MS. During the investigation that occurred in 2000, it was determined that the gauge was lost and a lot of the metal was sold to Northeast Metal Processors. DRH had sent a inspector to Southern Diversified and Northeast Metal to search for the gauge with no success. "Isotope(s): Strontium-90 "Activity: 25 mCi as of 11-84 "Date of Incident: 2-20-06 "Date Reported To DRH: 2-21-06 at 3:00 PM "Describe clean-up actions taken by DRH: DRH went to Northeast Metal Processors on 2-22-06 and picked up the gauge. The gauge is now stored at DRH headquarters awaiting disposal. "List radiation measurements taken by DRH: 70 mR/hr at surface. Average 2 mR/hr surface of gauge. DRH also performed leak tests of the source. "List any other actions required of DRH: Contacted Southern Diversified about disposal of gauge. DRH has already arraigned for contractor to pick up gauge for disposal. "List any actions taken to notify NRC, other Agreement States: NRC notified on 2-23-06 by e-mail. NMED also e-mailed. "Case Closed: Yes "Date Closed: 2-23-06 "Record of incident in RAM files: Yes "Enforcement action taken: None taken." MS Report No.: MS 06005 Notified R1DO (Cahill) and NMSS (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0